## 2020
RELIABILITY INDICES FOR MAT 08W CIRCUIT HARDENING PROJECT (2020)
DISTRIBUTION CIRCUIT OUTAGES ONLY
(Excluding 2.5b ME Days, ISO, Planned, Equipment Failure/Underground Outages)
Division | Feeder Name | Feeder # | Year | AIDI | AIFI | CAIDI | SO | CESO | C Min | Tot Cust | Miles (from Project List) | OH Miles | UG Miles | Total Miles
CENTRAL COAST | BEN LOMOND 0401 | 83040401 | 2020 | 147.7 | 2.246 | 65.8 | 9 | 1705 | 112116 | 759 | 21.0436 | 21.11 | 0.56 | 21.67
CENTRAL COAST | BEN LOMOND 1101 | 83041101 | 2020 | 601 | 5.977 | 100.6 | 28 | 4399 | 442328 | 736 | 15.1406 | 15.09 | 0.34 | 15.43
CENTRAL COAST | BIG BASIN 1101 | 82841101 | 2020 | 221.9 | 2.533 | 87.6 | 95 | 5816 | 509489 | 2296 | 55.6459 | 54.95 | 2.07 | 57.02
CENTRAL COAST | BIG TREES 0402 | 83050402 | 2020 | 195.4 | 2.672 | 73.1 | 13 | 2319 | 169629 | 868 | 16.5803 | 16.53 | 0.11 | 16.65
CENTRAL COAST | BURNS 2101 | 183582101 | 2020 | 418.4 | 3 | 139.5 | 7 | 87 | 12134 | 29 | 1.7044 | 1.68 | 0.01 | 1.69
CENTRAL COAST | CAMP EVERS 2103 | 83622103 | 2020 | 258.7 | 2.687 | 96.3 | 24 | 8784 | 845590 | 3269 | 46.8113 | 59.69 | 9.24 | 68.93
CENTRAL COAST | CAMP EVERS 2104 | 83622104 | 2020 | 159.3 | 1.758 | 90.6 | 23 | 5242 | 475103 | 2982 | 27.8594 | 36.21 | 18.04 | 54.25
CENTRAL COAST | CAMPHORA 1101 | 182071101 | 2020 | 50.6 | 0.408 | 124 | 8 | 138 | 17108 | 338 | 5.9826 | 58 | 1.94 | 59.93
CENTRAL COAST | CASTROVILLE 2104 | 182352104 | 2020 | 19.7 | 0.187 | 105.5 | 3 | 90 | 9494 | 481 | 0 | 50.05 | 8.85 | 58.89
CENTRAL COAST | COAST RD 0401 | 88820401 | 2020 | 0 | 0 | 128.3 | 4 | 182 | 23346 | 0 | 0.63308 | 0 | 0 | 0
CENTRAL COAST | DEL MONTE 1101 | 182221101 | 2020 | 16.1 | 0.698 | 23 | 3 | 2374 | 54617 | 3402 | 0.53069 | 14.88 | 11.29 | 26.17
CENTRAL COAST | DEL MONTE 2102 | 182222102 | 2020 | 4.2 | 0.039 | 107.8 | 4 | 156 | 16809 | 4029 | 0.94774 | 15.98 | 15.99 | 31.97
CENTRAL COAST | DEL MONTE 2103 | 182222103 | 2020 | 137.8 | 2.078 | 66.3 | 18 | 8195 | 543314 | 3944 | 15.1467 | 32.42 | 17.15 | 49.57
CENTRAL COAST | DEL MONTE 2104 | 182222104 | 2020 | 23.5 | 0.358 | 65.7 | 17 | 2372 | 155737 | 6623 | 60.9659 | 78.95 | 103.36 | 182.31
CENTRAL COAST | DOLAN ROAD 1101 | 182381101 | 2020 | 284.6 | 2.453 | 116 | 11 | 5070 | 588254 | 2067 | 4.0044 | 68.59 | 5.6 | 74.19
CENTRAL COAST | FELTON 0401 | 83140401 | 2020 | 20.9 | 1.063 | 19.7 | 2 | 51 | 1005 | 48 | 2.5249 | 2.55 | 0.66 | 3.21
CENTRAL COAST | FORT ORD 2106 | 182402106 | 2020 | 1.3 | 0.134 | 10 | 1 | 522 | 5220 | 3897 | 2.7942 | 24.49 | 25.02 | 49.51
CENTRAL COAST | FORT ORD 2107 | 182402107 | 2020 | 11.5 | 0.112 | 102.9 | 3 | 380 | 39108 | 3387 | 4.0848 | 19.36 | 13.8 | 33.17
CENTRAL COAST | GABILAN 1101 | 182331101 | 2020 | 37.3 | 0.226 | 164.7 | 14 | 971 | 159897 | 4290 | 6.604 | 71.68 | 26.49 | 98.17
CENTRAL COAST | GONZALES 1101 | 182131101 | 2020 | 44.3 | 1.004 | 44.1 | 2 | 1842 | 81246 | 1835 | 4.0888 | 25.87 | 8.68 | 34.54
CENTRAL COAST | GONZALES 1104 | 182131104 | 2020 | 657.4 | 1.452 | 452.7 | 26 | 848 | 383911 | 584 | 0.90201 | 53.97 | 0.57 | 54.55
CENTRAL COAST | HATTON 1101 | 182291101 | 2020 | 148.2 | 1.847 | 80.3 | 14 | 4806 | 385684 | 2602 | 13.9372 | 25.23 | 97.62 | 122.84
CENTRAL COAST | HATTON 1102 | 182291102 | 2020 | 34.8 | 1.069 | 32.6 | 6 | 2295 | 74763 | 2147 | 11.6254 | 22.37 | 12.37 | 34.75
CENTRAL COAST | HOLLISTER 2104 | 182492104 | 2020 | 94.2 | 0.317 | 296.8 | 18 | 671 | 199160 | 2114 | 6.338 | 120.99 | 15.85 | 136.84
CENTRAL COAST | HOLLISTER 2105 | 182492105 | 2020 | 58.9 | 0.59 | 99.9 | 19 | 2014 | 201247 | 3415 | 67.4841 | 156.46 | 31.99 | 188.45
CENTRAL COAST | HOLLISTER 2106 | 182492106 | 2020 | 10.5 | 0.074 | 142.8 | 8 | 314 | 44828 | 4258 | 8.7531 | 39.68 | 28.99 | 68.67
CENTRAL COAST | JOLON 1102 | 182981102 | 2020 | 151.4 | 1.863 | 81.3 | 22 | 1133 | 92080 | 608 | 70.9105 | 103.95 | 3.15 | 107.1
CENTRAL COAST | JOLON 1103 | 182981103 | 2020 | 377.8 | 1.235 | 305.9 | 2 | 21 | 6423 | 17 | 13.1598 | 8.84 | 0.27 | 9.11
CENTRAL COAST | KING CITY 1103 | 182031103 | 2020 | 4.5 | 0.004 | 1009.3 | 2 | 9 | 9084 | 2002 | 18.3291 | 27.45 | 13.21 | 40.66
CENTRAL COAST | LAURELES 1111 | 182371111 | 2020 | 430.5 | 1.818 | 236.8 | 46 | 2900 | 686655 | 1595 | 106.0334 | 106.04 | 11.13 | 117.17
CENTRAL COAST | LAURELES 1112 | 182371112 | 2020 | 129.2 | 1.139 | 113.5 | 12 | 2057 | 233386 | 1806 | 28.1644 | 35.84 | 8.64 | 44.48
CENTRAL COAST | LOS COCHES 1101 | 182151101 | 2020 | 6.1 | 0.063 | 96 | 1 | 9 | 864 | 142 | 2.6193 | 30.35 | 0.3 | 30.65
CENTRAL COAST | LOS OSITOS 2102 | 182082102 | 2020 | 49.8 | 0.191 | 261.2 | 7 | 45 | 11756 | 236 | 5.0496 | 51.21 | 0.23 | 51.44
CENTRAL COAST | LOS OSITOS 2103 | 182082103 | 2020 | 291.3 | 2.803 | 103.9 | 17 | 4045 | 420329 | 1443 | 46.1453 | 161.87 | 10.08 | 171.95
CENTRAL COAST | MONTEREY 0401 | 182090401 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 692 | 0 | 4.55 | 0.35 | 4.9
CENTRAL COAST | MONTEREY 0402 | 182090402 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 922 | 1.1362 | 4.25 | 1.06 | 5.31
CENTRAL COAST | OTTER 1101 | 182941101 | 2020 | 128.7 | 0.494 | 260.4 | 6 | 290 | 75520 | 587 | 23.9965 | 26.91 | 3.11 | 30.02
CENTRAL COAST | OTTER 1102 | 182941102 | 2020 | 420.1 | 1.578 | 266.1 | 10 | 835 | 222230 | 529 | 53.763 | 54.44 | 10.43 | 64.87
CENTRAL COAST | PACIFIC GROVE 0422 | 182440422 | 2020 | 16.9 | 0.074 | 228 | 1 | 58 | 13224 | 784 | 0.64463 | 6.89 | 1.36 | 8.25
CENTRAL COAST | PAUL SWEET 2102 | 83252102 | 2020 | 77.3 | 1.788 | 43.2 | 15 | 7838 | 338602 | 4383 | 2.1884 | 18.18 | 8.61 | 26.79
CENTRAL COAST | PAUL SWEET 2104 | 83252104 | 2020 | 37.6 | 1.067 | 35.3 | 4 | 6868 | 242325 | 6437 | 17.4386 | 38.49 | 17.88 | 56.38
CENTRAL COAST | PAUL SWEET 2105 | 83252105 | 2020 | 587.3 | 13.83 | 42.5 | 9 | 4633 | 196751 | 335 | 7.4461 | 29.61 | 10.74 | 40.35
CENTRAL COAST | PAUL SWEET 2106 | 83252106 | 2020 | 76.5 | 0.693 | 110.4 | 20 | 1178 | 130037 | 1699 | 36.4289 | 51.7 | 7.46 | 59.16
CENTRAL COAST | PAUL SWEET 2107 | 83252107 | 2020 | 8.9 | 0.825 | 10.8 | 11 | 6645 | 71587 | 8056 | 12.6712 | 52.17 | 11.92 | 64.09
CENTRAL COAST | PAUL SWEET 2109 | 83252109 | 2020 | 222.6 | 1.449 | 153.6 | 13 | 9524 | 1462930 | 6573 | 4.1319 | 23.58 | 15.26 | 38.84
CENTRAL COAST | PRUNEDALE 1110 | 182961110 | 2020 | 204 | 2.583 | 79 | 18 | 9698 | 765912 | 3755 | 0.42929 | 79.66 | 19.03 | 98.69
CENTRAL COAST | RESERVATION ROAD 1101 | 182731101 | 2020 | 117.7 | 2.051 | 57.4 | 8 | 3482 | 199835 | 1698 | 26.9821 | 31.67 | 14.96 | 46.63
CENTRAL COAST | RESERVATION ROAD 1102 | 182731102 | 2020 | 62 | 1.151 | 53.9 | 21 | 2433 | 131142 | 2114 | 23.8621 | 58.43 | 25.91 | 84.34
CENTRAL COAST | RIO DEL MAR 0401 | 83260401 | 2020 | 0.5 | 0.022 | 21 | 1 | 23 | 483 | 1049 | 2.2472 | 7.09 | 0.28 | 7.37
CENTRAL COAST | SAN ARDO 1101 | 182191101 | 2020 | 253.5 | 1.477 | 171.6 | 7 | 229 | 39288 | 155 | 4.9609 | 54.17 | 0.3 | 54.47
CENTRAL COAST | SAN BENITO 2101 | 182742101 | 2020 | 23.1 | 0.352 | 65.5 | 12 | 591 | 38730 | 1677 | 4.853 | 48.44 | 12.37 | 60.81
CENTRAL COAST | SAN BENITO 2104 | 182742104 | 2020 | 187.3 | 2.078 | 90.2 | 10 | 2697 | 243154 | 1298 | 29.1277 | 52.54 | 5.24 | 57.78
CENTRAL COAST | SAN JUSTO 1101 | 183181101 | 2020 | 174.3 | 2.28 | 76.4 | 9 | 1484 | 113438 | 651 | 38.6514 | 55.92 | 2.96 | 58.88
CENTRAL COAST | SEACLIFF 0401 | 83500401 | 2020 | 30.7 | 0.054 | 567 | 1 | 20 | 11340 | 369 | 8.1778 | 9.28 | 1.93 | 11.21
CENTRAL COAST | SEACLIFF 0402 | 83500402 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0.13496 | 1.56 | 1.27 | 2.83
CENTRAL COAST | SOLEDAD 1114 | 182051114 | 2020 | 1.3 | 0.008 | 169.1 | 3 | 22 | 3720 | 2758 | 1.4145 | 18.7 | 9.5 | 28.21
CENTRAL COAST | SOLEDAD 2101 | 182052101 | 2020 | 135 | 0.466 | 289.6 | 11 | 1171 | 339065 | 2511 | 5.8311 | 81.86 | 15.21 | 97.07
CENTRAL COAST | SOLEDAD 2102 | 182052102 | 2020 | 393.4 | 3.443 | 114.3 | 9 | 2186 | 249791 | 635 | 33.5941 | 53.68 | 4.02 | 57.69
CENTRAL COAST | SPENCE 1102 | 182201102 | 2020 | 18.7 | 0.042 | 445.2 | 2 | 12 | 5342 | 285 | 3.5403 | 33.4 | 0.68 | 34.08
CENTRAL COAST | SPENCE 1104 | 182201104 | 2020 | 358.1 | 2.397 | 149.4 | 19 | 1110 | 165822 | 463 | 9.2081 | 51.74 | 2.82 | 54.56
CENTRAL COAST | TRES PINOS 1111 | 183221111 | 2020 | 26 | 0.191 | 136.1 | 3 | 74 | 10068 | 387 | 0.066788 | 32.86 | 0.98 | 33.84
CENTRAL COAST | VIEJO 2201 | 182852201 | 2020 | 18.3 | 0.077 | 239.5 | 5 | 137 | 32818 | 1789 | 15.0967 | 17.42 | 13.65 | 31.07
CENTRAL COAST | VIEJO 2202 | 182852202 | 2020 | 95.8 | 0.337 | 284.3 | 12 | 2062 | 586232 | 6119 | 15.7878 | 46.54 | 16.81 | 63.35
CENTRAL COAST | VIEJO 2203 | 182852203 | 2020 | 8.3 | 0.035 | 239.7 | 6 | 168 | 40272 | 4842 | 3.3247 | 22.8 | 4.97 | 27.77
CENTRAL COAST | VIEJO 2204 | 182852204 | 2020 | 98.2 | 1.873 | 52.4 | 4 | 9142 | 479349 | 4882 | 4.6324 | 24.52 | 8.8 | 33.31
DE ANZA | BIG BASIN 1102 | 82841102 | 2020 | 583.4 | 1.831 | 318.6 | 120 | 3153 | 1004632 | 1722 | 76.6476 | 68.53 | 5.01 | 73.54
DE ANZA | CAMP EVERS 2105 | 83622105 | 2020 | 141.7 | 1.721 | 82.3 | 73 | 6925 | 569995 | 4023 | 88.5439 | 90.56 | 3.39 | 93.94
DE ANZA | CAMP EVERS 2106 | 83622106 | 2020 | 309.4 | 3.81 | 81.2 | 102 | 21165 | 1718753 | 5555 | 128.1918 | 136.87 | 19.56 | 156.43
DE ANZA | LOS GATOS 1101 | 82021101 | 2020 | 44.7 | 1.093 | 40.8 | 8 | 2425 | 99056 | 2218 | 12.3127 | 20.93 | 5.63 | 26.56
DE ANZA | LOS GATOS 1102 | 82021102 | 2020 | 12 | 0.149 | 80.5 | 3 | 288 | 23174 | 1932 | 1.1066 | 6.1 | 3.34 | 9.44
DE ANZA | LOS GATOS 1106 | 82021106 | 2020 | 318.9 | 4.727 | 67.5 | 25 | 7582 | 511472 | 1604 | 70.0685 | 70.52 | 2.84 | 73.36
DE ANZA | LOS GATOS 1107 | 82021107 | 2020 | 153.8 | 0.452 | 339.9 | 21 | 1051 | 357271 | 2323 | 96.1956 | 94.13 | 9.55 | 103.68
DE ANZA | LOS GATOS 1108 | 82021108 | 2020 | 130.2 | 1 | 130.2 | 1 | 1242 | 161670 | 1242 | 4.5188 | 6.08 | 2.66 | 8.74
DE ANZA | LOYOLA 1102 | 82161102 | 2020 | 14.6 | 0.071 | 207.4 | 13 | 208 | 43141 | 2948 | 0.093558 | 50.98 | 19.27 | 70.25
DE ANZA | SARATOGA 1103 | 83371103 | 2020 | 38.7 | 0.4 | 96.7 | 3 | 710 | 68663 | 1773 | 4.5962 | 10.49 | 7.75 | 18.25
DE ANZA | SARATOGA 1104 | 83371104 | 2020 | 26.1 | 0.303 | 86.1 | 7 | 525 | 45224 | 1731 | 3.0679 | 17.99 | 12.34 | 30.33
DE ANZA | SARATOGA 1105 | 83371105 | 2020 | 13.7 | 0.127 | 107.8 | 4 | 180 | 19412 | 1422 | 10.1799 | 16.66 | 13.12 | 29.78
DE ANZA | SARATOGA 1106 | 83371106 | 2020 | 146.1 | 1.362 | 107.3 | 9 | 2883 | 309243 | 2117 | 15.7224 | 27.12 | 8.88 | 36
DE ANZA | SARATOGA 1107 | 83371107 | 2020 | 161.5 | 3.423 | 47.2 | 20 | 8406 | 396693 | 2456 | 34.7937 | 45.75 | 13.39 | 59.14
DE ANZA | SARATOGA 1115 | 83371115 | 2020 | 49.8 | 0.821 | 60.6 | 8 | 2695 | 163391 | 3283 | 2.9197 | 12.58 | 16.97 | 29.55
DE ANZA | STELLING 1109 | 83481109 | 2020 | 21.9 | 0.165 | 133.3 | 6 | 532 | 70895 | 3230 | 1.0165 | 16.49 | 15.28 | 31.77
DE ANZA | STELLING 1110 | 83481110 | 2020 | 114.1 | 0.402 | 283.6 | 16 | 1524 | 432144 | 3787 | 33.4364 | 50.28 | 17.97 | 68.25
DE ANZA | VASONA 1102 | 83771102 | 2020 | 4 | 0.042 | 96 | 5 | 105 | 10078 | 2503 | 0.17566 | 15.62 | 8.33 | 23.95
DIABLO | ALHAMBRA 1102 | 14101102 | 2020 | 3.9 | 0.053 | 73.5 | 2 | 166 | 12208 | 3136 | 0.31193 | 14.19 | 5.1 | 19.28
DIABLO | BRYANT 0402 | 13090402 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 265 | 2.3419 | 3.96 | 0.05 | 4
DIABLO | CLAYTON 2212 | 12022212 | 2020 | 201.6 | 0.724 | 278.5 | 17 | 2485 | 691987 | 3433 | 48.3441 | 56.48 | 31.09 | 87.57
DIABLO | CLAYTON 2213 | 12022213 | 2020 | 111.1 | 0.789 | 140.7 | 8 | 2674 | 376167 | 3387 | 3.8725 | 6.12 | 29.88 | 36
DIABLO | CLAYTON 2215 | 12022215 | 2020 | 133.3 | 0.82 | 162.5 | 14 | 3702 | 601541 | 4512 | 8.8443 | 31.81 | 38 | 69.81
DIABLO | CLAYTON 2217 | 12022217 | 2020 | 19 | 0.572 | 33.2 | 2 | 2548 | 84515 | 4451 | 0.23231 | 19.76 | 22.31 | 42.07
DIABLO | KIRKER 2104 | 14452104 | 2020 | 13.6 | 0.171 | 79.4 | 5 | 874 | 69376 | 5116 | 5.8005 | 18.6 | 27.7 | 46.3
DIABLO | LAKEWOOD 1102 | 13531102 | 2020 | 91.5 | 2.057 | 44.5 | 5 | 3239 | 144160 | 1575 | 0.094315 | 9.61 | 4.91 | 14.51
DIABLO | LAKEWOOD 2107 | 13532107 | 2020 | 22.4 | 0.134 | 166.9 | 6 | 465 | 77602 | 3467 | 8.778 | 28.86 | 14.5 | 43.36
DIABLO | LAKEWOOD 2109 | 13532109 | 2020 | 15.5 | 0.312 | 49.6 | 5 | 795 | 39457 | 2546 | 0.56371 | 7.25 | 13.45 | 20.71
DIABLO | LAKEWOOD 2224 | 13532224 | 2020 | 127.3 | 0.853 | 149.2 | 4 | 2650 | 395273 | 3105 | 0.90013 | 24.33 | 6.86 | 31.19
DIABLO | LAKEWOOD 2227 | 13532227 | 2020 | 20.5 | 0.316 | 65 | 2 | 404 | 26278 | 1279 | 0.075745 | 7.89 | 4.77 | 12.66
DIABLO | LAS AROMAS 0401 | 13600401 | 2020 | 3.5 | 0.154 | 23 | 1 | 66 | 1518 | 429 | 5.3749 | 6.25 | 0.04 | 6.29
DIABLO | LONE TREE 2105 | 13232105 | 2020 | 18.9 | 0.036 | 521.1 | 5 | 81 | 42207 | 2238 | 12.8566 | 20.77 | 30.73 | 51.5
DIABLO | MEADOW LANE 2106 | 14302106 | 2020 | 138 | 1.33 | 103.8 | 5 | 5217 | 541481 | 3923 | 1.2073 | 23.35 | 22.62 | 45.97
DIABLO | MORAGA 1101 | 13801101 | 2020 | 210.6 | 1.993 | 105.7 | 9 | 2501 | 264256 | 1255 | 19.8563 | 20.19 | 9.24 | 29.43
DIABLO | MORAGA 1102 | 13801102 | 2020 | 7.2 | 0.298 | 24.2 | 3 | 261 | 6317 | 875 | 5.3075 | 9.25 | 4.7 | 13.95
DIABLO | MORAGA 1103 | 13801103 | 2020 | 42.1 | 0.599 | 70.2 | 5 | 1770 | 124227 | 2953 | 2.5954 | 18 | 13.37 | 31.37
DIABLO | MORAGA 1104 | 13801104 | 2020 | 15.5 | 0.127 | 121.8 | 3 | 225 | 27406 | 1768 | 14.4327 | 21.16 | 5.08 | 26.24
DIABLO | MORAGA 1105 | 13801105 | 2020 | 185.1 | 1.214 | 152.4 | 7 | 2294 | 349669 | 1889 | 7.9334 | 19.78 | 12.2 | 31.97
DIABLO | ORINDA 0401 | 12350401 | 2020 | 149 | 1 | 149 | 1 | 293 | 43657 | 293 | 3.5787 | 5.4 | 0.51 | 5.92
DIABLO | ORINDA 0402 | 12350402 | 2020 | 280.1 | 3.143 | 89.1 | 3 | 1433 | 127722 | 456 | 6.554 | 6.61 | 0.35 | 6.96
DIABLO | ROSSMOOR 1101 | 14161101 | 2020 | 36.9 | 0.297 | 124 | 10 | 960 | 119064 | 3228 | 13.4312 | 30.33 | 8.54 | 38.87
DIABLO | ROSSMOOR 1102 | 14161102 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 3096 | 0.57523 | 1.45 | 22.65 | 24.09
DIABLO | ROSSMOOR 1104 | 14161104 | 2020 | 208.7 | 1.763 | 118.4 | 15 | 4376 | 518044 | 2482 | 0.30817 | 19.29 | 7.91 | 27.21
DIABLO | ROSSMOOR 1106 | 14161106 | 2020 | 28.9 | 1.292 | 22.3 | 8 | 3675 | 82119 | 2844 | 5.4268 | 21.02 | 3.29 | 24.31
DIABLO | ROSSMOOR 1107 | 14161107 | 2020 | 0.1 | 0.002 | 41.6 | 1 | 5 | 208 | 2545 | 0.094493 | 10.5 | 9.7 | 20.2
DIABLO | ROSSMOOR 1108 | 14161108 | 2020 | 52.3 | 1.029 | 50.8 | 5 | 2976 | 151237 | 2892 | 12.8714 | 20.5 | 21.54 | 42.04
DIABLO | ROSSMOOR 1109 | 14161109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004705 | 0 | 0.01 | 0.01
DIABLO | SOBRANTE 1101 | 14671101 | 2020 | 108.9 | 2.066 | 52.7 | 8 | 4232 | 222932 | 2048 | 15.4469 | 21.38 | 6.85 | 28.24
DIABLO | SOBRANTE 1102 | 14671102 | 2020 | 5.2 | 0.063 | 83.5 | 4 | 115 | 9599 | 1830 | 27.4843 | 27.62 | 13.65 | 41.28
DIABLO | SOBRANTE 1103 | 14671103 | 2020 | 9.2 | 0.06 | 153.6 | 4 | 33 | 5068 | 551 | 4.4422 | 5.16 | 6.44 | 11.6
DIABLO | TASSAJARA 2103 | 14662103 | 2020 | 37.4 | 0.23 | 162.4 | 9 | 698 | 113346 | 3031 | 0.69788 | 19.89 | 47 | 66.89
DIABLO | TASSAJARA 2104 | 14662104 | 2020 | 32.3 | 0.054 | 593.4 | 2 | 154 | 91391 | 2827 | 6.3573 | 9.69 | 42.85 | 52.54
DIABLO | TASSAJARA 2106 | 14662106 | 2020 | 1.1 | 0.009 | 132 | 1 | 25 | 3300 | 2912 | 0.50317 | 3.05 | 32.88 | 35.92
DIABLO | TASSAJARA 2108 | 14662108 | 2020 | 16.2 | 0.102 | 157.9 | 8 | 302 | 47675 | 2949 | 1.6825 | 21.49 | 25.76 | 47.25
DIABLO | TASSAJARA 2112 | 14662112 | 2020 | 69 | 0.432 | 159.7 | 12 | 1066 | 170270 | 2466 | 11.1248 | 18.82 | 37.82 | 56.65
DIABLO | TIDEWATER 2106 | 14652106 | 2020 | 105.7 | 1.173 | 90.1 | 7 | 2550 | 229692 | 2173 | 7.8596 | 39.12 | 14.3 | 53.42
DIABLO | WAYNE 0401 | 13810401 | 2020 | 116.1 | 0.482 | 241 | 1 | 66 | 15906 | 137 | 0.17582 | 2.63 | 0.01 | 2.64
DIABLO | WILLOW PASS 1101 | 13911101 | 2020 | 68 | 1 | 68 | 1 | 1611 | 109548 | 1611 | 1.791 | 7.06 | 13.32 | 20.38
DIABLO | WILLOW PASS 2107 | 13912107 | 2020 | 3.3 | 0.059 | 56.3 | 3 | 194 | 10920 | 3289 | 0.66278 | 3.56 | 30.45 | 34.01
DIABLO | WILLOW PASS 2108 | 13912108 | 2020 | 0.5 | 0.007 | 66 | 1 | 37 | 2442 | 5009 | 0.19769 | 16.83 | 33.05 | 49.88
EAST BAY | ALHAMBRA 1105 | 14101105 | 2020 | 15.4 | 0.15 | 103 | 7 | 320 | 32953 | 2135 | 38.6547 | 45.15 | 14.91 | 60.06
EAST BAY | ARLINGTON 0401 | 13700401 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 657 | 0.87233 | 4 | 0.14 | 4.13
EAST BAY | BERKELEY F 0402 | 12060402 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1114 | 0.1697 | 2.13 | 0.53 | 2.66
EAST BAY | BERKELEY F 1103 | 12061103 | 2020 | 11.9 | 0.108 | 109.4 | 2 | 360 | 39378 | 3323 | 2.1185 | 6.25 | 7 | 13.26
EAST BAY | BERKELEY F 1105 | 12061105 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 5138 | 1.9702 | 11.37 | 6.62 | 17.99
EAST BAY | BERKELEY T 0404 | 12660404 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 589 | 0 | 1.21 | 0.31 | 1.52
EAST BAY | BOSTON 0401 | 13320401 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1173 | 0.31043 | 4.57 | 0.06 | 4.64
EAST BAY | EDES 1112 | 13681112 | 2020 | 13.9 | 0.176 | 78.7 | 5 | 557 | 43811 | 3157 | 15.6165 | 17.28 | 13.25 | 30.53
EAST BAY | EL CERRITO G 1105 | 12501105 | 2020 | 151.8 | 1.12 | 135.6 | 6 | 4321 | 585788 | 3859 | 19.6506 | 24.5 | 15.15 | 39.65
EAST BAY | EL CERRITO G 1108 | 12501108 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 3415 | 0.002699 | 14.4 | 6.3 | 20.7
EAST BAY | EL CERRITO G 1110 | 12501110 | 2020 | 38.6 | 1.016 | 37.9 | 2 | 2110 | 80054 | 2076 | 0.93769 | 10.14 | 2.24 | 12.38
EAST BAY | EL CERRITO G 1111 | 12501111 | 2020 | 8.1 | 0.172 | 47 | 1 | 377 | 17719 | 2193 | 0.21291 | 12.88 | 5.68 | 18.56
EAST BAY | EL CERRITO G 1112 | 12501112 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 4706 | 2.2026 | 24.69 | 8.76 | 33.45
EAST BAY | EL CERRITO G 1113 | 12501113 | 2020 | 0.2 | 0.003 | 65 | 1 | 10 | 650 | 3254 | 0.098306 | 9.55 | 5 | 14.55
EAST BAY | FAIRMOUNT 0401 | 12650401 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1337 | 1.407 | 5.69 | 0.05 | 5.74
EAST BAY | FAIRVIEW 2207 | 13432207 | 2020 | 143.2 | 2.416 | 59.3 | 10 | 11146 | 660727 | 4614 | 22.199 | 51.71 | 11.47 | 63.18
EAST BAY | FLORENCE 0401 | 12690401 | 2020 | 391.8 | 3.506 | 111.8 | 6 | 1732 | 193572 | 494 | 0.84938 | 4.29 | 0.29 | 4.58
EAST BAY | FRANKLIN 1101 | 13921101 | 2020 | 6.6 | 0.069 | 95.5 | 3 | 166 | 15852 | 2397 | 1.404 | 9.56 | 14.32 | 23.88
EAST BAY | FRANKLIN 1104 | 13921104 | 2020 | 38.5 | 1.042 | 36.9 | 3 | 5599 | 206739 | 5371 | 8.851 | 15.73 | 41.96 | 57.69
EAST BAY | HOLLYWOOD 0401 | 13170401 | 2020 | 23.1 | 0.109 | 212.1 | 2 | 166 | 35212 | 1524 | 2.862 | 5.29 | 0.96 | 6.26
EAST BAY | NORTH TOWER 2101 | 42042101 | 2020 | 15202 | 141 | 107.8 | 2 | 141 | 15202 | 1 | 1.3545 | 4.38 | 2.28 | 6.67
EAST BAY | OAK 0401 | 12600401 | 2020 | 16.6 | 0.535 | 31 | 1 | 544 | 16864 | 1016 | 3.4715 | 5.42 | 0.62 | 6.04
EAST BAY | OAKLAND D 1112 | 12041112 | 2020 | 24 | 0.961 | 24.9 | 1 | 3768 | 93944 | 3920 | 2.463 | 11.99 | 2.88 | 14.87
EAST BAY | OAKLAND J 1102 | 12091102 | 2020 | 90.6 | 0.579 | 156.3 | 13 | 3442 | 538050 | 5940 | 6.1385 | 18.33 | 11.23 | 29.55
EAST BAY | OAKLAND J 1105 | 12091105 | 2020 | 107.9 | 1.118 | 96.5 | 7 | 5217 | 503503 | 4667 | 1.7262 | 18.53 | 3.06 | 21.6
EAST BAY | OAKLAND J 1106 | 12091106 | 2020 | 55.9 | 0.839 | 66.6 | 3 | 4715 | 314108 | 5618 | 2.2132 | 19.68 | 3.85 | 23.53
EAST BAY | OAKLAND J 1116 | 12091116 | 2020 | 47.6 | 0.138 | 345.7 | 4 | 1057 | 365370 | 7675 | 0.59423 | 23.72 | 2.84 | 26.57
EAST BAY | OAKLAND J 1118 | 12091118 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 4009 | 0.32037 | 11.77 | 4.38 | 16.15
EAST BAY | OAKLAND K 1101 | 12101101 | 2020 | 140.3 | 1.027 | 136.6 | 2 | 2220 | 303249 | 2161 | 2.6831 | 7.28 | 9.37 | 16.65
EAST BAY | OAKLAND K 1102 | 12101102 | 2020 | 15.7 | 0.166 | 94.7 | 5 | 427 | 40446 | 2579 | 14.9702 | 14.92 | 13.42 | 28.35
EAST BAY | OAKLAND K 1103 | 12101103 | 2020 | 260.7 | 1.283 | 203.2 | 3 | 4004 | 813612 | 3121 | 6.0706 | 10.69 | 10.95 | 21.65
EAST BAY | OAKLAND K 1104 | 12101104 | 2020 | 212.5 | 2.241 | 94.8 | 4 | 6007 | 569709 | 2681 | 15.1724 | 14.92 | 9.38 | 24.3
EAST BAY | OAKLAND X 1101 | 12541101 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1975 | 0.52382 | 5.29 | 11.44 | 16.73
EAST BAY | OAKLAND X 1104 | 12541104 | 2020 | 788.1 | 1.252 | 629.6 | 6 | 2666 | 1678579 | 2130 | 12.3161 | 13.39 | 6.97 | 20.36
EAST BAY | OAKLAND X 1105 | 12541105 | 2020 | 40.8 | 0.16 | 255.8 | 2 | 728 | 186208 | 4561 | 2.6981 | 14.86 | 1.67 | 16.53
EAST BAY | OAKLAND X 1106 | 12541106 | 2020 | 100.1 | 2.15 | 46.6 | 12 | 8194 | 381634 | 3811 | 15.8719 | 23.38 | 13.19 | 36.57
EAST BAY | PALO SECO 0401 | 13180401 | 2020 | 257.8 | 0.998 | 258.2 | 1 | 616 | 159078 | 617 | 4.745 | 4.75 | 2.65 | 7.4
EAST BAY | RIDGE 0401 | 12840401 | 2020 | 178.1 | 1.236 | 144.1 | 2 | 498 | 71756 | 403 | 2.654 | 2.65 | 0.06 | 2.71
EAST BAY | RIDGE 0402 | 12840402 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 800 | 1.8211 | 2.4 | 0.39 | 2.78
EAST BAY | ROB ROY 2104 | 83692104 | 2020 | 179.2 | 1.184 | 151.3 | 48 | 4284 | 648325 | 3618 | 101.8119 | 134.55 | 18.73 | 153.27
EAST BAY | ROB ROY 2105 | 83692105 | 2020 | 107.8 | 0.739 | 146 | 46 | 5788 | 845043 | 7836 | 41.4311 | 85.53 | 29.66 | 115.19
EAST BAY | SPRUCE 0401 | 13340401 | 2020 | 126 | 1 | 126 | 1 | 720 | 90720 | 720 | 4.1073 | 4.11 | 1.24 | 5.34
EAST BAY | SPRUCE 0402 | 13340402 | 2020 | 223.9 | 1.823 | 122.8 | 2 | 1152 | 141504 | 632 | 1.4871 | 3.59 | 0.9 | 4.5
EAST BAY | VALLEY VIEW 1103 | 14341103 | 2020 | 25.2 | 0.373 | 67.7 | 3 | 1875 | 126850 | 5032 | 0.70793 | 18.22 | 13.52 | 31.74
EAST BAY | VALLEY VIEW 1105 | 14341105 | 2020 | 154.3 | 1.225 | 126 | 5 | 4177 | 526479 | 3411 | 4.1795 | 18.68 | 12.32 | 31
EAST BAY | VALLEY VIEW 1106 | 14341106 | 2020 | 24.1 | 0.384 | 62.7 | 5 | 1694 | 106211 | 4413 | 9.3105 | 21.49 | 30.27 | 51.76
EAST BAY | WALDO 0401 | 13350401 | 2020 | 77.7 | 1 | 77.7 | 1 | 1425 | 110698 | 1425 | 1.6425 | 5.7 | 0.4 | 6.09
EAST BAY | WALDO 0402 | 13350402 | 2020 | 76.8 | 0.448 | 171.7 | 1 | 462 | 79308 | 1032 | 2.9795 | 5.15 | 0.16 | 5.31
EAST BAY | WOOD 0401 | 13380401 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 724 | 0.24993 | 3.32 | 2.76 | 6.08
FRESNO | AUBERRY 1101 | 254151101 | 2020 | 394.4 | 0.586 | 673.5 | 18 | 1857 | 1250640 | 3171 | 244.4562 | 240.55 | 14.51 | 255.07
FRESNO | AUBERRY 1102 | 254151102 | 2020 | 292 | 1.232 | 236.9 | 13 | 2021 | 478856 | 1640 | 128.5836 | 129.22 | 3.63 | 132.85
FRESNO | BALCH NO 1 1101 | 252501101 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 14.7187 | 14.7 | 0 | 14.7
FRESNO | COPPERMINE 1104 | 252411104 | 2020 | 20.8 | 0.965 | 21.6 | 10 | 2617 | 56532 | 2713 | 9.9664 | 101.01 | 25.83 | 126.84
FRESNO | DUNLAP 1102 | 254061102 | 2020 | 384.7 | 0.53 | 726.1 | 7 | 373 | 270818 | 704 | 56.6666 | 56.89 | 33.56 | 90.45
FRESNO | DUNLAP 1103 | 254061103 | 2020 | 68.7 | 0.333 | 206.2 | 5 | 313 | 64531 | 940 | 71.2272 | 70.98 | 5.48 | 76.45
FRESNO | OROSI 1102 | 252841102 | 2020 | 9.1 | 0.055 | 165.3 | 3 | 21 | 3472 | 382 | 1.064 | 34.81 | 0.01 | 34.82
FRESNO | REEDLEY 1104 | 252341104 | 2020 | 63.8 | 0.936 | 68.2 | 12 | 1314 | 89631 | 1404 | 1.698 | 82.06 | 2.57 | 84.63
FRESNO | REEDLEY 1112 | 252341112 | 2020 | 13.2 | 0.093 | 141.4 | 16 | 283 | 40015 | 3030 | 1.1416 | 89.62 | 4.37 | 93.99
FRESNO | SAND CREEK 1103 | 254601103 | 2020 | 381.2 | 2.372 | 160.7 | 15 | 3985 | 640336 | 1680 | 149.7935 | 150.61 | 0.03 | 150.63
FRESNO | SHEPHERD 2111 | 252062111 | 2020 | 8.4 | 0.065 | 128.9 | 7 | 68 | 8762 | 1044 | 30.5677 | 71.92 | 15.77 | 87.69
FRESNO | STONE CORRAL 1108 | 252921108 | 2020 | 201 | 1.042 | 192.9 | 5 | 942 | 181698 | 904 | 2.3355 | 78.71 | 0.63 | 79.34
FRESNO | STONE CORRAL 1110 | 252921110 | 2020 | 11.6 | 0.08 | 146 | 3 | 62 | 9053 | 778 | 2.4936 | 62.31 | 0.3 | 62.61
FRESNO | TIVY VALLEY 1107 | 252941107 | 2020 | 67.3 | 0.802 | 83.9 | 7 | 1363 | 114327 | 1699 | 121.6008 | 168.14 | 5.48 | 173.62
FRESNO | TULE POWER HOUSE 1101 | 258591101 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4.0838 | 4.09 | 0 | 4.09
HUMBOLDT | ARCATA 1121 | 192021121 | 2020 | 14.6 | 0.126 | 116.2 | 5 | 348 | 40432 | 2762 | 6.9085 | 28.91 | 5.94 | 34.85
HUMBOLDT | ARCATA 1122 | 192021122 | 2020 | 34.3 | 0.332 | 103.5 | 16 | 1053 | 108978 | 3174 | 20.8805 | 67.79 | 5.85 | 73.64
HUMBOLDT | BIG RIVER 1101 | 43081101 | 2020 | 24.8 | 0.199 | 124.5 | 6 | 517 | 64365 | 2592 | 72.5961 | 86.11 | 16.56 | 102.66
HUMBOLDT | BRIDGEVILLE 1101 | 192461101 | 2020 | 544.7 | 2.926 | 186.2 | 4 | 275 | 51199 | 94 | 22.9727 | 23.92 | 0 | 23.92
HUMBOLDT | BRIDGEVILLE 1102 | 192461102 | 2020 | 217.6 | 0.362 | 601.7 | 10 | 102 | 61377 | 282 | 35.9302 | 46.29 | 0 | 46.29
HUMBOLDT | CALPELLA 1101 | 43411101 | 2020 | 116.9 | 1.111 | 105.2 | 7 | 1898 | 199658 | 1708 | 84.647 | 99.39 | 3.84 | 103.24
HUMBOLDT | CALPELLA 1102 | 43411102 | 2020 | 28.4 | 0.577 | 49.3 | 4 | 742 | 36554 | 1287 | 7.2297 | 26.1 | 4.81 | 30.91
HUMBOLDT | CARLOTTA 1121 | 192291121 | 2020 | 290.2 | 1.285 | 225.9 | 8 | 1443 | 325918 | 1123 | 19.4724 | 48.31 | 1.98 | 50.3
HUMBOLDT | CLEAR LAKE 1101 | 42141101 | 2020 | 76 | 1.031 | 73.7 | 18 | 2502 | 184341 | 2427 | 21.6474 | 113.82 | 2.42 | 116.24
HUMBOLDT | CLEAR LAKE 1102 | 42141102 | 2020 | 24.6 | 0.1 | 245.4 | 3 | 184 | 45152 | 1832 | 4.4959 | 37.11 | 6.93 | 44.04
HUMBOLDT | COVELO 1101 | 43061101 | 2020 | 504.1 | 1.52 | 331.7 | 27 | 2093 | 694192 | 1377 | 20.9757 | 120.36 | 0.99 | 121.35
HUMBOLDT | EEL RIVER 1102 | 192381102 | 2020 | 92.9 | 1.13 | 82.2 | 32 | 1817 | 149442 | 1608 | 40.6407 | 144.21 | 4.47 | 148.69
HUMBOLDT | EEL RIVER 1103 | 192381103 | 2020 | 31.4 | 0.301 | 104.4 | 22 | 440 | 45941 | 1463 | 3.4085 | 59.56 | 0.98 | 60.55
HUMBOLDT | ELK 1101 | 42981101 | 2020 | 503.3 | 0.827 | 608.6 | 16 | 1262 | 768014 | 1526 | 77.8844 | 106.53 | 12.6 | 119.12
HUMBOLDT | EUREKA E 1104 | 192331104 | 2020 | 285.6 | 2.411 | 118.5 | 6 | 9110 | 1079337 | 3779 | 0.048733 | 26.88 | 1.74 | 28.62
HUMBOLDT | FORT BRAGG A 1101 | 42761101 | 2020 | 33.9 | 0.337 | 100.6 | 9 | 906 | 91146 | 2686 | 70.7259 | 81.11 | 7.67 | 88.78
HUMBOLDT | FORT BRAGG A 1102 | 42761102 | 2020 | 21.9 | 0.088 | 247.5 | 7 | 210 | 51967 | 2374 | 66.5518 | 81.45 | 4.56 | 86.01
HUMBOLDT | FORT BRAGG A 1103 | 42761103 | 2020 | 18.2 | 0.553 | 33 | 1 | 415 | 13695 | 751 | 0.22971 | 2.67 | 5.57 | 8.24
HUMBOLDT | FORT BRAGG A 1104 | 42761104 | 2020 | 20.5 | 0.142 | 144 | 9 | 375 | 54018 | 2641 | 25.6837 | 38.29 | 1.38 | 39.67
HUMBOLDT | FORT SEWARD 1121 | 192321121 | 2020 | 178.6 | 0.745 | 239.8 | 5 | 175 | 41972 | 235 | 38.2181 | 47.84 | 0.02 | 47.86
HUMBOLDT | FORT SEWARD 1122 | 192321122 | 2020 | 507.3 | 0.515 | 986 | 1 | 53 | 52256 | 103 | 17.6589 | 21.79 | 0.06 | 21.85
HUMBOLDT | FRUITLAND 1141 | 192311141 | 2020 | 668.1 | 2.439 | 274 | 8 | 956 | 261902 | 392 | 24.9875 | 26.91 | 0.02 | 26.93
HUMBOLDT | FRUITLAND 1142 | 192311142 | 2020 | 596.3 | 1.659 | 359.5 | 14 | 1264 | 454386 | 762 | 60.0561 | 67.05 | 0.6 | 67.65
HUMBOLDT | GARBERVILLE 1101 | 192221101 | 2020 | 431 | 4.372 | 98.6 | 29 | 5600 | 552158 | 1281 | 85.2413 | 161.57 | 3.16 | 164.73
HUMBOLDT | GARBERVILLE 1102 | 192221102 | 2020 | 418.6 | 2.46 | 170.2 | 30 | 4440 | 755648 | 1805 | 127.9972 | 133.57 | 8.52 | 142.09
HUMBOLDT | GARBERVILLE 1103 | 192221103 | 2020 | 138.4 | 1.024 | 135.1 | 2 | 509 | 68785 | 497 | 0.60372 | 2.21 | 1.18 | 3.4
HUMBOLDT | GARCIA 0401 | 43040401 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 2.4358 | 2.44 | 0 | 2.44
HUMBOLDT | GUALALA 1111 | 42841111 | 2020 | 99.8 | 1.647 | 60.6 | 13 | 4087 | 247522 | 2481 | 35.4584 | 37.88 | 46.63 | 84.51
HUMBOLDT | GUALALA 1112 | 42841112 | 2020 | 114.3 | 0.862 | 132.6 | 8 | 1109 | 147104 | 1287 | 43.6238 | 47.43 | 6.3 | 53.73
HUMBOLDT | HARRIS 1108 | 192431108 | 2020 | 13.6 | 0.424 | 32.2 | 2 | 2128 | 68528 | 5023 | 1.9403 | 32.64 | 7.78 | 40.42
HUMBOLDT | HARRIS 1109 | 192431109 | 2020 | 69.8 | 1.278 | 54.6 | 12 | 5062 | 276633 | 3961 | 14.7167 | 50.61 | 5.03 | 55.64
HUMBOLDT | HARTLEY 1101 | 43211101 | 2020 | 35.1 | 0.305 | 115.2 | 11 | 923 | 106337 | 3028 | 30.169 | 65.81 | 6.52 | 72.33
HUMBOLDT | HARTLEY 1102 | 43211102 | 2020 | 11.7 | 0.12 | 97.5 | 4 | 179 | 17460 | 1496 | 5.0086 | 27.45 | 4.68 | 32.12
HUMBOLDT | HIGHLANDS 1102 | 43361102 | 2020 | 306.1 | 1.289 | 237.5 | 13 | 4645 | 1103339 | 3604 | 37.0394 | 60.04 | 3.99 | 64.03
HUMBOLDT | HIGHLANDS 1103 | 43361103 | 2020 | 118.3 | 2.152 | 55 | 16 | 5567 | 306164 | 2587 | 113.7592 | 122.61 | 3.94 | 126.55
HUMBOLDT | HIGHLANDS 1104 | 43361104 | 2020 | 26 | 0.368 | 70.8 | 14 | 1068 | 75635 | 2906 | 12.5545 | 29.4 | 3.42 | 32.82
HUMBOLDT | HOOPA 1101 | 192401101 | 2020 | 327.6 | 2.543 | 128.8 | 30 | 5343 | 688287 | 2101 | 110.9597 | 131.4 | 10.79 | 142.18
HUMBOLDT | HOPLAND 1101 | 42251101 | 2020 | 169.1 | 0.769 | 220.1 | 13 | 996 | 219202 | 1296 | 92.9488 | 129.58 | 4.19 | 133.78
HUMBOLDT | HUMBOLDT BAY 1102 | 192341102 | 2020 | 36.6 | 0.174 | 210.9 | 7 | 542 | 114286 | 3121 | 6.6613 | 41.42 | 11.55 | 52.97
HUMBOLDT | KONOCTI 1102 | 43311102 | 2020 | 162.1 | 1.069 | 151.6 | 15 | 3104 | 470542 | 2903 | 133.0977 | 146.69 | 9.23 | 155.92
HUMBOLDT | KONOCTI 1108 | 43311108 | 2020 | 112.6 | 0.727 | 154.7 | 2 | 1475 | 228252 | 2028 | 22.6047 | 33.01 | 0.43 | 33.44
HUMBOLDT | LAYTONVILLE 1101 | 42681101 | 2020 | 112.7 | 0.739 | 152.6 | 13 | 554 | 84526 | 750 | 53.6551 | 80.03 | 0.42 | 80.45
HUMBOLDT | LAYTONVILLE 1102 | 42681102 | 2020 | 214.2 | 0.299 | 715.6 | 11 | 291 | 208235 | 972 | 114.3114 | 119.32 | 3.42 | 122.74
HUMBOLDT | LOW GAP 1101 | 192411101 | 2020 | 494.1 | 1.004 | 492.1 | 14 | 747 | 367619 | 744 | 71.7991 | 72.86 | 0.52 | 73.38
HUMBOLDT | LUCERNE 1103 | 43351103 | 2020 | 22.6 | 0.191 | 118 | 7 | 430 | 50756 | 2250 | 28.0045 | 52.84 | 3.11 | 55.95
HUMBOLDT | LUCERNE 1106 | 43351106 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 3223 | 37.6314 | 46.73 | 2.88 | 49.61
HUMBOLDT | MAPLE CREEK 1101 | 192101101 | 2020 | 64.3 | 0.221 | 290.3 | 4 | 33 | 9579 | 149 | 10.3621 | 32.85 | 0.14 | 32.99
HUMBOLDT | MENDOCINO 1101 | 42951101 | 2020 | 8 | 0.039 | 203.2 | 5 | 66 | 13414 | 1687 | 34.5595 | 74.82 | 4.29 | 79.11
HUMBOLDT | MIDDLETOWN 1102 | 43141102 | 2020 | 86.4 | 1.012 | 85.4 | 4 | 2409 | 205678 | 2380 | 42.5194 | 55.31 | 2.08 | 57.39
HUMBOLDT | MIDDLETOWN 1103 | 43141103 | 2020 | 477.6 | 1.119 | 426.6 | 3 | 178 | 75931 | 159 | 27.7858 | 38.16 | 1.07 | 39.23
HUMBOLDT | NEWBURG 1131 | 192151131 | 2020 | 19.8 | 0.208 | 95.4 | 8 | 558 | 53245 | 2686 | 7.5953 | 39.14 | 7.04 | 46.18
HUMBOLDT | NEWBURG 1132 | 192151132 | 2020 | 100.3 | 1.233 | 81.3 | 4 | 4326 | 351916 | 3509 | 1.4042 | 22.24 | 11.76 | 34
HUMBOLDT | NEWBURG 1133 | 192151133 | 2020 | 10.9 | 0.135 | 80.5 | 3 | 70 | 5636 | 518 | 3.163 | 16.81 | 1.12 | 17.93
HUMBOLDT | PHILO 1101 | 42601101 | 2020 | 27 | 0.249 | 108.5 | 9 | 290 | 31473 | 1164 | 75.423 | 92.7 | 3.34 | 96.05
HUMBOLDT | PHILO 1102 | 42601102 | 2020 | 265.4 | 1.448 | 183.3 | 20 | 1522 | 278964 | 1051 | 91.4533 | 100.86 | 3.51 | 104.37
HUMBOLDT | POINT ARENA 1101 | 43381101 | 2020 | 11.1 | 0.083 | 133.5 | 8 | 76 | 10143 | 912 | 46.0473 | 66.15 | 6.27 | 72.42
HUMBOLDT | POTTER VALLEY P H 1104 | 42281104 | 2020 | 88.8 | 1.042 | 85.2 | 4 | 320 | 27255 | 307 | 6.2245 | 18.73 | 0.04 | 18.77
HUMBOLDT | POTTER VALLEY P H 1105 | 42281105 | 2020 | 146.9 | 1.977 | 74.3 | 13 | 1601 | 118993 | 810 | 51.1648 | 72.75 | 1.31 | 74.06
HUMBOLDT | REDBUD 1101 | 43191101 | 2020 | 42 | 0.653 | 64.3 | 3 | 1375 | 88406 | 2106 | 48.3795 | 70.32 | 1.64 | 71.96
HUMBOLDT | REDBUD 1102 | 43191102 | 2020 | 31.3 | 1.227 | 25.5 | 6 | 4188 | 106947 | 3414 | 31.111 | 58.33 | 3.01 | 61.34
HUMBOLDT | RIO DELL 1102 | 192251102 | 2020 | 190.5 | 1.605 | 118.7 | 16 | 2264 | 268812 | 1411 | 53.3284 | 72.46 | 7.59 | 80.05
HUMBOLDT | UKIAH 1111 | 42771111 | 2020 | 148.8 | 1.352 | 110.1 | 4 | 1717 | 188958 | 1270 | 23.2461 | 38.2 | 5.16 | 43.36
HUMBOLDT | UKIAH 1113 | 42771113 | 2020 | 15.4 | 0.059 | 263.7 | 3 | 71 | 18723 | 1212 | 7.8766 | 15.94 | 0.76 | 16.7
HUMBOLDT | UKIAH 1114 | 42771114 | 2020 | 29.3 | 0.291 | 100.5 | 8 | 511 | 51376 | 1754 | 56.2469 | 103.37 | 5.9 | 109.26
HUMBOLDT | UKIAH 1115 | 42771115 | 2020 | 21.6 | 0.193 | 112.1 | 3 | 136 | 15252 | 705 | 17.7531 | 25.32 | 5.48 | 30.8
HUMBOLDT | UPPER LAKE 1101 | 42871101 | 2020 | 230.3 | 1.889 | 121.9 | 17 | 2494 | 304037 | 1320 | 53.6406 | 86.15 | 0.85 | 86.99
HUMBOLDT | WILLITS 1102 | 42661102 | 2020 | 116.6 | 1.025 | 113.7 | 2 | 1298 | 147602 | 1266 | 5.3142 | 11.26 | 2.53 | 13.79
HUMBOLDT | WILLITS 1103 | 42661103 | 2020 | 244.3 | 1.786 | 136.8 | 30 | 3923 | 536670 | 2197 | 146.4658 | 151.41 | 4.65 | 156.06
HUMBOLDT | WILLITS 1104 | 42661104 | 2020 | 126.8 | 0.688 | 184.3 | 9 | 2159 | 397904 | 3139 | 88.3268 | 95.87 | 5.92 | 101.79
HUMBOLDT | WILLOW CREEK 1101 | 192171101 | 2020 | 186.2 | 1.179 | 158 | 9 | 924 | 145986 | 784 | 48.9071 | 56.63 | 3.56 | 60.2
HUMBOLDT | WILLOW CREEK 1102 | 192171102 | 2020 | 16.2 | 0.917 | 17.7 | 2 | 132 | 2332 | 144 | 9.575 | 9.6 | 1.36 | 10.96
HUMBOLDT | WILLOW CREEK 1103 | 192171103 | 2020 | 613 | 1.364 | 449.5 | 11 | 2125 | 955104 | 1558 | 85.0561 | 85.15 | 1.39 | 86.54
KERN | ANTELOPE 1101 | 252021101 | 2020 | 186.7 | 0.354 | 528.1 | 3 | 35 | 18484 | 99 | 1.4578 | 39.75 | 0.05 | 39.8
KERN | ARVIN 1101 | 253801101 | 2020 | 4 | 0.016 | 242.1 | 2 | 7 | 1695 | 427 | 0.21503 | 28.96 | 3 | 31.96
KERN | CAL WATER 1102 | 255451102 | 2020 | 92.5 | 1.032 | 89.6 | 4 | 2466 | 221055 | 2389 | 3.9839 | 26.12 | 37.01 | 63.13
KERN | CUYAMA 1103 | 253141103 | 2020 | 6.2 | 0.018 | 349.4 | 2 | 7 | 2446 | 392 | 3.0185 | 71.31 | 0.73 | 72.03
KERN | KERN OIL 1106 | 252721106 | 2020 | 47.6 | 0.27 | 176.7 | 8 | 76 | 13430 | 282 | 1.3565 | 44.92 | 4.16 | 49.07
KERN | LAMONT 1102 | 253911102 | 2020 | 183.4 | 1.698 | 108 | 13 | 849 | 91704 | 500 | 2.6385 | 70.93 | 1.01 | 71.94
KERN | POSO MOUNTAIN 2101 | 253642101 | 2020 | 385.4 | 1.07 | 360.2 | 6 | 153 | 55113 | 143 | 49.9205 | 59.58 | 0.12 | 59.7
KERN | POSO MOUNTAIN 2103 | 253642103 | 2020 | 230.2 | 2.885 | 79.8 | 4 | 75 | 5985 | 26 | 19.2447 | 20.54 | 0 | 20.54
KERN | POSO MOUNTAIN 2104 | 253642104 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 10.4203 | 12.33 | 0 | 12.33
KERN | SAN BERNARD 1101 | 253191101 | 2020 | 81.4 | 1.242 | 65.5 | 8 | 159 | 10413 | 128 | 1.7508 | 46.37 | 0.28 | 46.65
KERN | SCE TEHACHAPI 1101 | 258131101 | 2020 | 1799 | 1 | 1799 | 1 | 4 | 7196 | 4 | 1.1573 | 1.43 | 0 | 1.43
KERN | TEJON 1102 | 252931102 | 2020 | 1215.3 | 2.182 | 556.9 | 7 | 1857 | 1034180 | 851 | 34.2902 | 62.03 | 11.3 | 73.33
KERN | TEJON 1103 | 252931103 | 2020 | 32.7 | 0.138 | 237.8 | 4 | 19 | 4518 | 138 | 2.1764 | 40.41 | 0.22 | 40.63
LOS PADRES | ATASCADERO 1101 | 182541101 | 2020 | 59.3 | 0.425 | 139.6 | 12 | 1461 | 203931 | 3440 | 45.8488 | 62.23 | 9.01 | 71.24
LOS PADRES | ATASCADERO 1102 | 182541102 | 2020 | 82.6 | 1.005 | 82.2 | 5 | 1440 | 118432 | 1433 | 1.1789 | 12.15 | 4.2 | 16.35
LOS PADRES | ATASCADERO 1103 | 182541103 | 2020 | 87.3 | 0.997 | 87.6 | 13 | 4189 | 366817 | 4202 | 98.1849 | 130.4 | 20.13 | 150.53
LOS PADRES | BAYWOOD 1101 | 182801101 | 2020 | 118.1 | 1.8 | 65.6 | 11 | 513 | 33645 | 285 | 4.6156 | 29.73 | 2.49 | 32.23
LOS PADRES | BUELLTON 1101 | 183041101 | 2020 | 5.2 | 0.028 | 189.3 | 4 | 71 | 13437 | 2564 | 83.272 | 103.99 | 24.41 | 128.4
LOS PADRES | BUELLTON 1102 | 183041102 | 2020 | 1.2 | 0.011 | 102.3 | 3 | 23 | 2352 | 2031 | 17.7147 | 28.38 | 20.61 | 48.99
LOS PADRES | CABRILLO 1103 | 183101103 | 2020 | 43.1 | 0.281 | 153.6 | 10 | 476 | 73091 | 1694 | 66.2508 | 102.5 | 8.08 | 110.58
LOS PADRES | CABRILLO 1104 | 183101104 | 2020 | 147 | 1.354 | 108.5 | 7 | 1980 | 214916 | 1462 | 33.6912 | 76.84 | 5.69 | 82.53
LOS PADRES | CAMBRIA 1101 | 182771101 | 2020 | 3.8 | 0.032 | 121 | 3 | 12 | 1452 | 379 | 24.9389 | 31.43 | 3.9 | 35.34
LOS PADRES | CAMBRIA 1102 | 182771102 | 2020 | 101.9 | 0.219 | 466.2 | 6 | 274 | 127733 | 1253 | 16.626 | 27.17 | 7.23 | 34.4
LOS PADRES | CAYUCOS 1101 | 182551101 | 2020 | 19.1 | 0.111 | 173 | 8 | 90 | 15566 | 814 | 2.1061 | 44.62 | 5.81 | 50.43
LOS PADRES | CAYUCOS 1102 | 182551102 | 2020 | 0.6 | 0.004 | 155 | 1 | 16 | 2480 | 4052 | 15.8194 | 57.65 | 3.54 | 61.19
LOS PADRES | CHOLAME 2102 | 182562102 | 2020 | 283.2 | 1.185 | 238.9 | 28 | 716 | 171051 | 604 | 62.6162 | 211.04 | 2.1 | 213.14
LOS PADRES | CMC 1101 | 183111101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0423 | 1.84 | 0 | 1.84
LOS PADRES | CMC 1102 | 183111102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36161 | 0.44 | 0 | 0.44
LOS PADRES | DIABLO CANYON 1101 | 189001101 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 2.58 | 2.58
LOS PADRES | DIVIDE 1103 | 182571103 | 2020 | 0.6 | 0.009 | 75 | 1 | 1 | 75 | 117 | 2.5019 | 20.38 | 0 | 20.38
LOS PADRES | FOOTHILL 1101 | 182951101 | 2020 | 20.1 | 0.125 | 160.7 | 6 | 48 | 7715 | 384 | 21.6162 | 38.02 | 1.8 | 39.82
LOS PADRES | FOOTHILL 1102 | 182951102 | 2020 | 75.3 | 0.985 | 76.4 | 8 | 4009 | 306165 | 4068 | 11.598 | 25.09 | 20 | 45.09
LOS PADRES | GOLDTREE 1105 | 182581105 | 2020 | 1.4 | 0.008 | 169 | 2 | 21 | 3549 | 2491 | 7.4234 | 14.68 | 3.67 | 18.35
LOS PADRES | GOLDTREE 1107 | 182581107 | 2020 | 84.7 | 0.426 | 199 | 1 | 20 | 3980 | 47 | 0.9199 | 3.8 | 0.25 | 4.05
LOS PADRES | GOLDTREE 1108 | 182581108 | 2020 | 20.4 | 0.236 | 86.4 | 2 | 787 | 68006 | 3332 | 2.2661 | 14.67 | 6 | 20.67
LOS PADRES | MESA 1101 | 182821101 | 2020 | 353.4 | 5.545 | 63.7 | 14 | 11145 | 710269 | 2010 | 52.5946 | 81.76 | 9.04 | 90.8
LOS PADRES | MESA 1103 | 182821103 | 2020 | 36.1 | 0.737 | 48.9 | 10 | 5623 | 274957 | 7626 | 10.6165 | 75.59 | 57.05 | 132.65
LOS PADRES | MORRO BAY 1101 | 183011101 | 2020 | 15.7 | 0.097 | 161.5 | 4 | 485 | 78347 | 4978 | 6.1088 | 46.11 | 8 | 54.1
LOS PADRES | MORRO BAY 1102 | 183011102 | 2020 | 116.4 | 1.297 | 89.7 | 8 | 8769 | 786936 | 6759 | 24.1547 | 57.49 | 11.08 | 68.57
LOS PADRES | OCEANO 1102 | 182601102 | 2020 | 300.1 | 0.479 | 626.3 | 13 | 1291 | 808516 | 2694 | 37.8684 | 54.08 | 18.33 | 72.41
LOS PADRES | OCEANO 1103 | 182601103 | 2020 | 33.6 | 0.555 | 60.6 | 5 | 2282 | 138248 | 4110 | 1.2092 | 11.43 | 29.5 | 40.92
LOS PADRES | OCEANO 1104 | 182601104 | 2020 | 41.4 | 0.242 | 171.2 | 17 | 1299 | 222333 | 5374 | 91.1163 | 111.81 | 32.33 | 144.14
LOS PADRES | OCEANO 1105 | 182601105 | 2020 | 45.1 | 1.053 | 42.8 | 4 | 6988 | 299110 | 6635 | 0.90646 | 23.81 | 18.59 | 42.4
LOS PADRES | OCEANO 1106 | 182601106 | 2020 | 113.2 | 1.095 | 103.3 | 5 | 6216 | 642413 | 5676 | 2.3432 | 29.42 | 8.61 | 38.04
LOS PADRES | OILFIELDS 1103 | 182391103 | 2020 | 134 | 0.793 | 169.1 | 27 | 1842 | 311519 | 2324 | 119.3067 | 140.92 | 26.36 | 167.28
LOS PADRES | PALMER 1101 | 183031101 | 2020 | 113.3 | 1.045 | 108.4 | 2 | 936 | 101477 | 896 | 43.3899 | 62.79 | 9.72 | 72.52
LOS PADRES | PASO ROBLES 1103 | 182611103 | 2020 | 249.6 | 3.553 | 70.2 | 12 | 10173 | 714511 | 2863 | 40.8227 | 61.54 | 29.91 | 91.44
LOS PADRES | PASO ROBLES 1104 | 182611104 | 2020 | 63.8 | 0.329 | 193.6 | 8 | 1045 | 202329 | 3173 | 44.6473 | 67.16 | 11.26 | 78.42
LOS PADRES | PASO ROBLES 1107 | 182611107 | 2020 | 206.2 | 1.072 | 192.3 | 4 | 2291 | 440609 | 2137 | 0.27821 | 37.35 | 17.73 | 55.08
LOS PADRES | PERRY 1101 | 183071101 | 2020 | 28.5 | 0.156 | 183 | 15 | 553 | 101176 | 3554 | 65.9007 | 78.65 | 6.85 | 85.5
LOS PADRES | PURISIMA 1101 | 182971101 | 2020 | 16 | 0.174 | 92 | 8 | 418 | 38466 | 2398 | 19.7618 | 53.41 | 10.86 | 64.27
LOS PADRES | SAN LUIS OBISPO 1101 | 182631101 | 2020 | 124.5 | 0.834 | 149.4 | 5 | 2338 | 349183 | 2804 | 26.6993 | 39.13 | 3.79 | 42.91
LOS PADRES | SAN LUIS OBISPO 1102 | 182631102 | 2020 | 79 | 1.728 | 45.7 | 8 | 6087 | 278214 | 3523 | 0.64938 | 12.85 | 8.2 | 21.05
LOS PADRES | SAN LUIS OBISPO 1103 | 182631103 | 2020 | 0.6 | 0.002 | 315 | 1 | 6 | 1890 | 2950 | 22.2397 | 38.66 | 29.64 | 68.29
LOS PADRES | SAN LUIS OBISPO 1104 | 182631104 | 2020 | 162.5 | 0.834 | 194.8 | 8 | 1118 | 217731 | 1340 | 61.8061 | 81.31 | 22.7 | 104.02
LOS PADRES | SAN LUIS OBISPO 1105 | 182631105 | 2020 | 2 | 0.02 | 96.8 | 3 | 61 | 5905 | 2996 | 1.6051 | 11.71 | 4 | 15.71
LOS PADRES | SAN LUIS OBISPO 1107 | 182631107 | 2020 | 54.3 | 0.254 | 213.8 | 15 | 868 | 185545 | 3418 | 48.2391 | 51.69 | 28.54 | 80.23
LOS PADRES | SAN LUIS OBISPO 1108 | 182631108 | 2020 | 13.6 | 0.026 | 530.1 | 2 | 91 | 48238 | 3557 | 2.191 | 10.57 | 18.6 | 29.16
LOS PADRES | SAN MIGUEL 1104 | 182661104 | 2020 | 56 | 0.545 | 102.8 | 12 | 696 | 71554 | 1278 | 26.3041 | 138.62 | 9.98 | 148.59
LOS PADRES | SAN MIGUEL 1105 | 182661105 | 2020 | 14.4 | 0.143 | 100.2 | 2 | 157 | 15732 | 1095 | 1.5169 | 20.15 | 5.01 | 25.16
LOS PADRES | SAN MIGUEL 1106 | 182661106 | 2020 | 60.4 | 0.282 | 214.1 | 2 | 92 | 19701 | 326 | 39.2111 | 76.21 | 1.53 | 77.74
LOS PADRES | SANTA MARIA 1108 | 182671108 | 2020 | 11.9 | 0.065 | 182.9 | 10 | 372 | 68052 | 5695 | 73.5224 | 94.23 | 13.84 | 108.07
LOS PADRES | SANTA YNEZ 1101 | 182721101 | 2020 | 77.5 | 0.448 | 173.1 | 14 | 591 | 102286 | 1320 | 29.0429 | 58.55 | 15.96 | 74.51
LOS PADRES | SANTA YNEZ 1102 | 182721102 | 2020 | 10.3 | 0.066 | 155.7 | 6 | 154 | 23971 | 2327 | 14.8251 | 33.71 | 17.6 | 51.3
LOS PADRES | SANTA YNEZ 1104 | 182721104 | 2020 | 62 | 0.343 | 180.7 | 12 | 719 | 129935 | 2097 | 46.4394 | 84.71 | 22.44 | 107.15
LOS PADRES | SCE REFUGIO 1701 | 188071701 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0.002245 | 0.29 | 0 | 0.29
LOS PADRES | SCE VEGAS 1701 | 188881701 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.10467 | 0.17 | 0 | 0.17
LOS PADRES | SISQUOC 1102 | 182811102 | 2020 | 44.2 | 0.15 | 295.3 | 4 | 88 | 25984 | 588 | 53.8095 | 116.36 | 4.32 | 120.68
LOS PADRES | SISQUOC 1103 | 182811103 | 2020 | 259 | 1.597 | 162.2 | 9 | 479 | 77685 | 300 | 29.5661 | 50.67 | 0.9 | 51.58
LOS PADRES | TEMPLETON 2108 | 183052108 | 2020 | 26 | 0.347 | 75 | 4 | 1034 | 77554 | 2984 | 5.7967 | 36.15 | 9.07 | 45.21
LOS PADRES | TEMPLETON 2110 | 183052110 | 2020 | 271.8 | 2.315 | 117.4 | 17 | 7246 | 850598 | 3130 | 137.9686 | 175.25 | 35.69 | 210.94
LOS PADRES | TEMPLETON 2111 | 183052111 | 2020 | 65.1 | 0.425 | 153.1 | 16 | 1058 | 162002 | 2489 | 46.9331 | 64.02 | 13.74 | 77.77
LOS PADRES | TEMPLETON 2112 | 183052112 | 2020 | 33.3 | 0.298 | 111.6 | 3 | 334 | 37260 | 1120 | 2.5743 | 38.03 | 16.22 | 54.25
LOS PADRES | TEMPLETON 2113 | 183052113 | 2020 | 288.6 | 4.042 | 71.4 | 48 | 22213 | 1586262 | 5496 | 202.6297 | 324.08 | 28.37 | 352.45
LOS PADRES | ZACA 1101 | 182681101 | 2020 | 79 | 1.099 | 71.9 | 4 | 178 | 12799 | 162 | 20.5949 | 25.72 | 4.81 | 30.53
LOS PADRES | ZACA 1102 | 182681102 | 2020 | 59.4 | 0.403 | 147.4 | 8 | 575 | 84767 | 1427 | 64.606 | 80.16 | 26.05 | 106.21
MISSION | BANCROFT 0401 | 13030401 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1866 | 0.043075 | 8.22 | 1.5 | 9.72
MISSION | BANCROFT 0402 | 13030402 | 2020 | 643.3 | 1 | 643.3 | 1 | 973 | 625961 | 973 | 0.37117 | 4.58 | 0.42 | 4.99
MISSION | CASTRO VALLEY 1102 | 14091102 | 2020 | 12.7 | 0.228 | 55.7 | 5 | 1231 | 68591 | 5408 | 1.2404 | 22.03 | 19.23 | 41.26
MISSION | CASTRO VALLEY 1105 | 14091105 | 2020 | 115.4 | 1.164 | 99.2 | 8 | 6492 | 643936 | 5579 | 2.701 | 27.8 | 3.66 | 31.46
MISSION | CASTRO VALLEY 1108 | 14091108 | 2020 | 247.6 | 0.722 | 342.8 | 5 | 4191 | 1436680 | 5802 | 17.2261 | 41.12 | 14.12 | 55.23
MISSION | CASTRO VALLEY 1110 | 14091110 | 2020 | 41.1 | 0.388 | 105.9 | 12 | 1199 | 127009 | 3094 | 22.9459 | 24.79 | 24.62 | 49.41
MISSION | CASTRO VALLEY 1111 | 14091111 | 2020 | 4.5 | 0.034 | 133.8 | 1 | 87 | 11640 | 2589 | 6.0866 | 8.55 | 25.35 | 33.91
MISSION | CAYETANO 2109 | 14422109 | 2020 | 48.7 | 0.068 | 714.7 | 5 | 214 | 152937 | 3143 | 36.3201 | 49.55 | 29.47 | 79.03
MISSION | CAYETANO 2111 | 14422111 | 2020 | 10 | 0.042 | 239 | 4 | 86 | 20554 | 2055 | 5.5889 | 12.24 | 21.59 | 33.83
MISSION | ESTUDILLO 0401 | 13480401 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 787 | 0.85032 | 4.73 | 0.17 | 4.9
MISSION | FREMONT 1104 | 14351104 | 2020 | 2.3 | 0.039 | 59.3 | 2 | 160 | 9488 | 4112 | 1.1941 | 21.63 | 28.05 | 49.67
MISSION | JARVIS 1101 | 13501101 | 2020 | 28.4 | 0.174 | 162.9 | 8 | 804 | 130961 | 4615 | 0.81682 | 13.85 | 18.11 | 31.95
MISSION | JARVIS 1108 | 13501108 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 4324 | 0.83888 | 18.05 | 11.52 | 29.57
MISSION | JARVIS 1111 | 13501111 | 2020 | 3.6 | 0.059 | 61.9 | 4 | 374 | 23145 | 6392 | 1.5329 | 19.03 | 27.2 | 46.23
MISSION | LAS POSITAS 2108 | 14402108 | 2020 | 2.8 | 0.027 | 102.5 | 3 | 88 | 9017 | 3245 | 7.5237 | 20.58 | 56.2 | 76.79
MISSION | NORTH DUBLIN 2101 | 14052101 | 2020 | 1.6 | 0.013 | 120.2 | 1 | 63 | 7574 | 4886 | 3.8331 | 1.85 | 42.49 | 44.34
MISSION | NORTH DUBLIN 2103 | 14052103 | 2020 | 163.7 | 1.43 | 114.4 | 10 | 5194 | 594383 | 3631 | 19.9882 | 21.71 | 35.51 | 57.22
MISSION | RADUM 1105 | 13151105 | 2020 | 2.5 | 0.028 | 90.6 | 2 | 64 | 5796 | 2323 | 3.3853 | 11.86 | 10.06 | 21.91
MISSION | RESEARCH 2102 | 14692102 | 2020 | 16.4 | 0.725 | 22.7 | 8 | 3046 | 69034 | 4200 | 2.2849 | 20.71 | 33.37 | 54.08
MISSION | SAN LEANDRO U 1109 | 13111109 | 2020 | 11 | 0.061 | 180.7 | 5 | 241 | 43557 | 3958 | 12.533 | 19.75 | 11.7 | 31.44
MISSION | SAN LEANDRO U 1114 | 13111114 | 2020 | 251.3 | 0.593 | 424 | 7 | 3086 | 1308341 | 5206 | 10.7121 | 28.96 | 5.49 | 34.45
MISSION | SAN RAMON 2101 | 14232101 | 2020 | 1.1 | 0.028 | 38 | 1 | 172 | 6536 | 6086 | 0.79388 | 1.07 | 52.06 | 53.13
MISSION | SAN RAMON 2102 | 14232102 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 4855 | 1.763 | 2.33 | 44.47 | 46.8
MISSION | SAN RAMON 2103 | 14232103 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2701 | 0.002842 | 2.74 | 25.86 | 28.6
MISSION | SAN RAMON 2106 | 14232106 | 2020 | 134.9 | 1.086 | 124.2 | 3 | 2156 | 267782 | 1985 | 0.46931 | 5.1 | 17.81 | 22.9
MISSION | SAN RAMON 2107 | 14232107 | 2020 | 73.3 | 1.175 | 62.4 | 12 | 6000 | 374286 | 5106 | 15.0157 | 27.44 | 37.7 | 65.14
MISSION | SAN RAMON 2108 | 14232108 | 2020 | 33.5 | 0.159 | 211.2 | 10 | 604 | 127593 | 3805 | 16.5044 | 17.35 | 40.77 | 58.12
MISSION | SAN RAMON 2117 | 14232117 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1484 | 0.68297 | 1.68 | 18.08 | 19.75
MISSION | SAN RAMON 2119 | 14232119 | 2020 | 0.8 | 0.005 | 155.1 | 6 | 14 | 2172 | 2895 | 0.73831 | 3.24 | 28.57 | 31.81
MISSION | SUNOL 1101 | 14241101 | 2020 | 120.2 | 1.357 | 88.6 | 12 | 993 | 87961 | 732 | 35.3612 | 55.25 | 4.57 | 59.82
MISSION | TASSAJARA 2109 | 14662109 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2045 | 1.9336 | 4.03 | 35.2 | 39.23
MISSION | TASSAJARA 2113 | 14662113 | 2020 | 0 | 0 | 6 | 1 | 1 | 6 | 6078 | 3.8533 | 4.83 | 59.5 | 64.34
MISSION | VASCO 1102 | 13751102 | 2020 | 138 | 0.753 | 183.3 | 12 | 1250 | 229141 | 1661 | 47.2109 | 85.38 | 15.62 | 101.01
MISSION | VINEYARD 2107 | 14502107 | 2020 | 33.1 | 1.147 | 28.8 | 7 | 4022 | 115955 | 3507 | 3.439 | 13.76 | 36.22 | 49.98
MISSION | VINEYARD 2108 | 14502108 | 2020 | 78.4 | 0.83 | 94.4 | 7 | 3432 | 323890 | 4133 | 5.7262 | 13.28 | 42.89 | 56.16
MISSION | VINEYARD 2110 | 14502110 | 2020 | 0.1 | 0.002 | 37 | 1 | 15 | 555 | 6896 | 6.5108 | 11.2 | 57.31 | 68.52
NORTH BAY | ALTO 1120 | 42031120 | 2020 | 133.7 | 0.609 | 219.7 | 4 | 2865 | 629415 | 4707 | 4.0683 | 20.37 | 19.1 | 39.47
NORTH BAY | ALTO 1122 | 42031122 | 2020 | 38.1 | 0.775 | 49.2 | 4 | 2780 | 136810 | 3589 | 13.7111 | 21.88 | 6.51 | 28.39
NORTH BAY | ALTO 1123 | 42031123 | 2020 | 76.3 | 1.111 | 68.7 | 5 | 2595 | 178205 | 2336 | 0.70785 | 10.33 | 8.35 | 18.68
NORTH BAY | ALTO 1124 | 42031124 | 2020 | 82.3 | 1.152 | 71.5 | 9 | 4704 | 336277 | 4084 | 28.6021 | 35.11 | 4.12 | 39.22
NORTH BAY | ALTO 1125 | 42031125 | 2020 | 20.6 | 0.786 | 26.1 | 8 | 3144 | 82200 | 3999 | 37.6988 | 44.74 | 3.91 | 48.65
NORTH BAY | BOLINAS 1101 | 42261101 | 2020 | 43.2 | 0.353 | 122.3 | 7 | 575 | 70296 | 1628 | 35.645 | 51.68 | 7.83 | 59.51
NORTH BAY | CALISTOGA 1102 | 42711102 | 2020 | 300.8 | 3.538 | 85 | 15 | 7643 | 649729 | 2160 | 26.1764 | 45.31 | 8.45 | 53.75
NORTH BAY | GREENBRAE 1102 | 43091102 | 2020 | 0 | 0.001 | 43 | 1 | 2 | 86 | 3594 | 5.991 | 13.03 | 13.08 | 26.11
NORTH BAY | GREENBRAE 1103 | 43091103 | 2020 | 18.9 | 0.273 | 69.1 | 4 | 604 | 41762 | 2212 | 0.80908 | 7.87 | 7.39 | 15.26
NORTH BAY | GREENBRAE 1104 | 43091104 | 2020 | 85.5 | 0.966 | 88.6 | 12 | 2469 | 218645 | 2557 | 0.24266 | 18.3 | 11.57 | 29.87
NORTH BAY | IGNACIO 1101 | 42481101 | 2020 | 28.4 | 0.488 | 58.1 | 4 | 1377 | 80072 | 2819 | 7.1196 | 11.74 | 15.48 | 27.22
NORTH BAY | IGNACIO 1103 | 42481103 | 2020 | 5.6 | 0.038 | 144.7 | 1 | 71 | 10277 | 1846 | 0.78393 | 2.74 | 14.13 | 16.87
NORTH BAY | IGNACIO 1105 | 42481105 | 2020 | 13.7 | 0.166 | 82.4 | 4 | 735 | 60599 | 4437 | 5.4303 | 20.16 | 16.86 | 37.02
NORTH BAY | LAS GALLINAS A 1104 | 42991104 | 2020 | 5.2 | 0.135 | 38.8 | 4 | 273 | 10594 | 2021 | 0.45735 | 12.97 | 3.44 | 16.41
NORTH BAY | LAS GALLINAS A 1105 | 42991105 | 2020 | 39.3 | 0.808 | 48.6 | 3 | 2295 | 111597 | 2842 | 12.0235 | 21.48 | 18.4 | 39.88
NORTH BAY | LAS GALLINAS A 1106 | 42991106 | 2020 | 10.3 | 0.052 | 200.8 | 3 | 228 | 45779 | 4424 | 2.2744 | 15.78 | 18.05 | 33.83
NORTH BAY | LAS GALLINAS A 1107 | 42991107 | 2020 | 62.9 | 0.353 | 178.1 | 4 | 849 | 151182 | 2404 | 0.032931 | 8.33 | 11.59 | 19.92
NORTH BAY | MIDDLETOWN 1101 | 43141101 | 2020 | 435 | 0.952 | 456.9 | 25 | 2003 | 915240 | 2104 | 97.2671 | 106.54 | 4.14 | 110.68
NORTH BAY | NAPA 1102 | 42021102 | 2020 | 4 | 0.012 | 326.7 | 5 | 46 | 15026 | 3768 | 0.83751 | 32.15 | 5.45 | 37.6
NORTH BAY | NOVATO 1104 | 42211104 | 2020 | 4.8 | 0.025 | 187.4 | 19 | 61 | 11432 | 2396 | 4.1033 | 23.08 | 22.72 | 45.8
NORTH BAY | OLEMA 1101 | 42291101 | 2020 | 603 | 0.975 | 618.4 | 16 | 2078 | 1285097 | 2131 | 72.6884 | 119.87 | 13.35 | 133.23
NORTH BAY | PUEBLO 1104 | 43291104 | 2020 | 24.2 | 0.176 | 137.4 | 8 | 352 | 48354 | 1998 | 29.6433 | 51.16 | 19.92 | 71.07
NORTH BAY | PUEBLO 1105 | 43291105 | 2020 | 14 | 0.117 | 120.3 | 6 | 243 | 29231 | 2081 | 23.8452 | 70.35 | 7.87 | 78.22
NORTH BAY | PUEBLO 2103 | 43292103 | 2020 | 90.4 | 1.013 | 89.2 | 32 | 4746 | 423536 | 4684 | 47.3347 | 78.83 | 40.93 | 119.76
NORTH BAY | SAN RAFAEL 1101 | 42011101 | 2020 | 32.1 | 0.657 | 48.8 | 7 | 2641 | 128903 | 4018 | 9.5826 | 23.56 | 8.18 | 31.74
NORTH BAY | SAN RAFAEL 1104 | 42011104 | 2020 | 42.6 | 0.22 | 193.6 | 7 | 968 | 187387 | 4395 | 12.9759 | 24.91 | 7.53 | 32.44
NORTH BAY | SAN RAFAEL 1105 | 42011105 | 2020 | 7.7 | 0.064 | 120 | 4 | 198 | 23764 | 3106 | 1.9747 | 23.03 | 19.11 | 42.14
NORTH BAY | SAN RAFAEL 1106 | 42011106 | 2020 | 49.4 | 0.57 | 86.6 | 10 | 2611 | 226061 | 4578 | 4.0807 | 21 | 6.99 | 27.99
NORTH BAY | SAN RAFAEL 1107 | 42011107 | 2020 | 8.1 | 0.174 | 46.5 | 4 | 799 | 37122 | 4603 | 22.0819 | 29.17 | 11.92 | 41.08
NORTH BAY | SAN RAFAEL 1108 | 42011108 | 2020 | 23 | 0.223 | 103.2 | 6 | 1394 | 143878 | 6255 | 41.1805 | 46.72 | 6.85 | 53.57
NORTH BAY | SAN RAFAEL 1109 | 42011109 | 2020 | 53.9 | 0.635 | 84.9 | 10 | 2152 | 182611 | 3387 | 10.3683 | 26.25 | 6.94 | 33.19
NORTH BAY | SAUSALITO 1101 | 42491101 | 2020 | 160.2 | 1.103 | 145.3 | 3 | 2857 | 415124 | 2591 | 1.5479 | 6.66 | 9.55 | 16.22
NORTH BAY | SAUSALITO 1102 | 42491102 | 2020 | 46.9 | 0.697 | 67.2 | 14 | 2571 | 172872 | 3687 | 9.8277 | 17.97 | 9.22 | 27.18
NORTH BAY | SILVERADO 2102 | 43432102 | 2020 | 231.7 | 3.114 | 74.4 | 21 | 4195 | 312148 | 1347 | 60.0204 | 109.3 | 20.05 | 129.35
NORTH BAY | SILVERADO 2104 | 43432104 | 2020 | 248 | 2.265 | 109.5 | 43 | 8622 | 944093 | 3807 | 120.444 | 140.48 | 12.89 | 153.37
NORTH BAY | STAFFORD 1101 | 43201101 | 2020 | 51.8 | 1.081 | 47.9 | 3 | 5346 | 256056 | 4946 | 4.4161 | 21.99 | 13.53 | 35.52
NORTH BAY | STAFFORD 1102 | 43201102 | 2020 | 23.9 | 0.187 | 127.9 | 15 | 740 | 94646 | 3965 | 22.4142 | 37.28 | 15.19 | 52.47
NORTH BAY | TOCALOMA 0241 | 43150241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016479 | 0.03 | 0 | 0.03
NORTH BAY | TULUCAY 1101 | 42301101 | 2020 | 0.9 | 0.002 | 459 | 1 | 1 | 459 | 499 | 4.5517 | 19.15 | 16.17 | 35.31
NORTH BAY | WOODACRE 1101 | 43021101 | 2020 | 87 | 0.934 | 93.2 | 8 | 1139 | 106099 | 1220 | 37.6536 | 42.22 | 5.2 | 47.42
NORTH BAY | WOODACRE 1102 | 43021102 | 2020 | 120.8 | 1.327 | 91 | 12 | 4027 | 366483 | 3035 | 30.9142 | 31.02 | 6.26 | 37.27
NORTH COAST | HIGHLANDS 1101 | 43361101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.026415 | 0.03 | 0 | 0.03
NORTH VALLEY | ANDERSON 1101 | 103261101 | 2020 | 48.2 | 0.147 | 327.2 | 7 | 251 | 82136 | 1704 | 11.9608 | 20.17 | 8 | 28.17
NORTH VALLEY | ANDERSON 1103 | 103261103 | 2020 | 300.2 | 1.568 | 191.4 | 5 | 1430 | 273761 | 912 | 9.3704 | 31.64 | 3.54 | 35.18
NORTH VALLEY | ANITA 1106 | 102841106 | 2020 | 10.2 | 0.185 | 55.4 | 9 | 198 | 10965 | 1073 | 1.4691 | 90.16 | 10.99 | 101.15
NORTH VALLEY | ANTLER 1101 | 103271101 | 2020 | 776.8 | 2.071 | 375 | 13 | 1978 | 741846 | 955 | 62.4333 | 62.7 | 4.08 | 66.78
NORTH VALLEY | BIG BEND 1101 | 103751101 | 2020 | 52.8 | 0.106 | 499.7 | 5 | 30 | 14992 | 284 | 57.5413 | 55.87 | 0.97 | 56.83
NORTH VALLEY | BIG BEND 1102 | 103751102 | 2020 | 18.7 | 0.415 | 45.1 | 5 | 161 | 7269 | 388 | 38.333 | 38.37 | 0.07 | 38.44
NORTH VALLEY | BIG MEADOWS 2101 | 102812101 | 2020 | 63.8 | 0.617 | 103.3 | 12 | 1619 | 167315 | 2624 | 60.2854 | 77.94 | 23.92 | 101.86
NORTH VALLEY | BOGARD 1101 | 103301101 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0.51616 | 0.5 | 0 | 0.5
NORTH VALLEY | BUCKS CREEK 1101 | 102211101 | 2020 | 97.6 | 0.2 | 488 | 1 | 1 | 488 | 5 | 4.8008 | 4.8 | 0 | 4.8
NORTH VALLEY | BUCKS CREEK 1102 | 102211102 | 2020 | 2.3 | 0.008 | 297 | 1 | 1 | 297 | 131 | 29.5832 | 29.39 | 0.02 | 29.42
NORTH VALLEY | BUCKS CREEK 1103 | 102211103 | 2020 | 637.7 | 2.153 | 296.2 | 7 | 691 | 204704 | 321 | 12.9182 | 12.84 | 12.75 | 25.59
NORTH VALLEY | BURNEY 1101 | 103311101 | 2020 | 11 | 0.259 | 42.4 | 5 | 485 | 20576 | 1872 | 53.2486 | 59.94 | 15.71 | 75.65
NORTH VALLEY | BURNEY 1102 | 103311102 | 2020 | 82.3 | 1.446 | 57 | 3 | 798 | 45452 | 552 | 0.67018 | 4.07 | 3.93 | 8
NORTH VALLEY | BUTTE 1105 | 103081105 | 2020 | 0.5 | 0.036 | 14 | 1 | 40 | 560 | 1107 | 30.8841 | 37.97 | 11.4 | 49.37
NORTH VALLEY | CEDAR CREEK 1101 | 103321101 | 2020 | 2445.5 | 1.449 | 1688.3 | 15 | 1140 | 1924621 | 787 | 110.7596 | 110.13 | 1.01 | 111.14
NORTH VALLEY | CHALLENGE 1101 | 103201101 | 2020 | 2098.5 | 2.415 | 868.9 | 9 | 1693 | 1471070 | 701 | 48.6185 | 48.3 | 0.64 | 48.95
NORTH VALLEY | CHESTER 1101 | 103181101 | 2020 | 6 | 1 | 6 | 1 | 996 | 5976 | 996 | 2.1705 | 8.16 | 3.21 | 11.38
NORTH VALLEY | CHESTER 1102 | 103181102 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 667 | 2.528 | 5.38 | 23.63 | 29.01
NORTH VALLEY | CLARK ROAD 1101 | 103091101 | 2020 | 8 | 0.16 | 50 | 1 | 4 | 200 | 25 | 0.017868 | 0.02 | 3.72 | 3.74
NORTH VALLEY | CLARK ROAD 1102 | 103091102 | 2020 | 143.7 | 1.664 | 86.4 | 12 | 2027 | 175077 | 1218 | 126.4877 | 136.17 | 5.39 | 141.56
NORTH VALLEY | CORNING 1101 | 103331101 | 2020 | 150 | 0.5 | 300.1 | 9 | 1228 | 368494 | 2456 | 50.4996 | 161.3 | 5.04 | 166.34
NORTH VALLEY | CORNING 1102 | 103331102 | 2020 | 153.6 | 0.882 | 174.2 | 23 | 1601 | 278852 | 1816 | 81.4497 | 199.7 | 2.02 | 201.72
NORTH VALLEY | COTTONWOOD 1101 | 102931101 | 2020 | 86.2 | 0.184 | 468.8 | 4 | 307 | 143912 | 1670 | 72.4687 | 98.12 | 3.31 | 101.44
NORTH VALLEY | COTTONWOOD 1102 | 102931102 | 2020 | 28.3 | 0.135 | 210.2 | 9 | 243 | 51085 | 1802 | 59.0401 | 83.09 | 7.69 | 90.78
NORTH VALLEY | COTTONWOOD 1103 | 102931103 | 2020 | 88.1 | 0.46 | 191.7 | 16 | 1293 | 247811 | 2812 | 136.3849 | 161.2 | 13.5 | 174.7
NORTH VALLEY | CRESCENT MILLS 2101 | 103132101 | 2020 | 88.9 | 1.392 | 63.8 | 13 | 1224 | 78103 | 879 | 51.0532 | 79.29 | 6.08 | 85.36
NORTH VALLEY | CRESTA 1101 | 102251101 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1.1996 | 1.2 | 0.16 | 1.36
NORTH VALLEY | DESCHUTES 1101 | 103351101 | 2020 | 52 | 0.384 | 135.4 | 9 | 464 | 62823 | 1209 | 112.0645 | 130.7 | 3.41 | 134.11
NORTH VALLEY | DESCHUTES 1104 | 103351104 | 2020 | 29.3 | 0.157 | 186.9 | 7 | 384 | 71780 | 2451 | 84.377 | 131.07 | 9.57 | 140.65
NORTH VALLEY | EAST QUINCY 1101 | 102551101 | 2020 | 73.2 | 0.127 | 574.4 | 3 | 200 | 114885 | 1569 | 4.5014 | 17.46 | 5.67 | 23.13
NORTH VALLEY | ELK CREEK 1101 | 102781101 | 2020 | 120.1 | 1.096 | 109.6 | 11 | 1005 | 110158 | 917 | 105.2862 | 179.79 | 1.75 | 181.54
NORTH VALLEY | FRENCH GULCH 1101 | 103381101 | 2020 | 27 | 0.25 | 108 | 1 | 63 | 6804 | 252 | 16.0458 | 15.99 | 1.69 | 17.68
NORTH VALLEY | FRENCH GULCH 1102 | 103381102 | 2020 | 27.8 | 0.184 | 151 | 1 | 7 | 1057 | 38 | 18.6998 | 18.77 | 0.07 | 18.84
NORTH VALLEY | GANSNER 1101 | 103021101 | 2020 | 134.9 | 0.458 | 294.5 | 9 | 794 | 233836 | 1733 | 38.4934 | 48.23 | 6.34 | 54.57
NORTH VALLEY | GIRVAN 1101 | 103401101 | 2020 | 3412.6 | 0.23 | 14830 | 15 | 298 | 4419334 | 1295 | 107.8117 | 107.84 | 7.48 | 115.31
NORTH VALLEY | GIRVAN 1102 | 103401102 | 2020 | 460.2 | 1.485 | 309.9 | 10 | 2140 | 663208 | 1441 | 46.5405 | 75.99 | 9.97 | 85.96
NORTH VALLEY | GLENN 1101 | 102601101 | 2020 | 72.9 | 0.616 | 118.5 | 21 | 1131 | 133980 | 1837 | 2.3047 | 136.34 | 6.37 | 142.71
NORTH VALLEY | GRAYS FLAT 0401 | 102530401 | 2020 | 1.4 | 0.08 | 18 | 1 | 10 | 180 | 125 | 10.7279 | 10.64 | 0.17 | 10.81
NORTH VALLEY | HAMILTON BRANCH 1101 | 102361101 | 2020 | 227.3 | 1.674 | 135.8 | 4 | 3997 | 542824 | 2388 | 25.4399 | 34.01 | 25.95 | 59.97
NORTH VALLEY | JESSUP 1101 | 103441101 | 2020 | 118.2 | 1.956 | 60.4 | 5 | 3991 | 241127 | 2040 | 65.9412 | 79.68 | 7.87 | 87.55
NORTH VALLEY | JESSUP 1102 | 103441102 | 2020 | 69.9 | 0.648 | 107.8 | 6 | 1519 | 163782 | 2344 | 57.7513 | 86.88 | 4.55 | 91.42
NORTH VALLEY | JESSUP 1103 | 103441103 | 2020 | 73.7 | 1.105 | 66.7 | 5 | 1790 | 119360 | 1620 | 4.7174 | 38.07 | 5.65 | 43.73
NORTH VALLEY | KANAKA 1101 | 103221101 | 2020 | 14.8 | 0.057 | 258.1 | 4 | 34 | 8776 | 592 | 80.02 | 65.21 | 0.93 | 66.14
NORTH VALLEY | KESWICK 1101 | 103451101 | 2020 | 55.7 | 0.216 | 258.4 | 4 | 111 | 28681 | 515 | 51.7267 | 51.18 | 4.01 | 55.19
NORTH VALLEY | LOS MOLINOS 1101 | 103481101 | 2020 | 65.2 | 0.379 | 172.1 | 10 | 392 | 67448 | 1034 | 0.31276 | 55.8 | 1.37 | 57.17
NORTH VALLEY | MC ARTHUR 1101 | 103491101 | 2020 | 89.8 | 0.755 | 118.8 | 15 | 1103 | 131066 | 1460 | 72.875 | 177.52 | 9.87 | 187.39
NORTH VALLEY | MC ARTHUR 1102 | 103491102 | 2020 | 139.5 | 0.613 | 227.4 | 4 | 176 | 40025 | 287 | 2.283 | 30.31 | 1.96 | 32.27
NORTH VALLEY | NOTRE DAME 1103 | 102041103 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1895 | 0.54331 | 7.78 | 22.01 | 29.79
NORTH VALLEY | NOTRE DAME 1104 | 102041104 | 2020 | 22.1 | 0.148 | 149.1 | 4 | 357 | 53214 | 2409 | 28.2046 | 35.78 | 17.84 | 53.62
NORTH VALLEY | OREGON TRAIL 1102 | 103521102 | 2020 | 297 | 1.263 | 235.2 | 6 | 1105 | 259844 | 875 | 46.2542 | 49.26 | 6.08 | 55.34
NORTH VALLEY | OREGON TRAIL 1103 | 103521103 | 2020 | 18.2 | 0.293 | 62 | 4 | 524 | 32511 | 1789 | 117.3702 | 119.88 | 7.88 | 127.76
NORTH VALLEY | OREGON TRAIL 1104 | 103521104 | 2020 | 33.3 | 0.617 | 53.9 | 3 | 616 | 33224 | 998 | 45.5877 | 54.79 | 2.85 | 57.63
NORTH VALLEY | ORO FINO 1101 | 103031101 | 2020 | 24.8 | 0.576 | 43.2 | 12 | 1372 | 59224 | 2384 | 38.4205 | 38.29 | 0.82 | 39.11
NORTH VALLEY | ORO FINO 1102 | 103031102 | 2020 | 212.1 | 1.478 | 143.5 | 22 | 2999 | 430292 | 2029 | 110.01 | 109.75 | 4.06 | 113.81
NORTH VALLEY | PANORAMA 1101 | 103461101 | 2020 | 1.8 | 0.009 | 203.3 | 2 | 13 | 2643 | 1497 | 13.6885 | 39.15 | 1.63 | 40.79
NORTH VALLEY | PANORAMA 1102 | 103461102 | 2020 | 43 | 0.455 | 94.5 | 18 | 1140 | 107737 | 2507 | 33.3206 | 84.18 | 8.16 | 92.33
NORTH VALLEY | PARADISE 1103 | 102831103 | 2020 | 10.9 | 0.079 | 138.4 | 3 | 47 | 6504 | 595 | 7.6685 | 9.19 | 14.56 | 23.75
NORTH VALLEY | PARADISE 1104 | 102831104 | 2020 | 38.8 | 0.048 | 802.5 | 8 | 109 | 87472 | 2254 | 78.2383 | 92.13 | 36.95 | 129.08
NORTH VALLEY | PARADISE 1105 | 102831105 | 2020 | 243.3 | 1.012 | 240.4 | 8 | 1688 | 405787 | 1668 | 43.2576 | 49.53 | 14.21 | 63.74
NORTH VALLEY | PARADISE 1106 | 102831106 | 2020 | 14.7 | 0.043 | 342 | 2 | 22 | 7524 | 511 | 14.8476 | 14.74 | 11.25 | 25.99
NORTH VALLEY | PIT NO 1 1101 | 103721101 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 881 | 31.7476 | 52.82 | 4.65 | 57.47
NORTH VALLEY | PIT NO 3 2101 | 103732101 | 2020 | 110.1 | 0.184 | 597.6 | 4 | 28 | 16733 | 152 | 48.0303 | 48.54 | 3.8 | 52.33
NORTH VALLEY | PIT NO 5 1101 | 101321101 | 2020 | 2599.9 | 2.165 | 1200.7 | 5 | 262 | 314587 | 121 | 23.6874 | 23.63 | 2.97 | 26.6
NORTH VALLEY | PIT NO 7 1101 | 103501101 | 2020 | 2460 | 1 | 2460 | 1 | 2 | 4920 | 2 | 2.7084 | 2.71 | 0 | 2.71
NORTH VALLEY | RAWSON 1103 | 103531103 | 2020 | 19.4 | 0.317 | 61.2 | 6 | 804 | 49216 | 2533 | 4.5381 | 39.61 | 14 | 53.62
NORTH VALLEY | RED BLUFF 1101 | 103541101 | 2020 | 31.2 | 0.356 | 87.5 | 7 | 573 | 50158 | 1608 | 49.6258 | 74.35 | 2.41 | 76.76
NORTH VALLEY | RED BLUFF 1103 | 103541103 | 2020 | 6.7 | 0.086 | 77.8 | 5 | 235 | 18288 | 2718 | 16.857 | 38.06 | 7.61 | 45.67
NORTH VALLEY | RED BLUFF 1104 | 103541104 | 2020 | 214 | 2.797 | 76.5 | 10 | 4296 | 328745 | 1536 | 69.1888 | 93.45 | 5.53 | 98.98
NORTH VALLEY | RED BLUFF 1105 | 103541105 | 2020 | 61.3 | 0.471 | 130 | 8 | 901 | 117156 | 1912 | 14.0358 | 37.6 | 8.62 | 46.22
NORTH VALLEY | RISING RIVER 1101 | 103551101 | 2020 | 124.9 | 0.439 | 284.5 | 2 | 324 | 92162 | 738 | 47.9086 | 58.84 | 1.29 | 60.13
NORTH VALLEY | SPANISH CREEK 4401 | 103104401 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 7.7363 | 7.97 | 0 | 7.97
NORTH VALLEY | STILLWATER 1101 | 103561101 | 2020 | 24.2 | 0.397 | 60.9 | 4 | 297 | 18099 | 748 | 36.4913 | 36.58 | 0.8 | 37.38
NORTH VALLEY | STILLWATER 1102 | 103561102 | 2020 | 48 | 0.38 | 126.2 | 5 | 539 | 68045 | 1418 | 79.0175 | 78.77 | 2.42 | 81.19
NORTH VALLEY | SYCAMORE CREEK 1109 | 102971109 | 2020 | 8.9 | 0.038 | 232.4 | 3 | 98 | 22774 | 2570 | 0.16852 | 13.45 | 24.87 | 38.32
NORTH VALLEY | SYCAMORE CREEK 1111 | 102971111 | 2020 | 13.7 | 0.323 | 42.6 | 5 | 629 | 26781 | 1948 | 53.6888 | 64.94 | 14.16 | 79.1
NORTH VALLEY | TYLER 1105 | 103571105 | 2020 | 55.1 | 0.287 | 191.8 | 8 | 493 | 94568 | 1716 | 61.6796 | 111.2 | 7.91 | 119.11
NORTH VALLEY | VOLTA 1101 | 102541101 | 2020 | 213.1 | 1.742 | 122.3 | 12 | 2347 | 287095 | 1347 | 153.1783 | 153.56 | 0.73 | 154.29
NORTH VALLEY | VOLTA 1102 | 102541102 | 2020 | 919.9 | 2.98 | 308.7 | 17 | 7887 | 2435083 | 2647 | 129.7205 | 129.72 | 24.38 | 154.1
NORTH VALLEY | WHITMORE 1101 | 103601101 | 2020 | 1220.3 | 1.93 | 632.2 | 16 | 1052 | 665040 | 545 | 92.481 | 91.63 | 0.97 | 92.6
NORTH VALLEY | WILDWOOD 1101 | 103611101 | 2020 | 139.2 | 0.634 | 219.6 | 5 | 90 | 19766 | 142 | 32.3833 | 27.85 | 0.17 | 28.02
NORTH VALLEY | WYANDOTTE 1102 | 102911102 | 2020 | 154.4 | 0.988 | 156.3 | 11 | 2642 | 412888 | 2674 | 4.7699 | 39.14 | 9.94 | 49.08
NORTH VALLEY | WYANDOTTE 1103 | 102911103 | 2020 | 215.9 | 0.76 | 284.2 | 15 | 1751 | 497655 | 2305 | 85.5175 | 92.09 | 13.49 | 105.58
NORTH VALLEY | WYANDOTTE 1105 | 102911105 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 535 | 18.0394 | 25.67 | 0.09 | 25.77
NORTH VALLEY | WYANDOTTE 1106 | 102911106 | 2020 | 73.9 | 1.95 | 37.9 | 9 | 3323 | 125952 | 1704 | 1.1575 | 94.18 | 3.83 | 98
NORTH VALLEY | WYANDOTTE 1107 | 102911107 | 2020 | 40.5 | 0.864 | 46.9 | 9 | 2458 | 115185 | 2846 | 115.6437 | 153.02 | 2.1 | 155.12
NORTH VALLEY | WYANDOTTE 1109 | 102911109 | 2020 | 630.6 | 3 | 210.2 | 13 | 11013 | 2314810 | 3671 | 56.3565 | 120.64 | 7.47 | 128.11
NORTH VALLEY | WYANDOTTE 1110 | 102911110 | 2020 | 1896.4 | 1.566 | 1210.8 | 7 | 4271 | 5171526 | 2727 | 13.315 | 40.18 | 15.82 | 56.01
PENINSULA | BAY MEADOWS 2102 | 24012102 | 2020 | 3.3 | 0.038 | 87 | 1 | 128 | 11136 | 3410 | 4.1696 | 14.25 | 28.64 | 42.89
PENINSULA | BELMONT 1103 | 24031103 | 2020 | 5.6 | 0.046 | 121.2 | 2 | 179 | 21697 | 3869 | 3.6753 | 18.68 | 7.97 | 26.65
PENINSULA | BELMONT 1110 | 24031110 | 2020 | 27.4 | 1.209 | 22.7 | 5 | 7077 | 160621 | 5854 | 0.12403 | 24.13 | 5.93 | 30.06
PENINSULA | BERESFORD 0403 | 24040403 | 2020 | 24.5 | 0.45 | 54.5 | 2 | 639 | 34826 | 1420 | 5.4973 | 12.16 | 2.57 | 14.73
PENINSULA | CAROLANDS 0401 | 24060401 | 2020 | 51.6 | 0.095 | 545.8 | 2 | 83 | 45305 | 878 | 0 | 4.48 | 11.09 | 15.57
PENINSULA | CAROLANDS 0404 | 24060404 | 2020 | 55.3 | 0.444 | 124.6 | 3 | 476 | 59288 | 1073 | 4.2869 | 10.35 | 6.76 | 17.11
PENINSULA | EMERALD LAKE 0401 | 24080401 | 2020 | 250.2 | 1.216 | 205.8 | 5 | 744 | 153101 | 612 | 9.3444 | 13.23 | 1.64 | 14.87
PENINSULA | EMERALD LAKE 0402 | 24080402 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 925 | 8.3093 | 9.35 | 0.16 | 9.5
PENINSULA | HALF MOON BAY 1101 | 24101101 | 2020 | 44.3 | 1.161 | 38.1 | 15 | 3039 | 115815 | 2617 | 29.6606 | 49.16 | 10.61 | 59.77
PENINSULA | HALF MOON BAY 1102 | 24101102 | 2020 | 7.3 | 0.087 | 83.8 | 8 | 427 | 35802 | 4931 | 10.8533 | 47.94 | 12.69 | 60.62
PENINSULA | HALF MOON BAY 1103 | 24101103 | 2020 | 630.4 | 0.522 | 1206.5 | 46 | 2522 | 3042872 | 4827 | 130.649 | 164.18 | 28.15 | 192.33
PENINSULA | LAS PULGAS 0401 | 24120401 | 2020 | 0.1 | 0.001 | 92 | 1 | 1 | 92 | 1178 | 0.36135 | 6.08 | 0.32 | 6.4
PENINSULA | MENLO 1102 | 24131102 | 2020 | 64.1 | 1.448 | 44.3 | 11 | 3870 | 171254 | 2673 | 29.9127 | 63.63 | 17.98 | 81.6
PENINSULA | MENLO 1103 | 24131103 | 2020 | 299.1 | 1.098 | 272.3 | 18 | 2537 | 690858 | 2310 | 47.8497 | 65.68 | 21.36 | 87.03
PENINSULA | PACIFICA 1101 | 22811101 | 2020 | 0.4 | 0.002 | 176 | 1 | 4 | 704 | 1926 | 1.0387 | 9.18 | 1.62 | 10.79
PENINSULA | PACIFICA 1102 | 22811102 | 2020 | 4.4 | 0.061 | 71.3 | 3 | 244 | 17386 | 3979 | 3.3898 | 20.11 | 7.75 | 27.86
PENINSULA | PACIFICA 1103 | 22811103 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2817 | 1.2831 | 14.12 | 4.2 | 18.33
PENINSULA | PACIFICA 1104 | 22811104 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1294 | 0.85605 | 7.19 | 2.51 | 9.7
PENINSULA | POINT MORETTI 1101 | 82931101 | 2020 | 389.3 | 1.582 | 246.1 | 95 | 1637 | 402911 | 1035 | 61.7041 | 63.8 | 4.89 | 68.69
PENINSULA | RALSTON 1101 | 24141101 | 2020 | 85.4 | 1.003 | 85.2 | 2 | 2535 | 215968 | 2528 | 9.5342 | 14.46 | 8.53 | 23
PENINSULA | RALSTON 1102 | 24141102 | 2020 | 25.3 | 0.76 | 33.2 | 5 | 1743 | 57904 | 2293 | 4.0493 | 10.71 | 12.61 | 23.31
PENINSULA | SAN CARLOS 1103 | 24181103 | 2020 | 93 | 1.441 | 64.5 | 5 | 3510 | 226353 | 2435 | 3.9141 | 16.49 | 2.86 | 19.36
PENINSULA | SAN CARLOS 1104 | 24181104 | 2020 | 40.2 | 0.45 | 89.4 | 6 | 1821 | 162715 | 4050 | 10.9931 | 22.1 | 7.63 | 29.74
PENINSULA | SERRAMONTE 1104 | 22861104 | 2020 | 3 | 0.049 | 61 | 1 | 291 | 17751 | 5911 | 0 | 12.62 | 13.21 | 25.83
PENINSULA | SNEATH LANE 1101 | 22721101 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1800 | 3.001 | 9.42 | 1.83 | 11.25
PENINSULA | SNEATH LANE 1102 | 22721102 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 3788 | 1.5337 | 10.53 | 10.7 | 21.23
PENINSULA | SNEATH LANE 1106 | 22721106 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 4043 | 3.0362 | 11.42 | 7.88 | 19.3
PENINSULA | SNEATH LANE 1107 | 22721107 | 2020 | 15.6 | 0.129 | 120.4 | 4 | 366 | 44063 | 2831 | 1.3595 | 10.62 | 5.67 | 16.29
PENINSULA | WATERSHED 0402 | 24240402 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0.21316 | 1.19 | 0.07 | 1.26
PENINSULA | WOODSIDE 1101 | 24251101 | 2020 | 397.2 | 1.932 | 205.6 | 30 | 3476 | 714559 | 1799 | 43.905 | 61.99 | 12.06 | 74.05
PENINSULA | WOODSIDE 1102 | 24251102 | 2020 | 85.9 | 1.39 | 61.8 | 6 | 2913 | 180105 | 2096 | 0.077579 | 17.06 | 5.8 | 22.86
PENINSULA | WOODSIDE 1104 | 24251104 | 2020 | 76.3 | 0.656 | 116.4 | 18 | 1984 | 230878 | 3026 | 21.7322 | 44.17 | 16.88 | 61.05
SACRAMENTO | ARBUCKLE 1104 | 62081104 | 2020 | 94.4 | 1.186 | 79.6 | 5 | 1441 | 114677 | 1215 | 2.245 | 102.33 | 4.58 | 106.91
SACRAMENTO | BANGOR 1101 | 103191101 | 2020 | 219.8 | 1.379 | 159.4 | 27 | 3364 | 536253 | 2440 | 197.1003 | 227.93 | 2.85 | 230.78
SACRAMENTO | BROWNS VALLEY 1101 | 152921101 | 2020 | 19.8 | 0.219 | 90.7 | 9 | 132 | 11966 | 603 | 45.4989 | 66.68 | 0.22 | 66.9
SACRAMENTO | CHALLENGE 1102 | 103201102 | 2020 | 73.5 | 0.606 | 121.4 | 12 | 545 | 66137 | 900 | 63.1343 | 62.44 | 0.77 | 63.2
SACRAMENTO | CORTINA 1101 | 63121101 | 2020 | 18.3 | 0.096 | 190 | 3 | 32 | 6081 | 332 | 1.8916 | 76.57 | 1 | 77.57
SACRAMENTO | DOBBINS 1101 | 153741101 | 2020 | 35.4 | 0.207 | 170.5 | 6 | 190 | 32404 | 916 | 81.1839 | 82.34 | 3.16 | 85.51
SACRAMENTO | JAMESON 1102 | 63801102 | 2020 | 35 | 0.222 | 157.3 | 13 | 505 | 79448 | 2272 | 8.254 | 20.26 | 29.4 | 49.66
SACRAMENTO | JAMESON 1103 | 63801103 | 2020 | 22 | 0.118 | 186.6 | 8 | 155 | 28930 | 1315 | 2.3449 | 10.88 | 16.19 | 27.07
SACRAMENTO | JAMESON 1105 | 63801105 | 2020 | 79.7 | 0.563 | 141.5 | 23 | 1467 | 207614 | 2605 | 19.5848 | 64.18 | 22.28 | 86.45
SACRAMENTO | LOGAN CREEK 2102 | 103142102 | 2020 | 94.3 | 1.469 | 64.2 | 23 | 2154 | 138248 | 1466 | 3.7072 | 237.79 | 2.42 | 240.21
SACRAMENTO | MADISON 1105 | 63171105 | 2020 | 171.5 | 0.499 | 343.6 | 13 | 288 | 98971 | 577 | 0.53656 | 84.15 | 0.76 | 84.91
SACRAMENTO | MADISON 2101 | 63172101 | 2020 | 1017.8 | 3.082 | 330.3 | 33 | 6401 | 2113999 | 2077 | 8.3371 | 165.54 | 9.32 | 174.86
SACRAMENTO | MAXWELL 1105 | 62881105 | 2020 | 38.2 | 0.309 | 123.6 | 8 | 260 | 32126 | 842 | 8.4754 | 88.66 | 1.98 | 90.64
SACRAMENTO | MONTICELLO 1101 | 43051101 | 2020 | 537.2 | 1.994 | 269.4 | 31 | 2891 | 778930 | 1450 | 114.3182 | 124.46 | 9.41 | 133.86
SACRAMENTO | NAPA 1112 | 42021112 | 2020 | 33.5 | 0.355 | 94.5 | 11 | 987 | 93275 | 2782 | 20.6804 | 51.83 | 10.82 | 62.65
SACRAMENTO | PEABODY 2106 | 63642106 | 2020 | 85.4 | 1.003 | 85.1 | 4 | 2990 | 254396 | 2980 | 0.95159 | 2.72 | 34.03 | 36.75
SACRAMENTO | PEABODY 2108 | 63642108 | 2020 | 0.2 | 0.002 | 112.1 | 2 | 7 | 785 | 4009 | 0.36709 | 3.17 | 48.95 | 52.12
SACRAMENTO | PEABODY 2113 | 63642113 | 2020 | 37.9 | 0.254 | 149.2 | 2 | 1440 | 214902 | 5666 | 1.3889 | 10.21 | 41.47 | 51.67
SACRAMENTO | PUTAH CREEK 1102 | 63681102 | 2020 | 285.5 | 2.002 | 142.6 | 19 | 1824 | 260134 | 911 | 29.7913 | 51.23 | 1.21 | 52.44
SACRAMENTO | PUTAH CREEK 1103 | 63681103 | 2020 | 96.8 | 0.621 | 156 | 12 | 1267 | 197606 | 2041 | 4.2671 | 36.52 | 12.18 | 48.7
SACRAMENTO | PUTAH CREEK 1105 | 63681105 | 2020 | 78.1 | 0.501 | 155.8 | 7 | 506 | 78841 | 1009 | 2.0673 | 83.66 | 6.5 | 90.17
SACRAMENTO | VACA DIXON 1101 | 63591101 | 2020 | 5.7 | 0.058 | 98 | 1 | 62 | 6076 | 1065 | 0.83305 | 9.21 | 16.61 | 25.81
SACRAMENTO | VACA DIXON 1105 | 63591105 | 2020 | 177.1 | 3.103 | 57.1 | 18 | 4903 | 279866 | 1580 | 24.697 | 91.69 | 2.17 | 93.86
SACRAMENTO | VACAVILLE 1104 | 63601104 | 2020 | 118.1 | 2.29 | 51.6 | 11 | 3256 | 167987 | 1422 | 15.5047 | 17.62 | 9.86 | 27.48
SACRAMENTO | VACAVILLE 1108 | 63601108 | 2020 | 72 | 1.142 | 63.1 | 9 | 2659 | 167681 | 2328 | 30.045 | 47.54 | 11.29 | 58.83
SACRAMENTO | VACAVILLE 1109 | 63601109 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1834 | 0.59339 | 3.83 | 14.07 | 17.91
SACRAMENTO | VACAVILLE 1111 | 63601111 | 2020 | 104.8 | 1.374 | 76.2 | 5 | 2907 | 221630 | 2115 | 11.8933 | 17.41 | 17.55 | 34.96
SACRAMENTO | VACAVILLE 1112 | 63601112 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2567 | 0.23531 | 3.3 | 21.23 | 24.53
SAN JOSE | EDENVALE 1102 | 82951102 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2690 | 0.73065 | 5.73 | 18.63 | 24.37
SAN JOSE | EDENVALE 2107 | 82952107 | 2020 | 123.4 | 0.939 | 131.4 | 10 | 3163 | 415571 | 3369 | 4.2614 | 36.21 | 33.42 | 69.62
SAN JOSE | EDENVALE 2113 | 82952113 | 2020 | 32.6 | 0.211 | 154 | 4 | 990 | 152428 | 4682 | 0.015269 | 2.42 | 30.25 | 32.67
SAN JOSE | GREEN VALLEY 2101 | 83192101 | 2020 | 197 | 1.962 | 100.4 | 52 | 6118 | 614407 | 3119 | 43.29 | 156.77 | 10.33 | 167.1
SAN JOSE | HICKS 1115 | 83431115 | 2020 | 0.7 | 0.016 | 44.6 | 2 | 40 | 1785 | 2561 | 0.1368 | 15.41 | 4.29 | 19.69
SAN JOSE | HICKS 1116 | 83431116 | 2020 | 87.8 | 1.235 | 71.1 | 13 | 4211 | 299453 | 3410 | 14.2737 | 34.68 | 8.84 | 43.53
SAN JOSE | HICKS 2101 | 83432101 | 2020 | 58.4 | 0.407 | 143.3 | 11 | 2008 | 287751 | 4929 | 15.5227 | 42.35 | 47.55 | 89.9
SAN JOSE | HICKS 2103 | 83432103 | 2020 | 16.7 | 0.062 | 270.6 | 7 | 226 | 61163 | 3669 | 11.268 | 25.19 | 27.74 | 52.92
SAN JOSE | LLAGAS 2101 | 83182101 | 2020 | 86 | 1.074 | 80 | 28 | 2489 | 199242 | 2317 | 21.9761 | 101.76 | 20.57 | 122.33
SAN JOSE | LLAGAS 2104 | 83182104 | 2020 | 506.6 | 1.937 | 261.6 | 6 | 612 | 160089 | 316 | 2.9124 | 30.03 | 2.07 | 32.1
SAN JOSE | LLAGAS 2105 | 83182105 | 2020 | 62.1 | 0.499 | 124.3 | 5 | 2858 | 355344 | 5722 | 0.98365 | 17.55 | 29.48 | 47.03
SAN JOSE | LLAGAS 2106 | 83182106 | 2020 | 208.1 | 1.114 | 186.8 | 13 | 704 | 131498 | 632 | 2.051 | 32.94 | 13.59 | 46.53
SAN JOSE | LLAGAS 2107 | 83182107 | 2020 | 73.5 | 0.167 | 439.7 | 11 | 650 | 285812 | 3889 | 7.3526 | 22.42 | 41.74 | 64.16
SAN JOSE | MC KEE 1103 | 83531103 | 2020 | 148.4 | 0.623 | 238.2 | 7 | 2285 | 544338 | 3667 | 0.76232 | 21.92 | 6.08 | 28.01
SAN JOSE | MC KEE 1107 | 83531107 | 2020 | 135.5 | 0.446 | 304 | 9 | 1797 | 546366 | 4032 | 2.7862 | 38.01 | 7.18 | 45.19
SAN JOSE | MC KEE 1108 | 83531108 | 2020 | 3.3 | 0.017 | 193 | 2 | 72 | 13896 | 4250 | 1.0843 | 10.46 | 22.69 | 33.15
SAN JOSE | MC KEE 1111 | 83531111 | 2020 | 53 | 0.302 | 175.4 | 10 | 1062 | 186240 | 3511 | 8.9846 | 25.07 | 9.8 | 34.88
SAN JOSE | MILPITAS 1105 | 82831105 | 2020 | 13.2 | 0.66 | 20 | 2 | 2271 | 45383 | 3439 | 0.1045 | 4.7 | 31.96 | 36.66
SAN JOSE | MILPITAS 1108 | 82831108 | 2020 | 3.1 | 0.028 | 109.9 | 1 | 117 | 12864 | 4123 | 0.030458 | 13.28 | 20.24 | 33.52
SAN JOSE | MILPITAS 1109 | 82831109 | 2020 | 73.8 | 2.316 | 31.9 | 12 | 10036 | 319728 | 4334 | 31.5177 | 46.22 | 17.2 | 63.42
SAN JOSE | MORGAN HILL 2104 | 83242104 | 2020 | 3.4 | 0.034 | 100 | 10 | 135 | 13494 | 3963 | 6.4135 | 20.98 | 40.98 | 61.96
SAN JOSE | MORGAN HILL 2105 | 83242105 | 2020 | 336.7 | 3.722 | 90.5 | 23 | 15982 | 1445844 | 4294 | 54.389 | 81.39 | 38.89 | 120.28
SAN JOSE | MORGAN HILL 2106 | 83242106 | 2020 | 4.1 | 0.052 | 78.5 | 2 | 132 | 10362 | 2542 | 0.62349 | 39.07 | 20.49 | 59.57
SAN JOSE | MORGAN HILL 2109 | 83242109 | 2020 | 17.6 | 0.031 | 567.8 | 4 | 168 | 95382 | 5405 | 2.5479 | 26.35 | 39.38 | 65.73
SAN JOSE | MORGAN HILL 2110 | 83242110 | 2020 | 68.3 | 1.167 | 58.5 | 15 | 2879 | 168452 | 2467 | 2.8468 | 32.74 | 16.88 | 49.62
SAN JOSE | MORGAN HILL 2111 | 83242111 | 2020 | 118.8 | 1.243 | 95.5 | 25 | 3327 | 317825 | 2676 | 54.7286 | 71.92 | 32.9 | 104.82
SAN JOSE | PIERCY 2110 | 83912110 | 2020 | 1.6 | 0.009 | 183.3 | 3 | 27 | 4949 | 3061 | 21.9439 | 27.42 | 39.79 | 67.21
SAN JOSE | SWIFT 2102 | 83392102 | 2020 | 2.4 | 0.039 | 59.9 | 3 | 150 | 8987 | 3802 | 0.43933 | 2.97 | 34.51 | 37.47
SAN JOSE | SWIFT 2107 | 83392107 | 2020 | 201.7 | 2.1 | 96 | 13 | 9884 | 949030 | 4706 | 2.0918 | 11.92 | 34.7 | 46.62
SAN JOSE | SWIFT 2109 | 83392109 | 2020 | 3.3 | 0.059 | 55.1 | 2 | 284 | 15654 | 4793 | 0.32738 | 5.46 | 39.16 | 44.62
SIERRA | FLINT 1102 | 152531102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092864 | 0.07 | 0 | 0.07
SIERRA | NARROWS 2104 | 153132104 | 0 | 0 | 0 | 58.3 | 3 | 712 | 41539 | 0 | 0.002842 | 0 | 0.03 | 0.04
SIERRA | NARROWS PH 1151 | 153131151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17836 | 0 | 0 | 0
SIERRA | ALLEGHANY 1101 | 152101101 | 2020 | 733.8 | 2.636 | 278.4 | 13 | 2831 | 788062 | 1074 | 61.8688 | 77.15 | 1.72 | 78.87
SIERRA | ALLEGHANY 1102 | 152101102 | 2020 | 1718.5 | 3.315 | 518.4 | 10 | 547 | 283554 | 165 | 18.0314 | 17.79 | 0.58 | 18.37
SIERRA | APPLE HILL 1103 | 153661103 | 2020 | 150.8 | 2.42 | 62.3 | 16 | 3132 | 195143 | 1294 | 52.0777 | 60.06 | 5.85 | 65.91
SIERRA | APPLE HILL 1104 | 153661104 | 2020 | 583.5 | 1.918 | 304.2 | 32 | 4772 | 1451751 | 2488 | 92.0704 | 95.6 | 2.62 | 98.22
SIERRA | AUBURN 1101 | 152161101 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 718 | 3.2881 | 4.93 | 1.07 | 6
SIERRA | AUBURN 1102 | 152161102 | 2020 | 5.5 | 0.109 | 50.3 | 4 | 153 | 7696 | 1403 | 3.1893 | 8.92 | 3.17 | 12.09
SIERRA | BELL 1107 | 152701107 | 2020 | 62.4 | 0.298 | 209.2 | 15 | 434 | 90786 | 1454 | 43.5386 | 50.47 | 11.52 | 61.99
SIERRA | BELL 1108 | 152701108 | 2020 | 266.5 | 2.729 | 97.7 | 22 | 10030 | 979790 | 3676 | 67.0397 | 80.09 | 17.26 | 97.35
SIERRA | BELL 1109 | 152701109 | 2020 | 79 | 0.373 | 211.8 | 6 | 344 | 72860 | 922 | 14.3405 | 18.15 | 8.44 | 26.6
SIERRA | BELL 1110 | 152701110 | 2020 | 7 | 0.068 | 103.4 | 4 | 109 | 11273 | 1601 | 0.21901 | 11.25 | 13.41 | 24.66
SIERRA | BONNIE NOOK 1101 | 152301101 | 2020 | 2181.9 | 1.261 | 1730.6 | 17 | 643 | 1112786 | 510 | 24.0917 | 23.75 | 1.23 | 24.98
SIERRA | BONNIE NOOK 1102 | 152301102 | 2020 | 5313 | 1.962 | 2707.4 | 19 | 1044 | 2826497 | 532 | 34.0109 | 33.99 | 5.25 | 39.25
SIERRA | BRUNSWICK 1102 | 152481102 | 2020 | 248.1 | 0.394 | 629.4 | 19 | 572 | 360019 | 1451 | 51.836 | 54.13 | 9.1 | 63.23
SIERRA | BRUNSWICK 1103 | 152481103 | 2020 | 229.8 | 2.966 | 77.5 | 21 | 9679 | 749881 | 3263 | 56.396 | 62.39 | 11.1 | 73.49
SIERRA | BRUNSWICK 1104 | 152481104 | 2020 | 118 | 1.063 | 111.1 | 13 | 2715 | 301517 | 2555 | 56.2952 | 57.81 | 16.13 | 73.94
SIERRA | BRUNSWICK 1105 | 152481105 | 2020 | 152.9 | 0.652 | 234.6 | 32 | 2436 | 571543 | 3737 | 121.9416 | 122.01 | 29.35 | 151.36
SIERRA | BRUNSWICK 1106 | 152481106 | 2020 | 153.2 | 1.669 | 91.8 | 30 | 7584 | 696054 | 4544 | 173.4939 | 183.66 | 9.72 | 193.38
SIERRA | BRUNSWICK 1107 | 152481107 | 2020 | 21.4 | 0.34 | 63 | 1 | 920 | 57960 | 2705 | 9.7006 | 19.5 | 4.05 | 23.56
SIERRA | BRUNSWICK 1110 | 152481110 | 2020 | 30.7 | 0.509 | 60.3 | 9 | 1603 | 96718 | 3151 | 23.2063 | 32.9 | 15.21 | 48.11
SIERRA | CLARKSVILLE 2103 | 153612103 | 2020 | 15.6 | 0.135 | 115.8 | 3 | 394 | 45614 | 2915 | 32.3792 | 50.44 | 42.34 | 92.78
SIERRA | CLARKSVILLE 2104 | 153612104 | 2020 | 23.3 | 0.114 | 204.9 | 8 | 416 | 85228 | 3661 | 67.0596 | 75.72 | 31.94 | 107.66
SIERRA | CLARKSVILLE 2105 | 153612105 | 2020 | 62.5 | 0.298 | 209.6 | 5 | 1208 | 253237 | 4050 | 11.523 | 13.43 | 58.21 | 71.64
SIERRA | CLARKSVILLE 2106 | 153612106 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 4728 | 0.91427 | 2.21 | 67.58 | 69.79
SIERRA | CLARKSVILLE 2109 | 153612109 | 2020 | 107.6 | 1.585 | 67.9 | 4 | 4791 | 325146 | 3023 | 4.8914 | 12.29 | 42.18 | 54.47
SIERRA | COLUMBIA HILL 1101 | 152471101 | 2020 | 118.2 | 1.2 | 98.5 | 11 | 1387 | 136640 | 1156 | 90.3378 | 89.96 | 5.56 | 95.52
SIERRA | DEL MAR 2109 | 152582109 | 2020 | 27.7 | 1.009 | 27.5 | 4 | 3735 | 102583 | 3700 | 2.3059 | 7.02 | 59.64 | 66.66
SIERRA | DIAMOND SPRINGS 1103 | 152261103 | 2020 | 27.7 | 0.279 | 99.3 | 11 | 625 | 62048 | 2240 | 33.9382 | 51.04 | 6.36 | 57.4
SIERRA | DIAMOND SPRINGS 1104 | 152261104 | 2020 | 31.6 | 0.283 | 111.4 | 5 | 288 | 32087 | 1017 | 13.0093 | 18.1 | 4.35 | 22.45
SIERRA | DIAMOND SPRINGS 1106 | 152261106 | 2020 | 23.6 | 0.304 | 77.7 | 11 | 989 | 76804 | 3258 | 112.4156 | 121.96 | 9.64 | 131.6
SIERRA | DIAMOND SPRINGS 1107 | 152261107 | 2020 | 1.7 | 0.023 | 74.3 | 3 | 43 | 3194 | 1852 | 52.7256 | 58.87 | 14.03 | 72.9
SIERRA | DRUM 1101 | 152321101 | 2020 | 228.4 | 1.09 | 209.5 | 3 | 217 | 45455 | 199 | 18.3664 | 17.45 | 0.57 | 18.02
SIERRA | ECHO SUMMIT 1101 | 158031101 | 2020 | 82.1 | 2.512 | 32.7 | 3 | 1015 | 33158 | 404 | 6.1933 | 14.83 | 4.13 | 18.95
SIERRA | EL DORADO PH 2101 | 152762101 | 2020 | 2123.3 | 4.56 | 465.7 | 43 | 21207 | 9875399 | 4651 | 157.0822 | 165.95 | 2.18 | 168.13
SIERRA | EL DORADO PH 2102 | 152762102 | 2020 | 459.4 | 5.764 | 79.7 | 19 | 9488 | 756161 | 1646 | 34.3533 | 34.05 | 1.99 | 36.04
SIERRA | FLINT 1101 | 152531101 | 2020 | 6.5 | 0.093 | 70 | 1 | 191 | 13370 | 2054 | 6.5636 | 18.32 | 14.37 | 32.69
SIERRA | FORESTHILL 1101 | 152181101 | 2020 | 104 | 0.618 | 168.4 | 23 | 1396 | 235129 | 2260 | 64.9629 | 64.71 | 12.63 | 77.34
SIERRA | FORESTHILL 1102 | 152181102 | 2020 | 15.1 | 1.03 | 14.7 | 3 | 440 | 6453 | 427 | 29.5264 | 29.5 | 4.97 | 34.47
SIERRA | GRASS VALLEY 1101 | 152031101 | 2020 | 48.5 | 0.128 | 378.1 | 2 | 100 | 37805 | 779 | 16.3006 | 18.8 | 5.26 | 24.06
SIERRA | GRASS VALLEY 1102 | 152031102 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1469 | 0.081891 | 5.79 | 3.11 | 8.91
SIERRA | GRASS VALLEY 1103 | 152031103 | 2020 | 314.4 | 2.195 | 143.3 | 9 | 3248 | 465322 | 1480 | 86.981 | 87.61 | 5.74 | 93.36
SIERRA | HALSEY 1101 | 152241101 | 2020 | 72.7 | 0.514 | 141.4 | 18 | 1192 | 168556 | 2319 | 68.5093 | 68.56 | 15.34 | 83.91
SIERRA | HALSEY 1102 | 152241102 | 2020 | 813 | 2.084 | 390.1 | 20 | 4395 | 1714669 | 2109 | 59.4061 | 67.85 | 5.07 | 72.92
SIERRA | HIGGINS 1103 | 152691103 | 2020 | 488.2 | 3.098 | 157.6 | 16 | 6116 | 963631 | 1974 | 75.7902 | 79.5 | 3.68 | 83.19
SIERRA | HIGGINS 1104 | 152691104 | 2020 | 71.9 | 0.247 | 290.7 | 11 | 674 | 195928 | 2726 | 72.6268 | 84.15 | 0.85 | 85
SIERRA | HIGGINS 1107 | 152691107 | 2020 | 63.5 | 0.236 | 269.3 | 6 | 402 | 108275 | 1705 | 18.9261 | 32.51 | 4.03 | 36.54
SIERRA | HIGGINS 1109 | 152691109 | 2020 | 198.1 | 0.822 | 240.9 | 21 | 1375 | 331291 | 1672 | 140.9289 | 141.18 | 5.05 | 146.22
SIERRA | HIGGINS 1110 | 152691110 | 2020 | 191.3 | 0.747 | 256 | 9 | 1028 | 263199 | 1376 | 49.6826 | 57.36 | 6.34 | 63.7
SIERRA | HORSESHOE 1101 | 152571101 | 2020 | 51.6 | 1.184 | 43.6 | 9 | 1596 | 69520 | 1348 | 5.4877 | 36.28 | 14.02 | 50.3
SIERRA | HORSESHOE 1104 | 152571104 | 2020 | 0 | 0.002 | 12 | 1 | 3 | 36 | 1285 | 2.2351 | 11.65 | 11.21 | 22.86
SIERRA | LINCOLN 1101 | 153701101 | 2020 | 61.1 | 0.531 | 115 | 20 | 1343 | 154411 | 2527 | 19.1409 | 52.39 | 12.87 | 65.26
SIERRA | LINCOLN 1104 | 153701104 | 2020 | 112.4 | 0.742 | 151.6 | 35 | 964 | 146128 | 1300 | 37.1604 | 136.47 | 2.39 | 138.86
SIERRA | MOUNTAIN QUARRIES 2101 | 152282101 | 2020 | 162.9 | 1.274 | 127.8 | 30 | 4701 | 600978 | 3689 | 224.3149 | 224.13 | 12.74 | 236.87
SIERRA | NARROWS 2101 | 153132101 | 2020 | 1.4 | 0.008 | 187 | 1 | 4 | 748 | 532 | 61.341 | 61.39 | 1.26 | 62.65
SIERRA | NARROWS 2102 | 153132102 | 2020 | 103.9 | 1.437 | 72.3 | 10 | 4936 | 356842 | 3434 | 94.2903 | 117.76 | 4.94 | 122.7
SIERRA | NARROWS 2105 | 153132105 | 2020 | 297.3 | 1.585 | 187.6 | 32 | 6357 | 1192311 | 4010 | 179.1012 | 196.71 | 5.33 | 202.04
SIERRA | PENRYN 1103 | 152561103 | 2020 | 19.4 | 0.14 | 139.1 | 8 | 210 | 29212 | 1502 | 67.3893 | 79 | 5.24 | 84.24
SIERRA | PENRYN 1105 | 152561105 | 2020 | 109.6 | 0.832 | 131.8 | 19 | 1599 | 210798 | 1923 | 38.5494 | 92.2 | 2.86 | 95.06
SIERRA | PENRYN 1106 | 152561106 | 2020 | 45.4 | 0.353 | 128.4 | 13 | 772 | 99132 | 2185 | 1.0001 | 26.05 | 10.41 | 36.46
SIERRA | PENRYN 1107 | 152561107 | 2020 | 113.7 | 0.477 | 238.4 | 30 | 1349 | 321585 | 2828 | 40.7899 | 84.22 | 17.92 | 102.14
SIERRA | PIKE CITY 1101 | 152201101 | 2020 | 85.3 | 0.235 | 363.2 | 8 | 97 | 35235 | 413 | 34.0318 | 34.05 | 1.22 | 35.27
SIERRA | PIKE CITY 1102 | 152201102 | 2020 | 2546 | 1 | 2546 | 1 | 27 | 68742 | 27 | 9.5189 | 9.52 | 0 | 9.52
SIERRA | PLACER 1101 | 152461101 | 2020 | 35.7 | 0.143 | 250.3 | 2 | 159 | 39795 | 1114 | 1.3278 | 7.7 | 3.45 | 11.15
SIERRA | PLACER 1102 | 152461102 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 2.0893 | 2.15 | 0.01 | 2.17
SIERRA | PLACER 1103 | 152461103 | 2020 | 48.5 | 0.135 | 359.6 | 9 | 275 | 98896 | 2041 | 14.1287 | 29.51 | 9.75 | 39.26
SIERRA | PLACER 1104 | 152461104 | 2020 | 5.6 | 0.064 | 87.7 | 2 | 133 | 11659 | 2077 | 0.67967 | 13.37 | 9.47 | 22.85
SIERRA | PLACERVILLE 1109 | 153081109 | 2020 | 39.2 | 0.42 | 93.3 | 3 | 252 | 23517 | 600 | 10.8452 | 11.09 | 2.2 | 13.29
SIERRA | PLACERVILLE 1110 | 153081110 | 2020 | 264.6 | 3.447 | 76.7 | 7 | 5488 | 421185 | 1592 | 33.6078 | 34.36 | 4.95 | 39.32
SIERRA | PLACERVILLE 1111 | 153081111 | 2020 | 53.1 | 0.632 | 84.1 | 4 | 708 | 59562 | 1121 | 15.694 | 18.72 | 4.3 | 23.01
SIERRA | PLACERVILLE 1112 | 153081112 | 2020 | 16.2 | 0.087 | 185.4 | 3 | 184 | 34114 | 2111 | 27.9822 | 29.74 | 7.26 | 37.01
SIERRA | PLACERVILLE 2106 | 153082106 | 2020 | 320.2 | 2.243 | 142.7 | 61 | 11821 | 1687083 | 5269 | 275.756 | 273.87 | 12.55 | 286.42
SIERRA | SHADY GLEN 1101 | 152431101 | 2020 | 82 | 0.877 | 93.4 | 8 | 1683 | 157197 | 1918 | 40.7737 | 46.05 | 4.99 | 51.04
SIERRA | SHADY GLEN 1102 | 152431102 | 2020 | 149.2 | 0.624 | 239 | 12 | 470 | 112328 | 753 | 40.5151 | 41.36 | 4.3 | 45.67
SIERRA | SHINGLE SPRINGS 1103 | 153651103 | 2020 | 6.6 | 0.103 | 63.8 | 3 | 118 | 7527 | 1146 | 8.4748 | 13.72 | 10.1 | 23.82
SIERRA | SHINGLE SPRINGS 1104 | 153651104 | 2020 | 267.6 | 1.094 | 244.5 | 7 | 1485 | 363074 | 1357 | 45.672 | 60.04 | 1.54 | 61.58
SIERRA | SHINGLE SPRINGS 2105 | 153652105 | 2020 | 12.7 | 0.089 | 142.2 | 6 | 358 | 50908 | 4012 | 30.7153 | 32.93 | 28.62 | 61.55
SIERRA | SHINGLE SPRINGS 2108 | 153652108 | 2020 | 175.9 | 1.264 | 139.1 | 4 | 3649 | 507638 | 2886 | 16.8163 | 28 | 12.26 | 40.26
SIERRA | SHINGLE SPRINGS 2109 | 153652109 | 2020 | 183 | 1.855 | 98.6 | 54 | 6685 | 659305 | 3603 | 214.6231 | 213.22 | 7.91 | 221.13
SIERRA | SHINGLE SPRINGS 2110 | 153652110 | 2020 | 87.4 | 0.578 | 151.2 | 13 | 744 | 112524 | 1288 | 63.6448 | 65.16 | 4.7 | 69.86
SIERRA | SMARTVILLE 1101 | 153791101 | 2020 | 14.5 | 0.906 | 16 | 1 | 242 | 3872 | 267 | 16.1753 | 15.92 | 1.36 | 17.29
SIERRA | SPAULDING 1101 | 152251101 | 2020 | 840.5 | 0.53 | 1586.5 | 5 | 89 | 141201 | 168 | 20.6758 | 24.06 | 1.74 | 25.81
SIERRA | SUMMIT 1101 | 152591101 | 2020 | 10.8 | 0.02 | 551.6 | 2 | 21 | 11583 | 1069 | 9.0309 | 15.17 | 7.32 | 22.49
SIERRA | SUMMIT 1102 | 152591102 | 2020 | 29.3 | 0.442 | 66.2 | 2 | 130 | 8609 | 294 | 5.0372 | 5.02 | 8.27 | 13.3
SIERRA | TAMARACK 1101 | 152291101 | 2020 | 14 | 0.016 | 889 | 1 | 7 | 6223 | 444 | 17.479 | 19.51 | 0.32 | 19.83
SIERRA | WEIMAR 1101 | 152491101 | 2020 | 79 | 1.57 | 50.3 | 8 | 2592 | 130435 | 1651 | 74.4229 | 74.46 | 3.74 | 78.2
SIERRA | WEIMAR 1102 | 152491102 | 2020 | 94.1 | 0.739 | 127.4 | 5 | 472 | 60137 | 639 | 28.3002 | 28.27 | 1.07 | 29.33
SIERRA | WHEATLAND 1105 | 152811105 | 2020 | 83.7 | 0.697 | 120.1 | 8 | 457 | 54894 | 656 | 11.0172 | 74.63 | 1.66 | 76.29
SIERRA | WISE 1101 | 152271101 | 2020 | 5.9 | 0.043 | 139.6 | 2 | 42 | 5862 | 986 | 6.8707 | 13.46 | 10.48 | 23.94
SIERRA | WISE 1102 | 152271102 | 2020 | 128.3 | 1.37 | 93.7 | 25 | 2390 | 223896 | 1745 | 115.0587 | 119.59 | 6.94 | 126.53
SONOMA | ANNAPOLIS 1101 | 42861101 | 2020 | 62.3 | 0.197 | 315.6 | 5 | 45 | 14203 | 228 | 51.116 | 51.08 | 1.33 | 52.41
SONOMA | BASALT 1106 | 42461106 | 2020 | 232.7 | 2.248 | 103.5 | 28 | 7613 | 788040 | 3387 | 2.5995 | 70.24 | 14.84 | 85.08
SONOMA | BELLEVUE 1102 | 43181102 | 2020 | 31.5 | 1.081 | 29.2 | 11 | 1704 | 49720 | 1577 | 0.25165 | 43.55 | 7.08 | 50.62
SONOMA | BELLEVUE 2103 | 43182103 | 2020 | 51.3 | 0.595 | 86.2 | 18 | 4216 | 363435 | 7085 | 30.0137 | 69.78 | 50.32 | 120.09
SONOMA | CALISTOGA 1101 | 42711101 | 2020 | 335.5 | 3.803 | 88.2 | 38 | 6218 | 548620 | 1635 | 98.7432 | 113.19 | 10.54 | 123.73
SONOMA | CALPINE 1144 | 48011144 | 2020 | 10060 | 1 | 10060 | 1 | 17 | 171020 | 17 | 30.3896 | 0 | 0.34 | 0.34
SONOMA | CALPINE 1146 | 48011146 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6.2378 | 0 | 0 | 0
SONOMA | CLOVERDALE 1101 | 42821101 | 2020 | 74 | 1.434 | 51.6 | 7 | 3781 | 195192 | 2637 | 24.9489 | 36.66 | 9.55 | 46.21
SONOMA | CLOVERDALE 1102 | 42821102 | 2020 | 14.5 | 0.186 | 78.1 | 14 | 483 | 37735 | 2600 | 81.8888 | 107.39 | 15.94 | 123.33
SONOMA | CORONA 1103 | 43491103 | 2020 | 26.2 | 0.091 | 285.8 | 5 | 285 | 81462 | 3115 | 0.53707 | 17.43 | 20.66 | 38.09
SONOMA | COTATI 1102 | 42271102 | 2020 | 7.9 | 0.07 | 112.6 | 6 | 391 | 44037 | 5600 | 16.5039 | 34.9 | 29.63 | 64.53
SONOMA | COTATI 1103 | 42271103 | 2020 | 198.7 | 1.381 | 143.9 | 26 | 2019 | 290514 | 1462 | 86.1092 | 110.68 | 8.07 | 118.75
SONOMA | COTATI 1104 | 42271104 | 2020 | 20.2 | 0.486 | 41.6 | 8 | 642 | 26685 | 1321 | 9.8726 | 16.51 | 2.91 | 19.42
SONOMA | COTATI 1105 | 42271105 | 2020 | 197.3 | 1.248 | 158.1 | 19 | 3853 | 609049 | 3087 | 45.6729 | 130.65 | 7.39 | 138.04
SONOMA | DUNBAR 1101 | 43071101 | 2020 | 113.8 | 2.871 | 39.7 | 39 | 9513 | 377289 | 3314 | 41.69 | 64.33 | 24.52 | 88.86
SONOMA | DUNBAR 1102 | 43071102 | 2020 | 155.4 | 0.74 | 210.2 | 15 | 1295 | 272161 | 1751 | 50.6554 | 58.14 | 7.41 | 65.54
SONOMA | DUNBAR 1103 | 43071103 | 2020 | 72.8 | 0.917 | 79.5 | 10 | 2197 | 174594 | 2397 | 30.7428 | 53.36 | 9.63 | 62.99
SONOMA | FITCH MOUNTAIN 1111 | 42751111 | 2020 | 142.5 | 1.188 | 120 | 3 | 740 | 88801 | 623 | 0.6398 | 30.62 | 1.34 | 31.97
SONOMA | FITCH MOUNTAIN 1113 | 42751113 | 2020 | 490.6 | 2.228 | 220.2 | 61 | 5304 | 1168094 | 2381 | 77.9125 | 149.16 | 12.69 | 161.85
SONOMA | FORT ROSS 1121 | 42851121 | 2020 | 332.6 | 2.129 | 156.2 | 11 | 1369 | 213886 | 643 | 93.1541 | 93.09 | 3.72 | 96.81
SONOMA | FULTON 1102 | 42561102 | 2020 | 82.6 | 0.602 | 137.2 | 17 | 1485 | 203715 | 2466 | 31.0803 | 61.3 | 45.63 | 106.92
SONOMA | FULTON 1104 | 42561104 | 2020 | 39 | 0.339 | 115 | 2 | 984 | 113160 | 2902 | 0.38717 | 8.45 | 24.29 | 32.75
SONOMA | FULTON 1107 | 42561107 | 2020 | 56.9 | 1.093 | 52 | 11 | 3464 | 180112 | 3168 | 36.468 | 48.99 | 25.56 | 74.55
SONOMA | GEYSERVILLE 1101 | 42891101 | 2020 | 25.9 | 0.447 | 58 | 23 | 669 | 38771 | 1495 | 77.004 | 138.63 | 8.9 | 147.53
SONOMA | GEYSERVILLE 1102 | 42891102 | 2020 | 71.2 | 0.769 | 92.6 | 16 | 944 | 87441 | 1228 | 58.8661 | 116.69 | 9.34 | 126.03
SONOMA | IGNACIO 1104 | 42481104 | 2020 | 117.7 | 0.921 | 127.9 | 9 | 1475 | 188617 | 1602 | 7.0818 | 55.16 | 10.37 | 65.53
SONOMA | LAKEVILLE 1102 | 43371102 | 2020 | 36.6 | 0.209 | 175 | 13 | 286 | 50056 | 1366 | 20.9398 | 50.35 | 13.31 | 63.66
SONOMA | MIRABEL 1101 | 42091101 | 2020 | 141.7 | 0.955 | 148.4 | 21 | 1484 | 220212 | 1554 | 29.5969 | 51.14 | 3.07 | 54.21
SONOMA | MIRABEL 1102 | 42091102 | 2020 | 115 | 0.453 | 253.8 | 19 | 1099 | 278943 | 2426 | 37.5925 | 57.63 | 3.51 | 61.14
SONOMA | MOLINO 1101 | 42571101 | 2020 | 117 | 0.514 | 227.7 | 17 | 2643 | 601851 | 5144 | 35.0851 | 90.06 | 14.01 | 104.07
SONOMA | MOLINO 1102 | 42571102 | 2020 | 205.5 | 1.401 | 146.7 | 38 | 5721 | 839383 | 4084 | 113.2452 | 161.2 | 17.03 | 178.22
SONOMA | MOLINO 1104 | 42571104 | 2020 | 146.9 | 0.669 | 219.5 | 14 | 2831 | 621370 | 4231 | 2.7874 | 61.19 | 9.99 | 71.18
SONOMA | MONROE 2103 | 43302103 | 2020 | 0.6 | 0.012 | 49.5 | 2 | 49 | 2424 | 4215 | 0.5711 | 11.49 | 48.69 | 60.19
SONOMA | MONROE 2107 | 43302107 | 2020 | 15.4 | 0.387 | 39.7 | 8 | 1038 | 41225 | 2683 | 0.65446 | 10.34 | 11.48 | 21.82
SONOMA | MONTE RIO 1111 | 42811111 | 2020 | 103.2 | 1.132 | 91.1 | 11 | 1987 | 181073 | 1755 | 59.8011 | 63.96 | 1.09 | 65.05
SONOMA | MONTE RIO 1112 | 42811112 | 2020 | 555.7 | 1.701 | 326.7 | 11 | 1963 | 641327 | 1154 | 19.7435 | 19.64 | 0.8 | 20.43
SONOMA | MONTE RIO 1113 | 42811113 | 2020 | 357.5 | 2.219 | 161.1 | 25 | 8696 | 1400660 | 3918 | 61.2942 | 61.09 | 1.49 | 62.58
SONOMA | PENNGROVE 1101 | 43471101 | 2020 | 124.3 | 1.68 | 74 | 13 | 3720 | 275152 | 2214 | 20.9549 | 41.19 | 15.22 | 56.41
SONOMA | PETALUMA C 1108 | 42631108 | 2020 | 23.8 | 0.199 | 119.4 | 25 | 1112 | 132807 | 5587 | 76.4179 | 118.81 | 13.64 | 132.44
SONOMA | PETALUMA C 1109 | 42631109 | 2020 | 27.9 | 0.232 | 120.3 | 14 | 936 | 112638 | 4038 | 50.4271 | 66.67 | 19.12 | 85.79
SONOMA | PUEBLO 2102 | 43292102 | 2020 | 56 | 0.4 | 140 | 34 | 910 | 127423 | 2276 | 23.7896 | 98.97 | 24.76 | 123.72
SONOMA | RINCON 1101 | 43321101 | 2020 | 15.4 | 0.402 | 38.3 | 35 | 1478 | 56553 | 3675 | 21.6427 | 34.91 | 26.56 | 61.47
SONOMA | RINCON 1102 | 43321102 | 2020 | 281.3 | 2.039 | 138 | 7 | 9469 | 1306515 | 4644 | 3.3303 | 19.73 | 12.91 | 32.64
SONOMA | RINCON 1103 | 43321103 | 2020 | 219.8 | 1.223 | 179.7 | 9 | 2510 | 451032 | 2052 | 44.5432 | 47.25 | 13.03 | 60.28
SONOMA | RINCON 1104 | 43321104 | 2020 | 240.2 | 2.574 | 93.3 | 7 | 10372 | 967969 | 4030 | 2.7661 | 12.07 | 23.23 | 35.3
SONOMA | SALMON CREEK 1101 | 43161101 | 2020 | 29.5 | 0.086 | 342.6 | 11 | 154 | 52762 | 1787 | 27.3051 | 47.21 | 22.36 | 69.58
SONOMA | SANTA ROSA A 1104 | 42151104 | 2020 | 104.7 | 0.161 | 650 | 3 | 555 | 360760 | 3446 | 43.2497 | 56.14 | 17.27 | 73.4
SONOMA | SANTA ROSA A 1107 | 42151107 | 2020 | 48.6 | 1.331 | 36.5 | 4 | 1734 | 63297 | 1303 | 3.0326 | 6.15 | 5.53 | 11.68
SONOMA | SANTA ROSA A 1108 | 42151108 | 2020 | 172.1 | 2.537 | 67.9 | 7 | 8803 | 597332 | 3470 | 0.13619 | 6.81 | 20.1 | 26.91
SONOMA | SANTA ROSA A 1111 | 42151111 | 2020 | 18.2 | 0.151 | 120.5 | 14 | 721 | 86887 | 4779 | 6.4451 | 26.1 | 18.59 | 44.69
SONOMA | SILVERADO 2103 | 43432103 | 2020 | 265.7 | 3.586 | 74.1 | 15 | 3453 | 255862 | 963 | 11.7521 | 32.9 | 20.74 | 53.65
SONOMA | SILVERADO 2105 | 43432105 | 2020 | 152.4 | 1.652 | 92.2 | 33 | 3815 | 351850 | 2309 | 38.0992 | 63.2 | 13.46 | 76.66
SONOMA | SONOMA 1102 | 42721102 | 2020 | 12.3 | 0.193 | 64.1 | 4 | 661 | 42347 | 3429 | 6.1264 | 18.12 | 12.23 | 30.35
SONOMA | SONOMA 1103 | 42721103 | 2020 | 24.3 | 0.059 | 413.2 | 3 | 127 | 52476 | 2163 | 12.7844 | 25.57 | 9.59 | 35.16
SONOMA | SONOMA 1104 | 42721104 | 2020 | 168.5 | 1.875 | 89.9 | 16 | 7411 | 666168 | 3953 | 21.371 | 59.4 | 17.21 | 76.61
SONOMA | SONOMA 1105 | 42721105 | 2020 | 182.3 | 1.658 | 110 | 21 | 3728 | 410019 | 2249 | 14.7491 | 62.4 | 10.69 | 73.09
SONOMA | SONOMA 1106 | 42721106 | 2020 | 11.6 | 0.133 | 87.2 | 4 | 423 | 36873 | 3174 | 1.2978 | 11.11 | 11.17 | 22.29
SONOMA | SONOMA 1107 | 42721107 | 2020 | 5 | 0.057 | 87.5 | 7 | 97 | 8486 | 1699 | 4.7423 | 51.97 | 7.13 | 59.1
SONOMA | WINDSOR 1103 | 43501103 | 2020 | 1.9 | 0.018 | 109 | 1 | 26 | 2834 | 1456 | 2.2999 | 11.24 | 13.08 | 24.33
STOCKTON | APPLE HILL 2102 | 153662102 | 2020 | 304.6 | 2.653 | 114.8 | 62 | 12007 | 1378587 | 4526 | 339.4627 | 345.62 | 5.56 | 351.18
STOCKTON | BRENTWOOD 2105 | 14592105 | 2020 | 78.3 | 1.389 | 56.3 | 18 | 3980 | 224268 | 2865 | 11.3872 | 88 | 27.45 | 115.45
STOCKTON | CALAVERAS CEMENT 1101 | 162211101 | 2020 | 237.6 | 1.73 | 137.3 | 24 | 6052 | 831197 | 3498 | 229.1052 | 243.33 | 12.23 | 255.56
STOCKTON | CLAY 1101 | 163341101 | 2020 | 267.6 | 1.724 | 155.2 | 9 | 2984 | 463262 | 1731 | 27.3571 | 40.68 | 5.7 | 46.38
STOCKTON | CLAY 1103 | 163341103 | 2020 | 93.6 | 1.077 | 86.9 | 18 | 1632 | 141890 | 1516 | 55.8533 | 112.91 | 4.37 | 117.27
STOCKTON | CORRAL 1101 | 162991101 | 2020 | 91.7 | 0.513 | 178.7 | 19 | 1077 | 192461 | 2098 | 121.9438 | 186.56 | 5.51 | 192.07
STOCKTON | CORRAL 1102 | 162991102 | 2020 | 44.2 | 0.504 | 87.7 | 7 | 1131 | 99228 | 2244 | 49.9997 | 64.17 | 13.76 | 77.93
STOCKTON | CORRAL 1103 | 162991103 | 2020 | 72.1 | 0.39 | 185 | 4 | 820 | 151709 | 2105 | 20.6001 | 79.87 | 0.19 | 80.06
STOCKTON | DIAMOND SPRINGS 1105 | 152261105 | 2020 | 18.5 | 0.146 | 126.2 | 9 | 370 | 46704 | 2526 | 127.0971 | 133.47 | 7.42 | 140.89
STOCKTON | ELECTRA 1101 | 162161101 | 2020 | 119.6 | 1.195 | 100 | 6 | 2290 | 229074 | 1916 | 81.6505 | 85.05 | 5.06 | 90.11
STOCKTON | ELECTRA 1102 | 162161102 | 2020 | 34.6 | 0.346 | 100 | 4 | 235 | 23508 | 679 | 17.062 | 19.22 | 5.92 | 25.14
STOCKTON | FROGTOWN 1701 | 163451701 | 2020 | 21.4 | 0.158 | 135.7 | 6 | 312 | 42325 | 1974 | 70.9099 | 70.52 | 9.79 | 80.3
STOCKTON | FROGTOWN 1702 | 163451702 | 2020 | 221.5 | 2.497 | 88.7 | 24 | 10442 | 926078 | 4181 | 239.0557 | 249.22 | 18.62 | 267.83
STOCKTON | IONE 1101 | 163881101 | 2020 | 174.7 | 1.052 | 166.1 | 6 | 895 | 148640 | 851 | 15.6785 | 28.78 | 12.19 | 40.97
STOCKTON | MARTELL 1101 | 163011101 | 2020 | 106.1 | 1.628 | 65.1 | 8 | 3777 | 246069 | 2320 | 71.6591 | 82.71 | 10.46 | 93.18
STOCKTON | NORTH BRANCH 1101 | 163231101 | 2020 | 187.7 | 1.149 | 163.3 | 11 | 1485 | 242497 | 1292 | 66.0316 | 90.22 | 6.03 | 96.25
STOCKTON | OLETA 1101 | 163541101 | 2020 | 156.9 | 2.164 | 72.5 | 11 | 3806 | 275906 | 1759 | 94.3393 | 116.29 | 5.53 | 121.82
STOCKTON | OLETA 1102 | 163541102 | 2020 | 109.7 | 1.93 | 56.8 | 14 | 2144 | 121882 | 1111 | 61.8115 | 98.97 | 5.34 | 104.31
STOCKTON | PINE GROVE 1102 | 163751102 | 2020 | 74.5 | 0.474 | 157.2 | 20 | 2090 | 328519 | 4408 | 176.7598 | 175.84 | 13.39 | 189.23
STOCKTON | SALT SPRINGS 2101 | 163692101 | 2020 | 557.9 | 0.947 | 589.4 | 4 | 372 | 219273 | 393 | 18.4395 | 21.93 | 22.57 | 44.5
STOCKTON | SALT SPRINGS 2102 | 163692102 | 2020 | 228.5 | 2.146 | 106.5 | 15 | 4310 | 458853 | 2008 | 52.2706 | 51.82 | 17.71 | 69.53
STOCKTON | STANISLAUS 1701 | 162821701 | 2020 | 131.4 | 0.943 | 139.4 | 7 | 1743 | 242925 | 1849 | 45.4233 | 45.29 | 14.58 | 59.88
STOCKTON | TIGER CREEK 0201 | 161380201 | 2020 | 14.4 | 0.071 | 202 | 1 | 1 | 202 | 14 | 3.7431 | 3.76 | 0 | 3.76
STOCKTON | WEST POINT 1101 | 163201101 | 2020 | 114.5 | 1.345 | 85.1 | 11 | 2398 | 204159 | 1783 | 63.2893 | 62.99 | 5.44 | 68.43
STOCKTON | WEST POINT 1102 | 163201102 | 2020 | 284.8 | 2.698 | 105.5 | 20 | 8087 | 853470 | 2997 | 255.2716 | 253.33 | 2.56 | 255.89
YOSEMITE | BEAR VALLEY 2101 | 252192101 | 2020 | 231.3 | 1.453 | 159.1 | 12 | 1811 | 288207 | 1246 | 105.0571 | 166.62 | 0.47 | 167.09
YOSEMITE | BEAR VALLEY 2105 | 252192105 | 2020 | 255.2 | 2.146 | 118.9 | 11 | 2753 | 327364 | 1283 | 133.3677 | 130.96 | 1.79 | 132.74
YOSEMITE | CLAY 1102 | 163341102 | 2020 | 280.5 | 1.5 | 187 | 2 | 3 | 561 | 2 | 0.92759 | 2.1 | 0.02 | 2.12
YOSEMITE | COARSEGOLD 2102 | 254432102 | 2020 | 162.3 | 1.457 | 111.4 | 7 | 1946 | 216799 | 1336 | 69.9267 | 68.94 | 2.27 | 71.2
YOSEMITE | COARSEGOLD 2103 | 254432103 | 2020 | 83 | 0.382 | 217 | 10 | 777 | 168571 | 2032 | 94.4668 | 123.2 | 0.8 | 124
YOSEMITE | COARSEGOLD 2104 | 254432104 | 2020 | 93.2 | 0.585 | 159.4 | 18 | 2554 | 406995 | 4367 | 248.9768 | 266.53 | 3.18 | 269.71
YOSEMITE | CURTIS 1701 | 163351701 | 2020 | 31.8 | 0.341 | 93.2 | 4 | 634 | 59086 | 1858 | 13.7227 | 20.67 | 8.41 | 29.08
YOSEMITE | CURTIS 1702 | 163351702 | 2020 | 60.6 | 0.387 | 156.7 | 21 | 1718 | 269216 | 4445 | 111.5452 | 116.99 | 6.98 | 123.97
YOSEMITE | CURTIS 1703 | 163351703 | 2020 | 549.9 | 3.51 | 156.7 | 36 | 13556 | 2123894 | 3862 | 197.8801 | 198.94 | 7.71 | 206.66
YOSEMITE | CURTIS 1704 | 163351704 | 2020 | 140.5 | 0.959 | 146.5 | 18 | 2504 | 366859 | 2612 | 76.0693 | 75.8 | 14.25 | 90.05
YOSEMITE | CURTIS 1705 | 163351705 | 2020 | 211.8 | 1.483 | 142.8 | 17 | 4212 | 601416 | 2840 | 85.9556 | 88.38 | 8.36 | 96.74
YOSEMITE | HOLLISTER 2102 | 182492102 | 2020 | 180.9 | 2.487 | 72.8 | 21 | 1838 | 133716 | 739 | 30.5351 | 108.53 | 2.68 | 111.2
YOSEMITE | INDIAN FLAT 1104 | 252691104 | 2020 | 0.4 | 0.005 | 85 | 1 | 3 | 255 | 616 | 16.8139 | 16.75 | 16.69 | 33.45
YOSEMITE | KERCKHOFF 1101 | 252561101 | 2020 | 134.4 | 0.158 | 853.4 | 2 | 43 | 36697 | 273 | 34.6841 | 34.12 | 0.1 | 34.21
YOSEMITE | MARIPOSA 2101 | 254452101 | 2020 | 306 | 0.978 | 312.7 | 22 | 3723 | 1164239 | 3805 | 261.901 | 265.3 | 2.16 | 267.47
YOSEMITE | MARIPOSA 2102 | 254452102 | 2020 | 347.6 | 3.14 | 110.7 | 22 | 10433 | 1154919 | 3323 | 250.4446 | 258.81 | 3.96 | 262.77
YOSEMITE | MARTELL 1102 | 163011102 | 2020 | 213.8 | 3.348 | 63.9 | 7 | 4202 | 268358 | 1255 | 7.6361 | 12.13 | 4.68 | 16.8
YOSEMITE | MARTELL 1103 | 163011103 | 2020 | 7.2 | 0.031 | 230.2 | 3 | 37 | 8519 | 1190 | 21.2373 | 29.31 | 6.91 | 36.22
YOSEMITE | MERCED FALLS 1102 | 252811102 | 2020 | 365.5 | 2.191 | 166.8 | 21 | 4731 | 789184 | 2159 | 121.3257 | 186.57 | 1.62 | 188.2
YOSEMITE | MIWUK 1701 | 163661701 | 2020 | 167.2 | 1.738 | 96.2 | 21 | 6472 | 622726 | 3724 | 77.9941 | 75.98 | 7.49 | 83.47
YOSEMITE | MIWUK 1702 | 163661702 | 2020 | 158.9 | 2.805 | 56.6 | 18 | 10766 | 609824 | 3838 | 76.2721 | 74.8 | 5.25 | 80.05
YOSEMITE | OAKHURST 1101 | 254421101 | 2020 | 201 | 2.643 | 76.1 | 7 | 5457 | 415166 | 2065 | 91.9072 | 93 | 14.97 | 107.97
YOSEMITE | OAKHURST 1102 | 254421102 | 2020 | 66.3 | 1.087 | 61 | 5 | 1201 | 73266 | 1105 | 13.0374 | 16.57 | 3.69 | 20.25
YOSEMITE | OAKHURST 1103 | 254421103 | 2020 | 72.8 | 1.606 | 45.3 | 13 | 6373 | 288678 | 3968 | 127.7336 | 129.44 | 17.56 | 147.01
YOSEMITE | PANOCHE 1103 | 253671103 | 2020 | 99.3 | 0.794 | 125 | 3 | 270 | 33754 | 340 | 47.6674 | 121.22 | 5.65 | 126.87
YOSEMITE | PEORIA 1701 | 163781701 | 2020 | 664.8 | 4.451 | 149.4 | 15 | 8524 | 1273176 | 1915 | 78.6264 | 84.05 | 2.96 | 87.01
YOSEMITE | PEORIA 1704 | 163781704 | 2020 | 23.9 | 0.254 | 94.1 | 9 | 829 | 78000 | 3263 | 64.5238 | 117.53 | 32.4 | 149.94
YOSEMITE | PEORIA 1705 | 163781705 | 2020 | 59.9 | 0.568 | 105.5 | 16 | 1445 | 152464 | 2545 | 60.9338 | 71.98 | 6.88 | 78.86
YOSEMITE | PINE GROVE 1101 | 163751101 | 2020 | 262.1 | 1.879 | 139.5 | 13 | 2586 | 360648 | 1376 | 72.2128 | 72 | 3.95 | 75.95
YOSEMITE | PINECREST 0401 | 163160401 | 2020 | 1562.4 | 2.643 | 591.2 | 4 | 555 | 328095 | 210 | 3.0856 | 3.12 | 0 | 3.12
YOSEMITE | RACETRACK 1703 | 163761703 | 2020 | 64.1 | 0.918 | 69.9 | 16 | 3225 | 225375 | 3514 | 56.7171 | 61.49 | 13.2 | 74.7
YOSEMITE | RACETRACK 1704 | 163761704 | 2020 | 74 | 0.942 | 78.6 | 11 | 649 | 50996 | 689 | 46.4395 | 45.44 | 1.33 | 46.77
YOSEMITE | SAN JOAQUIN #2 1103 | 252521103 | 2020 | 28 | 0.397 | 70.3 | 9 | 418 | 29404 | 1052 | 82.9351 | 82.91 | 0.74 | 83.64
YOSEMITE | SAN JOAQUIN #3 1101 | 252531101 | 2020 | 688.4 | 2.917 | 236 | 7 | 2045 | 482547 | 701 | 24.5762 | 24.34 | 1.76 | 26.1
YOSEMITE | SAN JOAQUIN #3 1102 | 252531102 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 11.5179 | 11.42 | 0.03 | 11.45
YOSEMITE | SAN JOAQUIN #3 1103 | 252531103 | 2020 | 87.9 | 1.759 | 50 | 4 | 1594 | 79658 | 906 | 54.623 | 53.3 | 1.71 | 55.01
YOSEMITE | SO. CAL. EDISON #3 1101 | 258861101 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8.5384 | 6.46 | 0 | 6.46
YOSEMITE | SPRING GAP 1702 | 162831702 | 2020 | 1922.1 | 2.185 | 879.8 | 16 | 3266 | 2873492 | 1495 | 41.2095 | 43.68 | 3.77 | 47.45
YOSEMITE | STANISLAUS 1702 | 162821702 | 2020 | 327.4 | 2.384 | 137.4 | 32 | 11853 | 1628075 | 4972 | 85.4469 | 84.8 | 10.88 | 95.68
YOSEMITE | SWIFT 2110 | 83392110 | 2020 | 321 | 0.858 | 374.2 | 20 | 1936 | 724390 | 2257 | 83.3153 | 80.05 | 22.49 | 102.54
YOSEMITE | TAR FLAT 0401 | 163240401 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 346 | 3.4952 | 3.7 | 0 | 3.7
YOSEMITE | TAR FLAT 0402 | 163240402 | 2020 | 38.1 | 1.002 | 38 | 1 | 500 | 19000 | 499 | 5.662 | 6.44 | 0 | 6.44
YOSEMITE | TRIDAM POWERHOUSE 2101 | 168152101 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.050339 | 0 | 0 | 0
YOSEMITE | WESTLEY 1103 | 162671103 | 2020 | 30.1 | 0.322 | 93.5 | 7 | 349 | 32630 | 1085 | 0.92354 | 88.88 | 3.32 | 92.2
YOSEMITE | WISHON 1101 | 251511101 | 2020 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 7.6405 | 7.63 | 0 | 7.63
YOSEMITE | WOODWARD 2108 | 255292108 | 2020 | 139.4 | 0.696 | 200.4 | 7 | 834 | 167137 | 1199 | 19.5076 | 88.54 | 21.99 | 110.52
[7 empty] | 7825 | 1533840 | 212790531 |  |  | 41135.29
[11 empty] | Mins/Mile | 5172.9435
[11 empty] | Outage/Mile | 0.19023
[11 empty] | CESO/Mile | 37.2877
62% effectiveness
[11 empty] | Reduced Cmin/mile | 3207.225
[11 empty] | Reduced Outage/mile | 0.11794
[11 empty] | Reduced CESO/mile | 23.1184

## Reliability Benefits
[5 empty] | Customers = | 5631670
62% effectiveness
Reduced Cmin/mile | 3207.225
Reduced Outage/mile | 0.11794
Reduced CESO/mile | 23.1184 | [5 empty] | Running Total | Running Total
[5 empty] | Reduced | Reduced | Reduction | Reduction
Year | Miles 08W | Reduced Cmin | Reduced Outages | Reduced CESO | SAIDI | SAIFI | SAIDI | SAIFI
2021 | 180 | 577300.4945 | 21.2 | 4161.3064 | 0.10251 | 0.00073891 | 0 | 0
2022 | 470 | 1507395.7357 | 55.4 | 10865.6333 | 0.26766 | 0.0019294 | 0.10251 | 0.00073891
2023 | 470 | 1507395.7357 | 55.4 | 10865.6333 | 0.26766 | 0.0019294 | 0.37017 | 0.0026683
2024 | 450 | 1443251.2363 | 53.1 | 10403.2659 | 0.25627 | 0.0018473 | 0.63784 | 0.0045977
2025 | 450 | 1443251.2363 | 53.1 | 10403.2659 | 0.25627 | 0.0018473 | 0.89411 | 0.006445
2026 | 450 | 1443251.2363 | 53.1 | 10403.2659 | 0.25627 | 0.0018473 | 1.1504 | 0.0082922
2027 | [6 empty] | 1.4067 | 0.01014
Notes:
1. No benefits realized in the year of execution due to the impact of the involved planned outages
2. Reliability benefits are accumulative over the time period