{"text_format":"1","workbook":"xlsx","n_sheets":4,"sheets":["Spans","Poles","Trees","FEA Tables"],"not_rendered":{"charts":0,"images":0,"macros":1,"external_links":0,"defined_names":48,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Spans","index":0,"n_rows":53,"n_cols":44,"rows_kept":53,"cut":false,"hidden":false,"merged":[[2,7,2,8],[0,6,0,7],[0,18,0,24]]}
["File:",{"$f":"Poles!J3","v":0},null,null,null,null,{"$f":"Poles!I3","v":0},null,{"$f":"Trees!N3","v":"00:00:00"},null,null,null,null,null,null,null,null,"User Inputs","Formula",null,null,null,null,null,null,null,"Long 1","Lat 1","Elev 1",null,"Long 2","Lat 2","Elev 2",null,"Elev 1","Elev 2","Pole1 Height","Pole2 Height"]
["Threat Level","# Spans","(miles)","Weight Factor","Risk Score","Tree≤6ft",null,"Table Group:",0,"objectid","latitude","longitude","HFTD","bst_tag","ast_tag","span_tag","span_lgth","Span Shape","Span ID","Cond. Size","Wind Factor","No. Fail Trees","Threat Level","Tree≤6ft Count","≤6ft Level",null,"(°)","(°)","(m)",null,"(°)","(°)","(m)",null,"(ft)","(ft)","(ft)","(ft)",null,"\"ft\" to \"m\":",0.30480000000000002,null,"\"ft\" to \"mile\":",{"$f":"1/5280","v":1.8939393939393939E-4}]
[3,{"$f":"COUNTIFS(W$3:W$100000,A3)","v":0},{"$f":"SUMIF(W$3:W$100000,A3,Q$3:Q$100000)/5280","v":0},1,{"$f":"B3/B$7*D3","v":0},{"$f":"COUNTIFS(Y$3:Y$100000,A3)","v":0},null,"Span Shape",null,null,null,null,null,null,null,null,null,2,{"$f":"J3","v":0},0,{"$f":"Chk_wind($C$8,AA3,AB3,AE3,AF3)","v":1},{"$f":"COUNTIFS(TreeRange,S3,TreeFail,\"Yes\")*U3","v":0},{"$f":"IF(Q3<1,0,_xlfn.IFS(V3>15,3,V3>5,2,V3>0,1,V3=0,0))","v":0},{"$f":"COUNTIFS(TreeRange,S3,TreeOffset,\"Yes\")","v":0},{"$f":"IF(Q3<1,0,_xlfn.IFS(X3>15,3,X3>5,2,X3>0,1,X3=0,0))","v":0},null,{"$f":"IFERROR(VLOOKUP($N3,PoleRange,3,FALSE),0)","v":0},{"$f":"IFERROR(VLOOKUP($N3,PoleRange,2,FALSE),0)","v":0},{"$f":"(AI3+AK3-1)*0.3048","v":-0.30480000000000002},null,{"$f":"IFERROR(VLOOKUP($O3,PoleRange,3,FALSE),0)","v":0},{"$f":"IFERROR(VLOOKUP($O3,PoleRange,2,FALSE),0)","v":0},{"$f":"(AJ3+AL3-1)*0.3048","v":-0.30480000000000002},null,{"$f":"IFERROR(VLOOKUP($N3,PoleRange,6,FALSE),0)","v":0},{"$f":"IFERROR(VLOOKUP($O3,PoleRange,6,FALSE),0)","v":0},{"$f":"IFERROR(VLOOKUP($N3,PoleRange,7,FALSE),0)","v":0},{"$f":"IFERROR(VLOOKUP($O3,PoleRange,7,FALSE),0)","v":0}]
[2,{"$f":"COUNTIFS(W$3:W$100000,A4)","v":0},{"$f":"SUMIF(W$3:W$100000,A4,Q$3:Q$100000)/5280","v":0},0.75,{"$f":"B4/B$7*D4","v":0},{"$f":"COUNTIFS(Y$3:Y$100000,A4)","v":0},null,2,"Tangent"]
[1,{"$f":"COUNTIFS(W$3:W$100000,A5)","v":0},{"$f":"SUMIF(W$3:W$100000,A5,Q$3:Q$100000)/5280","v":0},0.5,{"$f":"B5/B$7*D5","v":0},{"$f":"COUNTIFS(Y$3:Y$100000,A5)","v":0},null,3,"45° Turn"]
[0,{"$f":"COUNTIFS(W$3:W$100000,A6)","v":1},{"$f":"SUMIF(W$3:W$100000,A6,Q$3:Q$100000)/5280","v":0},0,{"$f":"B6/B$7*D6","v":0},{"$f":"COUNTIFS(Y$3:Y$100000,A6)","v":1},null,4,"90° Turn"]
["Total:",{"$f":"SUM(B3:B6)","v":1},{"$f":"SUM(C3:C6)","v":0},null,{"$f":"SUM(E3:E6)","v":0},null,null,5,"T-Tap"]
[null,"Dominant Wind Dir:",-1,"deg (-1 = Ignore wind effect)",null,null,null,6,"X-Tap"]
[null,"KML Elevation:",-1,"(-1 = Use GL, # = Add to LiDAR)"]
[null,"Pole Height Adj:",0,"ft (to raise allowable)"]
[null,"Tier 2-3 Only?",1,"(1=Yes, 0=No)"]
["FEA Tables:"]
[0,"Zero Allowable"]
[1,{"$f":"'FEA Tables'!C2","v":"Composite, #2 Cu XLPE, Douglas Fir"}]
[2,{"$f":"'FEA Tables'!C16","v":"Composite, #2 Cu XLPE, Pine"}]
[3,{"$f":"'FEA Tables'!C30","v":"Composite, #2 Cu XLPE, Oak"}]
[4,{"$f":"'FEA Tables'!C44","v":"Composite, #2 Cu XLPE, Blue Gum / Eucalyptus"}]
[5,{"$f":"'FEA Tables'!C58","v":"Composite, 1/0 ACSR XLPE, Douglas Fir"}]
[6,{"$f":"'FEA Tables'!C72","v":"Composite, 1/0 ACSR XLPE, Pine"}]
[7,{"$f":"'FEA Tables'!C86","v":"Composite, 1/0 ACSR XLPE, Oak"}]
[8,{"$f":"'FEA Tables'!C100","v":"Composite, 1/0 ACSR XLPE, Blue Gum / Eucalyptus"}]
[9,{"$f":"'FEA Tables'!C114","v":"Composite, 397.5 AAC XLPE, Douglas Fir"}]
[10,{"$f":"'FEA Tables'!C128","v":"Composite, 397.5 AAC XLPE, Pine"}]
[11,{"$f":"'FEA Tables'!C142","v":"Composite, 397.5 AAC XLPE, Oak"}]
[12,{"$f":"'FEA Tables'!C156","v":"Composite, 397.5 AAC XLPE, Blue Gum / Eucalyptus"}]
[13,{"$f":"'FEA Tables'!C170","v":"Composite, 715.5 AAC XLPE, Douglas Fir"}]
[14,{"$f":"'FEA Tables'!C184","v":"Composite, 715.5 AAC XLPE, Pine"}]
[15,{"$f":"'FEA Tables'!C198","v":"Composite, 715.5 AAC XLPE, Oak"}]
[16,{"$f":"'FEA Tables'!C212","v":"Composite, 715.5 AAC XLPE, Blue Gum / Eucalyptus"}]
[17,{"$f":"'FEA Tables'!C226","v":0}]
[18,{"$f":"'FEA Tables'!C240","v":0}]
[19,{"$f":"'FEA Tables'!C254","v":0}]
[20,{"$f":"'FEA Tables'!C268","v":0}]
[21,{"$f":"'FEA Tables'!C282","v":"Wood, #6 Cu, Douglas Fir"}]
[22,{"$f":"'FEA Tables'!C296","v":"Wood, #6 Cu, Pine"}]
[23,{"$f":"'FEA Tables'!C310","v":"Wood, #6 Cu, Oak"}]
[24,{"$f":"'FEA Tables'!C324","v":"Wood, #6 Cu, Blue Gum / Eucalyptus"}]
[25,{"$f":"'FEA Tables'!C338","v":"Wood, 4 (6/1) ACSR, Douglas Fir"}]
[26,{"$f":"'FEA Tables'!C352","v":"Wood, 4 (6/1) ACSR, Pine"}]
[27,{"$f":"'FEA Tables'!C366","v":"Wood, 4 (6/1) ACSR, Oak"}]
[28,{"$f":"'FEA Tables'!C380","v":"Wood, 4 (6/1) ACSR, Blue Gum / Eucalyptus"}]
[29,{"$f":"'FEA Tables'!C394","v":"Wood, 2 (7/1) ACSR, Douglas Fir"}]
[30,{"$f":"'FEA Tables'!C408","v":"Wood, 2 (7/1) ACSR, Pine"}]
[31,{"$f":"'FEA Tables'!C422","v":"Wood, 2 (7/1) ACSR, Oak"}]
[32,{"$f":"'FEA Tables'!C436","v":"Wood, 2 (7/1) ACSR, Blue Gum / Eucalyptus"}]
[33,{"$f":"'FEA Tables'!C450","v":0}]
[34,{"$f":"'FEA Tables'!C464","v":0}]
[35,{"$f":"'FEA Tables'!C478","v":0}]
[36,{"$f":"'FEA Tables'!C492","v":0}]
[37,{"$f":"'FEA Tables'!C506","v":0}]
[38,{"$f":"'FEA Tables'!C520","v":0}]
[39,{"$f":"'FEA Tables'!C534","v":"Wood, 715.5 AAC, Oak"}]
[40,{"$f":"'FEA Tables'!C548","v":"Wood, 715.5 AAC, Blue Gum / Eucalyptus"}]

{"sheet":"Poles","index":1,"n_rows":2,"n_cols":11,"rows_kept":2,"cut":false,"hidden":false,"merged":[]}
[]
["objectid","str_geotag","latitude","longitude","x_coordinate","y_coordinate","elevation","height","line_id","line_name","HFTD"]

{"sheet":"Trees","index":2,"n_rows":3,"n_cols":21,"rows_kept":3,"cut":false,"hidden":false,"merged":[[0,14,0,18]]}
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"VLOOKUP"]
["ObjectID","TreeID","Latitude","Longitude","Height","Offset","Dist2Wire","Top3Species","PrimarySpecies","Overstrike","SpanTag","HFTD","Fall-In","AcqDate","Span ID","Span Length","Shape","FEA Table","Allowable","Tree Fail?","Offset≤6ft?"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"VLOOKUP($K3,SpanRange,4,FALSE)","v":{"$error":"#N/A"}},{"$f":"VLOOKUP($K3,SpanRange,2,FALSE)","v":{"$error":"#N/A"}},{"$f":"VLOOKUP($K3,SpanRange,3,FALSE)","v":{"$error":"#N/A"}},{"$f":"Find_Table(Spans!$I$2,I3)","v":0},{"$f":"IF(R3=0,Spans!$C$10,VLOOKUP(P3,INDIRECT(\"Table\"&R3),Q3,TRUE))","v":0},{"$f":"IFERROR(IF((-1)*J3>S3,\"Yes\",\"No\"),\"No Match\")","v":"No"},{"$f":"IF(F3<=6,\"Yes\",\"No\")","v":"Yes"}]

{"sheet":"FEA Tables","index":3,"n_rows":559,"n_cols":34,"rows_kept":559,"cut":false,"hidden":false,"merged":[[520,2,520,6],[520,9,520,13],[534,2,534,6],[534,9,534,13],[548,2,548,6],[548,9,548,13],[478,2,478,6],[478,9,478,13],[492,2,492,6],[492,9,492,13],[506,2,506,6],[506,9,506,13],[436,2,436,6],[436,9,436,13],[450,2,450,6],[450,9,450,13],[464,2,464,6],[464,9,464,13],[394,2,394,6],[394,9,394,13],[408,2,408,6],[408,9,408,13],[422,2,422,6],[422,9,422,13],[282,2,282,6],[282,9,282,13],[296,2,296,6],[296,9,296,13],[310,2,310,6],[310,9,310,13],[324,2,324,6],[324,9,324,13],[338,2,338,6],[338,9,338,13],[352,2,352,6],[352,9,352,13],[366,2,366,6],[366,9,366,13],[380,2,380,6],[380,9,380,13],[2,9,2,13],[2,2,2,6],[16,9,16,13],[16,2,16,6],[30,9,30,13],[30,2,30,6],[44,9,44,13],[44,2,44,6],[58,9,58,13],[58,2,58,6],[72,9,72,13],[72,2,72,6],[86,9,86,13],[86,2,86,6],[100,9,100,13],[100,2,100,6],[114,9,114,13],[114,2,114,6],[128,9,128,13],[128,2,128,6],[142,9,142,13],[142,2,142,6],[156,9,156,13],[156,2,156,6],[170,9,170,13],[170,2,170,6],[184,9,184,13],[184,2,184,6],[198,9,198,13],[198,2,198,6],[254,9,254,13],[254,2,254,6],[268,9,268,13],[268,2,268,6],[212,9,212,13],[212,2,212,6],[226,9,226,13],[226,2,226,6],[240,9,240,13],[240,2,240,6]]}
[null,null,null,null,null,null,null,null,"TABLE",1,null,null,null,null,null,null,"Conductor","Breaking Strength",null,null,"Tree","Failure","Density","Tip Radius","Ixx","MOR","Static Force Breaking Branch Length (ft)"]
[null,"FEA Table:","Composite, #2 Cu XLPE, Douglas Fir",null,null,null,null,null,"Span Shape:",2,3,4,5,6,null,null,"Doc 059626","(lbf)",null,null,"Species","Mode","(lb/ft3)","(in)","(in4)","(psi)","#6 Cu","4 (6/1) ACSR","2 (7/1) ACSR","715.5 AAC","#2 HD Cu XLPE","1/0 ACSR XLPE","397.5 AAC XLPE","715.5 AAC XLPE"]
[null,"Span",3,null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)",null,null,null,null,null,null,"#6 Cu",1010,null,null,"Douglas Fir","Trunk",33,3,{"$f":"X3^4*PI()/4","v":63.617251235193308},7700,{"$f":"$Z3*$Y3/$X3/$R$3/12","v":13.472300179070089},{"$f":"$Z3*$Y3/$X3/$R$4/12","v":7.315603860677844},{"$f":"$Z3*$Y3/$X3/$R$5/12","v":3.9326656592083213},{"$f":"$Z3*$Y3/$X3/$R$6/12","v":1.0630486860047492},{"$f":"$Z3*$Y3/$X3/$R$7/12","v":6.0745639200271384},{"$f":"$Z3*$Y3/$X3/$R$8/12","v":3.2709190338607672},{"$f":"$Z3*$Y3/$X3/$R$9/12","v":2.0146614126237474},{"$f":"$Z3*$Y3/$X3/$R$10/12","v":1.1189986168471044}]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,null,"4 (6/1) ACSR",1860,null,null,"Pine","Trunk",30,3,{"$f":"X4^4*PI()/4","v":63.617251235193308},5100,{"$f":"$Z4*$Y4/$X4/$R$3/12","v":8.9232118069165534},{"$f":"$Z4*$Y4/$X4/$R$4/12","v":4.8453999596697415},{"$f":"$Z4*$Y4/$X4/$R$5/12","v":2.6047525794756416},{"$f":"$Z4*$Y4/$X4/$R$6/12","v":0.7040971816395093},{"$f":"$Z4*$Y4/$X4/$R$7/12","v":4.0234124665114814},{"$f":"$Z4*$Y4/$X4/$R$8/12","v":2.1664528665831058},{"$f":"$Z4*$Y4/$X4/$R$9/12","v":1.3343861304391058},{"$f":"$Z4*$Y4/$X4/$R$10/12","v":0.74115492804158878}]
[null,1,{"$f":"C6","v":5},{"$f":"D6","v":5},{"$f":"E6","v":5},{"$f":"F6","v":5},{"$f":"G6","v":5},null,1,{"$f":"J6","v":5},{"$f":"K6","v":5},{"$f":"L6","v":5},{"$f":"M6","v":5},{"$f":"N6","v":5},null,null,"2 (7/1) ACSR",3460,null,null,"Oak","Branch",40,3,{"$f":"X5^4*PI()/4","v":63.617251235193308},8200,{"$f":"$Z5*$Y5/$X5/$R$3/12","v":14.347124866022691},{"$f":"$Z5*$Y5/$X5/$R$4/12","v":7.7906430724101723},{"$f":"$Z5*$Y5/$X5/$R$5/12","v":4.1880335591569127},{"$f":"$Z5*$Y5/$X5/$R$6/12","v":1.132077821459603},{"$f":"$Z5*$Y5/$X5/$R$7/12","v":6.4690161226263037},{"$f":"$Z5*$Y5/$X5/$R$8/12","v":3.4833163737218555},{"$f":"$Z5*$Y5/$X5/$R$9/12","v":2.1454835822746401},{"$f":"$Z5*$Y5/$X5/$R$10/12","v":1.191660864694319}]
[null,50,5,5,5,5,5,null,50,{"$f":"C6+Spans!$C$10","v":5},{"$f":"D6+Spans!$C$10","v":5},{"$f":"E6+Spans!$C$10","v":5},{"$f":"F6+Spans!$C$10","v":5},{"$f":"G6+Spans!$C$10","v":5},null,null,"715.5 AAC",12800,null,null,"Blue Gum / Eucalyptus","Branch",51,3,{"$f":"X6^4*PI()/4","v":63.617251235193308},19530,{"$f":"$Z6*$Y6/$X6/$R$3/12","v":34.170652272368677},{"$f":"$Z6*$Y6/$X6/$R$4/12","v":18.555031610264713},{"$f":"$Z6*$Y6/$X6/$R$5/12","v":9.974670171992015},{"$f":"$Z6*$Y6/$X6/$R$6/12","v":2.696278030866591},{"$f":"$Z6*$Y6/$X6/$R$7/12","v":15.407303033523378},{"$f":"$Z6*$Y6/$X6/$R$8/12","v":8.2962400949741273},{"$f":"$Z6*$Y6/$X6/$R$9/12","v":5.1099139465638688},{"$f":"$Z6*$Y6/$X6/$R$10/12","v":2.8381874009122012}]
[null,100,5,5,5,5,5,null,100,{"$f":"C7+Spans!$C$10","v":5},{"$f":"D7+Spans!$C$10","v":5},{"$f":"E7+Spans!$C$10","v":5},{"$f":"F7+Spans!$C$10","v":5},{"$f":"G7+Spans!$C$10","v":5},null,null,"#2 HD Cu XLPE",2240]
[null,150,5,5,5,5,5,null,150,{"$f":"C8+Spans!$C$10","v":5},{"$f":"D8+Spans!$C$10","v":5},{"$f":"E8+Spans!$C$10","v":5},{"$f":"F8+Spans!$C$10","v":5},{"$f":"G8+Spans!$C$10","v":5},null,null,"1/0 ACSR XLPE",4160]
[null,200,5,5,5,5,5,null,200,{"$f":"C9+Spans!$C$10","v":5},{"$f":"D9+Spans!$C$10","v":5},{"$f":"E9+Spans!$C$10","v":5},{"$f":"F9+Spans!$C$10","v":5},{"$f":"G9+Spans!$C$10","v":5},null,null,"397.5 AAC XLPE",6754]
[null,300,5,5,5,5,5,null,300,{"$f":"C10+Spans!$C$10","v":5},{"$f":"D10+Spans!$C$10","v":5},{"$f":"E10+Spans!$C$10","v":5},{"$f":"F10+Spans!$C$10","v":5},{"$f":"G10+Spans!$C$10","v":5},null,null,"715.5 AAC XLPE",12160]
[null,400,5,5,5,5,5,null,400,{"$f":"C11+Spans!$C$10","v":5},{"$f":"D11+Spans!$C$10","v":5},{"$f":"E11+Spans!$C$10","v":5},{"$f":"F11+Spans!$C$10","v":5},{"$f":"G11+Spans!$C$10","v":5}]
[null,500,5,5,5,5,5,null,500,{"$f":"C12+Spans!$C$10","v":5},{"$f":"D12+Spans!$C$10","v":5},{"$f":"E12+Spans!$C$10","v":5},{"$f":"F12+Spans!$C$10","v":5},{"$f":"G12+Spans!$C$10","v":5}]
[null,1000,{"$f":"C12","v":5},{"$f":"D12","v":5},{"$f":"E12","v":5},{"$f":"F12","v":5},{"$f":"G12","v":5},null,1000,{"$f":"J12","v":5},{"$f":"K12","v":5},{"$f":"L12","v":5},{"$f":"M12","v":5},{"$f":"N12","v":5}]
[]
[null,null,null,null,null,null,null,null,"TABLE",2]
[null,"FEA Table:","Composite, #2 Cu XLPE, Pine",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C20","v":5},{"$f":"D20","v":5},{"$f":"E20","v":5},{"$f":"F20","v":5},{"$f":"G20","v":5},null,1,{"$f":"J20","v":5},{"$f":"K20","v":5},{"$f":"L20","v":5},{"$f":"M20","v":5},{"$f":"N20","v":5}]
[null,50,5,5,5,5,5,null,50,{"$f":"C20+Spans!$C$10","v":5},{"$f":"D20+Spans!$C$10","v":5},{"$f":"E20+Spans!$C$10","v":5},{"$f":"F20+Spans!$C$10","v":5},{"$f":"G20+Spans!$C$10","v":5}]
[null,100,5,5,5,5,5,null,100,{"$f":"C21+Spans!$C$10","v":5},{"$f":"D21+Spans!$C$10","v":5},{"$f":"E21+Spans!$C$10","v":5},{"$f":"F21+Spans!$C$10","v":5},{"$f":"G21+Spans!$C$10","v":5}]
[null,150,5,5,5,5,5,null,150,{"$f":"C22+Spans!$C$10","v":5},{"$f":"D22+Spans!$C$10","v":5},{"$f":"E22+Spans!$C$10","v":5},{"$f":"F22+Spans!$C$10","v":5},{"$f":"G22+Spans!$C$10","v":5}]
[null,200,5,5,5,5,5,null,200,{"$f":"C23+Spans!$C$10","v":5},{"$f":"D23+Spans!$C$10","v":5},{"$f":"E23+Spans!$C$10","v":5},{"$f":"F23+Spans!$C$10","v":5},{"$f":"G23+Spans!$C$10","v":5}]
[null,300,5,5,5,5,5,null,300,{"$f":"C24+Spans!$C$10","v":5},{"$f":"D24+Spans!$C$10","v":5},{"$f":"E24+Spans!$C$10","v":5},{"$f":"F24+Spans!$C$10","v":5},{"$f":"G24+Spans!$C$10","v":5}]
[null,400,5,5,5,5,5,null,400,{"$f":"C25+Spans!$C$10","v":5},{"$f":"D25+Spans!$C$10","v":5},{"$f":"E25+Spans!$C$10","v":5},{"$f":"F25+Spans!$C$10","v":5},{"$f":"G25+Spans!$C$10","v":5}]
[null,500,5,5,5,5,5,null,500,{"$f":"C26+Spans!$C$10","v":5},{"$f":"D26+Spans!$C$10","v":5},{"$f":"E26+Spans!$C$10","v":5},{"$f":"F26+Spans!$C$10","v":5},{"$f":"G26+Spans!$C$10","v":5}]
[null,1000,{"$f":"C26","v":5},{"$f":"D26","v":5},{"$f":"E26","v":5},{"$f":"F26","v":5},{"$f":"G26","v":5},null,1000,{"$f":"J26","v":5},{"$f":"K26","v":5},{"$f":"L26","v":5},{"$f":"M26","v":5},{"$f":"N26","v":5}]
[]
[null,null,null,null,null,null,null,null,"TABLE",3]
[null,"FEA Table:","Composite, #2 Cu XLPE, Oak",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C34","v":17},{"$f":"D34","v":17},{"$f":"E34","v":17},{"$f":"F34","v":17},{"$f":"G34","v":17},null,1,{"$f":"J34","v":17},{"$f":"K34","v":17},{"$f":"L34","v":17},{"$f":"M34","v":17},{"$f":"N34","v":17}]
[null,50,17,17,17,17,17,null,50,{"$f":"C34+Spans!$C$10","v":17},{"$f":"D34+Spans!$C$10","v":17},{"$f":"E34+Spans!$C$10","v":17},{"$f":"F34+Spans!$C$10","v":17},{"$f":"G34+Spans!$C$10","v":17}]
[null,100,17,17,17,17,17,null,100,{"$f":"C35+Spans!$C$10","v":17},{"$f":"D35+Spans!$C$10","v":17},{"$f":"E35+Spans!$C$10","v":17},{"$f":"F35+Spans!$C$10","v":17},{"$f":"G35+Spans!$C$10","v":17}]
[null,150,17,17,17,17,17,null,150,{"$f":"C36+Spans!$C$10","v":17},{"$f":"D36+Spans!$C$10","v":17},{"$f":"E36+Spans!$C$10","v":17},{"$f":"F36+Spans!$C$10","v":17},{"$f":"G36+Spans!$C$10","v":17}]
[null,200,17,17,17,17,17,null,200,{"$f":"C37+Spans!$C$10","v":17},{"$f":"D37+Spans!$C$10","v":17},{"$f":"E37+Spans!$C$10","v":17},{"$f":"F37+Spans!$C$10","v":17},{"$f":"G37+Spans!$C$10","v":17}]
[null,300,17,17,17,17,17,null,300,{"$f":"C38+Spans!$C$10","v":17},{"$f":"D38+Spans!$C$10","v":17},{"$f":"E38+Spans!$C$10","v":17},{"$f":"F38+Spans!$C$10","v":17},{"$f":"G38+Spans!$C$10","v":17}]
[null,400,17,17,17,17,17,null,400,{"$f":"C39+Spans!$C$10","v":17},{"$f":"D39+Spans!$C$10","v":17},{"$f":"E39+Spans!$C$10","v":17},{"$f":"F39+Spans!$C$10","v":17},{"$f":"G39+Spans!$C$10","v":17}]
[null,500,17,17,17,17,17,null,500,{"$f":"C40+Spans!$C$10","v":17},{"$f":"D40+Spans!$C$10","v":17},{"$f":"E40+Spans!$C$10","v":17},{"$f":"F40+Spans!$C$10","v":17},{"$f":"G40+Spans!$C$10","v":17}]
[null,1000,{"$f":"C40","v":17},{"$f":"D40","v":17},{"$f":"E40","v":17},{"$f":"F40","v":17},{"$f":"G40","v":17},null,1000,{"$f":"J40","v":17},{"$f":"K40","v":17},{"$f":"L40","v":17},{"$f":"M40","v":17},{"$f":"N40","v":17}]
[]
[null,null,null,null,null,null,null,null,"TABLE",4]
[null,"FEA Table:","Composite, #2 Cu XLPE, Blue Gum / Eucalyptus",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C48","v":17},{"$f":"D48","v":17},{"$f":"E48","v":17},{"$f":"F48","v":17},{"$f":"G48","v":17},null,1,{"$f":"J48","v":17},{"$f":"K48","v":17},{"$f":"L48","v":17},{"$f":"M48","v":17},{"$f":"N48","v":17}]
[null,50,17,17,17,17,17,null,50,{"$f":"C48+Spans!$C$10","v":17},{"$f":"D48+Spans!$C$10","v":17},{"$f":"E48+Spans!$C$10","v":17},{"$f":"F48+Spans!$C$10","v":17},{"$f":"G48+Spans!$C$10","v":17}]
[null,100,17,17,17,17,17,null,100,{"$f":"C49+Spans!$C$10","v":17},{"$f":"D49+Spans!$C$10","v":17},{"$f":"E49+Spans!$C$10","v":17},{"$f":"F49+Spans!$C$10","v":17},{"$f":"G49+Spans!$C$10","v":17}]
[null,150,17,17,17,17,17,null,150,{"$f":"C50+Spans!$C$10","v":17},{"$f":"D50+Spans!$C$10","v":17},{"$f":"E50+Spans!$C$10","v":17},{"$f":"F50+Spans!$C$10","v":17},{"$f":"G50+Spans!$C$10","v":17}]
[null,200,17,17,17,17,17,null,200,{"$f":"C51+Spans!$C$10","v":17},{"$f":"D51+Spans!$C$10","v":17},{"$f":"E51+Spans!$C$10","v":17},{"$f":"F51+Spans!$C$10","v":17},{"$f":"G51+Spans!$C$10","v":17}]
[null,300,17,17,17,17,17,null,300,{"$f":"C52+Spans!$C$10","v":17},{"$f":"D52+Spans!$C$10","v":17},{"$f":"E52+Spans!$C$10","v":17},{"$f":"F52+Spans!$C$10","v":17},{"$f":"G52+Spans!$C$10","v":17}]
[null,400,17,17,17,17,17,null,400,{"$f":"C53+Spans!$C$10","v":17},{"$f":"D53+Spans!$C$10","v":17},{"$f":"E53+Spans!$C$10","v":17},{"$f":"F53+Spans!$C$10","v":17},{"$f":"G53+Spans!$C$10","v":17}]
[null,500,17,17,17,17,17,null,500,{"$f":"C54+Spans!$C$10","v":17},{"$f":"D54+Spans!$C$10","v":17},{"$f":"E54+Spans!$C$10","v":17},{"$f":"F54+Spans!$C$10","v":17},{"$f":"G54+Spans!$C$10","v":17}]
[null,1000,{"$f":"C54","v":17},{"$f":"D54","v":17},{"$f":"E54","v":17},{"$f":"F54","v":17},{"$f":"G54","v":17},null,1000,{"$f":"J54","v":17},{"$f":"K54","v":17},{"$f":"L54","v":17},{"$f":"M54","v":17},{"$f":"N54","v":17}]
[]
[null,null,null,null,null,null,null,null,"TABLE",5]
[null,"FEA Table:","Composite, 1/0 ACSR XLPE, Douglas Fir",null,null,null,null,null,"Span Shape:",2,3,4,5,6,null,null,null,{"$f":"VLOOKUP(100, Table5, 6, FALSE)","v":4}]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C62","v":5},{"$f":"D62","v":5},{"$f":"E62","v":5},{"$f":"F62","v":5},{"$f":"G62","v":3},null,1,{"$f":"J62","v":5},{"$f":"K62","v":5},{"$f":"L62","v":5},{"$f":"M62","v":5},{"$f":"N62","v":3}]
[null,50,5,5,5,5,3,null,50,{"$f":"C62+Spans!$C$10","v":5},{"$f":"D62+Spans!$C$10","v":5},{"$f":"E62+Spans!$C$10","v":5},{"$f":"F62+Spans!$C$10","v":5},{"$f":"G62+Spans!$C$10","v":3}]
[null,100,7,7,11,12,4,null,100,{"$f":"C63+Spans!$C$10","v":7},{"$f":"D63+Spans!$C$10","v":7},{"$f":"E63+Spans!$C$10","v":11},{"$f":"F63+Spans!$C$10","v":12},{"$f":"G63+Spans!$C$10","v":4}]
[null,150,7,11,16,13,6,null,150,{"$f":"C64+Spans!$C$10","v":7},{"$f":"D64+Spans!$C$10","v":11},{"$f":"E64+Spans!$C$10","v":16},{"$f":"F64+Spans!$C$10","v":13},{"$f":"G64+Spans!$C$10","v":6}]
[null,200,11,16,16,13,7,null,200,{"$f":"C65+Spans!$C$10","v":11},{"$f":"D65+Spans!$C$10","v":16},{"$f":"E65+Spans!$C$10","v":16},{"$f":"F65+Spans!$C$10","v":13},{"$f":"G65+Spans!$C$10","v":7}]
[null,300,16,16,16,15,12,null,300,{"$f":"C66+Spans!$C$10","v":16},{"$f":"D66+Spans!$C$10","v":16},{"$f":"E66+Spans!$C$10","v":16},{"$f":"F66+Spans!$C$10","v":15},{"$f":"G66+Spans!$C$10","v":12}]
[null,400,19,16,18,15,17,null,400,{"$f":"C67+Spans!$C$10","v":19},{"$f":"D67+Spans!$C$10","v":16},{"$f":"E67+Spans!$C$10","v":18},{"$f":"F67+Spans!$C$10","v":15},{"$f":"G67+Spans!$C$10","v":17}]
[null,500,21,16,22,17,18,null,500,{"$f":"C68+Spans!$C$10","v":21},{"$f":"D68+Spans!$C$10","v":16},{"$f":"E68+Spans!$C$10","v":22},{"$f":"F68+Spans!$C$10","v":17},{"$f":"G68+Spans!$C$10","v":18}]
[null,1000,{"$f":"C68","v":21},{"$f":"D68","v":16},{"$f":"E68","v":22},{"$f":"F68","v":17},{"$f":"G68","v":18},null,1000,{"$f":"J68","v":21},{"$f":"K68","v":16},{"$f":"L68","v":22},{"$f":"M68","v":17},{"$f":"N68","v":18}]
[]
[null,null,null,null,null,null,null,null,"TABLE",6]
[null,"FEA Table:","Composite, 1/0 ACSR XLPE, Pine",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C76","v":6},{"$f":"D76","v":6},{"$f":"E76","v":8},{"$f":"F76","v":7},{"$f":"G76","v":3},null,1,{"$f":"J76","v":6},{"$f":"K76","v":6},{"$f":"L76","v":8},{"$f":"M76","v":7},{"$f":"N76","v":3}]
[null,50,6,6,8,7,3,null,50,{"$f":"C76+Spans!$C$10","v":6},{"$f":"D76+Spans!$C$10","v":6},{"$f":"E76+Spans!$C$10","v":8},{"$f":"F76+Spans!$C$10","v":7},{"$f":"G76+Spans!$C$10","v":3}]
[null,100,10,10,13,15,8,null,100,{"$f":"C77+Spans!$C$10","v":10},{"$f":"D77+Spans!$C$10","v":10},{"$f":"E77+Spans!$C$10","v":13},{"$f":"F77+Spans!$C$10","v":15},{"$f":"G77+Spans!$C$10","v":8}]
[null,150,15,15,18,16,11,null,150,{"$f":"C78+Spans!$C$10","v":15},{"$f":"D78+Spans!$C$10","v":15},{"$f":"E78+Spans!$C$10","v":18},{"$f":"F78+Spans!$C$10","v":16},{"$f":"G78+Spans!$C$10","v":11}]
[null,200,17,20,20,18,16,null,200,{"$f":"C79+Spans!$C$10","v":17},{"$f":"D79+Spans!$C$10","v":20},{"$f":"E79+Spans!$C$10","v":20},{"$f":"F79+Spans!$C$10","v":18},{"$f":"G79+Spans!$C$10","v":16}]
[null,300,22,22,21,20,20,null,300,{"$f":"C80+Spans!$C$10","v":22},{"$f":"D80+Spans!$C$10","v":22},{"$f":"E80+Spans!$C$10","v":21},{"$f":"F80+Spans!$C$10","v":20},{"$f":"G80+Spans!$C$10","v":20}]
[null,400,27,23,22,21,23,null,400,{"$f":"C81+Spans!$C$10","v":27},{"$f":"D81+Spans!$C$10","v":23},{"$f":"E81+Spans!$C$10","v":22},{"$f":"F81+Spans!$C$10","v":21},{"$f":"G81+Spans!$C$10","v":23}]
[null,500,32,27,27,22,27,null,500,{"$f":"C82+Spans!$C$10","v":32},{"$f":"D82+Spans!$C$10","v":27},{"$f":"E82+Spans!$C$10","v":27},{"$f":"F82+Spans!$C$10","v":22},{"$f":"G82+Spans!$C$10","v":27}]
[null,1000,{"$f":"C82","v":32},{"$f":"D82","v":27},{"$f":"E82","v":27},{"$f":"F82","v":22},{"$f":"G82","v":27},null,1000,{"$f":"J82","v":32},{"$f":"K82","v":27},{"$f":"L82","v":27},{"$f":"M82","v":22},{"$f":"N82","v":27}]
[]
[null,null,null,null,null,null,null,null,"TABLE",7]
[null,"FEA Table:","Composite, 1/0 ACSR XLPE, Oak",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C90","v":24},{"$f":"D90","v":24},{"$f":"E90","v":24},{"$f":"F90","v":24},{"$f":"G90","v":24},null,1,{"$f":"J90","v":24},{"$f":"K90","v":24},{"$f":"L90","v":24},{"$f":"M90","v":24},{"$f":"N90","v":24}]
[null,50,24,24,24,24,24,null,50,{"$f":"C90+Spans!$C$10","v":24},{"$f":"D90+Spans!$C$10","v":24},{"$f":"E90+Spans!$C$10","v":24},{"$f":"F90+Spans!$C$10","v":24},{"$f":"G90+Spans!$C$10","v":24}]
[null,100,24,24,24,24,24,null,100,{"$f":"C91+Spans!$C$10","v":24},{"$f":"D91+Spans!$C$10","v":24},{"$f":"E91+Spans!$C$10","v":24},{"$f":"F91+Spans!$C$10","v":24},{"$f":"G91+Spans!$C$10","v":24}]
[null,150,24,24,24,24,24,null,150,{"$f":"C92+Spans!$C$10","v":24},{"$f":"D92+Spans!$C$10","v":24},{"$f":"E92+Spans!$C$10","v":24},{"$f":"F92+Spans!$C$10","v":24},{"$f":"G92+Spans!$C$10","v":24}]
[null,200,24,24,24,24,24,null,200,{"$f":"C93+Spans!$C$10","v":24},{"$f":"D93+Spans!$C$10","v":24},{"$f":"E93+Spans!$C$10","v":24},{"$f":"F93+Spans!$C$10","v":24},{"$f":"G93+Spans!$C$10","v":24}]
[null,300,28,28,24,24,24,null,300,{"$f":"C94+Spans!$C$10","v":28},{"$f":"D94+Spans!$C$10","v":28},{"$f":"E94+Spans!$C$10","v":24},{"$f":"F94+Spans!$C$10","v":24},{"$f":"G94+Spans!$C$10","v":24}]
[null,400,30,30,27,27,24,null,400,{"$f":"C95+Spans!$C$10","v":30},{"$f":"D95+Spans!$C$10","v":30},{"$f":"E95+Spans!$C$10","v":27},{"$f":"F95+Spans!$C$10","v":27},{"$f":"G95+Spans!$C$10","v":24}]
[null,500,30,30,30,30,30,null,500,{"$f":"C96+Spans!$C$10","v":30},{"$f":"D96+Spans!$C$10","v":30},{"$f":"E96+Spans!$C$10","v":30},{"$f":"F96+Spans!$C$10","v":30},{"$f":"G96+Spans!$C$10","v":30}]
[null,1000,{"$f":"C96","v":30},{"$f":"D96","v":30},{"$f":"E96","v":30},{"$f":"F96","v":30},{"$f":"G96","v":30},null,1000,{"$f":"J96","v":30},{"$f":"K96","v":30},{"$f":"L96","v":30},{"$f":"M96","v":30},{"$f":"N96","v":30}]
[]
[null,null,null,null,null,null,null,null,"TABLE",8]
[null,"FEA Table:","Composite, 1/0 ACSR XLPE, Blue Gum / Eucalyptus",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C104","v":17},{"$f":"D104","v":17},{"$f":"E104","v":17},{"$f":"F104","v":17},{"$f":"G104","v":17},null,1,{"$f":"J104","v":17},{"$f":"K104","v":17},{"$f":"L104","v":17},{"$f":"M104","v":17},{"$f":"N104","v":17}]
[null,50,17,17,17,17,17,null,50,{"$f":"C104+Spans!$C$10","v":17},{"$f":"D104+Spans!$C$10","v":17},{"$f":"E104+Spans!$C$10","v":17},{"$f":"F104+Spans!$C$10","v":17},{"$f":"G104+Spans!$C$10","v":17}]
[null,100,17,17,17,17,17,null,100,{"$f":"C105+Spans!$C$10","v":17},{"$f":"D105+Spans!$C$10","v":17},{"$f":"E105+Spans!$C$10","v":17},{"$f":"F105+Spans!$C$10","v":17},{"$f":"G105+Spans!$C$10","v":17}]
[null,150,17,17,17,17,17,null,150,{"$f":"C106+Spans!$C$10","v":17},{"$f":"D106+Spans!$C$10","v":17},{"$f":"E106+Spans!$C$10","v":17},{"$f":"F106+Spans!$C$10","v":17},{"$f":"G106+Spans!$C$10","v":17}]
[null,200,17,17,17,17,17,null,200,{"$f":"C107+Spans!$C$10","v":17},{"$f":"D107+Spans!$C$10","v":17},{"$f":"E107+Spans!$C$10","v":17},{"$f":"F107+Spans!$C$10","v":17},{"$f":"G107+Spans!$C$10","v":17}]
[null,300,17,17,17,17,17,null,300,{"$f":"C108+Spans!$C$10","v":17},{"$f":"D108+Spans!$C$10","v":17},{"$f":"E108+Spans!$C$10","v":17},{"$f":"F108+Spans!$C$10","v":17},{"$f":"G108+Spans!$C$10","v":17}]
[null,400,17,17,17,17,17,null,400,{"$f":"C109+Spans!$C$10","v":17},{"$f":"D109+Spans!$C$10","v":17},{"$f":"E109+Spans!$C$10","v":17},{"$f":"F109+Spans!$C$10","v":17},{"$f":"G109+Spans!$C$10","v":17}]
[null,500,17,17,17,17,17,null,500,{"$f":"C110+Spans!$C$10","v":17},{"$f":"D110+Spans!$C$10","v":17},{"$f":"E110+Spans!$C$10","v":17},{"$f":"F110+Spans!$C$10","v":17},{"$f":"G110+Spans!$C$10","v":17}]
[null,1000,{"$f":"C110","v":17},{"$f":"D110","v":17},{"$f":"E110","v":17},{"$f":"F110","v":17},{"$f":"G110","v":17},null,1000,{"$f":"J110","v":17},{"$f":"K110","v":17},{"$f":"L110","v":17},{"$f":"M110","v":17},{"$f":"N110","v":17}]
[]
[null,null,null,null,null,null,null,null,"TABLE",9]
[null,"FEA Table:","Composite, 397.5 AAC XLPE, Douglas Fir",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C118","v":16},{"$f":"D118","v":16},{"$f":"E118","v":20},{"$f":"F118","v":24},{"$f":"G118","v":10},null,1,{"$f":"J118","v":16},{"$f":"K118","v":16},{"$f":"L118","v":20},{"$f":"M118","v":24},{"$f":"N118","v":10}]
[null,50,16,16,20,24,10,null,50,{"$f":"C118+Spans!$C$10","v":16},{"$f":"D118+Spans!$C$10","v":16},{"$f":"E118+Spans!$C$10","v":20},{"$f":"F118+Spans!$C$10","v":24},{"$f":"G118+Spans!$C$10","v":10}]
[null,100,16,23,30,25,14,null,100,{"$f":"C119+Spans!$C$10","v":16},{"$f":"D119+Spans!$C$10","v":23},{"$f":"E119+Spans!$C$10","v":30},{"$f":"F119+Spans!$C$10","v":25},{"$f":"G119+Spans!$C$10","v":14}]
[null,150,21,26,30,25,24,null,150,{"$f":"C120+Spans!$C$10","v":21},{"$f":"D120+Spans!$C$10","v":26},{"$f":"E120+Spans!$C$10","v":30},{"$f":"F120+Spans!$C$10","v":25},{"$f":"G120+Spans!$C$10","v":24}]
[null,200,26,31,30,25,26,null,200,{"$f":"C121+Spans!$C$10","v":26},{"$f":"D121+Spans!$C$10","v":31},{"$f":"E121+Spans!$C$10","v":30},{"$f":"F121+Spans!$C$10","v":25},{"$f":"G121+Spans!$C$10","v":26}]
[null,300,31,31,30,27,29,null,300,{"$f":"C122+Spans!$C$10","v":31},{"$f":"D122+Spans!$C$10","v":31},{"$f":"E122+Spans!$C$10","v":30},{"$f":"F122+Spans!$C$10","v":27},{"$f":"G122+Spans!$C$10","v":29}]
[null,400,36,34,35,30,31,null,400,{"$f":"C123+Spans!$C$10","v":36},{"$f":"D123+Spans!$C$10","v":34},{"$f":"E123+Spans!$C$10","v":35},{"$f":"F123+Spans!$C$10","v":30},{"$f":"G123+Spans!$C$10","v":31}]
[null,500,36,34,37,34,34,null,500,{"$f":"C124+Spans!$C$10","v":36},{"$f":"D124+Spans!$C$10","v":34},{"$f":"E124+Spans!$C$10","v":37},{"$f":"F124+Spans!$C$10","v":34},{"$f":"G124+Spans!$C$10","v":34}]
[null,1000,{"$f":"C124","v":36},{"$f":"D124","v":34},{"$f":"E124","v":37},{"$f":"F124","v":34},{"$f":"G124","v":34},null,1000,{"$f":"J124","v":36},{"$f":"K124","v":34},{"$f":"L124","v":37},{"$f":"M124","v":34},{"$f":"N124","v":34}]
[]
[null,null,null,null,null,null,null,null,"TABLE",10]
[null,"FEA Table:","Composite, 397.5 AAC XLPE, Pine",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C132","v":19},{"$f":"D132","v":19},{"$f":"E132","v":30},{"$f":"F132","v":28},{"$f":"G132","v":18},null,1,{"$f":"J132","v":19},{"$f":"K132","v":19},{"$f":"L132","v":30},{"$f":"M132","v":28},{"$f":"N132","v":18}]
[null,50,19,19,30,28,18,null,50,{"$f":"C132+Spans!$C$10","v":19},{"$f":"D132+Spans!$C$10","v":19},{"$f":"E132+Spans!$C$10","v":30},{"$f":"F132+Spans!$C$10","v":28},{"$f":"G132+Spans!$C$10","v":18}]
[null,100,21,28,35,31,20,null,100,{"$f":"C133+Spans!$C$10","v":21},{"$f":"D133+Spans!$C$10","v":28},{"$f":"E133+Spans!$C$10","v":35},{"$f":"F133+Spans!$C$10","v":31},{"$f":"G133+Spans!$C$10","v":20}]
[null,150,26,37,36,32,27,null,150,{"$f":"C134+Spans!$C$10","v":26},{"$f":"D134+Spans!$C$10","v":37},{"$f":"E134+Spans!$C$10","v":36},{"$f":"F134+Spans!$C$10","v":32},{"$f":"G134+Spans!$C$10","v":27}]
[null,200,32,41,37,34,32,null,200,{"$f":"C135+Spans!$C$10","v":32},{"$f":"D135+Spans!$C$10","v":41},{"$f":"E135+Spans!$C$10","v":37},{"$f":"F135+Spans!$C$10","v":34},{"$f":"G135+Spans!$C$10","v":32}]
[null,300,36,41,39,35,33,null,300,{"$f":"C136+Spans!$C$10","v":36},{"$f":"D136+Spans!$C$10","v":41},{"$f":"E136+Spans!$C$10","v":39},{"$f":"F136+Spans!$C$10","v":35},{"$f":"G136+Spans!$C$10","v":33}]
[null,400,42,42,42,37,37,null,400,{"$f":"C137+Spans!$C$10","v":42},{"$f":"D137+Spans!$C$10","v":42},{"$f":"E137+Spans!$C$10","v":42},{"$f":"F137+Spans!$C$10","v":37},{"$f":"G137+Spans!$C$10","v":37}]
[null,500,46,47,43,40,42,null,500,{"$f":"C138+Spans!$C$10","v":46},{"$f":"D138+Spans!$C$10","v":47},{"$f":"E138+Spans!$C$10","v":43},{"$f":"F138+Spans!$C$10","v":40},{"$f":"G138+Spans!$C$10","v":42}]
[null,1000,{"$f":"C138","v":46},{"$f":"D138","v":47},{"$f":"E138","v":43},{"$f":"F138","v":40},{"$f":"G138","v":42},null,1000,{"$f":"J138","v":46},{"$f":"K138","v":47},{"$f":"L138","v":43},{"$f":"M138","v":40},{"$f":"N138","v":42}]
[]
[null,null,null,null,null,null,null,null,"TABLE",11]
[null,"FEA Table:","Composite, 397.5 AAC XLPE, Oak",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C146","v":30},{"$f":"D146","v":30},{"$f":"E146","v":30},{"$f":"F146","v":28},{"$f":"G146","v":28},null,1,{"$f":"J146","v":30},{"$f":"K146","v":30},{"$f":"L146","v":30},{"$f":"M146","v":28},{"$f":"N146","v":28}]
[null,50,30,30,30,28,28,null,50,{"$f":"C146+Spans!$C$10","v":30},{"$f":"D146+Spans!$C$10","v":30},{"$f":"E146+Spans!$C$10","v":30},{"$f":"F146+Spans!$C$10","v":28},{"$f":"G146+Spans!$C$10","v":28}]
[null,100,30,30,30,28,30,null,100,{"$f":"C147+Spans!$C$10","v":30},{"$f":"D147+Spans!$C$10","v":30},{"$f":"E147+Spans!$C$10","v":30},{"$f":"F147+Spans!$C$10","v":28},{"$f":"G147+Spans!$C$10","v":30}]
[null,150,30,30,30,30,30,null,150,{"$f":"C148+Spans!$C$10","v":30},{"$f":"D148+Spans!$C$10","v":30},{"$f":"E148+Spans!$C$10","v":30},{"$f":"F148+Spans!$C$10","v":30},{"$f":"G148+Spans!$C$10","v":30}]
[null,200,30,30,30,30,30,null,200,{"$f":"C149+Spans!$C$10","v":30},{"$f":"D149+Spans!$C$10","v":30},{"$f":"E149+Spans!$C$10","v":30},{"$f":"F149+Spans!$C$10","v":30},{"$f":"G149+Spans!$C$10","v":30}]
[null,300,30,30,30,30,30,null,300,{"$f":"C150+Spans!$C$10","v":30},{"$f":"D150+Spans!$C$10","v":30},{"$f":"E150+Spans!$C$10","v":30},{"$f":"F150+Spans!$C$10","v":30},{"$f":"G150+Spans!$C$10","v":30}]
[null,400,30,30,30,30,30,null,400,{"$f":"C151+Spans!$C$10","v":30},{"$f":"D151+Spans!$C$10","v":30},{"$f":"E151+Spans!$C$10","v":30},{"$f":"F151+Spans!$C$10","v":30},{"$f":"G151+Spans!$C$10","v":30}]
[null,500,30,30,30,30,30,null,500,{"$f":"C152+Spans!$C$10","v":30},{"$f":"D152+Spans!$C$10","v":30},{"$f":"E152+Spans!$C$10","v":30},{"$f":"F152+Spans!$C$10","v":30},{"$f":"G152+Spans!$C$10","v":30}]
[null,1000,{"$f":"C152","v":30},{"$f":"D152","v":30},{"$f":"E152","v":30},{"$f":"F152","v":30},{"$f":"G152","v":30},null,1000,{"$f":"J152","v":30},{"$f":"K152","v":30},{"$f":"L152","v":30},{"$f":"M152","v":30},{"$f":"N152","v":30}]
[]
[null,null,null,null,null,null,null,null,"TABLE",12]
[null,"FEA Table:","Composite, 397.5 AAC XLPE, Blue Gum / Eucalyptus",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C160","v":30},{"$f":"D160","v":30},{"$f":"E160","v":30},{"$f":"F160","v":28},{"$f":"G160","v":28},null,1,{"$f":"J160","v":30},{"$f":"K160","v":30},{"$f":"L160","v":30},{"$f":"M160","v":28},{"$f":"N160","v":28}]
[null,50,30,30,30,28,28,null,50,{"$f":"C160+Spans!$C$10","v":30},{"$f":"D160+Spans!$C$10","v":30},{"$f":"E160+Spans!$C$10","v":30},{"$f":"F160+Spans!$C$10","v":28},{"$f":"G160+Spans!$C$10","v":28}]
[null,100,30,30,30,28,30,null,100,{"$f":"C161+Spans!$C$10","v":30},{"$f":"D161+Spans!$C$10","v":30},{"$f":"E161+Spans!$C$10","v":30},{"$f":"F161+Spans!$C$10","v":28},{"$f":"G161+Spans!$C$10","v":30}]
[null,150,30,30,30,30,30,null,150,{"$f":"C162+Spans!$C$10","v":30},{"$f":"D162+Spans!$C$10","v":30},{"$f":"E162+Spans!$C$10","v":30},{"$f":"F162+Spans!$C$10","v":30},{"$f":"G162+Spans!$C$10","v":30}]
[null,200,30,30,30,30,30,null,200,{"$f":"C163+Spans!$C$10","v":30},{"$f":"D163+Spans!$C$10","v":30},{"$f":"E163+Spans!$C$10","v":30},{"$f":"F163+Spans!$C$10","v":30},{"$f":"G163+Spans!$C$10","v":30}]
[null,300,30,30,30,30,30,null,300,{"$f":"C164+Spans!$C$10","v":30},{"$f":"D164+Spans!$C$10","v":30},{"$f":"E164+Spans!$C$10","v":30},{"$f":"F164+Spans!$C$10","v":30},{"$f":"G164+Spans!$C$10","v":30}]
[null,400,30,30,30,30,30,null,400,{"$f":"C165+Spans!$C$10","v":30},{"$f":"D165+Spans!$C$10","v":30},{"$f":"E165+Spans!$C$10","v":30},{"$f":"F165+Spans!$C$10","v":30},{"$f":"G165+Spans!$C$10","v":30}]
[null,500,30,30,30,30,30,null,500,{"$f":"C166+Spans!$C$10","v":30},{"$f":"D166+Spans!$C$10","v":30},{"$f":"E166+Spans!$C$10","v":30},{"$f":"F166+Spans!$C$10","v":30},{"$f":"G166+Spans!$C$10","v":30}]
[null,1000,{"$f":"C166","v":30},{"$f":"D166","v":30},{"$f":"E166","v":30},{"$f":"F166","v":30},{"$f":"G166","v":30},null,1000,{"$f":"J166","v":30},{"$f":"K166","v":30},{"$f":"L166","v":30},{"$f":"M166","v":30},{"$f":"N166","v":30}]
[]
[null,null,null,null,null,null,null,null,"TABLE",13]
[null,"FEA Table:","Composite, 715.5 AAC XLPE, Douglas Fir",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C174","v":50},{"$f":"D174","v":50},{"$f":"E174","v":50},{"$f":"F174","v":50},{"$f":"G174","v":50},null,1,{"$f":"J174","v":50},{"$f":"K174","v":50},{"$f":"L174","v":50},{"$f":"M174","v":50},{"$f":"N174","v":50}]
[null,50,50,50,50,50,50,null,50,{"$f":"C174+Spans!$C$10","v":50},{"$f":"D174+Spans!$C$10","v":50},{"$f":"E174+Spans!$C$10","v":50},{"$f":"F174+Spans!$C$10","v":50},{"$f":"G174+Spans!$C$10","v":50}]
[null,100,50,50,50,50,50,null,100,{"$f":"C175+Spans!$C$10","v":50},{"$f":"D175+Spans!$C$10","v":50},{"$f":"E175+Spans!$C$10","v":50},{"$f":"F175+Spans!$C$10","v":50},{"$f":"G175+Spans!$C$10","v":50}]
[null,150,50,50,50,50,50,null,150,{"$f":"C176+Spans!$C$10","v":50},{"$f":"D176+Spans!$C$10","v":50},{"$f":"E176+Spans!$C$10","v":50},{"$f":"F176+Spans!$C$10","v":50},{"$f":"G176+Spans!$C$10","v":50}]
[null,200,50,50,50,50,50,null,200,{"$f":"C177+Spans!$C$10","v":50},{"$f":"D177+Spans!$C$10","v":50},{"$f":"E177+Spans!$C$10","v":50},{"$f":"F177+Spans!$C$10","v":50},{"$f":"G177+Spans!$C$10","v":50}]
[null,300,50,50,50,50,50,null,300,{"$f":"C178+Spans!$C$10","v":50},{"$f":"D178+Spans!$C$10","v":50},{"$f":"E178+Spans!$C$10","v":50},{"$f":"F178+Spans!$C$10","v":50},{"$f":"G178+Spans!$C$10","v":50}]
[null,400,50,50,50,50,50,null,400,{"$f":"C179+Spans!$C$10","v":50},{"$f":"D179+Spans!$C$10","v":50},{"$f":"E179+Spans!$C$10","v":50},{"$f":"F179+Spans!$C$10","v":50},{"$f":"G179+Spans!$C$10","v":50}]
[null,500,50,50,50,50,50,null,500,{"$f":"C180+Spans!$C$10","v":50},{"$f":"D180+Spans!$C$10","v":50},{"$f":"E180+Spans!$C$10","v":50},{"$f":"F180+Spans!$C$10","v":50},{"$f":"G180+Spans!$C$10","v":50}]
[null,1000,{"$f":"C180","v":50},{"$f":"D180","v":50},{"$f":"E180","v":50},{"$f":"F180","v":50},{"$f":"G180","v":50},null,1000,{"$f":"J180","v":50},{"$f":"K180","v":50},{"$f":"L180","v":50},{"$f":"M180","v":50},{"$f":"N180","v":50}]
[]
[null,null,null,null,null,null,null,null,"TABLE",14]
[null,"FEA Table:","Composite, 715.5 AAC XLPE, Pine",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C188","v":50},{"$f":"D188","v":50},{"$f":"E188","v":50},{"$f":"F188","v":50},{"$f":"G188","v":50},null,1,{"$f":"J188","v":50},{"$f":"K188","v":50},{"$f":"L188","v":50},{"$f":"M188","v":50},{"$f":"N188","v":50}]
[null,50,50,50,50,50,50,null,50,{"$f":"C188+Spans!$C$10","v":50},{"$f":"D188+Spans!$C$10","v":50},{"$f":"E188+Spans!$C$10","v":50},{"$f":"F188+Spans!$C$10","v":50},{"$f":"G188+Spans!$C$10","v":50}]
[null,100,50,50,50,50,50,null,100,{"$f":"C189+Spans!$C$10","v":50},{"$f":"D189+Spans!$C$10","v":50},{"$f":"E189+Spans!$C$10","v":50},{"$f":"F189+Spans!$C$10","v":50},{"$f":"G189+Spans!$C$10","v":50}]
[null,150,50,50,50,50,50,null,150,{"$f":"C190+Spans!$C$10","v":50},{"$f":"D190+Spans!$C$10","v":50},{"$f":"E190+Spans!$C$10","v":50},{"$f":"F190+Spans!$C$10","v":50},{"$f":"G190+Spans!$C$10","v":50}]
[null,200,50,50,50,50,50,null,200,{"$f":"C191+Spans!$C$10","v":50},{"$f":"D191+Spans!$C$10","v":50},{"$f":"E191+Spans!$C$10","v":50},{"$f":"F191+Spans!$C$10","v":50},{"$f":"G191+Spans!$C$10","v":50}]
[null,300,50,50,50,50,50,null,300,{"$f":"C192+Spans!$C$10","v":50},{"$f":"D192+Spans!$C$10","v":50},{"$f":"E192+Spans!$C$10","v":50},{"$f":"F192+Spans!$C$10","v":50},{"$f":"G192+Spans!$C$10","v":50}]
[null,400,50,50,50,50,50,null,400,{"$f":"C193+Spans!$C$10","v":50},{"$f":"D193+Spans!$C$10","v":50},{"$f":"E193+Spans!$C$10","v":50},{"$f":"F193+Spans!$C$10","v":50},{"$f":"G193+Spans!$C$10","v":50}]
[null,500,50,50,50,50,50,null,500,{"$f":"C194+Spans!$C$10","v":50},{"$f":"D194+Spans!$C$10","v":50},{"$f":"E194+Spans!$C$10","v":50},{"$f":"F194+Spans!$C$10","v":50},{"$f":"G194+Spans!$C$10","v":50}]
[null,1000,{"$f":"C194","v":50},{"$f":"D194","v":50},{"$f":"E194","v":50},{"$f":"F194","v":50},{"$f":"G194","v":50},null,1000,{"$f":"J194","v":50},{"$f":"K194","v":50},{"$f":"L194","v":50},{"$f":"M194","v":50},{"$f":"N194","v":50}]
[]
[null,null,null,null,null,null,null,null,"TABLE",15]
[null,"FEA Table:","Composite, 715.5 AAC XLPE, Oak",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C202","v":30},{"$f":"D202","v":30},{"$f":"E202","v":30},{"$f":"F202","v":30},{"$f":"G202","v":30},null,1,{"$f":"J202","v":30},{"$f":"K202","v":30},{"$f":"L202","v":30},{"$f":"M202","v":30},{"$f":"N202","v":30}]
[null,50,30,30,30,30,30,null,50,{"$f":"C202+Spans!$C$10","v":30},{"$f":"D202+Spans!$C$10","v":30},{"$f":"E202+Spans!$C$10","v":30},{"$f":"F202+Spans!$C$10","v":30},{"$f":"G202+Spans!$C$10","v":30}]
[null,100,30,30,30,30,30,null,100,{"$f":"C203+Spans!$C$10","v":30},{"$f":"D203+Spans!$C$10","v":30},{"$f":"E203+Spans!$C$10","v":30},{"$f":"F203+Spans!$C$10","v":30},{"$f":"G203+Spans!$C$10","v":30}]
[null,150,30,30,30,30,30,null,150,{"$f":"C204+Spans!$C$10","v":30},{"$f":"D204+Spans!$C$10","v":30},{"$f":"E204+Spans!$C$10","v":30},{"$f":"F204+Spans!$C$10","v":30},{"$f":"G204+Spans!$C$10","v":30}]
[null,200,30,30,30,30,30,null,200,{"$f":"C205+Spans!$C$10","v":30},{"$f":"D205+Spans!$C$10","v":30},{"$f":"E205+Spans!$C$10","v":30},{"$f":"F205+Spans!$C$10","v":30},{"$f":"G205+Spans!$C$10","v":30}]
[null,300,30,30,30,30,30,null,300,{"$f":"C206+Spans!$C$10","v":30},{"$f":"D206+Spans!$C$10","v":30},{"$f":"E206+Spans!$C$10","v":30},{"$f":"F206+Spans!$C$10","v":30},{"$f":"G206+Spans!$C$10","v":30}]
[null,400,30,30,30,30,30,null,400,{"$f":"C207+Spans!$C$10","v":30},{"$f":"D207+Spans!$C$10","v":30},{"$f":"E207+Spans!$C$10","v":30},{"$f":"F207+Spans!$C$10","v":30},{"$f":"G207+Spans!$C$10","v":30}]
[null,500,30,30,30,30,30,null,500,{"$f":"C208+Spans!$C$10","v":30},{"$f":"D208+Spans!$C$10","v":30},{"$f":"E208+Spans!$C$10","v":30},{"$f":"F208+Spans!$C$10","v":30},{"$f":"G208+Spans!$C$10","v":30}]
[null,1000,{"$f":"C208","v":30},{"$f":"D208","v":30},{"$f":"E208","v":30},{"$f":"F208","v":30},{"$f":"G208","v":30},null,1000,{"$f":"J208","v":30},{"$f":"K208","v":30},{"$f":"L208","v":30},{"$f":"M208","v":30},{"$f":"N208","v":30}]
[]
[null,null,null,null,null,null,null,null,"TABLE",16]
[null,"FEA Table:","Composite, 715.5 AAC XLPE, Blue Gum / Eucalyptus",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C216","v":30},{"$f":"D216","v":30},{"$f":"E216","v":30},{"$f":"F216","v":30},{"$f":"G216","v":30},null,1,{"$f":"J216","v":30},{"$f":"K216","v":30},{"$f":"L216","v":30},{"$f":"M216","v":30},{"$f":"N216","v":30}]
[null,50,30,30,30,30,30,null,50,{"$f":"C216+Spans!$C$10","v":30},{"$f":"D216+Spans!$C$10","v":30},{"$f":"E216+Spans!$C$10","v":30},{"$f":"F216+Spans!$C$10","v":30},{"$f":"G216+Spans!$C$10","v":30}]
[null,100,30,30,30,30,30,null,100,{"$f":"C217+Spans!$C$10","v":30},{"$f":"D217+Spans!$C$10","v":30},{"$f":"E217+Spans!$C$10","v":30},{"$f":"F217+Spans!$C$10","v":30},{"$f":"G217+Spans!$C$10","v":30}]
[null,150,30,30,30,30,30,null,150,{"$f":"C218+Spans!$C$10","v":30},{"$f":"D218+Spans!$C$10","v":30},{"$f":"E218+Spans!$C$10","v":30},{"$f":"F218+Spans!$C$10","v":30},{"$f":"G218+Spans!$C$10","v":30}]
[null,200,30,30,30,30,30,null,200,{"$f":"C219+Spans!$C$10","v":30},{"$f":"D219+Spans!$C$10","v":30},{"$f":"E219+Spans!$C$10","v":30},{"$f":"F219+Spans!$C$10","v":30},{"$f":"G219+Spans!$C$10","v":30}]
[null,300,30,30,30,30,30,null,300,{"$f":"C220+Spans!$C$10","v":30},{"$f":"D220+Spans!$C$10","v":30},{"$f":"E220+Spans!$C$10","v":30},{"$f":"F220+Spans!$C$10","v":30},{"$f":"G220+Spans!$C$10","v":30}]
[null,400,30,30,30,30,30,null,400,{"$f":"C221+Spans!$C$10","v":30},{"$f":"D221+Spans!$C$10","v":30},{"$f":"E221+Spans!$C$10","v":30},{"$f":"F221+Spans!$C$10","v":30},{"$f":"G221+Spans!$C$10","v":30}]
[null,500,30,30,30,30,30,null,500,{"$f":"C222+Spans!$C$10","v":30},{"$f":"D222+Spans!$C$10","v":30},{"$f":"E222+Spans!$C$10","v":30},{"$f":"F222+Spans!$C$10","v":30},{"$f":"G222+Spans!$C$10","v":30}]
[null,1000,{"$f":"C222","v":30},{"$f":"D222","v":30},{"$f":"E222","v":30},{"$f":"F222","v":30},{"$f":"G222","v":30},null,1000,{"$f":"J222","v":30},{"$f":"K222","v":30},{"$f":"L222","v":30},{"$f":"M222","v":30},{"$f":"N222","v":30}]
[]
[null,null,null,null,null,null,null,null,"TABLE",17]
[null,"Base Table:",null,null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C230","v":0},{"$f":"D230","v":0},{"$f":"E230","v":0},{"$f":"F230","v":0},{"$f":"G230","v":0},null,1,{"$f":"J230","v":0},{"$f":"K230","v":0},{"$f":"L230","v":0},{"$f":"M230","v":0},{"$f":"N230","v":0}]
[null,50,null,null,null,null,null,null,50,{"$f":"C230+Spans!$C$10","v":0},{"$f":"D230+Spans!$C$10","v":0},{"$f":"E230+Spans!$C$10","v":0},{"$f":"F230+Spans!$C$10","v":0},{"$f":"G230+Spans!$C$10","v":0}]
[null,100,null,null,null,null,null,null,100,{"$f":"C231+Spans!$C$10","v":0},{"$f":"D231+Spans!$C$10","v":0},{"$f":"E231+Spans!$C$10","v":0},{"$f":"F231+Spans!$C$10","v":0},{"$f":"G231+Spans!$C$10","v":0}]
[null,150,null,null,null,null,null,null,150,{"$f":"C232+Spans!$C$10","v":0},{"$f":"D232+Spans!$C$10","v":0},{"$f":"E232+Spans!$C$10","v":0},{"$f":"F232+Spans!$C$10","v":0},{"$f":"G232+Spans!$C$10","v":0}]
[null,200,null,null,null,null,null,null,200,{"$f":"C233+Spans!$C$10","v":0},{"$f":"D233+Spans!$C$10","v":0},{"$f":"E233+Spans!$C$10","v":0},{"$f":"F233+Spans!$C$10","v":0},{"$f":"G233+Spans!$C$10","v":0}]
[null,300,null,null,null,null,null,null,300,{"$f":"C234+Spans!$C$10","v":0},{"$f":"D234+Spans!$C$10","v":0},{"$f":"E234+Spans!$C$10","v":0},{"$f":"F234+Spans!$C$10","v":0},{"$f":"G234+Spans!$C$10","v":0}]
[null,400,null,null,null,null,null,null,400,{"$f":"C235+Spans!$C$10","v":0},{"$f":"D235+Spans!$C$10","v":0},{"$f":"E235+Spans!$C$10","v":0},{"$f":"F235+Spans!$C$10","v":0},{"$f":"G235+Spans!$C$10","v":0}]
[null,500,null,null,null,null,null,null,500,{"$f":"C236+Spans!$C$10","v":0},{"$f":"D236+Spans!$C$10","v":0},{"$f":"E236+Spans!$C$10","v":0},{"$f":"F236+Spans!$C$10","v":0},{"$f":"G236+Spans!$C$10","v":0}]
[null,1000,{"$f":"C236","v":0},{"$f":"D236","v":0},{"$f":"E236","v":0},{"$f":"F236","v":0},{"$f":"G236","v":0},null,1000,{"$f":"J236","v":0},{"$f":"K236","v":0},{"$f":"L236","v":0},{"$f":"M236","v":0},{"$f":"N236","v":0}]
[]
[null,null,null,null,null,null,null,null,"TABLE",18]
[null,"FEA Table:",null,null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C244","v":0},{"$f":"D244","v":0},{"$f":"E244","v":0},{"$f":"F244","v":0},{"$f":"G244","v":0},null,1,{"$f":"J244","v":0},{"$f":"K244","v":0},{"$f":"L244","v":0},{"$f":"M244","v":0},{"$f":"N244","v":0}]
[null,50,null,null,null,null,null,null,50,{"$f":"C244+Spans!$C$10","v":0},{"$f":"D244+Spans!$C$10","v":0},{"$f":"E244+Spans!$C$10","v":0},{"$f":"F244+Spans!$C$10","v":0},{"$f":"G244+Spans!$C$10","v":0}]
[null,100,null,null,null,null,null,null,100,{"$f":"C245+Spans!$C$10","v":0},{"$f":"D245+Spans!$C$10","v":0},{"$f":"E245+Spans!$C$10","v":0},{"$f":"F245+Spans!$C$10","v":0},{"$f":"G245+Spans!$C$10","v":0}]
[null,150,null,null,null,null,null,null,150,{"$f":"C246+Spans!$C$10","v":0},{"$f":"D246+Spans!$C$10","v":0},{"$f":"E246+Spans!$C$10","v":0},{"$f":"F246+Spans!$C$10","v":0},{"$f":"G246+Spans!$C$10","v":0}]
[null,200,null,null,null,null,null,null,200,{"$f":"C247+Spans!$C$10","v":0},{"$f":"D247+Spans!$C$10","v":0},{"$f":"E247+Spans!$C$10","v":0},{"$f":"F247+Spans!$C$10","v":0},{"$f":"G247+Spans!$C$10","v":0}]
[null,300,null,null,null,null,null,null,300,{"$f":"C248+Spans!$C$10","v":0},{"$f":"D248+Spans!$C$10","v":0},{"$f":"E248+Spans!$C$10","v":0},{"$f":"F248+Spans!$C$10","v":0},{"$f":"G248+Spans!$C$10","v":0}]
[null,400,null,null,null,null,null,null,400,{"$f":"C249+Spans!$C$10","v":0},{"$f":"D249+Spans!$C$10","v":0},{"$f":"E249+Spans!$C$10","v":0},{"$f":"F249+Spans!$C$10","v":0},{"$f":"G249+Spans!$C$10","v":0}]
[null,500,null,null,null,null,null,null,500,{"$f":"C250+Spans!$C$10","v":0},{"$f":"D250+Spans!$C$10","v":0},{"$f":"E250+Spans!$C$10","v":0},{"$f":"F250+Spans!$C$10","v":0},{"$f":"G250+Spans!$C$10","v":0}]
[null,1000,{"$f":"C250","v":0},{"$f":"D250","v":0},{"$f":"E250","v":0},{"$f":"F250","v":0},{"$f":"G250","v":0},null,1000,{"$f":"J250","v":0},{"$f":"K250","v":0},{"$f":"L250","v":0},{"$f":"M250","v":0},{"$f":"N250","v":0}]
[]
[null,null,null,null,null,null,null,null,"TABLE",19]
[null,"FEA Table:",null,null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C258","v":0},{"$f":"D258","v":0},{"$f":"E258","v":0},{"$f":"F258","v":0},{"$f":"G258","v":0},null,1,{"$f":"J258","v":0},{"$f":"K258","v":0},{"$f":"L258","v":0},{"$f":"M258","v":0},{"$f":"N258","v":0}]
[null,50,null,null,null,null,null,null,50,{"$f":"C258+Spans!$C$10","v":0},{"$f":"D258+Spans!$C$10","v":0},{"$f":"E258+Spans!$C$10","v":0},{"$f":"F258+Spans!$C$10","v":0},{"$f":"G258+Spans!$C$10","v":0}]
[null,100,null,null,null,null,null,null,100,{"$f":"C259+Spans!$C$10","v":0},{"$f":"D259+Spans!$C$10","v":0},{"$f":"E259+Spans!$C$10","v":0},{"$f":"F259+Spans!$C$10","v":0},{"$f":"G259+Spans!$C$10","v":0}]
[null,150,null,null,null,null,null,null,150,{"$f":"C260+Spans!$C$10","v":0},{"$f":"D260+Spans!$C$10","v":0},{"$f":"E260+Spans!$C$10","v":0},{"$f":"F260+Spans!$C$10","v":0},{"$f":"G260+Spans!$C$10","v":0}]
[null,200,null,null,null,null,null,null,200,{"$f":"C261+Spans!$C$10","v":0},{"$f":"D261+Spans!$C$10","v":0},{"$f":"E261+Spans!$C$10","v":0},{"$f":"F261+Spans!$C$10","v":0},{"$f":"G261+Spans!$C$10","v":0}]
[null,300,null,null,null,null,null,null,300,{"$f":"C262+Spans!$C$10","v":0},{"$f":"D262+Spans!$C$10","v":0},{"$f":"E262+Spans!$C$10","v":0},{"$f":"F262+Spans!$C$10","v":0},{"$f":"G262+Spans!$C$10","v":0}]
[null,400,null,null,null,null,null,null,400,{"$f":"C263+Spans!$C$10","v":0},{"$f":"D263+Spans!$C$10","v":0},{"$f":"E263+Spans!$C$10","v":0},{"$f":"F263+Spans!$C$10","v":0},{"$f":"G263+Spans!$C$10","v":0}]
[null,500,null,null,null,null,null,null,500,{"$f":"C264+Spans!$C$10","v":0},{"$f":"D264+Spans!$C$10","v":0},{"$f":"E264+Spans!$C$10","v":0},{"$f":"F264+Spans!$C$10","v":0},{"$f":"G264+Spans!$C$10","v":0}]
[null,1000,{"$f":"C264","v":0},{"$f":"D264","v":0},{"$f":"E264","v":0},{"$f":"F264","v":0},{"$f":"G264","v":0},null,1000,{"$f":"J264","v":0},{"$f":"K264","v":0},{"$f":"L264","v":0},{"$f":"M264","v":0},{"$f":"N264","v":0}]
[]
[null,null,null,null,null,null,null,null,"TABLE",20]
[null,"FEA Table:",null,null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C272","v":0},{"$f":"D272","v":0},{"$f":"E272","v":0},{"$f":"F272","v":0},{"$f":"G272","v":0},null,1,{"$f":"J272","v":0},{"$f":"K272","v":0},{"$f":"L272","v":0},{"$f":"M272","v":0},{"$f":"N272","v":0}]
[null,50,null,null,null,null,null,null,50,{"$f":"C272+Spans!$C$10","v":0},{"$f":"D272+Spans!$C$10","v":0},{"$f":"E272+Spans!$C$10","v":0},{"$f":"F272+Spans!$C$10","v":0},{"$f":"G272+Spans!$C$10","v":0}]
[null,100,null,null,null,null,null,null,100,{"$f":"C273+Spans!$C$10","v":0},{"$f":"D273+Spans!$C$10","v":0},{"$f":"E273+Spans!$C$10","v":0},{"$f":"F273+Spans!$C$10","v":0},{"$f":"G273+Spans!$C$10","v":0}]
[null,150,null,null,null,null,null,null,150,{"$f":"C274+Spans!$C$10","v":0},{"$f":"D274+Spans!$C$10","v":0},{"$f":"E274+Spans!$C$10","v":0},{"$f":"F274+Spans!$C$10","v":0},{"$f":"G274+Spans!$C$10","v":0}]
[null,200,null,null,null,null,null,null,200,{"$f":"C275+Spans!$C$10","v":0},{"$f":"D275+Spans!$C$10","v":0},{"$f":"E275+Spans!$C$10","v":0},{"$f":"F275+Spans!$C$10","v":0},{"$f":"G275+Spans!$C$10","v":0}]
[null,300,null,null,null,null,null,null,300,{"$f":"C276+Spans!$C$10","v":0},{"$f":"D276+Spans!$C$10","v":0},{"$f":"E276+Spans!$C$10","v":0},{"$f":"F276+Spans!$C$10","v":0},{"$f":"G276+Spans!$C$10","v":0}]
[null,400,null,null,null,null,null,null,400,{"$f":"C277+Spans!$C$10","v":0},{"$f":"D277+Spans!$C$10","v":0},{"$f":"E277+Spans!$C$10","v":0},{"$f":"F277+Spans!$C$10","v":0},{"$f":"G277+Spans!$C$10","v":0}]
[null,500,null,null,null,null,null,null,500,{"$f":"C278+Spans!$C$10","v":0},{"$f":"D278+Spans!$C$10","v":0},{"$f":"E278+Spans!$C$10","v":0},{"$f":"F278+Spans!$C$10","v":0},{"$f":"G278+Spans!$C$10","v":0}]
[null,1000,{"$f":"C278","v":0},{"$f":"D278","v":0},{"$f":"E278","v":0},{"$f":"F278","v":0},{"$f":"G278","v":0},null,1000,{"$f":"J278","v":0},{"$f":"K278","v":0},{"$f":"L278","v":0},{"$f":"M278","v":0},{"$f":"N278","v":0}]
[]
[null,null,null,null,null,null,null,null,"TABLE",21]
[null,"FEA Table:","Wood, #6 Cu, Douglas Fir",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C286","v":2},{"$f":"D286","v":2},{"$f":"E286","v":2},{"$f":"F286","v":2},{"$f":"G286","v":2},null,1,{"$f":"J286","v":2},{"$f":"K286","v":2},{"$f":"L286","v":2},{"$f":"M286","v":2},{"$f":"N286","v":2}]
[null,50,2,2,2,2,2,null,50,{"$f":"C286+Spans!$C$10","v":2},{"$f":"D286+Spans!$C$10","v":2},{"$f":"E286+Spans!$C$10","v":2},{"$f":"F286+Spans!$C$10","v":2},{"$f":"G286+Spans!$C$10","v":2}]
[null,100,2,2,2,2,2,null,100,{"$f":"C287+Spans!$C$10","v":2},{"$f":"D287+Spans!$C$10","v":2},{"$f":"E287+Spans!$C$10","v":2},{"$f":"F287+Spans!$C$10","v":2},{"$f":"G287+Spans!$C$10","v":2}]
[null,150,2,2,2,2,2,null,150,{"$f":"C288+Spans!$C$10","v":2},{"$f":"D288+Spans!$C$10","v":2},{"$f":"E288+Spans!$C$10","v":2},{"$f":"F288+Spans!$C$10","v":2},{"$f":"G288+Spans!$C$10","v":2}]
[null,200,2,2,2,2,2,null,200,{"$f":"C289+Spans!$C$10","v":2},{"$f":"D289+Spans!$C$10","v":2},{"$f":"E289+Spans!$C$10","v":2},{"$f":"F289+Spans!$C$10","v":2},{"$f":"G289+Spans!$C$10","v":2}]
[null,300,2,2,2,2,2,null,300,{"$f":"C290+Spans!$C$10","v":2},{"$f":"D290+Spans!$C$10","v":2},{"$f":"E290+Spans!$C$10","v":2},{"$f":"F290+Spans!$C$10","v":2},{"$f":"G290+Spans!$C$10","v":2}]
[null,400,2,2,2,2,2,null,400,{"$f":"C291+Spans!$C$10","v":2},{"$f":"D291+Spans!$C$10","v":2},{"$f":"E291+Spans!$C$10","v":2},{"$f":"F291+Spans!$C$10","v":2},{"$f":"G291+Spans!$C$10","v":2}]
[null,500,2,2,2,2,2,null,500,{"$f":"C292+Spans!$C$10","v":2},{"$f":"D292+Spans!$C$10","v":2},{"$f":"E292+Spans!$C$10","v":2},{"$f":"F292+Spans!$C$10","v":2},{"$f":"G292+Spans!$C$10","v":2}]
[null,1000,{"$f":"C292","v":2},{"$f":"D292","v":2},{"$f":"E292","v":2},{"$f":"F292","v":2},{"$f":"G292","v":2},null,1000,{"$f":"J292","v":2},{"$f":"K292","v":2},{"$f":"L292","v":2},{"$f":"M292","v":2},{"$f":"N292","v":2}]
[]
[null,null,null,null,null,null,null,null,"TABLE",22]
[null,"FEA Table:","Wood, #6 Cu, Pine",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C300","v":2},{"$f":"D300","v":2},{"$f":"E300","v":2},{"$f":"F300","v":2},{"$f":"G300","v":2},null,1,{"$f":"J300","v":2},{"$f":"K300","v":2},{"$f":"L300","v":2},{"$f":"M300","v":2},{"$f":"N300","v":2}]
[null,50,2,2,2,2,2,null,50,{"$f":"C300+Spans!$C$10","v":2},{"$f":"D300+Spans!$C$10","v":2},{"$f":"E300+Spans!$C$10","v":2},{"$f":"F300+Spans!$C$10","v":2},{"$f":"G300+Spans!$C$10","v":2}]
[null,100,2,2,2,2,2,null,100,{"$f":"C301+Spans!$C$10","v":2},{"$f":"D301+Spans!$C$10","v":2},{"$f":"E301+Spans!$C$10","v":2},{"$f":"F301+Spans!$C$10","v":2},{"$f":"G301+Spans!$C$10","v":2}]
[null,150,2,2,2,2,2,null,150,{"$f":"C302+Spans!$C$10","v":2},{"$f":"D302+Spans!$C$10","v":2},{"$f":"E302+Spans!$C$10","v":2},{"$f":"F302+Spans!$C$10","v":2},{"$f":"G302+Spans!$C$10","v":2}]
[null,200,2,2,2,2,2,null,200,{"$f":"C303+Spans!$C$10","v":2},{"$f":"D303+Spans!$C$10","v":2},{"$f":"E303+Spans!$C$10","v":2},{"$f":"F303+Spans!$C$10","v":2},{"$f":"G303+Spans!$C$10","v":2}]
[null,300,2,2,2,2,2,null,300,{"$f":"C304+Spans!$C$10","v":2},{"$f":"D304+Spans!$C$10","v":2},{"$f":"E304+Spans!$C$10","v":2},{"$f":"F304+Spans!$C$10","v":2},{"$f":"G304+Spans!$C$10","v":2}]
[null,400,2,2,2,2,2,null,400,{"$f":"C305+Spans!$C$10","v":2},{"$f":"D305+Spans!$C$10","v":2},{"$f":"E305+Spans!$C$10","v":2},{"$f":"F305+Spans!$C$10","v":2},{"$f":"G305+Spans!$C$10","v":2}]
[null,500,2,2,2,2,2,null,500,{"$f":"C306+Spans!$C$10","v":2},{"$f":"D306+Spans!$C$10","v":2},{"$f":"E306+Spans!$C$10","v":2},{"$f":"F306+Spans!$C$10","v":2},{"$f":"G306+Spans!$C$10","v":2}]
[null,1000,{"$f":"C306","v":2},{"$f":"D306","v":2},{"$f":"E306","v":2},{"$f":"F306","v":2},{"$f":"G306","v":2},null,1000,{"$f":"J306","v":2},{"$f":"K306","v":2},{"$f":"L306","v":2},{"$f":"M306","v":2},{"$f":"N306","v":2}]
[]
[null,null,null,null,null,null,null,null,"TABLE",23]
[null,"FEA Table:","Wood, #6 Cu, Oak",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C314","v":17},{"$f":"D314","v":17},{"$f":"E314","v":17},{"$f":"F314","v":17},{"$f":"G314","v":17},null,1,{"$f":"J314","v":17},{"$f":"K314","v":17},{"$f":"L314","v":17},{"$f":"M314","v":17},{"$f":"N314","v":17}]
[null,50,17,17,17,17,17,null,50,{"$f":"C314+Spans!$C$10","v":17},{"$f":"D314+Spans!$C$10","v":17},{"$f":"E314+Spans!$C$10","v":17},{"$f":"F314+Spans!$C$10","v":17},{"$f":"G314+Spans!$C$10","v":17}]
[null,100,17,17,17,17,17,null,100,{"$f":"C315+Spans!$C$10","v":17},{"$f":"D315+Spans!$C$10","v":17},{"$f":"E315+Spans!$C$10","v":17},{"$f":"F315+Spans!$C$10","v":17},{"$f":"G315+Spans!$C$10","v":17}]
[null,150,17,17,17,17,17,null,150,{"$f":"C316+Spans!$C$10","v":17},{"$f":"D316+Spans!$C$10","v":17},{"$f":"E316+Spans!$C$10","v":17},{"$f":"F316+Spans!$C$10","v":17},{"$f":"G316+Spans!$C$10","v":17}]
[null,200,17,17,17,17,17,null,200,{"$f":"C317+Spans!$C$10","v":17},{"$f":"D317+Spans!$C$10","v":17},{"$f":"E317+Spans!$C$10","v":17},{"$f":"F317+Spans!$C$10","v":17},{"$f":"G317+Spans!$C$10","v":17}]
[null,300,17,17,17,17,17,null,300,{"$f":"C318+Spans!$C$10","v":17},{"$f":"D318+Spans!$C$10","v":17},{"$f":"E318+Spans!$C$10","v":17},{"$f":"F318+Spans!$C$10","v":17},{"$f":"G318+Spans!$C$10","v":17}]
[null,400,17,17,17,17,17,null,400,{"$f":"C319+Spans!$C$10","v":17},{"$f":"D319+Spans!$C$10","v":17},{"$f":"E319+Spans!$C$10","v":17},{"$f":"F319+Spans!$C$10","v":17},{"$f":"G319+Spans!$C$10","v":17}]
[null,500,17,17,17,17,17,null,500,{"$f":"C320+Spans!$C$10","v":17},{"$f":"D320+Spans!$C$10","v":17},{"$f":"E320+Spans!$C$10","v":17},{"$f":"F320+Spans!$C$10","v":17},{"$f":"G320+Spans!$C$10","v":17}]
[null,1000,{"$f":"C320","v":17},{"$f":"D320","v":17},{"$f":"E320","v":17},{"$f":"F320","v":17},{"$f":"G320","v":17},null,1000,{"$f":"J320","v":17},{"$f":"K320","v":17},{"$f":"L320","v":17},{"$f":"M320","v":17},{"$f":"N320","v":17}]
[]
[null,null,null,null,null,null,null,null,"TABLE",24]
[null,"FEA Table:","Wood, #6 Cu, Blue Gum / Eucalyptus",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C328","v":17},{"$f":"D328","v":17},{"$f":"E328","v":17},{"$f":"F328","v":17},{"$f":"G328","v":17},null,1,{"$f":"J328","v":17},{"$f":"K328","v":17},{"$f":"L328","v":17},{"$f":"M328","v":17},{"$f":"N328","v":17}]
[null,50,17,17,17,17,17,null,50,{"$f":"C328+Spans!$C$10","v":17},{"$f":"D328+Spans!$C$10","v":17},{"$f":"E328+Spans!$C$10","v":17},{"$f":"F328+Spans!$C$10","v":17},{"$f":"G328+Spans!$C$10","v":17}]
[null,100,17,17,17,17,17,null,100,{"$f":"C329+Spans!$C$10","v":17},{"$f":"D329+Spans!$C$10","v":17},{"$f":"E329+Spans!$C$10","v":17},{"$f":"F329+Spans!$C$10","v":17},{"$f":"G329+Spans!$C$10","v":17}]
[null,150,17,17,17,17,17,null,150,{"$f":"C330+Spans!$C$10","v":17},{"$f":"D330+Spans!$C$10","v":17},{"$f":"E330+Spans!$C$10","v":17},{"$f":"F330+Spans!$C$10","v":17},{"$f":"G330+Spans!$C$10","v":17}]
[null,200,17,17,17,17,17,null,200,{"$f":"C331+Spans!$C$10","v":17},{"$f":"D331+Spans!$C$10","v":17},{"$f":"E331+Spans!$C$10","v":17},{"$f":"F331+Spans!$C$10","v":17},{"$f":"G331+Spans!$C$10","v":17}]
[null,300,17,17,17,17,17,null,300,{"$f":"C332+Spans!$C$10","v":17},{"$f":"D332+Spans!$C$10","v":17},{"$f":"E332+Spans!$C$10","v":17},{"$f":"F332+Spans!$C$10","v":17},{"$f":"G332+Spans!$C$10","v":17}]
[null,400,17,17,17,17,17,null,400,{"$f":"C333+Spans!$C$10","v":17},{"$f":"D333+Spans!$C$10","v":17},{"$f":"E333+Spans!$C$10","v":17},{"$f":"F333+Spans!$C$10","v":17},{"$f":"G333+Spans!$C$10","v":17}]
[null,500,17,17,17,17,17,null,500,{"$f":"C334+Spans!$C$10","v":17},{"$f":"D334+Spans!$C$10","v":17},{"$f":"E334+Spans!$C$10","v":17},{"$f":"F334+Spans!$C$10","v":17},{"$f":"G334+Spans!$C$10","v":17}]
[null,1000,{"$f":"C334","v":17},{"$f":"D334","v":17},{"$f":"E334","v":17},{"$f":"F334","v":17},{"$f":"G334","v":17},null,1000,{"$f":"J334","v":17},{"$f":"K334","v":17},{"$f":"L334","v":17},{"$f":"M334","v":17},{"$f":"N334","v":17}]
[]
[null,null,null,null,null,null,null,null,"TABLE",25]
[null,"FEA Table:","Wood, 4 (6/1) ACSR, Douglas Fir",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C342","v":2},{"$f":"D342","v":2},{"$f":"E342","v":2},{"$f":"F342","v":2},{"$f":"G342","v":2},null,1,{"$f":"J342","v":2},{"$f":"K342","v":2},{"$f":"L342","v":2},{"$f":"M342","v":2},{"$f":"N342","v":2}]
[null,50,2,2,2,2,2,null,50,{"$f":"C342+Spans!$C$10","v":2},{"$f":"D342+Spans!$C$10","v":2},{"$f":"E342+Spans!$C$10","v":2},{"$f":"F342+Spans!$C$10","v":2},{"$f":"G342+Spans!$C$10","v":2}]
[null,100,2,2,2,2,2,null,100,{"$f":"C343+Spans!$C$10","v":2},{"$f":"D343+Spans!$C$10","v":2},{"$f":"E343+Spans!$C$10","v":2},{"$f":"F343+Spans!$C$10","v":2},{"$f":"G343+Spans!$C$10","v":2}]
[null,150,2,2,2,2,2,null,150,{"$f":"C344+Spans!$C$10","v":2},{"$f":"D344+Spans!$C$10","v":2},{"$f":"E344+Spans!$C$10","v":2},{"$f":"F344+Spans!$C$10","v":2},{"$f":"G344+Spans!$C$10","v":2}]
[null,200,2,2,2,2,2,null,200,{"$f":"C345+Spans!$C$10","v":2},{"$f":"D345+Spans!$C$10","v":2},{"$f":"E345+Spans!$C$10","v":2},{"$f":"F345+Spans!$C$10","v":2},{"$f":"G345+Spans!$C$10","v":2}]
[null,300,2,2,2,2,2,null,300,{"$f":"C346+Spans!$C$10","v":2},{"$f":"D346+Spans!$C$10","v":2},{"$f":"E346+Spans!$C$10","v":2},{"$f":"F346+Spans!$C$10","v":2},{"$f":"G346+Spans!$C$10","v":2}]
[null,400,2,2,2,2,2,null,400,{"$f":"C347+Spans!$C$10","v":2},{"$f":"D347+Spans!$C$10","v":2},{"$f":"E347+Spans!$C$10","v":2},{"$f":"F347+Spans!$C$10","v":2},{"$f":"G347+Spans!$C$10","v":2}]
[null,500,2,2,2,2,2,null,500,{"$f":"C348+Spans!$C$10","v":2},{"$f":"D348+Spans!$C$10","v":2},{"$f":"E348+Spans!$C$10","v":2},{"$f":"F348+Spans!$C$10","v":2},{"$f":"G348+Spans!$C$10","v":2}]
[null,1000,{"$f":"C348","v":2},{"$f":"D348","v":2},{"$f":"E348","v":2},{"$f":"F348","v":2},{"$f":"G348","v":2},null,1000,{"$f":"J348","v":2},{"$f":"K348","v":2},{"$f":"L348","v":2},{"$f":"M348","v":2},{"$f":"N348","v":2}]
[]
[null,null,null,null,null,null,null,null,"TABLE",26]
[null,"FEA Table:","Wood, 4 (6/1) ACSR, Pine",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C356","v":2},{"$f":"D356","v":2},{"$f":"E356","v":2},{"$f":"F356","v":2},{"$f":"G356","v":2},null,1,{"$f":"J356","v":2},{"$f":"K356","v":2},{"$f":"L356","v":2},{"$f":"M356","v":2},{"$f":"N356","v":2}]
[null,50,2,2,2,2,2,null,50,{"$f":"C356+Spans!$C$10","v":2},{"$f":"D356+Spans!$C$10","v":2},{"$f":"E356+Spans!$C$10","v":2},{"$f":"F356+Spans!$C$10","v":2},{"$f":"G356+Spans!$C$10","v":2}]
[null,100,2,2,2,2,2,null,100,{"$f":"C357+Spans!$C$10","v":2},{"$f":"D357+Spans!$C$10","v":2},{"$f":"E357+Spans!$C$10","v":2},{"$f":"F357+Spans!$C$10","v":2},{"$f":"G357+Spans!$C$10","v":2}]
[null,150,2,2,2,2,2,null,150,{"$f":"C358+Spans!$C$10","v":2},{"$f":"D358+Spans!$C$10","v":2},{"$f":"E358+Spans!$C$10","v":2},{"$f":"F358+Spans!$C$10","v":2},{"$f":"G358+Spans!$C$10","v":2}]
[null,200,2,2,2,2,2,null,200,{"$f":"C359+Spans!$C$10","v":2},{"$f":"D359+Spans!$C$10","v":2},{"$f":"E359+Spans!$C$10","v":2},{"$f":"F359+Spans!$C$10","v":2},{"$f":"G359+Spans!$C$10","v":2}]
[null,300,2,2,2,2,2,null,300,{"$f":"C360+Spans!$C$10","v":2},{"$f":"D360+Spans!$C$10","v":2},{"$f":"E360+Spans!$C$10","v":2},{"$f":"F360+Spans!$C$10","v":2},{"$f":"G360+Spans!$C$10","v":2}]
[null,400,2,2,2,2,2,null,400,{"$f":"C361+Spans!$C$10","v":2},{"$f":"D361+Spans!$C$10","v":2},{"$f":"E361+Spans!$C$10","v":2},{"$f":"F361+Spans!$C$10","v":2},{"$f":"G361+Spans!$C$10","v":2}]
[null,500,2,2,2,2,2,null,500,{"$f":"C362+Spans!$C$10","v":2},{"$f":"D362+Spans!$C$10","v":2},{"$f":"E362+Spans!$C$10","v":2},{"$f":"F362+Spans!$C$10","v":2},{"$f":"G362+Spans!$C$10","v":2}]
[null,1000,{"$f":"C362","v":2},{"$f":"D362","v":2},{"$f":"E362","v":2},{"$f":"F362","v":2},{"$f":"G362","v":2},null,1000,{"$f":"J362","v":2},{"$f":"K362","v":2},{"$f":"L362","v":2},{"$f":"M362","v":2},{"$f":"N362","v":2}]
[]
[null,null,null,null,null,null,null,null,"TABLE",27]
[null,"FEA Table:","Wood, 4 (6/1) ACSR, Oak",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C370","v":17},{"$f":"D370","v":17},{"$f":"E370","v":17},{"$f":"F370","v":17},{"$f":"G370","v":17},null,1,{"$f":"J370","v":17},{"$f":"K370","v":17},{"$f":"L370","v":17},{"$f":"M370","v":17},{"$f":"N370","v":17}]
[null,50,17,17,17,17,17,null,50,{"$f":"C370+Spans!$C$10","v":17},{"$f":"D370+Spans!$C$10","v":17},{"$f":"E370+Spans!$C$10","v":17},{"$f":"F370+Spans!$C$10","v":17},{"$f":"G370+Spans!$C$10","v":17}]
[null,100,17,17,17,17,17,null,100,{"$f":"C371+Spans!$C$10","v":17},{"$f":"D371+Spans!$C$10","v":17},{"$f":"E371+Spans!$C$10","v":17},{"$f":"F371+Spans!$C$10","v":17},{"$f":"G371+Spans!$C$10","v":17}]
[null,150,17,17,17,17,17,null,150,{"$f":"C372+Spans!$C$10","v":17},{"$f":"D372+Spans!$C$10","v":17},{"$f":"E372+Spans!$C$10","v":17},{"$f":"F372+Spans!$C$10","v":17},{"$f":"G372+Spans!$C$10","v":17}]
[null,200,17,17,17,17,17,null,200,{"$f":"C373+Spans!$C$10","v":17},{"$f":"D373+Spans!$C$10","v":17},{"$f":"E373+Spans!$C$10","v":17},{"$f":"F373+Spans!$C$10","v":17},{"$f":"G373+Spans!$C$10","v":17}]
[null,300,17,17,17,17,17,null,300,{"$f":"C374+Spans!$C$10","v":17},{"$f":"D374+Spans!$C$10","v":17},{"$f":"E374+Spans!$C$10","v":17},{"$f":"F374+Spans!$C$10","v":17},{"$f":"G374+Spans!$C$10","v":17}]
[null,400,17,17,17,17,17,null,400,{"$f":"C375+Spans!$C$10","v":17},{"$f":"D375+Spans!$C$10","v":17},{"$f":"E375+Spans!$C$10","v":17},{"$f":"F375+Spans!$C$10","v":17},{"$f":"G375+Spans!$C$10","v":17}]
[null,500,17,17,17,17,17,null,500,{"$f":"C376+Spans!$C$10","v":17},{"$f":"D376+Spans!$C$10","v":17},{"$f":"E376+Spans!$C$10","v":17},{"$f":"F376+Spans!$C$10","v":17},{"$f":"G376+Spans!$C$10","v":17}]
[null,1000,{"$f":"C376","v":17},{"$f":"D376","v":17},{"$f":"E376","v":17},{"$f":"F376","v":17},{"$f":"G376","v":17},null,1000,{"$f":"J376","v":17},{"$f":"K376","v":17},{"$f":"L376","v":17},{"$f":"M376","v":17},{"$f":"N376","v":17}]
[]
[null,null,null,null,null,null,null,null,"TABLE",28]
[null,"FEA Table:","Wood, 4 (6/1) ACSR, Blue Gum / Eucalyptus",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C384","v":17},{"$f":"D384","v":17},{"$f":"E384","v":17},{"$f":"F384","v":17},{"$f":"G384","v":17},null,1,{"$f":"J384","v":17},{"$f":"K384","v":17},{"$f":"L384","v":17},{"$f":"M384","v":17},{"$f":"N384","v":17}]
[null,50,17,17,17,17,17,null,50,{"$f":"C384+Spans!$C$10","v":17},{"$f":"D384+Spans!$C$10","v":17},{"$f":"E384+Spans!$C$10","v":17},{"$f":"F384+Spans!$C$10","v":17},{"$f":"G384+Spans!$C$10","v":17}]
[null,100,17,17,17,17,17,null,100,{"$f":"C385+Spans!$C$10","v":17},{"$f":"D385+Spans!$C$10","v":17},{"$f":"E385+Spans!$C$10","v":17},{"$f":"F385+Spans!$C$10","v":17},{"$f":"G385+Spans!$C$10","v":17}]
[null,150,17,17,17,17,17,null,150,{"$f":"C386+Spans!$C$10","v":17},{"$f":"D386+Spans!$C$10","v":17},{"$f":"E386+Spans!$C$10","v":17},{"$f":"F386+Spans!$C$10","v":17},{"$f":"G386+Spans!$C$10","v":17}]
[null,200,17,17,17,17,17,null,200,{"$f":"C387+Spans!$C$10","v":17},{"$f":"D387+Spans!$C$10","v":17},{"$f":"E387+Spans!$C$10","v":17},{"$f":"F387+Spans!$C$10","v":17},{"$f":"G387+Spans!$C$10","v":17}]
[null,300,17,17,17,17,17,null,300,{"$f":"C388+Spans!$C$10","v":17},{"$f":"D388+Spans!$C$10","v":17},{"$f":"E388+Spans!$C$10","v":17},{"$f":"F388+Spans!$C$10","v":17},{"$f":"G388+Spans!$C$10","v":17}]
[null,400,17,17,17,17,17,null,400,{"$f":"C389+Spans!$C$10","v":17},{"$f":"D389+Spans!$C$10","v":17},{"$f":"E389+Spans!$C$10","v":17},{"$f":"F389+Spans!$C$10","v":17},{"$f":"G389+Spans!$C$10","v":17}]
[null,500,17,17,17,17,17,null,500,{"$f":"C390+Spans!$C$10","v":17},{"$f":"D390+Spans!$C$10","v":17},{"$f":"E390+Spans!$C$10","v":17},{"$f":"F390+Spans!$C$10","v":17},{"$f":"G390+Spans!$C$10","v":17}]
[null,1000,{"$f":"C390","v":17},{"$f":"D390","v":17},{"$f":"E390","v":17},{"$f":"F390","v":17},{"$f":"G390","v":17},null,1000,{"$f":"J390","v":17},{"$f":"K390","v":17},{"$f":"L390","v":17},{"$f":"M390","v":17},{"$f":"N390","v":17}]
[]
[null,null,null,null,null,null,null,null,"TABLE",29]
[null,"FEA Table:","Wood, 2 (7/1) ACSR, Douglas Fir",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C398","v":2},{"$f":"D398","v":2},{"$f":"E398","v":2},{"$f":"F398","v":2},{"$f":"G398","v":2},null,1,{"$f":"J398","v":2},{"$f":"K398","v":2},{"$f":"L398","v":2},{"$f":"M398","v":2},{"$f":"N398","v":2}]
[null,50,2,2,2,2,2,null,50,{"$f":"C398+Spans!$C$10","v":2},{"$f":"D398+Spans!$C$10","v":2},{"$f":"E398+Spans!$C$10","v":2},{"$f":"F398+Spans!$C$10","v":2},{"$f":"G398+Spans!$C$10","v":2}]
[null,100,2,2,10,2,2,null,100,{"$f":"C399+Spans!$C$10","v":2},{"$f":"D399+Spans!$C$10","v":2},{"$f":"E399+Spans!$C$10","v":10},{"$f":"F399+Spans!$C$10","v":2},{"$f":"G399+Spans!$C$10","v":2}]
[null,150,2,8,10,2,6,null,150,{"$f":"C400+Spans!$C$10","v":2},{"$f":"D400+Spans!$C$10","v":8},{"$f":"E400+Spans!$C$10","v":10},{"$f":"F400+Spans!$C$10","v":2},{"$f":"G400+Spans!$C$10","v":6}]
[null,200,7,10,11,2,9,null,200,{"$f":"C401+Spans!$C$10","v":7},{"$f":"D401+Spans!$C$10","v":10},{"$f":"E401+Spans!$C$10","v":11},{"$f":"F401+Spans!$C$10","v":2},{"$f":"G401+Spans!$C$10","v":9}]
[null,300,9,11,12,8,13,null,300,{"$f":"C402+Spans!$C$10","v":9},{"$f":"D402+Spans!$C$10","v":11},{"$f":"E402+Spans!$C$10","v":12},{"$f":"F402+Spans!$C$10","v":8},{"$f":"G402+Spans!$C$10","v":13}]
[null,400,11,11,14,11,13,null,400,{"$f":"C403+Spans!$C$10","v":11},{"$f":"D403+Spans!$C$10","v":11},{"$f":"E403+Spans!$C$10","v":14},{"$f":"F403+Spans!$C$10","v":11},{"$f":"G403+Spans!$C$10","v":13}]
[null,500,13,12,14,13,14,null,500,{"$f":"C404+Spans!$C$10","v":13},{"$f":"D404+Spans!$C$10","v":12},{"$f":"E404+Spans!$C$10","v":14},{"$f":"F404+Spans!$C$10","v":13},{"$f":"G404+Spans!$C$10","v":14}]
[null,1000,{"$f":"C404","v":13},{"$f":"D404","v":12},{"$f":"E404","v":14},{"$f":"F404","v":13},{"$f":"G404","v":14},null,1000,{"$f":"J404","v":13},{"$f":"K404","v":12},{"$f":"L404","v":14},{"$f":"M404","v":13},{"$f":"N404","v":14}]
[]
[null,null,null,null,null,null,null,null,"TABLE",30]
[null,"FEA Table:","Wood, 2 (7/1) ACSR, Pine",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C412","v":2},{"$f":"D412","v":2},{"$f":"E412","v":2},{"$f":"F412","v":7},{"$f":"G412","v":2},null,1,{"$f":"J412","v":2},{"$f":"K412","v":2},{"$f":"L412","v":2},{"$f":"M412","v":7},{"$f":"N412","v":2}]
[null,50,2,2,2,7,2,null,50,{"$f":"C412+Spans!$C$10","v":2},{"$f":"D412+Spans!$C$10","v":2},{"$f":"E412+Spans!$C$10","v":2},{"$f":"F412+Spans!$C$10","v":7},{"$f":"G412+Spans!$C$10","v":2}]
[null,100,2,2,14,10,2,null,100,{"$f":"C413+Spans!$C$10","v":2},{"$f":"D413+Spans!$C$10","v":2},{"$f":"E413+Spans!$C$10","v":14},{"$f":"F413+Spans!$C$10","v":10},{"$f":"G413+Spans!$C$10","v":2}]
[null,150,10,12,19,14,8,null,150,{"$f":"C414+Spans!$C$10","v":10},{"$f":"D414+Spans!$C$10","v":12},{"$f":"E414+Spans!$C$10","v":19},{"$f":"F414+Spans!$C$10","v":14},{"$f":"G414+Spans!$C$10","v":8}]
[null,200,14,17,20,15,15,null,200,{"$f":"C415+Spans!$C$10","v":14},{"$f":"D415+Spans!$C$10","v":17},{"$f":"E415+Spans!$C$10","v":20},{"$f":"F415+Spans!$C$10","v":15},{"$f":"G415+Spans!$C$10","v":15}]
[null,300,16,19,21,16,17,null,300,{"$f":"C416+Spans!$C$10","v":16},{"$f":"D416+Spans!$C$10","v":19},{"$f":"E416+Spans!$C$10","v":21},{"$f":"F416+Spans!$C$10","v":16},{"$f":"G416+Spans!$C$10","v":17}]
[null,400,19,19,21,17,20,null,400,{"$f":"C417+Spans!$C$10","v":19},{"$f":"D417+Spans!$C$10","v":19},{"$f":"E417+Spans!$C$10","v":21},{"$f":"F417+Spans!$C$10","v":17},{"$f":"G417+Spans!$C$10","v":20}]
[null,500,21,21,23,19,22,null,500,{"$f":"C418+Spans!$C$10","v":21},{"$f":"D418+Spans!$C$10","v":21},{"$f":"E418+Spans!$C$10","v":23},{"$f":"F418+Spans!$C$10","v":19},{"$f":"G418+Spans!$C$10","v":22}]
[null,1000,{"$f":"C418","v":21},{"$f":"D418","v":21},{"$f":"E418","v":23},{"$f":"F418","v":19},{"$f":"G418","v":22},null,1000,{"$f":"J418","v":21},{"$f":"K418","v":21},{"$f":"L418","v":23},{"$f":"M418","v":19},{"$f":"N418","v":22}]
[]
[null,null,null,null,null,null,null,null,"TABLE",31]
[null,"FEA Table:","Wood, 2 (7/1) ACSR, Oak",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C426","v":17},{"$f":"D426","v":17},{"$f":"E426","v":17},{"$f":"F426","v":17},{"$f":"G426","v":17},null,1,{"$f":"J426","v":17},{"$f":"K426","v":17},{"$f":"L426","v":17},{"$f":"M426","v":17},{"$f":"N426","v":17}]
[null,50,17,17,17,17,17,null,50,{"$f":"C426+Spans!$C$10","v":17},{"$f":"D426+Spans!$C$10","v":17},{"$f":"E426+Spans!$C$10","v":17},{"$f":"F426+Spans!$C$10","v":17},{"$f":"G426+Spans!$C$10","v":17}]
[null,100,17,17,17,17,17,null,100,{"$f":"C427+Spans!$C$10","v":17},{"$f":"D427+Spans!$C$10","v":17},{"$f":"E427+Spans!$C$10","v":17},{"$f":"F427+Spans!$C$10","v":17},{"$f":"G427+Spans!$C$10","v":17}]
[null,150,17,17,17,17,17,null,150,{"$f":"C428+Spans!$C$10","v":17},{"$f":"D428+Spans!$C$10","v":17},{"$f":"E428+Spans!$C$10","v":17},{"$f":"F428+Spans!$C$10","v":17},{"$f":"G428+Spans!$C$10","v":17}]
[null,200,17,17,17,17,17,null,200,{"$f":"C429+Spans!$C$10","v":17},{"$f":"D429+Spans!$C$10","v":17},{"$f":"E429+Spans!$C$10","v":17},{"$f":"F429+Spans!$C$10","v":17},{"$f":"G429+Spans!$C$10","v":17}]
[null,300,17,17,17,17,17,null,300,{"$f":"C430+Spans!$C$10","v":17},{"$f":"D430+Spans!$C$10","v":17},{"$f":"E430+Spans!$C$10","v":17},{"$f":"F430+Spans!$C$10","v":17},{"$f":"G430+Spans!$C$10","v":17}]
[null,400,17,17,17,17,17,null,400,{"$f":"C431+Spans!$C$10","v":17},{"$f":"D431+Spans!$C$10","v":17},{"$f":"E431+Spans!$C$10","v":17},{"$f":"F431+Spans!$C$10","v":17},{"$f":"G431+Spans!$C$10","v":17}]
[null,500,17,17,17,17,17,null,500,{"$f":"C432+Spans!$C$10","v":17},{"$f":"D432+Spans!$C$10","v":17},{"$f":"E432+Spans!$C$10","v":17},{"$f":"F432+Spans!$C$10","v":17},{"$f":"G432+Spans!$C$10","v":17}]
[null,1000,{"$f":"C432","v":17},{"$f":"D432","v":17},{"$f":"E432","v":17},{"$f":"F432","v":17},{"$f":"G432","v":17},null,1000,{"$f":"J432","v":17},{"$f":"K432","v":17},{"$f":"L432","v":17},{"$f":"M432","v":17},{"$f":"N432","v":17}]
[]
[null,null,null,null,null,null,null,null,"TABLE",32]
[null,"FEA Table:","Wood, 2 (7/1) ACSR, Blue Gum / Eucalyptus",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C440","v":17},{"$f":"D440","v":17},{"$f":"E440","v":17},{"$f":"F440","v":17},{"$f":"G440","v":17},null,1,{"$f":"J440","v":17},{"$f":"K440","v":17},{"$f":"L440","v":17},{"$f":"M440","v":17},{"$f":"N440","v":17}]
[null,50,17,17,17,17,17,null,50,{"$f":"C440+Spans!$C$10","v":17},{"$f":"D440+Spans!$C$10","v":17},{"$f":"E440+Spans!$C$10","v":17},{"$f":"F440+Spans!$C$10","v":17},{"$f":"G440+Spans!$C$10","v":17}]
[null,100,17,17,17,17,17,null,100,{"$f":"C441+Spans!$C$10","v":17},{"$f":"D441+Spans!$C$10","v":17},{"$f":"E441+Spans!$C$10","v":17},{"$f":"F441+Spans!$C$10","v":17},{"$f":"G441+Spans!$C$10","v":17}]
[null,150,17,17,17,17,17,null,150,{"$f":"C442+Spans!$C$10","v":17},{"$f":"D442+Spans!$C$10","v":17},{"$f":"E442+Spans!$C$10","v":17},{"$f":"F442+Spans!$C$10","v":17},{"$f":"G442+Spans!$C$10","v":17}]
[null,200,17,17,17,17,17,null,200,{"$f":"C443+Spans!$C$10","v":17},{"$f":"D443+Spans!$C$10","v":17},{"$f":"E443+Spans!$C$10","v":17},{"$f":"F443+Spans!$C$10","v":17},{"$f":"G443+Spans!$C$10","v":17}]
[null,300,17,17,17,17,17,null,300,{"$f":"C444+Spans!$C$10","v":17},{"$f":"D444+Spans!$C$10","v":17},{"$f":"E444+Spans!$C$10","v":17},{"$f":"F444+Spans!$C$10","v":17},{"$f":"G444+Spans!$C$10","v":17}]
[null,400,17,17,17,17,17,null,400,{"$f":"C445+Spans!$C$10","v":17},{"$f":"D445+Spans!$C$10","v":17},{"$f":"E445+Spans!$C$10","v":17},{"$f":"F445+Spans!$C$10","v":17},{"$f":"G445+Spans!$C$10","v":17}]
[null,500,17,17,17,17,17,null,500,{"$f":"C446+Spans!$C$10","v":17},{"$f":"D446+Spans!$C$10","v":17},{"$f":"E446+Spans!$C$10","v":17},{"$f":"F446+Spans!$C$10","v":17},{"$f":"G446+Spans!$C$10","v":17}]
[null,1000,{"$f":"C446","v":17},{"$f":"D446","v":17},{"$f":"E446","v":17},{"$f":"F446","v":17},{"$f":"G446","v":17},null,1000,{"$f":"J446","v":17},{"$f":"K446","v":17},{"$f":"L446","v":17},{"$f":"M446","v":17},{"$f":"N446","v":17}]
[]
[null,null,null,null,null,null,null,null,"TABLE",33]
[null,"FEA Table:",null,null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C454","v":0},{"$f":"D454","v":0},{"$f":"E454","v":0},{"$f":"F454","v":0},{"$f":"G454","v":0},null,1,{"$f":"J454","v":0},{"$f":"K454","v":0},{"$f":"L454","v":0},{"$f":"M454","v":0},{"$f":"N454","v":0}]
[null,50,null,null,null,null,null,null,50,{"$f":"C454+Spans!$C$10","v":0},{"$f":"D454+Spans!$C$10","v":0},{"$f":"E454+Spans!$C$10","v":0},{"$f":"F454+Spans!$C$10","v":0},{"$f":"G454+Spans!$C$10","v":0}]
[null,100,null,null,null,null,null,null,100,{"$f":"C455+Spans!$C$10","v":0},{"$f":"D455+Spans!$C$10","v":0},{"$f":"E455+Spans!$C$10","v":0},{"$f":"F455+Spans!$C$10","v":0},{"$f":"G455+Spans!$C$10","v":0}]
[null,150,null,null,null,null,null,null,150,{"$f":"C456+Spans!$C$10","v":0},{"$f":"D456+Spans!$C$10","v":0},{"$f":"E456+Spans!$C$10","v":0},{"$f":"F456+Spans!$C$10","v":0},{"$f":"G456+Spans!$C$10","v":0}]
[null,200,null,null,null,null,null,null,200,{"$f":"C457+Spans!$C$10","v":0},{"$f":"D457+Spans!$C$10","v":0},{"$f":"E457+Spans!$C$10","v":0},{"$f":"F457+Spans!$C$10","v":0},{"$f":"G457+Spans!$C$10","v":0}]
[null,300,null,null,null,null,null,null,300,{"$f":"C458+Spans!$C$10","v":0},{"$f":"D458+Spans!$C$10","v":0},{"$f":"E458+Spans!$C$10","v":0},{"$f":"F458+Spans!$C$10","v":0},{"$f":"G458+Spans!$C$10","v":0}]
[null,400,null,null,null,null,null,null,400,{"$f":"C459+Spans!$C$10","v":0},{"$f":"D459+Spans!$C$10","v":0},{"$f":"E459+Spans!$C$10","v":0},{"$f":"F459+Spans!$C$10","v":0},{"$f":"G459+Spans!$C$10","v":0}]
[null,500,null,null,null,null,null,null,500,{"$f":"C460+Spans!$C$10","v":0},{"$f":"D460+Spans!$C$10","v":0},{"$f":"E460+Spans!$C$10","v":0},{"$f":"F460+Spans!$C$10","v":0},{"$f":"G460+Spans!$C$10","v":0}]
[null,1000,{"$f":"C460","v":0},{"$f":"D460","v":0},{"$f":"E460","v":0},{"$f":"F460","v":0},{"$f":"G460","v":0},null,1000,{"$f":"J460","v":0},{"$f":"K460","v":0},{"$f":"L460","v":0},{"$f":"M460","v":0},{"$f":"N460","v":0}]
[]
[null,null,null,null,null,null,null,null,"TABLE",34]
[null,"FEA Table:",null,null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C468","v":0},{"$f":"D468","v":0},{"$f":"E468","v":0},{"$f":"F468","v":0},{"$f":"G468","v":0},null,1,{"$f":"J468","v":0},{"$f":"K468","v":0},{"$f":"L468","v":0},{"$f":"M468","v":0},{"$f":"N468","v":0}]
[null,50,null,null,null,null,null,null,50,{"$f":"C468+Spans!$C$10","v":0},{"$f":"D468+Spans!$C$10","v":0},{"$f":"E468+Spans!$C$10","v":0},{"$f":"F468+Spans!$C$10","v":0},{"$f":"G468+Spans!$C$10","v":0}]
[null,100,null,null,null,null,null,null,100,{"$f":"C469+Spans!$C$10","v":0},{"$f":"D469+Spans!$C$10","v":0},{"$f":"E469+Spans!$C$10","v":0},{"$f":"F469+Spans!$C$10","v":0},{"$f":"G469+Spans!$C$10","v":0}]
[null,150,null,null,null,null,null,null,150,{"$f":"C470+Spans!$C$10","v":0},{"$f":"D470+Spans!$C$10","v":0},{"$f":"E470+Spans!$C$10","v":0},{"$f":"F470+Spans!$C$10","v":0},{"$f":"G470+Spans!$C$10","v":0}]
[null,200,null,null,null,null,null,null,200,{"$f":"C471+Spans!$C$10","v":0},{"$f":"D471+Spans!$C$10","v":0},{"$f":"E471+Spans!$C$10","v":0},{"$f":"F471+Spans!$C$10","v":0},{"$f":"G471+Spans!$C$10","v":0}]
[null,300,null,null,null,null,null,null,300,{"$f":"C472+Spans!$C$10","v":0},{"$f":"D472+Spans!$C$10","v":0},{"$f":"E472+Spans!$C$10","v":0},{"$f":"F472+Spans!$C$10","v":0},{"$f":"G472+Spans!$C$10","v":0}]
[null,400,null,null,null,null,null,null,400,{"$f":"C473+Spans!$C$10","v":0},{"$f":"D473+Spans!$C$10","v":0},{"$f":"E473+Spans!$C$10","v":0},{"$f":"F473+Spans!$C$10","v":0},{"$f":"G473+Spans!$C$10","v":0}]
[null,500,null,null,null,null,null,null,500,{"$f":"C474+Spans!$C$10","v":0},{"$f":"D474+Spans!$C$10","v":0},{"$f":"E474+Spans!$C$10","v":0},{"$f":"F474+Spans!$C$10","v":0},{"$f":"G474+Spans!$C$10","v":0}]
[null,1000,{"$f":"C474","v":0},{"$f":"D474","v":0},{"$f":"E474","v":0},{"$f":"F474","v":0},{"$f":"G474","v":0},null,1000,{"$f":"J474","v":0},{"$f":"K474","v":0},{"$f":"L474","v":0},{"$f":"M474","v":0},{"$f":"N474","v":0}]
[]
[null,null,null,null,null,null,null,null,"TABLE",35]
[null,"FEA Table:",null,null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C482","v":0},{"$f":"D482","v":0},{"$f":"E482","v":0},{"$f":"F482","v":0},{"$f":"G482","v":0},null,1,{"$f":"J482","v":0},{"$f":"K482","v":0},{"$f":"L482","v":0},{"$f":"M482","v":0},{"$f":"N482","v":0}]
[null,50,null,null,null,null,null,null,50,{"$f":"C482+Spans!$C$10","v":0},{"$f":"D482+Spans!$C$10","v":0},{"$f":"E482+Spans!$C$10","v":0},{"$f":"F482+Spans!$C$10","v":0},{"$f":"G482+Spans!$C$10","v":0}]
[null,100,null,null,null,null,null,null,100,{"$f":"C483+Spans!$C$10","v":0},{"$f":"D483+Spans!$C$10","v":0},{"$f":"E483+Spans!$C$10","v":0},{"$f":"F483+Spans!$C$10","v":0},{"$f":"G483+Spans!$C$10","v":0}]
[null,150,null,null,null,null,null,null,150,{"$f":"C484+Spans!$C$10","v":0},{"$f":"D484+Spans!$C$10","v":0},{"$f":"E484+Spans!$C$10","v":0},{"$f":"F484+Spans!$C$10","v":0},{"$f":"G484+Spans!$C$10","v":0}]
[null,200,null,null,null,null,null,null,200,{"$f":"C485+Spans!$C$10","v":0},{"$f":"D485+Spans!$C$10","v":0},{"$f":"E485+Spans!$C$10","v":0},{"$f":"F485+Spans!$C$10","v":0},{"$f":"G485+Spans!$C$10","v":0}]
[null,300,null,null,null,null,null,null,300,{"$f":"C486+Spans!$C$10","v":0},{"$f":"D486+Spans!$C$10","v":0},{"$f":"E486+Spans!$C$10","v":0},{"$f":"F486+Spans!$C$10","v":0},{"$f":"G486+Spans!$C$10","v":0}]
[null,400,null,null,null,null,null,null,400,{"$f":"C487+Spans!$C$10","v":0},{"$f":"D487+Spans!$C$10","v":0},{"$f":"E487+Spans!$C$10","v":0},{"$f":"F487+Spans!$C$10","v":0},{"$f":"G487+Spans!$C$10","v":0}]
[null,500,null,null,null,null,null,null,500,{"$f":"C488+Spans!$C$10","v":0},{"$f":"D488+Spans!$C$10","v":0},{"$f":"E488+Spans!$C$10","v":0},{"$f":"F488+Spans!$C$10","v":0},{"$f":"G488+Spans!$C$10","v":0}]
[null,1000,{"$f":"C488","v":0},{"$f":"D488","v":0},{"$f":"E488","v":0},{"$f":"F488","v":0},{"$f":"G488","v":0},null,1000,{"$f":"J488","v":0},{"$f":"K488","v":0},{"$f":"L488","v":0},{"$f":"M488","v":0},{"$f":"N488","v":0}]
[]
[null,null,null,null,null,null,null,null,"TABLE",36]
[null,"FEA Table:",null,null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C496","v":0},{"$f":"D496","v":0},{"$f":"E496","v":0},{"$f":"F496","v":0},{"$f":"G496","v":0},null,1,{"$f":"J496","v":0},{"$f":"K496","v":0},{"$f":"L496","v":0},{"$f":"M496","v":0},{"$f":"N496","v":0}]
[null,50,null,null,null,null,null,null,50,{"$f":"C496+Spans!$C$10","v":0},{"$f":"D496+Spans!$C$10","v":0},{"$f":"E496+Spans!$C$10","v":0},{"$f":"F496+Spans!$C$10","v":0},{"$f":"G496+Spans!$C$10","v":0}]
[null,100,null,null,null,null,null,null,100,{"$f":"C497+Spans!$C$10","v":0},{"$f":"D497+Spans!$C$10","v":0},{"$f":"E497+Spans!$C$10","v":0},{"$f":"F497+Spans!$C$10","v":0},{"$f":"G497+Spans!$C$10","v":0}]
[null,150,null,null,null,null,null,null,150,{"$f":"C498+Spans!$C$10","v":0},{"$f":"D498+Spans!$C$10","v":0},{"$f":"E498+Spans!$C$10","v":0},{"$f":"F498+Spans!$C$10","v":0},{"$f":"G498+Spans!$C$10","v":0}]
[null,200,null,null,null,null,null,null,200,{"$f":"C499+Spans!$C$10","v":0},{"$f":"D499+Spans!$C$10","v":0},{"$f":"E499+Spans!$C$10","v":0},{"$f":"F499+Spans!$C$10","v":0},{"$f":"G499+Spans!$C$10","v":0}]
[null,300,null,null,null,null,null,null,300,{"$f":"C500+Spans!$C$10","v":0},{"$f":"D500+Spans!$C$10","v":0},{"$f":"E500+Spans!$C$10","v":0},{"$f":"F500+Spans!$C$10","v":0},{"$f":"G500+Spans!$C$10","v":0}]
[null,400,null,null,null,null,null,null,400,{"$f":"C501+Spans!$C$10","v":0},{"$f":"D501+Spans!$C$10","v":0},{"$f":"E501+Spans!$C$10","v":0},{"$f":"F501+Spans!$C$10","v":0},{"$f":"G501+Spans!$C$10","v":0}]
[null,500,null,null,null,null,null,null,500,{"$f":"C502+Spans!$C$10","v":0},{"$f":"D502+Spans!$C$10","v":0},{"$f":"E502+Spans!$C$10","v":0},{"$f":"F502+Spans!$C$10","v":0},{"$f":"G502+Spans!$C$10","v":0}]
[null,1000,{"$f":"C502","v":0},{"$f":"D502","v":0},{"$f":"E502","v":0},{"$f":"F502","v":0},{"$f":"G502","v":0},null,1000,{"$f":"J502","v":0},{"$f":"K502","v":0},{"$f":"L502","v":0},{"$f":"M502","v":0},{"$f":"N502","v":0}]
[]
[null,null,null,null,null,null,null,null,"TABLE",37]
[null,"Base Table:",null,null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C510","v":0},{"$f":"D510","v":0},{"$f":"E510","v":0},{"$f":"F510","v":0},{"$f":"G510","v":0},null,1,{"$f":"J510","v":0},{"$f":"K510","v":0},{"$f":"L510","v":0},{"$f":"M510","v":0},{"$f":"N510","v":0}]
[null,50,null,null,null,null,null,null,50,{"$f":"C510+Spans!$C$10","v":0},{"$f":"D510+Spans!$C$10","v":0},{"$f":"E510+Spans!$C$10","v":0},{"$f":"F510+Spans!$C$10","v":0},{"$f":"G510+Spans!$C$10","v":0}]
[null,100,null,null,null,null,null,null,100,{"$f":"C511+Spans!$C$10","v":0},{"$f":"D511+Spans!$C$10","v":0},{"$f":"E511+Spans!$C$10","v":0},{"$f":"F511+Spans!$C$10","v":0},{"$f":"G511+Spans!$C$10","v":0}]
[null,150,null,null,null,null,null,null,150,{"$f":"C512+Spans!$C$10","v":0},{"$f":"D512+Spans!$C$10","v":0},{"$f":"E512+Spans!$C$10","v":0},{"$f":"F512+Spans!$C$10","v":0},{"$f":"G512+Spans!$C$10","v":0}]
[null,200,null,null,null,null,null,null,200,{"$f":"C513+Spans!$C$10","v":0},{"$f":"D513+Spans!$C$10","v":0},{"$f":"E513+Spans!$C$10","v":0},{"$f":"F513+Spans!$C$10","v":0},{"$f":"G513+Spans!$C$10","v":0}]
[null,300,null,null,null,null,null,null,300,{"$f":"C514+Spans!$C$10","v":0},{"$f":"D514+Spans!$C$10","v":0},{"$f":"E514+Spans!$C$10","v":0},{"$f":"F514+Spans!$C$10","v":0},{"$f":"G514+Spans!$C$10","v":0}]
[null,400,null,null,null,null,null,null,400,{"$f":"C515+Spans!$C$10","v":0},{"$f":"D515+Spans!$C$10","v":0},{"$f":"E515+Spans!$C$10","v":0},{"$f":"F515+Spans!$C$10","v":0},{"$f":"G515+Spans!$C$10","v":0}]
[null,500,null,null,null,null,null,null,500,{"$f":"C516+Spans!$C$10","v":0},{"$f":"D516+Spans!$C$10","v":0},{"$f":"E516+Spans!$C$10","v":0},{"$f":"F516+Spans!$C$10","v":0},{"$f":"G516+Spans!$C$10","v":0}]
[null,1000,{"$f":"C516","v":0},{"$f":"D516","v":0},{"$f":"E516","v":0},{"$f":"F516","v":0},{"$f":"G516","v":0},null,1000,{"$f":"J516","v":0},{"$f":"K516","v":0},{"$f":"L516","v":0},{"$f":"M516","v":0},{"$f":"N516","v":0}]
[]
[null,null,null,null,null,null,null,null,"TABLE",38]
[null,"FEA Table:",null,null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C524","v":0},{"$f":"D524","v":0},{"$f":"E524","v":0},{"$f":"F524","v":0},{"$f":"G524","v":0},null,1,{"$f":"J524","v":0},{"$f":"K524","v":0},{"$f":"L524","v":0},{"$f":"M524","v":0},{"$f":"N524","v":0}]
[null,50,null,null,null,null,null,null,50,{"$f":"C524+Spans!$C$10","v":0},{"$f":"D524+Spans!$C$10","v":0},{"$f":"E524+Spans!$C$10","v":0},{"$f":"F524+Spans!$C$10","v":0},{"$f":"G524+Spans!$C$10","v":0}]
[null,100,null,null,null,null,null,null,100,{"$f":"C525+Spans!$C$10","v":0},{"$f":"D525+Spans!$C$10","v":0},{"$f":"E525+Spans!$C$10","v":0},{"$f":"F525+Spans!$C$10","v":0},{"$f":"G525+Spans!$C$10","v":0}]
[null,150,null,null,null,null,null,null,150,{"$f":"C526+Spans!$C$10","v":0},{"$f":"D526+Spans!$C$10","v":0},{"$f":"E526+Spans!$C$10","v":0},{"$f":"F526+Spans!$C$10","v":0},{"$f":"G526+Spans!$C$10","v":0}]
[null,200,null,null,null,null,null,null,200,{"$f":"C527+Spans!$C$10","v":0},{"$f":"D527+Spans!$C$10","v":0},{"$f":"E527+Spans!$C$10","v":0},{"$f":"F527+Spans!$C$10","v":0},{"$f":"G527+Spans!$C$10","v":0}]
[null,300,null,null,null,null,null,null,300,{"$f":"C528+Spans!$C$10","v":0},{"$f":"D528+Spans!$C$10","v":0},{"$f":"E528+Spans!$C$10","v":0},{"$f":"F528+Spans!$C$10","v":0},{"$f":"G528+Spans!$C$10","v":0}]
[null,400,null,null,null,null,null,null,400,{"$f":"C529+Spans!$C$10","v":0},{"$f":"D529+Spans!$C$10","v":0},{"$f":"E529+Spans!$C$10","v":0},{"$f":"F529+Spans!$C$10","v":0},{"$f":"G529+Spans!$C$10","v":0}]
[null,500,null,null,null,null,null,null,500,{"$f":"C530+Spans!$C$10","v":0},{"$f":"D530+Spans!$C$10","v":0},{"$f":"E530+Spans!$C$10","v":0},{"$f":"F530+Spans!$C$10","v":0},{"$f":"G530+Spans!$C$10","v":0}]
[null,1000,{"$f":"C530","v":0},{"$f":"D530","v":0},{"$f":"E530","v":0},{"$f":"F530","v":0},{"$f":"G530","v":0},null,1000,{"$f":"J530","v":0},{"$f":"K530","v":0},{"$f":"L530","v":0},{"$f":"M530","v":0},{"$f":"N530","v":0}]
[]
[null,null,null,null,null,null,null,null,"TABLE",39]
[null,"FEA Table:","Wood, 715.5 AAC, Oak",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C538","v":17},{"$f":"D538","v":17},{"$f":"E538","v":17},{"$f":"F538","v":17},{"$f":"G538","v":17},null,1,{"$f":"J538","v":17},{"$f":"K538","v":17},{"$f":"L538","v":17},{"$f":"M538","v":17},{"$f":"N538","v":17}]
[null,50,17,17,17,17,17,null,50,{"$f":"C538+Spans!$C$10","v":17},{"$f":"D538+Spans!$C$10","v":17},{"$f":"E538+Spans!$C$10","v":17},{"$f":"F538+Spans!$C$10","v":17},{"$f":"G538+Spans!$C$10","v":17}]
[null,100,17,17,17,17,17,null,100,{"$f":"C539+Spans!$C$10","v":17},{"$f":"D539+Spans!$C$10","v":17},{"$f":"E539+Spans!$C$10","v":17},{"$f":"F539+Spans!$C$10","v":17},{"$f":"G539+Spans!$C$10","v":17}]
[null,150,17,17,17,17,17,null,150,{"$f":"C540+Spans!$C$10","v":17},{"$f":"D540+Spans!$C$10","v":17},{"$f":"E540+Spans!$C$10","v":17},{"$f":"F540+Spans!$C$10","v":17},{"$f":"G540+Spans!$C$10","v":17}]
[null,200,17,17,17,17,17,null,200,{"$f":"C541+Spans!$C$10","v":17},{"$f":"D541+Spans!$C$10","v":17},{"$f":"E541+Spans!$C$10","v":17},{"$f":"F541+Spans!$C$10","v":17},{"$f":"G541+Spans!$C$10","v":17}]
[null,300,17,17,17,17,17,null,300,{"$f":"C542+Spans!$C$10","v":17},{"$f":"D542+Spans!$C$10","v":17},{"$f":"E542+Spans!$C$10","v":17},{"$f":"F542+Spans!$C$10","v":17},{"$f":"G542+Spans!$C$10","v":17}]
[null,400,17,17,17,17,17,null,400,{"$f":"C543+Spans!$C$10","v":17},{"$f":"D543+Spans!$C$10","v":17},{"$f":"E543+Spans!$C$10","v":17},{"$f":"F543+Spans!$C$10","v":17},{"$f":"G543+Spans!$C$10","v":17}]
[null,500,17,17,17,17,17,null,500,{"$f":"C544+Spans!$C$10","v":17},{"$f":"D544+Spans!$C$10","v":17},{"$f":"E544+Spans!$C$10","v":17},{"$f":"F544+Spans!$C$10","v":17},{"$f":"G544+Spans!$C$10","v":17}]
[null,1000,{"$f":"C544","v":17},{"$f":"D544","v":17},{"$f":"E544","v":17},{"$f":"F544","v":17},{"$f":"G544","v":17},null,1000,{"$f":"J544","v":17},{"$f":"K544","v":17},{"$f":"L544","v":17},{"$f":"M544","v":17},{"$f":"N544","v":17}]
[]
[null,null,null,null,null,null,null,null,"TABLE",40]
[null,"FEA Table:","Wood, 715.5 AAC, Blue Gum / Eucalyptus",null,null,null,null,null,"Span Shape:",2,3,4,5,6]
[null,"Span","Allowable Overstrike Length (ft)",null,null,null,null,null,"Span","Adjusted Allowable Overstrike Length (ft)"]
[null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap",null,"Len (ft)","Tangent","45° Turn","90° Turn","T-Tap","X-Tap"]
[null,1,{"$f":"C552","v":17},{"$f":"D552","v":17},{"$f":"E552","v":17},{"$f":"F552","v":17},{"$f":"G552","v":17},null,1,{"$f":"J552","v":17},{"$f":"K552","v":17},{"$f":"L552","v":17},{"$f":"M552","v":17},{"$f":"N552","v":17}]
[null,50,17,17,17,17,17,null,50,{"$f":"C552+Spans!$C$10","v":17},{"$f":"D552+Spans!$C$10","v":17},{"$f":"E552+Spans!$C$10","v":17},{"$f":"F552+Spans!$C$10","v":17},{"$f":"G552+Spans!$C$10","v":17}]
[null,100,17,17,17,17,17,null,100,{"$f":"C553+Spans!$C$10","v":17},{"$f":"D553+Spans!$C$10","v":17},{"$f":"E553+Spans!$C$10","v":17},{"$f":"F553+Spans!$C$10","v":17},{"$f":"G553+Spans!$C$10","v":17}]
[null,150,17,17,17,17,17,null,150,{"$f":"C554+Spans!$C$10","v":17},{"$f":"D554+Spans!$C$10","v":17},{"$f":"E554+Spans!$C$10","v":17},{"$f":"F554+Spans!$C$10","v":17},{"$f":"G554+Spans!$C$10","v":17}]
[null,200,17,17,17,17,17,null,200,{"$f":"C555+Spans!$C$10","v":17},{"$f":"D555+Spans!$C$10","v":17},{"$f":"E555+Spans!$C$10","v":17},{"$f":"F555+Spans!$C$10","v":17},{"$f":"G555+Spans!$C$10","v":17}]
[null,300,17,17,17,17,17,null,300,{"$f":"C556+Spans!$C$10","v":17},{"$f":"D556+Spans!$C$10","v":17},{"$f":"E556+Spans!$C$10","v":17},{"$f":"F556+Spans!$C$10","v":17},{"$f":"G556+Spans!$C$10","v":17}]
[null,400,17,17,17,17,17,null,400,{"$f":"C557+Spans!$C$10","v":17},{"$f":"D557+Spans!$C$10","v":17},{"$f":"E557+Spans!$C$10","v":17},{"$f":"F557+Spans!$C$10","v":17},{"$f":"G557+Spans!$C$10","v":17}]
[null,500,17,17,17,17,17,null,500,{"$f":"C558+Spans!$C$10","v":17},{"$f":"D558+Spans!$C$10","v":17},{"$f":"E558+Spans!$C$10","v":17},{"$f":"F558+Spans!$C$10","v":17},{"$f":"G558+Spans!$C$10","v":17}]
[null,1000,{"$f":"C558","v":17},{"$f":"D558","v":17},{"$f":"E558","v":17},{"$f":"F558","v":17},{"$f":"G558","v":17},null,1000,{"$f":"J558","v":17},{"$f":"K558","v":17},{"$f":"L558","v":17},{"$f":"M558","v":17},{"$f":"N558","v":17}]