## Sheet1
Priority | DIV | Substation | Two Bank | Notes
1 | CC | Big Basin | N | Good candidate
2 | NB | Woodacre | N | Short taps
3 | SI | Forest Hill | N | Good candidate, 2 feeders
4 | YO | Miwuk | N | Good candidate, 2 feeders
5 | ST | Stanislaus PH | N | Good candidate, 2 feeders
6 | NV | Girvan | N | Good candidate, 2 feeders
7 | NB | Monticello | Y | Single feeder
8 | SI | Columbia Hill | N | Single feeder, 100 miles
9 | HB | Konocti | Y | 2 feeders, well balanced, could reconfigure to 1 bank
10 | HB | Highlands | Y | 3 feeders, well balanced, adequate space
11 | SI | Allegany | N | 2 feeders, 18 mile single phase tap
12 | SI | Bonnie Nook | N | 2 feeders, 17 mile single phase tap
13 | SI | Pike City | N | Good candidate, not a lot of circuit mileage (45 mi total)
14 | NV | Kanaka | N | Only 1 feeder
15 | SI | Mountain Quarries | N | Single feeder, 15 mile single phase tap
16 | HB | Willits | N | 15 mile single phase tap
17 | NV | Big Bend | N | 20 mile single phase tap
18 | SO | Monte Rio | Y | 1 bank is spare, 3 feeders, well balanced

## System Hardening List
Rank | Substation | # Banks | # Feeders | Fire Risk (excl Egress) | REFCL rank | Notes
1 | Miwuk | 1 |  |  | 4
2 | El Dorado PH | 2 |  |  |  | 21 kv
3 | Spring Gap |  |  |  |  | 17 kv
4 | Salt Springs |  |  |  |  | 21 kv
5 | Brunswick
6 | Mariposa |  |  |  |  | 21 kv
7 | Placerville
8 | Oro Fino
9 | Wyandotte
10 | Bonnie Nook |  |  |  | 12
11 | Pine Grove
12 | Stanislaus |  |  |  | 5
13 | Foresthill |  |  |  | 3
14 | Los Gatos
15 | Middletown
16 | Challenge
17 | West Point
18 | Pike City |  |  |  | 13
19 | Pine Grove
20 | Columbia Hill |  |  |  | 8
21 | Calistoga |  |  |  | 0
22 | Pueblo
23 | Big Bend |  |  |  | 17
24 | Camp Evers
25 | Willits |  |  |  | 16
26 | Whitmore
27 | Alleghany |  |  |  | 11
28 | Monte Rio |  |  |  | 18
29 | Rincon
30 | Apple Hill
31 | Paradise
32 | Mirabel
33 | Sycamore Creek
34 | Oakhurst
35 | Kanaka |  |  |  | 14
36 | Volta
37 | Molino
38 | Drum
39 | Woodside
40 | Bucks Creek
41 | Electra
42 | Woodacre |  |  |  | 2
43 | Downieville Diesel
44 | Silverado
45 | Auberry
46 | Fulton
47 | Shingle Springs
48 | Big Basin |  |  |  | 1
49 | Fort Ross
50 | Mountain Quarries |  |  |  | 15
51 | Stelling
52 | Big Trees
53 | Fitch Mountain
54 | San Rafael
55 | Konocti |  |  |  | 9
56 | Diamond Springs
57 | Half Moon Bay
58 | Curtis
59 | Dunbar
60 | Clarksville
61 | Washington City
62 | Willow Creek
63 | Alto
64 | Morgan Hill
65 | Highlands |  |  |  | 10
66 | Shady Glen
67 | Mendocino
68 | Redbud
69 | Paul Sweet
70 | Oakland X
71 | Bellevue
72 | Burns
73 | Point Moretti
74 | Las Gallinas A
75 | Grass Valley
76 | Bear Valley
77 | Tiger Creek
78 | Cabrillo
79 | Calpine
80 | SCE Refugio
81 | Rossmoor
82 | Clayton
83 | Otter
84 | Moraga
85 | Rob Roy

## Sheet3
Dx Prioritization Output - System Hardening | [6 empty] | Planned 2019 implementation
Circuit Information |  |  |  |  | Independent Variables | [5 empty] | Dependent Variable
Protection Zone | Substation | Feeder Name | District | Tier 2/3 OH Miles | Env Risk Component | Material A - % of total miles | Vegetation Outages | Company Outages | HFTD Miles per Total Miles | Tier 3 per HFTD Miles | Ignition Indicator (1+ ignition occurred) | Likelihood of failure | Likelihood of spread and consequence | Fire Risk | Risk / Mi
MIWUK 170110600 | MIWUK | MIWUK 1701 | YOSEMITE | 10.9092 | 90.0653 | 100% | 20 | 16 | 100% | 100% | 1 | 0.80002 | 102.1389 | 81.7128 | 7.4903
EL DORADO PH 210119752 | EL DO | EL DORADO PH 2101 | SIERRA | 38.577 | 80.8747 | 99.99% | 20 | 11 | 100% | 99.16% | 1 | 0.69086 | 102.1389 | 70.5639 | 1.8292
SPRING GAP 17029690 | SPRIN | SPRING GAP 1702 | YOSEMITE | 17.3345 | 90.5752 | 98.76% | 12 | 12 | 100% | 100% | 0 | 0.65826 | 102.1389 | 67.2336 | 3.8786
MIWUK 1701CB | MIWUK | MIWUK 1701 | YOSEMITE | 17.9054 | 91.659 | 81.59% | 16 | 15 | 100% | 100% | 0 | 0.65411 | 102.1389 | 66.8104 | 3.7313
SALT SPRINGS 21023142 | SALT | SALT SPRINGS 2102 | STOCKTON | 16.894 | 90.205 | 100% | 15 | 9 | 100% | 100% | 0 | 0.62396 | 102.1389 | 63.7309 | 3.7724
BRUNSWICK 11021010 | BRUNS | BRUNSWICK 1102 | SIERRA | 44.041 | 87.3695 | 84.93% | 12 | 13 | 100% | 98.91% | 0 | 0.59607 | 102.1389 | 60.8822 | 1.3824
BRUNSWICK 110532536 | BRUNS | BRUNSWICK 1105 | SIERRA | 21.7333 | 94.8632 | 99.08% | 11 | 14 | 100% | 100% | 0 | 0.54536 | 102.1389 | 55.7026 | 2.563
BRUNSWICK 110350070 | BRUNS | BRUNSWICK 1103 | SIERRA | 28.1191 | 94.0552 | 99.83% | 13 | 12 | 100% | 100% | 1 | 0.54169 | 102.1389 | 55.3273 | 1.9676
BRUNSWICK 11052210 | BRUNS | BRUNSWICK 1105 | SIERRA | 22.8031 | 97.1876 | 99.8% | 8 | 12 | 100% | 100% | 0 | 0.53048 | 102.1389 | 54.1827 | 2.3761
EL DORADO PH 21016852 | EL DO | EL DORADO PH 2101 | SIERRA | 25.3514 | 89.3624 | 96.21% | 18 | 8 | 100% | 100% | 0 | 0.52183 | 102.1389 | 53.299 | 2.1024
MARIPOSA 210110170 | MARIP | MARIPOSA 2101 | YOSEMITE | 16.3113 | 93.2169 | 77.6% | 14 | 34 | 100% | 100% | 1 | 0.51304 | 102.1389 | 52.4012 | 3.2126
BRUNSWICK 11052140 | BRUNS | BRUNSWICK 1105 | SIERRA | 34.5645 | 95.4853 | 99.76% | 25 | 10 | 100% | 100% | 0 | 0.50651 | 102.1389 | 51.7342 | 1.4967
PLACERVILLE 21061104 | PLACE | PLACERVILLE 2106 | SIERRA | 50.3628 | 96.0676 | 90.37% | 13 | 6 | 100% | 100% | 1 | 0.49422 | 102.1389 | 50.479 | 1.0023
ORO FINO 1101CB | ORO F | ORO FINO 1101 | NORTH VALLEY | 22.1887 | 87.2953 | 86.14% | 9 | 11 | 100% | 100% | 0 | 0.48349 | 102.1389 | 49.3837 | 2.2256
EL DORADO PH 210126000 | EL DO | EL DORADO PH 2101 | SIERRA | 34.0468 | 93.5067 | 99.32% | 9 | 8 | 100% | 100% | 0 | 0.57184 | 85.4511 | 48.8647 | 1.4352
WYANDOTTE 11031974 | WYAND | WYANDOTTE 1103 | NORTH VALLEY | 22.8741 | 92.9076 | 99.55% | 6 | 6 | 100% | 100% | 1 | 0.45135 | 102.1389 | 46.1001 | 2.0154
BONNIE NOOK 1102CB | BONNI | BONNIE NOOK 1102 | SIERRA | 34.3352 | 94.488 | 85.18% | 18 | 16 | 100% | 100% | 0 | 0.44981 | 102.1389 | 45.9434 | 1.3381
PINE GROVE 110245292 | PINE | PINE GROVE 1102 | STOCKTON | 10.8778 | 85.9329 | 100% | 1 | 11 | 100% | 99.38% | 0 | 0.44757 | 102.1389 | 45.714 | 4.2025
STANISLAUS 17021888 | STANI | STANISLAUS 1702 | YOSEMITE | 18.9533 | 77.9476 | 99.71% | 9 | 14 | 100% | 100% | 0 | 0.44468 | 102.1389 | 45.4193 | 2.3964
FORESTHILL 110150486 | FORES | FORESTHILL 1101 | SIERRA | 11.6566 | 81.112 | 97.86% | 4 | 8 | 100% | 100% | 0 | 0.43184 | 102.1389 | 44.1076 | 3.7839
LOS GATOS 110760114 | LOS G | LOS GATOS 1107 | DE ANZA | 24.3274 | 75.5493 | 92.99% | 9 | 3 | 100% | 100% | 1 | 0.66312 | 65.3912 | 43.362 | 1.7824
MIDDLETOWN 1101548 | MIDDL | MIDDLETOWN 1101 | HUMBOLDT | 22.1669 | 84.1532 | 73.95% | 13 | 16 | 88.6% | 97.32% | 1 | 0.42028 | 102.1389 | 42.9273 | 1.9365
MIWUK 17018060 | MIWUK | MIWUK 1701 | YOSEMITE | 11.8537 | 93.2164 | 72.89% | 5 | 17 | 100% | 100% | 0 | 0.41847 | 102.1389 | 42.7418 | 3.6058
BRUNSWICK 110651486 | BRUNS | BRUNSWICK 1106 | SIERRA | 56.6992 | 84.1552 | 88.14% | 22 | 15 | 100% | 87.68% | 1 | 0.49605 | 85.4511 | 42.3883 | 0.7476
CHALLENGE 1102CB | CHALL | CHALLENGE 1102 | NORTH VALLEY | 15.5217 | 96.52 | 90.77% | 6 | 5 | 100% | 100% | 0 | 0.4019 | 102.1389 | 41.0501 | 2.6447
FORESTHILL 11011802 | FORES | FORESTHILL 1101 | SIERRA | 22.1758 | 72.9192 | 91.83% | 12 | 21 | 100% | 100% | 0 | 0.40081 | 102.1389 | 40.9378 | 1.8461
WEST POINT 110136674 | WEST | WEST POINT 1101 | STOCKTON | 9.4896 | 86.8002 | 98.6% | 2 | 6 | 100% | 100% | 0 | 0.39381 | 102.1389 | 40.2233 | 4.2387
PIKE CITY 1101CB | PIKE | PIKE CITY 1101 | SIERRA | 19.8554 | 96.0592 | 99.76% | 13 | 13 | 100% | 100% | 1 | 0.38542 | 102.1389 | 39.3662 | 1.9826
STANISLAUS 17021804 | STANI | STANISLAUS 1702 | YOSEMITE | 8.3693 | 84.6121 | 100% | 9 | 6 | 100% | 100% | 0 | 0.38328 | 102.1389 | 39.1474 | 4.6775
PINE GROVE 110213438 | PINE | PINE GROVE 1102 | STOCKTON | 16.4176 | 84.6476 | 100% | 6 | 6 | 100% | 85.87% | 0 | 0.38268 | 102.1389 | 39.087 | 2.3808
CHALLENGE 1101CB | CHALL | CHALLENGE 1101 | NORTH VALLEY | 16.6203 | 96.135 | 99.73% | 4 | 3 | 100% | 100% | 0 | 0.37094 | 102.1389 | 37.8874 | 2.2796
WEST POINT 11014706 | WEST | WEST POINT 1101 | STOCKTON | 11.5214 | 90.5528 | 100% | 4 | 4 | 100% | 100% | 0 | 0.36745 | 102.1389 | 37.5307 | 3.2575
ORO FINO 110276008 | ORO F | ORO FINO 1102 | NORTH VALLEY | 15.9665 | 80.1873 | 99.98% | 4 | 7 | 100% | 100% | 1 | 0.36557 | 102.1389 | 37.3387 | 2.3386
WYANDOTTE 11031976 | WYAND | WYANDOTTE 1103 | NORTH VALLEY | 23.9896 | 86.4323 | 100% | 4 | 6 | 100% | 100% | 0 | 0.43481 | 85.4511 | 37.155 | 1.5488
ORO FINO 11012022 | ORO F | ORO FINO 1101 | NORTH VALLEY | 24.1719 | 81.0032 | 94.33% | 6 | 13 | 100% | 100% | 1 | 0.36043 | 102.1389 | 36.814 | 1.523
PINE GROVE 11021222 | PINE | PINE GROVE 1102 | STOCKTON | 17.2284 | 80.3851 | 88.79% | 6 | 14 | 100% | 93.15% | 0 | 0.35881 | 102.1389 | 36.6489 | 2.1272
COLUMBIA HILL 11012212 | COLUM | COLUMBIA HILL 1101 | SIERRA | 9.1875 | 95.8225 | 100% | 9 | 3 | 100% | 100% | 0 | 0.35537 | 102.1389 | 36.2974 | 3.9507
CALISTOGA 1101736 | CALIS | CALISTOGA 1101 | NORTH BAY | 33.5094 | 79.1543 | 66.69% | 16 | 14 | 100% | 100% | 1 | 0.74565 | 47.6367 | 35.5203 | 1.06
SALT SPRINGS 21024796 | SALT | SALT SPRINGS 2102 | STOCKTON | 7.1845 | 85.6584 | 100% | 4 | 1 | 100% | 100% | 0 | 0.34533 | 102.1389 | 35.2718 | 4.9094
PUEBLO 2102792 | PUEBL | PUEBLO 2102 | NORTH BAY | 17.9619 | 85.883 | 96.12% | 13 | 4 | 86.21% | 100% | 0 | 0.41118 | 85.4511 | 35.1362 | 1.9561
BIG BEND 11021972 | BIG B | BIG BEND 1102 | NORTH VALLEY | 21.0549 | 95.6632 | 96.1% | 4 | 6 | 100% | 100% | 0 | 0.40978 | 85.4511 | 35.0163 | 1.6631
EL DORADO PH 210219562 | EL DO | EL DORADO PH 2102 | SIERRA | 14.8519 | 89.5871 | 100% | 10 | 7 | 100% | 100% | 0 | 0.33748 | 102.1389 | 34.4696 | 2.3209
CHALLENGE 11021064 | CHALL | CHALLENGE 1102 | NORTH VALLEY | 19.9876 | 84.0327 | 100% | 6 | 2 | 100% | 94.93% | 0 | 0.33496 | 102.1389 | 34.2124 | 1.7117
CAMP EVERS 21065020 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 15.2094 | 69.3374 | 87.56% | 19 | 11 | 100% | 100% | 1 | 0.52218 | 65.3912 | 34.1458 | 2.2451
MOLINO 1102318 | MOLIN | MOLINO 1102 | SONOMA | 19.2803 | 89.5364 | 61.35% | 11 | 8 | 100% | 100% | 1 | 0.39524 | 85.4511 | 33.7736 | 1.7517
WEST POINT 110113444 | WEST | WEST POINT 1101 | STOCKTON | 16.633 | 82.1566 | 100% | 5 | 15 | 100% | 100% | 0 | 0.31924 | 102.1389 | 32.6072 | 1.9604
EL DORADO PH 2101CB | EL DO | EL DORADO PH 2101 | SIERRA | 16.7983 | 90.3781 | 74.43% | 12 | 5 | 100% | 100% | 0 | 0.3182 | 102.1389 | 32.5001 | 1.9347
CAMP EVERS 210660124 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 22.5394 | 63.6568 | 80.34% | 20 | 3 | 100% | 100% | 1 | 0.4923 | 65.3912 | 32.1923 | 1.4283
WILLITS 110434008 | WILLI | WILLITS 1104 | HUMBOLDT | 22.9278 | 77.1143 | 100% | 14 | 12 | 100% | 97.76% | 0 | 0.3764 | 85.4511 | 32.1635 | 1.4028
WHITMORE 11011598 | WHITM | WHITMORE 1101 | NORTH VALLEY | 33.6511 | 71.823 | 81.12% | 6 | 5 | 100% | 75.5% | 0 | 0.37493 | 85.4511 | 32.038 | 0.95206
CHALLENGE 11015460 | CHALL | CHALLENGE 1101 | NORTH VALLEY | 11.8115 | 93.9312 | 100% | 4 | 4 | 100% | 100% | 0 | 0.31277 | 102.1389 | 31.9457 | 2.7046
EL DORADO PH 210219542 | EL DO | EL DORADO PH 2102 | SIERRA | 9.4332 | 77.5631 | 77.77% | 6 | 4 | 100% | 100% | 0 | 0.31239 | 102.1389 | 31.907 | 3.3824
ALLEGHANY 1102CB | ALLEG | ALLEGHANY 1102 | SIERRA | 18.0939 | 92.7974 | 39.16% | 4 | 24 | 100% | 100% | 1 | 0.48104 | 65.3912 | 31.4559 | 1.7385
COLUMBIA HILL 1101764 | COLUM | COLUMBIA HILL 1101 | SIERRA | 14.8572 | 87.6214 | 100% | 5 | 10 | 100% | 100% | 1 | 0.36409 | 85.4511 | 31.1119 | 2.0941
MONTE RIO 1113524 | MONTE | MONTE RIO 1113 | SONOMA | 6.2702 | 72.7249 | 28.23% | 16 | 4 | 100% | 100% | 0 | 0.30334 | 102.1389 | 30.9824 | 4.9412
WEST POINT 1101L373 | WEST | WEST POINT 1101 | STOCKTON | 7.4413 | 94.6949 | 100% | 2 | 9 | 100% | 100% | 0 | 0.30215 | 102.1389 | 30.8608 | 4.1473
STANISLAUS 170237276 | STANI | STANISLAUS 1702 | YOSEMITE | 11.7226 | 82.7291 | 100% | 8 | 9 | 100% | 100% | 0 | 0.30163 | 102.1389 | 30.8083 | 2.6281
BRUNSWICK 11052130 | BRUNS | BRUNSWICK 1105 | SIERRA | 14.272 | 96.3517 | 99.69% | 5 | 6 | 100% | 100% | 0 | 0.29909 | 102.1389 | 30.5492 | 2.1405
STANISLAUS 170275348 | STANI | STANISLAUS 1702 | YOSEMITE | 5.3962 | 93.3092 | 100% | 1 | 9 | 100% | 100% | 0 | 0.29738 | 102.1389 | 30.3738 | 5.6287
ALLEGHANY 1101VR816 | ALLEG | ALLEGHANY 1101 | SIERRA | 4.1512 | 96.2894 | 73.9% | 6 | 8 | 100% | 100% | 0 | 0.294 | 102.1389 | 30.0293 | 7.2339
CHALLENGE 110198174 | CHALL | CHALLENGE 1101 | NORTH VALLEY | 12.1176 | 88.3942 | 100% | 4 | 1 | 100% | 100% | 0 | 0.34958 | 85.4511 | 29.8716 | 2.4651
BIG BEND 1101CB | BIG B | BIG BEND 1101 | NORTH VALLEY | 23.102 | 80.4105 | 77.16% | 7 | 10 | 100% | 100% | 1 | 0.34627 | 85.4511 | 29.5895 | 1.2808
BONNIE NOOK 1101CB | BONNI | BONNIE NOOK 1101 | SIERRA | 14.7401 | 89.8232 | 47.01% | 8 | 12 | 100% | 100% | 0 | 0.28941 | 102.1389 | 29.5604 | 2.0054
MIWUK 17026018 | MIWUK | MIWUK 1702 | YOSEMITE | 19.5117 | 86.3615 | 100% | 3 | 8 | 100% | 100% | 0 | 0.28867 | 102.1389 | 29.4843 | 1.5111
MIWUK 1702CB | MIWUK | MIWUK 1702 | YOSEMITE | 10.2382 | 90.3115 | 82.25% | 5 | 6 | 100% | 100% | 0 | 0.28839 | 102.1389 | 29.4558 | 2.877
COLUMBIA HILL 110135424 | COLUM | COLUMBIA HILL 1101 | SIERRA | 13.9113 | 71.6588 | 100% | 8 | 11 | 100% | 100% | 1 | 0.44882 | 65.3912 | 29.3488 | 2.1097
RINCON 1103474 | RINCO | RINCON 1103 | SONOMA | 18.561 | 87.2265 | 99.41% | 8 | 6 | 100% | 100% | 0 | 0.44799 | 65.3912 | 29.2949 | 1.5783
APPLE HILL 110497086 | APPLE | APPLE HILL 1104 | SIERRA | 25.6232 | 83.1632 | 99.98% | 8 | 5 | 100% | 100% | 1 | 0.28482 | 102.1389 | 29.0916 | 1.1354
PARADISE 11062084 | PARAD | PARADISE 1106 | NORTH VALLEY | 11.3566 | 77.2193 | 100% | 4 | 9 | 100% | 100% | 1 | 0.28289 | 102.1389 | 28.8939 | 2.5442
MIRABEL 1101298 | MIRAB | MIRABEL 1101 | SONOMA | 12.8273 | 89.1513 | 37.51% | 16 | 9 | 99.59% | 100% | 0 | 0.33734 | 85.4511 | 28.8258 | 2.2472
PIKE CITY 11011730 | PIKE | PIKE CITY 1101 | SIERRA | 8.599 | 94.8581 | 99.91% | 4 | 2 | 100% | 100% | 0 | 0.33402 | 85.4511 | 28.5428 | 3.3193
MONTE RIO 1112120 | MONTE | MONTE RIO 1112 | SONOMA | 6.8692 | 90.5188 | 64.49% | 17 | 9 | 100% | 100% | 0 | 0.33336 | 85.4511 | 28.4857 | 4.1469
CALISTOGA 110143924 | CALIS | CALISTOGA 1101 | NORTH BAY | 4.45 | 80.4513 | 94.31% | 6 | 6 | 47.81% | 100% | 0 | 0.32892 | 85.4511 | 28.1068 | 6.3162
BRUNSWICK 11041020 | BRUNS | BRUNSWICK 1104 | SIERRA | 28.7777 | 77.1 | 87.63% | 9 | 9 | 100% | 83.4% | 1 | 0.27484 | 102.1389 | 28.0721 | 0.97548
SYCAMORE CREEK 11112268 | SYCAM | SYCAMORE CREEK 1111 | NORTH VALLEY | 22.2352 | 96.7379 | 99.96% | 3 | 8 | 100% | 99.53% | 1 | 0.2744 | 102.1389 | 28.0273 | 1.2605
APPLE HILL 110413512 | APPLE | APPLE HILL 1104 | SIERRA | 27.848 | 80.8375 | 86.09% | 15 | 14 | 89.98% | 77.01% | 0 | 0.27338 | 102.1389 | 27.9228 | 1.0027
COLUMBIA HILL 11018233 | COLUM | COLUMBIA HILL 1101 | SIERRA | 5.0061 | 92.4069 | 99.94% | 1 | 3 | 100% | 100% | 0 | 0.27044 | 102.1389 | 27.6227 | 5.5178
SILVERADO 2104632 | SILVE | SILVERADO 2104 | NORTH BAY | 18.1239 | 77.5447 | 73.72% | 15 | 5 | 96.09% | 100% | 1 | 0.42045 | 65.3912 | 27.494 | 1.517
MIWUK 170238218 | MIWUK | MIWUK 1702 | YOSEMITE | 10.8246 | 77.698 | 74.49% | 4 | 9 | 100% | 100% | 0 | 0.26818 | 102.1389 | 27.3914 | 2.5305
OAKHURST 110310190 | OAKHU | OAKHURST 1103 | YOSEMITE | 11.5271 | 95.517 | 27.67% | 12 | 10 | 100% | 100% | 1 | 0.26739 | 102.1389 | 27.311 | 2.3693
ORO FINO 11022560 | ORO F | ORO FINO 1102 | NORTH VALLEY | 16.7196 | 97.5242 | 100% | 5 | 6 | 100% | 81.54% | 1 | 0.26733 | 102.1389 | 27.3045 | 1.6331
ALLEGHANY 1101806 | ALLEG | ALLEGHANY 1101 | SIERRA | 11.8065 | 97.171 | 100% | 0 | 7 | 100% | 100% | 0 | 0.2646 | 102.1389 | 27.0262 | 2.2891
LOS GATOS 110760118 | LOS G | LOS GATOS 1107 | DE ANZA | 20.0923 | 57.6089 | 83.76% | 25 | 2 | 100% | 100% | 1 | 0.5667 | 47.6367 | 26.9958 | 1.3436
KANAKA 110183288 | KANAK | KANAKA 1101 | NORTH VALLEY | 17.5828 | 90.1927 | 100% | 7 | 4 | 100% | 100% | 0 | 0.26111 | 102.1389 | 26.6692 | 1.5168
MIWUK 17018050 | MIWUK | MIWUK 1701 | YOSEMITE | 12.1253 | 91.2725 | 97.35% | 8 | 4 | 100% | 100% | 1 | 0.26086 | 102.1389 | 26.6441 | 2.1974
FORESTHILL 11022106 | FORES | FORESTHILL 1102 | SIERRA | 28.0974 | 67.1045 | 99.85% | 8 | 14 | 100% | 71.38% | 1 | 0.26076 | 102.1389 | 26.6336 | 0.9479
PARADISE 11062234 | PARAD | PARADISE 1106 | NORTH VALLEY | 8.8367 | 79.1592 | 100% | 3 | 8 | 100% | 100% | 0 | 0.30628 | 85.4511 | 26.1721 | 2.9618
ORO FINO 110265932 | ORO F | ORO FINO 1102 | NORTH VALLEY | 4.3114 | 96.8708 | 92.73% | 3 | 5 | 100% | 100% | 0 | 0.25228 | 102.1389 | 25.7678 | 5.9767
KANAKA 110165606 | KANAK | KANAKA 1101 | NORTH VALLEY | 12.8238 | 91.9272 | 96.33% | 13 | 4 | 100% | 100% | 1 | 0.30035 | 85.4511 | 25.6651 | 2.0014
VOLTA 110253130 | VOLTA | VOLTA 1102 | NORTH VALLEY | 13.8858 | 76.696 | 100% | 3 | 7 | 100% | 92.09% | 0 | 0.29929 | 85.4511 | 25.5745 | 1.8418
STANISLAUS 17024905 | STANI | STANISLAUS 1702 | YOSEMITE | 2.3422 | 97.8548 | 99.88% | 2 | 2 | 100% | 100% | 0 | 0.25032 | 102.1389 | 25.567 | 10.9156
MONTE RIO 1113202 | MONTE | MONTE RIO 1113 | SONOMA | 5.2496 | 89.4483 | 68.59% | 13 | 9 | 100% | 100% | 0 | 0.2988 | 85.4511 | 25.5328 | 4.8637
MOLINO 1102104 | MOLIN | MOLINO 1102 | SONOMA | 21.7365 | 84.6047 | 53.29% | 22 | 10 | 100% | 100% | 1 | 0.38423 | 65.3912 | 25.1255 | 1.1559
DRUM 1101CB | DRUM | DRUM 1101 | SIERRA | 2.1059 | 96.8742 | 100% | 2 | 0 | 100% | 100% | 0 | 0.2937 | 85.4511 | 25.0967 | 11.9172
MIWUK 1702S1547 | MIWUK | MIWUK 1702 | YOSEMITE | 2.7688 | 85.4231 | 100% | 1 | 5 | 100% | 100% | 0 | 0.24392 | 102.1389 | 24.9141 | 8.998
ORO FINO 11022096 | ORO F | ORO FINO 1102 | NORTH VALLEY | 14.098 | 93.7734 | 100% | 8 | 2 | 100% | 100% | 0 | 0.28682 | 85.4511 | 24.5089 | 1.7385
FORESTHILL 11011820 | FORES | FORESTHILL 1101 | SIERRA | 5.5828 | 97.995 | 99.82% | 0 | 0 | 100% | 100% | 1 | 0.23777 | 102.1389 | 24.2855 | 4.3501
WEST POINT 11021303 | WEST | WEST POINT 1102 | STOCKTON | 15.8188 | 90.4672 | 99.8% | 4 | 11 | 100% | 100% | 0 | 0.28235 | 85.4511 | 24.1273 | 1.5252
WOODSIDE 11018974 | WOODS | WOODSIDE 1101 | PENINSULA | 13.435 | 54.2631 | 29.29% | 40 | 16 | 100% | 100% | 0 | 0.50532 | 47.6367 | 24.0717 | 1.7917
BUCKS CREEK 11032414 | BUCKS | BUCKS CREEK 1103 | NORTH VALLEY | 6.1362 | 87.0222 | 100% | 6 | 5 | 76.6% | 80.44% | 0 | 0.28097 | 85.4511 | 24.0095 | 3.9127
ELECTRA 110277204 | ELECT | ELECTRA 1102 | STOCKTON | 18.6351 | 80.9647 | 100% | 2 | 8 | 100% | 100% | 0 | 0.27848 | 85.4511 | 23.7964 | 1.277
APPLE HILL 210297982 | APPLE | APPLE HILL 2102 | SIERRA | 10.1443 | 88.7232 | 100% | 1 | 1 | 100% | 100% | 0 | 0.23278 | 102.1389 | 23.7764 | 2.3438
STANISLAUS 1702L611 | STANI | STANISLAUS 1702 | YOSEMITE | 2.9906 | 79.5104 | 100% | 2 | 2 | 100% | 100% | 0 | 0.27802 | 85.4511 | 23.757 | 7.9438
SALT SPRINGS 2102L485 | SALT | SALT SPRINGS 2102 | STOCKTON | 0.82893 | 87.1462 | 100% | 0 | 2 | 100% | 100% | 0 | 0.23224 | 102.1389 | 23.721 | 28.6164
EL DORADO PH 21026645 | EL DO | EL DORADO PH 2102 | SIERRA | 4.2976 | 91.6097 | 86.84% | 4 | 3 | 100% | 100% | 0 | 0.23151 | 102.1389 | 23.6465 | 5.5023
MIWUK 1702S2247 | MIWUK | MIWUK 1702 | YOSEMITE | 1.4764 | 81.7159 | 100% | 2 | 2 | 100% | 100% | 0 | 0.23034 | 102.1389 | 23.5271 | 15.9357
WOODACRE 1101404 | WOODA | WOODACRE 1101 | NORTH BAY | 12.4182 | 78.1166 | 26.88% | 20 | 20 | 100% | 92.07% | 0 | 0.22897 | 102.1389 | 23.3871 | 1.8833
MIDDLETOWN 11011079 | MIDDL | MIDDLETOWN 1101 | HUMBOLDT | 3.6508 | 95.1699 | 100% | 2 | 3 | 100% | 100% | 1 | 0.22672 | 102.1389 | 23.1571 | 6.3431
SPRING GAP 170210720 | SPRIN | SPRING GAP 1702 | YOSEMITE | 4.7512 | 90.1119 | 100% | 2 | 3 | 100% | 100% | 0 | 0.27005 | 85.4511 | 23.076 | 4.8569
BRUNSWICK 11053611 | BRUNS | BRUNSWICK 1105 | SIERRA | 1.6138 | 98 | 100% | 0 | 3 | 100% | 100% | 0 | 0.22548 | 102.1389 | 23.03 | 14.2704
BRUNSWICK 11032200 | BRUNS | BRUNSWICK 1103 | SIERRA | 5.571 | 90.9239 | 99.7% | 2 | 4 | 100% | 100% | 0 | 0.22488 | 102.1389 | 22.9688 | 4.1229
MONTE RIO 111164758 | MONTE | MONTE RIO 1111 | SONOMA | 10.5474 | 85.3267 | 35.52% | 9 | 6 | 100% | 100% | 0 | 0.26838 | 85.4511 | 22.933 | 2.1743
WEST POINT 11024790 | WEST | WEST POINT 1102 | STOCKTON | 28.9338 | 75.0976 | 91.62% | 9 | 12 | 100% | 75.46% | 1 | 0.35051 | 65.3912 | 22.92 | 0.79215
ORO FINO 110239154 | ORO F | ORO FINO 1102 | NORTH VALLEY | 0.88251 | 98 | 100% | 3 | 0 | 100% | 100% | 1 | 0.22144 | 102.1389 | 22.618 | 25.6292
FORESTHILL 110137238 | FORES | FORESTHILL 1101 | SIERRA | 11.5057 | 97.4901 | 100% | 2 | 5 | 100% | 100% | 1 | 0.26202 | 85.4511 | 22.3899 | 1.946
BRUNSWICK 1105 | BRUNS | BRUNSWICK 1105 | SIERRA | 0.032568 | 98 | 100% | 2 | 0 | 100% | 100% | 0 | 0.21917 | 102.1389 | 22.3858 | 687.346
WEST POINT 1101L2219 | WEST | WEST POINT 1101 | STOCKTON | 3.4094 | 90.8965 | 100% | 0 | 2 | 100% | 100% | 0 | 0.26183 | 85.4511 | 22.3739 | 6.5625
WILLITS 1104504 | WILLI | WILLITS 1104 | HUMBOLDT | 22.5336 | 70.0895 | 92.93% | 13 | 8 | 100% | 60.82% | 1 | 0.2605 | 85.4511 | 22.2602 | 0.98787
WEST POINT 110112256 | WEST | WEST POINT 1101 | STOCKTON | 6.5157 | 90.9675 | 74.92% | 4 | 4 | 100% | 100% | 0 | 0.21727 | 102.1389 | 22.192 | 3.406
CHALLENGE 110113026 | CHALL | CHALLENGE 1101 | NORTH VALLEY | 7.8248 | 63.8642 | 100% | 1 | 1 | 97.67% | 96.11% | 0 | 0.25947 | 85.4511 | 22.1717 | 2.8335
WILLITS 110391810 | WILLI | WILLITS 1103 | HUMBOLDT | 29.3984 | 69.6626 | 100% | 19 | 14 | 100% | 85.03% | 1 | 0.25809 | 85.4511 | 22.0543 | 0.75019
SALT SPRINGS 2102L491 | SALT | SALT SPRINGS 2102 | STOCKTON | 2.2143 | 88.9765 | 100% | 2 | 2 | 100% | 100% | 0 | 0.21581 | 102.1389 | 22.0423 | 9.9545
DOWNIEVILLE DIESEL 1101CB | DOWNI | DOWNIEVILLE DIESEL 1101 | SIERRA | 0.022979 | 98 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21467 | 102.1389 | 21.9265 | 954.1952
DOWNIEVILLE DIESEL 11011101/2 | DOWNI | DOWNIEVILLE DIESEL 1101 | SIERRA | 0.0097328 | 98 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21467 | 102.1389 | 21.9265 | 2252.843
WILLITS 1103 | WILLI | WILLITS 1103 | HUMBOLDT | 0.065999 | 98 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21467 | 102.1389 | 21.9265 | 332.2223
SILVERADO 210478268 | SILVE | SILVERADO 2104 | NORTH BAY | 11.9793 | 67.2464 | 60.11% | 10 | 4 | 100% | 100% | 0 | 0.3351 | 65.3912 | 21.9127 | 1.8292
VOLTA 11029742 | VOLTA | VOLTA 1102 | NORTH VALLEY | 9.1189 | 78.986 | 100% | 1 | 2 | 100% | 94.08% | 0 | 0.25585 | 85.4511 | 21.8624 | 2.3975
AUBERRY 1101R324 | AUBER | AUBERRY 1101 | FRESNO | 10.7908 | 83.7222 | 99.89% | 3 | 1 | 100% | 100% | 0 | 0.25584 | 85.4511 | 21.8618 | 2.026
PUEBLO 21033583 | PUEBL | PUEBLO 2103 | NORTH BAY | 9.4952 | 94.4646 | 44.31% | 6 | 11 | 100% | 100% | 1 | 0.25545 | 85.4511 | 21.8289 | 2.2989
FORESTHILL 1101CB | FORES | FORESTHILL 1101 | SIERRA | 9.3514 | 78.4608 | 92.08% | 4 | 4 | 100% | 100% | 0 | 0.33375 | 65.3912 | 21.8245 | 2.3338
WEST POINT 11021535 | WEST | WEST POINT 1102 | STOCKTON | 3.0651 | 85.9665 | 100% | 1 | 1 | 100% | 100% | 0 | 0.2539 | 85.4511 | 21.6957 | 7.0784
OAKHURST 110310723 | OAKHU | OAKHURST 1103 | YOSEMITE | 0.0026429 | 95 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21123 | 102.1389 | 21.5751 | 8163.5107
MONTE RIO 11138299 | MONTE | MONTE RIO 1113 | SONOMA | 1.1981 | 94.52 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21069 | 102.1389 | 21.5193 | 17.9617
LOS GATOS 1107LA60 | LOS G | LOS GATOS 1107 | DE ANZA | 8.6011 | 90.5119 | 96.22% | 1 | 0 | 100% | 100% | 0 | 0.24993 | 85.4511 | 21.3565 | 2.483
STANISLAUS 17021850 | STANI | STANISLAUS 1702 | YOSEMITE | 13.465 | 54.7158 | 83.98% | 13 | 14 | 100% | 100% | 0 | 0.32626 | 65.3912 | 21.3346 | 1.5845
STANISLAUS 1702L5381 | STANI | STANISLAUS 1702 | YOSEMITE | 1.2094 | 89.7596 | 100% | 0 | 1 | 100% | 100% | 0 | 0.20877 | 102.1389 | 21.3233 | 17.6315
STANISLAUS 170237278 | STANI | STANISLAUS 1702 | YOSEMITE | 6.8063 | 74.4331 | 100% | 1 | 5 | 100% | 100% | 0 | 0.2075 | 102.1389 | 21.1942 | 3.1139
APPLE HILL 21027502 | APPLE | APPLE HILL 2102 | SIERRA | 23.0839 | 77.5827 | 99.99% | 4 | 7 | 100% | 82.95% | 0 | 0.24712 | 85.4511 | 21.1165 | 0.91477
SALT SPRINGS 2102L7283 | SALT | SALT SPRINGS 2102 | STOCKTON | 0.66272 | 87.1614 | 100% | 0 | 1 | 100% | 100% | 0 | 0.20585 | 102.1389 | 21.0249 | 31.7252
STANISLAUS 1702 | STANI | STANISLAUS 1702 | YOSEMITE | 0.0021222 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 102.1389 | 20.9988 | 9894.6086
WEST POINT 1101L3355 | WEST | WEST POINT 1101 | STOCKTON | 2.2225 | 89.0928 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20458 | 102.1389 | 20.8954 | 9.4019
FULTON 1107214 | FULTO | FULTON 1107 | SONOMA | 12.2376 | 47.3525 | 63.1% | 7 | 19 | 100% | 100% | 0 | 0.43673 | 47.6367 | 20.8046 | 1.7001
WEST POINT 1101L1969 | WEST | WEST POINT 1101 | STOCKTON | 1.0816 | 86.0606 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20122 | 102.1389 | 20.5528 | 19.0015
SHINGLE SPRINGS 210912392 | SHING | SHINGLE SPRINGS 2109 | SIERRA | 14.9169 | 46.1952 | 91.69% | 7 | 8 | 100% | 100% | 0 | 0.31183 | 65.3912 | 20.3908 | 1.367
ALLEGHANY 1101CB | ALLEG | ALLEGHANY 1101 | SIERRA | 4.3289 | 94.1851 | 45.96% | 2 | 2 | 100% | 100% | 0 | 0.23753 | 85.4511 | 20.2969 | 4.6887
MONTE RIO 11131991 | MONTE | MONTE RIO 1113 | SONOMA | 7.0583 | 93.2573 | 64.98% | 0 | 4 | 100% | 100% | 0 | 0.19767 | 102.1389 | 20.1896 | 2.8604
CHALLENGE 11025462 | CHALL | CHALLENGE 1102 | NORTH VALLEY | 23.3648 | 66.9386 | 100% | 8 | 5 | 100% | 97.29% | 1 | 0.30821 | 65.3912 | 20.154 | 0.86258
FORESTHILL 110175340 | FORES | FORESTHILL 1101 | SIERRA | 4.974 | 93.375 | 69.57% | 0 | 2 | 100% | 100% | 0 | 0.19715 | 102.1389 | 20.1366 | 4.0483
VOLTA 11021504 | VOLTA | VOLTA 1102 | NORTH VALLEY | 8.3043 | 82.9659 | 100% | 2 | 3 | 100% | 100% | 0 | 0.23562 | 85.4511 | 20.1342 | 2.4245
VOLTA 110280982 | VOLTA | VOLTA 1102 | NORTH VALLEY | 0.52007 | 92.783 | 99.45% | 2 | 0 | 100% | 100% | 1 | 0.23557 | 85.4511 | 20.1294 | 38.7056
ORO FINO 11022090 | ORO F | ORO FINO 1102 | NORTH VALLEY | 14.7385 | 94.0575 | 68.97% | 5 | 5 | 100% | 100% | 1 | 0.1964 | 102.1389 | 20.0604 | 1.3611
WOODSIDE 11018884 | WOODS | WOODSIDE 1101 | PENINSULA | 7.7125 | 85.1128 | 91.16% | 13 | 3 | 100% | 100% | 0 | 0.30526 | 65.3912 | 19.9613 | 2.5882
EL DORADO PH 2102CB | EL DO | EL DORADO PH 2102 | SIERRA | 5.6703 | 93.9988 | 79.03% | 2 | 2 | 100% | 100% | 0 | 0.19325 | 102.1389 | 19.7388 | 3.4811
PINE GROVE 11023172 | PINE | PINE GROVE 1102 | STOCKTON | 36.8095 | 74.2107 | 73.54% | 9 | 20 | 100% | 71.26% | 1 | 0.23027 | 85.4511 | 19.6764 | 0.53455
EL DORADO PH 210119612 | EL DO | EL DORADO PH 2101 | SIERRA | 9.1713 | 87.7197 | 45.56% | 7 | 1 | 100% | 100% | 0 | 0.19221 | 102.1389 | 19.6316 | 2.1406
SALT SPRINGS 210297924 | SALT | SALT SPRINGS 2102 | STOCKTON | 5.0873 | 68.1168 | 100% | 5 | 4 | 100% | 100% | 0 | 0.22834 | 85.4511 | 19.5118 | 3.8354
WILLITS 1104934 | WILLI | WILLITS 1104 | HUMBOLDT | 30.5846 | 72.5028 | 89.66% | 17 | 12 | 100% | 39.29% | 1 | 0.29588 | 65.3912 | 19.3479 | 0.6326
KANAKA 11011034 | KANAK | KANAKA 1101 | NORTH VALLEY | 13.1567 | 96.9359 | 65.02% | 4 | 2 | 100% | 100% | 0 | 0.22603 | 85.4511 | 19.3146 | 1.468
PINE GROVE 110235576 | PINE | PINE GROVE 1102 | STOCKTON | 7.978 | 78.3459 | 100% | 3 | 1 | 100% | 100% | 0 | 0.22493 | 85.4511 | 19.2204 | 2.4092
MIWUK 17028130 | MIWUK | MIWUK 1702 | YOSEMITE | 9.8769 | 52.0925 | 100% | 2 | 8 | 100% | 100% | 0 | 0.29268 | 65.3912 | 19.1389 | 1.9377
CAMP EVERS 210510214 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 14.0274 | 70.1914 | 71.02% | 31 | 1 | 100% | 100% | 0 | 0.29021 | 65.3912 | 18.9774 | 1.3529
SILVERADO 2105658898 | SILVE | SILVERADO 2105 | NORTH BAY | 17.239 | 89.5362 | 92.68% | 6 | 3 | 99.53% | 97.17% | 1 | 0.28431 | 65.3912 | 18.5917 | 1.0785
STANISLAUS 17026028 | STANI | STANISLAUS 1702 | YOSEMITE | 5.3481 | 47.3801 | 91.01% | 3 | 4 | 100% | 100% | 0 | 0.28374 | 65.3912 | 18.5544 | 3.4693
BIG BASIN 110110720 | BIG B | BIG BASIN 1101 | CENTRAL COAST | 4.6838 | 66.6097 | 31.56% | 7 | 1 | 100% | 100% | 0 | 0.21501 | 85.4511 | 18.3729 | 3.9226
FORT ROSS 112170288 | FORT | FORT ROSS 1121 | SONOMA | 11.744 | 93.8091 | 82.61% | 5 | 5 | 100% | 100% | 0 | 0.2145 | 85.4511 | 18.3292 | 1.5607
MOUNTAIN QUARRIES 21011184 | MOUNT | MOUNTAIN QUARRIES 2101 | SIERRA | 11.7903 | 85.233 | 82.22% | 1 | 4 | 100% | 100% | 0 | 0.21412 | 85.4511 | 18.2964 | 1.5518
PARADISE 11011155 | PARAD | PARADISE 1101 | NORTH VALLEY | 0.42051 | 84.3729 | 100% | 5 | 1 | 100% | 100% | 0 | 0.21365 | 85.4511 | 18.257 | 43.4167
MONTE RIO 111153477 | MONTE | MONTE RIO 1111 | SONOMA | 2.1403 | 90.336 | 44.25% | 6 | 1 | 100% | 100% | 0 | 0.21276 | 85.4511 | 18.1807 | 8.4943
WILLITS 1103968 | WILLI | WILLITS 1103 | HUMBOLDT | 24.6966 | 68.3381 | 85.93% | 14 | 10 | 88.86% | 68.54% | 1 | 0.21234 | 85.4511 | 18.1447 | 0.73471
SALT SPRINGS 210237300 | SALT | SALT SPRINGS 2102 | STOCKTON | 6.9933 | 87.6909 | 82.66% | 1 | 2 | 100% | 100% | 0 | 0.21052 | 85.4511 | 17.9888 | 2.5723
MOLINO 1102396 | MOLIN | MOLINO 1102 | SONOMA | 16.1282 | 58.4363 | 35.51% | 9 | 10 | 100% | 100% | 0 | 0.275 | 65.3912 | 17.9823 | 1.115
STELLING 111060094 | STELL | STELLING 1110 | DE ANZA | 13.9579 | 79.5 | 89.71% | 7 | 6 | 100% | 94.63% | 1 | 0.27357 | 65.3912 | 17.8888 | 1.2816
BIG TREES 04025300 | BIG T | BIG TREES 0402 | CENTRAL COAST | 9.8017 | 22.3436 | 42.94% | 37 | 4 | 100% | 100% | 1 | 0.37529 | 47.6367 | 17.8776 | 1.8239
FITCH MOUNTAIN 111324918 | FITCH | FITCH MOUNTAIN 1113 | SONOMA | 5.4494 | 96.6209 | 46.61% | 13 | 1 | 100% | 100% | 0 | 0.17452 | 102.1389 | 17.8255 | 3.2711
AUBERRY 1101D4982 | AUBER | AUBERRY 1101 | FRESNO | 2.6789 | 91.9989 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20783 | 85.4511 | 17.7595 | 6.6293
MOLINO 1102658 | MOLIN | MOLINO 1102 | SONOMA | 10.901 | 83.5071 | 77.94% | 19 | 4 | 100% | 73.87% | 0 | 0.26881 | 65.3912 | 17.5775 | 1.6125
WEST POINT 11021391 | WEST | WEST POINT 1102 | STOCKTON | 3.974 | 89.103 | 100% | 2 | 3 | 100% | 100% | 0 | 0.26869 | 65.3912 | 17.57 | 4.4213
WEST POINT 1101 | WEST | WEST POINT 1101 | STOCKTON | 0.004924 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 85.4511 | 17.5679 | 3567.8364
MONTE RIO 1113678 | MONTE | MONTE RIO 1113 | SONOMA | 1.8444 | 89.0499 | 49.28% | 0 | 1 | 100% | 100% | 0 | 0.20505 | 85.4511 | 17.5214 | 9.4996
SAN RAFAEL 11081250 | SAN R | SAN RAFAEL 1108 | NORTH BAY | 3.5796 | 93.2481 | 59.75% | 1 | 1 | 100% | 100% | 1 | 0.20419 | 85.4511 | 17.4483 | 4.8744
BRUNSWICK 110584480 | BRUNS | BRUNSWICK 1105 | SIERRA | 4.5786 | 96.5256 | 65.31% | 1 | 0 | 100% | 100% | 0 | 0.17078 | 102.1389 | 17.4429 | 3.8097
MONTE RIO 1113320 | MONTE | MONTE RIO 1113 | SONOMA | 2.745 | 95.3298 | 21.97% | 16 | 1 | 100% | 100% | 1 | 0.16899 | 102.1389 | 17.2604 | 6.2878
BRUNSWICK 11052204 | BRUNS | BRUNSWICK 1105 | SIERRA | 7.2073 | 87.5526 | 78.12% | 3 | 0 | 100% | 100% | 0 | 0.2017 | 85.4511 | 17.2351 | 2.3913
BONNIE NOOK 110186696 | BONNI | BONNIE NOOK 1101 | SIERRA | 9.7026 | 94.616 | 77.04% | 2 | 5 | 100% | 100% | 0 | 0.2013 | 85.4511 | 17.2011 | 1.7728
MONTE RIO 11111703 | MONTE | MONTE RIO 1111 | SONOMA | 1.2714 | 84.0743 | 95.02% | 2 | 1 | 100% | 100% | 0 | 0.20007 | 85.4511 | 17.096 | 13.4466
KONOCTI 1102532 | KONOC | KONOCTI 1102 | HUMBOLDT | 9.613 | 73.4923 | 78.9% | 8 | 7 | 100% | 100% | 1 | 0.20006 | 85.4511 | 17.0951 | 1.7783
MONTE RIO 1113652 | MONTE | MONTE RIO 1113 | SONOMA | 1.6252 | 74.26 | 59.28% | 4 | 0 | 100% | 100% | 0 | 0.16674 | 102.1389 | 17.0307 | 10.479
MIDDLETOWN 11014646 | MIDDL | MIDDLETOWN 1101 | HUMBOLDT | 18.5612 | 85.1867 | 99.86% | 4 | 10 | 100% | 100% | 0 | 0.35694 | 47.6367 | 17.0035 | 0.91608
MOLINO 110266006 | MOLIN | MOLINO 1102 | SONOMA | 9.0487 | 82.4735 | 54.27% | 8 | 4 | 100% | 100% | 1 | 0.25799 | 65.3912 | 16.8704 | 1.8644
BRUNSWICK 11062796 | BRUNS | BRUNSWICK 1106 | SIERRA | 19.8739 | 59.7898 | 71.67% | 4 | 4 | 100% | 99.1% | 0 | 0.19738 | 85.4511 | 16.8661 | 0.84865
MIDDLETOWN 1101614 | MIDDL | MIDDLETOWN 1101 | HUMBOLDT | 1.393 | 87.6673 | 76.7% | 0 | 1 | 100% | 100% | 0 | 0.19696 | 85.4511 | 16.8302 | 12.0816
MONTE RIO 111215401 | MONTE | MONTE RIO 1112 | SONOMA | 0.86292 | 85.2793 | 87.8% | 1 | 3 | 100% | 100% | 0 | 0.19647 | 85.4511 | 16.7884 | 19.4554
PINE GROVE 11029145 | PINE | PINE GROVE 1102 | STOCKTON | 2.9225 | 81.0955 | 99.74% | 0 | 0 | 100% | 100% | 0 | 0.19549 | 85.4511 | 16.7046 | 5.7159
WEST POINT 110234416 | WEST | WEST POINT 1102 | STOCKTON | 10.524 | 86.8553 | 100% | 7 | 3 | 100% | 100% | 1 | 0.25274 | 65.3912 | 16.5271 | 1.5704
WEST POINT 1102L3733 | WEST | WEST POINT 1102 | STOCKTON | 1.754 | 90.0843 | 100% | 0 | 0 | 100% | 94.99% | 0 | 0.19267 | 85.4511 | 16.464 | 9.3866
ORO FINO 11022556 | ORO F | ORO FINO 1102 | NORTH VALLEY | 6.6623 | 79.6419 | 97.8% | 0 | 4 | 100% | 100% | 0 | 0.25169 | 65.3912 | 16.4582 | 2.4703
MONTE RIO 1113180 | MONTE | MONTE RIO 1113 | SONOMA | 1.9463 | 80.579 | 66.84% | 3 | 0 | 100% | 100% | 0 | 0.1611 | 102.1389 | 16.4543 | 8.4541
WOODACRE 11011238 | WOODA | WOODACRE 1101 | NORTH BAY | 3.6828 | 94.4368 | 22.55% | 16 | 2 | 100% | 100% | 0 | 0.19161 | 85.4511 | 16.373 | 4.4459
PIKE CITY 11011720 | PIKE | PIKE CITY 1101 | SIERRA | 6.0835 | 93.4602 | 100% | 4 | 2 | 100% | 100% | 0 | 0.24982 | 65.3912 | 16.3363 | 2.6853
FITCH MOUNTAIN 11136751 | FITCH | FITCH MOUNTAIN 1113 | SONOMA | 22.3305 | 96.8838 | 61.93% | 21 | 1 | 100% | 75.68% | 1 | 0.19015 | 85.4511 | 16.2482 | 0.72763
STANISLAUS 17011331 | STANI | STANISLAUS 1701 | YOSEMITE | 4.3931 | 65.9467 | 100% | 5 | 0 | 100% | 100% | 0 | 0.18999 | 85.4511 | 16.2348 | 3.6955
DIAMOND SPRINGS 11071402 | DIAMO | DIAMOND SPRINGS 1107 | SIERRA | 44.1487 | 51.2712 | 86.92% | 1 | 21 | 100% | 76.75% | 0 | 0.24689 | 65.3912 | 16.1444 | 0.36568
PARADISE 110195728 | PARAD | PARADISE 1101 | NORTH VALLEY | 5.026 | 85.7627 | 38.06% | 1 | 6 | 100% | 100% | 0 | 0.18459 | 85.4511 | 15.7736 | 3.1384
MIWUK 17028090 | MIWUK | MIWUK 1702 | YOSEMITE | 4.0244 | 68.0843 | 40.03% | 1 | 7 | 100% | 100% | 0 | 0.1541 | 102.1389 | 15.7396 | 3.911
WEST POINT 110236676 | WEST | WEST POINT 1102 | STOCKTON | 16.994 | 84.9293 | 78.04% | 3 | 4 | 100% | 93.46% | 0 | 0.24051 | 65.3912 | 15.7272 | 0.92546
MONTE RIO 1113CB | MONTE | MONTE RIO 1113 | SONOMA | 4.5623 | 78.3408 | 32.43% | 11 | 4 | 100% | 100% | 0 | 0.18356 | 85.4511 | 15.6855 | 3.438
HALF MOON BAY 11012500 | HALF | HALF MOON BAY 1101 | PENINSULA | 5.7745 | 85.7148 | 84.59% | 4 | 6 | 82.94% | 96.61% | 1 | 0.2396 | 65.3912 | 15.668 | 2.7133
FULTON 1107604 | FULTO | FULTON 1107 | SONOMA | 17.5324 | 71.8219 | 64.8% | 2 | 17 | 100% | 100% | 0 | 0.3284 | 47.6367 | 15.6441 | 0.89229
CURTIS 1705843 | CURTI | CURTIS 1705 | YOSEMITE | 6.6016 | 54.6165 | 100% | 2 | 2 | 100% | 93.53% | 0 | 0.18286 | 85.4511 | 15.6252 | 2.3669
RINCON 1103568 | RINCO | RINCON 1103 | SONOMA | 12.8289 | 71.6958 | 48.67% | 11 | 11 | 100% | 100% | 0 | 0.32682 | 47.6367 | 15.5685 | 1.2135
MONTE RIO 111137520 | MONTE | MONTE RIO 1111 | SONOMA | 2.1617 | 88.6545 | 55.37% | 6 | 0 | 100% | 100% | 0 | 0.18002 | 85.4511 | 15.383 | 7.116
BRUNSWICK 11062104 | BRUNS | BRUNSWICK 1106 | SIERRA | 9.719 | 86.4087 | 57.37% | 4 | 1 | 100% | 100% | 0 | 0.17938 | 85.4511 | 15.3282 | 1.5771
MIRABEL 11027347 | MIRAB | MIRABEL 1102 | SONOMA | 0.81707 | 70.8306 | 59.55% | 4 | 1 | 100% | 100% | 0 | 0.14897 | 102.1389 | 15.2154 | 18.6219
LOS GATOS 11072917 | LOS G | LOS GATOS 1107 | DE ANZA | 7.7152 | 64.4105 | 89.16% | 10 | 1 | 100% | 100% | 0 | 0.23223 | 65.3912 | 15.1861 | 1.9683
SILVERADO 2104645 | SILVE | SILVERADO 2104 | NORTH BAY | 1.0113 | 86.4283 | 53.43% | 4 | 2 | 100% | 100% | 0 | 0.17771 | 85.4511 | 15.1851 | 15.0159
CALISTOGA 11011085 | CALIS | CALISTOGA 1101 | NORTH BAY | 2.0832 | 81.9335 | 72.65% | 1 | 1 | 100% | 100% | 0 | 0.23189 | 65.3912 | 15.1634 | 7.2788
PARADISE 11052214 | PARAD | PARADISE 1105 | NORTH VALLEY | 9.8398 | 58.7584 | 53.2% | 6 | 6 | 86.04% | 100% | 1 | 0.14771 | 102.1389 | 15.0873 | 1.5333
APPLE HILL 2102CB | APPLE | APPLE HILL 2102 | SIERRA | 41.3043 | 54.0794 | 88.14% | 11 | 9 | 100% | 60.25% | 1 | 0.23023 | 65.3912 | 15.0548 | 0.36448
SHINGLE SPRINGS 210961892 | SHING | SHINGLE SPRINGS 2109 | SIERRA | 30.1835 | 48.4981 | 100% | 2 | 8 | 100% | 100% | 0 | 0.31574 | 47.6367 | 15.0409 | 0.49832
SILVERADO 21051421 | SILVE | SILVERADO 2105 | NORTH BAY | 9.2052 | 85.2373 | 78.89% | 5 | 4 | 92.75% | 100% | 1 | 0.22901 | 65.3912 | 14.9751 | 1.6268
ORO FINO 1102CB | ORO F | ORO FINO 1102 | NORTH VALLEY | 2.0939 | 90.4736 | 31.39% | 1 | 0 | 100% | 100% | 0 | 0.1458 | 102.1389 | 14.8924 | 7.1122
CURTIS 17048140 | CURTI | CURTIS 1704 | YOSEMITE | 26.2498 | 65.6672 | 76.6% | 12 | 12 | 100% | 76.04% | 0 | 0.17401 | 85.4511 | 14.8696 | 0.56647
MIWUK 170193062 | MIWUK | MIWUK 1701 | YOSEMITE | 8.21 | 73.287 | 98.21% | 5 | 3 | 100% | 79.03% | 0 | 0.17366 | 85.4511 | 14.8399 | 1.8075
SILVERADO 2104722 | SILVE | SILVERADO 2104 | NORTH BAY | 7.8999 | 65.7561 | 63.09% | 2 | 4 | 100% | 100% | 0 | 0.17105 | 85.4511 | 14.6165 | 1.8502
MOLINO 1101322 | MOLIN | MOLINO 1101 | SONOMA | 15.8907 | 58.1086 | 71.61% | 14 | 10 | 100% | 44.47% | 0 | 0.22351 | 65.3912 | 14.6154 | 0.91975
APPLE HILL 110412832 | APPLE | APPLE HILL 1104 | SIERRA | 15.3272 | 73.0049 | 95.88% | 8 | 6 | 99.79% | 19.25% | 1 | 0.22229 | 65.3912 | 14.536 | 0.94838
DUNBAR 1101343 | DUNBA | DUNBAR 1101 | SONOMA | 4.4643 | 78.5129 | 81.48% | 1 | 3 | 100% | 97.94% | 0 | 0.21869 | 65.3912 | 14.3001 | 3.2032
PINE GROVE 110283098 | PINE | PINE GROVE 1102 | STOCKTON | 8.0988 | 80.2841 | 100% | 2 | 7 | 100% | 98.1% | 0 | 0.21828 | 65.3912 | 14.2738 | 1.7625
MIWUK 170219772 | MIWUK | MIWUK 1702 | YOSEMITE | 3.8508 | 59.5505 | 82.54% | 2 | 3 | 100% | 100% | 0 | 0.16594 | 85.4511 | 14.1801 | 3.6824
KANAKA 110175744 | KANAK | KANAKA 1101 | NORTH VALLEY | 10.5898 | 74.5656 | 100% | 3 | 3 | 100% | 74.87% | 0 | 0.16375 | 85.4511 | 13.9922 | 1.3213
CHALLENGE 11021902 | CHALL | CHALLENGE 1102 | NORTH VALLEY | 5.0391 | 84.0879 | 100% | 3 | 2 | 100% | 100% | 0 | 0.21241 | 65.3912 | 13.8896 | 2.7564
VOLTA 11021648 | VOLTA | VOLTA 1102 | NORTH VALLEY | 4.8649 | 85.7622 | 100% | 2 | 2 | 100% | 79.51% | 0 | 0.16163 | 85.4511 | 13.8114 | 2.839
CAMP EVERS 210611533 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 2.6563 | 88.3756 | 100% | 3 | 0 | 100% | 100% | 0 | 0.2103 | 65.3912 | 13.7518 | 5.177
MONTE RIO 11131989 | MONTE | MONTE RIO 1113 | SONOMA | 0.72387 | 90 | 37.43% | 0 | 0 | 100% | 100% | 0 | 0.13376 | 102.1389 | 13.6625 | 18.8744
DUNBAR 1103534 | DUNBA | DUNBAR 1103 | SONOMA | 15.5924 | 79.0775 | 96.69% | 3 | 12 | 89.43% | 96.98% | 1 | 0.28566 | 47.6367 | 13.6079 | 0.87273
CLARKSVILLE 210419772 | CLARK | CLARKSVILLE 2104 | SIERRA | 18.3365 | 58.7112 | 99.97% | 3 | 3 | 99.31% | 100% | 1 | 0.20806 | 65.3912 | 13.6054 | 0.74199
KONOCTI 11024300 | KONOC | KONOCTI 1102 | HUMBOLDT | 26.3294 | 77.3617 | 62.75% | 9 | 28 | 97.14% | 84.42% | 1 | 0.28482 | 47.6367 | 13.5681 | 0.51532
LOS GATOS 110712041 | LOS G | LOS GATOS 1107 | DE ANZA | 6.3296 | 61.8932 | 100% | 5 | 1 | 100% | 100% | 0 | 0.28444 | 47.6367 | 13.5499 | 2.1407
MIWUK 170111800 | MIWUK | MIWUK 1701 | YOSEMITE | 9.4843 | 50.073 | 65.97% | 8 | 9 | 100% | 100% | 0 | 0.20689 | 65.3912 | 13.5287 | 1.4264
LOS GATOS 110760024 | LOS G | LOS GATOS 1107 | DE ANZA | 3.9994 | 92.5853 | 100% | 0 | 0 | 100% | 100% | 0 | 0.28225 | 47.6367 | 13.4456 | 3.3619
WASHINGTON CITY GEN. 1101CB | WASHI | WASHINGTON CITY GEN. 1101 | SIERRA | 0.012645 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 65.3912 | 13.4438 | 1063.1366
WASHINGTON CITY GEN. 11011101/2 | WASHI | WASHINGTON CITY GEN. 1101 | SIERRA | 0.0035486 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 65.3912 | 13.4438 | 3788.4451
RINCON 1101578 | RINCO | RINCON 1101 | SONOMA | 17.3381 | 67.0315 | 100% | 2 | 9 | 93.38% | 92.03% | 0 | 0.20486 | 65.3912 | 13.3958 | 0.77262
RINCON 1103198 | RINCO | RINCON 1103 | SONOMA | 6.4573 | 72.5696 | 80.26% | 6 | 3 | 100% | 100% | 0 | 0.20459 | 65.3912 | 13.3782 | 2.0718
WILLOW CREEK 11013050 | WILLO | WILLOW CREEK 1101 | HUMBOLDT | 2.7741 | 81.978 | 100% | 0 | 2 | 100% | 100% | 1 | 0.20349 | 65.3912 | 13.3065 | 4.7966
CAMP EVERS 210660120 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 4.3678 | 67.866 | 79.91% | 12 | 0 | 100% | 100% | 0 | 0.20157 | 65.3912 | 13.1807 | 3.0177
ALTO 11243121 | ALTO | ALTO 1124 | NORTH BAY | 2.756 | 78.1169 | 17.87% | 3 | 11 | 100% | 100% | 0 | 0.1536 | 85.4511 | 13.1255 | 4.7625
MONTE RIO 111123916 | MONTE | MONTE RIO 1111 | SONOMA | 5.2149 | 69.8916 | 48.27% | 12 | 5 | 100% | 100% | 0 | 0.20017 | 65.3912 | 13.0895 | 2.51
MORGAN HILL 21114461 | MORGA | MORGAN HILL 2111 | SAN JOSE | 2.2769 | 88.7487 | 84.71% | 4 | 2 | 100% | 100% | 0 | 0.19916 | 65.3912 | 13.0233 | 5.7198
VOLTA 110254932 | VOLTA | VOLTA 1102 | NORTH VALLEY | 4.3783 | 73.0618 | 100% | 0 | 1 | 100% | 95.18% | 0 | 0.19916 | 65.3912 | 13.0232 | 2.9745
PIKE CITY 1102CB | PIKE | PIKE CITY 1102 | SIERRA | 9.4149 | 96.7439 | 75.24% | 4 | 3 | 100% | 100% | 0 | 0.19876 | 65.3912 | 12.9975 | 1.3805
SILVERADO 2103CB | SILVE | SILVERADO 2103 | NORTH BAY | 8.6664 | 84.0044 | 89.49% | 1 | 4 | 46.48% | 100% | 0 | 0.27216 | 47.6367 | 12.965 | 1.496
HIGHLANDS 1103520 | HIGHL | HIGHLANDS 1103 | HUMBOLDT | 46.4816 | 67.4675 | 99% | 5 | 17 | 100% | 0% | 0 | 0.27204 | 47.6367 | 12.9592 | 0.2788
CAMP EVERS 210574170 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 3.5599 | 43.1898 | 71.52% | 10 | 5 | 100% | 100% | 0 | 0.19742 | 65.3912 | 12.9096 | 3.6264
WEST POINT 1102CB | WEST | WEST POINT 1102 | STOCKTON | 17.7809 | 76.7324 | 62.09% | 5 | 4 | 100% | 79.61% | 1 | 0.19732 | 65.3912 | 12.9027 | 0.72565
ALLEGHANY 1101804 | ALLEG | ALLEGHANY 1101 | SIERRA | 21.9183 | 93.3631 | 99.35% | 2 | 14 | 100% | 31.47% | 0 | 0.15061 | 85.4511 | 12.8696 | 0.58716
MONTE RIO 111264682 | MONTE | MONTE RIO 1112 | SONOMA | 1.7634 | 73.4411 | 19.23% | 8 | 4 | 100% | 100% | 0 | 0.12546 | 102.1389 | 12.8145 | 7.2669
SHADY GLEN 11022232 | SHADY | SHADY GLEN 1102 | SIERRA | 10.57 | 94.8997 | 90.23% | 5 | 11 | 100% | 60.37% | 0 | 0.14836 | 85.4511 | 12.6776 | 1.1994
MENDOCINO 110148750 | MENDO | MENDOCINO 1101 | HUMBOLDT | 17.302 | 87.2326 | 98.93% | 5 | 5 | 100% | 70.23% | 0 | 0.19367 | 65.3912 | 12.6646 | 0.73198
CURTIS 17022123 | CURTI | CURTIS 1702 | YOSEMITE | 1.861 | 56.934 | 100% | 1 | 0 | 100% | 100% | 0 | 0.19293 | 65.3912 | 12.6157 | 6.779
WOODACRE 110196844 | WOODA | WOODACRE 1101 | NORTH BAY | 5.9237 | 87.2691 | 22.46% | 5 | 8 | 100% | 88.33% | 0 | 0.12278 | 102.1389 | 12.5411 | 2.1171
MONTE RIO 11131313 | MONTE | MONTE RIO 1113 | SONOMA | 1.2316 | 65.332 | 67.8% | 0 | 1 | 100% | 100% | 0 | 0.14614 | 85.4511 | 12.4876 | 10.139
REDBUD 1101323962 | REDBU | REDBUD 1101 | HUMBOLDT | 18.9728 | 78.4739 | 90.21% | 1 | 14 | 68.24% | 71.99% | 0 | 0.19082 | 65.3912 | 12.4782 | 0.65769
CAMP EVERS 210510294 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 8.3995 | 27.1368 | 59.21% | 34 | 11 | 100% | 100% | 0 | 0.26177 | 47.6367 | 12.4698 | 1.4846
WOODACRE 11011456 | WOODA | WOODACRE 1101 | NORTH BAY | 3.8267 | 75.1652 | 37.76% | 1 | 5 | 100% | 88.56% | 0 | 0.14581 | 85.4511 | 12.4595 | 3.256
PAUL SWEET 2104 | PAUL | PAUL SWEET 2104 | CENTRAL COAST | 0.043661 | 75 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18934 | 65.3912 | 12.3809 | 283.5676
MOLINO 11026917 | MOLIN | MOLINO 1102 | SONOMA | 7.1386 | 86.8229 | 45.11% | 6 | 1 | 100% | 100% | 0 | 0.18864 | 65.3912 | 12.3355 | 1.728
SAN RAFAEL 110863598 | SAN R | SAN RAFAEL 1108 | NORTH BAY | 1.9128 | 87.2214 | 45.64% | 1 | 1 | 100% | 100% | 0 | 0.14368 | 85.4511 | 12.2776 | 6.4187
CAMP EVERS 210510225 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 0.18205 | 47.7189 | 100% | 3 | 0 | 100% | 100% | 0 | 0.1873 | 65.3912 | 12.2475 | 67.2745
SHADY GLEN 1102CB | SHADY | SHADY GLEN 1102 | SIERRA | 20.4139 | 69.5808 | 89.02% | 6 | 13 | 95.14% | 27.66% | 0 | 0.14313 | 85.4511 | 12.231 | 0.59915
OAKHURST 11015490 | OAKHU | OAKHURST 1101 | YOSEMITE | 24.9631 | 65.8497 | 73.62% | 1 | 51 | 100% | 0% | 0 | 0.18555 | 65.3912 | 12.1331 | 0.48604
ALTO 1125510 | ALTO | ALTO 1125 | NORTH BAY | 7.3822 | 55.9602 | 19.39% | 13 | 14 | 100% | 100% | 0 | 0.45487 | 26.5534 | 12.0783 | 1.6361
APPLE HILL 110412842 | APPLE | APPLE HILL 1104 | SIERRA | 15.4186 | 86.4877 | 86.23% | 1 | 6 | 91.92% | 56.31% | 0 | 0.11821 | 102.1389 | 12.0736 | 0.78306
PAUL SWEET 21045394 | PAUL | PAUL SWEET 2104 | CENTRAL COAST | 14.2856 | 38.4642 | 72.86% | 5 | 2 | 93.82% | 100% | 0 | 0.25339 | 47.6367 | 12.0708 | 0.84496
WILLOW CREEK 11015002 | WILLO | WILLOW CREEK 1101 | HUMBOLDT | 12.8071 | 51.1134 | 93.52% | 24 | 21 | 94.53% | 2.43% | 0 | 0.18408 | 65.3912 | 12.0369 | 0.93986
OAKLAND X 1106CR020 | OAKLA | OAKLAND X 1106 | EAST BAY | 2.4457 | 82.3898 | 55.47% | 10 | 1 | 100% | 99.48% | 0 | 0.18349 | 65.3912 | 11.9989 | 4.9061
CAMP EVERS 21061625 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 0.904 | 67.0004 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18108 | 65.3912 | 11.841 | 13.0984
BELLEVUE 2103646 | BELLE | BELLEVUE 2103 | SONOMA | 9.4191 | 67.7942 | 94.53% | 3 | 3 | 77.28% | 93.12% | 0 | 0.17965 | 65.3912 | 11.7473 | 1.2472
BURNS 2101 | BURNS | BURNS 2101 | CENTRAL COAST | 0.0053489 | 65 | 100% | 0 | 0 | 100% | 100% | 0 | 0.17906 | 65.3912 | 11.7089 | 2189.0024
POINT MORETTI 1101 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 0.0096753 | 65 | 100% | 0 | 0 | 100% | 100% | 0 | 0.17906 | 65.3912 | 11.7089 | 1210.1813
SHINGLE SPRINGS 210519522 | SHING | SHINGLE SPRINGS 2105 | SIERRA | 9.9042 | 70.9474 | 99.53% | 2 | 6 | 96.11% | 80.98% | 0 | 0.17524 | 65.3912 | 11.4593 | 1.157
SILVERADO 210258626 | SILVE | SILVERADO 2102 | NORTH BAY | 15.2462 | 83.9933 | 97.52% | 2 | 7 | 100% | 88.88% | 0 | 0.23976 | 47.6367 | 11.4212 | 0.74912
LAS GALLINAS A 110599904 | LAS G | LAS GALLINAS A 1105 | NORTH BAY | 5.5637 | 84.5434 | 55.29% | 2 | 2 | 100% | 100% | 0 | 0.17422 | 65.3912 | 11.3927 | 2.0477
PARADISE 11022098 | PARAD | PARADISE 1102 | NORTH VALLEY | 4.2185 | 79.6766 | 65.19% | 0 | 7 | 42.14% | 100% | 0 | 0.13292 | 85.4511 | 11.3582 | 2.6925
WOODSIDE 11018972 | WOODS | WOODSIDE 1101 | PENINSULA | 6.2078 | 92.0365 | 25.89% | 9 | 0 | 100% | 100% | 1 | 0.17321 | 65.3912 | 11.3261 | 1.8245
BRUNSWICK 110663124 | BRUNS | BRUNSWICK 1106 | SIERRA | 5.9024 | 71.9691 | 59.9% | 2 | 1 | 100% | 94.93% | 0 | 0.17164 | 65.3912 | 11.2236 | 1.9015
MONTE RIO 11111701 | MONTE | MONTE RIO 1111 | SONOMA | 1.3661 | 76.5396 | 84.13% | 0 | 0 | 100% | 100% | 0 | 0.17154 | 65.3912 | 11.217 | 8.2112
MIWUK 17021808 | MIWUK | MIWUK 1702 | YOSEMITE | 1.8341 | 72.798 | 17.3% | 1 | 2 | 100% | 100% | 0 | 0.10942 | 102.1389 | 11.1764 | 6.0936
PARADISE 11011212 | PARAD | PARADISE 1101 | NORTH VALLEY | 8.5723 | 27.6396 | 21.52% | 13 | 13 | 100% | 100% | 0 | 0.17074 | 65.3912 | 11.1651 | 1.3025
MONTE RIO 1112999 | MONTE | MONTE RIO 1112 | SONOMA | 0.78347 | 81.1849 | 29.39% | 4 | 2 | 100% | 100% | 0 | 0.13014 | 85.4511 | 11.1202 | 14.1936
GRASS VALLEY 11012766 | GRASS | GRASS VALLEY 1101 | SIERRA | 3.3601 | 83.6304 | 59.47% | 0 | 1 | 100% | 75.75% | 0 | 0.10872 | 102.1389 | 11.1047 | 3.3048
SAN RAFAEL 11081247 | SAN R | SAN RAFAEL 1108 | NORTH BAY | 0.2757 | 81.1642 | 57.56% | 3 | 0 | 100% | 100% | 0 | 0.16951 | 65.3912 | 11.0844 | 40.2048
BUCKS CREEK 11031131 | BUCKS | BUCKS CREEK 1103 | NORTH VALLEY | 2.7493 | 88.8735 | 99.9% | 0 | 1 | 100% | 56.92% | 0 | 0.12924 | 85.4511 | 11.0435 | 4.0168
ORO FINO 1102127563 | ORO F | ORO FINO 1102 | NORTH VALLEY | 6.9027 | 86.7717 | 100% | 0 | 2 | 100% | 100% | 1 | 0.23179 | 47.6367 | 11.0415 | 1.5996
WEST POINT 110293116 | WEST | WEST POINT 1102 | STOCKTON | 24.1031 | 66.8044 | 100% | 9 | 9 | 100% | 51.27% | 1 | 0.16857 | 65.3912 | 11.0231 | 0.45733
MIRABEL 11014859 | MIRAB | MIRABEL 1101 | SONOMA | 1.8526 | 77.0765 | 99.9% | 8 | 0 | 100% | 100% | 0 | 0.23121 | 47.6367 | 11.014 | 5.9453
ORO FINO 11022040 | ORO F | ORO FINO 1102 | NORTH VALLEY | 9.1589 | 98 | 100% | 4 | 1 | 100% | 12.34% | 0 | 0.10744 | 102.1389 | 10.9734 | 1.1981
BEAR VALLEY 210513430 | BEAR | BEAR VALLEY 2105 | YOSEMITE | 13.3191 | 78.8388 | 99.94% | 4 | 1 | 100% | 48.72% | 0 | 0.12752 | 85.4511 | 10.8965 | 0.81811
MIRABEL 1102332 | MIRAB | MIRABEL 1102 | SONOMA | 5.7552 | 66.9134 | 43.76% | 9 | 11 | 100% | 100% | 1 | 0.16469 | 65.3912 | 10.7691 | 1.8712
OAKLAND K 110217430 | OAKLA | OAKLAND K 1102 | EAST BAY | 2.0764 | 84.0676 | 31.48% | 0 | 1 | 100% | 100% | 0 | 0.12601 | 85.4511 | 10.7674 | 5.1856
MIWUK 17029270 | MIWUK | MIWUK 1702 | YOSEMITE | 5.8553 | 48.3944 | 46.92% | 2 | 9 | 100% | 95.13% | 0 | 0.12583 | 85.4511 | 10.7524 | 1.8363
PARADISE 1106CB | PARAD | PARADISE 1106 | NORTH VALLEY | 4.354 | 81.9365 | 3.23% | 2 | 3 | 96.39% | 100% | 0 | 0.10412 | 102.1389 | 10.6351 | 2.4426
PLACERVILLE 210692012 | PLACE | PLACERVILLE 2106 | SIERRA | 18.5713 | 72.0312 | 64.51% | 6 | 1 | 100% | 92.15% | 0 | 0.22084 | 47.6367 | 10.5203 | 0.56648
MONTE RIO 1111240 | MONTE | MONTE RIO 1111 | SONOMA | 3.0687 | 71.6003 | 66.68% | 5 | 7 | 100% | 100% | 0 | 0.21886 | 47.6367 | 10.4259 | 3.3975
BIG BEND 1101180398 | BIG B | BIG BEND 1101 | NORTH VALLEY | 5.6176 | 75.1769 | 68.58% | 0 | 2 | 100% | 100% | 0 | 0.15837 | 65.3912 | 10.3561 | 1.8435
MIRABEL 1101116 | MIRAB | MIRABEL 1101 | SONOMA | 9.7562 | 60.7427 | 68.47% | 10 | 5 | 91.79% | 57.41% | 1 | 0.21711 | 47.6367 | 10.3426 | 1.0601
MONTE RIO 11131137 | MONTE | MONTE RIO 1113 | SONOMA | 2.8427 | 88.9858 | 48.94% | 0 | 5 | 100% | 100% | 0 | 0.15775 | 65.3912 | 10.3156 | 3.6289
PARADISE 110135976 | PARAD | PARADISE 1101 | NORTH VALLEY | 3.5298 | 50.3669 | 45.43% | 3 | 2 | 100% | 100% | 0 | 0.1201 | 85.4511 | 10.2625 | 2.9074
BRUNSWICK 1106CB | BRUNS | BRUNSWICK 1106 | SIERRA | 8.5018 | 76.2711 | 34.63% | 3 | 2 | 96.43% | 63.8% | 0 | 0.11976 | 85.4511 | 10.2335 | 1.2037
SHINGLE SPRINGS 110419502 | SHING | SHINGLE SPRINGS 1104 | SIERRA | 42.2119 | 45.6817 | 99.02% | 5 | 5 | 73.54% | 87.16% | 0 | 0.15459 | 65.3912 | 10.1086 | 0.23947
TIGER CREEK 0201CB | TIGER | TIGER CREEK 0201 | STOCKTON | 3.8998 | 93.0419 | 100% | 1 | 1 | 100% | 66.65% | 0 | 0.15361 | 65.3912 | 10.0449 | 2.5758
DUNBAR 11021249 | DUNBA | DUNBAR 1102 | SONOMA | 13.5745 | 82.3664 | 58.44% | 5 | 8 | 100% | 36.11% | 1 | 0.11715 | 85.4511 | 10.0108 | 0.73747
VOLTA 11021502 | VOLTA | VOLTA 1102 | NORTH VALLEY | 7.6156 | 84.4703 | 99.46% | 2 | 2 | 100% | 100% | 0 | 0.2099 | 47.6367 | 9.999 | 1.313
MIRABEL 11022043 | MIRAB | MIRABEL 1102 | SONOMA | 0.56871 | 88.7155 | 17.22% | 0 | 1 | 100% | 100% | 0 | 0.11685 | 85.4511 | 9.9846 | 17.5564
CABRILLO 1103Y12 | CABRI | CABRILLO 1103 | LOS PADRES | 26.1562 | 62.7349 | 69.42% | 1 | 11 | 84.42% | 0% | 0 | 0.20939 | 47.6367 | 9.9744 | 0.38134
WILLOW CREEK 1102CB | WILLO | WILLOW CREEK 1102 | HUMBOLDT | 7.3308 | 78.4297 | 99.3% | 9 | 9 | 100% | 47.32% | 0 | 0.15188 | 65.3912 | 9.9319 | 1.3548
CALPINE 1146200-G | CALPI | CALPINE 1146 | SONOMA | 0.0085256 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 47.6367 | 9.7937 | 1148.7325
CALPINE 1146394G | CALPI | CALPINE 1146 | SONOMA | 0.011293 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 47.6367 | 9.7937 | 867.225
SCE REFUGIO 1101CB | SCE R | SCE REFUGIO 1101 | LOS PADRES | 0.29161 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 47.6367 | 9.7937 | 33.5847
MONTE RIO 11113891 | MONTE | MONTE RIO 1111 | SONOMA | 3.5454 | 89.5117 | 50.47% | 2 | 0 | 100% | 100% | 1 | 0.14965 | 65.3912 | 9.7859 | 2.7602
PARADISE 11042472 | PARAD | PARADISE 1104 | NORTH VALLEY | 7.3384 | 31.16 | 42.96% | 7 | 6 | 100% | 100% | 0 | 0.14941 | 65.3912 | 9.7702 | 1.3314
ROSSMOOR 110837848 | ROSSM | ROSSMOOR 1108 | DIABLO | 5.9561 | 79.6593 | 23.72% | 0 | 5 | 100% | 88.12% | 0 | 0.14934 | 65.3912 | 9.7653 | 1.6396
CLAYTON 22122951 | CLAYT | CLAYTON 2212 | DIABLO | 10.1032 | 61.4187 | 78.88% | 4 | 1 | 100% | 100% | 0 | 0.27294 | 35.3263 | 9.6421 | 0.95436
CLARKSVILLE 210413352 | CLARK | CLARKSVILLE 2104 | SIERRA | 32.6724 | 49.7642 | 94.33% | 3 | 19 | 89.71% | 64.9% | 0 | 0.20162 | 47.6367 | 9.6046 | 0.29397
PLACERVILLE 21062224 | PLACE | PLACERVILLE 2106 | SIERRA | 10.4972 | 65.7358 | 76.35% | 3 | 1 | 100% | 100% | 0 | 0.2002 | 47.6367 | 9.5368 | 0.90851
OAKHURST 11035120 | OAKHU | OAKHURST 1103 | YOSEMITE | 6.3491 | 97.3123 | 0.04473% | 0 | 2 | 100% | 100% | 0 | 0.11061 | 85.4511 | 9.4514 | 1.4886
MONTE RIO 1113532 | MONTE | MONTE RIO 1113 | SONOMA | 0.51993 | 90.7851 | 10.39% | 0 | 0 | 100% | 100% | 0 | 0.11048 | 85.4511 | 9.4408 | 18.1578
OTTER 11012052 | OTTER | OTTER 1101 | CENTRAL COAST | 4.8416 | 80.234 | 20.15% | 9 | 2 | 100% | 100% | 0 | 0.14395 | 65.3912 | 9.4134 | 1.9443
MORAGA 1105CB | MORAG | MORAGA 1105 | DIABLO | 7.1365 | 67.7298 | 20.75% | 5 | 12 | 65.86% | 77.06% | 1 | 0.092052 | 102.1389 | 9.4021 | 1.3175
ROB ROY 21055166 | ROB R | ROB ROY 2105 | CENTRAL COAST | 5.4938 | 45.154 | 99.95% | 6 | 2 | 100% | 100% | 0 | 0.19719 | 47.6367 | 9.3933 | 1.7098
MIDDLETOWN 110148212 | MIDDL | MIDDLETOWN 1101 | HUMBOLDT | 10.2049 | 74.7586 | 62.81% | 5 | 4 | 94.29% | 99.65% | 0 | 0.19647 | 47.6367 | 9.3592 | 0.91713
MONTE RIO 1112212 | MONTE | MONTE RIO 1112 | SONOMA | 2.2491 | 44.7156 | 75.38% | 4 | 1 | 100% | 100% | 0 | 0.14298 | 65.3912 | 9.3496 | 4.157
BRUNSWICK 11052102 | BRUNS | BRUNSWICK 1105 | SIERRA | 3.6478 | 67.9602 | 63.58% | 1 | 3 | 100% | 48.36% | 1 | 0.091021 | 102.1389 | 9.2968 | 2.5486
SILVERADO 2104563322 | SILVE | SILVERADO 2104 | NORTH BAY | 3.653 | 77.3083 | 48.88% | 3 | 1 | 100% | 100% | 1 | 0.14188 | 65.3912 | 9.2779 | 2.5398
WOODSIDE 11018601 | WOODS | WOODSIDE 1101 | PENINSULA | 0.59795 | 81.8692 | 48.65% | 2 | 0 | 100% | 100% | 0 | 0.14129 | 65.3912 | 9.2392 | 15.4516
MONTE RIO 1111 | MONTE | MONTE RIO 1111 | SONOMA | 0.032125 | 95 | 0% | 0 | 1 | 100% | 100% | 0 | 0.107 | 85.4511 | 9.1434 | 284.6221
BEN LOMOND 04015144 | BEN L | BEN LOMOND 0401 | CENTRAL COAST | 3.9861 | 45.8832 | 59.52% | 1 | 1 | 100% | 100% | 0 | 0.13946 | 65.3912 | 9.1195 | 2.2878
BIG BASIN 1101CB | BIG B | BIG BASIN 1101 | CENTRAL COAST | 4.7811 | 77.9416 | 33.87% | 2 | 0 | 100% | 100% | 0 | 0.13944 | 65.3912 | 9.1184 | 1.9072
WILLOW CREEK 110237374 | WILLO | WILLOW CREEK 1102 | HUMBOLDT | 2.2967 | 96.0041 | 99.34% | 1 | 0 | 100% | 68.24% | 0 | 0.13938 | 65.3912 | 9.1142 | 3.9684
WOODACRE 1102851 | WOODA | WOODACRE 1102 | NORTH BAY | 1.2766 | 60.3664 | 19.35% | 1 | 3 | 100% | 100% | 0 | 0.10492 | 85.4511 | 8.9652 | 7.0227
ATASCADERO 1103A06 | ATASC | ATASCADERO 1103 | LOS PADRES | 34.0507 | 59.0569 | 96.54% | 3 | 5 | 91.06% | 64.46% | 1 | 0.13601 | 65.3912 | 8.8937 | 0.26119
VINEYARD 2108MR172 | VINEY | VINEYARD 2108 | MISSION | 3.1156 | 86.4654 | 47.06% | 1 | 2 | 35.54% | 100% | 1 | 0.13362 | 65.3912 | 8.7379 | 2.8046
STANISLAUS 1702L3151 | STANI | STANISLAUS 1702 | YOSEMITE | 0.9933 | 86.9694 | 85.25% | 0 | 0 | 100% | 100% | 0 | 0.1833 | 47.6367 | 8.7317 | 8.7906
KONOCTI 11024421 | KONOC | KONOCTI 1102 | HUMBOLDT | 0.36385 | 69.0599 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18318 | 47.6367 | 8.726 | 23.9823
MOLINO 1102178 | MOLIN | MOLINO 1102 | SONOMA | 13.3443 | 48.7979 | 52.24% | 13 | 10 | 88.89% | 58.63% | 0 | 0.18298 | 47.6367 | 8.7167 | 0.65322
COARSEGOLD 21045310 | COARS | COARSEGOLD 2104 | YOSEMITE | 17.6177 | 41.6297 | 82.56% | 2 | 60 | 100% | 0% | 0 | 0.18205 | 47.6367 | 8.6723 | 0.49225
BRUNSWICK 11051030 | BRUNS | BRUNSWICK 1105 | SIERRA | 4.9418 | 79.0296 | 79.8% | 3 | 3 | 100% | 45.4% | 0 | 0.084675 | 102.1389 | 8.6486 | 1.7501
SHINGLE SPRINGS 21092679 | SHING | SHINGLE SPRINGS 2109 | SIERRA | 7.0526 | 59.0742 | 100% | 0 | 2 | 100% | 100% | 1 | 0.17927 | 47.6367 | 8.5398 | 1.2109
PARADISE 11015185 | PARAD | PARADISE 1101 | NORTH VALLEY | 0.8075 | 38.303 | 73.08% | 0 | 1 | 100% | 100% | 0 | 0.12937 | 65.3912 | 8.4598 | 10.4765
POINT MORETTI 110136516 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 4.1652 | 32.5436 | 68.9% | 12 | 2 | 100% | 100% | 0 | 0.17749 | 47.6367 | 8.4551 | 2.0299
GARBERVILLE 11022500 | GARBE | GARBERVILLE 1102 | HUMBOLDT | 16.0185 | 91.6655 | 50.61% | 18 | 6 | 100% | 0% | 0 | 0.098692 | 85.4511 | 8.4333 | 0.52647
SARATOGA 1107167792 | SARAT | SARATOGA 1107 | DE ANZA | 4.6876 | 89.4882 | 89.82% | 13 | 1 | 100% | 18.23% | 0 | 0.1289 | 65.3912 | 8.429 | 1.7981
MIWUK 170236888 | MIWUK | MIWUK 1702 | YOSEMITE | 0.61573 | 72.472 | 39.92% | 0 | 2 | 100% | 100% | 0 | 0.12726 | 65.3912 | 8.3216 | 13.5152
FULTON 110777670 | FULTO | FULTON 1107 | SONOMA | 6.8809 | 26.8333 | 74.89% | 3 | 6 | 100% | 100% | 0 | 0.17389 | 47.6367 | 8.2837 | 1.2039
KANAKA 11011044 | KANAK | KANAKA 1101 | NORTH VALLEY | 6.134 | 63.1535 | 33.69% | 2 | 5 | 100% | 70.49% | 0 | 0.080757 | 102.1389 | 8.2484 | 1.3447
CORRAL 1101CB | CORRA | CORRAL 1101 | STOCKTON | 26.1508 | 58.878 | 76.15% | 2 | 13 | 95.28% | 0% | 0 | 0.12599 | 65.3912 | 8.2388 | 0.31505
MONTE RIO 11125040 | MONTE | MONTE RIO 1112 | SONOMA | 3.9901 | 73.555 | 15.29% | 9 | 5 | 100% | 100% | 1 | 0.12574 | 65.3912 | 8.222 | 2.0606
PARADISE 11022206 | PARAD | PARADISE 1102 | NORTH VALLEY | 5.1983 | 53.3962 | 55.37% | 4 | 4 | 89% | 100% | 0 | 0.12523 | 65.3912 | 8.1891 | 1.5753
VOLTA 110237350 | VOLTA | VOLTA 1102 | NORTH VALLEY | 24.2981 | 64.1392 | 95.8% | 2 | 5 | 100% | 58.24% | 1 | 0.17108 | 47.6367 | 8.1495 | 0.3354
EL DORADO PH 210136764 | EL DO | EL DORADO PH 2101 | SIERRA | 3.1646 | 79.8685 | 100% | 3 | 0 | 72.39% | 0% | 0 | 0.12435 | 65.3912 | 8.1314 | 2.5695
SHINGLE SPRINGS 21092053 | SHING | SHINGLE SPRINGS 2109 | SIERRA | 5.7202 | 32.6339 | 100% | 0 | 1 | 100% | 100% | 0 | 0.16944 | 47.6367 | 8.0716 | 1.4111
MONTE RIO 1111256 | MONTE | MONTE RIO 1111 | SONOMA | 7.2865 | 62.779 | 22.47% | 12 | 6 | 100% | 100% | 1 | 0.22703 | 35.3263 | 8.0203 | 1.1007
CLARKSVILLE 210419632 | CLARK | CLARKSVILLE 2104 | SIERRA | 5.4715 | 65.8905 | 97.91% | 0 | 0 | 60.07% | 97.91% | 1 | 0.12258 | 65.3912 | 8.0156 | 1.465
ALTO 11221212 | ALTO | ALTO 1122 | NORTH BAY | 1.5919 | 41.9573 | 53.59% | 1 | 4 | 67.44% | 92.64% | 0 | 0.09288 | 85.4511 | 7.9367 | 4.9857
CORRAL 110112608 | CORRA | CORRAL 1101 | STOCKTON | 35.0176 | 52.1044 | 87.04% | 0 | 19 | 100% | 0% | 0 | 0.16618 | 47.6367 | 7.9163 | 0.22607
ANNAPOLIS 1101554 | ANNAP | ANNAPOLIS 1101 | HUMBOLDT | 27.1366 | 85.1288 | 100% | 26 | 12 | 100% | 0% | 0 | 0.1656 | 47.6367 | 7.8886 | 0.2907
FORT ROSS 11212987 | FORT | FORT ROSS 1121 | SONOMA | 2.0798 | 87.0149 | 100% | 0 | 1 | 100% | 83.64% | 0 | 0.16552 | 47.6367 | 7.8847 | 3.7911
OLEMA 110150396 | OLEMA | OLEMA 1101 | NORTH BAY | 12.5505 | 59.0331 | 35.48% | 29 | 15 | 95.94% | 0% | 0 | 0.11931 | 65.3912 | 7.8017 | 0.62162
OAKLAND K 1102CB | OAKLA | OAKLAND K 1102 | EAST BAY | 3.0081 | 48.3984 | 19.08% | 4 | 5 | 100% | 100% | 0 | 0.11788 | 65.3912 | 7.7083 | 2.5625
BRUNSWICK 1105CB | BRUNS | BRUNSWICK 1105 | SIERRA | 2.0209 | 50.1126 | 64.77% | 1 | 2 | 85.09% | 53.11% | 0 | 0.075406 | 102.1389 | 7.7019 | 3.8112
BRUNSWICK 11052100 | BRUNS | BRUNSWICK 1105 | SIERRA | 3.9656 | 82.5395 | 61.98% | 2 | 1 | 100% | 39.89% | 0 | 0.074817 | 102.1389 | 7.6417 | 1.927
BRUNSWICK 11032784 | BRUNS | BRUNSWICK 1103 | SIERRA | 14.361 | 51.6275 | 64.59% | 9 | 6 | 93.84% | 32.3% | 0 | 0.11661 | 65.3912 | 7.6256 | 0.53099
PARADISE 110136042 | PARAD | PARADISE 1101 | NORTH VALLEY | 2.7098 | 42.4595 | 41.3% | 5 | 3 | 86.87% | 100% | 0 | 0.11607 | 65.3912 | 7.5898 | 2.8008
WOODSIDE 11018912 | WOODS | WOODSIDE 1101 | PENINSULA | 3.8497 | 42.1497 | 27.37% | 5 | 2 | 96.59% | 100% | 0 | 0.15841 | 47.6367 | 7.5459 | 1.9601
PUEBLO 2103 | PUEBL | PUEBLO 2103 | NORTH BAY | 0.012243 | 90 | 0% | 0 | 0 | 100% | 100% | 0 | 0.11472 | 65.3912 | 7.502 | 612.7449
BURNS 2101CB | BURNS | BURNS 2101 | CENTRAL COAST | 1.6587 | 56.6807 | 25.38% | 1 | 0 | 100% | 100% | 0 | 0.11419 | 65.3912 | 7.4673 | 4.502
LOS GATOS 1106LA46 | LOS G | LOS GATOS 1106 | DE ANZA | 1.5345 | 25.7114 | 95.32% | 1 | 0 | 100% | 100% | 0 | 0.15665 | 47.6367 | 7.4623 | 4.8629
WILLITS 1103826 | WILLI | WILLITS 1103 | HUMBOLDT | 7.7428 | 68.4696 | 97.36% | 4 | 8 | 100% | 35.78% | 0 | 0.11113 | 65.3912 | 7.267 | 0.93855
FORT ROSS 1121204 | FORT | FORT ROSS 1121 | SONOMA | 18.7577 | 93.0498 | 90.41% | 0 | 2 | 100% | 39.05% | 1 | 0.10967 | 65.3912 | 7.1716 | 0.38233
VOLTA 11021646 | VOLTA | VOLTA 1102 | NORTH VALLEY | 22.2648 | 70.368 | 99.98% | 0 | 4 | 92.24% | 75.72% | 0 | 0.14906 | 47.6367 | 7.1006 | 0.31892
BIG BASIN 11015000 | BIG B | BIG BASIN 1101 | CENTRAL COAST | 1.9973 | 72.3321 | 15.8% | 2 | 1 | 100% | 100% | 0 | 0.10717 | 65.3912 | 7.0083 | 3.5089
MONTE RIO 1112CB | MONTE | MONTE RIO 1112 | SONOMA | 3.7135 | 57.2951 | 17.86% | 14 | 2 | 100% | 100% | 0 | 0.14693 | 47.6367 | 6.9992 | 1.8848
WOODSIDE 11011922 | WOODS | WOODSIDE 1101 | PENINSULA | 3.7722 | 56.2856 | 79.83% | 3 | 6 | 79.05% | 92.98% | 1 | 0.14505 | 47.6367 | 6.9098 | 1.8317
SILVERADO 2102 | SILVE | SILVERADO 2102 | NORTH BAY | 0.0045192 | 80 | 100% | 0 | 0 | 100% | 100% | 0 | 0.19464 | 35.3263 | 6.876 | 1521.4908
BIG BASIN 110110296 | BIG B | BIG BASIN 1101 | CENTRAL COAST | 14.4399 | 15.6542 | 52.28% | 39 | 5 | 100% | 100% | 0 | 0.45917 | 14.9507 | 6.8649 | 0.47541
MORAGA 1101108540 | MORAG | MORAGA 1101 | DIABLO | 4.7825 | 66.0707 | 6.533% | 0 | 5 | 99.19% | 93.66% | 1 | 0.10343 | 65.3912 | 6.7632 | 1.4142
OAKLAND X 1106CR266 | OAKLA | OAKLAND X 1106 | EAST BAY | 1.1822 | 88.5589 | 1.895% | 0 | 0 | 100% | 100% | 0 | 0.10237 | 65.3912 | 6.6941 | 5.6623
CASTRO VALLEY 110810315 | CASTR | CASTRO VALLEY 1108 | MISSION | 5.494 | 83.0408 | 14.23% | 2 | 0 | 100% | 100% | 0 | 0.14022 | 47.6367 | 6.6796 | 1.2158
CAMP EVERS 21059031 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 1.0934 | 18.456 | 18.86% | 2 | 2 | 100% | 100% | 0 | 0.10201 | 65.3912 | 6.6703 | 6.1003
BRIDGEVILLE 1101CB | BRIDG | BRIDGEVILLE 1101 | HUMBOLDT | 8.4707 | 94.1626 | 99.27% | 7 | 0 | 100% | 9.505% | 1 | 0.10184 | 65.3912 | 6.6593 | 0.78616
GARBERVILLE 110135706 | GARBE | GARBERVILLE 1101 | HUMBOLDT | 9.7846 | 69.4909 | 86.47% | 18 | 6 | 100% | 0% | 0 | 0.099644 | 65.3912 | 6.5159 | 0.66593
SILVERADO 2104 | SILVE | SILVERADO 2104 | NORTH BAY | 0.061489 | 85 | 0% | 0 | 0 | 100% | 100% | 0 | 0.098754 | 65.3912 | 6.4577 | 105.0217
TEMPLETON 21136055 | TEMPL | TEMPLETON 2113 | LOS PADRES | 39.7266 | 74.9616 | 83.37% | 3 | 5 | 100% | 12.3% | 1 | 0.24234 | 26.5534 | 6.435 | 0.16198
SANTA ROSA A 1104642 | SANTA | SANTA ROSA A 1104 | SONOMA | 13.3386 | 23.4287 | 85.18% | 3 | 22 | 100% | 84.73% | 0 | 0.24187 | 26.5534 | 6.4225 | 0.4815
CASTRO VALLEY 1108MR748 | CASTR | CASTRO VALLEY 1108 | MISSION | 6.2273 | 76.3747 | 18.01% | 3 | 1 | 100% | 95.99% | 0 | 0.13481 | 47.6367 | 6.422 | 1.0313
MIRABEL 11021139 | MIRAB | MIRABEL 1102 | SONOMA | 2.0153 | 64.752 | 50.11% | 2 | 2 | 100% | 100% | 0 | 0.1338 | 47.6367 | 6.374 | 3.1628
OAKLAND X 1104CR214 | OAKLA | OAKLAND X 1104 | EAST BAY | 2.8836 | 10 | 25.8% | 4 | 2 | 100% | 100% | 0 | 0.13215 | 47.6367 | 6.2952 | 2.1831
MIDDLETOWN 11011325 | MIDDL | MIDDLETOWN 1101 | HUMBOLDT | 8.5949 | 66.5337 | 99.94% | 1 | 2 | 100% | 100% | 0 | 0.23318 | 26.5534 | 6.1918 | 0.72041
SAN RAMON 2108CB | SAN R | SAN RAMON 2108 | MISSION | 8.6488 | 65.614 | 48.13% | 2 | 4 | 90.54% | 100% | 0 | 0.12664 | 47.6367 | 6.0329 | 0.69753
PARADISE 1101CB | PARAD | PARADISE 1101 | NORTH VALLEY | 2.6336 | 51.0801 | 25.12% | 2 | 4 | 70.38% | 100% | 0 | 0.092062 | 65.3912 | 6.02 | 2.2858
BEN LOMOND 1101BL 1101 | BEN L | BEN LOMOND 1101 | CENTRAL COAST | 8.6011 | 33.9399 | 41.85% | 31 | 2 | 100% | 100% | 0 | 0.22644 | 26.5534 | 6.0127 | 0.69906
OAKHURST 11035470 | OAKHU | OAKHURST 1103 | YOSEMITE | 9.6183 | 65.532 | 32.55% | 7 | 21 | 100% | 20.07% | 0 | 0.090249 | 65.3912 | 5.9015 | 0.61357
POINT MORETTI 11015401 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 2.5449 | 35.7837 | 49.53% | 3 | 0 | 100% | 100% | 0 | 0.12284 | 47.6367 | 5.8517 | 2.2994
TEMPLETON 2113A10 | TEMPL | TEMPLETON 2113 | LOS PADRES | 30.9401 | 69.101 | 70.57% | 5 | 5 | 100% | 93.66% | 0 | 0.21943 | 26.5534 | 5.8266 | 0.18832
SILVERADO 21038401 | SILVE | SILVERADO 2103 | NORTH BAY | 0.63211 | 87.9301 | 93.73% | 0 | 0 | 9.105% | 100% | 0 | 0.088787 | 65.3912 | 5.8059 | 9.185
BRUNSWICK 110750010 | BRUNS | BRUNSWICK 1107 | SIERRA | 4.0845 | 61.0721 | 60.14% | 3 | 2 | 43.91% | 47.61% | 1 | 0.056677 | 102.1389 | 5.789 | 1.4173
MIDDLETOWN 1101CB | MIDDL | MIDDLETOWN 1101 | HUMBOLDT | 8.5904 | 74.5605 | 79.65% | 0 | 4 | 45.66% | 67.1% | 0 | 0.067737 | 85.4511 | 5.7882 | 0.6738
BEN LOMOND 110196738 | BEN L | BEN LOMOND 1101 | CENTRAL COAST | 6.8007 | 19.3556 | 74.88% | 14 | 2 | 100% | 100% | 0 | 0.21743 | 26.5534 | 5.7735 | 0.84895
CAMP EVERS 210510786 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 4.5287 | 29.7458 | 98.51% | 7 | 0 | 100% | 100% | 1 | 0.21707 | 26.5534 | 5.764 | 1.2728
SHINGLE SPRINGS 210551738 | SHING | SHINGLE SPRINGS 2105 | SIERRA | 0.38011 | 59.0013 | 92.98% | 0 | 0 | 33.17% | 96.59% | 0 | 0.087308 | 65.3912 | 5.7091 | 15.0198
CAMP EVERS 210533542 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 2.4779 | 18.5991 | 43.01% | 16 | 2 | 100% | 100% | 0 | 0.1603 | 35.3263 | 5.6629 | 2.2854
CALISTOGA 1102706 | CALIS | CALISTOGA 1102 | NORTH BAY | 0.14479 | 80 | 100% | 0 | 1 | 2.91% | 100% | 0 | 0.085322 | 65.3912 | 5.5793 | 38.5332
PUEBLO 2102618 | PUEBL | PUEBLO 2102 | NORTH BAY | 2.0485 | 88.1559 | 93.93% | 0 | 0 | 12.3% | 100% | 0 | 0.11649 | 47.6367 | 5.5491 | 2.7088
SAN RAMON 210853732 | SAN R | SAN RAMON 2108 | MISSION | 7.923 | 73.3065 | 51.9% | 0 | 2 | 100% | 100% | 0 | 0.15613 | 35.3263 | 5.5156 | 0.69616
CASTRO VALLEY 11068971 | CASTR | CASTRO VALLEY 1106 | MISSION | 7.918 | 68.6499 | 16.36% | 0 | 1 | 100% | 100% | 0 | 0.11574 | 47.6367 | 5.5135 | 0.69632
VOLTA 1102CB | VOLTA | VOLTA 1102 | NORTH VALLEY | 3.2998 | 84.686 | 16.79% | 3 | 0 | 100% | 100% | 0 | 0.11557 | 47.6367 | 5.5056 | 1.6684
GARBERVILLE 11028652 | GARBE | GARBERVILLE 1102 | HUMBOLDT | 13.0139 | 91.1649 | 97.21% | 18 | 2 | 100% | 0% | 0 | 0.11424 | 47.6367 | 5.4418 | 0.41815
KONOCTI 110275382 | KONOC | KONOCTI 1102 | HUMBOLDT | 21.8665 | 65.7136 | 85.11% | 11 | 7 | 94.25% | 84.3% | 0 | 0.27016 | 19.9979 | 5.4025 | 0.24707
POINT MORETTI 11015078 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 14.6844 | 28.4071 | 32.64% | 18 | 2 | 100% | 99.93% | 1 | 0.2007 | 26.5534 | 5.3293 | 0.36292
DUNBAR 1101302 | DUNBA | DUNBAR 1101 | SONOMA | 7.7166 | 55.3691 | 64.87% | 1 | 11 | 75.08% | 68.56% | 0 | 0.15076 | 35.3263 | 5.3259 | 0.69018
FRUITLAND 114293234 | FRUIT | FRUITLAND 1142 | HUMBOLDT | 11.3813 | 94.4975 | 76.78% | 16 | 5 | 100% | 0% | 0 | 0.081313 | 65.3912 | 5.3172 | 0.46719
FORT ROSS 11214947 | FORT | FORT ROSS 1121 | SONOMA | 10.2762 | 93.0727 | 99.97% | 4 | 1 | 100% | 8.448% | 0 | 0.11096 | 47.6367 | 5.2856 | 0.51436
PHILO 11022600 | PHILO | PHILO 1102 | HUMBOLDT | 19.2386 | 94.0358 | 55.52% | 12 | 3 | 96.16% | 0% | 0 | 0.060847 | 85.4511 | 5.1995 | 0.27026
PETALUMA C 1108208 | PETAL | PETALUMA C 1108 | SONOMA | 12.4029 | 84.7631 | 33.65% | 1 | 1 | 100% | 0% | 0 | 0.07858 | 65.3912 | 5.1384 | 0.41429
MIDDLETOWN 1101622 | MIDDL | MIDDLETOWN 1101 | HUMBOLDT | 15.6831 | 77.1942 | 76.84% | 4 | 8 | 78.63% | 70.55% | 1 | 0.1922 | 26.5534 | 5.1034 | 0.32541
BIG BASIN 11029741 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 0.65144 | 10 | 32.18% | 5 | 0 | 100% | 100% | 0 | 0.10666 | 47.6367 | 5.0809 | 7.7995
SANTA ROSA A 1104716 | SANTA | SANTA ROSA A 1104 | SONOMA | 8.9162 | 55.6538 | 91.58% | 1 | 3 | 100% | 100% | 0 | 0.19056 | 26.5534 | 5.06 | 0.56751
PARADISE 1105CB | PARAD | PARADISE 1105 | NORTH VALLEY | 3.6905 | 42.5038 | 17.46% | 4 | 4 | 44.69% | 100% | 0 | 0.058684 | 85.4511 | 5.0146 | 1.3588
RACETRACK 1704CB | RACET | RACETRACK 1704 | YOSEMITE | 22.0312 | 55.84 | 32.56% | 4 | 25 | 99.99% | 0% | 0 | 0.18885 | 26.5534 | 5.0145 | 0.22761
APPLE HILL 110412947 | APPLE | APPLE HILL 1104 | SIERRA | 3.4561 | 89.425 | 100% | 0 | 1 | 100% | 0% | 0 | 0.04907 | 102.1389 | 5.012 | 1.4502
RINCON 11035152 | RINCO | RINCON 1103 | SONOMA | 1.5925 | 84.6014 | 46.06% | 2 | 0 | 100% | 100% | 0 | 0.14097 | 35.3263 | 4.9799 | 3.1271
HOOPA 11017468 | HOOPA | HOOPA 1101 | HUMBOLDT | 5.6936 | 54.3189 | 96.19% | 3 | 8 | 47.51% | 49.77% | 1 | 0.076067 | 65.3912 | 4.9741 | 0.87363
MONTE RIO 1111140 | MONTE | MONTE RIO 1111 | SONOMA | 2.6327 | 49.961 | 28.63% | 14 | 1 | 100% | 100% | 0 | 0.18634 | 26.5534 | 4.9479 | 1.8794
PINE GROVE 11021765 | PINE | PINE GROVE 1102 | STOCKTON | 1.4479 | 48.9693 | 100% | 0 | 0 | 100% | 66.6% | 0 | 0.10186 | 47.6367 | 4.8523 | 3.3514
PINE GROVE 1102CB | PINE | PINE GROVE 1102 | STOCKTON | 10.707 | 66.221 | 86.49% | 3 | 11 | 100% | 3.567% | 1 | 0.074056 | 65.3912 | 4.8426 | 0.45229
MORAGA 110118216 | MORAG | MORAGA 1101 | DIABLO | 5.0361 | 38.4811 | 22.22% | 5 | 16 | 100% | 100% | 0 | 0.24183 | 19.9979 | 4.8362 | 0.96031
POINT MORETTI 110110726 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 10.5855 | 11.8484 | 44.34% | 15 | 5 | 100% | 100% | 1 | 0.18125 | 26.5534 | 4.8128 | 0.45466
LOW GAP 1101CB | LOW G | LOW GAP 1101 | HUMBOLDT | 2.17 | 82.2052 | 100% | 6 | 1 | 100% | 0% | 0 | 0.073547 | 65.3912 | 4.8093 | 2.2163
TASSAJARA 21126392 | TASSA | TASSAJARA 2112 | DIABLO | 5.4625 | 75.7434 | 2.892% | 0 | 3 | 100% | 100% | 0 | 0.10087 | 47.6367 | 4.8049 | 0.87961
SALMON CREEK 110188998 | SALMO | SALMON CREEK 1101 | SONOMA | 8.1183 | 72.1541 | 32.11% | 1 | 1 | 59.97% | 96.61% | 1 | 0.10072 | 47.6367 | 4.7981 | 0.59103
PARADISE 110476064 | PARAD | PARADISE 1104 | NORTH VALLEY | 6.3823 | 13.6814 | 48.59% | 6 | 11 | 100% | 100% | 1 | 0.13538 | 35.3263 | 4.7824 | 0.74932
WEST POINT 110272036 | WEST | WEST POINT 1102 | STOCKTON | 2.3575 | 87.7642 | 47.51% | 4 | 2 | 100% | 22.74% | 0 | 0.055692 | 85.4511 | 4.759 | 2.0187
SHINGLE SPRINGS 210851476 | SHING | SHINGLE SPRINGS 2108 | SIERRA | 2.9778 | 55.1791 | 91.84% | 0 | 4 | 47.94% | 85.32% | 1 | 0.09969 | 47.6367 | 4.7489 | 1.5948
POINT MORETTI 110139126 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 2.2477 | 14.3797 | 26.31% | 9 | 1 | 100% | 100% | 0 | 0.099437 | 47.6367 | 4.7369 | 2.1074
ELECTRA 11017104 | ELECT | ELECTRA 1101 | STOCKTON | 12.3464 | 47.2231 | 81.14% | 1 | 3 | 100% | 0% | 0 | 0.072301 | 65.3912 | 4.7279 | 0.38293
BERKELEY F 1103BR110 | BERKE | BERKELEY F 1103 | EAST BAY | 1.8512 | 58.149 | 51.38% | 3 | 2 | 32.55% | 100% | 0 | 0.071417 | 65.3912 | 4.67 | 2.5227
MONTE RIO 1111506 | MONTE | MONTE RIO 1111 | SONOMA | 1.1523 | 40.8732 | 25.9% | 6 | 0 | 100% | 100% | 0 | 0.097983 | 47.6367 | 4.6676 | 4.0506
LOW GAP 110186816 | LOW G | LOW GAP 1101 | HUMBOLDT | 4.4169 | 87.0623 | 100% | 0 | 8 | 100% | 0% | 0 | 0.071339 | 65.3912 | 4.6649 | 1.0562
BRIDGEVILLE 110169866 | BRIDG | BRIDGEVILLE 1101 | HUMBOLDT | 6.5416 | 93.8748 | 99.88% | 6 | 2 | 100% | 0% | 0 | 0.071282 | 65.3912 | 4.6612 | 0.71255
BRUNSWICK 110456468 | BRUNS | BRUNSWICK 1104 | SIERRA | 5.7301 | 68.1683 | 52.05% | 5 | 6 | 95.81% | 0% | 0 | 0.070779 | 65.3912 | 4.6283 | 0.80772
LAYTONVILLE 1101CB | LAYTO | LAYTONVILLE 1101 | HUMBOLDT | 7.0679 | 79.2729 | 100% | 10 | 7 | 78.03% | 0% | 0 | 0.054066 | 85.4511 | 4.62 | 0.65367
TASSAJARA 210865438 | TASSA | TASSAJARA 2108 | DIABLO | 0.52908 | 90 | 0% | 0 | 2 | 14.01% | 100% | 0 | 0.054006 | 85.4511 | 4.6148 | 8.7223
MESA 11016111 | MESA | MESA 1101 | LOS PADRES | 23.8724 | 66.2721 | 84.61% | 0 | 7 | 92.83% | 48.37% | 0 | 0.23056 | 19.9979 | 4.6108 | 0.19314
ORO FINO 110238698 | ORO F | ORO FINO 1102 | NORTH VALLEY | 15.5224 | 87.0508 | 99.92% | 2 | 6 | 100% | 0% | 0 | 0.070272 | 65.3912 | 4.5952 | 0.29604
REDBUD 1101708166 | REDBU | REDBUD 1101 | HUMBOLDT | 10.1809 | 81.1955 | 96.21% | 0 | 3 | 49.7% | 53.54% | 1 | 0.096142 | 47.6367 | 4.5799 | 0.44985
EAST QUINCY 11012452 | EAST | EAST QUINCY 1101 | NORTH VALLEY | 1.102 | 63.1536 | 79.93% | 0 | 1 | 13.25% | 52.23% | 1 | 0.04476 | 102.1389 | 4.5718 | 4.1484
CAMP EVERS 210510912 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 4.9849 | 57.147 | 56.28% | 17 | 4 | 100% | 100% | 0 | 0.22661 | 19.9979 | 4.5316 | 0.90907
OAKLAND K 110491060 | OAKLA | OAKLAND K 1104 | EAST BAY | 0.36025 | 77.0512 | 0% | 0 | 0 | 100% | 100% | 0 | 0.094019 | 47.6367 | 4.4788 | 12.4324
SILVERADO 210365334 | SILVE | SILVERADO 2103 | NORTH BAY | 0.51221 | 90 | 100% | 0 | 0 | 7.915% | 100% | 0 | 0.093253 | 47.6367 | 4.4422 | 8.6727
BRIDGEVILLE 110137484 | BRIDG | BRIDGEVILLE 1101 | HUMBOLDT | 7.5279 | 94.876 | 100% | 3 | 6 | 74.55% | 0% | 0 | 0.051968 | 85.4511 | 4.4407 | 0.5899
CALPINE 1144962 | CALPI | CALPINE 1144 | SONOMA | 4.058 | 94.9648 | 64.72% | 0 | 0 | 100% | 100% | 0 | 0.16674 | 26.5534 | 4.4275 | 1.0911
WISE 11022230 | WISE | WISE 1102 | SIERRA | 22.0893 | 25.2486 | 59.65% | 3 | 10 | 89.01% | 0% | 0 | 0.09262 | 47.6367 | 4.4121 | 0.19974
LAYTONVILLE 1102CB | LAYTO | LAYTONVILLE 1102 | HUMBOLDT | 10.2076 | 95.4582 | 95.78% | 0 | 7 | 78.57% | 0% | 0 | 0.051516 | 85.4511 | 4.4021 | 0.43126
BEN LOMOND 04015206 | BEN L | BEN LOMOND 0401 | CENTRAL COAST | 7.179 | 20.3543 | 52.81% | 22 | 2 | 100% | 100% | 0 | 0.16558 | 26.5534 | 4.3967 | 0.61243
CAMP EVERS 210616000 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 2.1434 | 16.7013 | 23.49% | 1 | 3 | 54.85% | 97.54% | 1 | 0.067002 | 65.3912 | 4.3813 | 2.0441
MONTE RIO 1113250 | MONTE | MONTE RIO 1113 | SONOMA | 1.2254 | 74.4629 | 18.87% | 1 | 1 | 100% | 100% | 0 | 0.1235 | 35.3263 | 4.3628 | 3.5604
CLAYTON 22127758 | CLAYT | CLAYTON 2212 | DIABLO | 3.2393 | 62.3034 | 85.96% | 2 | 0 | 100% | 100% | 0 | 0.16375 | 26.5534 | 4.3482 | 1.3424
WEST POINT 11025357 | WEST | WEST POINT 1102 | STOCKTON | 3.286 | 83.7938 | 100% | 3 | 2 | 100% | 17.3% | 0 | 0.065365 | 65.3912 | 4.2743 | 1.3008
PENNGROVE 1101170 | PENNG | PENNGROVE 1101 | SONOMA | 18.4109 | 61.4183 | 85.26% | 5 | 17 | 81.28% | 0% | 0 | 0.065227 | 65.3912 | 4.2653 | 0.23167
SIERRA CITY GEN 1101CB | SIERR | SIERRA CITY GEN 1101 | SIERRA | 0.013222 | 95 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049877 | 85.4511 | 4.262 | 322.3556
SIERRA CITY GEN 11011101/2 | SIERR | SIERRA CITY GEN 1101 | SIERRA | 0.0052893 | 95 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049877 | 85.4511 | 4.262 | 805.7777
GIRVAN 11021028 | GIRVA | GIRVAN 1102 | NORTH VALLEY | 17.4682 | 30.4656 | 99.97% | 3 | 19 | 100% | 100% | 1 | 0.28494 | 14.9507 | 4.26 | 0.24387
CRESCENT MILLS 21013113 | CRESC | CRESCENT MILLS 2101 | NORTH VALLEY | 1.193 | 94.468 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049705 | 85.4511 | 4.2473 | 3.5603
POINT MORETTI 110110722 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 0.60606 | 15.6405 | 41.46% | 0 | 0 | 100% | 100% | 0 | 0.087584 | 47.6367 | 4.1722 | 6.8841
BIG MEADOWS 21012474 | BIG M | BIG MEADOWS 2101 | NORTH VALLEY | 8.0369 | 74.0553 | 100% | 0 | 14 | 96.17% | 0% | 0 | 0.062896 | 65.3912 | 4.1128 | 0.51174
BRUNSWICK 1104761310 | BRUNS | BRUNSWICK 1104 | SIERRA | 0.029625 | 37.5776 | 100% | 0 | 0 | 100% | 100% | 0 | 0.15312 | 26.5534 | 4.0659 | 137.2444
BRUNSWICK 1102CB | BRUNS | BRUNSWICK 1102 | SIERRA | 6.3271 | 51.9471 | 61.35% | 4 | 0 | 99.87% | 31.38% | 0 | 0.047536 | 85.4511 | 4.062 | 0.64199
COTATI 1105CB | COTAT | COTATI 1105 | SONOMA | 3.1602 | 63.5412 | 54.85% | 1 | 0 | 100% | 0% | 0 | 0.061793 | 65.3912 | 4.0407 | 1.2786
WILLOW CREEK 1101CB | WILLO | WILLOW CREEK 1101 | HUMBOLDT | 0.28035 | 73.844 | 25.25% | 2 | 0 | 100% | 100% | 0 | 0.11379 | 35.3263 | 4.0198 | 14.3388
BELL 11072400 | BELL | BELL 1107 | SIERRA | 24.3699 | 40.733 | 58.06% | 2 | 11 | 87.78% | 0% | 0 | 0.061332 | 65.3912 | 4.0106 | 0.16457
OAKLAND K 1104CR326 | OAKLA | OAKLAND K 1104 | EAST BAY | 1.3049 | 10 | 98.1% | 3 | 0 | 100% | 100% | 0 | 0.14914 | 26.5534 | 3.9602 | 3.0348
HAMILTON BRANCH 110190334 | HAMIL | HAMILTON BRANCH 1101 | NORTH VALLEY | 3.3715 | 83.9014 | 99.76% | 0 | 0 | 100% | 0% | 0 | 0.046313 | 85.4511 | 3.9575 | 1.1738
MONTE RIO 11135024 | MONTE | MONTE RIO 1113 | SONOMA | 0.33932 | 27.3622 | 58.73% | 2 | 0 | 100% | 100% | 0 | 0.10965 | 35.3263 | 3.8736 | 11.4159
PARADISE 1103CB | PARAD | PARADISE 1103 | NORTH VALLEY | 2.4339 | 10 | 32.27% | 5 | 0 | 48.95% | 100% | 0 | 0.058983 | 65.3912 | 3.857 | 1.5847
OLEMA 11011318 | OLEMA | OLEMA 1101 | NORTH BAY | 6.3563 | 77.6358 | 7.161% | 18 | 6 | 61.46% | 0% | 0 | 0.045105 | 85.4511 | 3.8543 | 0.60636
SANTA YNEZ 1104Y66 | SANTA | SANTA YNEZ 1104 | LOS PADRES | 16.6796 | 85.1619 | 76.69% | 1 | 3 | 92.13% | 26.5% | 0 | 0.10816 | 35.3263 | 3.8208 | 0.22907
LAYTONVILLE 1102572 | LAYTO | LAYTONVILLE 1102 | HUMBOLDT | 21.4369 | 82.6922 | 96.68% | 7 | 18 | 100% | 0% | 0 | 0.14346 | 26.5534 | 3.8094 | 0.1777
RESEARCH 21029746 | RESEA | RESEARCH 2102 | DIABLO | 0.70252 | 57.1565 | 2.503% | 0 | 3 | 24.99% | 100% | 0 | 0.044375 | 85.4511 | 3.7919 | 5.3975
SHADY GLEN 11012768 | SHADY | SHADY GLEN 1101 | SIERRA | 7.6983 | 67.5569 | 97.78% | 0 | 5 | 95.39% | 10.27% | 0 | 0.057683 | 65.3912 | 3.7719 | 0.48997
MENLO 11038512 | MENLO | MENLO 1103 | PENINSULA | 16.8652 | 73.7343 | 67.92% | 14 | 5 | 100% | 0% | 0 | 0.10603 | 35.3263 | 3.7456 | 0.22209
MOUNTAIN QUARRIES 2101CB | MOUNT | MOUNTAIN QUARRIES 2101 | SIERRA | 24.9741 | 44.4478 | 67.2% | 2 | 3 | 100% | 0% | 0 | 0.056988 | 65.3912 | 3.7265 | 0.14922
MONTE RIO 1111CB | MONTE | MONTE RIO 1111 | SONOMA | 0.26962 | 44.4262 | 0% | 0 | 1 | 100% | 100% | 0 | 0.078152 | 47.6367 | 3.7229 | 13.808
CAMP EVERS 21045096 | CAMP | CAMP EVERS 2104 | CENTRAL COAST | 20.6359 | 43.5028 | 64.15% | 34 | 7 | 100% | 100% | 0 | 0.33163 | 11.2183 | 3.7203 | 0.18028
FORT ROSS 1121124 | FORT | FORT ROSS 1121 | SONOMA | 18.5728 | 86.0744 | 76.02% | 1 | 2 | 100% | 0% | 0 | 0.077065 | 47.6367 | 3.6711 | 0.19766
OLEMA 11011252 | OLEMA | OLEMA 1101 | NORTH BAY | 4.0529 | 83.346 | 14.42% | 10 | 5 | 98.65% | 0% | 0 | 0.042756 | 85.4511 | 3.6535 | 0.90147
FRUITLAND 11426064 | FRUIT | FRUITLAND 1142 | HUMBOLDT | 6.4216 | 80.9642 | 100% | 2 | 4 | 77.51% | 0% | 0 | 0.076552 | 47.6367 | 3.6467 | 0.56788
FORT SEWARD 11211690 | FORT | FORT SEWARD 1121 | HUMBOLDT | 10.4929 | 86.5731 | 100% | 15 | 3 | 64.42% | 0% | 0 | 0.055586 | 65.3912 | 3.6348 | 0.34641
BRUNSWICK 11042112 | BRUNS | BRUNSWICK 1104 | SIERRA | 19.306 | 55.1614 | 89% | 4 | 7 | 100% | 25.18% | 0 | 0.10285 | 35.3263 | 3.6335 | 0.1882
MONROE 2103CB | MONRO | MONROE 2103 | SONOMA | 0.73533 | 61.5712 | 100% | 0 | 0 | 5.132% | 100% | 0 | 0.076074 | 47.6367 | 3.6239 | 4.9282
DESCHUTES 110449024 | DESCH | DESCHUTES 1104 | NORTH VALLEY | 16.4286 | 33.9792 | 100% | 0 | 7 | 97.93% | 0% | 0 | 0.055326 | 65.3912 | 3.6179 | 0.22022
HATTON 1101 | HATTO | HATTON 1101 | CENTRAL COAST | 0.058169 | 90 | 100% | 0 | 0 | 100% | 0% | 0 | 0.054802 | 65.3912 | 3.5836 | 61.6058
MEADOW LANE 2106C558R | MEADO | MEADOW LANE 2106 | DIABLO | 0.20712 | 95 | 0% | 0 | 0 | 1.459% | 100% | 0 | 0.041876 | 85.4511 | 3.5783 | 17.2762
GARBERVILLE 11012026 | GARBE | GARBERVILLE 1101 | HUMBOLDT | 6.3529 | 96.5509 | 100% | 5 | 1 | 100% | 0% | 0 | 0.05472 | 65.3912 | 3.5782 | 0.56324
OAKHURST 110363334 | OAKHU | OAKHURST 1103 | YOSEMITE | 17.2522 | 47.378 | 100% | 1 | 11 | 100% | 10.77% | 0 | 0.054511 | 65.3912 | 3.5646 | 0.20661
GARCIA 0401666 | GARCI | GARCIA 0401 | HUMBOLDT | 2.4311 | 97.9965 | 100% | 2 | 2 | 100% | 0% | 0 | 0.054265 | 65.3912 | 3.5484 | 1.4596
DUNBAR 11021285 | DUNBA | DUNBAR 1102 | SONOMA | 4.061 | 83.8717 | 58.26% | 1 | 2 | 100% | 27.24% | 1 | 0.053737 | 65.3912 | 3.5139 | 0.86528
FITCH MOUNTAIN 1113356 | FITCH | FITCH MOUNTAIN 1113 | SONOMA | 9.9757 | 80.7752 | 75.25% | 5 | 1 | 65.83% | 51.2% | 1 | 0.073371 | 47.6367 | 3.4951 | 0.35037
MIWUK 170179118 | MIWUK | MIWUK 1701 | YOSEMITE | 0.019355 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 26.5534 | 3.4578 | 178.654
SONOMA 1106376 | SONOM | SONOMA 1106 | SONOMA | 0.6618 | 42.582 | 100% | 0 | 0 | 12.23% | 100% | 0 | 0.072044 | 47.6367 | 3.4319 | 5.1858
CRESCENT MILLS 21012232 | CRESC | CRESCENT MILLS 2101 | NORTH VALLEY | 17.0798 | 82.544 | 99.96% | 2 | 0 | 84.55% | 0% | 0 | 0.052465 | 65.3912 | 3.4308 | 0.20087
ZACA 1102CB | ZACA | ZACA 1102 | LOS PADRES | 15.8871 | 63.476 | 75.75% | 0 | 4 | 76.4% | 37.44% | 0 | 0.096438 | 35.3263 | 3.4068 | 0.21444
FRUITLAND 1142CB | FRUIT | FRUITLAND 1142 | HUMBOLDT | 10.4822 | 87.3271 | 88.71% | 7 | 4 | 68.32% | 0% | 0 | 0.071375 | 47.6367 | 3.4 | 0.32436
MIDDLETOWN 11011314 | MIDDL | MIDDLETOWN 1101 | HUMBOLDT | 0.82482 | 85.7951 | 100% | 0 | 0 | 88.81% | 5.14% | 1 | 0.051914 | 65.3912 | 3.3947 | 4.1157
LAYTONVILLE 1102682 | LAYTO | LAYTONVILLE 1102 | HUMBOLDT | 14.8214 | 90.6873 | 91.3% | 5 | 3 | 100% | 0% | 0 | 0.051212 | 65.3912 | 3.3488 | 0.22594
PASO ROBLES 1103N04 | PASO | PASO ROBLES 1103 | LOS PADRES | 0.58532 | 54.1264 | 3.167% | 0 | 8 | 100% | 0% | 0 | 0.051036 | 65.3912 | 3.3373 | 5.7017
GARCIA 0401CB | GARCI | GARCIA 0401 | HUMBOLDT | 0.042407 | 98 | 100% | 0 | 0 | 100% | 0% | 0 | 0.050859 | 65.3912 | 3.3257 | 78.4228
SILVERADO 21051306 | SILVE | SILVERADO 2105 | NORTH BAY | 2.7442 | 84.7075 | 83.99% | 0 | 2 | 34.98% | 54.43% | 0 | 0.068801 | 47.6367 | 3.2775 | 1.1943
PINE GROVE 1101CB | PINE | PINE GROVE 1101 | STOCKTON | 4.2594 | 78.3336 | 50.63% | 0 | 5 | 100% | 0% | 0 | 0.038055 | 85.4511 | 3.2518 | 0.76344
BIG BASIN 110165444 | BIG B | BIG BASIN 1101 | CENTRAL COAST | 0.47094 | 48.0736 | 0% | 2 | 0 | 100% | 100% | 0 | 0.090816 | 35.3263 | 3.2082 | 6.8123
SHINGLE SPRINGS 21099372 | SHING | SHINGLE SPRINGS 2109 | SIERRA | 17.5824 | 48.8833 | 68.76% | 2 | 5 | 100% | 52.97% | 0 | 0.1201 | 26.5534 | 3.1891 | 0.18138
TASSAJARA 210812712 | TASSA | TASSAJARA 2108 | DIABLO | 0.60405 | 70.6966 | 76.13% | 0 | 2 | 18.42% | 100% | 0 | 0.089254 | 35.3263 | 3.153 | 5.2198
CORNING 110185152 | CORNI | CORNING 1101 | NORTH VALLEY | 23.0821 | 26.0719 | 100% | 2 | 8 | 100% | 0% | 0 | 0.11691 | 26.5534 | 3.1042 | 0.13449
COTATI 110379140 | COTAT | COTATI 1103 | SONOMA | 9.8425 | 61.4372 | 48.82% | 7 | 2 | 79.77% | 0% | 0 | 0.047459 | 65.3912 | 3.1034 | 0.31531
DIAMOND SPRINGS 110518935 | DIAMO | DIAMOND SPRINGS 1105 | SIERRA | 6.6942 | 21.2209 | 100% | 2 | 4 | 100% | 72.5% | 0 | 0.11646 | 26.5534 | 3.0925 | 0.46197
CALISTOGA 11011087 | CALIS | CALISTOGA 1101 | NORTH BAY | 1.9847 | 74.7271 | 70.51% | 0 | 0 | 100% | 100% | 0 | 0.15452 | 19.9979 | 3.0901 | 1.5569
RACETRACK 170455798 | RACET | RACETRACK 1704 | YOSEMITE | 15.7881 | 56.8107 | 46.06% | 3 | 13 | 100% | 0% | 0 | 0.064582 | 47.6367 | 3.0765 | 0.19486
CAMP EVERS 210511010 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 2.2251 | 32.8132 | 34.55% | 4 | 3 | 100% | 100% | 0 | 0.11572 | 26.5534 | 3.0729 | 1.381
DUNBAR 11014817 | DUNBA | DUNBAR 1101 | SONOMA | 3.1798 | 21.7127 | 52.45% | 3 | 3 | 100% | 100% | 0 | 0.15344 | 19.9979 | 3.0685 | 0.96499
COTTONWOOD 11039072 | COTTO | COTTONWOOD 1103 | NORTH VALLEY | 28.4061 | 60.3164 | 100% | 4 | 3 | 99.13% | 0% | 0 | 0.06438 | 47.6367 | 3.0669 | 0.10797
CLOVERDALE 1101 | CLOVE | CLOVERDALE 1101 | SONOMA | 0.067026 | 85 | 100% | 0 | 0 | 100% | 0% | 0 | 0.046733 | 65.3912 | 3.0559 | 45.5934
TASSAJARA 21123202 | TASSA | TASSAJARA 2112 | DIABLO | 0.99352 | 84.671 | 60.56% | 0 | 0 | 100% | 100% | 0 | 0.15269 | 19.9979 | 3.0536 | 3.0735
ATASCADERO 11012537 | ATASC | ATASCADERO 1101 | LOS PADRES | 15.4143 | 42.2463 | 87.6% | 5 | 1 | 100% | 82.31% | 1 | 0.15256 | 19.9979 | 3.0509 | 0.19793
OAKLAND X 1104CR022 | OAKLA | OAKLAND X 1104 | EAST BAY | 5.946 | 14.8032 | 44.25% | 8 | 4 | 100% | 100% | 0 | 0.14986 | 19.9979 | 2.997 | 0.50404
WILLOW CREEK 11037514 | WILLO | WILLOW CREEK 1103 | HUMBOLDT | 9.2339 | 70.9692 | 70.67% | 10 | 14 | 91.91% | 2.029% | 1 | 0.062494 | 47.6367 | 2.977 | 0.3224
SANTA ROSA A 1104220 | SANTA | SANTA ROSA A 1104 | SONOMA | 9.5297 | 27.599 | 64.91% | 1 | 14 | 100% | 64.31% | 0 | 0.11149 | 26.5534 | 2.9604 | 0.31065
CAMP EVERS 210511384 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 4.1064 | 10 | 25.57% | 1 | 1 | 100% | 100% | 0 | 0.11123 | 26.5534 | 2.9535 | 0.71923
WILLITS 110337506 | WILLI | WILLITS 1103 | HUMBOLDT | 11.4286 | 90.7952 | 60.25% | 4 | 3 | 100% | 0% | 0 | 0.04503 | 65.3912 | 2.9446 | 0.25765
JESSUP 110276068 | JESSU | JESSUP 1102 | NORTH VALLEY | 15.5129 | 23.0172 | 100% | 2 | 4 | 80.72% | 0% | 0 | 0.061753 | 47.6367 | 2.9417 | 0.18963
SPANISH CREEK 4401CB | SPANI | SPANISH CREEK 4401 | NORTH VALLEY | 7.9163 | 94.7918 | 10.89% | 2 | 9 | 99.83% | 0% | 0 | 0.034339 | 85.4511 | 2.9343 | 0.37066
PENRYN 1103604 | PENRY | PENRYN 1103 | SIERRA | 26.4899 | 35.3404 | 72.55% | 7 | 11 | 100% | 0% | 0 | 0.061577 | 47.6367 | 2.9333 | 0.11073
PARADISE 110181966 | PARAD | PARADISE 1101 | NORTH VALLEY | 0.1834 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 47.6367 | 2.9325 | 15.9897
TIVY VALLEY 1107869946 | TIVY | TIVY VALLEY 1107 | FRESNO | 29.8533 | 31.5996 | 100% | 0 | 2 | 100% | 0% | 0 | 0.044292 | 65.3912 | 2.8963 | 0.097019
GIRVAN 11019732 | GIRVA | GIRVAN 1101 | NORTH VALLEY | 21.139 | 36.4737 | 100% | 2 | 6 | 100% | 100% | 0 | 0.1928 | 14.9507 | 2.8825 | 0.13636
CORRAL 1101 | CORRA | CORRAL 1101 | STOCKTON | 0.001152 | 75 | 100% | 0 | 0 | 100% | 0% | 0 | 0.043778 | 65.3912 | 2.8627 | 2485.0793
BIG BASIN 11026219 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 0.89903 | 23.7161 | 100% | 1 | 0 | 100% | 100% | 0 | 0.14284 | 19.9979 | 2.8564 | 3.1773
PINE GROVE 11011021 | PINE | PINE GROVE 1101 | STOCKTON | 4.1934 | 79.4355 | 93.37% | 0 | 1 | 100% | 0% | 0 | 0.043638 | 65.3912 | 2.8535 | 0.68049
MIRABEL 110213597 | MIRAB | MIRABEL 1102 | SONOMA | 0.47204 | 30.1701 | 51.63% | 3 | 0 | 100% | 100% | 0 | 0.10712 | 26.5534 | 2.8444 | 6.0258
KONOCTI 110264664 | KONOC | KONOCTI 1102 | HUMBOLDT | 27.2111 | 54.3183 | 71% | 3 | 9 | 94.13% | 22.47% | 0 | 0.10647 | 26.5534 | 2.8272 | 0.1039
COTATI 110599720 | COTAT | COTATI 1105 | SONOMA | 7.8564 | 53.7004 | 71.89% | 3 | 7 | 63.87% | 0% | 0 | 0.042996 | 65.3912 | 2.8115 | 0.35787
BRUNSWICK 11102664 | BRUNS | BRUNSWICK 1110 | SIERRA | 9.7807 | 42.9965 | 66.17% | 2 | 0 | 90.12% | 0% | 0 | 0.042278 | 65.3912 | 2.7646 | 0.28266
LOW GAP 11012094 | LOW G | LOW GAP 1101 | HUMBOLDT | 15.318 | 83.9747 | 100% | 2 | 4 | 90.42% | 0% | 0 | 0.077716 | 35.3263 | 2.7454 | 0.17923
COTTONWOOD 11031616 | COTTO | COTTONWOOD 1103 | NORTH VALLEY | 45.6614 | 47.3529 | 99.79% | 2 | 10 | 92.93% | 0% | 0 | 0.10209 | 26.5534 | 2.7109 | 0.05937
PARADISE 110236656 | PARAD | PARADISE 1102 | NORTH VALLEY | 3.3309 | 17.0477 | 19.52% | 3 | 5 | 87.51% | 100% | 0 | 0.076178 | 35.3263 | 2.6911 | 0.8079
BRUNSWICK 1102940 | BRUNS | BRUNSWICK 1102 | SIERRA | 0.6541 | 82.3173 | 27.04% | 0 | 0 | 18.81% | 100% | 0 | 0.056253 | 47.6367 | 2.6797 | 4.0968
BRUNSWICK 11047181 | BRUNS | BRUNSWICK 1104 | SIERRA | 0.77307 | 57.8754 | 100% | 1 | 1 | 100% | 0% | 0 | 0.040435 | 65.3912 | 2.6441 | 3.4203
MIDDLETOWN 1102998 | MIDDL | MIDDLETOWN 1102 | HUMBOLDT | 14.694 | 30.2565 | 100% | 0 | 1 | 86% | 0% | 0 | 0.055128 | 47.6367 | 2.6261 | 0.17872
SANTA ROSA A 1111114 | SANTA | SANTA ROSA A 1111 | SONOMA | 5.593 | 82.824 | 61.55% | 3 | 5 | 48.78% | 0.05081% | 0 | 0.039882 | 65.3912 | 2.608 | 0.46629
MENLO 11028952 | MENLO | MENLO 1102 | PENINSULA | 6.6194 | 37.3674 | 79.3% | 6 | 6 | 97.26% | 0% | 0 | 0.07359 | 35.3263 | 2.5996 | 0.39273
COTATI 110536536 | COTAT | COTATI 1105 | SONOMA | 14.0222 | 66.9943 | 49.66% | 3 | 4 | 71.19% | 0% | 0 | 0.039741 | 65.3912 | 2.5987 | 0.18533
BIG BASIN 110112838 | BIG B | BIG BASIN 1101 | CENTRAL COAST | 2.3481 | 22.8055 | 19.65% | 7 | 1 | 100% | 100% | 0 | 0.097327 | 26.5534 | 2.5844 | 1.1006
MORAGA 110183424 | MORAG | MORAGA 1101 | DIABLO | 1.6164 | 79.1593 | 0% | 0 | 0 | 100% | 62.3% | 0 | 0.053892 | 47.6367 | 2.5672 | 1.5883
SHADY GLEN 110248894 | SHADY | SHADY GLEN 1102 | SIERRA | 8.076 | 49.6205 | 67.94% | 0 | 5 | 80.69% | 16.07% | 0 | 0.038596 | 65.3912 | 2.5239 | 0.31251
HALF MOON BAY 11038894 | HALF | HALF MOON BAY 1103 | PENINSULA | 11.2938 | 71.3584 | 49.24% | 24 | 2 | 100% | 0% | 0 | 0.052113 | 47.6367 | 2.4825 | 0.21981
COTATI 1105634 | COTAT | COTATI 1105 | SONOMA | 6.9392 | 85.5117 | 61.91% | 2 | 3 | 100% | 0% | 0 | 0.037803 | 65.3912 | 2.472 | 0.35623
LAURELES 111110141 | LAURE | LAURELES 1111 | CENTRAL COAST | 2.922 | 83.2816 | 100% | 0 | 0 | 100% | 100% | 0 | 0.22027 | 11.2183 | 2.471 | 0.84567
COARSEGOLD 2104570682 | COARS | COARSEGOLD 2104 | YOSEMITE | 2.0271 | 37.4462 | 79.77% | 2 | 5 | 100% | 0% | 0 | 0.037588 | 65.3912 | 2.4579 | 1.2125
PETALUMA C 1108296 | PETAL | PETALUMA C 1108 | SONOMA | 14.7729 | 78.7625 | 21.22% | 3 | 7 | 100% | 0% | 0 | 0.037166 | 65.3912 | 2.4303 | 0.16451
MOLINO 110279306 | MOLIN | MOLINO 1102 | SONOMA | 3.6243 | 55.9348 | 57.2% | 3 | 2 | 44.33% | 48.34% | 1 | 0.037109 | 65.3912 | 2.4266 | 0.66954
LAYTONVILLE 110268436 | LAYTO | LAYTONVILLE 1102 | HUMBOLDT | 9.1013 | 91.8828 | 93.46% | 1 | 2 | 100% | 32.77% | 1 | 0.091162 | 26.5534 | 2.4207 | 0.26597
VACA DIXON 110540092 | VACA | VACA DIXON 1105 | SACRAMENTO | 23.831 | 65.7788 | 89.52% | 2 | 6 | 55.42% | 0% | 0 | 0.036947 | 65.3912 | 2.416 | 0.10138
BIG BASIN 110212758 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 6.1262 | 42.4144 | 40.92% | 12 | 2 | 100% | 100% | 0 | 0.21481 | 11.2183 | 2.4099 | 0.39337
HALF MOON BAY 11038089 | HALF | HALF MOON BAY 1103 | PENINSULA | 2.9815 | 77.4451 | 41.57% | 4 | 4 | 100% | 0% | 0 | 0.036303 | 65.3912 | 2.3739 | 0.79621
COARSEGOLD 2104369777 | COARS | COARSEGOLD 2104 | YOSEMITE | 18.4298 | 46.1002 | 90.43% | 1 | 34 | 100% | 0% | 0 | 0.066997 | 35.3263 | 2.3668 | 0.12842
SHADY GLEN 1101CB | SHADY | SHADY GLEN 1101 | SIERRA | 4.4237 | 59.4195 | 32.95% | 0 | 5 | 80.65% | 0% | 0 | 0.027502 | 85.4511 | 2.3501 | 0.53125
PETALUMA C 1108636 | PETAL | PETALUMA C 1108 | SONOMA | 9.2277 | 74.6783 | 45.5% | 1 | 1 | 100% | 0% | 0 | 0.048927 | 47.6367 | 2.3307 | 0.25258
CAMP EVERS 210595394 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 0.49589 | 10 | 8.806% | 0 | 0 | 100% | 100% | 0 | 0.065893 | 35.3263 | 2.3278 | 4.6941
OCEANO 1104Q10 | OCEAN | OCEANO 1104 | LOS PADRES | 23.5484 | 28.2238 | 59% | 7 | 3 | 100% | 0% | 0 | 0.065893 | 35.3263 | 2.3277 | 0.098849
COTTONWOOD 11031344 | COTTO | COTTONWOOD 1103 | NORTH VALLEY | 7.7962 | 44.5024 | 98.83% | 0 | 5 | 62.89% | 0% | 0 | 0.035503 | 65.3912 | 2.3216 | 0.29778
LAYTONVILLE 1102500 | LAYTO | LAYTONVILLE 1102 | HUMBOLDT | 20.1821 | 81.3832 | 99.67% | 9 | 6 | 69.04% | 0% | 0 | 0.048589 | 47.6367 | 2.3146 | 0.11469
MOLINO 1101338 | MOLIN | MOLINO 1101 | SONOMA | 7.3596 | 75.7123 | 66.21% | 4 | 4 | 51.47% | 0% | 0 | 0.035347 | 65.3912 | 2.3114 | 0.31406
REDBUD 1102CB | REDBU | REDBUD 1102 | HUMBOLDT | 15.5011 | 65.2981 | 72.86% | 2 | 2 | 77.01% | 9.757% | 0 | 0.048504 | 47.6367 | 2.3106 | 0.14906
PASO ROBLES 1103N54 | PASO | PASO ROBLES 1103 | LOS PADRES | 19.5682 | 48.3867 | 60.55% | 1 | 29 | 90.91% | 0% | 0 | 0.065373 | 35.3263 | 2.3094 | 0.11802
PENRYN 11032198 | PENRY | PENRYN 1103 | SIERRA | 19.8234 | 39.0911 | 53.27% | 4 | 16 | 94.86% | 0% | 0 | 0.048469 | 47.6367 | 2.3089 | 0.11647
DUNBAR 1102246 | DUNBA | DUNBAR 1102 | SONOMA | 14.7102 | 40.7068 | 52.1% | 6 | 13 | 100% | 1.558% | 0 | 0.064871 | 35.3263 | 2.2917 | 0.15579
PETALUMA C 1108628 | PETAL | PETALUMA C 1108 | SONOMA | 9.0995 | 58.7807 | 34.73% | 0 | 3 | 82.01% | 0% | 0 | 0.035008 | 65.3912 | 2.2892 | 0.25158
COARSEGOLD 210210207 | COARS | COARSEGOLD 2102 | YOSEMITE | 3.5762 | 10 | 99.5% | 3 | 11 | 100% | 100% | 0 | 0.20336 | 11.2183 | 2.2814 | 0.63793
OCEANO 1104V36 | OCEAN | OCEANO 1104 | LOS PADRES | 8.9209 | 45.6964 | 61.88% | 2 | 5 | 67.02% | 0% | 0 | 0.047581 | 47.6367 | 2.2666 | 0.25408
PUTAH CREEK 11033851 | PUTAH | PUTAH CREEK 1103 | SACRAMENTO | 3.6658 | 82.0611 | 100% | 0 | 0 | 70.81% | 0% | 0 | 0.034621 | 65.3912 | 2.2639 | 0.61757
SHEPHERD 2111R1400 | SHEPH | SHEPHERD 2111 | FRESNO | 19.9144 | 43.3803 | 100% | 0 | 4 | 86.57% | 0% | 0 | 0.063987 | 35.3263 | 2.2604 | 0.11351
FORESTHILL 1102CB | FORES | FORESTHILL 1102 | SIERRA | 1.6478 | 87.6992 | 97.59% | 0 | 0 | 100% | 100% | 0 | 0.19983 | 11.2183 | 2.2418 | 1.3605
OILFIELDS 1103N46 | OILFI | OILFIELDS 1103 | CENTRAL COAST | 5.8257 | 79.2916 | 67.5% | 0 | 4 | 100% | 0% | 0 | 0.062709 | 35.3263 | 2.2153 | 0.38026
COTATI 1103CB | COTAT | COTATI 1103 | SONOMA | 12.0212 | 77.6953 | 26.01% | 1 | 5 | 100% | 0% | 0 | 0.046374 | 47.6367 | 2.2091 | 0.18377
CAMP EVERS 21055188 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 1.985 | 10 | 58.42% | 1 | 0 | 100% | 100% | 0 | 0.10955 | 19.9979 | 2.1908 | 1.1037
CORNING 110164090 | CORNI | CORNING 1101 | NORTH VALLEY | 13.6992 | 19.4323 | 100% | 1 | 9 | 100% | 0% | 0 | 0.061365 | 35.3263 | 2.1678 | 0.15824
SILVERADO 21051308 | SILVE | SILVERADO 2105 | NORTH BAY | 0.01945 | 80.9995 | 16% | 3 | 1 | 0.3576% | 100% | 0 | 0.045462 | 47.6367 | 2.1657 | 111.3457
CAMP EVERS 21055577 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 1.1615 | 10 | 45.86% | 6 | 1 | 100% | 100% | 0 | 0.10796 | 19.9979 | 2.1589 | 1.8588
PARADISE 11041571 | PARAD | PARADISE 1104 | NORTH VALLEY | 0.64266 | 10 | 49.69% | 2 | 2 | 100% | 100% | 0 | 0.10792 | 19.9979 | 2.1582 | 3.3583
HIGHLANDS 1103828 | HIGHL | HIGHLANDS 1103 | HUMBOLDT | 6.7375 | 63.3162 | 90.74% | 0 | 3 | 64.07% | 0% | 0 | 0.032181 | 65.3912 | 2.1043 | 0.31233
PACIFICA 1101CB | PACIF | PACIFICA 1101 | PENINSULA | 1.1754 | 10 | 25.99% | 0 | 0 | 43.55% | 100% | 0 | 0.044128 | 47.6367 | 2.1021 | 1.7885
SAN LUIS OBISPO 110342344 | SAN L | SAN LUIS OBISPO 1103 | LOS PADRES | 7.6647 | 51.698 | 64.08% | 0 | 1 | 70.58% | 0% | 0 | 0.031898 | 65.3912 | 2.0859 | 0.27214
CAMP EVERS 21035753 | CAMP | CAMP EVERS 2103 | CENTRAL COAST | 2.4228 | 18.1993 | 27.31% | 10 | 4 | 100% | 100% | 0 | 0.13875 | 14.9507 | 2.0744 | 0.8562
NORTH BRANCH 110111206 | NORTH | NORTH BRANCH 1101 | STOCKTON | 17.2475 | 65.0034 | 87.98% | 1 | 4 | 96.4% | 0% | 0 | 0.057888 | 35.3263 | 2.045 | 0.11857
WEIMER 1101 | WEIME | WEIMER 1101 | (blank) | 0.15676 | 70 | 100% | 0 | 0 | 100% | 0% | 0 | 0.042368 | 47.6367 | 2.0183 | 12.8751
PASO ROBLES 1103N50 | PASO | PASO ROBLES 1103 | LOS PADRES | 2.1383 | 48.485 | 34.16% | 0 | 1 | 100% | 0% | 0 | 0.042301 | 47.6367 | 2.0151 | 0.94241
CRESCENT MILLS 2101CB | CRESC | CRESCENT MILLS 2101 | NORTH VALLEY | 4.0564 | 89.8056 | 75.4% | 0 | 1 | 71.09% | 0% | 0 | 0.030639 | 65.3912 | 2.0035 | 0.49391
MOLINO 11015042 | MOLIN | MOLINO 1101 | SONOMA | 5.4336 | 70.9721 | 53.86% | 5 | 2 | 79.32% | 0% | 0 | 0.030542 | 65.3912 | 1.9971 | 0.36756
DUNBAR 11022359 | DUNBA | DUNBAR 1102 | SONOMA | 4.5098 | 82.5925 | 84.36% | 0 | 1 | 100% | 0% | 0 | 0.041489 | 47.6367 | 1.9764 | 0.43825
BRUNSWICK 111063100 | BRUNS | BRUNSWICK 1110 | SIERRA | 4.1271 | 39.6111 | 66.99% | 1 | 2 | 100% | 0% | 0 | 0.041392 | 47.6367 | 1.9718 | 0.47776
HALF MOON BAY 110398440 | HALF | HALF MOON BAY 1103 | PENINSULA | 8.1037 | 78.0886 | 41.99% | 8 | 1 | 100% | 0% | 0 | 0.041193 | 47.6367 | 1.9623 | 0.24215
COTATI 1103132 | COTAT | COTATI 1103 | SONOMA | 25.3022 | 74.6812 | 24.81% | 4 | 9 | 100% | 0% | 0 | 0.073801 | 26.5534 | 1.9597 | 0.07745
VACAVILLE 1108 | VACAV | VACAVILLE 1108 | SACRAMENTO | 0.027876 | 65 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041002 | 47.6367 | 1.9532 | 70.0681
BIG BASIN 11019773 | BIG B | BIG BASIN 1101 | CENTRAL COAST | 0.4507 | 10 | 17.07% | 7 | 0 | 100% | 100% | 0 | 0.097654 | 19.9979 | 1.9529 | 4.333
PINECREST 0401CB | PINEC | PINECREST 0401 | YOSEMITE | 0.021247 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 14.9507 | 1.9469 | 91.6321
PINECREST 0401 | PINEC | PINECREST 0401 | YOSEMITE | 0.0016115 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 14.9507 | 1.9469 | 1208.1685
SILVERADO 2104726 | SILVE | SILVERADO 2104 | NORTH BAY | 29.6312 | 77.5719 | 85.35% | 3 | 1 | 83.81% | 20.91% | 0 | 0.072604 | 26.5534 | 1.9279 | 0.065062
BELLEVUE 2103478 | BELLE | BELLEVUE 2103 | SONOMA | 7.8213 | 71.5626 | 88.7% | 0 | 2 | 38.92% | 0% | 0 | 0.02921 | 65.3912 | 1.9101 | 0.24421
MIRABEL 11027401 | MIRAB | MIRABEL 1102 | SONOMA | 1.0644 | 17.3394 | 6.536% | 3 | 1 | 100% | 100% | 0 | 0.071799 | 26.5534 | 1.9065 | 1.7912
HIGHLANDS 1102628 | HIGHL | HIGHLANDS 1102 | HUMBOLDT | 14.1896 | 81.6211 | 32.89% | 0 | 6 | 100% | 58.23% | 1 | 0.095308 | 19.9979 | 1.906 | 0.13432
CLARKSVILLE 2104CB | CLARK | CLARKSVILLE 2104 | SIERRA | 9.4695 | 34.2727 | 54.5% | 0 | 3 | 89.57% | 0% | 0 | 0.028962 | 65.3912 | 1.8939 | 0.2
CORRAL 110136652 | CORRA | CORRAL 1101 | STOCKTON | 18.0317 | 36.0873 | 87.44% | 1 | 8 | 100% | 0% | 0 | 0.053562 | 35.3263 | 1.8922 | 0.10493
VACAVILLE 110838316 | VACAV | VACAVILLE 1108 | SACRAMENTO | 14.7024 | 65.6281 | 99.57% | 1 | 4 | 63.02% | 0% | 0 | 0.052621 | 35.3263 | 1.8589 | 0.12644
BRUNSWICK 110378862 | BRUNS | BRUNSWICK 1103 | SIERRA | 0.84386 | 75.0835 | 56.54% | 0 | 0 | 62.09% | 0% | 0 | 0.021418 | 85.4511 | 1.8302 | 2.1688
RED BLUFF 110451238 | RED B | RED BLUFF 1104 | NORTH VALLEY | 39.381 | 43.7242 | 96.09% | 3 | 21 | 100% | 0% | 0 | 0.089857 | 19.9979 | 1.7969 | 0.04563
HIGHLANDS 11031282 | HIGHL | HIGHLANDS 1103 | HUMBOLDT | 15.0139 | 42.6416 | 99.84% | 3 | 8 | 89.98% | 0% | 0 | 0.050585 | 35.3263 | 1.787 | 0.11902
BUELLTON 1102Y50 | BUELL | BUELLTON 1102 | LOS PADRES | 11.1963 | 40.402 | 55.79% | 1 | 7 | 87.11% | 0% | 0 | 0.037194 | 47.6367 | 1.7718 | 0.15825
PUTAH CREEK 110267858 | PUTAH | PUTAH CREEK 1102 | SACRAMENTO | 11.5068 | 51.7319 | 80.2% | 2 | 0 | 99.07% | 0% | 0 | 0.037122 | 47.6367 | 1.7684 | 0.15368
RACETRACK 170423195 | RACET | RACETRACK 1704 | YOSEMITE | 7.7484 | 59.3101 | 42.51% | 0 | 0 | 100% | 0% | 0 | 0.036794 | 47.6367 | 1.7528 | 0.22621
OLEMA 11011200 | OLEMA | OLEMA 1101 | NORTH BAY | 2.8963 | 61.7343 | 11.72% | 2 | 7 | 100% | 0% | 0 | 0.026697 | 65.3912 | 1.7458 | 0.60276
PACIFICA 11015001 | PACIF | PACIFICA 1101 | PENINSULA | 1.7299 | 13.6047 | 57.13% | 0 | 0 | 33.8% | 76.31% | 0 | 0.036346 | 47.6367 | 1.7314 | 1.0008
LAYTONVILLE 110189606 | LAYTO | LAYTONVILLE 1101 | HUMBOLDT | 11.3479 | 67.7426 | 99.65% | 4 | 7 | 95.33% | 0% | 0 | 0.048183 | 35.3263 | 1.7021 | 0.15
ELK CREEK 1101CB | ELK C | ELK CREEK 1101 | NORTH VALLEY | 0.084247 | 80 | 68.8% | 0 | 0 | 100% | 0% | 0 | 0.035328 | 47.6367 | 1.6829 | 19.9757
VACA DIXON 110118292 | VACA | VACA DIXON 1101 | SACRAMENTO | 0.82637 | 74.5954 | 100% | 0 | 2 | 13.83% | 0% | 0 | 0.019682 | 85.4511 | 1.6818 | 2.0352
COARSEGOLD 21046288 | COARS | COARSEGOLD 2104 | YOSEMITE | 10.4247 | 64.6171 | 98.8% | 1 | 30 | 100% | 0% | 0 | 0.084064 | 19.9979 | 1.6811 | 0.16126
MORAGA 110531512 | MORAG | MORAGA 1105 | DIABLO | 1.6381 | 82.7006 | 6.913% | 0 | 1 | 35.45% | 68.16% | 0 | 0.035075 | 47.6367 | 1.6709 | 1.02
IGNACIO 11042447 | IGNAC | IGNACIO 1104 | NORTH BAY | 0.96609 | 32.7068 | 67.19% | 4 | 5 | 90.01% | 0% | 0 | 0.034924 | 47.6367 | 1.6637 | 1.7221
LAKEVILLE 11023341 | LAKEV | LAKEVILLE 1102 | SONOMA | 8.3809 | 81.4101 | 63.14% | 2 | 0 | 66.79% | 0% | 0 | 0.02532 | 65.3912 | 1.6557 | 0.19755
WISE 1102307494 | WISE | WISE 1102 | SIERRA | 32.9312 | 34.3215 | 79.46% | 1 | 9 | 98.67% | 0% | 0 | 0.082577 | 19.9979 | 1.6514 | 0.050146
SPRING GAP 17029280 | SPRIN | SPRING GAP 1702 | YOSEMITE | 6.3606 | 34.7112 | 42.89% | 5 | 5 | 100% | 100% | 0 | 0.14642 | 11.2183 | 1.6426 | 0.25824
CAMP EVERS 2105BL 2101 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 0.0032282 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 26.5534 | 1.6346 | 506.3508
GREENBRAE 1103 | GREEN | GREENBRAE 1103 | NORTH BAY | 0.019268 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 26.5534 | 1.6346 | 84.8333
LAURELES 111184523 | LAURE | LAURELES 1111 | CENTRAL COAST | 1.2223 | 80.6528 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045426 | 35.3263 | 1.6047 | 1.3129
MERCED FALLS 110285002 | MERCE | MERCED FALLS 1102 | YOSEMITE | 35.632 | 29.6878 | 97.17% | 0 | 6 | 100% | 0% | 0 | 0.059691 | 26.5534 | 1.585 | 0.044483
BELL 111056214 | BELL | BELL 1110 | SIERRA | 0.30639 | 85 | 100% | 0 | 0 | 4.593% | 0% | 0 | 0.018495 | 85.4511 | 1.5804 | 5.1583
VACAVILLE 111113652 | VACAV | VACAVILLE 1111 | SACRAMENTO | 4.3673 | 25.6376 | 64.23% | 1 | 3 | 100% | 0% | 0 | 0.033137 | 47.6367 | 1.5785 | 0.36144
APPLE HILL 1104CB | APPLE | APPLE HILL 1104 | SIERRA | 4.2262 | 51.4608 | 51.9% | 3 | 4 | 100% | 0% | 0 | 0.03278 | 47.6367 | 1.5616 | 0.36949
ROSSMOOR 1102CB | ROSSM | ROSSMOOR 1102 | DIABLO | 0.0028423 | 10 | 0% | 0 | 0 | 0.1985% | 100% | 0 | 0.023559 | 65.3912 | 1.5406 | 542.0086
STELLING 11102243 | STELL | STELLING 1110 | DE ANZA | 1.8981 | 73.5691 | 46.49% | 9 | 0 | 100% | 0% | 0 | 0.031796 | 47.6367 | 1.5146 | 0.79798
JESSUP 11011993 | JESSU | JESSUP 1101 | NORTH VALLEY | 2.9672 | 23.0128 | 100% | 0 | 1 | 100% | 0% | 0 | 0.031722 | 47.6367 | 1.5111 | 0.50929
TEMPLETON 2113A70 | TEMPL | TEMPLETON 2113 | LOS PADRES | 22.5502 | 49.7318 | 87.96% | 0 | 9 | 33.69% | 0% | 0 | 0.03134 | 47.6367 | 1.4929 | 0.066204
CORRAL 110112612 | CORRA | CORRAL 1101 | STOCKTON | 18.7862 | 47.6011 | 68.25% | 0 | 10 | 93.49% | 0% | 0 | 0.042229 | 35.3263 | 1.4918 | 0.079409
NORTH DUBLIN 210311101 | NORTH | NORTH DUBLIN 2103 | MISSION | 3.6926 | 66.2488 | 89.68% | 0 | 0 | 100% | 0% | 0 | 0.05582 | 26.5534 | 1.4822 | 0.4014
BIG BASIN 1102 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 0.014511 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 11.2183 | 1.4609 | 100.6745
GIRVAN 1102 | GIRVA | GIRVAN 1102 | NORTH VALLEY | 0.038598 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 11.2183 | 1.4609 | 37.8488
SEACLIFF 0402CB | SEACL | SEACLIFF 0402 | CENTRAL COAST | 0.96395 | 10 | 24.34% | 2 | 0 | 62.04% | 63.7% | 0 | 0.030212 | 47.6367 | 1.4392 | 1.493
WISE 11022054 | WISE | WISE 1102 | SIERRA | 12.9562 | 34.6019 | 54.65% | 2 | 5 | 100% | 0% | 0 | 0.030193 | 47.6367 | 1.4383 | 0.11101
CRESCENT MILLS 21012056 | CRESC | CRESCENT MILLS 2101 | NORTH VALLEY | 2.8566 | 93.184 | 33.06% | 0 | 0 | 44.02% | 0% | 0 | 0.016743 | 85.4511 | 1.4307 | 0.50083
FULTON 1107CB | FULTO | FULTON 1107 | SONOMA | 0.65239 | 10 | 62.57% | 2 | 0 | 4.947% | 100% | 0 | 0.053816 | 26.5534 | 1.429 | 2.1904
OCEANO 1104Q08 | OCEAN | OCEANO 1104 | LOS PADRES | 12.4392 | 24.3462 | 67.44% | 7 | 8 | 100% | 0% | 0 | 0.040257 | 35.3263 | 1.4221 | 0.11433
UKIAH 1113CB | UKIAH | UKIAH 1113 | HUMBOLDT | 6.3928 | 56.8513 | 87.48% | 1 | 9 | 40.25% | 0% | 0 | 0.040164 | 35.3263 | 1.4188 | 0.22194
CORRAL 110112606 | CORRA | CORRAL 1101 | STOCKTON | 22.4607 | 31.7729 | 96.48% | 1 | 4 | 100% | 0% | 0 | 0.040006 | 35.3263 | 1.4133 | 0.062921
RESERVATION ROAD 11013026 | RESER | RESERVATION ROAD 1101 | CENTRAL COAST | 21.8928 | 54.2364 | 36.93% | 7 | 8 | 96.87% | 0% | 0 | 0.070296 | 19.9979 | 1.4058 | 0.064212
SAND CREEK 11037140 | SAND | SAND CREEK 1103 | FRESNO | 26.314 | 18.5001 | 91.83% | 0 | 4 | 100% | 0% | 0 | 0.03967 | 35.3263 | 1.4014 | 0.053256
GUALALA 11124431 | GUALA | GUALALA 1112 | HUMBOLDT | 1.4123 | 70.1709 | 0% | 0 | 4 | 100% | 0% | 0 | 0.02067 | 65.3912 | 1.3517 | 0.95704
ALTO 1125935 | ALTO | ALTO 1125 | NORTH BAY | 3.0231 | 20.8124 | 24.9% | 7 | 7 | 94.09% | 0% | 0 | 0.038197 | 35.3263 | 1.3494 | 0.44635
PARADISE 110299226 | PARAD | PARADISE 1102 | NORTH VALLEY | 0.94174 | 38.0724 | 24.71% | 0 | 0 | 9.702% | 100% | 0 | 0.037935 | 35.3263 | 1.3401 | 1.423
MOUNTAIN QUARRIES 21016953 | MOUNT | MOUNTAIN QUARRIES 2101 | SIERRA | 5.7089 | 53.1337 | 100% | 0 | 0 | 100% | 0% | 0 | 0.037926 | 35.3263 | 1.3398 | 0.23469
SHINGLE SPRINGS 211051800 | SHING | SHINGLE SPRINGS 2110 | SIERRA | 9.4169 | 11.4226 | 65.37% | 2 | 2 | 96.5% | 41.26% | 0 | 0.049018 | 26.5534 | 1.3016 | 0.13822
HAMILTON BRANCH 11012046 | HAMIL | HAMILTON BRANCH 1101 | NORTH VALLEY | 9.1511 | 77.8147 | 51.04% | 2 | 2 | 99.57% | 0% | 0 | 0.036581 | 35.3263 | 1.2923 | 0.14122
WOODSIDE 1101 | WOODS | WOODSIDE 1101 | PENINSULA | 0.091557 | 33.2557 | 52.71% | 3 | 2 | 100% | 100% | 0 | 0.1142 | 11.2183 | 1.2812 | 13.9932
PAUL SWEET 2102 | PAUL | PAUL SWEET 2102 | CENTRAL COAST | 0.085046 | 10 | 0% | 3 | 0 | 100% | 100% | 0 | 0.063894 | 19.9979 | 1.2777 | 15.0242
ELK CREEK 11012008 | ELK C | ELK CREEK 1101 | NORTH VALLEY | 2.1575 | 78.9163 | 100% | 0 | 1 | 11.89% | 0% | 0 | 0.019472 | 65.3912 | 1.2733 | 0.59017
MADISON 210113372 | MADIS | MADISON 2101 | SACRAMENTO | 3.7782 | 89.8591 | 100% | 0 | 0 | 99.16% | 0% | 0 | 0.047853 | 26.5534 | 1.2706 | 0.33631
DEL MAR 210975802 | DEL M | DEL MAR 2109 | SIERRA | 0.35089 | 17.4936 | 85.01% | 0 | 1 | 84.46% | 0% | 0 | 0.026543 | 47.6367 | 1.2644 | 3.6035
MONTE RIO 1113477 | MONTE | MONTE RIO 1113 | SONOMA | 1.8187 | 34.6297 | 52.03% | 0 | 3 | 100% | 100% | 0 | 0.11271 | 11.2183 | 1.2644 | 0.69524
DESCHUTES 11049726 | DESCH | DESCHUTES 1104 | NORTH VALLEY | 14.9653 | 23.7872 | 88.61% | 1 | 3 | 89% | 0% | 0 | 0.03574 | 35.3263 | 1.2626 | 0.084367
WILLITS 1103538 | WILLI | WILLITS 1103 | HUMBOLDT | 6.4253 | 81.3489 | 100% | 3 | 1 | 100% | 27.62% | 0 | 0.083475 | 14.9507 | 1.248 | 0.19423
TAR FLAT 0401 | TAR F | TAR FLAT 0401 | YOSEMITE | 0.026649 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 19.9979 | 1.2311 | 46.1953
BELL 110750172 | BELL | BELL 1107 | SIERRA | 17.5892 | 13.0992 | 68.99% | 0 | 6 | 94.29% | 0% | 0 | 0.046234 | 26.5534 | 1.2277 | 0.069797
FLINT 1101750 | FLINT | FLINT 1101 | SIERRA | 3.8545 | 52.6304 | 83.81% | 0 | 0 | 41.31% | 0% | 0 | 0.018732 | 65.3912 | 1.2249 | 0.31778
RINCON 1103CB | RINCO | RINCON 1103 | SONOMA | 2.6796 | 27.7294 | 25.63% | 1 | 1 | 89.08% | 47% | 0 | 0.034549 | 35.3263 | 1.2205 | 0.45548
HAMILTON BRANCH 11013049 | HAMIL | HAMILTON BRANCH 1101 | NORTH VALLEY | 0.54973 | 41.4686 | 100% | 0 | 1 | 32.98% | 0% | 0 | 0.018634 | 65.3912 | 1.2185 | 2.2166
COARSEGOLD 2104CB | COARS | COARSEGOLD 2104 | YOSEMITE | 2.4475 | 54.0073 | 41.51% | 0 | 3 | 100% | 0% | 0 | 0.025403 | 47.6367 | 1.2101 | 0.49442
VALLEY VIEW 1103CB | VALLE | VALLEY VIEW 1103 | EAST BAY | 0.06028 | 65 | 0% | 0 | 0 | 0.9308% | 100% | 0 | 0.034198 | 35.3263 | 1.2081 | 20.0412
PUTAH CREEK 1102CB | PUTAH | PUTAH CREEK 1102 | SACRAMENTO | 4.8366 | 82.2611 | 100% | 0 | 0 | 37.85% | 0% | 0 | 0.025161 | 47.6367 | 1.1986 | 0.24782
PANORAMA 11019092 | PANOR | PANORAMA 1101 | NORTH VALLEY | 9.7913 | 10 | 99.08% | 0 | 8 | 48.48% | 0% | 0 | 0.033887 | 35.3263 | 1.1971 | 0.12226
OAKHURST 110348842 | OAKHU | OAKHURST 1103 | YOSEMITE | 2.3666 | 32.8421 | 100% | 0 | 9 | 82.85% | 0% | 0 | 0.033725 | 35.3263 | 1.1914 | 0.50341
SILVERADO 2104CB | SILVE | SILVERADO 2104 | NORTH BAY | 1.8059 | 23.2702 | 84.92% | 2 | 1 | 36.1% | 66.89% | 0 | 0.044573 | 26.5534 | 1.1836 | 0.65541
SANTA YNEZ 1104Y04 | SANTA | SANTA YNEZ 1104 | LOS PADRES | 15.3206 | 51.8152 | 75.91% | 0 | 12 | 68.36% | 0% | 0 | 0.033153 | 35.3263 | 1.1712 | 0.076444
BASALT 11065039 | BASAL | BASALT 1106 | NORTH BAY | 1.6775 | 85.8937 | 60.16% | 0 | 1 | 30.77% | 0% | 0 | 0.017795 | 65.3912 | 1.1636 | 0.69369
STAFFORD 1102524 | STAFF | STAFFORD 1102 | NORTH BAY | 3.4472 | 66.1749 | 51.31% | 1 | 2 | 26.91% | 0% | 0 | 0.024387 | 47.6367 | 1.1617 | 0.33701
CORRAL 110214026 | CORRA | CORRAL 1102 | STOCKTON | 10.1342 | 44.5079 | 47.19% | 1 | 3 | 100% | 0% | 0 | 0.03277 | 35.3263 | 1.1576 | 0.11423
MONTICELLO 1101720 | MONTI | MONTICELLO 1101 | NORTH BAY | 7.5573 | 64.5271 | 99.74% | 1 | 2 | 90.69% | 0% | 0 | 0.057594 | 19.9979 | 1.1518 | 0.1524
HICKS 2101XR250 | HICKS | HICKS 2101 | SAN JOSE | 7.0147 | 55.6197 | 44.17% | 2 | 7 | 53.71% | 28.46% | 0 | 0.042978 | 26.5534 | 1.1412 | 0.16269
STAFFORD 11021202 | STAFF | STAFFORD 1102 | NORTH BAY | 7.2996 | 85.3549 | 21.22% | 0 | 3 | 92.36% | 0% | 0 | 0.031995 | 35.3263 | 1.1303 | 0.15484
JESSUP 11023105 | JESSU | JESSUP 1102 | NORTH VALLEY | 5.7601 | 31.7951 | 100% | 0 | 2 | 92.48% | 0% | 0 | 0.031899 | 35.3263 | 1.1269 | 0.19563
LINCOLN 11042070 | LINCO | LINCOLN 1104 | SIERRA | 21.0429 | 49.8208 | 65.19% | 5 | 11 | 72.52% | 0% | 0 | 0.042249 | 26.5534 | 1.1219 | 0.053312
GARBERVILLE 11022124 | GARBE | GARBERVILLE 1102 | HUMBOLDT | 3.1243 | 97.624 | 0% | 0 | 1 | 100% | 0% | 0 | 0.023355 | 47.6367 | 1.1125 | 0.35609
PASO ROBLES 110359763 | PASO | PASO ROBLES 1103 | LOS PADRES | 2.8193 | 65.7222 | 66.01% | 0 | 0 | 100% | 0% | 0 | 0.031437 | 35.3263 | 1.1106 | 0.39391
MORAGA 110518396 | MORAG | MORAGA 1105 | DIABLO | 0.21093 | 45.5725 | 100% | 0 | 2 | 18.41% | 0% | 0 | 0.016943 | 65.3912 | 1.1079 | 5.2526
GANSNER 110199388 | GANSN | GANSNER 1101 | NORTH VALLEY | 2.0835 | 75.9591 | 98.87% | 1 | 0 | 93.65% | 0% | 0 | 0.041605 | 26.5534 | 1.1048 | 0.53024
PARADISE 1104CB | PARAD | PARADISE 1104 | NORTH VALLEY | 0.54287 | 10 | 13.72% | 1 | 1 | 13.43% | 100% | 0 | 0.030938 | 35.3263 | 1.0929 | 2.0132
MOLINO 1101891 | MOLIN | MOLINO 1101 | SONOMA | 3.0063 | 38.1554 | 45.65% | 1 | 1 | 95.38% | 41.51% | 0 | 0.054529 | 19.9979 | 1.0905 | 0.36273
FROGTOWN 1702 | FROGT | FROGTOWN 1702 | STOCKTON | 0.0028747 | 65 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041002 | 26.5534 | 1.0887 | 378.7335
SHINGLE SPRINGS 210935598 | SHING | SHINGLE SPRINGS 2109 | SIERRA | 10.9289 | 31.2867 | 70.52% | 1 | 5 | 100% | 42.6% | 0 | 0.072647 | 14.9507 | 1.0861 | 0.09938
MOLINO 110241392 | MOLIN | MOLINO 1102 | SONOMA | 3.7264 | 58.0945 | 65.77% | 1 | 0 | 25.48% | 0% | 0 | 0.016595 | 65.3912 | 1.0852 | 0.29122
PUEBLO 11042802 | PUEBL | PUEBLO 1104 | NORTH BAY | 9.7765 | 58.2394 | 48.14% | 0 | 5 | 89.72% | 0% | 0 | 0.072026 | 14.9507 | 1.0768 | 0.11015
OLETA 11011217 | OLETA | OLETA 1101 | STOCKTON | 14.427 | 60.7702 | 100% | 1 | 3 | 83.71% | 43.16% | 1 | 0.071429 | 14.9507 | 1.0679 | 0.074022
OAKHURST 1101CB | OAKHU | OAKHURST 1101 | YOSEMITE | 2.8974 | 35.5621 | 74.52% | 0 | 12 | 97.3% | 1.934% | 0 | 0.040153 | 26.5534 | 1.0662 | 0.36798
FOOTHILL 1101CB | FOOTH | FOOTHILL 1101 | LOS PADRES | 10.7012 | 70.0715 | 52.58% | 0 | 2 | 48.74% | 0% | 0 | 0.039956 | 26.5534 | 1.061 | 0.099145
PETALUMA C 1108618 | PETAL | PETALUMA C 1108 | SONOMA | 8.1405 | 67.3719 | 25.14% | 5 | 1 | 74.64% | 0% | 0 | 0.022157 | 47.6367 | 1.0555 | 0.12966
BRUNSWICK 1106 | BRUNS | BRUNSWICK 1106 | SIERRA | 0.037997 | 60 | 100% | 0 | 0 | 100% | 0% | 0 | 0.039678 | 26.5534 | 1.0536 | 27.7279
EAST QUINCY 1101CB | EAST | EAST QUINCY 1101 | NORTH VALLEY | 2.2646 | 54.1438 | 97.01% | 0 | 2 | 28.47% | 0% | 0 | 0.022042 | 47.6367 | 1.05 | 0.46366
LINCOLN 11045391 | LINCO | LINCOLN 1104 | SIERRA | 0.95086 | 68.8646 | 19.08% | 0 | 0 | 100% | 0% | 0 | 0.022019 | 47.6367 | 1.0489 | 1.1031
ELECTRA 1101L1697 | ELECT | ELECTRA 1101 | STOCKTON | 5.4545 | 12.0564 | 100% | 1 | 2 | 100% | 0% | 0 | 0.039464 | 26.5534 | 1.0479 | 0.19212
CAMP EVERS 2106834583 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 0.60497 | 39.087 | 36.91% | 0 | 0 | 100% | 69.26% | 0 | 0.069915 | 14.9507 | 1.0453 | 1.7278
PEORIA 170411232 | PEORI | PEORIA 1704 | YOSEMITE | 13.0063 | 19.4612 | 87.58% | 0 | 2 | 75.44% | 0% | 0 | 0.029217 | 35.3263 | 1.0321 | 0.079355
BRUNSWICK 11038918 | BRUNS | BRUNSWICK 1103 | SIERRA | 0.62743 | 83.4132 | 18.44% | 0 | 0 | 29.2% | 0% | 0 | 0.012022 | 85.4511 | 1.0273 | 1.6374
NAPA 1112 | NAPA | NAPA 1112 | NORTH BAY | 0.032215 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 35.3263 | 1.0072 | 31.2653
TEMPLETON 21132949 | TEMPL | TEMPLETON 2113 | LOS PADRES | 0.47714 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 35.3263 | 1.0072 | 2.1109
CLOVERDALE 110247214 | CLOVE | CLOVERDALE 1102 | SONOMA | 0.027332 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 35.3263 | 1.0072 | 36.8508
HOOPA 1101561116 | HOOPA | HOOPA 1101 | HUMBOLDT | 0.012979 | 85 | 0% | 0 | 0 | 100% | 0% | 0 | 0.021028 | 47.6367 | 1.0017 | 77.1754
CLARKSVILLE 210575884 | CLARK | CLARKSVILLE 2105 | SIERRA | 10.3522 | 19.5403 | 73.75% | 1 | 8 | 92.27% | 38.69% | 1 | 0.049935 | 19.9979 | 0.9986 | 0.096463
BRUNSWICK 110633050 | BRUNS | BRUNSWICK 1106 | SIERRA | 1.709 | 18.2327 | 78.9% | 2 | 0 | 44.77% | 0% | 0 | 0.015167 | 65.3912 | 0.99181 | 0.58036
SANTA YNEZ 110477098 | SANTA | SANTA YNEZ 1104 | LOS PADRES | 10.6194 | 59.0619 | 89.18% | 0 | 4 | 81.31% | 0% | 0 | 0.037257 | 26.5534 | 0.98931 | 0.09316
SPRING GAP 170286032 | SPRIN | SPRING GAP 1702 | YOSEMITE | 1.0066 | 66.0059 | 100% | 0 | 0 | 34.72% | 25.18% | 0 | 0.037122 | 26.5534 | 0.98571 | 0.97923
PETALUMA C 1108600 | PETAL | PETALUMA C 1108 | SONOMA | 4.0703 | 32.8182 | 38.32% | 2 | 6 | 47.11% | 0% | 0 | 0.020667 | 47.6367 | 0.98451 | 0.24187
OLETA 1101CB | OLETA | OLETA 1101 | STOCKTON | 3.1205 | 69.4789 | 19.21% | 0 | 0 | 92.33% | 0% | 0 | 0.02053 | 47.6367 | 0.97799 | 0.31341
GRASS VALLEY 1101CB | GRASS | GRASS VALLEY 1101 | SIERRA | 1.7504 | 55.588 | 24.73% | 1 | 1 | 65.41% | 2.088% | 0 | 0.027071 | 35.3263 | 0.9563 | 0.54635
CLOVERDALE 110254760 | CLOVE | CLOVERDALE 1102 | SONOMA | 0.13003 | 10 | 100% | 0 | 0 | 93.87% | 0% | 0 | 0.026858 | 35.3263 | 0.94881 | 7.2971
BOLINAS 11011232 | BOLIN | BOLINAS 1101 | NORTH BAY | 2.4469 | 73.1714 | 0% | 0 | 1 | 100% | 0% | 0 | 0.019829 | 47.6367 | 0.94457 | 0.38603
BELLEVUE 2103648 | BELLE | BELLEVUE 2103 | SONOMA | 2.2962 | 73.8161 | 100% | 0 | 2 | 14.14% | 0% | 0 | 0.019638 | 47.6367 | 0.93548 | 0.40741
PASO ROBLES 1104R56 | PASO | PASO ROBLES 1104 | LOS PADRES | 11.0427 | 56.2868 | 57.45% | 0 | 4 | 89.88% | 0% | 0 | 0.035115 | 26.5534 | 0.93242 | 0.084437
MORAGA 11058354 | MORAG | MORAGA 1105 | DIABLO | 0.25208 | 83.2522 | 100% | 0 | 0 | 8.053% | 20.65% | 0 | 0.026277 | 35.3263 | 0.92827 | 3.6824
GONZALES 110422418 | GONZA | GONZALES 1104 | CENTRAL COAST | 0.8424 | 88.5066 | 100% | 0 | 0 | 6.858% | 0% | 0 | 0.019362 | 47.6367 | 0.92235 | 1.0949
MARIPOSA 210190130 | MARIP | MARIPOSA 2101 | YOSEMITE | 0.091387 | 70 | 0% | 0 | 0 | 100% | 0% | 0 | 0.019016 | 47.6367 | 0.90585 | 9.9123
NARROWS 21052214 | NARRO | NARROWS 2105 | SIERRA | 0.0028409 | 70 | 0% | 0 | 0 | 100% | 0% | 0 | 0.019016 | 47.6367 | 0.90585 | 318.8577
PENRYN 11051342 | PENRY | PENRYN 1105 | SIERRA | 20.5672 | 12.393 | 56.11% | 3 | 12 | 53.03% | 0% | 0 | 0.025263 | 35.3263 | 0.89244 | 0.043392
FRUITLAND 1141CB | FRUIT | FRUITLAND 1141 | HUMBOLDT | 3.1926 | 94.3084 | 31.06% | 2 | 0 | 100% | 0% | 0 | 0.03355 | 26.5534 | 0.89086 | 0.27904
COTATI 1102282 | COTAT | COTATI 1102 | SONOMA | 4.4441 | 39.13 | 50.31% | 2 | 2 | 88.16% | 0% | 0 | 0.025185 | 35.3263 | 0.8897 | 0.2002
PENRYN 110550548 | PENRY | PENRYN 1105 | SIERRA | 4.6613 | 28.5134 | 63.43% | 0 | 1 | 38.43% | 0% | 0 | 0.013391 | 65.3912 | 0.87563 | 0.18785
UPPER LAKE 11016663 | UPPER | UPPER LAKE 1101 | HUMBOLDT | 2.3336 | 74.5453 | 100% | 0 | 0 | 100% | 0% | 0 | 0.043648 | 19.9979 | 0.87287 | 0.37404
MONTICELLO 110165454 | MONTI | MONTICELLO 1101 | NORTH BAY | 0.17975 | 75.7164 | 100% | 0 | 0 | 9.577% | 0% | 0 | 0.018251 | 47.6367 | 0.8694 | 4.8367
DESCHUTES 11019722 | DESCH | DESCHUTES 1101 | NORTH VALLEY | 2.8886 | 47.2823 | 92.43% | 0 | 2 | 60.75% | 0% | 0 | 0.024427 | 35.3263 | 0.8629 | 0.29873
PINECREST 04011818 | PINEC | PINECREST 0401 | YOSEMITE | 1.9342 | 47.9328 | 100% | 2 | 2 | 61.15% | 48.76% | 0 | 0.057579 | 14.9507 | 0.86084 | 0.44507
CORRAL 110336680 | CORRA | CORRAL 1103 | STOCKTON | 9.9701 | 19.0488 | 89.57% | 1 | 2 | 49.8% | 0% | 0 | 0.017976 | 47.6367 | 0.85633 | 0.08589
ANITA 1106CB | ANITA | ANITA 1106 | NORTH VALLEY | 0.115 | 85 | 100% | 0 | 0 | 0.3281% | 0% | 0 | 0.017735 | 47.6367 | 0.84484 | 7.3466
DUNLAP 11037991F | DUNLA | DUNLAP 1103 | FRESNO | 2.6521 | 79.9208 | 100% | 1 | 4 | 100% | 0% | 0 | 0.056283 | 14.9507 | 0.84147 | 0.31728
LINCOLN 110451756 | LINCO | LINCOLN 1104 | SIERRA | 15.5512 | 62.1844 | 61.25% | 0 | 6 | 27.35% | 0% | 0 | 0.031506 | 26.5534 | 0.8366 | 0.053796
PEORIA 170413494 | PEORI | PEORIA 1704 | YOSEMITE | 3.2575 | 18.8459 | 98.09% | 0 | 1 | 43.79% | 0% | 0 | 0.017531 | 47.6367 | 0.8351 | 0.25636
ATASCADERO 1103A18 | ATASC | ATASCADERO 1103 | LOS PADRES | 8.0258 | 28.4878 | 70.03% | 3 | 2 | 44.28% | 0% | 0 | 0.023538 | 35.3263 | 0.8315 | 0.1036
WOODSIDE 11012299 | WOODS | WOODSIDE 1101 | PENINSULA | 1.6209 | 33.6689 | 6.985% | 2 | 3 | 88.38% | 100% | 0 | 0.073666 | 11.2183 | 0.82641 | 0.50986
BELLEVUE 2103552 | BELLE | BELLEVUE 2103 | SONOMA | 9.102 | 59.5579 | 60.22% | 2 | 0 | 60.99% | 9.086% | 0 | 0.023335 | 35.3263 | 0.82433 | 0.090566
BIG BEND 11011704 | BIG B | BIG BEND 1101 | NORTH VALLEY | 2.999 | 64.818 | 100% | 0 | 0 | 100% | 0% | 0 | 0.040953 | 19.9979 | 0.81898 | 0.27308
PASO ROBLES 1103N02 | PASO | PASO ROBLES 1103 | LOS PADRES | 0.044146 | 10 | 36.23% | 0 | 0 | 100% | 0% | 0 | 0.017045 | 47.6367 | 0.81194 | 18.3922
JESSUP 110296554 | JESSU | JESSUP 1102 | NORTH VALLEY | 6.2214 | 43.1199 | 99.72% | 1 | 1 | 41.3% | 0% | 0 | 0.030545 | 26.5534 | 0.81106 | 0.13037
PEABODY 2113CB | PEABO | PEABODY 2113 | SACRAMENTO | 1.6686 | 58.5758 | 80.04% | 0 | 1 | 27.33% | 0% | 0 | 0.01682 | 47.6367 | 0.80125 | 0.48019
GABILAN 11013090 | GABIL | GABILAN 1101 | CENTRAL COAST | 1.8466 | 75 | 100% | 0 | 0 | 5.274% | 0% | 0 | 0.02262 | 35.3263 | 0.7991 | 0.43274
OLETA 110163500 | OLETA | OLETA 1101 | STOCKTON | 4.0006 | 22.1026 | 38.92% | 0 | 1 | 53.39% | 0% | 0 | 0.012178 | 65.3912 | 0.79634 | 0.19906
MOLINO 1101152 | MOLIN | MOLINO 1101 | SONOMA | 2.0022 | 35.0368 | 46.62% | 3 | 1 | 17.51% | 2.1% | 0 | 0.012176 | 65.3912 | 0.79623 | 0.39767
PASO ROBLES 1107CB | PASO | PASO ROBLES 1107 | LOS PADRES | 0.069192 | 75 | 100% | 0 | 0 | 0.6192% | 0% | 0 | 0.016629 | 47.6367 | 0.79217 | 11.4488
WOODACRE 110191900 | WOODA | WOODACRE 1101 | NORTH BAY | 7.6804 | 74.1444 | 47.27% | 4 | 8 | 55.53% | 8.222% | 1 | 0.029825 | 26.5534 | 0.79194 | 0.10311
CLEAR LAKE 110192870 | CLEAR | CLEAR LAKE 1101 | HUMBOLDT | 1.0943 | 58.4315 | 90.41% | 0 | 0 | 6.07% | 0% | 0 | 0.016559 | 47.6367 | 0.78881 | 0.72085
SANTA YNEZ 1101Y14 | SANTA | SANTA YNEZ 1101 | LOS PADRES | 4.5467 | 84.753 | 58.25% | 0 | 0 | 27.67% | 0% | 0 | 0.016519 | 47.6367 | 0.78692 | 0.17307
GEYSERVILLE 1102CB | GEYSE | GEYSERVILLE 1102 | SONOMA | 2.3641 | 61.3374 | 59.74% | 1 | 1 | 32.38% | 57.77% | 0 | 0.03873 | 19.9979 | 0.77452 | 0.32762
HIGHLANDS 110280660 | HIGHL | HIGHLANDS 1102 | HUMBOLDT | 5.365 | 78.0742 | 39.2% | 1 | 2 | 71.03% | 0% | 0 | 0.021888 | 35.3263 | 0.77324 | 0.14413
DUNBAR 11033135 | DUNBA | DUNBAR 1103 | SONOMA | 0.22216 | 10 | 100% | 0 | 0 | 29.43% | 100% | 0 | 0.068741 | 11.2183 | 0.77116 | 3.4711
SAUSALITO 110284278 | SAUSA | SAUSALITO 1102 | NORTH BAY | 1.3711 | 32.8864 | 5.777% | 0 | 2 | 90.29% | 0% | 0 | 0.021793 | 35.3263 | 0.76987 | 0.5615
EL CERRITO G 1112BR180 | EL CE | EL CERRITO G 1112 | EAST BAY | 1.3621 | 12.166 | 3.332% | 1 | 0 | 71.61% | 74.96% | 0 | 0.038138 | 19.9979 | 0.76268 | 0.55995
VACA DIXON 11059792 | VACA | VACA DIXON 1105 | SACRAMENTO | 2.2981 | 58.3899 | 100% | 0 | 0 | 7.932% | 0% | 0 | 0.015982 | 47.6367 | 0.76135 | 0.3313
SAN JUSTO 11014339 | SAN J | SAN JUSTO 1101 | CENTRAL COAST | 8.8141 | 41.5112 | 42.23% | 1 | 1 | 80.23% | 0% | 0 | 0.021456 | 35.3263 | 0.75797 | 0.085995
OAKHURST 1102CB | OAKHU | OAKHURST 1102 | YOSEMITE | 2.1514 | 10 | 95.52% | 0 | 10 | 44.96% | 59.79% | 0 | 0.050548 | 14.9507 | 0.75573 | 0.35127
JAMESON 11057652 | JAMES | JAMESON 1105 | SACRAMENTO | 15.7797 | 54.8992 | 80.61% | 0 | 3 | 36.24% | 0% | 0 | 0.021376 | 35.3263 | 0.75514 | 0.047855
FULTON 110410281 | FULTO | FULTON 1104 | SONOMA | 0.51664 | 22.43 | 74.95% | 0 | 1 | 49.63% | 0% | 0 | 0.015765 | 47.6367 | 0.75099 | 1.4536
CAMP EVERS 210612760 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 26.714 | 47.9231 | 63.13% | 29 | 6 | 100% | 100% | 0 | 0.75098 | 1 | 0.75098 | 0.028112
MOLINO 1104380 | MOLIN | MOLINO 1104 | SONOMA | 2.046 | 71.2548 | 46.79% | 0 | 0 | 7.207% | 0% | 0 | 0.011223 | 65.3912 | 0.73385 | 0.35868
VASCO 110211338 | VASCO | VASCO 1102 | MISSION | 3.3669 | 79.9716 | 100% | 0 | 1 | 17.52% | 0% | 0 | 0.020726 | 35.3263 | 0.73217 | 0.21746
ROB ROY 21045082 | ROB R | ROB ROY 2104 | CENTRAL COAST | 24.4071 | 49.5744 | 97.38% | 64 | 6 | 98.22% | 97.15% | 0 | 0.73013 | 1 | 0.73013 | 0.029915
MENLO 11028896 | MENLO | MENLO 1102 | PENINSULA | 0.53492 | 85.6249 | 0.9567% | 0 | 0 | 34.58% | 0% | 0 | 0.01116 | 65.3912 | 0.72979 | 1.3643
MARIPOSA 21019400 | MARIP | MARIPOSA 2101 | YOSEMITE | 62.7736 | 22.0188 | 81.32% | 9 | 129 | 100% | 40.79% | 1 | 0.72296 | 1 | 0.72296 | 0.011517
COTTONWOOD 110335470 | COTTO | COTTONWOOD 1103 | NORTH VALLEY | 18.2496 | 46.5174 | 67.33% | 0 | 6 | 73.33% | 0% | 0 | 0.03595 | 19.9979 | 0.71893 | 0.039394
BRIDGEVILLE 1102CB | BRIDG | BRIDGEVILLE 1102 | HUMBOLDT | 0.72529 | 72.3371 | 88.58% | 0 | 0 | 5.257% | 0% | 0 | 0.020259 | 35.3263 | 0.71568 | 0.98676
BUELLTON 1102CB | BUELL | BUELLTON 1102 | LOS PADRES | 4.428 | 55.4455 | 60.97% | 0 | 2 | 34.48% | 0% | 0 | 0.02009 | 35.3263 | 0.7097 | 0.16028
SALMON CREEK 1101196 | SALMO | SALMON CREEK 1101 | SONOMA | 5.0547 | 72.9126 | 4.053% | 3 | 0 | 69.63% | 0% | 0 | 0.020086 | 35.3263 | 0.70955 | 0.14038
STAFFORD 1102361952 | STAFF | STAFFORD 1102 | NORTH BAY | 1.3655 | 84.7322 | 98.54% | 0 | 1 | 100% | 0% | 0 | 0.04705 | 14.9507 | 0.70344 | 0.51513
PASO ROBLES 1103N58 | PASO | PASO ROBLES 1103 | LOS PADRES | 4.5123 | 48.6182 | 39.94% | 0 | 1 | 60.11% | 0% | 0 | 0.026481 | 26.5534 | 0.70315 | 0.15583
WISE 1102697216 | WISE | WISE 1102 | SIERRA | 13.1816 | 10.264 | 71.09% | 2 | 0 | 100% | 0% | 0 | 0.026461 | 26.5534 | 0.70264 | 0.053305
PUEBLO 2103678 | PUEBL | PUEBLO 2103 | NORTH BAY | 25.5805 | 63.7412 | 53.4% | 28 | 21 | 98.22% | 87.3% | 1 | 0.69166 | 1 | 0.69166 | 0.027038
PUTAH CREEK 110546162 | PUTAH | PUTAH CREEK 1105 | SACRAMENTO | 0.70535 | 84.6256 | 100% | 0 | 0 | 10.52% | 0% | 0 | 0.019556 | 35.3263 | 0.69085 | 0.97944
CAMP EVERS 210510996 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 0.7626 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 0.69059 | 0.90558
EL CERRITO G 1105R6998 | EL CE | EL CERRITO G 1105 | EAST BAY | 0.025405 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 0.69059 | 27.183
VINEYARD 21086952 | VINEY | VINEYARD 2108 | MISSION | 0.0028424 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 0.69059 | 242.9599
BIG BASIN 11015479 | BIG B | BIG BASIN 1101 | CENTRAL COAST | 0.17042 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 0.69059 | 4.0522
HALSEY 1101 | HALSE | HALSEY 1101 | SIERRA | 0.058617 | 10 | 52.88% | 0 | 0 | 100% | 0% | 0 | 0.019506 | 35.3263 | 0.68906 | 11.7553
TEMPLETON 2113A60 | TEMPL | TEMPLETON 2113 | LOS PADRES | 7.4093 | 57.7033 | 62.45% | 1 | 2 | 82.52% | 0.05121% | 0 | 0.025802 | 26.5534 | 0.68512 | 0.092468
CORTINA 1101302192 | CORTI | CORTINA 1101 | SACRAMENTO | 1.036 | 90 | 100% | 0 | 0 | 5.795% | 0% | 0 | 0.019354 | 35.3263 | 0.6837 | 0.65992
COTATI 1102681 | COTAT | COTATI 1102 | SONOMA | 3.8076 | 32.2436 | 43.14% | 1 | 3 | 100% | 0% | 0 | 0.025685 | 26.5534 | 0.68203 | 0.17912
WILDWOOD 1101CB | WILDW | WILDWOOD 1101 | NORTH VALLEY | 0.055929 | 81.1882 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045585 | 14.9507 | 0.68153 | 12.1857
GEYSERVILLE 1101482 | GEYSE | GEYSERVILLE 1101 | SONOMA | 0.45328 | 77.9574 | 100% | 0 | 0 | 13.09% | 0% | 0 | 0.019179 | 35.3263 | 0.67751 | 1.4947
STAFFORD 1102784704 | STAFF | STAFFORD 1102 | NORTH BAY | 0.02728 | 80 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045233 | 14.9507 | 0.67626 | 24.7895
WHEATLAND 110591170 | WHEAT | WHEATLAND 1105 | SIERRA | 9.9882 | 49.4424 | 100% | 0 | 0 | 18.55% | 0% | 0 | 0.019051 | 35.3263 | 0.67299 | 0.067379
SILVERADO 210437632 | SILVE | SILVERADO 2104 | NORTH BAY | 22.9342 | 51.0024 | 44.2% | 16 | 15 | 100% | 100% | 0 | 0.67223 | 1 | 0.67223 | 0.029311
SAN RAFAEL 11071415 | SAN R | SAN RAFAEL 1107 | NORTH BAY | 0.70882 | 10 | 28.8% | 0 | 0 | 59.59% | 100% | 0 | 0.059639 | 11.2183 | 0.66905 | 0.9439
ATASCADERO 1101A02 | ATASC | ATASCADERO 1101 | LOS PADRES | 11.1355 | 10.7743 | 66.74% | 2 | 2 | 100% | 7.928% | 0 | 0.044541 | 14.9507 | 0.66592 | 0.059802
JESSUP 110141356 | JESSU | JESSUP 1101 | NORTH VALLEY | 32.7394 | 40.1195 | 100% | 1 | 5 | 100% | 0% | 0 | 0.044331 | 14.9507 | 0.66278 | 0.020244
SONOMA 1104414 | SONOM | SONOMA 1104 | SONOMA | 0.58433 | 88.0945 | 100% | 0 | 0 | 3.279% | 0% | 0 | 0.018641 | 35.3263 | 0.65851 | 1.1269
SONOMA 110310257 | SONOM | SONOMA 1103 | SONOMA | 0.24108 | 10 | 100% | 0 | 0 | 12.38% | 100% | 0 | 0.058573 | 11.2183 | 0.65709 | 2.7256
FRUITLAND 11418746 | FRUIT | FRUITLAND 1141 | HUMBOLDT | 0.40721 | 85 | 7.434% | 0 | 0 | 50.57% | 0% | 0 | 0.013725 | 47.6367 | 0.65382 | 1.6056
PENRYN 110551676 | PENRY | PENRYN 1105 | SIERRA | 8.707 | 10 | 49.11% | 4 | 2 | 74.33% | 0% | 0 | 0.018392 | 35.3263 | 0.64971 | 0.074619
MILPITAS 1108XR122 | MILPI | MILPITAS 1108 | SAN JOSE | 0.28331 | 75 | 0% | 0 | 0 | 3.797% | 0% | 0 | 0.0075908 | 85.4511 | 0.64865 | 2.2895
COARSEGOLD 210410335 | COARS | COARSEGOLD 2104 | YOSEMITE | 5.8238 | 24.9128 | 98.65% | 0 | 10 | 100% | 0% | 0 | 0.043347 | 14.9507 | 0.64806 | 0.11128
DEL MONTE 21049500 | DEL M | DEL MONTE 2104 | CENTRAL COAST | 6.5395 | 26.3217 | 40.33% | 0 | 7 | 96.32% | 0% | 0 | 0.03234 | 19.9979 | 0.64673 | 0.098895
FREMONT 1104MR339 | FREMO | FREMONT 1104 | MISSION | 1.2378 | 84.498 | 6.265% | 0 | 0 | 17.79% | 0% | 0 | 0.0097922 | 65.3912 | 0.64033 | 0.51731
LAKEWOOD 2110W577R | LAKEW | LAKEWOOD 2110 | DIABLO | 0.42837 | 10 | 37.2% | 0 | 0 | 46.99% | 100% | 0 | 0.056527 | 11.2183 | 0.63414 | 1.4803
PETALUMA C 1109373772 | PETAL | PETALUMA C 1109 | SONOMA | 0.017822 | 70 | 100% | 0 | 0 | 100% | 0% | 0 | 0.042368 | 14.9507 | 0.63344 | 35.542
OLEMA 11011686 | OLEMA | OLEMA 1101 | NORTH BAY | 0.41347 | 93.229 | 0% | 4 | 1 | 8.166% | 0% | 0 | 0.0096532 | 65.3912 | 0.63124 | 1.5267
HIGGINS 11032194 | HIGGI | HIGGINS 1103 | SIERRA | 1.6953 | 10 | 78.66% | 3 | 1 | 63.02% | 0% | 0 | 0.017732 | 35.3263 | 0.62642 | 0.3695
RED BLUFF 11011334 | RED B | RED BLUFF 1101 | NORTH VALLEY | 1.7587 | 68.6115 | 100% | 0 | 0 | 11.05% | 0% | 0 | 0.017653 | 35.3263 | 0.62362 | 0.35459
COTATI 110387402 | COTAT | COTATI 1103 | SONOMA | 11.4171 | 74.8765 | 25.02% | 0 | 0 | 100% | 0% | 0 | 0.031179 | 19.9979 | 0.62351 | 0.054612
MARTELL 11016074 | MARTE | MARTELL 1101 | STOCKTON | 3.6867 | 10 | 89.99% | 1 | 1 | 100% | 0% | 0 | 0.030968 | 19.9979 | 0.6193 | 0.16798
SONOMA 1107294 | SONOM | SONOMA 1107 | SONOMA | 0.1154 | 80 | 100% | 0 | 0 | 1.248% | 0% | 0 | 0.017305 | 35.3263 | 0.61132 | 5.2974
PEORIA 170575274 | PEORI | PEORIA 1705 | YOSEMITE | 0.58699 | 10 | 100% | 0 | 0 | 18.06% | 0% | 0 | 0.012746 | 47.6367 | 0.60716 | 1.0344
LAURELES 11116617 | LAURE | LAURELES 1111 | CENTRAL COAST | 1.819 | 41.7117 | 100% | 1 | 0 | 100% | 0% | 0 | 0.040513 | 14.9507 | 0.6057 | 0.33299
CRESCENT MILLS 21012230 | CRESC | CRESCENT MILLS 2101 | NORTH VALLEY | 1.0766 | 89.5687 | 97.05% | 0 | 1 | 9.699% | 0% | 0 | 0.022777 | 26.5534 | 0.60481 | 0.56178
VALLEY VIEW 1103P160 | VALLE | VALLEY VIEW 1103 | EAST BAY | 0.28761 | 80 | 0% | 0 | 0 | 7.876% | 100% | 0 | 0.040365 | 14.9507 | 0.60349 | 2.0983
PEORIA 1705CB | PEORI | PEORIA 1705 | YOSEMITE | 7.2378 | 70.7531 | 12.14% | 0 | 3 | 100% | 0% | 0 | 0.022424 | 26.5534 | 0.59543 | 0.082267
STAFFORD 11011082 | STAFF | STAFFORD 1101 | NORTH BAY | 2.5227 | 43.9762 | 98.79% | 0 | 0 | 81.83% | 0% | 0 | 0.029652 | 19.9979 | 0.59297 | 0.23506
GREEN VALLEY 210111054 | GREEN | GREEN VALLEY 2101 | CENTRAL COAST | 24.5092 | 42.4361 | 63.08% | 38 | 3 | 95.34% | 97.52% | 1 | 0.59075 | 1 | 0.59075 | 0.024103
JESSUP 11021314 | JESSU | JESSUP 1102 | NORTH VALLEY | 5.6244 | 41.4572 | 97.17% | 0 | 1 | 39.97% | 0% | 0 | 0.022232 | 26.5534 | 0.59034 | 0.10496
LAKEWOOD 2224W544R | LAKEW | LAKEWOOD 2224 | DIABLO | 0.041988 | 10 | 100% | 0 | 0 | 0.7884% | 100% | 0 | 0.052488 | 11.2183 | 0.58883 | 14.0236
LAYTONVILLE 1101518 | LAYTO | LAYTONVILLE 1101 | HUMBOLDT | 1.7269 | 84.7584 | 100% | 0 | 1 | 7.655% | 0% | 0 | 0.02214 | 26.5534 | 0.58789 | 0.34042
INDIAN FLAT 11044440 | INDIA | INDIAN FLAT 1104 | YOSEMITE | 0.21912 | 58.2464 | 100% | 0 | 0 | 100% | 0% | 0 | 0.039224 | 14.9507 | 0.58642 | 2.6763
PETALUMA C 1109664732 | PETAL | PETALUMA C 1109 | SONOMA | 0.8938 | 76.1937 | 84.67% | 0 | 0 | 100% | 0% | 0 | 0.039085 | 14.9507 | 0.58434 | 0.65377
STAFFORD 11021943 | STAFF | STAFFORD 1102 | NORTH BAY | 1.2184 | 10 | 29.26% | 2 | 0 | 100% | 0% | 0 | 0.016531 | 35.3263 | 0.58398 | 0.47929
OREGON TRAIL 1102CB | OREGO | OREGON TRAIL 1102 | NORTH VALLEY | 9.1345 | 24.6852 | 60.79% | 2 | 5 | 97.5% | 0% | 0 | 0.028979 | 19.9979 | 0.57952 | 0.063442
HARTLEY 110158095 | HARTL | HARTLEY 1101 | HUMBOLDT | 0.15659 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 19.9979 | 0.57017 | 3.6412
MARIPOSA 2102 | MARIP | MARIPOSA 2102 | YOSEMITE | 0.0020154 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 19.9979 | 0.57017 | 282.9059
MONTICELLO 11011780 | MONTI | MONTICELLO 1101 | NORTH BAY | 0.07232 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 19.9979 | 0.57017 | 7.8841
FULTON 11024522 | FULTO | FULTON 1102 | SONOMA | 7.7633 | 52.5177 | 82.8% | 0 | 6 | 63.13% | 6.863% | 0 | 0.037536 | 14.9507 | 0.56119 | 0.072288
CLARKSVILLE 21096502 | CLARK | CLARKSVILLE 2109 | SIERRA | 2.6781 | 10 | 70.1% | 1 | 1 | 48.48% | 45.39% | 0 | 0.03731 | 14.9507 | 0.55781 | 0.20829
HORSESHOE 110450142 | HORSE | HORSESHOE 1104 | SIERRA | 0.99943 | 10 | 98.77% | 0 | 1 | 24.44% | 0% | 0 | 0.015652 | 35.3263 | 0.55294 | 0.55326
JARVIS 1101MR210 | JARVI | JARVIS 1101 | MISSION | 0.45193 | 56.1032 | 64.09% | 0 | 0 | 5.821% | 0% | 0 | 0.011506 | 47.6367 | 0.54812 | 1.2128
SALMON CREEK 1101 | SALMO | SALMON CREEK 1101 | SONOMA | 0.026066 | 45.8588 | 0% | 0 | 0 | 100% | 51.23% | 0 | 0.036485 | 14.9507 | 0.54548 | 20.9267
AUBERRY 110149122 | AUBER | AUBERRY 1101 | FRESNO | 3.8865 | 26.9324 | 92.34% | 0 | 3 | 100% | 0% | 0 | 0.036287 | 14.9507 | 0.54251 | 0.13959
SANTA YNEZ 1101CB | SANTA | SANTA YNEZ 1101 | LOS PADRES | 0.10675 | 60 | 100% | 0 | 1 | 0.6877% | 0% | 0 | 0.015356 | 35.3263 | 0.54248 | 5.0816
PENRYN 110351658 | PENRY | PENRYN 1103 | SIERRA | 7.9841 | 27.4219 | 66.1% | 1 | 2 | 91.67% | 0% | 0 | 0.027021 | 19.9979 | 0.54036 | 0.067679
RINCON 1102644 | RINCO | RINCON 1102 | SONOMA | 0.010111 | 60 | 100% | 0 | 1 | 0.1009% | 0% | 0 | 0.015268 | 35.3263 | 0.53935 | 53.3429
SHINGLE SPRINGS 21107742 | SHING | SHINGLE SPRINGS 2110 | SIERRA | 45.6192 | 28.4995 | 92.18% | 17 | 14 | 99.89% | 99.12% | 1 | 0.53387 | 1 | 0.53387 | 0.011703
MONTICELLO 110152910 | MONTI | MONTICELLO 1101 | NORTH BAY | 2.1786 | 24.2187 | 98.28% | 0 | 1 | 69.32% | 0% | 0 | 0.026641 | 19.9979 | 0.53277 | 0.24455
WILLITS 110391948 | WILLI | WILLITS 1103 | HUMBOLDT | 6.1069 | 55.6867 | 72.29% | 1 | 4 | 82.53% | 5.563% | 0 | 0.035629 | 14.9507 | 0.53267 | 0.087224
DESCHUTES 11043719 | DESCH | DESCHUTES 1104 | NORTH VALLEY | 11.6781 | 40.3272 | 100% | 0 | 2 | 67.24% | 0% | 0 | 0.026406 | 19.9979 | 0.52806 | 0.045218
HIGGINS 110432747 | HIGGI | HIGGINS 1104 | SIERRA | 1.0824 | 10 | 100% | 1 | 0 | 61.76% | 0% | 0 | 0.019868 | 26.5534 | 0.52758 | 0.4874
RESEARCH 210263274 | RESEA | RESEARCH 2102 | DIABLO | 0.57886 | 29.7225 | 25.19% | 0 | 1 | 5.113% | 100% | 0 | 0.035184 | 14.9507 | 0.52603 | 0.90872
OAKHURST 110310140 | OAKHU | OAKHURST 1103 | YOSEMITE | 16.859 | 26.9049 | 99.84% | 3 | 44 | 100% | 99.31% | 0 | 0.52553 | 1 | 0.52553 | 0.031172
CLEAR LAKE 1102904 | CLEAR | CLEAR LAKE 1102 | HUMBOLDT | 3.3866 | 10 | 44.47% | 0 | 0 | 94.14% | 0% | 0 | 0.01961 | 26.5534 | 0.52071 | 0.15376
HIGHLANDS 1102556 | HIGHL | HIGHLANDS 1102 | HUMBOLDT | 0.14444 | 10 | 100% | 0 | 0 | 1.909% | 0% | 0 | 0.010862 | 47.6367 | 0.51744 | 3.5823
BRUNSWICK 11064639 | BRUNS | BRUNSWICK 1106 | SIERRA | 3.2486 | 31.5408 | 99.46% | 0 | 1 | 100% | 1.568% | 1 | 0.034254 | 14.9507 | 0.51212 | 0.15764
WISE 11022234 | WISE | WISE 1102 | SIERRA | 15.1055 | 10 | 57.56% | 1 | 4 | 100% | 0% | 0 | 0.025382 | 19.9979 | 0.5076 | 0.033603
WYANDOTTE 110641650 | WYAND | WYANDOTTE 1106 | NORTH VALLEY | 1.9508 | 59.4004 | 100% | 0 | 0 | 12.07% | 0% | 0 | 0.01911 | 26.5534 | 0.50744 | 0.26011
PACIFICA 11026783 | PACIF | PACIFICA 1102 | PENINSULA | 1.5821 | 10 | 0% | 0 | 2 | 24.72% | 24.2% | 0 | 0.010579 | 47.6367 | 0.50395 | 0.31854
LOS GATOS 1106LA64 | LOS G | LOS GATOS 1106 | DE ANZA | 12.775 | 27.6673 | 77.8% | 17 | 7 | 100% | 100% | 1 | 0.50336 | 1 | 0.50336 | 0.039402
ATASCADERO 1103CB | ATASC | ATASCADERO 1103 | LOS PADRES | 7.2499 | 46.2369 | 39.81% | 0 | 1 | 74.99% | 13.24% | 0 | 0.025143 | 19.9979 | 0.50281 | 0.069355
PARADISE 11022024 | PARAD | PARADISE 1102 | NORTH VALLEY | 0.64392 | 10 | 28.85% | 0 | 1 | 39.71% | 100% | 0 | 0.044388 | 11.2183 | 0.49795 | 0.77332
PUTAH CREEK 110264044 | PUTAH | PUTAH CREEK 1102 | SACRAMENTO | 5.0213 | 75.9618 | 100% | 0 | 1 | 67.37% | 0% | 0 | 0.03282 | 14.9507 | 0.49069 | 0.097721
PUEBLO 2102698 | PUEBL | PUEBLO 2102 | NORTH BAY | 0.45229 | 80 | 34.45% | 0 | 0 | 2.749% | 0% | 0 | 0.0103 | 47.6367 | 0.49067 | 1.0849
BIG MEADOWS 2101439 | BIG M | BIG MEADOWS 2101 | NORTH VALLEY | 0.034644 | 85 | 100% | 0 | 0 | 3.714% | 0% | 0 | 0.018336 | 26.5534 | 0.48688 | 14.054
BRUNSWICK 1104CB | BRUNS | BRUNSWICK 1104 | SIERRA | 1.9366 | 10 | 53.96% | 0 | 0 | 63.09% | 0% | 0 | 0.013676 | 35.3263 | 0.48311 | 0.24946
CAMP EVERS 210311046 | CAMP | CAMP EVERS 2103 | CENTRAL COAST | 16.2531 | 44.8404 | 64.25% | 23 | 4 | 100% | 100% | 0 | 0.47552 | 1 | 0.47552 | 0.029257
GEYSERVILLE 1102274 | GEYSE | GEYSERVILLE 1102 | SONOMA | 4.0814 | 46.8618 | 69.12% | 1 | 0 | 22.13% | 0% | 0 | 0.013409 | 35.3263 | 0.47371 | 0.11606
JAMESON 11028842 | JAMES | JAMESON 1102 | SACRAMENTO | 0.46739 | 47.8727 | 32.07% | 0 | 0 | 8.162% | 0% | 0 | 0.0097873 | 47.6367 | 0.46623 | 0.99752
COLUMBIA HILL 1101CB | COLUM | COLUMBIA HILL 1101 | SIERRA | 39.662 | 48.9114 | 99.72% | 21 | 18 | 100% | 77.89% | 0 | 0.46568 | 1 | 0.46568 | 0.011741
JAMESON 110265516 | JAMES | JAMESON 1102 | SACRAMENTO | 7.9053 | 31.2245 | 60.83% | 1 | 6 | 69.63% | 0% | 0 | 0.023245 | 19.9979 | 0.46484 | 0.058801
MOLINO 1102344 | MOLIN | MOLINO 1102 | SONOMA | 1.1141 | 30.1016 | 80.53% | 0 | 2 | 18.52% | 0% | 0 | 0.013045 | 35.3263 | 0.46084 | 0.41366
ANDERSON 11012051 | ANDER | ANDERSON 1101 | NORTH VALLEY | 4.6467 | 13.4745 | 100% | 0 | 2 | 87.22% | 0% | 0 | 0.030553 | 14.9507 | 0.45678 | 0.098303
WEST POINT 11024788 | WEST | WEST POINT 1102 | STOCKTON | 70.3316 | 50.1461 | 97.21% | 9 | 19 | 100% | 60.3% | 0 | 0.45673 | 1 | 0.45673 | 0.0064939
ATASCADERO 1101 | ATASC | ATASCADERO 1101 | LOS PADRES | 0.011512 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 35.3263 | 0.44848 | 38.9564
BIG BASIN 110212992 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 14.2865 | 29.6471 | 74.67% | 30 | 1 | 100% | 100% | 1 | 0.44527 | 1 | 0.44527 | 0.031167
SAN JOAQUIN #2 1103CB | SAN J | SAN JOAQUIN #2 1103 | YOSEMITE | 67.7251 | 13.3684 | 94.77% | 0 | 65 | 100% | 13.79% | 0 | 0.44439 | 1 | 0.44439 | 0.0065617
DRUM 11011602 | DRUM | DRUM 1101 | SIERRA | 16.7313 | 80.5912 | 98.54% | 5 | 3 | 100% | 100% | 0 | 0.44264 | 1 | 0.44264 | 0.026456
LOS GATOS 1106LB44 | LOS G | LOS GATOS 1106 | DE ANZA | 19.5005 | 14.2956 | 68.84% | 20 | 1 | 100% | 100% | 0 | 0.44075 | 1 | 0.44075 | 0.022602
RED BLUFF 11051564 | RED B | RED BLUFF 1105 | NORTH VALLEY | 1.279 | 15.2296 | 100% | 0 | 0 | 12.04% | 0% | 0 | 0.012441 | 35.3263 | 0.43949 | 0.34362
MERCED FALLS 110222772 | MERCE | MERCED FALLS 1102 | YOSEMITE | 2.2922 | 12.637 | 100% | 0 | 0 | 100% | 0% | 0 | 0.029016 | 14.9507 | 0.4338 | 0.18926
SONOMA 11045661 | SONOM | SONOMA 1104 | SONOMA | 2.0903 | 69.2654 | 50.64% | 0 | 1 | 41.25% | 0% | 0 | 0.016332 | 26.5534 | 0.43366 | 0.20747
GANSNER 110137550 | GANSN | GANSNER 1101 | NORTH VALLEY | 0.5773 | 95.7309 | 100% | 0 | 0 | 12.36% | 0% | 0 | 0.021451 | 19.9979 | 0.42898 | 0.74308
EEL RIVER 11024814 | EEL R | EEL RIVER 1102 | HUMBOLDT | 27.3153 | 76.7361 | 63.94% | 7 | 10 | 97.55% | 0% | 0 | 0.42884 | 1 | 0.42884 | 0.015699
LAYTONVILLE 110264908 | LAYTO | LAYTONVILLE 1102 | HUMBOLDT | 3.5532 | 21.2702 | 61.98% | 6 | 8 | 55.85% | 0% | 0 | 0.021316 | 19.9979 | 0.42627 | 0.11997
CURTIS 1702 | CURTI | CURTIS 1702 | YOSEMITE | 0.020195 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 14.9507 | 0.42627 | 21.1079
INDIAN FLAT 1104 | INDIA | INDIAN FLAT 1104 | YOSEMITE | 0.0039208 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 14.9507 | 0.42627 | 108.7207
PENRYN 11052406 | PENRY | PENRYN 1105 | SIERRA | 3.0306 | 20.0804 | 58.87% | 1 | 0 | 24.58% | 0% | 0 | 0.012032 | 35.3263 | 0.42506 | 0.14026
SAN JOAQUIN #3 110110010 | SAN J | SAN JOAQUIN #3 1101 | YOSEMITE | 12.729 | 58.6534 | 88.53% | 3 | 19 | 100% | 90.16% | 0 | 0.42208 | 1 | 0.42208 | 0.033159
CORRAL 110275622 | CORRA | CORRAL 1102 | STOCKTON | 0.45257 | 14.2481 | 100% | 0 | 0 | 7.908% | 0% | 0 | 0.011863 | 35.3263 | 0.41909 | 0.92602
ELECTRA 11011238 | ELECT | ELECTRA 1101 | STOCKTON | 4.7136 | 30.1636 | 44.85% | 1 | 1 | 66.69% | 0% | 0 | 0.015593 | 26.5534 | 0.41404 | 0.08784
PEABODY 2108CB | PEABO | PEABODY 2108 | SACRAMENTO | 0.80945 | 40.6035 | 58.6% | 0 | 0 | 21.91% | 0% | 0 | 0.01162 | 35.3263 | 0.41049 | 0.50712
CLARKSVILLE 210551478 | CLARK | CLARKSVILLE 2105 | SIERRA | 0.050363 | 10 | 0% | 0 | 0 | 89.86% | 0% | 0 | 0.011483 | 35.3263 | 0.40565 | 8.0545
MARIPOSA 210237288 | MARIP | MARIPOSA 2102 | YOSEMITE | 85.1145 | 35.7142 | 99.54% | 6 | 74 | 100% | 7.812% | 0 | 0.40262 | 1 | 0.40262 | 0.0047304
STAFFORD 1102CB | STAFF | STAFFORD 1102 | NORTH BAY | 0.24035 | 10 | 0% | 0 | 0 | 45.06% | 0% | 0 | 0.0084029 | 47.6367 | 0.40029 | 1.6654
NORTH DUBLIN 21039473 | NORTH | NORTH DUBLIN 2103 | MISSION | 2.5582 | 55.4552 | 10.6% | 0 | 1 | 86.9% | 2.14% | 0 | 0.019896 | 19.9979 | 0.39788 | 0.15553
SUNOL 1101MR196 | SUNOL | SUNOL 1101 | MISSION | 2.4505 | 75.1937 | 26.76% | 0 | 1 | 18.84% | 0% | 0 | 0.011214 | 35.3263 | 0.39615 | 0.16166
MIDDLETOWN 1102414 | MIDDL | MIDDLETOWN 1102 | HUMBOLDT | 5.0571 | 54.0321 | 100% | 0 | 3 | 42.26% | 0% | 0 | 0.026354 | 14.9507 | 0.39402 | 0.077914
VACAVILLE 110941782 | VACAV | VACAVILLE 1109 | SACRAMENTO | 0.50066 | 79.3838 | 12.32% | 0 | 0 | 29.37% | 0% | 0 | 0.011149 | 35.3263 | 0.39386 | 0.78667
LOS GATOS 1106LB48 | LOS G | LOS GATOS 1106 | DE ANZA | 14.9866 | 67.642 | 90.94% | 14 | 1 | 100% | 100% | 1 | 0.39219 | 1 | 0.39219 | 0.026169
WOODSIDE 110147872 | WOODS | WOODSIDE 1101 | PENINSULA | 4.1743 | 60.8207 | 75.33% | 12 | 4 | 100% | 100% | 0 | 0.39089 | 1 | 0.39089 | 0.093641
CALISTOGA 1101734 | CALIS | CALISTOGA 1101 | NORTH BAY | 11.7939 | 55.3179 | 62.25% | 13 | 12 | 73.13% | 81.49% | 0 | 0.39061 | 1 | 0.39061 | 0.03312
CORRAL 110313474 | CORRA | CORRAL 1103 | STOCKTON | 3.1745 | 31.5086 | 69.33% | 0 | 0 | 44.02% | 0% | 0 | 0.019295 | 19.9979 | 0.38586 | 0.12155
UPPER LAKE 1101452 | UPPER | UPPER LAKE 1101 | HUMBOLDT | 1.5567 | 30.5905 | 77.99% | 1 | 7 | 7.943% | 0% | 0 | 0.019247 | 19.9979 | 0.3849 | 0.24725
PENRYN 110550550 | PENRY | PENRYN 1105 | SIERRA | 3.146 | 23.6879 | 96.13% | 0 | 1 | 22.41% | 0% | 0 | 0.014437 | 26.5534 | 0.38336 | 0.12185
TAMARACK 1101CB | TAMAR | TAMARACK 1101 | SIERRA | 16.4477 | 32.6722 | 67.46% | 23 | 13 | 91.62% | 0% | 0 | 0.38292 | 1 | 0.38292 | 0.023281
COTATI 1105328 | COTAT | COTATI 1105 | SONOMA | 0.42542 | 48.6287 | 27.07% | 0 | 1 | 3.098% | 0% | 0 | 0.0080325 | 47.6367 | 0.38264 | 0.89945
SAN JOAQUIN #3 1103CB | SAN J | SAN JOAQUIN #3 1103 | YOSEMITE | 28.2713 | 13.2744 | 82.63% | 4 | 63 | 100% | 35.67% | 0 | 0.37964 | 1 | 0.37964 | 0.013428
ROB ROY 21055090 | ROB R | ROB ROY 2105 | CENTRAL COAST | 21.1859 | 44.752 | 78.23% | 40 | 3 | 100% | 97.19% | 1 | 0.37924 | 1 | 0.37924 | 0.017901
MONTICELLO 1101666 | MONTI | MONTICELLO 1101 | NORTH BAY | 10.1625 | 67.7354 | 65.91% | 1 | 1 | 73.12% | 0% | 0 | 0.025333 | 14.9507 | 0.37875 | 0.037269
SHADY GLEN 110151696 | SHADY | SHADY GLEN 1101 | SIERRA | 17.0578 | 38.8695 | 93.61% | 4 | 7 | 82.3% | 0% | 0 | 0.033526 | 11.2183 | 0.37611 | 0.022049
LOS GATOS 110660116 | LOS G | LOS GATOS 1106 | DE ANZA | 12.3794 | 30.6322 | 46% | 28 | 5 | 100% | 100% | 0 | 0.37151 | 1 | 0.37151 | 0.03001
COTATI 1104CB | COTAT | COTATI 1104 | SONOMA | 2.3176 | 10.9581 | 56.63% | 1 | 1 | 30.19% | 0% | 0 | 0.010506 | 35.3263 | 0.37113 | 0.16014
VIEJO 2202CB | VIEJO | VIEJO 2202 | CENTRAL COAST | 2.1755 | 10 | 21.89% | 2 | 2 | 100% | 0% | 0 | 0.018504 | 19.9979 | 0.37005 | 0.1701
APPLE HILL 21029722 | APPLE | APPLE HILL 2102 | SIERRA | 38.3357 | 63.3481 | 100% | 10 | 4 | 100% | 82.49% | 1 | 0.36946 | 1 | 0.36946 | 0.0096375
HOPLAND 110180620 | HOPLA | HOPLAND 1101 | HUMBOLDT | 0.61898 | 10 | 82.97% | 0 | 0 | 11.01% | 0% | 0 | 0.010345 | 35.3263 | 0.36545 | 0.59041
COARSEGOLD 210410110 | COARS | COARSEGOLD 2104 | YOSEMITE | 49.586 | 26.2952 | 95.51% | 5 | 92 | 100% | 6.102% | 1 | 0.36439 | 1 | 0.36439 | 0.0073487
PUEBLO 21021326 | PUEBL | PUEBLO 2102 | NORTH BAY | 0.81465 | 66.7263 | 75.65% | 0 | 0 | 6.742% | 0% | 0 | 0.013708 | 26.5534 | 0.364 | 0.44681
BEN LOMOND 0401CB | BEN L | BEN LOMOND 0401 | CENTRAL COAST | 7.8222 | 35.8204 | 30.8% | 32 | 5 | 100% | 100% | 0 | 0.3629 | 1 | 0.3629 | 0.046394
SANTA ROSA A 1108626 | SANTA | SANTA ROSA A 1108 | SONOMA | 0.13621 | 75 | 0% | 0 | 0 | 3.381% | 0% | 0 | 0.0075596 | 47.6367 | 0.36011 | 2.6437
FITCH MOUNTAIN 1113406 | FITCH | FITCH MOUNTAIN 1113 | SONOMA | 1.4439 | 43.4794 | 97.1% | 1 | 1 | 15.43% | 0% | 0 | 0.01793 | 19.9979 | 0.35857 | 0.24833
PENRYN 11072706 | PENRY | PENRYN 1107 | SIERRA | 5.0792 | 12.8578 | 75.5% | 0 | 3 | 34.23% | 0% | 0 | 0.013291 | 26.5534 | 0.35292 | 0.069483
BOLINAS 110146152 | BOLIN | BOLINAS 1101 | NORTH BAY | 0.43174 | 69.1568 | 0% | 0 | 0 | 4.254% | 0% | 0 | 0.0073288 | 47.6367 | 0.34912 | 0.80864
BRIDGEVILLE 110255612 | BRIDG | BRIDGEVILLE 1102 | HUMBOLDT | 22.2453 | 91.4485 | 100% | 11 | 10 | 100% | 97.29% | 1 | 0.34757 | 1 | 0.34757 | 0.015624
DIAMOND SPRINGS 1105CB | DIAMO | DIAMOND SPRINGS 1105 | SIERRA | 1.4833 | 10 | 14.23% | 0 | 1 | 31.56% | 62.47% | 0 | 0.022985 | 14.9507 | 0.34364 | 0.23166
WEST POINT 11021305 | WEST | WEST POINT 1102 | STOCKTON | 11.4284 | 52.5642 | 100% | 4 | 5 | 100% | 100% | 1 | 0.34333 | 1 | 0.34333 | 0.030041
SILVERADO 210234959 | SILVE | SILVERADO 2102 | NORTH BAY | 24.7275 | 77.6516 | 100% | 5 | 11 | 91.78% | 69.47% | 1 | 0.34288 | 1 | 0.34288 | 0.013867
MESA 11016113 | MESA | MESA 1101 | LOS PADRES | 1.5145 | 57.2852 | 100% | 0 | 0 | 15.55% | 0% | 0 | 0.017101 | 19.9979 | 0.34199 | 0.22581
CAMP EVERS 210612518 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 15.9361 | 56.9453 | 43.9% | 39 | 3 | 100% | 100% | 0 | 0.3407 | 1 | 0.3407 | 0.021379
WEST POINT 11021341 | WEST | WEST POINT 1102 | STOCKTON | 10.0456 | 74.4483 | 100% | 1 | 5 | 100% | 100% | 0 | 0.33803 | 1 | 0.33803 | 0.03365
MIRABEL 1101228 | MIRAB | MIRABEL 1101 | SONOMA | 2.2414 | 32.2817 | 68.07% | 3 | 1 | 22.76% | 0% | 0 | 0.012705 | 26.5534 | 0.33736 | 0.15051
CLOVERDALE 1102672 | CLOVE | CLOVERDALE 1102 | SONOMA | 22.2941 | 69.8865 | 97.84% | 1 | 12 | 98.19% | 94.9% | 0 | 0.3373 | 1 | 0.3373 | 0.01513
WOODWARD 2108688294 | WOODW | WOODWARD 2108 | FRESNO | 0.015135 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 26.5534 | 0.3371 | 22.2725
SAN LUIS OBISPO 1108CB | SAN L | SAN LUIS OBISPO 1108 | LOS PADRES | 0.74619 | 53.8272 | 22.96% | 0 | 1 | 8.668% | 0% | 0 | 0.012642 | 26.5534 | 0.33568 | 0.44986
OAKHURST 11035480 | OAKHU | OAKHURST 1103 | YOSEMITE | 17.1484 | 38.4474 | 78.11% | 4 | 31 | 100% | 97.69% | 0 | 0.33517 | 1 | 0.33517 | 0.019545
WILLOW CREEK 11014904 | WILLO | WILLOW CREEK 1101 | HUMBOLDT | 18.7302 | 84.4323 | 100% | 25 | 5 | 100% | 99.66% | 0 | 0.33351 | 1 | 0.33351 | 0.017806
DUNBAR 1103CB | DUNBA | DUNBAR 1103 | SONOMA | 1.9287 | 52.9434 | 74.35% | 2 | 2 | 15.81% | 20.29% | 0 | 0.029588 | 11.2183 | 0.33193 | 0.1721
OILFIELDS 1103N40 | OILFI | OILFIELDS 1103 | CENTRAL COAST | 0.75328 | 20.1382 | 3.227% | 0 | 2 | 100% | 0% | 0 | 0.01659 | 19.9979 | 0.33177 | 0.44043
CLAYTON 22159765 | CLAYT | CLAYTON 2215 | DIABLO | 0.13991 | 10 | 100% | 0 | 0 | 14.93% | 0% | 0 | 0.012358 | 26.5534 | 0.32814 | 2.3453
CAMP EVERS 210312990 | CAMP | CAMP EVERS 2103 | CENTRAL COAST | 13.5574 | 33.1797 | 62.33% | 16 | 15 | 100% | 100% | 0 | 0.32668 | 1 | 0.32668 | 0.024096
OAKHURST 1103CB | OAKHU | OAKHURST 1103 | YOSEMITE | 29.7308 | 28.0867 | 78.34% | 5 | 58 | 96.61% | 65.89% | 1 | 0.32601 | 1 | 0.32601 | 0.010966
PLACERVILLE 210611132 | PLACE | PLACERVILLE 2106 | SIERRA | 43.1899 | 37.6905 | 78.66% | 11 | 29 | 100% | 66.95% | 0 | 0.3241 | 1 | 0.3241 | 0.0075042
BIG BASIN 110169550 | BIG B | BIG BASIN 1101 | CENTRAL COAST | 17.8925 | 32.0488 | 71.29% | 38 | 3 | 100% | 100% | 0 | 0.32055 | 1 | 0.32055 | 0.017915
OTTER 11017611 | OTTER | OTTER 1101 | CENTRAL COAST | 4.3976 | 73.491 | 75.26% | 4 | 3 | 100% | 100% | 1 | 0.3205 | 1 | 0.3205 | 0.07288
GOLDTREE 1105551904 | GOLDT | GOLDTREE 1105 | LOS PADRES | 0.022237 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 0.31985 | 14.3838
NARROWS 2105 | NARRO | NARROWS 2105 | SIERRA | 0.056021 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 0.31985 | 5.7095
ELECTRA 1101 | ELECT | ELECTRA 1101 | STOCKTON | 0.02594 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 0.31985 | 12.3305
MOUNTAIN QUARRIES 2101 | MOUNT | MOUNTAIN QUARRIES 2101 | SIERRA | 0.00097812 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 0.31985 | 327.006
WISE 1102 | WISE | WISE 1102 | SIERRA | 0.065469 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 0.31985 | 4.8855
FOOTHILL 1101549904 | FOOTH | FOOTHILL 1101 | LOS PADRES | 7.1079 | 49.5665 | 45.77% | 1 | 3 | 40.61% | 0% | 0 | 0.021381 | 14.9507 | 0.31966 | 0.044973
LLAGAS 2101XR264 | LLAGA | LLAGAS 2101 | SAN JOSE | 0.73019 | 64.4385 | 100% | 0 | 0 | 3.559% | 0% | 0 | 0.015944 | 19.9979 | 0.31885 | 0.43666
ROSSMOOR 1106L522R | ROSSM | ROSSMOOR 1106 | DIABLO | 1.0378 | 10 | 19.41% | 3 | 11 | 24.6% | 0% | 0 | 0.011991 | 26.5534 | 0.31841 | 0.30681
COARSEGOLD 210210040 | COARS | COARSEGOLD 2102 | YOSEMITE | 17.3327 | 15.2245 | 73.22% | 8 | 45 | 100% | 100% | 0 | 0.31716 | 1 | 0.31716 | 0.018299
HARTLEY 1102524 | HARTL | HARTLEY 1102 | HUMBOLDT | 1.3594 | 63.3777 | 100% | 0 | 1 | 30.18% | 0% | 0 | 0.020999 | 14.9507 | 0.31394 | 0.23095
FROGTOWN 170113412 | FROGT | FROGTOWN 1701 | STOCKTON | 38.8157 | 21.4669 | 89.5% | 2 | 31 | 100% | 20.91% | 0 | 0.31378 | 1 | 0.31378 | 0.0080839
RED BLUFF 110176020 | RED B | RED BLUFF 1101 | NORTH VALLEY | 8.959 | 16.3023 | 99.96% | 0 | 1 | 62.16% | 0% | 0 | 0.020958 | 14.9507 | 0.31334 | 0.034975
SAN MIGUEL 1105CB | SAN M | SAN MIGUEL 1105 | LOS PADRES | 0.96596 | 53.2217 | 100% | 0 | 0 | 9.014% | 0% | 0 | 0.015601 | 19.9979 | 0.312 | 0.32299
SHINGLE SPRINGS 2109CB | SHING | SHINGLE SPRINGS 2109 | SIERRA | 27.1022 | 21.2732 | 81.89% | 8 | 12 | 97.37% | 94.72% | 0 | 0.31197 | 1 | 0.31197 | 0.011511
SAN RAFAEL 1108516 | SAN R | SAN RAFAEL 1108 | NORTH BAY | 10.7797 | 42.2809 | 10.51% | 16 | 17 | 98.34% | 99.7% | 0 | 0.30979 | 1 | 0.30979 | 0.028739
PENRYN 110790970 | PENRY | PENRYN 1107 | SIERRA | 0.86048 | 10 | 69.3% | 0 | 0 | 20.31% | 0% | 0 | 0.011579 | 26.5534 | 0.30746 | 0.35731
SAN RAFAEL 11071166 | SAN R | SAN RAFAEL 1107 | NORTH BAY | 8.1619 | 27.5709 | 35.32% | 8 | 36 | 90.61% | 87.37% | 0 | 0.30659 | 1 | 0.30659 | 0.037563
AUBERRY 1101R319 | AUBER | AUBERRY 1101 | FRESNO | 21.0846 | 48.2226 | 98.48% | 8 | 8 | 100% | 93.05% | 1 | 0.30543 | 1 | 0.30543 | 0.014486
STANISLAUS 17011812 | STANI | STANISLAUS 1701 | YOSEMITE | 19.5078 | 54.4191 | 60.13% | 9 | 15 | 100% | 99.79% | 0 | 0.30454 | 1 | 0.30454 | 0.015611
DIAMOND SPRINGS 11052102 | DIAMO | DIAMOND SPRINGS 1105 | SIERRA | 37.6923 | 30.2782 | 83.99% | 5 | 15 | 95.84% | 86.14% | 1 | 0.30069 | 1 | 0.30069 | 0.0079776
TEMPLETON 2110901690 | TEMPL | TEMPLETON 2110 | LOS PADRES | 36.531 | 44.497 | 99.02% | 7 | 6 | 93.11% | 83.54% | 1 | 0.29843 | 1 | 0.29843 | 0.0081692
MONTE RIO 1113346 | MONTE | MONTE RIO 1113 | SONOMA | 10.1076 | 73.6223 | 44.96% | 12 | 4 | 100% | 100% | 0 | 0.29448 | 1 | 0.29448 | 0.029134
HALF MOON BAY 1103H82 | HALF | HALF MOON BAY 1103 | PENINSULA | 53.0127 | 52.0051 | 39.35% | 29 | 11 | 92.34% | 3.002% | 1 | 0.29233 | 1 | 0.29233 | 0.0055143
WOODSIDE 11043583 | WOODS | WOODSIDE 1104 | PENINSULA | 2.721 | 71.077 | 98.47% | 8 | 4 | 97.67% | 92.99% | 0 | 0.28756 | 1 | 0.28756 | 0.10568
NARROWS 21052216 | NARRO | NARROWS 2105 | SIERRA | 56.6943 | 15.1323 | 85.75% | 7 | 36 | 98.06% | 0% | 0 | 0.28652 | 1 | 0.28652 | 0.0050538
MARIPOSA 2101439030 | MARIP | MARIPOSA 2101 | YOSEMITE | 19.5499 | 36.6756 | 99.56% | 7 | 29 | 100% | 98.19% | 0 | 0.28602 | 1 | 0.28602 | 0.01463
LAKEVILLE 1102280 | LAKEV | LAKEVILLE 1102 | SONOMA | 2.0715 | 72.9124 | 15.25% | 0 | 2 | 23.31% | 0% | 0 | 0.010728 | 26.5534 | 0.28487 | 0.13752
SAN LUIS OBISPO 1104V46 | SAN L | SAN LUIS OBISPO 1104 | LOS PADRES | 18.1965 | 66.1378 | 91.34% | 1 | 13 | 87.31% | 73.08% | 1 | 0.28268 | 1 | 0.28268 | 0.015535
TEMPLETON 2111CB | TEMPL | TEMPLETON 2111 | LOS PADRES | 1.8275 | 10 | 27.26% | 0 | 0 | 16.54% | 0% | 0 | 0.0079104 | 35.3263 | 0.27944 | 0.15291
SPRING GAP 1702693441 | SPRIN | SPRING GAP 1702 | YOSEMITE | 4.1995 | 35.8935 | 98.37% | 5 | 2 | 100% | 100% | 0 | 0.27702 | 1 | 0.27702 | 0.065964
CLARKSVILLE 210619642 | CLARK | CLARKSVILLE 2106 | SIERRA | 0.81481 | 10 | 0% | 0 | 0 | 51.08% | 0% | 0 | 0.007814 | 35.3263 | 0.27604 | 0.33878
CABRILLO 1103CB | CABRI | CABRILLO 1103 | LOS PADRES | 0.14089 | 80 | 0% | 0 | 0 | 3.139% | 0% | 0 | 0.0078018 | 35.3263 | 0.27561 | 1.9562
WYANDOTTE 110932586 | WYAND | WYANDOTTE 1109 | NORTH VALLEY | 1.4371 | 18.342 | 79.5% | 0 | 0 | 94.84% | 0% | 0 | 0.024309 | 11.2183 | 0.27271 | 0.18977
LLAGAS 2107XR178 | LLAGA | LLAGAS 2107 | SAN JOSE | 0.65323 | 27.1294 | 68.86% | 0 | 0 | 9.688% | 0% | 0 | 0.010217 | 26.5534 | 0.2713 | 0.41532
COTTONWOOD 11011510 | COTTO | COTTONWOOD 1101 | NORTH VALLEY | 0.7279 | 10 | 33.06% | 0 | 0 | 21.95% | 0% | 0 | 0.0076675 | 35.3263 | 0.27086 | 0.37212
JARVIS 1108MR576 | JARVI | JARVIS 1108 | MISSION | 1.3706 | 10 | 32.22% | 0 | 0 | 22.29% | 0% | 0 | 0.0076408 | 35.3263 | 0.26992 | 0.19694
CURTIS 17039180 | CURTI | CURTIS 1703 | YOSEMITE | 56.1725 | 23.1853 | 91.13% | 4 | 41 | 100% | 0% | 0 | 0.26987 | 1 | 0.26987 | 0.0048043
PENRYN 1103660 | PENRY | PENRYN 1103 | SIERRA | 10.4724 | 10.4096 | 69.5% | 2 | 4 | 53.75% | 0% | 0 | 0.018041 | 14.9507 | 0.26972 | 0.025755
COARSEGOLD 210410400 | COARS | COARSEGOLD 2104 | YOSEMITE | 42.0443 | 18.5406 | 94.25% | 4 | 95 | 94% | 0% | 0 | 0.26956 | 1 | 0.26956 | 0.0064114
MIWUK 170153038 | MIWUK | MIWUK 1701 | YOSEMITE | 6.638 | 67.6188 | 100% | 3 | 9 | 100% | 100% | 0 | 0.26716 | 1 | 0.26716 | 0.040247
MIDDLETOWN 1102CB | MIDDL | MIDDLETOWN 1102 | HUMBOLDT | 4.3813 | 57.1831 | 32.04% | 0 | 1 | 66.6% | 5.967% | 1 | 0.023754 | 11.2183 | 0.26649 | 0.060823
COTATI 1102260 | COTAT | COTATI 1102 | SONOMA | 1.6248 | 13.946 | 2.286% | 0 | 1 | 27.41% | 0% | 0 | 0.0075335 | 35.3263 | 0.26613 | 0.16379
ALTO 1124430 | ALTO | ALTO 1124 | NORTH BAY | 7.2931 | 30.5125 | 12.77% | 14 | 16 | 100% | 100% | 0 | 0.26455 | 1 | 0.26455 | 0.036274
FOOTHILL 1102V06 | FOOTH | FOOTHILL 1102 | LOS PADRES | 1.4055 | 48.154 | 31.22% | 0 | 1 | 21.48% | 0% | 0 | 0.0099416 | 26.5534 | 0.26398 | 0.18782
DEL MONTE 21042760 | DEL M | DEL MONTE 2104 | CENTRAL COAST | 2.7139 | 31.1425 | 17.74% | 0 | 3 | 100% | 0% | 0 | 0.023371 | 11.2183 | 0.26219 | 0.09661
KESWICK 11019712 | KESWI | KESWICK 1101 | NORTH VALLEY | 18.8507 | 17.0815 | 97.11% | 2 | 13 | 100% | 100% | 0 | 0.26099 | 1 | 0.26099 | 0.013845
CAMP EVERS 210510728 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 10.465 | 15.413 | 38.24% | 13 | 4 | 100% | 100% | 0 | 0.2598 | 1 | 0.2598 | 0.024826
CALISTOGA 1101890 | CALIS | CALISTOGA 1101 | NORTH BAY | 22.5646 | 51.954 | 60.75% | 7 | 3 | 89.13% | 61.5% | 0 | 0.25974 | 1 | 0.25974 | 0.011511
COARSEGOLD 210210050 | COARS | COARSEGOLD 2102 | YOSEMITE | 7.18 | 18.0295 | 97.64% | 2 | 12 | 100% | 100% | 0 | 0.25905 | 1 | 0.25905 | 0.036079
MONTE RIO 11133970 | MONTE | MONTE RIO 1113 | SONOMA | 7.3428 | 62.8724 | 47.81% | 13 | 10 | 100% | 100% | 0 | 0.25889 | 1 | 0.25889 | 0.035258
PLACERVILLE 21069712 | PLACE | PLACERVILLE 2106 | SIERRA | 24.7737 | 54.0303 | 80.14% | 10 | 4 | 100% | 89.29% | 1 | 0.25885 | 1 | 0.25885 | 0.010448
SARATOGA 1107413816 | SARAT | SARATOGA 1107 | DE ANZA | 11.1604 | 62.8545 | 90.16% | 13 | 7 | 100% | 89.94% | 0 | 0.25675 | 1 | 0.25675 | 0.023005
CLARK ROAD 110290548 | CLARK | CLARK ROAD 1102 | NORTH VALLEY | 18.3619 | 41.0434 | 98.73% | 0 | 11 | 100% | 100% | 0 | 0.25625 | 1 | 0.25625 | 0.013956
OAKHURST 110377384 | OAKHU | OAKHURST 1103 | YOSEMITE | 4.7334 | 12.9583 | 82.83% | 5 | 23 | 100% | 100% | 0 | 0.25524 | 1 | 0.25524 | 0.053922
MIRABEL 110238514 | MIRAB | MIRABEL 1102 | SONOMA | 10.5875 | 61.5593 | 46.21% | 16 | 8 | 100% | 100% | 0 | 0.25422 | 1 | 0.25422 | 0.024012
CAMP EVERS 21065302 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 5.9826 | 48.1403 | 77.43% | 11 | 0 | 100% | 95.97% | 0 | 0.25415 | 1 | 0.25415 | 0.042481
NARROWS 21021252 | NARRO | NARROWS 2102 | SIERRA | 0.0028409 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 19.9979 | 0.25388 | 89.3655
MARIPOSA 21021960 | MARIP | MARIPOSA 2102 | YOSEMITE | 24.6612 | 47.7521 | 99.87% | 3 | 23 | 100% | 69.1% | 1 | 0.25188 | 1 | 0.25188 | 0.010214
PLACERVILLE 21066512 | PLACE | PLACERVILLE 2106 | SIERRA | 20.9994 | 19.5513 | 83.24% | 2 | 9 | 100% | 100% | 0 | 0.25186 | 1 | 0.25186 | 0.011994
SAN JOAQUIN #3 11035100 | SAN J | SAN JOAQUIN #3 1103 | YOSEMITE | 26.246 | 20.2846 | 88.04% | 8 | 29 | 100% | 82.8% | 0 | 0.25116 | 1 | 0.25116 | 0.0095693
ARBUCKLE 110447282 | ARBUC | ARBUCKLE 1104 | SACRAMENTO | 2.0417 | 83.3119 | 73.53% | 0 | 0 | 17.21% | 0% | 0 | 0.016706 | 14.9507 | 0.24977 | 0.12234
CALISTOGA 110135588 | CALIS | CALISTOGA 1101 | NORTH BAY | 3.0755 | 87.0174 | 100% | 0 | 0 | 100% | 100% | 0 | 0.24881 | 1 | 0.24881 | 0.080901
HALF MOON BAY 11038898 | HALF | HALF MOON BAY 1103 | PENINSULA | 0.64191 | 18.722 | 22.54% | 0 | 1 | 100% | 0% | 0 | 0.016511 | 14.9507 | 0.24685 | 0.38456
SAN BENITO 210136912 | SAN B | SAN BENITO 2101 | CENTRAL COAST | 2.942 | 68.099 | 74.6% | 0 | 1 | 23.25% | 0% | 0 | 0.016483 | 14.9507 | 0.24643 | 0.083763
JARVIS 1110CB | JARVI | JARVIS 1110 | MISSION | 0.094443 | 65 | 0% | 0 | 0 | 1.965% | 0% | 0 | 0.0069643 | 35.3263 | 0.24602 | 2.605
ALTO 11243745 | ALTO | ALTO 1124 | NORTH BAY | 4.5809 | 48.7454 | 24.8% | 4 | 26 | 100% | 100% | 0 | 0.24571 | 1 | 0.24571 | 0.053638
MOLINO 110251788 | MOLIN | MOLINO 1102 | SONOMA | 5.6218 | 26.7859 | 66.33% | 10 | 1 | 38.47% | 5.373% | 0 | 0.021877 | 11.2183 | 0.24543 | 0.043657
BUCKS CREEK 1103CB | BUCKS | BUCKS CREEK 1103 | NORTH VALLEY | 2.2994 | 96.1203 | 100% | 2 | 1 | 100% | 100% | 0 | 0.24438 | 1 | 0.24438 | 0.10628
MORGAN HILL 2111XR398 | MORGA | MORGAN HILL 2111 | SAN JOSE | 36.8919 | 62.4019 | 77.2% | 15 | 15 | 93.25% | 35.33% | 1 | 0.2433 | 1 | 0.2433 | 0.0065948
PURISIMA 110154728 | PURIS | PURISIMA 1101 | LOS PADRES | 0.37057 | 45.459 | 76.61% | 0 | 0 | 8.245% | 0% | 0 | 0.012146 | 19.9979 | 0.2429 | 0.65548
GUALALA 11121294 | GUALA | GUALALA 1112 | HUMBOLDT | 19.9398 | 39.726 | 11.78% | 10 | 62 | 100% | 0% | 0 | 0.24042 | 1 | 0.24042 | 0.012057
ZACA 1102Y54 | ZACA | ZACA 1102 | LOS PADRES | 34.3968 | 50.4695 | 82.24% | 0 | 23 | 99.37% | 51.02% | 1 | 0.23948 | 1 | 0.23948 | 0.0069623
PENRYN 1103CB | PENRY | PENRYN 1103 | SIERRA | 2.2673 | 10 | 57.81% | 1 | 1 | 71.12% | 0% | 0 | 0.015799 | 14.9507 | 0.23621 | 0.10418
CLAYTON 221296224 | CLAYT | CLAYTON 2212 | DIABLO | 6.0784 | 53.8659 | 38.47% | 4 | 5 | 100% | 98.09% | 0 | 0.23534 | 1 | 0.23534 | 0.038717
COARSEGOLD 21025380 | COARS | COARSEGOLD 2102 | YOSEMITE | 14.1287 | 13.3143 | 99.57% | 3 | 25 | 100% | 100% | 0 | 0.23471 | 1 | 0.23471 | 0.016612
OAKLAND K 1102CR014 | OAKLA | OAKLAND K 1102 | EAST BAY | 10.5526 | 27.0866 | 16.24% | 14 | 8 | 100% | 100% | 1 | 0.23413 | 1 | 0.23413 | 0.022187
VALLEY VIEW 1106P166 | VALLE | VALLEY VIEW 1106 | EAST BAY | 3.4384 | 77.0381 | 8.804% | 5 | 1 | 75.32% | 0% | 0 | 0.020855 | 11.2183 | 0.23396 | 0.068044
CALISTOGA 1102634 | CALIS | CALISTOGA 1102 | NORTH BAY | 11.7799 | 49.1315 | 63.48% | 13 | 6 | 61.37% | 93.22% | 1 | 0.23196 | 1 | 0.23196 | 0.019692
SAN LUIS OBISPO 1101CB | SAN L | SAN LUIS OBISPO 1101 | LOS PADRES | 6.447 | 57.4459 | 18.1% | 1 | 2 | 37.74% | 0% | 0 | 0.01156 | 19.9979 | 0.23118 | 0.035859
SAN LUIS OBISPO 1107V60 | SAN L | SAN LUIS OBISPO 1107 | LOS PADRES | 16.0455 | 59.2942 | 63.57% | 4 | 4 | 100% | 91.12% | 0 | 0.23106 | 1 | 0.23106 | 0.0144
ALTO 11251226 | ALTO | ALTO 1125 | NORTH BAY | 7.7199 | 13.4122 | 30.57% | 9 | 29 | 98.37% | 100% | 0 | 0.23095 | 1 | 0.23095 | 0.029916
WILLITS 1103964 | WILLI | WILLITS 1103 | HUMBOLDT | 2.7651 | 34.3373 | 95.61% | 0 | 1 | 51.42% | 0% | 0 | 0.02055 | 11.2183 | 0.23053 | 0.083372
HARTLEY 1101658 | HARTL | HARTLEY 1101 | HUMBOLDT | 2.7971 | 52.1185 | 100% | 0 | 1 | 20.57% | 0% | 0 | 0.020197 | 11.2183 | 0.22658 | 0.081005
BIG BEND 1102CB | BIG B | BIG BEND 1102 | NORTH VALLEY | 17.1238 | 77.0813 | 99.95% | 1 | 3 | 100% | 100% | 0 | 0.22606 | 1 | 0.22606 | 0.013201
SHINGLE SPRINGS 210913322 | SHING | SHINGLE SPRINGS 2109 | SIERRA | 41.4342 | 33.754 | 99.99% | 7 | 13 | 100% | 26.15% | 1 | 0.22465 | 1 | 0.22465 | 0.0054218
SAN RAMON 2102CB | SAN R | SAN RAMON 2102 | MISSION | 1.535 | 41.2314 | 0% | 0 | 0 | 65.73% | 0% | 0 | 0.011168 | 19.9979 | 0.22333 | 0.14549
ALTO 1124432 | ALTO | ALTO 1124 | NORTH BAY | 7.823 | 44.0512 | 43.81% | 6 | 19 | 100% | 100% | 0 | 0.22255 | 1 | 0.22255 | 0.028449
LLAGAS 2101XR244 | LLAGA | LLAGAS 2101 | SAN JOSE | 0.29573 | 10 | 100% | 0 | 1 | 2.088% | 0% | 0 | 0.01111 | 19.9979 | 0.22217 | 0.75127
VIEJO 220235388 | VIEJO | VIEJO 2202 | CENTRAL COAST | 0.45244 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.014786 | 14.9507 | 0.22106 | 0.48859
KESWICK 110148480 | KESWI | KESWICK 1101 | NORTH VALLEY | 10.8916 | 45.1063 | 95.79% | 1 | 7 | 100% | 100% | 0 | 0.2199 | 1 | 0.2199 | 0.020189
SANTA YNEZ 1104Y30 | SANTA | SANTA YNEZ 1104 | LOS PADRES | 0.89443 | 34.2503 | 70.68% | 0 | 2 | 6.535% | 0% | 0 | 0.010995 | 19.9979 | 0.21987 | 0.24582
SANTA MARIA 1108M18 | SANTA | SANTA MARIA 1108 | LOS PADRES | 14.6945 | 77.5423 | 92.38% | 1 | 8 | 82.48% | 56.56% | 1 | 0.21976 | 1 | 0.21976 | 0.014955
ALTO 1125902 | ALTO | ALTO 1125 | NORTH BAY | 12.0705 | 57.5388 | 0.5919% | 9 | 8 | 100% | 85.9% | 1 | 0.21954 | 1 | 0.21954 | 0.018188
FROGTOWN 170274648 | FROGT | FROGTOWN 1702 | STOCKTON | 0.21722 | 10 | 30.03% | 0 | 0 | 4.115% | 0% | 0 | 0.0081651 | 26.5534 | 0.21681 | 0.99814
FULTON 11024994 | FULTO | FULTON 1102 | SONOMA | 1.7055 | 60.2868 | 44.56% | 0 | 1 | 40.25% | 0% | 0 | 0.014488 | 14.9507 | 0.21661 | 0.127
OCEANO 110391240 | OCEAN | OCEANO 1103 | LOS PADRES | 0.011387 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.014483 | 14.9507 | 0.21654 | 19.0154
GREENBRAE 11021254 | GREEN | GREENBRAE 1102 | NORTH BAY | 7.0201 | 10 | 37.52% | 8 | 16 | 74.16% | 100% | 0 | 0.21468 | 1 | 0.21468 | 0.030581
SISQUOC 1103M14 | SISQU | SISQUOC 1103 | LOS PADRES | 21.2959 | 68.8259 | 69.24% | 0 | 10 | 65.02% | 94.4% | 0 | 0.21174 | 1 | 0.21174 | 0.0099429
MIDDLETOWN 1102878 | MIDDL | MIDDLETOWN 1102 | HUMBOLDT | 0.98449 | 64.5076 | 97.38% | 0 | 3 | 16.45% | 0% | 0 | 0.018862 | 11.2183 | 0.2116 | 0.21493
SAN RAFAEL 1108322 | SAN R | SAN RAFAEL 1108 | NORTH BAY | 7.1088 | 25.427 | 14.01% | 10 | 9 | 95.89% | 89.81% | 0 | 0.21074 | 1 | 0.21074 | 0.029646
OTTER 1101CB | OTTER | OTTER 1101 | CENTRAL COAST | 6.5139 | 35.3423 | 0.6325% | 8 | 1 | 96.47% | 87.12% | 1 | 0.20943 | 1 | 0.20943 | 0.032151
SNEATH LANE 110715341 | SNEAT | SNEATH LANE 1107 | PENINSULA | 0.71839 | 10 | 29.45% | 0 | 0 | 55.75% | 0% | 0 | 0.010414 | 19.9979 | 0.20826 | 0.2899
MARIPOSA 210237282 | MARIP | MARIPOSA 2102 | YOSEMITE | 48.8925 | 28.6255 | 92.59% | 4 | 51 | 82.09% | 39.78% | 0 | 0.20818 | 1 | 0.20818 | 0.0042579
CAMP EVERS 210511004 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 4.2954 | 13.9666 | 78.63% | 3 | 0 | 100% | 100% | 0 | 0.2074 | 1 | 0.2074 | 0.048285
ROB ROY 2104CB | ROB R | ROB ROY 2104 | CENTRAL COAST | 14.3247 | 30.9167 | 85.32% | 22 | 10 | 100% | 61.11% | 0 | 0.20721 | 1 | 0.20721 | 0.014466
CAYETANO 21099504 | CAYET | CAYETANO 2109 | MISSION | 14.1558 | 53.8418 | 95.53% | 0 | 2 | 97.78% | 75.62% | 1 | 0.20657 | 1 | 0.20657 | 0.014592
COARSEGOLD 210210330 | COARS | COARSEGOLD 2102 | YOSEMITE | 9.5583 | 29.5023 | 99.75% | 4 | 3 | 100% | 94.16% | 0 | 0.20649 | 1 | 0.20649 | 0.021603
SANTA MARIA 1108M80 | SANTA | SANTA MARIA 1108 | LOS PADRES | 58.3414 | 79.2858 | 99.51% | 1 | 8 | 100% | 61.18% | 1 | 0.20649 | 1 | 0.20649 | 0.0035393
CLOVERDALE 1102 | CLOVE | CLOVERDALE 1102 | SONOMA | 0.015567 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 1 | 0.20559 | 13.2068
SAN RAMON 2107MR284 | SAN R | SAN RAMON 2107 | MISSION | 13.084 | 58.0067 | 71.73% | 0 | 4 | 87.08% | 97.71% | 0 | 0.20548 | 1 | 0.20548 | 0.015705
LLAGAS 2101XR584 | LLAGA | LLAGAS 2101 | SAN JOSE | 1.1341 | 38.093 | 49.38% | 0 | 3 | 12.45% | 0% | 0 | 0.010267 | 19.9979 | 0.20532 | 0.18104
BIG BASIN 11025066 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 14.538 | 30.1342 | 55.77% | 35 | 1 | 100% | 92.59% | 1 | 0.20391 | 1 | 0.20391 | 0.014026
CORRAL 1103CB | CORRA | CORRAL 1103 | STOCKTON | 5.566 | 15.4342 | 82.99% | 0 | 1 | 19.4% | 0% | 0 | 0.013588 | 14.9507 | 0.20315 | 0.036498
ROB ROY 210410298 | ROB R | ROB ROY 2104 | CENTRAL COAST | 11.1938 | 57.3937 | 79.09% | 34 | 2 | 83.3% | 78.37% | 0 | 0.2019 | 1 | 0.2019 | 0.018037
SHINGLE SPRINGS 2105CB | SHING | SHINGLE SPRINGS 2105 | SIERRA | 19.4761 | 21.3342 | 76.42% | 1 | 7 | 100% | 96.24% | 0 | 0.20055 | 1 | 0.20055 | 0.010297
MIDDLETOWN 1101612 | MIDDL | MIDDLETOWN 1101 | HUMBOLDT | 3.8703 | 82.8475 | 40.87% | 13 | 3 | 100% | 100% | 1 | 0.19998 | 1 | 0.19998 | 0.051671
PLACERVILLE 21067522 | PLACE | PLACERVILLE 2106 | SIERRA | 67.5844 | 32.7125 | 84.62% | 19 | 16 | 100% | 11.4% | 0 | 0.1992 | 1 | 0.1992 | 0.0029474
BRUNSWICK 11062416 | BRUNS | BRUNSWICK 1106 | SIERRA | 28.6672 | 22.1211 | 86.48% | 10 | 9 | 92.26% | 60.33% | 1 | 0.19856 | 1 | 0.19856 | 0.0069265
MARTELL 110292172 | MARTE | MARTELL 1102 | STOCKTON | 1.6199 | 10 | 31.25% | 0 | 0 | 49.18% | 0% | 0 | 0.0099007 | 19.9979 | 0.19799 | 0.12222
GIRVAN 11011636 | GIRVA | GIRVAN 1101 | NORTH VALLEY | 16.6216 | 29.0593 | 66.7% | 0 | 3 | 90.3% | 84.26% | 1 | 0.19797 | 1 | 0.19797 | 0.01191
PENRYN 1107CB | PENRY | PENRYN 1107 | SIERRA | 5.4827 | 14.0733 | 57.47% | 3 | 1 | 34.07% | 0% | 0 | 0.01315 | 14.9507 | 0.19661 | 0.035859
BIG BASIN 110195690 | BIG B | BIG BASIN 1101 | CENTRAL COAST | 3.9003 | 22.8227 | 33.75% | 15 | 4 | 100% | 100% | 0 | 0.19661 | 1 | 0.19661 | 0.050408
LAS GALLINAS A 1105532 | LAS G | LAS GALLINAS A 1105 | NORTH BAY | 3.6841 | 80.5371 | 66.72% | 3 | 5 | 83.44% | 94.05% | 0 | 0.19645 | 1 | 0.19645 | 0.053325
SONOMA 1105138 | SONOM | SONOMA 1105 | SONOMA | 0.57477 | 60.5779 | 43.92% | 0 | 0 | 3.3% | 0% | 0 | 0.0098109 | 19.9979 | 0.1962 | 0.34135
OREGON TRAIL 110335002 | OREGO | OREGON TRAIL 1103 | NORTH VALLEY | 57.2663 | 26.028 | 93.47% | 4 | 13 | 100% | 0% | 0 | 0.19614 | 1 | 0.19614 | 0.003425
BIG RIVER 1101952 | BIG R | BIG RIVER 1101 | HUMBOLDT | 16.8032 | 42.8498 | 13.29% | 16 | 25 | 100% | 0% | 0 | 0.19578 | 1 | 0.19578 | 0.011651
REDBUD 1101454 | REDBU | REDBUD 1101 | HUMBOLDT | 5.6455 | 80.3546 | 100% | 0 | 0 | 100% | 100% | 0 | 0.19502 | 1 | 0.19502 | 0.034545
BOLINAS 1101530 | BOLIN | BOLINAS 1101 | NORTH BAY | 10.9693 | 95.0787 | 44.47% | 2 | 3 | 100% | 100% | 1 | 0.19488 | 1 | 0.19488 | 0.017766
BRUNSWICK 11103907 | BRUNS | BRUNSWICK 1110 | SIERRA | 0.89347 | 10 | 0% | 2 | 0 | 100% | 0% | 0 | 0.013031 | 14.9507 | 0.19483 | 0.21806
MORGAN HILL 2105CB | MORGA | MORGAN HILL 2105 | SAN JOSE | 0.38186 | 10 | 60.48% | 0 | 1 | 21.31% | 0% | 0 | 0.0097345 | 19.9979 | 0.19467 | 0.50979
BIG TREES 0402CB | BIG T | BIG TREES 0402 | CENTRAL COAST | 6.3055 | 27.5904 | 28.63% | 15 | 5 | 91.1% | 95.73% | 0 | 0.19443 | 1 | 0.19443 | 0.030835
ATASCADERO 1103A88 | ATASC | ATASCADERO 1103 | LOS PADRES | 0.25306 | 10 | 42.36% | 0 | 0 | 9.428% | 0% | 0 | 0.0073051 | 26.5534 | 0.19397 | 0.76652
DUNBAR 11033127 | DUNBA | DUNBAR 1103 | SONOMA | 8.8393 | 48.2541 | 93.29% | 0 | 4 | 91.69% | 100% | 0 | 0.19391 | 1 | 0.19391 | 0.021937
TIVY VALLEY 110737522 | TIVY | TIVY VALLEY 1107 | FRESNO | 0.51792 | 52.3595 | 87.8% | 0 | 0 | 16.67% | 0% | 0 | 0.017278 | 11.2183 | 0.19383 | 0.37424
BIG BASIN 1102CB | BIG B | BIG BASIN 1102 | CENTRAL COAST | 6.2676 | 51.463 | 36.35% | 17 | 4 | 100% | 100% | 0 | 0.19295 | 1 | 0.19295 | 0.030786
POINT MORETTI 110136514 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 6.8197 | 17.0171 | 90.44% | 21 | 1 | 100% | 87.46% | 0 | 0.19239 | 1 | 0.19239 | 0.028212
BRUNSWICK 110750008 | BRUNS | BRUNSWICK 1107 | SIERRA | 3.5553 | 10 | 37.92% | 1 | 5 | 44.72% | 0% | 0 | 0.01283 | 14.9507 | 0.19182 | 0.053953
PERRY 1101V88 | PERRY | PERRY 1101 | LOS PADRES | 1.2286 | 10 | 3.935% | 0 | 0 | 39.45% | 0% | 0 | 0.0071884 | 26.5534 | 0.19088 | 0.15536
IGNACIO 11011264 | IGNAC | IGNACIO 1101 | NORTH BAY | 1.5242 | 13.9644 | 55.83% | 0 | 4 | 38.01% | 4.721% | 0 | 0.016971 | 11.2183 | 0.19038 | 0.1249
BIG BASIN 11015028 | BIG B | BIG BASIN 1101 | CENTRAL COAST | 4.9702 | 16.4741 | 66.18% | 6 | 3 | 100% | 100% | 0 | 0.1889 | 1 | 0.1889 | 0.038007
SONOMA 11033052 | SONOM | SONOMA 1103 | SONOMA | 13.4991 | 28.4052 | 91.89% | 6 | 9 | 83.64% | 100% | 0 | 0.18717 | 1 | 0.18717 | 0.013866
CEDAR CREEK 11011710 | CEDAR | CEDAR CREEK 1101 | NORTH VALLEY | 0.076338 | 70.3009 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18445 | 1 | 0.18445 | 2.4162
CURTIS 170268380 | CURTI | CURTIS 1702 | YOSEMITE | 6.6498 | 16.4166 | 99.81% | 2 | 11 | 100% | 65.93% | 0 | 0.18443 | 1 | 0.18443 | 0.027735
COTATI 11055156 | COTAT | COTATI 1105 | SONOMA | 3.6981 | 31.1041 | 18.22% | 1 | 1 | 37.15% | 0% | 0 | 0.012279 | 14.9507 | 0.18358 | 0.049642
GARBERVILLE 11026084 | GARBE | GARBERVILLE 1102 | HUMBOLDT | 15.3135 | 81.9421 | 99.24% | 23 | 2 | 100% | 0% | 0 | 0.18331 | 1 | 0.18331 | 0.011971
CALISTOGA 110189150 | CALIS | CALISTOGA 1101 | NORTH BAY | 9.6361 | 72.7174 | 50.49% | 2 | 3 | 100% | 93.01% | 1 | 0.18208 | 1 | 0.18208 | 0.018895
CENTERVILLE 11012448 | CENTE | CENTERVILLE 1101 | NORTH VALLEY | 24.8271 | 10 | 80.77% | 5 | 8 | 100% | 95.09% | 1 | 0.182 | 1 | 0.182 | 0.0073305
SISQUOC 1102M52 | SISQU | SISQUOC 1102 | LOS PADRES | 31.4004 | 61.3581 | 49.81% | 0 | 2 | 87.94% | 100% | 0 | 0.18147 | 1 | 0.18147 | 0.0057791
GIRVAN 11029012 | GIRVA | GIRVAN 1102 | NORTH VALLEY | 15.986 | 25.3548 | 93.5% | 4 | 4 | 100% | 96.14% | 1 | 0.18146 | 1 | 0.18146 | 0.011351
OAKLAND X 1104CR288 | OAKLA | OAKLAND X 1104 | EAST BAY | 2.7135 | 13.3002 | 40.68% | 11 | 2 | 100% | 100% | 0 | 0.18087 | 1 | 0.18087 | 0.066655
PINE GROVE 11013170 | PINE | PINE GROVE 1101 | STOCKTON | 40.3025 | 15.3788 | 88.67% | 12 | 21 | 100% | 0% | 0 | 0.18 | 1 | 0.18 | 0.0044661
CALISTOGA 110266730 | CALIS | CALISTOGA 1102 | NORTH BAY | 1.1709 | 73.9432 | 93.25% | 0 | 0 | 100% | 100% | 0 | 0.17987 | 1 | 0.17987 | 0.15361
PASO ROBLES 11032731 | PASO | PASO ROBLES 1103 | LOS PADRES | 1.1994 | 24.9201 | 47.66% | 0 | 0 | 73.66% | 0% | 0 | 0.015948 | 11.2183 | 0.17891 | 0.14917
CURTIS 17039330 | CURTI | CURTIS 1703 | YOSEMITE | 41.1713 | 48.6933 | 100% | 9 | 13 | 100% | 41.49% | 1 | 0.1783 | 1 | 0.1783 | 0.0043308
LOS GATOS 110760092 | LOS G | LOS GATOS 1107 | DE ANZA | 9.7412 | 27.0068 | 22.28% | 14 | 2 | 100% | 100% | 0 | 0.17816 | 1 | 0.17816 | 0.018289
MORAGA 1102CB | MORAG | MORAGA 1102 | DIABLO | 3.3475 | 12.7577 | 17.22% | 0 | 6 | 36.14% | 35.27% | 0 | 0.015794 | 11.2183 | 0.17719 | 0.05293
GABILAN 1101579969 | GABIL | GABILAN 1101 | CENTRAL COAST | 4.2047 | 48.3297 | 40.21% | 0 | 0 | 62.81% | 0% | 0 | 0.01579 | 11.2183 | 0.17714 | 0.042129
CAMP EVERS 210610718 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 8.4743 | 22.3341 | 66.06% | 7 | 3 | 100% | 100% | 0 | 0.17677 | 1 | 0.17677 | 0.020859
DOBBINS 11011264 | DOBBI | DOBBINS 1101 | SIERRA | 34.6636 | 46.9951 | 96.43% | 5 | 9 | 99.16% | 60.09% | 0 | 0.17584 | 1 | 0.17584 | 0.0050729
WYANDOTTE 11031508 | WYAND | WYANDOTTE 1103 | NORTH VALLEY | 25.7036 | 27.6675 | 92.16% | 3 | 8 | 99.06% | 81.42% | 1 | 0.17558 | 1 | 0.17558 | 0.0068309
PLACERVILLE 210619552 | PLACE | PLACERVILLE 2106 | SIERRA | 21.1288 | 10.9472 | 81.54% | 2 | 6 | 100% | 88.4% | 1 | 0.17549 | 1 | 0.17549 | 0.0083057
SAN RAMON 2119CB | SAN R | SAN RAMON 2119 | MISSION | 0.46097 | 10 | 0% | 0 | 2 | 29.99% | 0% | 0 | 0.0066042 | 26.5534 | 0.17536 | 0.38042
TASSAJARA 2106CB | TASSA | TASSAJARA 2106 | DIABLO | 0.13696 | 51.6086 | 30.65% | 0 | 2 | 4.465% | 0% | 0 | 0.0087354 | 19.9979 | 0.17469 | 1.2755
SPRING GAP 1702CB | SPRIN | SPRING GAP 1702 | YOSEMITE | 7.418 | 94.1072 | 60.1% | 3 | 1 | 100% | 85.76% | 0 | 0.17407 | 1 | 0.17407 | 0.023466
SANTA ROSA A 1104210 | SANTA | SANTA ROSA A 1104 | SONOMA | 6.8749 | 10 | 33.39% | 9 | 10 | 88.77% | 100% | 0 | 0.17303 | 1 | 0.17303 | 0.025168
CASTRO VALLEY 1108MR273 | CASTR | CASTRO VALLEY 1108 | MISSION | 0.47624 | 26.7875 | 0% | 0 | 0 | 65.66% | 0% | 0 | 0.01155 | 14.9507 | 0.17268 | 0.3626
CALPINE 1146400 | CALPI | CALPINE 1146 | SONOMA | 3.1435 | 89.9771 | 73.48% | 0 | 0 | 100% | 100% | 0 | 0.17211 | 1 | 0.17211 | 0.054751
PAUL SWEET 21065178 | PAUL | PAUL SWEET 2106 | CENTRAL COAST | 7.3151 | 10 | 46.38% | 7 | 0 | 100% | 100% | 0 | 0.17066 | 1 | 0.17066 | 0.02333
BIG BASIN 110296986 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 5.8731 | 33.0475 | 64.84% | 22 | 1 | 100% | 100% | 0 | 0.16999 | 1 | 0.16999 | 0.028943
PLACER 1102CB | PLACE | PLACER 1102 | SIERRA | 2.1407 | 10 | 18.98% | 0 | 1 | 100% | 0% | 0 | 0.015126 | 11.2183 | 0.16968 | 0.079265
NARROWS 210248484 | NARRO | NARROWS 2102 | SIERRA | 41.4937 | 26.7261 | 86.16% | 7 | 18 | 100% | 0% | 0 | 0.16958 | 1 | 0.16958 | 0.004087
CALPINE 1146CB | CALPI | CALPINE 1146 | SONOMA | 3.8475 | 90.2876 | 70.72% | 0 | 0 | 100% | 100% | 0 | 0.16919 | 1 | 0.16919 | 0.043974
MARIPOSA 210110990 | MARIP | MARIPOSA 2101 | YOSEMITE | 39.8367 | 17.0819 | 99.94% | 3 | 69 | 100% | 0% | 0 | 0.16909 | 1 | 0.16909 | 0.0042446
COTATI 110475972 | COTAT | COTATI 1104 | SONOMA | 2.7371 | 10 | 35.68% | 0 | 3 | 41.48% | 0% | 0 | 0.015037 | 11.2183 | 0.1687 | 0.061633
WILLOW CREEK 110129362 | WILLO | WILLOW CREEK 1101 | HUMBOLDT | 6.8106 | 67.3887 | 96.73% | 8 | 5 | 58.77% | 100% | 1 | 0.16769 | 1 | 0.16769 | 0.024622
PUEBLO 1105716 | PUEBL | PUEBLO 1105 | NORTH BAY | 2.9378 | 34.7126 | 67.65% | 0 | 0 | 14.86% | 0% | 0 | 0.01121 | 14.9507 | 0.16759 | 0.057048
CORNING 11021900 | CORNI | CORNING 1102 | NORTH VALLEY | 0.99921 | 77.9025 | 2.304% | 0 | 2 | 5.388% | 0% | 0 | 0.0083558 | 19.9979 | 0.1671 | 0.16723
SAN LUIS OBISPO 11042293 | SAN L | SAN LUIS OBISPO 1104 | LOS PADRES | 9.0237 | 83.3193 | 68.53% | 2 | 1 | 100% | 100% | 0 | 0.16663 | 1 | 0.16663 | 0.018466
BIG BASIN 110276752 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 2.6798 | 26.5426 | 60.49% | 5 | 8 | 100% | 100% | 0 | 0.1665 | 1 | 0.1665 | 0.062131
WYANDOTTE 11091040 | WYAND | WYANDOTTE 1109 | NORTH VALLEY | 0.63854 | 10 | 53.93% | 1 | 0 | 10.55% | 0% | 0 | 0.0082291 | 19.9979 | 0.16456 | 0.25772
SUNOL 1101MR299 | SUNOL | SUNOL 1101 | MISSION | 4.988 | 63.7936 | 27.4% | 3 | 3 | 100% | 100% | 0 | 0.16428 | 1 | 0.16428 | 0.032934
PENRYN 11072704 | PENRY | PENRYN 1107 | SIERRA | 1.9532 | 10 | 45.97% | 0 | 0 | 34.19% | 0% | 0 | 0.010983 | 14.9507 | 0.1642 | 0.08407
STAFFORD 110233692 | STAFF | STAFFORD 1102 | NORTH BAY | 0.31495 | 10 | 16.33% | 0 | 0 | 14.09% | 0% | 0 | 0.0061817 | 26.5534 | 0.16415 | 0.52118
GOLDTREE 1105CB | GOLDT | GOLDTREE 1105 | LOS PADRES | 7.0823 | 62.297 | 33.11% | 0 | 1 | 49.12% | 0% | 0 | 0.014604 | 11.2183 | 0.16384 | 0.023133
SAN JOAQUIN #3 110210342 | SAN J | SAN JOAQUIN #3 1102 | YOSEMITE | 1.8206 | 16.0634 | 100% | 0 | 4 | 100% | 100% | 0 | 0.16247 | 1 | 0.16247 | 0.089238
PASO ROBLES 1104P02 | PASO | PASO ROBLES 1104 | LOS PADRES | 0.077403 | 10 | 100% | 0 | 0 | 1.071% | 0% | 0 | 0.010772 | 14.9507 | 0.16105 | 2.0807
PARADISE 110445674 | PARAD | PARADISE 1104 | NORTH VALLEY | 5.0463 | 10.402 | 42.33% | 2 | 14 | 100% | 100% | 0 | 0.16095 | 1 | 0.16095 | 0.031896
WOODACRE 1102137662 | WOODA | WOODACRE 1102 | NORTH BAY | 8.5017 | 38.382 | 27.15% | 11 | 8 | 98.65% | 72.31% | 0 | 0.16033 | 1 | 0.16033 | 0.018858
SILVERADO 2104708 | SILVE | SILVERADO 2104 | NORTH BAY | 4.377 | 40.803 | 65.23% | 1 | 8 | 88.72% | 99% | 0 | 0.16025 | 1 | 0.16025 | 0.036612
SAN RAMON 2101CB | SAN R | SAN RAMON 2101 | MISSION | 0.57317 | 10 | 0% | 0 | 0 | 53.42% | 0% | 0 | 0.0079978 | 19.9979 | 0.15994 | 0.27904
SAN JOAQUIN #3 1101CB | SAN J | SAN JOAQUIN #3 1101 | YOSEMITE | 5.4085 | 45.9214 | 90.84% | 2 | 3 | 100% | 98.42% | 0 | 0.15907 | 1 | 0.15907 | 0.029412
DUNLAP 11027050 | DUNLA | DUNLAP 1102 | FRESNO | 9.1044 | 57.339 | 92.11% | 4 | 10 | 100% | 0% | 0 | 0.15825 | 1 | 0.15825 | 0.017382
BIG BASIN 11028403 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 4.9235 | 33.659 | 85.64% | 2 | 1 | 100% | 100% | 0 | 0.15781 | 1 | 0.15781 | 0.032053
DIAMOND SPRINGS 110519910 | DIAMO | DIAMOND SPRINGS 1105 | SIERRA | 20.7681 | 27.6002 | 62.16% | 0 | 7 | 100% | 83.55% | 0 | 0.1574 | 1 | 0.1574 | 0.0075791
NOTRE DAME 11042028 | NOTRE | NOTRE DAME 1104 | NORTH VALLEY | 10.9017 | 45.9089 | 89% | 0 | 3 | 100% | 100% | 0 | 0.15694 | 1 | 0.15694 | 0.014396
MONTE RIO 111159046 | MONTE | MONTE RIO 1111 | SONOMA | 2.6767 | 61.8101 | 0% | 1 | 1 | 70.69% | 0% | 0 | 0.013942 | 11.2183 | 0.15641 | 0.058434
KESWICK 11011590 | KESWI | KESWICK 1101 | NORTH VALLEY | 6.51 | 47.89 | 75.62% | 0 | 1 | 100% | 100% | 0 | 0.15625 | 1 | 0.15625 | 0.024001
NEWBURG 11323425 | NEWBU | NEWBURG 1132 | HUMBOLDT | 0.9717 | 21.9962 | 41.93% | 1 | 0 | 64.08% | 0% | 0 | 0.013757 | 11.2183 | 0.15433 | 0.15882
HORSESHOE 1101CB | HORSE | HORSESHOE 1101 | SIERRA | 1.5163 | 10 | 43.57% | 1 | 0 | 28.38% | 0% | 0 | 0.010302 | 14.9507 | 0.15402 | 0.10157
CAMP EVERS 210637210 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 6.3592 | 23.8928 | 45.59% | 8 | 2 | 100% | 100% | 0 | 0.15389 | 1 | 0.15389 | 0.0242
SARATOGA 1107LC12 | SARAT | SARATOGA 1107 | DE ANZA | 7.3147 | 36.5682 | 63.55% | 4 | 7 | 100% | 57.8% | 0 | 0.15388 | 1 | 0.15388 | 0.021038
BIG BEND 1101641808 | BIG B | BIG BEND 1101 | NORTH VALLEY | 24.9976 | 36.2263 | 100% | 6 | 10 | 95.85% | 52.55% | 1 | 0.15307 | 1 | 0.15307 | 0.0061233
LOS GATOS 1106LA42 | LOS G | LOS GATOS 1106 | DE ANZA | 2.7943 | 10 | 80.03% | 3 | 2 | 100% | 100% | 1 | 0.15252 | 1 | 0.15252 | 0.054582
CLARKSVILLE 210319572 | CLARK | CLARKSVILLE 2103 | SIERRA | 33.5123 | 41.8595 | 99.97% | 3 | 7 | 77.35% | 59.23% | 1 | 0.15209 | 1 | 0.15209 | 0.0045384
ELK 11011272 | ELK 1 | ELK 1101 | HUMBOLDT | 22.2131 | 39.0938 | 18.17% | 28 | 27 | 99.76% | 0% | 0 | 0.15006 | 1 | 0.15006 | 0.0067553
SAUSALITO 1101CB | SAUSA | SAUSALITO 1101 | NORTH BAY | 0.084384 | 10 | 39.07% | 0 | 0 | 1.452% | 0% | 0 | 0.0074993 | 19.9979 | 0.14997 | 1.7773
WOODACRE 1102CB | WOODA | WOODACRE 1102 | NORTH BAY | 12.3335 | 47.7292 | 17.58% | 11 | 6 | 98.44% | 71.03% | 1 | 0.14985 | 1 | 0.14985 | 0.01215
CURTIS 17028000 | CURTI | CURTIS 1702 | YOSEMITE | 14.3249 | 17.4723 | 99.98% | 1 | 11 | 100% | 50.67% | 0 | 0.14933 | 1 | 0.14933 | 0.010425
CAMP EVERS 2105CB | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 8.5381 | 22.2654 | 52.34% | 18 | 3 | 83.09% | 96.05% | 0 | 0.14927 | 1 | 0.14927 | 0.017482
MORGAN HILL 2105XR268 | MORGA | MORGAN HILL 2105 | SAN JOSE | 7.973 | 60.2912 | 70.21% | 1 | 2 | 100% | 100% | 0 | 0.14861 | 1 | 0.14861 | 0.018639
MORGAN HILL 210542348 | MORGA | MORGAN HILL 2105 | SAN JOSE | 1.0024 | 17.5681 | 55.95% | 0 | 0 | 23.75% | 0% | 0 | 0.0099083 | 14.9507 | 0.14814 | 0.14778
ELECTRA 11022646 | ELECT | ELECTRA 1102 | STOCKTON | 25.2162 | 27.1707 | 98.11% | 7 | 13 | 100% | 22.04% | 1 | 0.14592 | 1 | 0.14592 | 0.0057868
FULTON 1107 | FULTO | FULTON 1107 | SONOMA | 0.4544 | 32.639 | 77.88% | 0 | 1 | 100% | 100% | 1 | 0.14528 | 1 | 0.14528 | 0.31971
WILLITS 1103966 | WILLI | WILLITS 1103 | HUMBOLDT | 1.3235 | 20.8407 | 41.93% | 0 | 1 | 57.92% | 0% | 0 | 0.012942 | 11.2183 | 0.14519 | 0.1097
CAMP EVERS 210310946 | CAMP | CAMP EVERS 2103 | CENTRAL COAST | 5.6138 | 10 | 43.31% | 5 | 3 | 66.4% | 100% | 0 | 0.14518 | 1 | 0.14518 | 0.02586
REDBUD 11022013 | REDBU | REDBUD 1102 | HUMBOLDT | 0.11285 | 35.1068 | 100% | 0 | 0 | 2.449% | 0% | 0 | 0.01294 | 11.2183 | 0.14517 | 1.2864
CAMP EVERS 21055146 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 6.0305 | 10 | 32.63% | 11 | 6 | 100% | 100% | 0 | 0.14397 | 1 | 0.14397 | 0.023874
CAMP EVERS 21055232 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 4.5381 | 18.453 | 49.44% | 6 | 6 | 100% | 100% | 0 | 0.14357 | 1 | 0.14357 | 0.031638
SAN RAFAEL 1101310 | SAN R | SAN RAFAEL 1101 | NORTH BAY | 1.3967 | 10 | 2.818% | 0 | 0 | 39.65% | 0% | 0 | 0.0071371 | 19.9979 | 0.14273 | 0.10219
COARSEGOLD 21025722 | COARS | COARSEGOLD 2102 | YOSEMITE | 1.9829 | 10 | 100% | 0 | 5 | 100% | 100% | 0 | 0.14258 | 1 | 0.14258 | 0.071902
NORTH DUBLIN 2103 | NORTH | NORTH DUBLIN 2103 | MISSION | 0.0011266 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 11.2183 | 0.14242 | 126.4119
DEL MONTE 21043066 | DEL M | DEL MONTE 2104 | CENTRAL COAST | 0.016196 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 11.2183 | 0.14242 | 8.7937
PUEBLO 1104 | PUEBL | PUEBLO 1104 | NORTH BAY | 0.072037 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 11.2183 | 0.14242 | 1.9771
WILLITS 11032500 | WILLI | WILLITS 1103 | HUMBOLDT | 29.9853 | 83.8453 | 100% | 11 | 13 | 100% | 0% | 0 | 0.14143 | 1 | 0.14143 | 0.0047165
BOLINAS 1101806 | BOLIN | BOLINAS 1101 | NORTH BAY | 3.0453 | 88.6877 | 5.762% | 0 | 3 | 100% | 100% | 0 | 0.14085 | 1 | 0.14085 | 0.046251
RED BLUFF 1104CB | RED B | RED BLUFF 1104 | NORTH VALLEY | 2.0518 | 10 | 96.16% | 0 | 0 | 19.48% | 0% | 0 | 0.012529 | 11.2183 | 0.14056 | 0.068503
REDBUD 11021212 | REDBU | REDBUD 1102 | HUMBOLDT | 0.436 | 23.3209 | 21.35% | 0 | 1 | 11.49% | 0% | 0 | 0.0070167 | 19.9979 | 0.14032 | 0.32184
SUNOL 1101MR298 | SUNOL | SUNOL 1101 | MISSION | 5.4024 | 53.1471 | 44.07% | 1 | 5 | 100% | 100% | 0 | 0.1402 | 1 | 0.1402 | 0.025952
SEACLIFF 0401CB | SEACL | SEACLIFF 0401 | CENTRAL COAST | 5.8801 | 16.5923 | 59.63% | 6 | 2 | 97.46% | 83.75% | 0 | 0.13923 | 1 | 0.13923 | 0.023678
SALT SPRINGS 21028442 | SALT | SALT SPRINGS 2102 | STOCKTON | 12.1299 | 48.4336 | 100% | 5 | 7 | 100% | 9.936% | 1 | 0.13919 | 1 | 0.13919 | 0.011475
CLAYTON 2212CB | CLAYT | CLAYTON 2212 | DIABLO | 1.3959 | 28.1061 | 22.31% | 0 | 2 | 11% | 15.16% | 0 | 0.01235 | 11.2183 | 0.13855 | 0.099254
MARIPOSA 21014410 | MARIP | MARIPOSA 2101 | YOSEMITE | 22.8041 | 16.019 | 99.74% | 6 | 25 | 100% | 48.37% | 1 | 0.13823 | 1 | 0.13823 | 0.0060618
DUNBAR 110147964 | DUNBA | DUNBAR 1101 | SONOMA | 6.3806 | 61.1795 | 83.1% | 1 | 6 | 83.19% | 93% | 0 | 0.13803 | 1 | 0.13803 | 0.021632
MIWUK 170247143 | MIWUK | MIWUK 1702 | YOSEMITE | 4.8917 | 41.2668 | 100% | 1 | 8 | 100% | 79.87% | 0 | 0.13801 | 1 | 0.13801 | 0.028213
TASSAJARA 2113MR276 | TASSA | TASSAJARA 2113 | DIABLO | 3.6023 | 62.8969 | 34.15% | 1 | 2 | 92.48% | 100% | 0 | 0.13782 | 1 | 0.13782 | 0.038257
PAUL SWEET 2106428102 | PAUL | PAUL SWEET 2106 | CENTRAL COAST | 11.5695 | 14.0231 | 80.02% | 8 | 3 | 89.09% | 75.97% | 1 | 0.13775 | 1 | 0.13775 | 0.011906
MARIPOSA 210110240 | MARIP | MARIPOSA 2101 | YOSEMITE | 21.4769 | 25.894 | 68.07% | 2 | 22 | 100% | 66.83% | 0 | 0.13718 | 1 | 0.13718 | 0.0063872
DUNBAR 1101416 | DUNBA | DUNBAR 1101 | SONOMA | 2.8528 | 67.3035 | 61.83% | 0 | 0 | 84.79% | 100% | 0 | 0.13696 | 1 | 0.13696 | 0.048009
MARIPOSA 21029590 | MARIP | MARIPOSA 2102 | YOSEMITE | 36.36 | 19.6403 | 97.41% | 1 | 52 | 100% | 0% | 0 | 0.13645 | 1 | 0.13645 | 0.0037527
CLARK ROAD 11022068 | CLARK | CLARK ROAD 1102 | NORTH VALLEY | 10.7164 | 15.0462 | 99.79% | 0 | 2 | 100% | 90.22% | 1 | 0.13587 | 1 | 0.13587 | 0.012679
SPAULDING 1101578852 | SPAUL | SPAULDING 1101 | SIERRA | 20.1063 | 56.8104 | 73.09% | 2 | 12 | 82.23% | 8.84% | 1 | 0.13582 | 1 | 0.13582 | 0.0067553
ALLEGHANY 1101808 | ALLEG | ALLEGHANY 1101 | SIERRA | 6.1403 | 95.663 | 12.49% | 0 | 2 | 100% | 100% | 0 | 0.13475 | 1 | 0.13475 | 0.021945
OAKHURST 110310570 | OAKHU | OAKHURST 1103 | YOSEMITE | 9.7802 | 19.5863 | 100% | 0 | 5 | 100% | 83.62% | 0 | 0.13448 | 1 | 0.13448 | 0.013751
BEAR VALLEY 21059560 | BEAR | BEAR VALLEY 2105 | YOSEMITE | 36.2873 | 45.8774 | 99.97% | 7 | 2 | 100% | 13.33% | 1 | 0.13437 | 1 | 0.13437 | 0.0037029
ANNAPOLIS 1101608 | ANNAP | ANNAPOLIS 1101 | HUMBOLDT | 17.8008 | 87.1454 | 94.8% | 10 | 5 | 100% | 0% | 0 | 0.13339 | 1 | 0.13339 | 0.0074933
SAN JOAQUIN #3 110110060 | SAN J | SAN JOAQUIN #3 1101 | YOSEMITE | 6.5306 | 43.2657 | 65.2% | 0 | 4 | 100% | 100% | 0 | 0.133 | 1 | 0.133 | 0.020366
MARIPOSA 210210880 | MARIP | MARIPOSA 2102 | YOSEMITE | 39.106 | 24.6164 | 88.93% | 0 | 41 | 98.36% | 24.49% | 0 | 0.13284 | 1 | 0.13284 | 0.003397
COARSEGOLD 210210610 | COARS | COARSEGOLD 2102 | YOSEMITE | 1.3639 | 10 | 100% | 0 | 1 | 100% | 100% | 0 | 0.13262 | 1 | 0.13262 | 0.097235
DOBBINS 110169722 | DOBBI | DOBBINS 1101 | SIERRA | 6.6325 | 10 | 87.38% | 1 | 4 | 100% | 93.4% | 1 | 0.13241 | 1 | 0.13241 | 0.019964
OLEMA 1101416 | OLEMA | OLEMA 1101 | NORTH BAY | 15.842 | 82.0626 | 5.587% | 9 | 6 | 97.77% | 72.25% | 1 | 0.13235 | 1 | 0.13235 | 0.0083546
CAMP EVERS 210612840 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 4.0602 | 32.5066 | 59.36% | 5 | 0 | 100% | 100% | 0 | 0.13232 | 1 | 0.13232 | 0.032588
CALPINE 1144CB | CALPI | CALPINE 1144 | SONOMA | 26.2964 | 85.7305 | 55.05% | 0 | 0 | 100% | 92.09% | 0 | 0.1323 | 1 | 0.1323 | 0.0050311
ECHO SUMMIT 11018922 | ECHO | ECHO SUMMIT 1101 | (blank) | 2.2784 | 12.8457 | 99.62% | 6 | 2 | 64% | 0% | 0 | 0.13221 | 1 | 0.13221 | 0.058028
GIRVAN 11011330 | GIRVA | GIRVAN 1101 | NORTH VALLEY | 31.2468 | 42.7568 | 99.67% | 0 | 4 | 100% | 24.65% | 1 | 0.13164 | 1 | 0.13164 | 0.0042128
SAN LUIS OBISPO 1107V62 | SAN L | SAN LUIS OBISPO 1107 | LOS PADRES | 6.9341 | 31.5234 | 48.48% | 0 | 11 | 100% | 70.79% | 1 | 0.1315 | 1 | 0.1315 | 0.018964
SAN JOAQUIN #3 1102CB | SAN J | SAN JOAQUIN #3 1102 | YOSEMITE | 9.6989 | 12.3012 | 62.24% | 3 | 14 | 100% | 56.8% | 0 | 0.1304 | 1 | 0.1304 | 0.013445
OAKLAND X 1104 | OAKLA | OAKLAND X 1104 | EAST BAY | 0.11526 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 0.13022 | 1.1298
CENTERVILLE 1101 | CENTE | CENTERVILLE 1101 | NORTH VALLEY | 0.0017292 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 0.13022 | 75.3097
GREEN VALLEY 21011645 | GREEN | GREEN VALLEY 2101 | CENTRAL COAST | 0.48374 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 0.13022 | 0.2692
SCE VEGAS 1701CB | SCE V | SCE VEGAS 1701 | LOS PADRES | 0.17032 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 0.13022 | 0.76457
WILLOW CREEK 11032936 | WILLO | WILLOW CREEK 1103 | HUMBOLDT | 32.9597 | 79.3849 | 82.84% | 19 | 24 | 100% | 0% | 0 | 0.12943 | 1 | 0.12943 | 0.0039268
GEYSERVILLE 1102484 | GEYSE | GEYSERVILLE 1102 | SONOMA | 33.3601 | 63.5348 | 83.52% | 3 | 7 | 68.39% | 43.97% | 0 | 0.12892 | 1 | 0.12892 | 0.0038645
MORAGA 1101CB | MORAG | MORAGA 1101 | DIABLO | 6.145 | 55.6277 | 5.196% | 2 | 13 | 81.97% | 88.05% | 0 | 0.12886 | 1 | 0.12886 | 0.02097
HALSEY 110239104 | HALSE | HALSEY 1102 | SIERRA | 30.6401 | 10.3566 | 73.57% | 9 | 18 | 100% | 0% | 0 | 0.1288 | 1 | 0.1288 | 0.0042036
HARTLEY 1101471 | HARTL | HARTLEY 1101 | HUMBOLDT | 0.38585 | 10 | 33.51% | 0 | 1 | 31.01% | 0% | 0 | 0.0085975 | 14.9507 | 0.12854 | 0.33314
PARADISE 11032534 | PARAD | PARADISE 1103 | NORTH VALLEY | 4.7177 | 10 | 61.75% | 3 | 6 | 100% | 100% | 0 | 0.12837 | 1 | 0.12837 | 0.027211
APPLE HILL 11038412 | APPLE | APPLE HILL 1103 | SIERRA | 20.0804 | 56.3777 | 98.03% | 4 | 10 | 100% | 56.18% | 1 | 0.12834 | 1 | 0.12834 | 0.0063913
OAKHURST 110110090 | OAKHU | OAKHURST 1101 | YOSEMITE | 44.1093 | 32.6301 | 93.91% | 4 | 19 | 100% | 7.446% | 0 | 0.12831 | 1 | 0.12831 | 0.002909
PAUL SWEET 210411074 | PAUL | PAUL SWEET 2104 | CENTRAL COAST | 2.9891 | 10 | 96.78% | 2 | 0 | 97.58% | 100% | 0 | 0.12749 | 1 | 0.12749 | 0.042651
PAUL SWEET 21068091 | PAUL | PAUL SWEET 2106 | CENTRAL COAST | 6.0187 | 18.6502 | 32.26% | 14 | 1 | 100% | 100% | 0 | 0.12726 | 1 | 0.12726 | 0.021144
SAN LUIS OBISPO 1107V02 | SAN L | SAN LUIS OBISPO 1107 | LOS PADRES | 17.85 | 46.8397 | 49.77% | 4 | 7 | 97.96% | 39.87% | 0 | 0.12708 | 1 | 0.12708 | 0.0071196
VIEJO 22019704 | VIEJO | VIEJO 2201 | CENTRAL COAST | 1.0374 | 10 | 50.89% | 1 | 2 | 40.52% | 0% | 0 | 0.011266 | 11.2183 | 0.12638 | 0.12183
PLACERVILLE 210619732 | PLACE | PLACERVILLE 2106 | SIERRA | 9.0659 | 10 | 43.47% | 3 | 13 | 100% | 82.12% | 1 | 0.12525 | 1 | 0.12525 | 0.013816
MONTE RIO 11131067 | MONTE | MONTE RIO 1113 | SONOMA | 0.80536 | 36.8006 | 36.57% | 2 | 0 | 100% | 100% | 0 | 0.12505 | 1 | 0.12505 | 0.15528
BELL 1107CB | BELL | BELL 1107 | SIERRA | 0.084936 | 10 | 100% | 0 | 1 | 2.211% | 0% | 0 | 0.011123 | 11.2183 | 0.12478 | 1.4691
DEL MONTE 21029060 | DEL M | DEL MONTE 2102 | CENTRAL COAST | 0.0023123 | 10 | 0% | 0 | 0 | 0.0258% | 0% | 0 | 0.0046992 | 26.5534 | 0.12478 | 53.9628
VINEYARD 2107MR332 | VINEY | VINEYARD 2107 | MISSION | 0.086505 | 10 | 100% | 1 | 0 | 2.473% | 0% | 0 | 0.011067 | 11.2183 | 0.12415 | 1.4352
VIEJO 22029112 | VIEJO | VIEJO 2202 | CENTRAL COAST | 0.78302 | 10 | 22.17% | 1 | 0 | 23.74% | 0% | 0 | 0.008258 | 14.9507 | 0.12346 | 0.15768
HIGGINS 11102408 | HIGGI | HIGGINS 1110 | SIERRA | 35.5285 | 10.5577 | 99.97% | 6 | 7 | 100% | 0% | 0 | 0.12315 | 1 | 0.12315 | 0.0034664
SAN RAMON 2117CB | SAN R | SAN RAMON 2117 | MISSION | 0.44721 | 10 | 0% | 0 | 0 | 26.74% | 0% | 0 | 0.0061326 | 19.9979 | 0.12264 | 0.27424
WYANDOTTE 1109CB | WYAND | WYANDOTTE 1109 | NORTH VALLEY | 2.5841 | 10 | 31.89% | 0 | 1 | 27.38% | 0% | 0 | 0.0081836 | 14.9507 | 0.12235 | 0.047348
ORO FINO 11022236 | ORO F | ORO FINO 1102 | NORTH VALLEY | 2.5402 | 88.3654 | 18.46% | 0 | 3 | 100% | 100% | 0 | 0.12209 | 1 | 0.12209 | 0.048063
SAN RAFAEL 11071276 | SAN R | SAN RAFAEL 1107 | NORTH BAY | 3.842 | 10 | 17.39% | 6 | 6 | 100% | 100% | 0 | 0.12189 | 1 | 0.12189 | 0.031726
HORSESHOE 11011682 | HORSE | HORSESHOE 1101 | SIERRA | 1.1361 | 10 | 70.68% | 0 | 0 | 11.64% | 0% | 0 | 0.010746 | 11.2183 | 0.12055 | 0.10611
WILLOW CREEK 110347966 | WILLO | WILLOW CREEK 1103 | HUMBOLDT | 17.0216 | 48.5214 | 76.15% | 20 | 19 | 100% | 0% | 0 | 0.11952 | 1 | 0.11952 | 0.0070219
CLOVERDALE 1102570 | CLOVE | CLOVERDALE 1102 | SONOMA | 17.3117 | 48.3271 | 69.88% | 1 | 6 | 81.35% | 95.94% | 0 | 0.11928 | 1 | 0.11928 | 0.0068903
MIRABEL 110257840 | MIRAB | MIRABEL 1102 | SONOMA | 2.5892 | 51.5846 | 26.12% | 5 | 1 | 100% | 100% | 0 | 0.11884 | 1 | 0.11884 | 0.045897
GRASS VALLEY 11032180 | GRASS | GRASS VALLEY 1103 | SIERRA | 44.2075 | 22.3739 | 98.77% | 3 | 16 | 100% | 0% | 0 | 0.11816 | 1 | 0.11816 | 0.0026728
VOLTA 110185234 | VOLTA | VOLTA 1101 | NORTH VALLEY | 7.9136 | 44.4652 | 95.46% | 10 | 12 | 100% | 0% | 0 | 0.11805 | 1 | 0.11805 | 0.014917
DIAMOND SPRINGS 11057722 | DIAMO | DIAMOND SPRINGS 1105 | SIERRA | 59.1027 | 30.4266 | 87.61% | 10 | 7 | 94.99% | 35.49% | 0 | 0.11755 | 1 | 0.11755 | 0.0019889
PUEBLO 210378504 | PUEBL | PUEBLO 2103 | NORTH BAY | 7.9718 | 44.4313 | 84.9% | 7 | 4 | 65.86% | 87.65% | 1 | 0.11699 | 1 | 0.11699 | 0.014676
OTTER 1102CB | OTTER | OTTER 1102 | CENTRAL COAST | 6.6866 | 58.389 | 0% | 3 | 0 | 98.35% | 55.62% | 1 | 0.11663 | 1 | 0.11663 | 0.017443
BIG BASIN 110210254 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 2.1303 | 79.74 | 23.5% | 0 | 1 | 100% | 100% | 1 | 0.11586 | 1 | 0.11586 | 0.054386
PARADISE 11032488 | PARAD | PARADISE 1103 | NORTH VALLEY | 3.2215 | 10 | 53.79% | 1 | 2 | 100% | 95.34% | 0 | 0.11569 | 1 | 0.11569 | 0.035911
PUEBLO 1105696 | PUEBL | PUEBLO 1105 | NORTH BAY | 20.5418 | 62.3545 | 78.14% | 5 | 4 | 69.81% | 0% | 0 | 0.11569 | 1 | 0.11569 | 0.0056317
OAKLAND K 1104CR204 | OAKLA | OAKLAND K 1104 | EAST BAY | 3.7332 | 23.8088 | 27.59% | 6 | 1 | 100% | 100% | 0 | 0.11562 | 1 | 0.11562 | 0.030971
APPLE HILL 21028372 | APPLE | APPLE HILL 2102 | SIERRA | 56.1866 | 51.1532 | 100% | 7 | 2 | 89.5% | 31.4% | 1 | 0.11526 | 1 | 0.11526 | 0.0020514
TASSAJARA 2112CB | TASSA | TASSAJARA 2112 | DIABLO | 0.3541 | 10 | 9.426% | 1 | 0 | 26.89% | 0% | 0 | 0.0076765 | 14.9507 | 0.11477 | 0.32412
VOLTA 110297816 | VOLTA | VOLTA 1102 | NORTH VALLEY | 5.2578 | 25.9131 | 100% | 2 | 2 | 100% | 80.28% | 1 | 0.11476 | 1 | 0.11476 | 0.021827
MORGAN HILL 2105XR176 | MORGA | MORGAN HILL 2105 | SAN JOSE | 18.5618 | 37.9512 | 61.14% | 2 | 13 | 67.38% | 10.57% | 0 | 0.11466 | 1 | 0.11466 | 0.0061773
EMERALD LAKE 0401CB | EMERA | EMERALD LAKE 0401 | PENINSULA | 15.5314 | 21.1198 | 27.73% | 5 | 20 | 73.41% | 27.29% | 1 | 0.11416 | 1 | 0.11416 | 0.0073502
MONROE 210392868 | MONRO | MONROE 2103 | SONOMA | 0.69734 | 10 | 73.35% | 0 | 3 | 74% | 100% | 0 | 0.11412 | 1 | 0.11412 | 0.16365
MIRABEL 1102841 | MIRAB | MIRABEL 1102 | SONOMA | 0.78827 | 21.9552 | 18.73% | 8 | 3 | 100% | 100% | 0 | 0.11386 | 1 | 0.11386 | 0.14445
HOOPA 11013174 | HOOPA | HOOPA 1101 | HUMBOLDT | 17.6485 | 69.5085 | 99.93% | 19 | 10 | 80.04% | 0% | 0 | 0.11313 | 1 | 0.11313 | 0.0064099
LAURELES 11112020 | LAURE | LAURELES 1111 | CENTRAL COAST | 33.1343 | 48.734 | 70.7% | 2 | 9 | 100% | 9.9% | 1 | 0.11304 | 1 | 0.11304 | 0.0034116
JESSUP 1103CB | JESSU | JESSUP 1103 | NORTH VALLEY | 0.3876 | 22.4131 | 79.44% | 0 | 0 | 2.712% | 0% | 0 | 0.010068 | 11.2183 | 0.11295 | 0.2914
KANAKA 1101CB | KANAK | KANAKA 1101 | NORTH VALLEY | 4.6774 | 55.1611 | 80.24% | 0 | 1 | 100% | 79.67% | 1 | 0.11271 | 1 | 0.11271 | 0.024096
HALF MOON BAY 1101CB | HALF | HALF MOON BAY 1101 | PENINSULA | 8.298 | 59.005 | 12.7% | 3 | 2 | 59.24% | 75.84% | 1 | 0.11209 | 1 | 0.11209 | 0.013508
SILVERADO 2102636 | SILVE | SILVERADO 2102 | NORTH BAY | 3.9682 | 44.4482 | 89.35% | 2 | 0 | 70.53% | 80.46% | 1 | 0.11193 | 1 | 0.11193 | 0.028206
CURTIS 17039210 | CURTI | CURTIS 1703 | YOSEMITE | 23.0078 | 62.9555 | 99.96% | 11 | 7 | 100% | 0% | 0 | 0.11179 | 1 | 0.11179 | 0.0048587
CENTERVILLE 11011243 | CENTE | CENTERVILLE 1101 | NORTH VALLEY | 5.1549 | 10 | 65.95% | 0 | 5 | 100% | 100% | 0 | 0.11154 | 1 | 0.11154 | 0.021638
LAURELES 1111432 | LAURE | LAURELES 1111 | CENTRAL COAST | 49.1946 | 74.7913 | 100% | 10 | 10 | 100% | 0% | 0 | 0.11153 | 1 | 0.11153 | 0.0022671
WEST POINT 1101CB | WEST | WEST POINT 1101 | STOCKTON | 4.7054 | 80.5028 | 15.54% | 1 | 1 | 100% | 100% | 0 | 0.11111 | 1 | 0.11111 | 0.023614
FITCH MOUNTAIN 1111CB | FITCH | FITCH MOUNTAIN 1111 | SONOMA | 0.55902 | 10 | 52% | 0 | 0 | 3.182% | 0% | 0 | 0.0074291 | 14.9507 | 0.11107 | 0.19869
CLARKSVILLE 2105CB | CLARK | CLARKSVILLE 2105 | SIERRA | 0.54433 | 10 | 0% | 0 | 0 | 45.8% | 0% | 0 | 0.0074141 | 14.9507 | 0.11085 | 0.20364
SONOMA 1102118 | SONOM | SONOMA 1102 | SONOMA | 5.4359 | 22.1228 | 81.08% | 2 | 7 | 71.73% | 100% | 0 | 0.11084 | 1 | 0.11084 | 0.020391
CORNING 11021622 | CORNI | CORNING 1102 | NORTH VALLEY | 34.031 | 83.6384 | 99.67% | 1 | 6 | 100% | 0% | 0 | 0.11037 | 1 | 0.11037 | 0.0032434
MOUNTAIN QUARRIES 21011102 | MOUNT | MOUNTAIN QUARRIES 2101 | SIERRA | 44.4218 | 34.6112 | 86.6% | 0 | 15 | 100% | 0% | 0 | 0.11033 | 1 | 0.11033 | 0.0024838
MIDDLETOWN 1103CB | MIDDL | MIDDLETOWN 1103 | HUMBOLDT | 0.052982 | 70.6148 | 0% | 0 | 0 | 32.86% | 0% | 0 | 0.009835 | 11.2183 | 0.11033 | 2.0825
PENNGROVE 1101554 | PENNG | PENNGROVE 1101 | SONOMA | 0.80578 | 23.6637 | 31.41% | 1 | 1 | 6.241% | 0% | 0 | 0.0073444 | 14.9507 | 0.1098 | 0.13627
GARBERVILLE 11011514 | GARBE | GARBERVILLE 1101 | HUMBOLDT | 14.7707 | 71.7705 | 51.17% | 15 | 7 | 100% | 0% | 0 | 0.10959 | 1 | 0.10959 | 0.0074197
NARROWS 21011202 | NARRO | NARROWS 2101 | SIERRA | 45.5016 | 16.7658 | 94.84% | 2 | 35 | 100% | 0% | 0 | 0.10949 | 1 | 0.10949 | 0.0024062
CEDAR CREEK 11011608 | CEDAR | CEDAR CREEK 1101 | NORTH VALLEY | 33.3899 | 31.7775 | 100% | 3 | 12 | 100% | 36.09% | 1 | 0.10917 | 1 | 0.10917 | 0.0032697
HOOPA 110182542 | HOOPA | HOOPA 1101 | HUMBOLDT | 9.9783 | 60.316 | 90.42% | 13 | 6 | 65.67% | 0% | 0 | 0.10839 | 1 | 0.10839 | 0.010862
PARADISE 11042034 | PARAD | PARADISE 1104 | NORTH VALLEY | 10.6989 | 15.2166 | 88.93% | 0 | 6 | 94.14% | 86.31% | 1 | 0.10808 | 1 | 0.10808 | 0.010102
COARSEGOLD 2102383092 | COARS | COARSEGOLD 2102 | YOSEMITE | 0.3809 | 10 | 73.97% | 0 | 0 | 100% | 100% | 0 | 0.10776 | 1 | 0.10776 | 0.28291
BIG BASIN 110212124 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 4.2617 | 10 | 33.1% | 2 | 2 | 100% | 100% | 0 | 0.1076 | 1 | 0.1076 | 0.025248
SHINGLE SPRINGS 211051790 | SHING | SHINGLE SPRINGS 2110 | SIERRA | 8.0868 | 16.0955 | 60.72% | 1 | 8 | 93.48% | 72.08% | 0 | 0.10718 | 1 | 0.10718 | 0.013253
STILLWATER 11011320 | STILL | STILLWATER 1101 | NORTH VALLEY | 18.8372 | 23.2893 | 80.24% | 9 | 10 | 93.78% | 0% | 0 | 0.10603 | 1 | 0.10603 | 0.005629
GARBERVILLE 110197300 | GARBE | GARBERVILLE 1101 | HUMBOLDT | 14.1538 | 63.6884 | 85.32% | 13 | 2 | 100% | 0% | 0 | 0.1059 | 1 | 0.1059 | 0.0074819
STANISLAUS 17017144 | STANI | STANISLAUS 1701 | YOSEMITE | 4.4552 | 18.8557 | 79.41% | 0 | 8 | 100% | 0% | 0 | 0.10581 | 1 | 0.10581 | 0.02375
BRUNSWICK 11067099 | BRUNS | BRUNSWICK 1106 | SIERRA | 7.5715 | 32.7231 | 90.35% | 0 | 3 | 100% | 52.26% | 0 | 0.1055 | 1 | 0.1055 | 0.013934
SAN LUIS OBISPO 1101V12 | SAN L | SAN LUIS OBISPO 1101 | LOS PADRES | 21.0121 | 75.506 | 48.74% | 1 | 1 | 99.72% | 49% | 1 | 0.10534 | 1 | 0.10534 | 0.0050134
AUBERRY 1101R2845 | AUBER | AUBERRY 1101 | FRESNO | 17.7605 | 28.7565 | 100% | 4 | 13 | 100% | 0% | 0 | 0.10532 | 1 | 0.10532 | 0.0059302
MARTELL 110191216 | MARTE | MARTELL 1101 | STOCKTON | 41.3413 | 10.8803 | 100% | 3 | 13 | 100% | 0% | 0 | 0.10514 | 1 | 0.10514 | 0.0025432
MOUNTAIN QUARRIES 210192474 | MOUNT | MOUNTAIN QUARRIES 2101 | SIERRA | 14.6687 | 46.984 | 70.43% | 1 | 2 | 94.19% | 51.74% | 0 | 0.10478 | 1 | 0.10478 | 0.0071431
MONTE RIO 11135026 | MONTE | MONTE RIO 1113 | SONOMA | 1.8374 | 45.7535 | 31.21% | 4 | 1 | 100% | 100% | 0 | 0.1045 | 1 | 0.1045 | 0.056875
SANTA YNEZ 1101Y52 | SANTA | SANTA YNEZ 1101 | LOS PADRES | 18.8234 | 75.9887 | 74.53% | 0 | 5 | 76.28% | 53.44% | 1 | 0.10447 | 1 | 0.10447 | 0.0055501
COARSEGOLD 21045300 | COARS | COARSEGOLD 2104 | YOSEMITE | 37.3624 | 19.4525 | 89.47% | 1 | 28 | 100% | 0% | 0 | 0.10447 | 1 | 0.10447 | 0.0027962
PUEBLO 11041304 | PUEBL | PUEBLO 1104 | NORTH BAY | 19.9743 | 65.3191 | 45.92% | 2 | 4 | 100% | 0% | 0 | 0.10431 | 1 | 0.10431 | 0.0052223
AUBERRY 1101R2838 | AUBER | AUBERRY 1101 | FRESNO | 20.2113 | 19.1577 | 100% | 5 | 21 | 100% | 0% | 0 | 0.10363 | 1 | 0.10363 | 0.0051272
SAN LUIS OBISPO 1108V92 | SAN L | SAN LUIS OBISPO 1108 | LOS PADRES | 0.46755 | 10 | 74.28% | 0 | 0 | 6.559% | 0% | 0 | 0.0092193 | 11.2183 | 0.10343 | 0.22121
CLAYTON 2215CB | CLAYT | CLAYTON 2215 | DIABLO | 2.6028 | 67.9246 | 0.2184% | 0 | 2 | 23.77% | 0% | 0 | 0.0092153 | 11.2183 | 0.10338 | 0.039718
BANGOR 11011958 | BANGO | BANGOR 1101 | NORTH VALLEY | 33.6731 | 10.1792 | 87.16% | 3 | 30 | 100% | 0% | 0 | 0.10317 | 1 | 0.10317 | 0.0030639
CALAVERAS CEMENT 1101502 | CALAV | CALAVERAS CEMENT 1101 | STOCKTON | 38.3009 | 27.6645 | 90.32% | 2 | 8 | 92.84% | 0% | 0 | 0.10314 | 1 | 0.10314 | 0.0026928
CLARKSVILLE 2110CB | CLARK | CLARKSVILLE 2110 | SIERRA | 0.17765 | 10 | 0% | 0 | 0 | 9.133% | 0% | 0 | 0.005146 | 19.9979 | 0.10291 | 0.57927
CLARK ROAD 11022582 | CLARK | CLARK ROAD 1102 | NORTH VALLEY | 20.3761 | 33.4275 | 100% | 2 | 6 | 97.24% | 8.705% | 1 | 0.10279 | 1 | 0.10279 | 0.0050444
CALISTOGA 1102769230 | CALIS | CALISTOGA 1102 | NORTH BAY | 9.3152 | 56.0979 | 70.25% | 3 | 0 | 54.25% | 96.26% | 0 | 0.10199 | 1 | 0.10199 | 0.010949
CLAYTON 2212Y504R | CLAYT | CLAYTON 2212 | DIABLO | 11.7508 | 28.9647 | 42.97% | 1 | 6 | 100% | 29.53% | 1 | 0.10152 | 1 | 0.10152 | 0.0086391
RED BLUFF 11011556 | RED B | RED BLUFF 1101 | NORTH VALLEY | 35.2007 | 32.6588 | 100% | 1 | 11 | 88.02% | 0% | 0 | 0.10148 | 1 | 0.10148 | 0.0028828
CURTIS 170390320 | CURTI | CURTIS 1703 | YOSEMITE | 27.855 | 17.0394 | 100% | 4 | 21 | 100% | 0% | 0 | 0.10108 | 1 | 0.10108 | 0.0036288
RIO DELL 1102CB | RIO D | RIO DELL 1102 | HUMBOLDT | 0.14635 | 60 | 0% | 0 | 0 | 2.061% | 0% | 0 | 0.0067382 | 14.9507 | 0.10074 | 0.68834
DIAMOND SPRINGS 1103 | DIAMO | DIAMOND SPRINGS 1103 | SIERRA | 0.10469 | 10 | 100% | 0 | 0 | 70.96% | 100% | 0 | 0.10065 | 1 | 0.10065 | 0.96137
CEDAR CREEK 11011656 | CEDAR | CEDAR CREEK 1101 | NORTH VALLEY | 32.2585 | 60.8127 | 100% | 10 | 9 | 100% | 0% | 0 | 0.10049 | 1 | 0.10049 | 0.0031151
PETALUMA C 1109128 | PETAL | PETALUMA C 1109 | SONOMA | 20.216 | 67.8419 | 37.87% | 1 | 18 | 85.88% | 0% | 0 | 0.1003 | 1 | 0.1003 | 0.0049614
CAMP EVERS 210694770 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 2.6769 | 10 | 36.19% | 10 | 8 | 66.11% | 100% | 0 | 0.09995 | 1 | 0.09995 | 0.037339
CAMP EVERS 210410442 | CAMP | CAMP EVERS 2104 | CENTRAL COAST | 5.2532 | 33.0345 | 51.92% | 6 | 3 | 50.36% | 93.05% | 0 | 0.099232 | 1 | 0.099232 | 0.01889
VIEJO 22029118 | VIEJO | VIEJO 2202 | CENTRAL COAST | 0.57077 | 10 | 0.8969% | 1 | 0 | 19.02% | 0% | 0 | 0.0066199 | 14.9507 | 0.098972 | 0.1734
CALPINE 1144304 | CALPI | CALPINE 1144 | SONOMA | 0.046375 | 85 | 0% | 0 | 0 | 100% | 100% | 0 | 0.098754 | 1 | 0.098754 | 2.1295
BOLINAS 110137034 | BOLIN | BOLINAS 1101 | NORTH BAY | 4.5303 | 84.6023 | 6.363% | 1 | 1 | 100% | 94.68% | 0 | 0.098509 | 1 | 0.098509 | 0.021744
CENTERVILLE 11012592 | CENTE | CENTERVILLE 1101 | NORTH VALLEY | 6.3933 | 51.1304 | 7.659% | 2 | 0 | 100% | 100% | 0 | 0.098005 | 1 | 0.098005 | 0.015329
HALF MOON BAY 11018902 | HALF | HALF MOON BAY 1101 | PENINSULA | 14.8934 | 73.1287 | 41.51% | 11 | 3 | 82.58% | 40.17% | 0 | 0.097706 | 1 | 0.097706 | 0.0065604
KANAKA 11011406 | KANAK | KANAKA 1101 | NORTH VALLEY | 26.9635 | 16.7709 | 74.27% | 2 | 6 | 97.41% | 16.93% | 0 | 0.097652 | 1 | 0.097652 | 0.0036216
SILVERADO 2105616 | SILVE | SILVERADO 2105 | NORTH BAY | 7.7876 | 45.8077 | 54.02% | 4 | 6 | 42.79% | 95.93% | 0 | 0.097353 | 1 | 0.097353 | 0.012501
COTTONWOOD 11011610 | COTTO | COTTONWOOD 1101 | NORTH VALLEY | 38.431 | 59.7392 | 100% | 4 | 5 | 100% | 0% | 0 | 0.097181 | 1 | 0.097181 | 0.0025287
NEWBURG 11313446 | NEWBU | NEWBURG 1131 | HUMBOLDT | 0.24063 | 10 | 0% | 0 | 0 | 2.893% | 0% | 0 | 0.0048356 | 19.9979 | 0.096701 | 0.40187
CORRAL 11012128 | CORRA | CORRAL 1101 | STOCKTON | 0.10849 | 55.3351 | 0% | 0 | 0 | 0.5187% | 0% | 0 | 0.0064285 | 14.9507 | 0.09611 | 0.88593
BIG BASIN 110211062 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 9.0842 | 63.1207 | 47.86% | 15 | 1 | 100% | 69.62% | 1 | 0.096095 | 1 | 0.096095 | 0.010578
CURTIS 17026008 | CURTI | CURTIS 1702 | YOSEMITE | 17.4763 | 49.3908 | 89.43% | 4 | 7 | 100% | 47.18% | 0 | 0.095869 | 1 | 0.095869 | 0.0054857
BELLEVUE 1102392 | BELLE | BELLEVUE 1102 | SONOMA | 0.13708 | 10 | 0% | 0 | 0 | 2.019% | 0% | 0 | 0.0047936 | 19.9979 | 0.095862 | 0.69929
CAMP EVERS 21067603 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 0.9357 | 10 | 57.8% | 0 | 0 | 100% | 100% | 0 | 0.095589 | 1 | 0.095589 | 0.10216
AUBERRY 1102R2850 | AUBER | AUBERRY 1102 | FRESNO | 25.8464 | 30.8369 | 100% | 0 | 16 | 100% | 0% | 0 | 0.095456 | 1 | 0.095456 | 0.0036932
VACAVILLE 111112342 | VACAV | VACAVILLE 1111 | SACRAMENTO | 0.015645 | 10 | 0% | 0 | 0 | 1.482% | 0% | 0 | 0.004768 | 19.9979 | 0.095349 | 6.0946
SANTA ROSA A 1107CB | SANTA | SANTA ROSA A 1107 | SONOMA | 2.9541 | 10 | 71.96% | 6 | 3 | 60.44% | 100% | 0 | 0.095269 | 1 | 0.095269 | 0.03225
HIGHLANDS 110439458 | HIGHL | HIGHLANDS 1104 | HUMBOLDT | 0.83315 | 10 | 36.61% | 0 | 0 | 15.6% | 0% | 0 | 0.0084597 | 11.2183 | 0.094904 | 0.11391
FORT BRAGG A 110231304 | FORT | FORT BRAGG A 1102 | HUMBOLDT | 21.5206 | 61.6048 | 34.35% | 17 | 8 | 100% | 0% | 0 | 0.094856 | 1 | 0.094856 | 0.0044077
SAN RAFAEL 11081262 | SAN R | SAN RAFAEL 1108 | NORTH BAY | 4.0586 | 23.1286 | 14.29% | 3 | 8 | 91.28% | 100% | 0 | 0.094261 | 1 | 0.094261 | 0.023225
BRYANT 0402CB | BRYAN | BRYANT 0402 | DIABLO | 1.2282 | 10 | 3.772% | 0 | 5 | 15.75% | 0% | 0 | 0.0062931 | 14.9507 | 0.094086 | 0.076606
NARROWS 2105CB | NARRO | NARROWS 2105 | SIERRA | 35.605 | 11.8579 | 78.33% | 4 | 9 | 98.55% | 0% | 0 | 0.094041 | 1 | 0.094041 | 0.0026412
PARADISE 11032486 | PARAD | PARADISE 1103 | NORTH VALLEY | 6.2013 | 10 | 48.71% | 9 | 1 | 91.06% | 100% | 0 | 0.093491 | 1 | 0.093491 | 0.015076
FELTON 0401CB | FELTO | FELTON 0401 | CENTRAL COAST | 2.2987 | 17.6192 | 4.577% | 5 | 0 | 89.41% | 100% | 0 | 0.093336 | 1 | 0.093336 | 0.040603
APPLE HILL 2102186912 | APPLE | APPLE HILL 2102 | SIERRA | 48.9257 | 16.1646 | 100% | 9 | 3 | 96.19% | 0% | 0 | 0.093311 | 1 | 0.093311 | 0.0019072
DIAMOND SPRINGS 11039432 | DIAMO | DIAMOND SPRINGS 1103 | SIERRA | 17.0625 | 19.7634 | 81.43% | 3 | 12 | 84.57% | 8.24% | 1 | 0.093192 | 1 | 0.093192 | 0.0054618
CALPINE 1144276-G | CALPI | CALPINE 1144 | SONOMA | 0.014761 | 75 | 0% | 0 | 0 | 100% | 100% | 0 | 0.092831 | 1 | 0.092831 | 6.2887
TEMPLETON 2113A12 | TEMPL | TEMPLETON 2113 | LOS PADRES | 40.4505 | 77.6946 | 67.36% | 2 | 5 | 100% | 23.89% | 1 | 0.092809 | 1 | 0.092809 | 0.0022944
SEACLIFF 040112946 | SEACL | SEACLIFF 0401 | CENTRAL COAST | 2.6944 | 41.521 | 88.42% | 0 | 1 | 83.31% | 77.78% | 0 | 0.092179 | 1 | 0.092179 | 0.034211
CAMP EVERS 210512590 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 4.822 | 13.1146 | 60.2% | 9 | 1 | 87.03% | 85.9% | 0 | 0.091772 | 1 | 0.091772 | 0.019032
PINE GROVE 11023168 | PINE | PINE GROVE 1102 | STOCKTON | 30.4079 | 52.9502 | 87.84% | 3 | 16 | 100% | 16.23% | 0 | 0.091596 | 1 | 0.091596 | 0.0030122
BANGOR 110182350 | BANGO | BANGOR 1101 | NORTH VALLEY | 20.6431 | 13.6369 | 91.07% | 2 | 31 | 93.75% | 0% | 0 | 0.091535 | 1 | 0.091535 | 0.0044341
PLACERVILLE 111019582 | PLACE | PLACERVILLE 1110 | SIERRA | 22.4014 | 26.1615 | 63.31% | 2 | 22 | 100% | 0% | 0 | 0.091322 | 1 | 0.091322 | 0.0040766
CLOVERDALE 1102156 | CLOVE | CLOVERDALE 1102 | SONOMA | 6.0801 | 52.6986 | 63.14% | 2 | 11 | 52.14% | 81.66% | 0 | 0.091237 | 1 | 0.091237 | 0.015006
GOLDTREE 1107CB | GOLDT | GOLDTREE 1107 | LOS PADRES | 1.1277 | 39.1961 | 5.234% | 0 | 0 | 30.84% | 0% | 0 | 0.008131 | 11.2183 | 0.091216 | 0.080889
TEMPLETON 2111A66 | TEMPL | TEMPLETON 2111 | LOS PADRES | 33.7371 | 15.0206 | 78.96% | 12 | 6 | 100% | 0.9159% | 0 | 0.091159 | 1 | 0.091159 | 0.0027021
PAUL SWEET 21025291 | PAUL | PAUL SWEET 2102 | CENTRAL COAST | 3.3045 | 10 | 22.71% | 10 | 3 | 77.46% | 100% | 0 | 0.091104 | 1 | 0.091104 | 0.027569
WHITMORE 11011594 | WHITM | WHITMORE 1101 | NORTH VALLEY | 24.2582 | 53.3221 | 84.24% | 2 | 1 | 100% | 29.39% | 0 | 0.09099 | 1 | 0.09099 | 0.0037509
LOW GAP 11014086 | LOW G | LOW GAP 1101 | HUMBOLDT | 11.4979 | 83.0021 | 100% | 1 | 2 | 100% | 0% | 0 | 0.090624 | 1 | 0.090624 | 0.0078818
NEWBURG 11322074 | NEWBU | NEWBURG 1132 | HUMBOLDT | 1.2262 | 10 | 0% | 0 | 0 | 11.58% | 0% | 0 | 0.0060224 | 14.9507 | 0.090039 | 0.073428
CALAVERAS CEMENT 110180930 | CALAV | CALAVERAS CEMENT 1101 | STOCKTON | 18.4785 | 30.1878 | 99.81% | 1 | 6 | 100% | 0% | 0 | 0.089656 | 1 | 0.089656 | 0.0048519
SAN JUSTO 11014002 | SAN J | SAN JUSTO 1101 | CENTRAL COAST | 18.1183 | 71.0394 | 96.75% | 4 | 7 | 95.15% | 0% | 0 | 0.089593 | 1 | 0.089593 | 0.0049449
AUBERRY 1102CB | AUBER | AUBERRY 1102 | FRESNO | 34.5018 | 23.0923 | 82.62% | 0 | 22 | 100% | 0% | 0 | 0.089542 | 1 | 0.089542 | 0.0025953
KESWICK 11011588 | KESWI | KESWICK 1101 | NORTH VALLEY | 6.9485 | 28.4638 | 99.9% | 2 | 4 | 79.32% | 55.95% | 0 | 0.089394 | 1 | 0.089394 | 0.012865
PINE GROVE 11026080 | PINE | PINE GROVE 1102 | STOCKTON | 34.785 | 21.8457 | 100% | 6 | 11 | 100% | 0.6625% | 0 | 0.089074 | 1 | 0.089074 | 0.0025607
MOUNTAIN QUARRIES 21011130 | MOUNT | MOUNTAIN QUARRIES 2101 | SIERRA | 20.0304 | 57.0085 | 99.98% | 8 | 6 | 100% | 22.7% | 1 | 0.088009 | 1 | 0.088009 | 0.0043938
PARADISE 110317711 | PARAD | PARADISE 1103 | NORTH VALLEY | 6.5808 | 11.9806 | 85.8% | 3 | 1 | 100% | 51.08% | 0 | 0.087993 | 1 | 0.087993 | 0.013371
OAKHURST 11035732 | OAKHU | OAKHURST 1103 | YOSEMITE | 3.391 | 10.7516 | 100% | 0 | 1 | 100% | 54.98% | 0 | 0.087919 | 1 | 0.087919 | 0.025927
CURTIS 170539256 | CURTI | CURTIS 1705 | YOSEMITE | 26.4541 | 14.8561 | 72.89% | 2 | 39 | 100% | 0% | 0 | 0.087881 | 1 | 0.087881 | 0.003322
GARBERVILLE 11011770 | GARBE | GARBERVILLE 1101 | HUMBOLDT | 8.6092 | 87.0246 | 95.86% | 7 | 3 | 100% | 0% | 0 | 0.087398 | 1 | 0.087398 | 0.010152
VOLTA 110293418 | VOLTA | VOLTA 1102 | NORTH VALLEY | 2.6513 | 65.9048 | 100% | 5 | 0 | 100% | 44.92% | 0 | 0.087226 | 1 | 0.087226 | 0.032899
FROGTOWN 170275252 | FROGT | FROGTOWN 1702 | STOCKTON | 57.5264 | 53.766 | 80.82% | 0 | 20 | 95.14% | 0% | 0 | 0.087181 | 1 | 0.087181 | 0.0015155
SANTA ROSA A 110464565 | SANTA | SANTA ROSA A 1104 | SONOMA | 0.80928 | 10 | 22.53% | 1 | 2 | 100% | 100% | 0 | 0.087105 | 1 | 0.087105 | 0.10763
HARRIS 1109700 | HARRI | HARRIS 1109 | HUMBOLDT | 13.0569 | 19.3799 | 29.7% | 17 | 20 | 44.54% | 0% | 0 | 0.086853 | 1 | 0.086853 | 0.0066519
OAKLAND K 1103CR188 | OAKLA | OAKLAND K 1103 | EAST BAY | 3.5811 | 10 | 48.05% | 3 | 7 | 100% | 62.42% | 0 | 0.086851 | 1 | 0.086851 | 0.024253
HOOPA 11013304 | HOOPA | HOOPA 1101 | HUMBOLDT | 16.9885 | 82.5702 | 98.71% | 15 | 4 | 100% | 0% | 0 | 0.086315 | 1 | 0.086315 | 0.0050808
HALSEY 1101CB | HALSE | HALSEY 1101 | SIERRA | 17.1561 | 10.5573 | 71.81% | 7 | 24 | 100% | 0% | 0 | 0.08631 | 1 | 0.08631 | 0.0050309
CURTIS 170510590 | CURTI | CURTIS 1705 | YOSEMITE | 9.8062 | 25.1511 | 99.51% | 1 | 1 | 100% | 47.11% | 0 | 0.086282 | 1 | 0.086282 | 0.0087987
GANSNER 11012006 | GANSN | GANSNER 1101 | NORTH VALLEY | 17.1959 | 52.9981 | 98.77% | 5 | 5 | 100% | 2.795% | 0 | 0.086274 | 1 | 0.086274 | 0.0050171
CAMP EVERS 210611006 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 2.073 | 10 | 22.12% | 2 | 1 | 100% | 100% | 0 | 0.086223 | 1 | 0.086223 | 0.041594
HOOPA 1101CB | HOOPA | HOOPA 1101 | HUMBOLDT | 15.2475 | 59.0191 | 97.73% | 17 | 6 | 56.28% | 0% | 0 | 0.085954 | 1 | 0.085954 | 0.0056373
KESWICK 11011586 | KESWI | KESWICK 1101 | NORTH VALLEY | 7.6307 | 36.5577 | 16.39% | 0 | 2 | 100% | 100% | 1 | 0.085854 | 1 | 0.085854 | 0.011251
DIAMOND SPRINGS 1103CB | DIAMO | DIAMOND SPRINGS 1103 | SIERRA | 16.7869 | 10 | 71.13% | 6 | 16 | 54.37% | 47.43% | 1 | 0.08564 | 1 | 0.08564 | 0.0051016
HIGGINS 1103CB | HIGGI | HIGGINS 1103 | SIERRA | 27.5586 | 18.1402 | 77.71% | 6 | 7 | 99.3% | 0% | 0 | 0.085581 | 1 | 0.085581 | 0.0031054
POINT ARENA 110137426 | POINT | POINT ARENA 1101 | HUMBOLDT | 0.081405 | 10 | 0% | 2 | 1 | 1.62% | 0% | 0 | 0.0057167 | 14.9507 | 0.085468 | 1.0499
ALTO 11252243 | ALTO | ALTO 1125 | NORTH BAY | 2.9262 | 21.9292 | 59.4% | 1 | 4 | 100% | 22.94% | 0 | 0.085029 | 1 | 0.085029 | 0.029058
BRUNSWICK 11062790 | BRUNS | BRUNSWICK 1106 | SIERRA | 8.9258 | 13.4181 | 98.75% | 0 | 3 | 81.13% | 52.78% | 0 | 0.084645 | 1 | 0.084645 | 0.0094832
VOLTA 11011516 | VOLTA | VOLTA 1101 | NORTH VALLEY | 25.7297 | 67.2634 | 100% | 4 | 8 | 100% | 0% | 0 | 0.084582 | 1 | 0.084582 | 0.0032873
GUALALA 111135562 | GUALA | GUALALA 1111 | HUMBOLDT | 14.2585 | 63.006 | 19.44% | 12 | 36 | 100% | 0% | 0 | 0.084547 | 1 | 0.084547 | 0.0059296
NARROWS 21022220 | NARRO | NARROWS 2102 | SIERRA | 27.523 | 12.681 | 87.5% | 7 | 17 | 97.87% | 0% | 0 | 0.084411 | 1 | 0.084411 | 0.0030669
EL DORADO PH 210163464 | EL DO | EL DORADO PH 2101 | SIERRA | 13.6531 | 63.9369 | 100% | 0 | 2 | 100% | 36.69% | 1 | 0.084238 | 1 | 0.084238 | 0.0061699
SWIFT 2110XR254 | SWIFT | SWIFT 2110 | SAN JOSE | 24.8145 | 55.7178 | 60.2% | 2 | 3 | 100% | 0% | 0 | 0.084233 | 1 | 0.084233 | 0.0033945
VASCO 1102MR176 | VASCO | VASCO 1102 | MISSION | 38.5569 | 70.5523 | 85.5% | 0 | 7 | 89.92% | 0% | 0 | 0.084198 | 1 | 0.084198 | 0.0021837
APPLE HILL 210277546 | APPLE | APPLE HILL 2102 | SIERRA | 43.2651 | 10.0567 | 100% | 8 | 8 | 100% | 3.986% | 0 | 0.084095 | 1 | 0.084095 | 0.0019437
CAMP EVERS 210311056 | CAMP | CAMP EVERS 2103 | CENTRAL COAST | 1.8179 | 16.722 | 18.6% | 7 | 3 | 97.69% | 100% | 0 | 0.083758 | 1 | 0.083758 | 0.046073
SAN RAFAEL 110839156 | SAN R | SAN RAFAEL 1108 | NORTH BAY | 3.0298 | 11.0786 | 11.96% | 3 | 10 | 63.16% | 96.57% | 0 | 0.083717 | 1 | 0.083717 | 0.027631
LOS GATOS 1106CB | LOS G | LOS GATOS 1106 | DE ANZA | 6.7095 | 14.253 | 23.95% | 2 | 3 | 87.56% | 91.62% | 0 | 0.083012 | 1 | 0.083012 | 0.012372
EL DORADO PH 210113532 | EL DO | EL DORADO PH 2101 | SIERRA | 5.3271 | 64.1847 | 100% | 5 | 1 | 100% | 0% | 0 | 0.082958 | 1 | 0.082958 | 0.015573
SANTA YNEZ 1101Y16 | SANTA | SANTA YNEZ 1101 | LOS PADRES | 7.1745 | 86.5871 | 96.55% | 0 | 1 | 49.62% | 51.9% | 0 | 0.082863 | 1 | 0.082863 | 0.01155
ANTLER 11011384 | ANTLE | ANTLER 1101 | NORTH VALLEY | 8.8576 | 10 | 98.19% | 3 | 9 | 97.22% | 0% | 0 | 0.08259 | 1 | 0.08259 | 0.0093242
CAMP EVERS 210355638 | CAMP | CAMP EVERS 2103 | CENTRAL COAST | 1.9801 | 10 | 57.05% | 1 | 0 | 56.59% | 100% | 0 | 0.082558 | 1 | 0.082558 | 0.041693
LOW GAP 11014160 | LOW G | LOW GAP 1101 | HUMBOLDT | 21.5735 | 61.654 | 100% | 10 | 5 | 99.51% | 0% | 0 | 0.082527 | 1 | 0.082527 | 0.0038254
BIG MEADOWS 21012246 | BIG M | BIG MEADOWS 2101 | NORTH VALLEY | 1.3711 | 10 | 100% | 1 | 20 | 75.1% | 0% | 0 | 0.082406 | 1 | 0.082406 | 0.060103
BOLINAS 1101504 | BOLIN | BOLINAS 1101 | NORTH BAY | 6.5349 | 26.1981 | 0% | 2 | 2 | 100% | 100% | 0 | 0.082308 | 1 | 0.082308 | 0.012595
CLOVERDALE 1102674 | CLOVE | CLOVERDALE 1102 | SONOMA | 17.0598 | 62.482 | 68.42% | 4 | 8 | 84.92% | 25.35% | 0 | 0.082178 | 1 | 0.082178 | 0.0048171
OCEANO 1102CB | OCEAN | OCEANO 1102 | LOS PADRES | 20.8775 | 11.5809 | 41.43% | 7 | 19 | 75.87% | 0% | 0 | 0.081976 | 1 | 0.081976 | 0.0039265
BUELLTON 1101Y36 | BUELL | BUELLTON 1101 | LOS PADRES | 33.0581 | 70.2256 | 71.54% | 1 | 11 | 92.67% | 5.931% | 1 | 0.081946 | 1 | 0.081946 | 0.0024788
BANGOR 11017446 | BANGO | BANGOR 1101 | NORTH VALLEY | 43.441 | 11.2625 | 85.83% | 3 | 18 | 100% | 0% | 0 | 0.081818 | 1 | 0.081818 | 0.0018834
GEYSERVILLE 110179788 | GEYSE | GEYSERVILLE 1101 | SONOMA | 36.3345 | 85.553 | 97.66% | 5 | 7 | 86.55% | 0% | 0 | 0.081783 | 1 | 0.081783 | 0.0022508
SHINGLE SPRINGS 210911092 | SHING | SHINGLE SPRINGS 2109 | SIERRA | 22.1149 | 21.1094 | 82.77% | 7 | 7 | 100% | 0% | 0 | 0.081649 | 1 | 0.081649 | 0.003692
PERRY 1101V78 | PERRY | PERRY 1101 | LOS PADRES | 29.478 | 56.2687 | 60.85% | 2 | 3 | 100% | 21.68% | 1 | 0.081321 | 1 | 0.081321 | 0.0027587
GARBERVILLE 11011750 | GARBE | GARBERVILLE 1101 | HUMBOLDT | 14.3678 | 85.1825 | 100% | 14 | 8 | 96.86% | 0% | 0 | 0.081262 | 1 | 0.081262 | 0.0056559
GANSNER 11012424 | GANSN | GANSNER 1101 | NORTH VALLEY | 18.9007 | 82.3071 | 77.09% | 4 | 10 | 100% | 0% | 0 | 0.081226 | 1 | 0.081226 | 0.0042975
MORGAN HILL 2111XR186 | MORGA | MORGAN HILL 2111 | SAN JOSE | 0.89677 | 65 | 0% | 0 | 0 | 5.591% | 0% | 0 | 0.0072203 | 11.2183 | 0.080999 | 0.090324
GRASS VALLEY 11032110 | GRASS | GRASS VALLEY 1103 | SIERRA | 19.6542 | 17.5047 | 70.11% | 3 | 10 | 97.43% | 0% | 0 | 0.080807 | 1 | 0.080807 | 0.0041114
MIRABEL 1102CB | MIRAB | MIRABEL 1102 | SONOMA | 4.5501 | 24.245 | 39.21% | 4 | 11 | 40.5% | 94.81% | 0 | 0.080685 | 1 | 0.080685 | 0.017733
SAND CREEK 11037110 | SAND | SAND CREEK 1103 | FRESNO | 19.4155 | 27.8259 | 94.86% | 5 | 7 | 100% | 0% | 0 | 0.080582 | 1 | 0.080582 | 0.0041504
LLAGAS 210740407 | LLAGA | LLAGAS 2107 | SAN JOSE | 4.4461 | 62.3794 | 79.11% | 0 | 0 | 69.99% | 65.8% | 1 | 0.080349 | 1 | 0.080349 | 0.018072
BUCKS CREEK 1101CB | BUCKS | BUCKS CREEK 1101 | NORTH VALLEY | 20.005 | 83.6146 | 6.119% | 5 | 12 | 100% | 23.08% | 0 | 0.080342 | 1 | 0.080342 | 0.0040161
CABRILLO 1104Y24 | CABRI | CABRILLO 1104 | LOS PADRES | 18.0747 | 69.8881 | 25.08% | 0 | 8 | 92.92% | 0% | 0 | 0.080321 | 1 | 0.080321 | 0.0044438
CALPELLA 1101600 | CALPE | CALPELLA 1101 | HUMBOLDT | 20.3203 | 63.0301 | 92.94% | 2 | 3 | 76.37% | 16.27% | 1 | 0.080296 | 1 | 0.080296 | 0.0039515
WEIMAR 11012740 | WEIMA | WEIMAR 1101 | SIERRA | 19.1962 | 52.0643 | 71.74% | 1 | 4 | 100% | 0% | 0 | 0.080042 | 1 | 0.080042 | 0.0041697
OILFIELDS 1103N44 | OILFI | OILFIELDS 1103 | CENTRAL COAST | 18.7718 | 55.8541 | 96.36% | 0 | 0 | 100% | 0% | 0 | 0.079917 | 1 | 0.079917 | 0.0042573
SHINGLE SPRINGS 1103CB | SHING | SHINGLE SPRINGS 1103 | SIERRA | 6.5783 | 25.7936 | 79.81% | 1 | 6 | 56.03% | 80.43% | 1 | 0.079857 | 1 | 0.079857 | 0.01214
GREEN VALLEY 210112824 | GREEN | GREEN VALLEY 2101 | CENTRAL COAST | 0.066956 | 70 | 0% | 0 | 0 | 0.5469% | 0% | 0 | 0.007104 | 11.2183 | 0.079695 | 1.1903
VOLTA 11021650 | VOLTA | VOLTA 1102 | NORTH VALLEY | 21.7066 | 54.4838 | 100% | 4 | 9 | 100% | 0% | 0 | 0.079578 | 1 | 0.079578 | 0.0036661
BUELLTON 1101Y06 | BUELL | BUELLTON 1101 | LOS PADRES | 29.0172 | 49.4932 | 60.5% | 0 | 10 | 72.26% | 0% | 0 | 0.079416 | 1 | 0.079416 | 0.0027369
TIVY VALLEY 1107584840 | TIVY | TIVY VALLEY 1107 | FRESNO | 44.9458 | 14.7533 | 99.99% | 0 | 18 | 100% | 0% | 0 | 0.079403 | 1 | 0.079403 | 0.0017666
PARADISE 11032558 | PARAD | PARADISE 1103 | NORTH VALLEY | 2.3505 | 10 | 33.28% | 3 | 2 | 78.43% | 100% | 0 | 0.079398 | 1 | 0.079398 | 0.033779
COARSEGOLD 210310820 | COARS | COARSEGOLD 2103 | YOSEMITE | 28.8124 | 11.1753 | 93.73% | 0 | 47 | 100% | 0% | 0 | 0.07927 | 1 | 0.07927 | 0.0027513
CAYUCOS 1102CB | CAYUC | CAYUCOS 1102 | LOS PADRES | 11.9239 | 72.3136 | 83.3% | 3 | 2 | 41.34% | 71.02% | 0 | 0.079048 | 1 | 0.079048 | 0.0066293
BERKELEY F 1105BR100 | BERKE | BERKELEY F 1105 | EAST BAY | 0.38346 | 10 | 26.17% | 0 | 2 | 14.66% | 0% | 0 | 0.0070264 | 11.2183 | 0.078824 | 0.20556
POTTER VALLEY P H 11051904 | POTTE | POTTER VALLEY P H 1105 | HUMBOLDT | 28.466 | 59.7756 | 95.28% | 1 | 23 | 70.74% | 17.93% | 1 | 0.078348 | 1 | 0.078348 | 0.0027523
MARIPOSA 210110070 | MARIP | MARIPOSA 2101 | YOSEMITE | 25.9306 | 26.9034 | 96.01% | 1 | 27 | 100% | 0% | 0 | 0.078332 | 1 | 0.078332 | 0.0030209
SHINGLE SPRINGS 2108CB | SHING | SHINGLE SPRINGS 2108 | SIERRA | 1.2634 | 35.9265 | 24.64% | 0 | 1 | 85.58% | 100% | 1 | 0.078196 | 1 | 0.078196 | 0.061891
GREENBRAE 11032371 | GREEN | GREENBRAE 1103 | NORTH BAY | 0.40055 | 47.8608 | 0% | 1 | 4 | 90.05% | 100% | 0 | 0.078151 | 1 | 0.078151 | 0.19511
SAND CREEK 110345190 | SAND | SAND CREEK 1103 | FRESNO | 36.6214 | 13.3834 | 99.51% | 0 | 5 | 100% | 0% | 0 | 0.078024 | 1 | 0.078024 | 0.0021306
HOOPA 11013290 | HOOPA | HOOPA 1101 | HUMBOLDT | 13.744 | 63.8622 | 97.01% | 10 | 15 | 100% | 0% | 0 | 0.077955 | 1 | 0.077955 | 0.005672
BOLINAS 1101CB | BOLIN | BOLINAS 1101 | NORTH BAY | 2.176 | 69.2661 | 1.123% | 3 | 1 | 100% | 77.9% | 0 | 0.077604 | 1 | 0.077604 | 0.035664
SHINGLE SPRINGS 210819762 | SHING | SHINGLE SPRINGS 2108 | SIERRA | 4.2221 | 28.8991 | 60.1% | 3 | 6 | 78.12% | 39.2% | 0 | 0.077593 | 1 | 0.077593 | 0.018378
TEMPLETON 2110R90 | TEMPL | TEMPLETON 2110 | LOS PADRES | 27.6614 | 57.9463 | 69.12% | 2 | 5 | 77.95% | 0% | 0 | 0.077528 | 1 | 0.077528 | 0.0028027
BUCKS CREEK 1102CB | BUCKS | BUCKS CREEK 1102 | NORTH VALLEY | 29.5609 | 73.8859 | 50.06% | 3 | 10 | 100% | 23.04% | 0 | 0.077422 | 1 | 0.077422 | 0.0026191
SAN RAFAEL 1107CB | SAN R | SAN RAFAEL 1107 | NORTH BAY | 4.2653 | 10 | 28.65% | 2 | 4 | 53.65% | 97.72% | 0 | 0.077391 | 1 | 0.077391 | 0.018144
PARADISE 110439216 | PARAD | PARADISE 1104 | NORTH VALLEY | 2.1396 | 10 | 44.98% | 1 | 0 | 59.38% | 100% | 0 | 0.07729 | 1 | 0.07729 | 0.036124
AUBERRY 1101R2578 | AUBER | AUBERRY 1101 | FRESNO | 46.349 | 12.9087 | 87.94% | 4 | 13 | 100% | 0% | 0 | 0.077203 | 1 | 0.077203 | 0.0016657
NARROWS 21057203 | NARRO | NARROWS 2105 | SIERRA | 17.8971 | 13.4012 | 99.97% | 2 | 5 | 95.78% | 0% | 0 | 0.077172 | 1 | 0.077172 | 0.004312
PENRYN 110651674 | PENRY | PENRYN 1106 | SIERRA | 0.99996 | 10 | 36.11% | 0 | 0 | 8.247% | 0% | 0 | 0.0068595 | 11.2183 | 0.076952 | 0.076955
SAN LUIS OBISPO 1107V58 | SAN L | SAN LUIS OBISPO 1107 | LOS PADRES | 0.84617 | 10 | 0% | 0 | 0 | 37.96% | 0% | 0 | 0.006858 | 11.2183 | 0.076935 | 0.090921
OREGON TRAIL 11031500 | OREGO | OREGON TRAIL 1103 | NORTH VALLEY | 24.8639 | 16.6581 | 98.22% | 2 | 4 | 96.57% | 0% | 0 | 0.076799 | 1 | 0.076799 | 0.0030888
CALAVERAS CEMENT 11014786 | CALAV | CALAVERAS CEMENT 1101 | STOCKTON | 18.0051 | 18.3515 | 89.75% | 0 | 8 | 100% | 55.25% | 1 | 0.076728 | 1 | 0.076728 | 0.0042615
MENLO 1102W80 | MENLO | MENLO 1102 | PENINSULA | 17.326 | 69.2206 | 62.7% | 1 | 9 | 91.54% | 1.485% | 1 | 0.076689 | 1 | 0.076689 | 0.0044262
PEORIA 17051834 | PEORI | PEORIA 1705 | YOSEMITE | 22.9121 | 21.3201 | 69.84% | 0 | 15 | 96.15% | 0% | 0 | 0.076648 | 1 | 0.076648 | 0.0033453
HIGGINS 110332120 | HIGGI | HIGGINS 1103 | SIERRA | 40.5815 | 16.4911 | 85.22% | 7 | 11 | 99.04% | 0% | 0 | 0.076505 | 1 | 0.076505 | 0.0018852
VOLTA 110180454 | VOLTA | VOLTA 1101 | NORTH VALLEY | 31.4882 | 39.839 | 95.78% | 4 | 1 | 97.71% | 0.9246% | 0 | 0.076439 | 1 | 0.076439 | 0.0024275
LUCERNE 110638632 | LUCER | LUCERNE 1106 | HUMBOLDT | 4.4543 | 54.342 | 100% | 6 | 8 | 95.13% | 0% | 0 | 0.076393 | 1 | 0.076393 | 0.01715
BIG BASIN 110212779 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 0.25335 | 10 | 27.94% | 0 | 0 | 100% | 100% | 0 | 0.076303 | 1 | 0.076303 | 0.30117
INDIAN FLAT 1104CB | INDIA | INDIAN FLAT 1104 | YOSEMITE | 12.7115 | 39.8985 | 69.22% | 2 | 12 | 100% | 0% | 0 | 0.075983 | 1 | 0.075983 | 0.0059775
ALTO 1124428 | ALTO | ALTO 1124 | NORTH BAY | 4.8403 | 17.2865 | 1.418% | 0 | 4 | 81.37% | 100% | 0 | 0.075976 | 1 | 0.075976 | 0.015696
TYLER 110585132 | TYLER | TYLER 1105 | NORTH VALLEY | 30.9692 | 56.9117 | 100% | 0 | 21 | 100% | 0% | 0 | 0.075876 | 1 | 0.075876 | 0.0024501
SHINGLE SPRINGS 210981390 | SHING | SHINGLE SPRINGS 2109 | SIERRA | 18.7493 | 21.0161 | 63.9% | 1 | 8 | 100% | 0% | 0 | 0.075764 | 1 | 0.075764 | 0.0040409
OILFIELDS 1103N48 | OILFI | OILFIELDS 1103 | CENTRAL COAST | 47.0468 | 56.1397 | 99.69% | 2 | 26 | 100% | 0% | 0 | 0.075176 | 1 | 0.075176 | 0.0015979
PHILO 1102920 | PHILO | PHILO 1102 | HUMBOLDT | 17.5582 | 57.0245 | 91.25% | 3 | 12 | 67.45% | 0% | 0 | 0.075007 | 1 | 0.075007 | 0.0042719
APPLE HILL 1103CB | APPLE | APPLE HILL 1103 | SIERRA | 27.6878 | 21.3856 | 62.7% | 5 | 24 | 82.6% | 2.955% | 0 | 0.074928 | 1 | 0.074928 | 0.0027062
SANTA ROSA A 110432180 | SANTA | SANTA ROSA A 1104 | SONOMA | 2.5189 | 19.7323 | 62.59% | 0 | 1 | 99.89% | 67.69% | 0 | 0.074867 | 1 | 0.074867 | 0.029723
WISHON 1101CB | WISHO | WISHON 1101 | YOSEMITE | 7.7822 | 34.1369 | 78.45% | 1 | 2 | 100% | 51.22% | 1 | 0.074616 | 1 | 0.074616 | 0.0095881
STELLING 111060080 | STELL | STELLING 1110 | DE ANZA | 9.1723 | 64.142 | 26.3% | 6 | 3 | 90.37% | 0% | 0 | 0.074583 | 1 | 0.074583 | 0.0081314
CALAVERAS CEMENT 11011419 | CALAV | CALAVERAS CEMENT 1101 | STOCKTON | 15.0795 | 14.8417 | 100% | 2 | 7 | 100% | 0% | 0 | 0.074427 | 1 | 0.074427 | 0.0049357
FORT SEWARD 11211602 | FORT | FORT SEWARD 1121 | HUMBOLDT | 18.3365 | 83.3472 | 100% | 8 | 9 | 80.72% | 0% | 0 | 0.074162 | 1 | 0.074162 | 0.0040445
ECHO SUMMIT 11012500 | ECHO | ECHO SUMMIT 1101 | (blank) | 2.8817 | 10 | 100% | 2 | 2 | 100% | 0% | 0 | 0.074119 | 1 | 0.074119 | 0.025721
RED BLUFF 11031702 | RED B | RED BLUFF 1103 | NORTH VALLEY | 15.929 | 23.8535 | 100% | 1 | 4 | 87.44% | 0% | 0 | 0.073954 | 1 | 0.073954 | 0.0046427
MORRO BAY 110247584 | MORRO | MORRO BAY 1102 | LOS PADRES | 8.6089 | 11.2458 | 21.08% | 1 | 2 | 89.3% | 46.55% | 1 | 0.073801 | 1 | 0.073801 | 0.0085726
WEST POINT 11021369 | WEST | WEST POINT 1102 | STOCKTON | 10.5051 | 72.1066 | 100% | 1 | 0 | 98.44% | 18.78% | 0 | 0.073587 | 1 | 0.073587 | 0.0070049
BEN LOMOND 040116010 | BEN L | BEN LOMOND 0401 | CENTRAL COAST | 1.6971 | 10 | 15.35% | 1 | 2 | 100% | 100% | 0 | 0.072945 | 1 | 0.072945 | 0.042981
PENRYN 1105CB | PENRY | PENRYN 1105 | SIERRA | 0.038025 | 10 | 0% | 0 | 0 | 3.678% | 0% | 0 | 0.0048736 | 14.9507 | 0.072863 | 1.9162
SONOMA 1105404 | SONOM | SONOMA 1105 | SONOMA | 12.3578 | 22.8821 | 50.06% | 1 | 16 | 68.86% | 37.07% | 0 | 0.072855 | 1 | 0.072855 | 0.0058955
VOLTA 11011568 | VOLTA | VOLTA 1101 | NORTH VALLEY | 23.0081 | 45.5317 | 55% | 0 | 5 | 100% | 29.05% | 0 | 0.072817 | 1 | 0.072817 | 0.0031648
OCEANO 1104Q06 | OCEAN | OCEANO 1104 | LOS PADRES | 12.4604 | 18.1576 | 68.47% | 10 | 12 | 100% | 0% | 0 | 0.07261 | 1 | 0.07261 | 0.0058273
ALHAMBRA 110582622 | ALHAM | ALHAMBRA 1105 | DIABLO | 25.9018 | 63.5576 | 53.56% | 4 | 18 | 100% | 1.973% | 1 | 0.072547 | 1 | 0.072547 | 0.0028008
SAN RAMON 2107CB | SAN R | SAN RAMON 2107 | MISSION | 0.08762 | 60 | 100% | 0 | 0 | 0.9683% | 100% | 0 | 0.072467 | 1 | 0.072467 | 0.82706
PHILO 1101CB | PHILO | PHILO 1101 | HUMBOLDT | 30.1647 | 49.3506 | 76.4% | 12 | 16 | 60.92% | 0% | 0 | 0.072449 | 1 | 0.072449 | 0.0024018
AUBERRY 1101R314 | AUBER | AUBERRY 1101 | FRESNO | 42.3727 | 21.0608 | 99.17% | 0 | 7 | 96.03% | 0% | 0 | 0.072346 | 1 | 0.072346 | 0.0017074
MOUNTAIN QUARRIES 21011346 | MOUNT | MOUNTAIN QUARRIES 2101 | SIERRA | 30.7365 | 10.3256 | 98.49% | 5 | 12 | 100% | 0% | 0 | 0.072232 | 1 | 0.072232 | 0.00235
VOLTA 11011640 | VOLTA | VOLTA 1101 | NORTH VALLEY | 10.4338 | 80.2423 | 83.4% | 1 | 4 | 100% | 0% | 0 | 0.072189 | 1 | 0.072189 | 0.0069187
COARSEGOLD 21045525 | COARS | COARSEGOLD 2104 | YOSEMITE | 13.0444 | 10.8034 | 99.82% | 2 | 45 | 100% | 0% | 0 | 0.072179 | 1 | 0.072179 | 0.0055333
DESCHUTES 11011580 | DESCH | DESCHUTES 1101 | NORTH VALLEY | 44.5215 | 20.6467 | 99.77% | 3 | 12 | 90.01% | 10.49% | 0 | 0.071696 | 1 | 0.071696 | 0.0016104
SAN BENITO 210488772 | SAN B | SAN BENITO 2104 | CENTRAL COAST | 23.9825 | 25.5059 | 54.82% | 18 | 5 | 55.63% | 0% | 0 | 0.071687 | 1 | 0.071687 | 0.0029892
HALSEY 11011704 | HALSE | HALSEY 1101 | SIERRA | 12.7864 | 10 | 79.44% | 4 | 15 | 96.8% | 0% | 0 | 0.071684 | 1 | 0.071684 | 0.0056063
UKIAH 1114408 | UKIAH | UKIAH 1114 | HUMBOLDT | 37.0058 | 66.3521 | 67.33% | 5 | 13 | 97.48% | 0% | 0 | 0.071452 | 1 | 0.071452 | 0.0019308
CENTERVILLE 1101CB | CENTE | CENTERVILLE 1101 | NORTH VALLEY | 0.015747 | 10 | 0% | 0 | 1 | 100% | 100% | 0 | 0.071117 | 1 | 0.071117 | 4.5161
LAYTONVILLE 1101402 | LAYTO | LAYTONVILLE 1101 | HUMBOLDT | 22.8392 | 79.1892 | 99.99% | 6 | 8 | 96.88% | 0% | 0 | 0.070954 | 1 | 0.070954 | 0.0031067
BRUNSWICK 110651484 | BRUNS | BRUNSWICK 1106 | SIERRA | 20.7709 | 48.7311 | 68.62% | 4 | 3 | 82.69% | 37.09% | 0 | 0.070762 | 1 | 0.070762 | 0.0034068
GREEN VALLEY 210190860 | GREEN | GREEN VALLEY 2101 | CENTRAL COAST | 3.8052 | 10 | 95.69% | 0 | 0 | 20.73% | 93.04% | 0 | 0.070746 | 1 | 0.070746 | 0.018592
WILDWOOD 11011576 | WILDW | WILDWOOD 1101 | NORTH VALLEY | 8.159 | 75.9447 | 99.97% | 1 | 4 | 100% | 0% | 0 | 0.070451 | 1 | 0.070451 | 0.0086347
GUALALA 111223444 | GUALA | GUALALA 1112 | HUMBOLDT | 14.5206 | 71.4539 | 16.53% | 7 | 15 | 100% | 0% | 0 | 0.069914 | 1 | 0.069914 | 0.0048148
SYCAMORE CREEK 11112014 | SYCAM | SYCAMORE CREEK 1111 | NORTH VALLEY | 22.6561 | 53.0217 | 99.04% | 1 | 4 | 99.97% | 25.97% | 0 | 0.069882 | 1 | 0.069882 | 0.0030845
PARADISE 11042470 | PARAD | PARADISE 1104 | NORTH VALLEY | 5.1264 | 10.5174 | 41.48% | 3 | 8 | 44.97% | 100% | 0 | 0.069868 | 1 | 0.069868 | 0.013629
BIG BASIN 11022253 | BIG B | BIG BASIN 1102 | CENTRAL COAST | 1.463 | 10 | 16.17% | 0 | 0 | 100% | 100% | 0 | 0.069736 | 1 | 0.069736 | 0.047668
FROGTOWN 170212282 | FROGT | FROGTOWN 1702 | STOCKTON | 36.3191 | 39.3074 | 54.5% | 2 | 7 | 100% | 0% | 0 | 0.069451 | 1 | 0.069451 | 0.0019122
ROB ROY 210410714 | ROB R | ROB ROY 2104 | CENTRAL COAST | 15.4812 | 20.2777 | 49.42% | 12 | 6 | 79.24% | 0% | 0 | 0.069343 | 1 | 0.069343 | 0.0044792
CURTIS 17036064 | CURTI | CURTIS 1703 | YOSEMITE | 19.198 | 23.357 | 96.92% | 3 | 15 | 97.54% | 0% | 0 | 0.069239 | 1 | 0.069239 | 0.0036066
PLACERVILLE 2106CB | PLACE | PLACERVILLE 2106 | SIERRA | 6.6569 | 17.5661 | 15.58% | 1 | 6 | 100% | 71.65% | 0 | 0.069168 | 1 | 0.069168 | 0.01039
OAKLAND K 1101CR178 | OAKLA | OAKLAND K 1101 | EAST BAY | 0.32942 | 10 | 9.622% | 0 | 2 | 100% | 100% | 0 | 0.068955 | 1 | 0.068955 | 0.20932
GIRVAN 1101323094 | GIRVA | GIRVAN 1101 | NORTH VALLEY | 36.2683 | 55.5247 | 99.98% | 1 | 3 | 100% | 0% | 0 | 0.068706 | 1 | 0.068706 | 0.0018944
PAUL SWEET 2109CB | PAUL | PAUL SWEET 2109 | CENTRAL COAST | 4.2704 | 10 | 67.66% | 4 | 1 | 34.14% | 43.22% | 0 | 0.068584 | 1 | 0.068584 | 0.01606
FORT BRAGG A 110235592 | FORT | FORT BRAGG A 1102 | HUMBOLDT | 13.0568 | 10.5094 | 9.263% | 19 | 29 | 100% | 0% | 0 | 0.068352 | 1 | 0.068352 | 0.0052349
HIGGINS 110950072 | HIGGI | HIGGINS 1109 | SIERRA | 42.3856 | 25.4799 | 92.02% | 2 | 15 | 100% | 0% | 0 | 0.068313 | 1 | 0.068313 | 0.0016117
HIGGINS 110950078 | HIGGI | HIGGINS 1109 | SIERRA | 48.4681 | 37.033 | 99.96% | 1 | 15 | 100% | 0% | 0 | 0.068168 | 1 | 0.068168 | 0.0014064
WOODACRE 1101CB | WOODA | WOODACRE 1101 | NORTH BAY | 2.7386 | 31.1084 | 27.17% | 14 | 8 | 96.75% | 56.15% | 0 | 0.068112 | 1 | 0.068112 | 0.024872
NARROWS 21052228 | NARRO | NARROWS 2105 | SIERRA | 20.4861 | 37.6865 | 94.14% | 3 | 11 | 96.44% | 0% | 0 | 0.06797 | 1 | 0.06797 | 0.0033178
MONROE 210765424 | MONRO | MONROE 2107 | SONOMA | 0.75479 | 10 | 100% | 0 | 0 | 14.79% | 100% | 0 | 0.067899 | 1 | 0.067899 | 0.089958
CEDAR CREEK 1101CB | CEDAR | CEDAR CREEK 1101 | NORTH VALLEY | 15.4651 | 37.802 | 95.68% | 0 | 0 | 100% | 38.1% | 1 | 0.067896 | 1 | 0.067896 | 0.0043903
FORT SEWARD 1122CB | FORT | FORT SEWARD 1122 | HUMBOLDT | 17.3427 | 75.2963 | 100% | 3 | 11 | 79.07% | 0% | 0 | 0.067846 | 1 | 0.067846 | 0.0039121
PAUL SWEET 210610424 | PAUL | PAUL SWEET 2106 | CENTRAL COAST | 5.7029 | 19.0788 | 48.59% | 2 | 1 | 80% | 79.15% | 0 | 0.067843 | 1 | 0.067843 | 0.011896
CEDAR CREEK 11011664 | CEDAR | CEDAR CREEK 1101 | NORTH VALLEY | 29.6947 | 28.7537 | 98.78% | 0 | 12 | 100% | 0% | 0 | 0.067598 | 1 | 0.067598 | 0.0022764
MONTICELLO 1101718 | MONTI | MONTICELLO 1101 | NORTH BAY | 26.9011 | 60.1825 | 63.96% | 4 | 11 | 90.43% | 0% | 0 | 0.067428 | 1 | 0.067428 | 0.0025065
OILFIELDS 110383158 | OILFI | OILFIELDS 1103 | CENTRAL COAST | 18.1787 | 60.504 | 100% | 0 | 4 | 93.79% | 0% | 0 | 0.067417 | 1 | 0.067417 | 0.0037086
OREGON TRAIL 11041634 | OREGO | OREGON TRAIL 1104 | NORTH VALLEY | 17.7143 | 33.9199 | 93.56% | 1 | 0 | 97.56% | 0% | 0 | 0.067366 | 1 | 0.067366 | 0.0038029
TASSAJARA 2104CB | TASSA | TASSAJARA 2104 | DIABLO | 0.10747 | 10 | 0% | 0 | 1 | 9.092% | 0% | 0 | 0.0059985 | 11.2183 | 0.067293 | 0.62615
SOBRANTE 1102L510R | SOBRA | SOBRANTE 1102 | DIABLO | 9.7593 | 10 | 23.81% | 5 | 6 | 100% | 0% | 0 | 0.067265 | 1 | 0.067265 | 0.0068924
FORT BRAGG A 1102956 | FORT | FORT BRAGG A 1102 | HUMBOLDT | 10.8506 | 10 | 43.99% | 19 | 14 | 88.12% | 0% | 0 | 0.067263 | 1 | 0.067263 | 0.006199
ATASCADERO 1101A50 | ATASC | ATASCADERO 1101 | LOS PADRES | 19.8065 | 10 | 78.19% | 4 | 9 | 94.43% | 5.217% | 1 | 0.066857 | 1 | 0.066857 | 0.0033755
COTATI 1103148 | COTAT | COTATI 1103 | SONOMA | 14.0913 | 49.2874 | 1.408% | 9 | 10 | 90.64% | 0% | 0 | 0.066855 | 1 | 0.066855 | 0.0047444
FORT BRAGG A 11014622 | FORT | FORT BRAGG A 1101 | HUMBOLDT | 13.4572 | 19.3216 | 4.804% | 12 | 12 | 100% | 0% | 0 | 0.066763 | 1 | 0.066763 | 0.0049611
OAKLAND K 1104CR206 | OAKLA | OAKLAND K 1104 | EAST BAY | 1.7925 | 10 | 7.751% | 0 | 1 | 100% | 100% | 0 | 0.066653 | 1 | 0.066653 | 0.037184
PARADISE 11031231 | PARAD | PARADISE 1103 | NORTH VALLEY | 2.541 | 10 | 17.59% | 3 | 2 | 90.53% | 96.98% | 0 | 0.066519 | 1 | 0.066519 | 0.026178
STILLWATER 1102CB | STILL | STILLWATER 1102 | NORTH VALLEY | 25.0709 | 15.0844 | 83.36% | 3 | 7 | 99.96% | 0% | 0 | 0.066396 | 1 | 0.066396 | 0.0026483
PAUL SWEET 210710986 | PAUL | PAUL SWEET 2107 | CENTRAL COAST | 10.6088 | 30.4341 | 52.14% | 3 | 2 | 53.14% | 44.56% | 0 | 0.066361 | 1 | 0.066361 | 0.0062552
MORGAN HILL 2111CB | MORGA | MORGAN HILL 2111 | SAN JOSE | 0.34374 | 10 | 12.74% | 0 | 0 | 12.6% | 0% | 0 | 0.0059141 | 11.2183 | 0.066347 | 0.19301
WEIMAR 11012084 | WEIMA | WEIMAR 1101 | SIERRA | 18.471 | 37.3973 | 99.11% | 2 | 13 | 100% | 0% | 0 | 0.066085 | 1 | 0.066085 | 0.0035777
ROB ROY 210571630 | ROB R | ROB ROY 2105 | CENTRAL COAST | 1.807 | 10 | 61.71% | 5 | 2 | 96.47% | 60.73% | 0 | 0.066075 | 1 | 0.066075 | 0.036566
SAN RAFAEL 11079532 | SAN R | SAN RAFAEL 1107 | NORTH BAY | 0.83024 | 10 | 59.24% | 0 | 0 | 45.34% | 100% | 0 | 0.066016 | 1 | 0.066016 | 0.079514
FROGTOWN 17011623 | FROGT | FROGTOWN 1701 | STOCKTON | 15.2549 | 27.6688 | 92.79% | 0 | 7 | 100% | 0% | 0 | 0.065843 | 1 | 0.065843 | 0.0043162
ELK CREEK 110137334 | ELK C | ELK CREEK 1101 | NORTH VALLEY | 9.7022 | 59.8583 | 100% | 0 | 0 | 100% | 0% | 0 | 0.065795 | 1 | 0.065795 | 0.0067815
COTTONWOOD 11031348 | COTTO | COTTONWOOD 1103 | NORTH VALLEY | 25.9721 | 33.8083 | 99.17% | 2 | 10 | 81.37% | 0% | 0 | 0.065681 | 1 | 0.065681 | 0.0025289
CURTIS 170411300 | CURTI | CURTIS 1704 | YOSEMITE | 3.6591 | 33.4299 | 41.14% | 0 | 2 | 100% | 62.71% | 0 | 0.065584 | 1 | 0.065584 | 0.017923
LAURELES 11116421 | LAURE | LAURELES 1111 | CENTRAL COAST | 1.7279 | 54.1809 | 100% | 1 | 1 | 100% | 0% | 0 | 0.065512 | 1 | 0.065512 | 0.037914
MONTICELLO 1101630 | MONTI | MONTICELLO 1101 | NORTH BAY | 17.6986 | 68.0589 | 26.54% | 2 | 4 | 90.07% | 0% | 0 | 0.065491 | 1 | 0.065491 | 0.0037004
DIAMOND SPRINGS 11062100 | DIAMO | DIAMOND SPRINGS 1106 | SIERRA | 38.9747 | 13.5244 | 95.18% | 3 | 8 | 100% | 0% | 0 | 0.064847 | 1 | 0.064847 | 0.0016638
OAKLAND K 1101CR346 | OAKLA | OAKLAND K 1101 | EAST BAY | 0.18736 | 10 | 0% | 1 | 2 | 100% | 100% | 0 | 0.064827 | 1 | 0.064827 | 0.34599
WILLITS 11032506 | WILLI | WILLITS 1103 | HUMBOLDT | 12.7779 | 67.5224 | 88.76% | 15 | 4 | 100% | 16.88% | 0 | 0.06476 | 1 | 0.06476 | 0.0050681
TEMPLETON 2113CB | TEMPL | TEMPLETON 2113 | LOS PADRES | 0.49234 | 10 | 22.58% | 0 | 0 | 1.889% | 0% | 0 | 0.0057624 | 11.2183 | 0.064645 | 0.1313
BANGOR 11011804 | BANGO | BANGOR 1101 | NORTH VALLEY | 42.8631 | 13.9127 | 93.17% | 8 | 9 | 100% | 3.48% | 0 | 0.064625 | 1 | 0.064625 | 0.0015077
PHILO 11021308 | PHILO | PHILO 1102 | HUMBOLDT | 31.8312 | 64.2643 | 100% | 9 | 11 | 100% | 0% | 0 | 0.06454 | 1 | 0.06454 | 0.0020276
LAYTONVILLE 110237586 | LAYTO | LAYTONVILLE 1102 | HUMBOLDT | 13.9719 | 83.5514 | 97.33% | 7 | 7 | 100% | 0% | 0 | 0.064508 | 1 | 0.064508 | 0.004617
SAN RAFAEL 11081210 | SAN R | SAN RAFAEL 1108 | NORTH BAY | 3.0269 | 13.7905 | 14.91% | 3 | 2 | 55.23% | 100% | 0 | 0.064455 | 1 | 0.064455 | 0.021294
PAUL SWEET 2105CB | PAUL | PAUL SWEET 2105 | CENTRAL COAST | 8.1216 | 24.934 | 34.71% | 10 | 1 | 52.4% | 90.68% | 0 | 0.064304 | 1 | 0.064304 | 0.0079176
SALT SPRINGS 21011232 | SALT | SALT SPRINGS 2101 | STOCKTON | 6.1779 | 10 | 100% | 4 | 2 | 68.77% | 0% | 0 | 0.064284 | 1 | 0.064284 | 0.010405
PANOCHE 11034008 | PANOC | PANOCHE 1103 | YOSEMITE | 35.3708 | 69.547 | 99.82% | 0 | 2 | 100% | 0% | 0 | 0.064167 | 1 | 0.064167 | 0.0018141
UKIAH 1111534 | UKIAH | UKIAH 1111 | HUMBOLDT | 18.7979 | 74.5032 | 100% | 2 | 4 | 89.62% | 0% | 0 | 0.064153 | 1 | 0.064153 | 0.0034128
DESCHUTES 11011654 | DESCH | DESCHUTES 1101 | NORTH VALLEY | 17.3592 | 41.2096 | 100% | 1 | 5 | 100% | 6.956% | 0 | 0.063997 | 1 | 0.063997 | 0.0036866
GARBERVILLE 11021510 | GARBE | GARBERVILLE 1102 | HUMBOLDT | 13.0211 | 67.6864 | 30.88% | 5 | 7 | 100% | 0% | 0 | 0.063582 | 1 | 0.063582 | 0.004883
DEL MONTE 21043088 | DEL M | DEL MONTE 2104 | CENTRAL COAST | 15.4442 | 31.6262 | 48.83% | 2 | 7 | 100% | 0% | 0 | 0.063303 | 1 | 0.063303 | 0.0040988
HALF MOON BAY 110148868 | HALF | HALF MOON BAY 1101 | PENINSULA | 1.1515 | 26.9273 | 98.35% | 0 | 1 | 38.91% | 72.96% | 0 | 0.06326 | 1 | 0.06326 | 0.054936
CURTIS 17058170 | CURTI | CURTIS 1705 | YOSEMITE | 7.5122 | 10 | 100% | 1 | 19 | 95.23% | 28.76% | 0 | 0.063226 | 1 | 0.063226 | 0.0084165
CURTIS 17039240 | CURTI | CURTIS 1703 | YOSEMITE | 10.9351 | 23.2344 | 88.01% | 0 | 12 | 100% | 3.336% | 0 | 0.063182 | 1 | 0.063182 | 0.0057779
GRAYS FLAT 0401CB | GRAYS | GRAYS FLAT 0401 | NORTH VALLEY | 10.7057 | 82.9815 | 68.42% | 5 | 6 | 100% | 0% | 0 | 0.063148 | 1 | 0.063148 | 0.0058985
CLARKSVILLE 210951744 | CLARK | CLARKSVILLE 2109 | SIERRA | 0.69986 | 10 | 100% | 0 | 1 | 39% | 87.04% | 0 | 0.062946 | 1 | 0.062946 | 0.089941
EL CERRITO G 111257953 | EL CE | EL CERRITO G 1112 | EAST BAY | 0.7567 | 10 | 0% | 0 | 1 | 100% | 100% | 0 | 0.062783 | 1 | 0.062783 | 0.08297
LOW GAP 110137498 | LOW G | LOW GAP 1101 | HUMBOLDT | 16.1307 | 72.1022 | 98.67% | 6 | 3 | 100% | 0% | 0 | 0.062673 | 1 | 0.062673 | 0.0038853
CAMP EVERS 210611044 | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 6.5538 | 10.6438 | 23.66% | 12 | 2 | 52.73% | 81.08% | 0 | 0.062668 | 1 | 0.062668 | 0.0095621
NOTRE DAME 11042537 | NOTRE | NOTRE DAME 1104 | NORTH VALLEY | 5.2925 | 55.6781 | 100% | 0 | 0 | 100% | 22.56% | 0 | 0.062104 | 1 | 0.062104 | 0.011734
SAN RAFAEL 1101494 | SAN R | SAN RAFAEL 1101 | NORTH BAY | 4.1663 | 10 | 20.21% | 1 | 4 | 47.93% | 100% | 0 | 0.062096 | 1 | 0.062096 | 0.014904
TEMPLETON 2110N32 | TEMPL | TEMPLETON 2110 | LOS PADRES | 28.0596 | 53.4927 | 95.78% | 1 | 9 | 94.62% | 0% | 0 | 0.061984 | 1 | 0.061984 | 0.002209
ARCATA 11225384 | ARCAT | ARCATA 1122 | HUMBOLDT | 15.2841 | 39.9172 | 40.09% | 14 | 5 | 87.62% | 0% | 0 | 0.061973 | 1 | 0.061973 | 0.0040547
SAN RAFAEL 1101CB | SAN R | SAN RAFAEL 1101 | NORTH BAY | 1.7156 | 10 | 28.81% | 3 | 3 | 39.77% | 100% | 1 | 0.061788 | 1 | 0.061788 | 0.036015
BEN LOMOND 04015400 | BEN L | BEN LOMOND 0401 | CENTRAL COAST | 0.44316 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 0.061559 | 0.13891
OAKLAND X 1104CR101 | OAKLA | OAKLAND X 1104 | EAST BAY | 0.017651 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 0.061559 | 3.4876
SAN RAFAEL 11073323 | SAN R | SAN RAFAEL 1107 | NORTH BAY | 0.13349 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 0.061559 | 0.46114
CAMP EVERS 210595050 | CAMP | CAMP EVERS 2105 | CENTRAL COAST | 0.13882 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 0.061559 | 0.44346
CASTRO VALLEY 1108 | CASTR | CASTRO VALLEY 1108 | MISSION | 0.019583 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 0.061559 | 3.1436
BOLINAS 1101 | BOLIN | BOLINAS 1101 | NORTH BAY | 0.01843 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 0.061559 | 3.3402
CURTIS 170511790 | CURTI | CURTIS 1705 | YOSEMITE | 0.014226 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 0.061559 | 4.3273
KESWICK 1101CB | KESWI | KESWICK 1101 | NORTH VALLEY | 0.016582 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 0.061559 | 3.7124
CALISTOGA 1101 | CALIS | CALISTOGA 1101 | NORTH BAY | 0.0027683 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 0.061559 | 22.2374
BIG RIVER 110179628 | BIG R | BIG RIVER 1101 | HUMBOLDT | 14.7546 | 28.3298 | 27.17% | 16 | 19 | 100% | 0% | 0 | 0.06147 | 1 | 0.06147 | 0.0041661
CAMP EVERS 2103CB | CAMP | CAMP EVERS 2103 | CENTRAL COAST | 0.092755 | 10 | 13.07% | 0 | 0 | 75.74% | 100% | 0 | 0.061458 | 1 | 0.061458 | 0.66258
BOLINAS 1101528 | BOLIN | BOLINAS 1101 | NORTH BAY | 2.2652 | 10 | 0% | 1 | 5 | 74.53% | 100% | 0 | 0.061356 | 1 | 0.061356 | 0.027087
CALAVERAS CEMENT 1101585 | CALAV | CALAVERAS CEMENT 1101 | STOCKTON | 14.1114 | 60.1241 | 100% | 0 | 9 | 100% | 0% | 0 | 0.061249 | 1 | 0.061249 | 0.0043404
WILDWOOD 110185112 | WILDW | WILDWOOD 1101 | NORTH VALLEY | 6.7175 | 80.7667 | 100% | 4 | 6 | 100% | 0% | 0 | 0.061113 | 1 | 0.061113 | 0.0090976
SHINGLE SPRINGS 210985766 | SHING | SHINGLE SPRINGS 2109 | SIERRA | 18.4459 | 50.1321 | 99.71% | 3 | 4 | 100% | 0% | 0 | 0.06111 | 1 | 0.06111 | 0.0033129
FRUITLAND 114263170 | FRUIT | FRUITLAND 1142 | HUMBOLDT | 12.2406 | 74.2009 | 74.01% | 12 | 5 | 90.64% | 0% | 0 | 0.061047 | 1 | 0.061047 | 0.0049873
SAN RAFAEL 1107714160 | SAN R | SAN RAFAEL 1107 | NORTH BAY | 2.7558 | 15.5208 | 10.99% | 0 | 10 | 98.34% | 63.23% | 0 | 0.060966 | 1 | 0.060966 | 0.022122
OAKHURST 11016220 | OAKHU | OAKHURST 1101 | YOSEMITE | 20.9199 | 34.4609 | 88.69% | 0 | 15 | 100% | 0% | 0 | 0.060711 | 1 | 0.060711 | 0.0029021
SISQUOC 1103M98 | SISQU | SISQUOC 1103 | LOS PADRES | 6.4595 | 29.4274 | 100% | 0 | 1 | 65.51% | 60.21% | 1 | 0.060705 | 1 | 0.060705 | 0.0093978
FROGTOWN 170291134 | FROGT | FROGTOWN 1702 | STOCKTON | 14.7309 | 23.5525 | 81.54% | 0 | 12 | 92.7% | 0% | 0 | 0.060562 | 1 | 0.060562 | 0.0041112
DIAMOND SPRINGS 110610587 | DIAMO | DIAMOND SPRINGS 1106 | SIERRA | 21.9902 | 32.7231 | 99.97% | 4 | 2 | 100% | 0% | 0 | 0.060422 | 1 | 0.060422 | 0.0027477
GREENBRAE 11031260 | GREEN | GREENBRAE 1103 | NORTH BAY | 2.3256 | 16.3667 | 42.46% | 2 | 2 | 86.56% | 70.2% | 0 | 0.060164 | 1 | 0.060164 | 0.025871
PHILO 110137222 | PHILO | PHILO 1101 | HUMBOLDT | 25.4322 | 53.3862 | 64.87% | 9 | 12 | 100% | 0% | 0 | 0.060092 | 1 | 0.060092 | 0.0023628
DOBBINS 11015202 | DOBBI | DOBBINS 1101 | SIERRA | 15.7094 | 33.0821 | 86.66% | 1 | 6 | 92.01% | 0% | 0 | 0.059877 | 1 | 0.059877 | 0.0038115
MAPLE CREEK 1101CB | MAPLE | MAPLE CREEK 1101 | HUMBOLDT | 9.8748 | 78.7819 | 78.72% | 13 | 5 | 66.88% | 0% | 0 | 0.059846 | 1 | 0.059846 | 0.0060604
WYANDOTTE 11071510 | WYAND | WYANDOTTE 1107 | NORTH VALLEY | 25.4968 | 11.1229 | 100% | 1 | 4 | 100% | 0% | 0 | 0.05976 | 1 | 0.05976 | 0.0023438
HATTON 11019220 | HATTO | HATTON 1101 | CENTRAL COAST | 2.6965 | 89.4573 | 0% | 1 | 3 | 100% | 51.79% | 0 | 0.059721 | 1 | 0.059721 | 0.022148
CLOVERDALE 11024646 | CLOVE | CLOVERDALE 1102 | SONOMA | 14.4526 | 74.9071 | 80.61% | 2 | 4 | 97.6% | 0% | 0 | 0.059667 | 1 | 0.059667 | 0.0041285
DIAMOND SPRINGS 1104CB | DIAMO | DIAMOND SPRINGS 1104 | SIERRA | 6.9541 | 10 | 49.56% | 0 | 3 | 69.41% | 79.56% | 0 | 0.059614 | 1 | 0.059614 | 0.0085725
EL CERRITO G 1105BR160 | EL CE | EL CERRITO G 1105 | EAST BAY | 7.9453 | 33.1195 | 38.34% | 5 | 6 | 69.23% | 42.93% | 0 | 0.059441 | 1 | 0.059441 | 0.0074812
MIDDLETOWN 1103830 | MIDDL | MIDDLETOWN 1103 | HUMBOLDT | 23.5041 | 79 | 88.01% | 1 | 2 | 60.51% | 36.87% | 0 | 0.059437 | 1 | 0.059437 | 0.0025288
VOLTA 1101CB | VOLTA | VOLTA 1101 | NORTH VALLEY | 9.2068 | 22.5796 | 72.56% | 6 | 5 | 100% | 27.96% | 0 | 0.059425 | 1 | 0.059425 | 0.0064544
PUEBLO 2102656 | PUEBL | PUEBLO 2102 | NORTH BAY | 0.064775 | 10 | 100% | 0 | 0 | 0.3672% | 100% | 0 | 0.059306 | 1 | 0.059306 | 0.91557
MC KEE 1111711900 | MC KE | MC KEE 1111 | SAN JOSE | 8.3733 | 57.1059 | 68.22% | 0 | 5 | 66.5% | 0% | 0 | 0.059287 | 1 | 0.059287 | 0.0070804
LAURELES 111268454 | LAURE | LAURELES 1112 | CENTRAL COAST | 8.3342 | 11.1816 | 20.6% | 3 | 7 | 75.56% | 0% | 0 | 0.059265 | 1 | 0.059265 | 0.007111
CLAY 110113442 | CLAY | CLAY 1101 | STOCKTON | 25.1981 | 33.4611 | 98.28% | 1 | 6 | 81.01% | 0% | 0 | 0.059218 | 1 | 0.059218 | 0.0023501
FROGTOWN 1702290609 | FROGT | FROGTOWN 1702 | STOCKTON | 18.0385 | 28.1983 | 98.5% | 3 | 10 | 100% | 0% | 0 | 0.059181 | 1 | 0.059181 | 0.0032808
BELL 11082202 | BELL | BELL 1108 | SIERRA | 31.9475 | 20.6823 | 70.59% | 0 | 8 | 96.19% | 0% | 0 | 0.059129 | 1 | 0.059129 | 0.0018508
CAMP EVERS 21035402 | CAMP | CAMP EVERS 2103 | CENTRAL COAST | 2.8538 | 10 | 29.07% | 11 | 2 | 42.31% | 90.21% | 0 | 0.05912 | 1 | 0.05912 | 0.020716
WILLOW CREEK 11033090 | WILLO | WILLOW CREEK 1103 | HUMBOLDT | 10.7823 | 82.4459 | 100% | 5 | 3 | 100% | 0% | 0 | 0.058956 | 1 | 0.058956 | 0.0054678
POTTER VALLEY P H 110576498 | POTTE | POTTER VALLEY P H 1105 | HUMBOLDT | 14.8769 | 81.1366 | 60.61% | 2 | 8 | 100% | 0% | 0 | 0.058866 | 1 | 0.058866 | 0.0039569
HICKS 2103LB50 | HICKS | HICKS 2103 | SAN JOSE | 10.8958 | 72.4633 | 80.45% | 3 | 2 | 82.11% | 27.73% | 0 | 0.058713 | 1 | 0.058713 | 0.0053886
BIG RIVER 11013002 | BIG R | BIG RIVER 1101 | HUMBOLDT | 6.8985 | 10 | 4.337% | 11 | 17 | 83.84% | 0% | 0 | 0.058669 | 1 | 0.058669 | 0.0085046
MOUNTAIN QUARRIES 21011350 | MOUNT | MOUNTAIN QUARRIES 2101 | SIERRA | 21.7386 | 30.8372 | 63.86% | 7 | 7 | 100% | 0% | 0 | 0.058591 | 1 | 0.058591 | 0.0026952
ATASCADERO 1103A14 | ATASC | ATASCADERO 1103 | LOS PADRES | 25.1166 | 61.0387 | 72.56% | 0 | 2 | 99.83% | 36.1% | 0 | 0.058565 | 1 | 0.058565 | 0.0023317
CURTIS 170234426 | CURTI | CURTIS 1702 | YOSEMITE | 4.917 | 10 | 82.09% | 0 | 4 | 71.87% | 67.24% | 1 | 0.058493 | 1 | 0.058493 | 0.011896
CALPELLA 1101542 | CALPE | CALPELLA 1101 | HUMBOLDT | 23.4567 | 35.4534 | 89.83% | 1 | 18 | 100% | 0% | 0 | 0.058405 | 1 | 0.058405 | 0.0024899
KING CITY 11037038 | KING | KING CITY 1103 | CENTRAL COAST | 17.5881 | 72.8479 | 99.95% | 0 | 5 | 81.26% | 0% | 0 | 0.058354 | 1 | 0.058354 | 0.0033178
SONOMA 1106CB | SONOM | SONOMA 1106 | SONOMA | 0.46405 | 10 | 100% | 0 | 0 | 11.88% | 100% | 0 | 0.058298 | 1 | 0.058298 | 0.12563
ANTLER 11011378 | ANTLE | ANTLER 1101 | NORTH VALLEY | 23.3437 | 22.2502 | 87.11% | 6 | 14 | 92.94% | 12.19% | 1 | 0.058255 | 1 | 0.058255 | 0.0024955
PHILO 1102928 | PHILO | PHILO 1102 | HUMBOLDT | 13.0575 | 61.4578 | 77.17% | 8 | 4 | 85.6% | 0% | 0 | 0.058135 | 1 | 0.058135 | 0.0044522
EL DORADO PH 210152456 | EL DO | EL DORADO PH 2101 | SIERRA | 10.1963 | 62.6198 | 100% | 3 | 10 | 100% | 0% | 0 | 0.058118 | 1 | 0.058118 | 0.0056999
OILFIELDS 1103N62 | OILFI | OILFIELDS 1103 | CENTRAL COAST | 5.5689 | 75.4181 | 98.3% | 0 | 2 | 100% | 0% | 0 | 0.05809 | 1 | 0.05809 | 0.010431
FRUITLAND 11426054 | FRUIT | FRUITLAND 1142 | HUMBOLDT | 10.4759 | 81.7883 | 49.67% | 26 | 9 | 100% | 0% | 0 | 0.058078 | 1 | 0.058078 | 0.005544
MILPITAS 1109XR082 | MILPI | MILPITAS 1109 | SAN JOSE | 19.1832 | 53.2607 | 99.6% | 3 | 3 | 94.55% | 0% | 0 | 0.058023 | 1 | 0.058023 | 0.0030247
DUNLAP 11037170 | DUNLA | DUNLAP 1103 | FRESNO | 5.3633 | 51.4528 | 91.12% | 7 | 8 | 100% | 0% | 0 | 0.057836 | 1 | 0.057836 | 0.010784
PAUL SWEET 2106CB | PAUL | PAUL SWEET 2106 | CENTRAL COAST | 5.2267 | 14.0145 | 33.08% | 1 | 5 | 37.05% | 92.49% | 0 | 0.057775 | 1 | 0.057775 | 0.011054
GREEN VALLEY 210136820 | GREEN | GREEN VALLEY 2101 | CENTRAL COAST | 6.5982 | 36.5973 | 46.31% | 12 | 2 | 35.52% | 88.5% | 0 | 0.057708 | 1 | 0.057708 | 0.008746
DEL MONTE 21042624 | DEL M | DEL MONTE 2104 | CENTRAL COAST | 18.1708 | 31.8719 | 33.21% | 2 | 17 | 94.85% | 0% | 0 | 0.05749 | 1 | 0.05749 | 0.0031638
LOS OSITOS 21033010 | LOS O | LOS OSITOS 2103 | CENTRAL COAST | 30.8565 | 64.7553 | 97.74% | 3 | 10 | 99.12% | 0% | 0 | 0.057419 | 1 | 0.057419 | 0.0018608
GRASS VALLEY 11031700 | GRASS | GRASS VALLEY 1103 | SIERRA | 21.5982 | 19.8547 | 93.5% | 3 | 7 | 99.55% | 0% | 0 | 0.057412 | 1 | 0.057412 | 0.0026582
FRENCH GULCH 11022902 | FRENC | FRENCH GULCH 1102 | NORTH VALLEY | 6.9875 | 84.5854 | 100% | 0 | 4 | 100% | 0% | 0 | 0.057283 | 1 | 0.057283 | 0.0081979
BELL 11082226 | BELL | BELL 1108 | SIERRA | 24.7638 | 11.2765 | 87.34% | 1 | 8 | 97.2% | 0% | 0 | 0.057141 | 1 | 0.057141 | 0.0023074
SOBRANTE 1102L520R | SOBRA | SOBRANTE 1102 | DIABLO | 7.4675 | 10 | 48.68% | 1 | 16 | 100% | 8.05% | 0 | 0.05711 | 1 | 0.05711 | 0.0076478
ROSSMOOR 1106CB | ROSSM | ROSSMOOR 1106 | DIABLO | 1.4865 | 10 | 68.08% | 0 | 8 | 30.91% | 92.75% | 0 | 0.057048 | 1 | 0.057048 | 0.038377
SOBRANTE 1103N510R | SOBRA | SOBRANTE 1103 | DIABLO | 0.050894 | 10 | 0% | 1 | 0 | 5.822% | 0% | 0 | 0.0050449 | 11.2183 | 0.056595 | 1.112
LAKEWOOD 210964992 | LAKEW | LAKEWOOD 2109 | DIABLO | 0.21818 | 10 | 100% | 0 | 0 | 8.548% | 100% | 0 | 0.056493 | 1 | 0.056493 | 0.25892
SANTA ROSA A 110439786 | SANTA | SANTA ROSA A 1104 | SONOMA | 1.14 | 10 | 49.93% | 0 | 3 | 16.83% | 100% | 0 | 0.056488 | 1 | 0.056488 | 0.049552
CURTIS 170247488 | CURTI | CURTIS 1702 | YOSEMITE | 18.0809 | 16.9513 | 84.37% | 2 | 17 | 87.6% | 0% | 0 | 0.05643 | 1 | 0.05643 | 0.003121
COARSEGOLD 2103CB | COARS | COARSEGOLD 2103 | YOSEMITE | 38.4222 | 32.3373 | 83.55% | 1 | 26 | 100% | 0% | 0 | 0.056308 | 1 | 0.056308 | 0.0014655
SAN RAFAEL 11081457 | SAN R | SAN RAFAEL 1108 | NORTH BAY | 0.58979 | 10 | 0% | 0 | 0 | 77.17% | 100% | 0 | 0.056282 | 1 | 0.056282 | 0.095427
SALT SPRINGS 21011216 | SALT | SALT SPRINGS 2101 | STOCKTON | 5.4385 | 73.7435 | 99.91% | 0 | 1 | 98.38% | 0% | 0 | 0.056184 | 1 | 0.056184 | 0.010331
RACETRACK 1703CB | RACET | RACETRACK 1703 | YOSEMITE | 15.5569 | 10 | 47.8% | 4 | 26 | 86.61% | 0% | 0 | 0.05588 | 1 | 0.05588 | 0.003592
ANNAPOLIS 110176842 | ANNAP | ANNAPOLIS 1101 | HUMBOLDT | 5.647 | 81.667 | 98.52% | 2 | 3 | 100% | 0% | 0 | 0.055858 | 1 | 0.055858 | 0.0098917
AUBERRY 110137536 | AUBER | AUBERRY 1101 | FRESNO | 5.4818 | 31.3295 | 100% | 3 | 2 | 100% | 20.77% | 1 | 0.055781 | 1 | 0.055781 | 0.010176
OAKLAND K 1101CR170 | OAKLA | OAKLAND K 1101 | EAST BAY | 1.2514 | 10 | 10.22% | 0 | 3 | 100% | 84.34% | 0 | 0.055611 | 1 | 0.055611 | 0.044438
PALMER 110198478 | PALME | PALMER 1101 | LOS PADRES | 4.9874 | 64.4051 | 90.52% | 0 | 0 | 100% | 0% | 0 | 0.05552 | 1 | 0.05552 | 0.011132
CURTIS 17029220 | CURTI | CURTIS 1702 | YOSEMITE | 11.0663 | 17.9965 | 77.35% | 2 | 13 | 99.21% | 0.02567% | 0 | 0.05548 | 1 | 0.05548 | 0.0050134
RINCON 1101576 | RINCO | RINCON 1101 | SONOMA | 2.0608 | 10 | 77.6% | 0 | 6 | 19.69% | 79.16% | 0 | 0.055451 | 1 | 0.055451 | 0.026908
CALAVERAS CEMENT 110147968 | CALAV | CALAVERAS CEMENT 1101 | STOCKTON | 17.4467 | 25.9867 | 99.97% | 0 | 4 | 100% | 6.1% | 1 | 0.055443 | 1 | 0.055443 | 0.0031779
APPLE HILL 110313312 | APPLE | APPLE HILL 1103 | SIERRA | 11.1165 | 24.9201 | 69.91% | 1 | 7 | 61.36% | 40.78% | 0 | 0.055379 | 1 | 0.055379 | 0.0049816
FULTON 110746958 | FULTO | FULTON 1107 | SONOMA | 0.032131 | 10 | 100% | 0 | 0 | 6.208% | 100% | 0 | 0.055255 | 1 | 0.055255 | 1.7197
NORTH TOWER 2101CB | NORTH | NORTH TOWER 2101 | NORTH BAY | 0.18972 | 10 | 0% | 0 | 0 | 4.663% | 0% | 0 | 0.0049217 | 11.2183 | 0.055213 | 0.29103
HOPLAND 11014626 | HOPLA | HOPLAND 1101 | HUMBOLDT | 24.0779 | 57.1108 | 92.12% | 0 | 5 | 79.18% | 0% | 0 | 0.055167 | 1 | 0.055167 | 0.0022912
WEIMAR 11012058 | WEIMA | WEIMAR 1101 | SIERRA | 21.2651 | 19.5754 | 79.75% | 4 | 16 | 100% | 0% | 0 | 0.055164 | 1 | 0.055164 | 0.0025941
OAKLAND D 1112CR192 | OAKLA | OAKLAND D 1112 | EAST BAY | 2.6688 | 25.8444 | 29.93% | 2 | 4 | 64.82% | 77.45% | 0 | 0.054951 | 1 | 0.054951 | 0.02059
MONTICELLO 110137384 | MONTI | MONTICELLO 1101 | NORTH BAY | 9.3433 | 47.0333 | 65.93% | 7 | 4 | 99.86% | 0% | 0 | 0.054846 | 1 | 0.054846 | 0.0058701
MERCED FALLS 110287352 | MERCE | MERCED FALLS 1102 | YOSEMITE | 26.2614 | 32.8974 | 99.99% | 0 | 0 | 98.93% | 0% | 0 | 0.054765 | 1 | 0.054765 | 0.0020854
HALF MOON BAY 11038920 | HALF | HALF MOON BAY 1103 | PENINSULA | 8.6186 | 37.4312 | 39.37% | 7 | 11 | 100% | 0% | 0 | 0.054692 | 1 | 0.054692 | 0.0063458
OAKLAND X 1106CR006 | OAKLA | OAKLAND X 1106 | EAST BAY | 3.6093 | 38.5923 | 23.16% | 2 | 2 | 100% | 56.08% | 0 | 0.054619 | 1 | 0.054619 | 0.015133
OAKHURST 110210100 | OAKHU | OAKHURST 1102 | YOSEMITE | 9.1816 | 28.1335 | 94.5% | 4 | 24 | 77.46% | 0% | 0 | 0.054576 | 1 | 0.054576 | 0.005944
CASTRO VALLEY 1108MR243 | CASTR | CASTRO VALLEY 1108 | MISSION | 5.5308 | 36.4789 | 12.29% | 0 | 3 | 99.61% | 62.99% | 0 | 0.054568 | 1 | 0.054568 | 0.0098661
CORNING 110290036 | CORNI | CORNING 1102 | NORTH VALLEY | 14.194 | 60.2901 | 81.06% | 0 | 11 | 98.89% | 0% | 0 | 0.054481 | 1 | 0.054481 | 0.0038383
CAMP EVERS 2104CB | CAMP | CAMP EVERS 2104 | CENTRAL COAST | 1.0591 | 10 | 55.62% | 0 | 2 | 23.71% | 100% | 0 | 0.05446 | 1 | 0.05446 | 0.051422
VIEJO 22029104 | VIEJO | VIEJO 2202 | CENTRAL COAST | 5.9155 | 10 | 5.95% | 8 | 7 | 99.2% | 0% | 0 | 0.054282 | 1 | 0.054282 | 0.0091762
ROB ROY 210538430 | ROB R | ROB ROY 2105 | CENTRAL COAST | 4.0485 | 27.4617 | 42.48% | 11 | 1 | 61.21% | 68.36% | 0 | 0.05425 | 1 | 0.05425 | 0.0134
BRIDGEVILLE 110237486 | BRIDG | BRIDGEVILLE 1102 | HUMBOLDT | 10.3672 | 71.0468 | 99.35% | 4 | 7 | 92.24% | 0% | 0 | 0.054132 | 1 | 0.054132 | 0.0052214
DIAMOND SPRINGS 11042093 | DIAMO | DIAMOND SPRINGS 1104 | SIERRA | 7.2925 | 22.8545 | 79.86% | 0 | 2 | 83.65% | 44.87% | 0 | 0.053967 | 1 | 0.053967 | 0.0074004
GRASS VALLEY 11012208 | GRASS | GRASS VALLEY 1101 | SIERRA | 12.2835 | 20.913 | 70.74% | 4 | 7 | 96.31% | 0% | 0 | 0.053929 | 1 | 0.053929 | 0.0043904
FORT BRAGG A 110195294 | FORT | FORT BRAGG A 1101 | HUMBOLDT | 25.9363 | 28.0829 | 8.119% | 33 | 16 | 99.05% | 0% | 0 | 0.053875 | 1 | 0.053875 | 0.0020772
CAMP EVERS 210411048 | CAMP | CAMP EVERS 2104 | CENTRAL COAST | 0.87487 | 10 | 18.94% | 3 | 1 | 63.94% | 100% | 0 | 0.053728 | 1 | 0.053728 | 0.061413
FORT BRAGG A 1102418 | FORT | FORT BRAGG A 1102 | HUMBOLDT | 13.7424 | 13.0618 | 15.86% | 29 | 14 | 98.4% | 0% | 0 | 0.053533 | 1 | 0.053533 | 0.0038955
CASTRO VALLEY 1106MR337 | CASTR | CASTRO VALLEY 1106 | MISSION | 10.471 | 41.4878 | 74.2% | 2 | 2 | 55.31% | 63.23% | 0 | 0.053395 | 1 | 0.053395 | 0.0050993
SALMON CREEK 1101194 | SALMO | SALMON CREEK 1101 | SONOMA | 6.5546 | 49.1883 | 4.108% | 3 | 3 | 77.1% | 22.41% | 0 | 0.053234 | 1 | 0.053234 | 0.0081216
CURTIS 1702CB | CURTI | CURTIS 1702 | YOSEMITE | 21.952 | 21.1187 | 82.49% | 5 | 14 | 95.73% | 0% | 0 | 0.0532 | 1 | 0.0532 | 0.0024235
OCEANO 1104V38 | OCEAN | OCEANO 1104 | LOS PADRES | 12.9054 | 24.0827 | 46.82% | 5 | 8 | 68.56% | 8.41% | 1 | 0.053152 | 1 | 0.053152 | 0.0041186
MORAGA 1104CB | MORAG | MORAGA 1104 | DIABLO | 12.3977 | 11.1682 | 54.34% | 6 | 17 | 72.33% | 3.443% | 1 | 0.053103 | 1 | 0.053103 | 0.0042833
RIO DELL 11024230 | RIO D | RIO DELL 1102 | HUMBOLDT | 22.9435 | 79.495 | 27.47% | 20 | 5 | 99.94% | 0% | 0 | 0.05306 | 1 | 0.05306 | 0.0023127
RIO DELL 110275970 | RIO D | RIO DELL 1102 | HUMBOLDT | 7.0738 | 89.4562 | 39.39% | 2 | 2 | 100% | 0% | 0 | 0.05303 | 1 | 0.05303 | 0.0074968
CAMP EVERS 21035404 | CAMP | CAMP EVERS 2103 | CENTRAL COAST | 2.6779 | 10 | 26.91% | 3 | 0 | 57.99% | 100% | 0 | 0.052978 | 1 | 0.052978 | 0.019783
CURTIS 170463502 | CURTI | CURTIS 1704 | YOSEMITE | 10.4605 | 25.8863 | 57.75% | 1 | 16 | 100% | 0% | 0 | 0.052892 | 1 | 0.052892 | 0.0050563
VOLTA 11011596 | VOLTA | VOLTA 1101 | NORTH VALLEY | 21.7972 | 45.4978 | 99.98% | 1 | 12 | 100% | 0% | 0 | 0.052789 | 1 | 0.052789 | 0.0024218
POSO MOUNTAIN 21014456 | POSO | POSO MOUNTAIN 2101 | KERN | 23.5359 | 61.9546 | 91.99% | 0 | 4 | 100% | 0% | 0 | 0.052745 | 1 | 0.052745 | 0.002241
CASTRO VALLEY 1109MR334 | CASTR | CASTRO VALLEY 1109 | MISSION | 5.7287 | 41.5825 | 24.73% | 0 | 3 | 90.6% | 49.57% | 0 | 0.052651 | 1 | 0.052651 | 0.0091907
SAN RAMON 2107MR287 | SAN R | SAN RAMON 2107 | MISSION | 0.029952 | 10 | 100% | 0 | 0 | 0.9859% | 100% | 0 | 0.052586 | 1 | 0.052586 | 1.7557
ELK CREEK 11012106 | ELK C | ELK CREEK 1101 | NORTH VALLEY | 13.2055 | 80.5547 | 100% | 0 | 1 | 100% | 0% | 0 | 0.052586 | 1 | 0.052586 | 0.0039821
ORINDA 0401CB | ORIND | ORINDA 0401 | DIABLO | 0.11326 | 10 | 23.54% | 0 | 0 | 63.88% | 100% | 0 | 0.052555 | 1 | 0.052555 | 0.46402
VOLTA 110153118 | VOLTA | VOLTA 1101 | NORTH VALLEY | 9.6297 | 40.8133 | 100% | 0 | 1 | 100% | 0% | 0 | 0.05235 | 1 | 0.05235 | 0.0054364
CURTIS 1704803 | CURTI | CURTIS 1704 | YOSEMITE | 9.5141 | 57.4155 | 65.91% | 1 | 6 | 100% | 27.61% | 0 | 0.05233 | 1 | 0.05233 | 0.0055003
DUNLAP 11037080 | DUNLA | DUNLAP 1103 | FRESNO | 7.9166 | 53.1398 | 56.92% | 4 | 5 | 100% | 0% | 0 | 0.052315 | 1 | 0.052315 | 0.0066082
FRENCH GULCH 11021462 | FRENC | FRENCH GULCH 1102 | NORTH VALLEY | 13.6588 | 44.7353 | 99.62% | 1 | 1 | 99.24% | 22.55% | 0 | 0.052153 | 1 | 0.052153 | 0.0038182
CLEAR LAKE 1101406 | CLEAR | CLEAR LAKE 1101 | HUMBOLDT | 10.6464 | 76.543 | 93.36% | 0 | 1 | 32.19% | 54.28% | 0 | 0.052045 | 1 | 0.052045 | 0.0048885
OCEANO 1104Q12 | OCEAN | OCEANO 1104 | LOS PADRES | 9.3393 | 55.4094 | 73.47% | 0 | 5 | 57.92% | 27.55% | 0 | 0.051953 | 1 | 0.051953 | 0.0055629
HIGGINS 1109594 | HIGGI | HIGGINS 1109 | SIERRA | 14.2898 | 11.2028 | 80.24% | 1 | 11 | 100% | 0% | 0 | 0.051909 | 1 | 0.051909 | 0.0036326
SONOMA 110478372 | SONOM | SONOMA 1104 | SONOMA | 16.4405 | 56.415 | 74.14% | 3 | 12 | 96.01% | 0% | 0 | 0.051874 | 1 | 0.051874 | 0.0031552
HALF MOON BAY 11028848 | HALF | HALF MOON BAY 1102 | PENINSULA | 3.8931 | 27.5705 | 29.99% | 4 | 3 | 38.64% | 80.42% | 0 | 0.051782 | 1 | 0.051782 | 0.013301
NOTRE DAME 11042408 | NOTRE | NOTRE DAME 1104 | NORTH VALLEY | 11.2331 | 23.0626 | 36.02% | 1 | 3 | 81.2% | 47.16% | 1 | 0.051652 | 1 | 0.051652 | 0.0045981
LAYTONVILLE 11022502 | LAYTO | LAYTONVILLE 1102 | HUMBOLDT | 17.8026 | 72.9803 | 99.59% | 0 | 9 | 100% | 0% | 0 | 0.051556 | 1 | 0.051556 | 0.002896
OAKLAND X 1106CR008 | OAKLA | OAKLAND X 1106 | EAST BAY | 4.2343 | 10.8634 | 21.85% | 11 | 17 | 100% | 13.39% | 0 | 0.051531 | 1 | 0.051531 | 0.01217
SILVERADO 2104806 | SILVE | SILVERADO 2104 | NORTH BAY | 20.224 | 80.8764 | 82.09% | 0 | 5 | 59.08% | 2.927% | 0 | 0.051436 | 1 | 0.051436 | 0.0025433
SO. CAL. EDISON #2 1101CB | SO. C | SO. CAL. EDISON #2 1101 | YOSEMITE | 1.1766 | 10 | 100% | 0 | 0 | 100% | 37.67% | 0 | 0.051431 | 1 | 0.051431 | 0.043711
ELECTRA 11026014 | ELECT | ELECTRA 1102 | STOCKTON | 28.5875 | 15.0573 | 83.7% | 1 | 14 | 100% | 0% | 0 | 0.051142 | 1 | 0.051142 | 0.0017889
ALTO 1122CB | ALTO | ALTO 1122 | NORTH BAY | 2.386 | 10 | 11.27% | 0 | 1 | 68.83% | 100% | 0 | 0.05105 | 1 | 0.05105 | 0.021396
STILLWATER 11021466 | STILL | STILLWATER 1102 | NORTH VALLEY | 19.2831 | 16.0387 | 100% | 1 | 10 | 94.09% | 0% | 0 | 0.051049 | 1 | 0.051049 | 0.0026473
PEORIA 170190090 | PEORI | PEORIA 1701 | YOSEMITE | 29.5241 | 42.6688 | 45.08% | 1 | 8 | 98.45% | 0% | 0 | 0.050945 | 1 | 0.050945 | 0.0017255
DOBBINS 110191464 | DOBBI | DOBBINS 1101 | SIERRA | 7.0765 | 18.3456 | 88.34% | 2 | 2 | 100% | 2.371% | 0 | 0.050871 | 1 | 0.050871 | 0.0071887
ALTO 1124CB | ALTO | ALTO 1124 | NORTH BAY | 3.2561 | 10 | 7.135% | 1 | 6 | 46.3% | 100% | 0 | 0.050654 | 1 | 0.050654 | 0.015557
ROB ROY 210410954 | ROB R | ROB ROY 2104 | CENTRAL COAST | 7.1077 | 10 | 88.57% | 7 | 3 | 100% | 0% | 0 | 0.050548 | 1 | 0.050548 | 0.0071117
OREGON TRAIL 11021584 | OREGO | OREGON TRAIL 1102 | NORTH VALLEY | 13.0863 | 23.8771 | 100% | 1 | 4 | 100% | 0% | 0 | 0.050417 | 1 | 0.050417 | 0.0038527
PEORIA 170488630 | PEORI | PEORIA 1704 | YOSEMITE | 0.77831 | 38.0661 | 100% | 0 | 0 | 100% | 0% | 0 | 0.050412 | 1 | 0.050412 | 0.064771
HALSEY 110176178 | HALSE | HALSEY 1101 | SIERRA | 19.4389 | 10 | 66.26% | 6 | 14 | 96.3% | 0% | 0 | 0.050379 | 1 | 0.050379 | 0.0025916
FORT BRAGG A 11044690 | FORT | FORT BRAGG A 1104 | HUMBOLDT | 12.2439 | 49.0226 | 37.04% | 15 | 12 | 85.93% | 0% | 0 | 0.050332 | 1 | 0.050332 | 0.0041108
HALSEY 11012414 | HALSE | HALSEY 1101 | SIERRA | 14.7964 | 13.1515 | 76.48% | 3 | 9 | 100% | 0% | 0 | 0.050299 | 1 | 0.050299 | 0.0033994
PEORIA 170184318 | PEORI | PEORIA 1701 | YOSEMITE | 9.9103 | 10 | 99.97% | 1 | 8 | 100% | 0% | 0 | 0.049883 | 1 | 0.049883 | 0.0050334
CALAVERAS CEMENT 1101544800 | CALAV | CALAVERAS CEMENT 1101 | STOCKTON | 23.1954 | 36.7246 | 100% | 2 | 5 | 100% | 0% | 0 | 0.049871 | 1 | 0.049871 | 0.0021501
CHOLAME 21025597 | CHOLA | CHOLAME 2102 | LOS PADRES | 5.1199 | 69.1665 | 100% | 0 | 2 | 100% | 0% | 0 | 0.049821 | 1 | 0.049821 | 0.0097308
ANTLER 11011376 | ANTLE | ANTLER 1101 | NORTH VALLEY | 9.003 | 26.8195 | 100% | 0 | 3 | 100% | 0% | 0 | 0.049747 | 1 | 0.049747 | 0.0055256
SWIFT 2110XR332 | SWIFT | SWIFT 2110 | SAN JOSE | 49.6657 | 79.4868 | 80.03% | 0 | 0 | 100% | 0% | 0 | 0.049698 | 1 | 0.049698 | 0.0010007
SAND CREEK 11037070 | SAND | SAND CREEK 1103 | FRESNO | 17.8283 | 24.5064 | 100% | 1 | 3 | 100% | 0% | 0 | 0.049625 | 1 | 0.049625 | 0.0027835
OCEANO 1103221092 | OCEAN | OCEANO 1103 | LOS PADRES | 1.2243 | 45.1389 | 92.5% | 0 | 2 | 95.43% | 0% | 0 | 0.049591 | 1 | 0.049591 | 0.040504
EL CERRITO G 1112BR178 | EL CE | EL CERRITO G 1112 | EAST BAY | 1.8955 | 10 | 57.49% | 2 | 1 | 23.53% | 92.74% | 0 | 0.049573 | 1 | 0.049573 | 0.026154
UPPER LAKE 1101CB | UPPER | UPPER LAKE 1101 | HUMBOLDT | 1.1134 | 70.0562 | 95.06% | 2 | 2 | 100% | 0% | 0 | 0.049432 | 1 | 0.049432 | 0.044398
CORNING 110253184 | CORNI | CORNING 1102 | NORTH VALLEY | 31.925 | 68.303 | 86.89% | 0 | 7 | 100% | 0% | 0 | 0.049388 | 1 | 0.049388 | 0.001547
CALPELLA 11013419 | CALPE | CALPELLA 1101 | HUMBOLDT | 8.0753 | 59.7032 | 100% | 1 | 1 | 100% | 3.769% | 0 | 0.0493 | 1 | 0.0493 | 0.006105
BEAR VALLEY 210511210 | BEAR | BEAR VALLEY 2105 | YOSEMITE | 17.0195 | 54.7309 | 100% | 0 | 6 | 100% | 0% | 0 | 0.049124 | 1 | 0.049124 | 0.0028864
PIT NO 5 11011614 | PIT N | PIT NO 5 1101 | NORTH VALLEY | 1.8659 | 92.5056 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049074 | 1 | 0.049074 | 0.026301
COTTONWOOD 11021578 | COTTO | COTTONWOOD 1102 | NORTH VALLEY | 28.4377 | 38.0859 | 100% | 1 | 7 | 81.08% | 0% | 0 | 0.049028 | 1 | 0.049028 | 0.0017241
DUNLAP 11027360 | DUNLA | DUNLAP 1102 | FRESNO | 8.5319 | 14.1381 | 99.93% | 0 | 0 | 100% | 0% | 0 | 0.048964 | 1 | 0.048964 | 0.0057389
COARSEGOLD 21035020 | COARS | COARSEGOLD 2103 | YOSEMITE | 16.1848 | 19.8956 | 69.91% | 1 | 23 | 97.69% | 0% | 0 | 0.048835 | 1 | 0.048835 | 0.0030173
MARTELL 110111244 | MARTE | MARTELL 1101 | STOCKTON | 21.6798 | 10 | 87.92% | 5 | 3 | 99.45% | 0% | 0 | 0.048788 | 1 | 0.048788 | 0.0022504
BURNEY 11019042 | BURNE | BURNEY 1101 | NORTH VALLEY | 3.0554 | 28.762 | 87.06% | 1 | 1 | 96.72% | 0% | 0 | 0.048736 | 1 | 0.048736 | 0.015951
WEIMAR 1101CB | WEIMA | WEIMAR 1101 | SIERRA | 9.2462 | 10 | 51.97% | 4 | 11 | 100% | 0% | 0 | 0.04865 | 1 | 0.04865 | 0.0052616
PARADISE 1102CB | PARAD | PARADISE 1102 | NORTH VALLEY | 0.74465 | 10 | 6.716% | 2 | 0 | 53.22% | 100% | 0 | 0.048451 | 1 | 0.048451 | 0.065065
MORGAN HILL 2111XR292 | MORGA | MORGAN HILL 2111 | SAN JOSE | 10.8242 | 23.3354 | 98.35% | 1 | 8 | 89.12% | 0% | 0 | 0.048423 | 1 | 0.048423 | 0.0044736
STILLWATER 11021644 | STILL | STILLWATER 1102 | NORTH VALLEY | 22.854 | 11.5095 | 100% | 1 | 6 | 100% | 0% | 0 | 0.048415 | 1 | 0.048415 | 0.0021184
NARROWS 210534069 | NARRO | NARROWS 2105 | SIERRA | 15.7398 | 14.9961 | 98.66% | 0 | 6 | 100% | 0% | 0 | 0.048393 | 1 | 0.048393 | 0.0030746
MOUNTAIN QUARRIES 21011180 | MOUNT | MOUNTAIN QUARRIES 2101 | SIERRA | 12.8441 | 30.3787 | 92.22% | 1 | 2 | 100% | 9.293% | 0 | 0.048359 | 1 | 0.048359 | 0.0037651
BRIDGEVILLE 1102 | BRIDG | BRIDGEVILLE 1102 | HUMBOLDT | 0.0078479 | 90 | 100% | 0 | 0 | 100% | 0% | 0 | 0.048281 | 1 | 0.048281 | 6.1521
AUBERRY 110237466 | AUBER | AUBERRY 1102 | FRESNO | 31.5797 | 23.1987 | 95.92% | 2 | 3 | 100% | 0% | 0 | 0.048258 | 1 | 0.048258 | 0.0015281
WILLOW CREEK 1103CB | WILLO | WILLOW CREEK 1103 | HUMBOLDT | 3.9217 | 18.1592 | 58.12% | 1 | 8 | 100% | 7.1% | 0 | 0.048009 | 1 | 0.048009 | 0.012242
SAND CREEK 11037420 | SAND | SAND CREEK 1103 | FRESNO | 23.394 | 10 | 99.98% | 4 | 4 | 100% | 0% | 0 | 0.04783 | 1 | 0.04783 | 0.0020445
GARBERVILLE 11024744 | GARBE | GARBERVILLE 1102 | HUMBOLDT | 16.8626 | 50.888 | 35.22% | 7 | 3 | 83.26% | 0% | 0 | 0.047692 | 1 | 0.047692 | 0.0028283
INDIAN FLAT 110410270 | INDIA | INDIAN FLAT 1104 | YOSEMITE | 3.8012 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.047687 | 1 | 0.047687 | 0.012545
SAN RAFAEL 1108CB | SAN R | SAN RAFAEL 1108 | NORTH BAY | 3.0131 | 10 | 10.73% | 6 | 1 | 40.8% | 100% | 0 | 0.047654 | 1 | 0.047654 | 0.015816
ROSSMOOR 110168920 | ROSSM | ROSSMOOR 1101 | DIABLO | 5.9925 | 29.5829 | 31.67% | 8 | 11 | 82.31% | 24.74% | 0 | 0.047645 | 1 | 0.047645 | 0.0079508
SHADY GLEN 110132726 | SHADY | SHADY GLEN 1101 | SIERRA | 12.4872 | 23.3088 | 84.95% | 3 | 6 | 100% | 0% | 0 | 0.047638 | 1 | 0.047638 | 0.0038149
SAN JOAQUIN #2 110310320 | SAN J | SAN JOAQUIN #2 1103 | YOSEMITE | 11.8104 | 12.4719 | 98.89% | 1 | 18 | 100% | 0% | 0 | 0.047599 | 1 | 0.047599 | 0.0040303
FORT SEWARD 1121CB | FORT | FORT SEWARD 1121 | HUMBOLDT | 7.2358 | 72.7632 | 100% | 3 | 3 | 100% | 0% | 0 | 0.047585 | 1 | 0.047585 | 0.0065763
HIGHLANDS 110448262 | HIGHL | HIGHLANDS 1104 | HUMBOLDT | 5.8216 | 10 | 84.42% | 0 | 6 | 100% | 0% | 0 | 0.047568 | 1 | 0.047568 | 0.008171
SHINGLE SPRINGS 2110CB | SHING | SHINGLE SPRINGS 2110 | SIERRA | 0.10881 | 10 | 92.58% | 0 | 0 | 8.524% | 92.58% | 0 | 0.047519 | 1 | 0.047519 | 0.43671
CHESTER 11022564 | CHEST | CHESTER 1102 | NORTH VALLEY | 2.0894 | 10 | 100% | 0 | 3 | 93.3% | 0% | 0 | 0.047498 | 1 | 0.047498 | 0.022733
PIT NO 5 11011618 | PIT N | PIT NO 5 1101 | NORTH VALLEY | 6.0991 | 69.0036 | 93.71% | 0 | 2 | 100% | 0% | 0 | 0.047368 | 1 | 0.047368 | 0.0077664
FROGTOWN 17027134 | FROGT | FROGTOWN 1702 | STOCKTON | 19.267 | 44.0538 | 84.25% | 0 | 2 | 84.8% | 0% | 0 | 0.047354 | 1 | 0.047354 | 0.0024578
MONTICELLO 110193384 | MONTI | MONTICELLO 1101 | NORTH BAY | 15.2847 | 55.7693 | 100% | 0 | 3 | 88.22% | 0% | 0 | 0.047273 | 1 | 0.047273 | 0.0030928
BEAR VALLEY 2101CB | BEAR | BEAR VALLEY 2101 | YOSEMITE | 18.7199 | 23.9906 | 55.73% | 0 | 6 | 100% | 0% | 0 | 0.047229 | 1 | 0.047229 | 0.0025229
OREGON TRAIL 11041574 | OREGO | OREGON TRAIL 1104 | NORTH VALLEY | 16.4858 | 16.0641 | 94.5% | 2 | 4 | 88.21% | 0% | 0 | 0.04716 | 1 | 0.04716 | 0.0028607
CORNING 110185162 | CORNI | CORNING 1101 | NORTH VALLEY | 5.7561 | 60.2607 | 100% | 0 | 2 | 100% | 0% | 0 | 0.047015 | 1 | 0.047015 | 0.0081678
MIDDLETOWN 11021312 | MIDDL | MIDDLETOWN 1102 | HUMBOLDT | 9.8496 | 13.9462 | 100% | 1 | 10 | 100% | 0% | 0 | 0.046919 | 1 | 0.046919 | 0.0047635
DUNLAP 11027290 | DUNLA | DUNLAP 1102 | FRESNO | 0.73169 | 39.1465 | 99.26% | 0 | 9 | 100% | 0% | 0 | 0.04685 | 1 | 0.04685 | 0.06403
MORGAN HILL 2105XR070 | MORGA | MORGAN HILL 2105 | SAN JOSE | 6.67 | 37.7183 | 68.61% | 0 | 0 | 76.77% | 50.18% | 1 | 0.046839 | 1 | 0.046839 | 0.0070223
CORNING 110182846 | CORNI | CORNING 1101 | NORTH VALLEY | 5.0438 | 29.0672 | 100% | 1 | 5 | 99.85% | 0% | 0 | 0.046785 | 1 | 0.046785 | 0.0092758
PIT NO 5 11013308 | PIT N | PIT NO 5 1101 | NORTH VALLEY | 0.044135 | 85 | 100% | 0 | 0 | 100% | 0% | 0 | 0.046733 | 1 | 0.046733 | 1.0589
SWIFT 2110XR366 | SWIFT | SWIFT 2110 | SAN JOSE | 8.8402 | 27.8534 | 70.07% | 1 | 1 | 80.04% | 0% | 0 | 0.04663 | 1 | 0.04663 | 0.0052748
LOS OSITOS 21037062 | LOS O | LOS OSITOS 2103 | CENTRAL COAST | 12.2332 | 84.1604 | 73.22% | 2 | 3 | 100% | 0% | 0 | 0.046568 | 1 | 0.046568 | 0.0038067
CORRAL 110236666 | CORRA | CORRAL 1102 | STOCKTON | 17.3526 | 23.3821 | 99.95% | 1 | 2 | 96.21% | 0% | 0 | 0.046553 | 1 | 0.046553 | 0.0026827
RINCON 1104CB | RINCO | RINCON 1104 | SONOMA | 2.6764 | 10 | 22.48% | 3 | 5 | 47.86% | 77.17% | 0 | 0.046471 | 1 | 0.046471 | 0.017363
GARBERVILLE 11022540 | GARBE | GARBERVILLE 1102 | HUMBOLDT | 15.3454 | 59.7556 | 6.792% | 13 | 5 | 85.73% | 0% | 0 | 0.046446 | 1 | 0.046446 | 0.0030267
MONTE RIO 1111292 | MONTE | MONTE RIO 1111 | SONOMA | 14.6924 | 53.0276 | 14.56% | 3 | 9 | 74.19% | 33.55% | 0 | 0.046445 | 1 | 0.046445 | 0.0031611
MENDOCINO 1101CB | MENDO | MENDOCINO 1101 | HUMBOLDT | 11.0353 | 11.0346 | 86.58% | 0 | 6 | 81.55% | 0% | 0 | 0.046385 | 1 | 0.046385 | 0.0042033
HIGGINS 1104324510 | HIGGI | HIGGINS 1104 | SIERRA | 12.4769 | 10 | 100% | 3 | 3 | 100% | 0% | 0 | 0.046303 | 1 | 0.046303 | 0.0037111
BROWNS VALLEY 11011268 | BROWN | BROWNS VALLEY 1101 | SIERRA | 10.9063 | 24.7365 | 96.96% | 1 | 7 | 100% | 0% | 0 | 0.046288 | 1 | 0.046288 | 0.0042441
PIT NO 7 1101CB | PIT N | PIT NO 7 1101 | NORTH VALLEY | 2.7098 | 77.1247 | 100% | 0 | 2 | 100% | 0% | 0 | 0.046206 | 1 | 0.046206 | 0.017051
KONOCTI 1102596 | KONOC | KONOCTI 1102 | HUMBOLDT | 8.591 | 44.5897 | 35.58% | 1 | 10 | 63.73% | 0% | 0 | 0.046139 | 1 | 0.046139 | 0.0053706
POINT ARENA 11012637 | POINT | POINT ARENA 1101 | HUMBOLDT | 4.0404 | 84.4232 | 59.73% | 1 | 2 | 100% | 0% | 0 | 0.046116 | 1 | 0.046116 | 0.011414
SAN LEANDRO U 1109CR182 | SAN L | SAN LEANDRO U 1109 | MISSION | 4.81 | 10 | 62.88% | 5 | 1 | 100% | 19.48% | 0 | 0.046108 | 1 | 0.046108 | 0.0095859
DUNBAR 110297160 | DUNBA | DUNBAR 1102 | SONOMA | 0.058569 | 82.8928 | 100% | 0 | 0 | 100% | 0% | 0 | 0.046095 | 1 | 0.046095 | 0.78702
WYANDOTTE 110738438 | WYAND | WYANDOTTE 1107 | NORTH VALLEY | 16.8538 | 17.2711 | 100% | 1 | 4 | 100% | 13.33% | 1 | 0.046053 | 1 | 0.046053 | 0.0027325
STILLWATER 110148950 | STILL | STILLWATER 1101 | NORTH VALLEY | 12.4263 | 10 | 99.94% | 1 | 4 | 100% | 0% | 0 | 0.046041 | 1 | 0.046041 | 0.0037052
HIGHLANDS 1103482 | HIGHL | HIGHLANDS 1103 | HUMBOLDT | 23.7709 | 84.3418 | 64.96% | 1 | 10 | 92.07% | 0% | 0 | 0.046005 | 1 | 0.046005 | 0.0019354
PETALUMA C 1109848654 | PETAL | PETALUMA C 1109 | SONOMA | 13.3481 | 80.6017 | 79.77% | 0 | 10 | 97.01% | 0% | 0 | 0.045978 | 1 | 0.045978 | 0.0034445
COTTONWOOD 110168190 | COTTO | COTTONWOOD 1101 | NORTH VALLEY | 22.7429 | 39.5713 | 100% | 3 | 4 | 90.15% | 0% | 0 | 0.045908 | 1 | 0.045908 | 0.0020185
PINE GROVE 11013166 | PINE | PINE GROVE 1101 | STOCKTON | 12.5063 | 11.3177 | 79.03% | 1 | 18 | 100% | 0% | 0 | 0.045896 | 1 | 0.045896 | 0.0036699
SCE TEHACHAPI 1101CB | SCE T | SCE TEHACHAPI 1101 | KERN | 1.4276 | 82.1535 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045873 | 1 | 0.045873 | 0.032133
SALT SPRINGS 210110416 | SALT | SALT SPRINGS 2101 | STOCKTON | 0.57657 | 81.6052 | 94.63% | 2 | 1 | 100% | 0% | 0 | 0.045848 | 1 | 0.045848 | 0.079518
GARBERVILLE 110237054 | GARBE | GARBERVILLE 1102 | HUMBOLDT | 8.8244 | 78.2726 | 22.8% | 0 | 2 | 95.32% | 0% | 0 | 0.04584 | 1 | 0.04584 | 0.0051947
DUNBAR 1103440 | DUNBA | DUNBAR 1103 | SONOMA | 3.5573 | 21.3081 | 50.04% | 0 | 2 | 25.85% | 93.78% | 0 | 0.045809 | 1 | 0.045809 | 0.012878
BURNEY 11011340 | BURNE | BURNEY 1101 | NORTH VALLEY | 18.024 | 21.8274 | 89.51% | 4 | 2 | 100% | 0% | 0 | 0.045714 | 1 | 0.045714 | 0.0025363
PLACERVILLE 111219712 | PLACE | PLACERVILLE 1112 | SIERRA | 12.7698 | 10 | 100% | 3 | 10 | 97.13% | 0% | 0 | 0.045629 | 1 | 0.045629 | 0.0035732
PASO ROBLES 1104R12 | PASO | PASO ROBLES 1104 | LOS PADRES | 26.4117 | 63.4802 | 89.23% | 0 | 7 | 66.23% | 0% | 0 | 0.045549 | 1 | 0.045549 | 0.0017246
TASSAJARA 210419042 | TASSA | TASSAJARA 2104 | DIABLO | 7.0796 | 47.3825 | 57.65% | 1 | 2 | 83.81% | 25.74% | 0 | 0.045532 | 1 | 0.045532 | 0.0064314
APPLE HILL 21026552 | APPLE | APPLE HILL 2102 | SIERRA | 12.3732 | 14.1708 | 74.28% | 2 | 0 | 100% | 6.545% | 1 | 0.045443 | 1 | 0.045443 | 0.0036727
DUNLAP 11027060 | DUNLA | DUNLAP 1102 | FRESNO | 17.8164 | 21.4268 | 100% | 3 | 11 | 100% | 0% | 0 | 0.045381 | 1 | 0.045381 | 0.0025471
MARIPOSA 210135244 | MARIP | MARIPOSA 2101 | YOSEMITE | 17.3356 | 16.4968 | 77.7% | 2 | 10 | 100% | 23.66% | 0 | 0.045381 | 1 | 0.045381 | 0.0026178
AUBERRY 1101R2579 | AUBER | AUBERRY 1101 | FRESNO | 34.5067 | 14.4508 | 99.64% | 2 | 14 | 100% | 0% | 0 | 0.045338 | 1 | 0.045338 | 0.0013139
ELK CREEK 11012002 | ELK C | ELK CREEK 1101 | NORTH VALLEY | 17.647 | 82.0427 | 100% | 0 | 0 | 58.67% | 0% | 0 | 0.045253 | 1 | 0.045253 | 0.0025643
APPLE HILL 21021532 | APPLE | APPLE HILL 2102 | SIERRA | 38.7437 | 26.3677 | 83.01% | 8 | 10 | 92.13% | 0.1028% | 0 | 0.045174 | 1 | 0.045174 | 0.001166
ATASCADERO 1103A16 | ATASC | ATASCADERO 1103 | LOS PADRES | 18.5162 | 60.2309 | 48.27% | 0 | 1 | 91.95% | 38.05% | 0 | 0.045156 | 1 | 0.045156 | 0.0024387
HOOPA 110137202 | HOOPA | HOOPA 1101 | HUMBOLDT | 23.7883 | 81.2571 | 100% | 8 | 3 | 82.1% | 0% | 0 | 0.045151 | 1 | 0.045151 | 0.001898
PIT NO 5 1101CB | PIT N | PIT NO 5 1101 | NORTH VALLEY | 0.72275 | 65.782 | 100% | 4 | 2 | 100% | 0% | 0 | 0.045131 | 1 | 0.045131 | 0.062444
JARVIS 1111MR121 | JARVI | JARVIS 1111 | MISSION | 1.1185 | 70.124 | 6.252% | 0 | 0 | 20.83% | 100% | 0 | 0.045013 | 1 | 0.045013 | 0.040244
MENLO 11031721 | MENLO | MENLO 1103 | PENINSULA | 6.795 | 58.431 | 89.52% | 4 | 2 | 100% | 0% | 0 | 0.044995 | 1 | 0.044995 | 0.0066218
FRENCH GULCH 11011464 | FRENC | FRENCH GULCH 1101 | NORTH VALLEY | 3.9608 | 72.3083 | 100% | 3 | 0 | 100% | 0% | 0 | 0.044678 | 1 | 0.044678 | 0.01128
LUCERNE 110638436 | LUCER | LUCERNE 1106 | HUMBOLDT | 4.6279 | 61.4353 | 100% | 0 | 7 | 96.43% | 0% | 0 | 0.044553 | 1 | 0.044553 | 0.009627
MILPITAS 110987800 | MILPI | MILPITAS 1109 | SAN JOSE | 1.61 | 77.3424 | 100% | 0 | 0 | 100% | 0% | 0 | 0.044454 | 1 | 0.044454 | 0.027612
TYLER 11051536 | TYLER | TYLER 1105 | NORTH VALLEY | 17.0203 | 70.2834 | 100% | 0 | 5 | 94.18% | 0% | 0 | 0.044384 | 1 | 0.044384 | 0.0026077
HOLLISTER 21054018 | HOLLI | HOLLISTER 2105 | CENTRAL COAST | 42.8602 | 78.3807 | 68.88% | 1 | 1 | 81.19% | 0% | 0 | 0.044317 | 1 | 0.044317 | 0.001034
WILLOW CREEK 11035012 | WILLO | WILLOW CREEK 1103 | HUMBOLDT | 10.8623 | 35.544 | 71.11% | 10 | 12 | 100% | 0% | 0 | 0.044176 | 1 | 0.044176 | 0.0040669
SILVERADO 2105CB | SILVE | SILVERADO 2105 | NORTH BAY | 0.47706 | 10 | 63.84% | 0 | 1 | 10.39% | 100% | 0 | 0.044175 | 1 | 0.044175 | 0.092599
WILDWOOD 110198896 | WILDW | WILDWOOD 1101 | NORTH VALLEY | 9.9251 | 71.2641 | 100% | 1 | 1 | 100% | 0% | 0 | 0.044142 | 1 | 0.044142 | 0.0044476
ELK CREEK 11012032 | ELK C | ELK CREEK 1101 | NORTH VALLEY | 9.5675 | 53.63 | 100% | 0 | 1 | 99.9% | 0% | 0 | 0.044086 | 1 | 0.044086 | 0.0046079
MARIPOSA 21029490 | MARIP | MARIPOSA 2102 | YOSEMITE | 4.2707 | 19.9086 | 45.43% | 0 | 1 | 100% | 49.91% | 0 | 0.044074 | 1 | 0.044074 | 0.01032
STANISLAUS 170179826 | STANI | STANISLAUS 1701 | YOSEMITE | 10.1928 | 54.2786 | 66.14% | 1 | 7 | 100% | 0% | 0 | 0.044036 | 1 | 0.044036 | 0.0043203
FRENCH GULCH 11011892 | FRENC | FRENCH GULCH 1101 | NORTH VALLEY | 2.9079 | 75.8107 | 100% | 0 | 0 | 100% | 0% | 0 | 0.044011 | 1 | 0.044011 | 0.015135
RIO DELL 11027124 | RIO D | RIO DELL 1102 | HUMBOLDT | 0.67226 | 75.6649 | 100% | 0 | 0 | 100% | 0% | 0 | 0.043969 | 1 | 0.043969 | 0.065404
ELK 11011260 | ELK 1 | ELK 1101 | HUMBOLDT | 15.6745 | 74.4455 | 25.71% | 10 | 4 | 100% | 0% | 0 | 0.043784 | 1 | 0.043784 | 0.0027933
COARSEGOLD 21045516 | COARS | COARSEGOLD 2104 | YOSEMITE | 18.4464 | 11.3018 | 100% | 1 | 1 | 100% | 0% | 0 | 0.043744 | 1 | 0.043744 | 0.0023714
EEL RIVER 11021902 | EEL R | EEL RIVER 1102 | HUMBOLDT | 5.1093 | 87.5518 | 84.86% | 3 | 2 | 68.94% | 0% | 0 | 0.043714 | 1 | 0.043714 | 0.0085558
NORTH DUBLIN 2103CB | NORTH | NORTH DUBLIN 2103 | MISSION | 12.6489 | 55.8047 | 31.35% | 1 | 2 | 83.95% | 0% | 0 | 0.043695 | 1 | 0.043695 | 0.0034544
BEAR VALLEY 210521160 | BEAR | BEAR VALLEY 2105 | YOSEMITE | 23.7351 | 48.0267 | 99.88% | 2 | 5 | 100% | 3.193% | 0 | 0.043692 | 1 | 0.043692 | 0.0018408
OAKLAND K 1104CR208 | OAKLA | OAKLAND K 1104 | EAST BAY | 2.4051 | 10 | 34.97% | 0 | 3 | 100% | 39.7% | 0 | 0.0436 | 1 | 0.0436 | 0.018128
ANTLER 11011612 | ANTLE | ANTLER 1101 | NORTH VALLEY | 8.3928 | 10 | 100% | 2 | 6 | 90.86% | 15.08% | 1 | 0.043586 | 1 | 0.043586 | 0.0051932
POINT ARENA 110147952 | POINT | POINT ARENA 1101 | HUMBOLDT | 10.391 | 76.4518 | 10.32% | 20 | 9 | 100% | 0% | 0 | 0.043386 | 1 | 0.043386 | 0.0041754
CABRILLO 1103Y46 | CABRI | CABRILLO 1103 | LOS PADRES | 20.218 | 55.531 | 56.98% | 1 | 5 | 42.55% | 0% | 0 | 0.043329 | 1 | 0.043329 | 0.0021431
VIEJO 22019114 | VIEJO | VIEJO 2201 | CENTRAL COAST | 6.3385 | 10 | 15.64% | 12 | 5 | 93.11% | 0% | 0 | 0.043315 | 1 | 0.043315 | 0.0068336
DOBBINS 11011808 | DOBBI | DOBBINS 1101 | SIERRA | 15.539 | 16.962 | 100% | 1 | 0 | 100% | 6.412% | 0 | 0.043272 | 1 | 0.043272 | 0.0027847
STANISLAUS 1702CB | STANI | STANISLAUS 1702 | YOSEMITE | 7.977 | 43.3363 | 28.21% | 1 | 3 | 100% | 19.55% | 0 | 0.043216 | 1 | 0.043216 | 0.0054176
MENLO 11038982 | MENLO | MENLO 1103 | PENINSULA | 4.6231 | 36.5586 | 24.74% | 19 | 4 | 100% | 0% | 0 | 0.043182 | 1 | 0.043182 | 0.0093405
FULTON 1102287172 | FULTO | FULTON 1102 | SONOMA | 17.3701 | 47.5802 | 77.47% | 4 | 10 | 64.9% | 11.1% | 0 | 0.043179 | 1 | 0.043179 | 0.0024858
DUNLAP 1103CB | DUNLA | DUNLAP 1103 | FRESNO | 5.3266 | 46.6515 | 99.77% | 2 | 1 | 100% | 0% | 0 | 0.043161 | 1 | 0.043161 | 0.008103
LUCERNE 1103630 | LUCER | LUCERNE 1103 | HUMBOLDT | 12.5736 | 13.6837 | 90.26% | 2 | 19 | 92.62% | 0% | 0 | 0.043155 | 1 | 0.043155 | 0.0034321
HATTON 11022010 | HATTO | HATTON 1102 | CENTRAL COAST | 4.0217 | 30.548 | 30.01% | 17 | 5 | 100% | 0% | 0 | 0.043055 | 1 | 0.043055 | 0.010706
CURTIS 17058110 | CURTI | CURTIS 1705 | YOSEMITE | 8.154 | 12.6611 | 71.8% | 0 | 7 | 100% | 22.12% | 0 | 0.043018 | 1 | 0.043018 | 0.0052757
TEJON 11022455 | TEJON | TEJON 1102 | KERN | 6.4984 | 10 | 98.01% | 0 | 2 | 100% | 0% | 0 | 0.043014 | 1 | 0.043014 | 0.0066191
JOLON 11027068 | JOLON | JOLON 1102 | CENTRAL COAST | 3.8301 | 72.2303 | 100% | 0 | 0 | 100% | 0% | 0 | 0.042992 | 1 | 0.042992 | 0.011225
CORRAL 1102CB | CORRA | CORRAL 1102 | STOCKTON | 17.6005 | 19.3826 | 70.6% | 2 | 10 | 83.31% | 0% | 0 | 0.04296 | 1 | 0.04296 | 0.0024408
ZACA 1102Y02 | ZACA | ZACA 1102 | LOS PADRES | 10.6195 | 15.4408 | 92.94% | 0 | 5 | 80.71% | 0% | 0 | 0.042959 | 1 | 0.042959 | 0.0040453
ELECTRA 1101CB | ELECT | ELECTRA 1101 | STOCKTON | 26.464 | 31.8119 | 57.82% | 4 | 8 | 100% | 0% | 0 | 0.042866 | 1 | 0.042866 | 0.0016198
SARATOGA 1103LC16 | SARAT | SARATOGA 1103 | DE ANZA | 4.0893 | 10 | 47.33% | 3 | 10 | 80.63% | 0% | 0 | 0.042849 | 1 | 0.042849 | 0.010478
ANTLER 1101CB | ANTLE | ANTLER 1101 | NORTH VALLEY | 1.601 | 30.2969 | 97.79% | 1 | 1 | 100% | 0% | 0 | 0.042837 | 1 | 0.042837 | 0.026757
BRENTWOOD 2105B504R | BRENT | BRENTWOOD 2105 | DIABLO | 7.4348 | 10 | 79.77% | 0 | 6 | 65.97% | 0% | 0 | 0.042733 | 1 | 0.042733 | 0.0057477
PAUL SWEET 2102CB | PAUL | PAUL SWEET 2102 | CENTRAL COAST | 0.80988 | 10 | 58.15% | 0 | 0 | 13.51% | 100% | 0 | 0.042651 | 1 | 0.042651 | 0.052663
GARBERVILLE 11022010 | GARBE | GARBERVILLE 1102 | HUMBOLDT | 6.6438 | 69.4132 | 9.089% | 2 | 3 | 100% | 0% | 0 | 0.042493 | 1 | 0.042493 | 0.0063958
POINT ARENA 1101474 | POINT | POINT ARENA 1101 | HUMBOLDT | 9.0104 | 63.6125 | 35.39% | 4 | 6 | 100% | 0% | 0 | 0.042479 | 1 | 0.042479 | 0.0047144
SANTA ROSA A 1104CB | SANTA | SANTA ROSA A 1104 | SONOMA | 1.1731 | 10 | 48.07% | 0 | 1 | 19.25% | 100% | 0 | 0.042461 | 1 | 0.042461 | 0.036195
STAFFORD 11021048 | STAFF | STAFFORD 1102 | NORTH BAY | 4.9722 | 28.2651 | 55.55% | 1 | 7 | 93.63% | 17.79% | 1 | 0.042409 | 1 | 0.042409 | 0.0085291
MILPITAS 1109XR524 | MILPI | MILPITAS 1109 | SAN JOSE | 7.8802 | 65.8723 | 90.15% | 0 | 1 | 82.17% | 0% | 0 | 0.042366 | 1 | 0.042366 | 0.0053763
FROGTOWN 17021573 | FROGT | FROGTOWN 1702 | STOCKTON | 18.0626 | 46.2084 | 95.86% | 0 | 3 | 100% | 0% | 0 | 0.042352 | 1 | 0.042352 | 0.0023447
SOBRANTE 1102CB | SOBRA | SOBRANTE 1102 | DIABLO | 10.2599 | 28.2629 | 22.78% | 2 | 15 | 98.33% | 12.04% | 0 | 0.042314 | 1 | 0.042314 | 0.0041243
DUNLAP 1102778286 | DUNLA | DUNLAP 1102 | FRESNO | 2.6016 | 93.4441 | 63.93% | 0 | 0 | 100% | 0% | 0 | 0.042218 | 1 | 0.042218 | 0.016228
AUBERRY 1101CB | AUBER | AUBERRY 1101 | FRESNO | 18.1441 | 19.2243 | 60.88% | 0 | 19 | 100% | 0% | 0 | 0.042195 | 1 | 0.042195 | 0.0023255
FITCH MOUNTAIN 11134566 | FITCH | FITCH MOUNTAIN 1113 | SONOMA | 10.4618 | 71.5628 | 83.49% | 1 | 5 | 60.29% | 0% | 0 | 0.042183 | 1 | 0.042183 | 0.004032
PACIFICA 11033907 | PACIF | PACIFICA 1103 | PENINSULA | 3.5027 | 51.2022 | 0% | 4 | 0 | 72.69% | 71.75% | 0 | 0.042148 | 1 | 0.042148 | 0.012033
ALTO 112278672 | ALTO | ALTO 1122 | NORTH BAY | 2.7277 | 18.1694 | 27.03% | 6 | 9 | 33.13% | 66.64% | 0 | 0.042144 | 1 | 0.042144 | 0.01545
VACAVILLE 11088762 | VACAV | VACAVILLE 1108 | SACRAMENTO | 13.206 | 54.7168 | 79.67% | 1 | 3 | 78.91% | 0% | 0 | 0.042096 | 1 | 0.042096 | 0.0031876
PALMER 1101M84 | PALME | PALMER 1101 | LOS PADRES | 19.4244 | 65.3938 | 31.64% | 0 | 6 | 79.33% | 0% | 0 | 0.042007 | 1 | 0.042007 | 0.0021626
APPLE HILL 210251792 | APPLE | APPLE HILL 2102 | SIERRA | 9.3607 | 11.5456 | 100% | 6 | 2 | 100% | 0% | 0 | 0.04191 | 1 | 0.04191 | 0.0044772
KANAKA 11011036 | KANAK | KANAKA 1101 | NORTH VALLEY | 0.60846 | 67.9249 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041796 | 1 | 0.041796 | 0.068691
WISE 1102CB | WISE | WISE 1102 | SIERRA | 18.631 | 17.4842 | 45.37% | 6 | 22 | 98.52% | 0% | 0 | 0.0417 | 1 | 0.0417 | 0.0022382
ANNAPOLIS 1101CB | ANNAP | ANNAPOLIS 1101 | HUMBOLDT | 0.65809 | 81.2301 | 84.52% | 1 | 1 | 100% | 0% | 0 | 0.041698 | 1 | 0.041698 | 0.063362
BEAR VALLEY 21059480 | BEAR | BEAR VALLEY 2105 | YOSEMITE | 12.4081 | 50.2702 | 94.93% | 2 | 0 | 100% | 0% | 0 | 0.041692 | 1 | 0.041692 | 0.0033601
FRUITLAND 11422006 | FRUIT | FRUITLAND 1142 | HUMBOLDT | 8.3587 | 77.2327 | 73.06% | 6 | 2 | 90.12% | 0% | 0 | 0.041689 | 1 | 0.041689 | 0.0049875
TIVY VALLEY 1107R1817 | TIVY | TIVY VALLEY 1107 | FRESNO | 19.042 | 15.3654 | 99.23% | 0 | 5 | 99.01% | 0% | 0 | 0.041647 | 1 | 0.041647 | 0.0021871
ALTO 11251158 | ALTO | ALTO 1125 | NORTH BAY | 2.2748 | 24.9991 | 11.61% | 1 | 1 | 41.4% | 88.18% | 0 | 0.041574 | 1 | 0.041574 | 0.018276
OREGON TRAIL 11031448 | OREGO | OREGON TRAIL 1103 | NORTH VALLEY | 30.932 | 14.1761 | 100% | 1 | 10 | 100% | 0% | 0 | 0.041357 | 1 | 0.041357 | 0.001337
STILLWATER 110248952 | STILL | STILLWATER 1102 | NORTH VALLEY | 10.5922 | 15.961 | 100% | 1 | 3 | 100% | 0% | 0 | 0.041312 | 1 | 0.041312 | 0.0039003
CLAYTON 221355668 | CLAYT | CLAYTON 2213 | DIABLO | 3.8789 | 27.0823 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041308 | 1 | 0.041308 | 0.010649
BEAR VALLEY 21054170 | BEAR | BEAR VALLEY 2105 | YOSEMITE | 9.5178 | 57.2029 | 100% | 3 | 1 | 100% | 0% | 0 | 0.041292 | 1 | 0.041292 | 0.0043384
LOS GATOS 1107CB | LOS G | LOS GATOS 1107 | DE ANZA | 13.6639 | 15.4902 | 38.19% | 1 | 13 | 86.42% | 10.54% | 0 | 0.041286 | 1 | 0.041286 | 0.0030215
LOS GATOS 1101LB40 | LOS G | LOS GATOS 1101 | DE ANZA | 7.214 | 10 | 65.42% | 2 | 3 | 77.51% | 0% | 0 | 0.041155 | 1 | 0.041155 | 0.0057048
CARLOTTA 11214914 | CARLO | CARLOTTA 1121 | HUMBOLDT | 11.4615 | 25.5188 | 70.14% | 16 | 11 | 80.82% | 0% | 0 | 0.041044 | 1 | 0.041044 | 0.003581
TEMPLETON 2110N30 | TEMPL | TEMPLETON 2110 | LOS PADRES | 20.4995 | 52.4771 | 52.2% | 1 | 3 | 100% | 0% | 0 | 0.040875 | 1 | 0.040875 | 0.0019939
TEMPLETON 2110R06 | TEMPL | TEMPLETON 2110 | LOS PADRES | 5.1326 | 51.0168 | 86.51% | 3 | 1 | 19.81% | 33.5% | 0 | 0.040874 | 1 | 0.040874 | 0.0079637
ROSSMOOR 1108CB | ROSSM | ROSSMOOR 1108 | DIABLO | 3.0229 | 50.0663 | 2.294% | 0 | 11 | 53.4% | 61.71% | 0 | 0.040788 | 1 | 0.040788 | 0.013493
OLETA 11014768 | OLETA | OLETA 1101 | STOCKTON | 12.2184 | 44.115 | 100% | 0 | 5 | 89.74% | 0% | 0 | 0.040719 | 1 | 0.040719 | 0.0033326
COLUMBIA HILL 110190730 | COLUM | COLUMBIA HILL 1101 | SIERRA | 8.3212 | 17.8031 | 100% | 1 | 4 | 100% | 5.083% | 1 | 0.040638 | 1 | 0.040638 | 0.0048837
GREENBRAE 11036083 | GREEN | GREENBRAE 1103 | NORTH BAY | 0.34152 | 10 | 10.92% | 0 | 0 | 100% | 67.56% | 0 | 0.040594 | 1 | 0.040594 | 0.11886
SAN LEANDRO U 1109CR002 | SAN L | SAN LEANDRO U 1109 | MISSION | 7.0761 | 10 | 24.57% | 6 | 16 | 90.45% | 0% | 0 | 0.040555 | 1 | 0.040555 | 0.0057312
AUBERRY 1102R309 | AUBER | AUBERRY 1102 | FRESNO | 8.5895 | 21.9499 | 78.92% | 1 | 2 | 100% | 0% | 0 | 0.04051 | 1 | 0.04051 | 0.0047163
CLOVERDALE 110112719 | CLOVE | CLOVERDALE 1101 | SONOMA | 4.9181 | 80.6066 | 85.19% | 0 | 3 | 67.33% | 0% | 0 | 0.040502 | 1 | 0.040502 | 0.0082353
GEYSERVILLE 1102350 | GEYSE | GEYSERVILLE 1102 | SONOMA | 3.9586 | 50.2588 | 84.68% | 0 | 1 | 20.33% | 44.47% | 1 | 0.040497 | 1 | 0.040497 | 0.01023
HAMILTON BRANCH 110118205 | HAMIL | HAMILTON BRANCH 1101 | NORTH VALLEY | 4.0384 | 59.6103 | 100% | 0 | 1 | 100% | 0% | 0 | 0.040382 | 1 | 0.040382 | 0.0099996
MERCED FALLS 11029470 | MERCE | MERCED FALLS 1102 | YOSEMITE | 22.9864 | 12.6287 | 82.62% | 0 | 4 | 100% | 0% | 0 | 0.040338 | 1 | 0.040338 | 0.0017549
EL CERRITO G 1105CB | EL CE | EL CERRITO G 1105 | EAST BAY | 7.4165 | 22.6789 | 12.34% | 2 | 5 | 100% | 20.23% | 0 | 0.040319 | 1 | 0.040319 | 0.0054364
SARATOGA 1105LC14 | SARAT | SARATOGA 1105 | DE ANZA | 9.6151 | 10 | 69.49% | 2 | 9 | 86.08% | 0% | 0 | 0.040305 | 1 | 0.040305 | 0.0041918
SHINGLE SPRINGS 11038752 | SHING | SHINGLE SPRINGS 1103 | SIERRA | 1.8752 | 10 | 77.05% | 0 | 1 | 100% | 7.72% | 0 | 0.040295 | 1 | 0.040295 | 0.021489
PACIFICA 1102CB | PACIF | PACIFICA 1102 | PENINSULA | 2.2873 | 19.4 | 0% | 0 | 1 | 33.56% | 100% | 0 | 0.040266 | 1 | 0.040266 | 0.017604
TEJON 11023760 | TEJON | TEJON 1102 | KERN | 5.5529 | 84.6891 | 100% | 0 | 0 | 84.6% | 0% | 0 | 0.040235 | 1 | 0.040235 | 0.0072458
BEAR VALLEY 2105CB | BEAR | BEAR VALLEY 2105 | YOSEMITE | 3.852 | 80.717 | 62.63% | 2 | 1 | 100% | 0% | 0 | 0.040229 | 1 | 0.040229 | 0.010444
OLETA 11011208 | OLETA | OLETA 1101 | STOCKTON | 32.4243 | 51.211 | 80.1% | 0 | 12 | 85.11% | 0% | 0 | 0.040132 | 1 | 0.040132 | 0.0012377
BEAR VALLEY 210110019 | BEAR | BEAR VALLEY 2101 | YOSEMITE | 1.9804 | 23.7531 | 100% | 0 | 6 | 100% | 0% | 0 | 0.04012 | 1 | 0.04012 | 0.020258
CURTIS 1705CB | CURTI | CURTIS 1705 | YOSEMITE | 13.2215 | 11.2937 | 56.4% | 2 | 15 | 96.23% | 0% | 0 | 0.040107 | 1 | 0.040107 | 0.0030334
PANORAMA 11021632 | PANOR | PANORAMA 1102 | NORTH VALLEY | 8.5492 | 81.3182 | 43.52% | 0 | 3 | 100% | 0% | 0 | 0.040056 | 1 | 0.040056 | 0.0046853
KERCKHOFF 1101R353 | KERCK | KERCKHOFF 1101 | YOSEMITE | 13.7831 | 33.1172 | 88.25% | 0 | 1 | 100% | 0% | 0 | 0.039955 | 1 | 0.039955 | 0.0028988
HALF MOON BAY 11036012 | HALF | HALF MOON BAY 1103 | PENINSULA | 5.8906 | 54.5639 | 76.22% | 11 | 4 | 61.12% | 0% | 0 | 0.039954 | 1 | 0.039954 | 0.0067826
SAN JOAQUIN #2 1103157026 | SAN J | SAN JOAQUIN #2 1103 | YOSEMITE | 3.2012 | 10 | 100% | 2 | 9 | 100% | 0% | 0 | 0.039941 | 1 | 0.039941 | 0.012477
PHILO 11013700 | PHILO | PHILO 1101 | HUMBOLDT | 18.1219 | 64.058 | 52.24% | 7 | 7 | 100% | 0% | 0 | 0.039935 | 1 | 0.039935 | 0.0022037
DEL MONTE 210436720 | DEL M | DEL MONTE 2104 | CENTRAL COAST | 6.1198 | 15.0991 | 78.82% | 1 | 2 | 76.61% | 0% | 0 | 0.039935 | 1 | 0.039935 | 0.0065255
VOLTA 110165764 | VOLTA | VOLTA 1101 | NORTH VALLEY | 10.3627 | 58.9136 | 100% | 1 | 0 | 100% | 0% | 0 | 0.0399 | 1 | 0.0399 | 0.0038503
DEL MONTE 21042762 | DEL M | DEL MONTE 2104 | CENTRAL COAST | 9.4859 | 27.7626 | 17.65% | 2 | 4 | 85.79% | 0% | 0 | 0.03979 | 1 | 0.03979 | 0.0041946
BEAR VALLEY 210110000 | BEAR | BEAR VALLEY 2101 | YOSEMITE | 29.476 | 56.7898 | 61.86% | 4 | 0 | 88.5% | 0% | 0 | 0.039743 | 1 | 0.039743 | 0.0013483
BUELLTON 1101Y26 | BUELL | BUELLTON 1101 | LOS PADRES | 14.0549 | 47.3747 | 54.06% | 1 | 8 | 88.5% | 0% | 0 | 0.039723 | 1 | 0.039723 | 0.0028263
ALTO 1125CB | ALTO | ALTO 1125 | NORTH BAY | 0.27217 | 10 | 45.49% | 2 | 1 | 11.73% | 100% | 0 | 0.039699 | 1 | 0.039699 | 0.14586
VIEJO 2203CB | VIEJO | VIEJO 2203 | CENTRAL COAST | 3.0922 | 10 | 21.75% | 26 | 9 | 92.05% | 0% | 0 | 0.039672 | 1 | 0.039672 | 0.01283
WHITMORE 110145262 | WHITM | WHITMORE 1101 | NORTH VALLEY | 28.7585 | 25.719 | 87.63% | 2 | 2 | 100% | 0% | 0 | 0.03964 | 1 | 0.03964 | 0.0013784
CARLOTTA 112144150 | CARLO | CARLOTTA 1121 | HUMBOLDT | 3.5728 | 56.6428 | 100% | 0 | 1 | 100% | 0% | 0 | 0.039603 | 1 | 0.039603 | 0.011084
CAMBRIA 1101V76 | CAMBR | CAMBRIA 1101 | LOS PADRES | 20.0895 | 13.7459 | 1.828% | 1 | 2 | 100% | 0% | 0 | 0.039572 | 1 | 0.039572 | 0.0019698
ZACA 1101Y72 | ZACA | ZACA 1101 | LOS PADRES | 6.264 | 51.6717 | 31.17% | 0 | 0 | 97.2% | 23.49% | 0 | 0.039557 | 1 | 0.039557 | 0.0063149
MESA 1103M72 | MESA | MESA 1103 | LOS PADRES | 9.6841 | 10 | 75.44% | 1 | 10 | 38.47% | 0% | 0 | 0.039556 | 1 | 0.039556 | 0.0040846
RACETRACK 17038120 | RACET | RACETRACK 1703 | YOSEMITE | 8.8205 | 16.6525 | 57.46% | 3 | 10 | 100% | 16.02% | 1 | 0.03955 | 1 | 0.03955 | 0.0044838
LAYTONVILLE 11011760 | LAYTO | LAYTONVILLE 1101 | HUMBOLDT | 8.2141 | 83.102 | 88.6% | 5 | 4 | 64.9% | 0% | 0 | 0.039524 | 1 | 0.039524 | 0.0048117
SUNOL 1101MR387 | SUNOL | SUNOL 1101 | MISSION | 4.657 | 55.0854 | 92.88% | 0 | 1 | 93.35% | 0% | 0 | 0.03951 | 1 | 0.03951 | 0.008484
UPPER LAKE 11011276 | UPPER | UPPER LAKE 1101 | HUMBOLDT | 12.9332 | 76.2596 | 54.71% | 3 | 4 | 100% | 0% | 0 | 0.039478 | 1 | 0.039478 | 0.0030525
PEORIA 170169124 | PEORI | PEORIA 1701 | YOSEMITE | 2.706 | 13.7023 | 100% | 0 | 2 | 100% | 0% | 0 | 0.039389 | 1 | 0.039389 | 0.014556
FROGTOWN 1702L5407 | FROGT | FROGTOWN 1702 | STOCKTON | 17.9809 | 33.0373 | 100% | 0 | 9 | 98.72% | 0% | 0 | 0.03936 | 1 | 0.03936 | 0.002189
COTTONWOOD 1102CB | COTTO | COTTONWOOD 1102 | NORTH VALLEY | 16.7139 | 23.1081 | 88.08% | 1 | 4 | 71.09% | 0% | 0 | 0.039338 | 1 | 0.039338 | 0.0023536
PIT NO 5 11011658 | PIT N | PIT NO 5 1101 | NORTH VALLEY | 4.5542 | 60.6461 | 59.05% | 1 | 2 | 100% | 0% | 0 | 0.039255 | 1 | 0.039255 | 0.0086194
AUBERRY 1102R1013 | AUBER | AUBERRY 1102 | FRESNO | 12.3506 | 22.637 | 85.13% | 0 | 11 | 100% | 0% | 0 | 0.039152 | 1 | 0.039152 | 0.00317
SILVERADO 2102808 | SILVE | SILVERADO 2102 | NORTH BAY | 1.929 | 85.4925 | 100% | 0 | 0 | 40.02% | 25.27% | 0 | 0.039111 | 1 | 0.039111 | 0.020275
BROWNS VALLEY 110197188 | BROWN | BROWNS VALLEY 1101 | SIERRA | 6.5763 | 19.9978 | 93.03% | 2 | 3 | 95.83% | 0% | 0 | 0.03906 | 1 | 0.03906 | 0.0059395
DUNLAP 11037040 | DUNLA | DUNLAP 1103 | FRESNO | 24.7254 | 12.3243 | 100% | 0 | 2 | 100% | 0% | 0 | 0.039034 | 1 | 0.039034 | 0.0015787
ORINDA 0401N545R | ORIND | ORINDA 0401 | DIABLO | 4.3157 | 10 | 9.802% | 1 | 11 | 83.77% | 52.25% | 0 | 0.038927 | 1 | 0.038927 | 0.0090197
HIGGINS 11097831 | HIGGI | HIGGINS 1109 | SIERRA | 5.5525 | 26.5829 | 100% | 4 | 1 | 100% | 0% | 0 | 0.038882 | 1 | 0.038882 | 0.0070026
OLETA 1102CB | OLETA | OLETA 1102 | STOCKTON | 12.9237 | 28.5426 | 79.87% | 0 | 5 | 85.32% | 0% | 0 | 0.038817 | 1 | 0.038817 | 0.0030036
OCEANO 1102V56 | OCEAN | OCEANO 1102 | LOS PADRES | 9.7421 | 10 | 68.41% | 1 | 15 | 98.35% | 0% | 0 | 0.03877 | 1 | 0.03877 | 0.0039796
SO. CAL. EDISON #3 1101CB | SO. C | SO. CAL. EDISON #3 1101 | FRESNO | 6.4255 | 72.2284 | 15.88% | 0 | 1 | 100% | 34.58% | 0 | 0.038701 | 1 | 0.038701 | 0.0060231
HALF MOON BAY 110369412 | HALF | HALF MOON BAY 1103 | PENINSULA | 16.9285 | 23.3773 | 24.92% | 11 | 5 | 79.06% | 0% | 0 | 0.038624 | 1 | 0.038624 | 0.0022816
GEYSERVILLE 1102522 | GEYSE | GEYSERVILLE 1102 | SONOMA | 8.3806 | 11.5615 | 69.84% | 1 | 7 | 78.98% | 12.25% | 0 | 0.038533 | 1 | 0.038533 | 0.0045979
LUCERNE 1106664 | LUCER | LUCERNE 1106 | HUMBOLDT | 6.0536 | 25.8226 | 47.99% | 4 | 24 | 54.26% | 0% | 0 | 0.038531 | 1 | 0.038531 | 0.006365
MIRABEL 1102334 | MIRAB | MIRABEL 1102 | SONOMA | 5.6083 | 39.7869 | 41.25% | 2 | 2 | 61.12% | 47.7% | 0 | 0.038421 | 1 | 0.038421 | 0.0068508
DUNLAP 11037220 | DUNLA | DUNLAP 1103 | FRESNO | 24.8173 | 17.858 | 99.97% | 1 | 5 | 100% | 0% | 0 | 0.0383 | 1 | 0.0383 | 0.0015433
DIAMOND SPRINGS 110650324 | DIAMO | DIAMOND SPRINGS 1106 | SIERRA | 17.7246 | 10 | 70.6% | 6 | 3 | 87.05% | 0% | 0 | 0.038264 | 1 | 0.038264 | 0.0021588
VOLTA 110149742 | VOLTA | VOLTA 1101 | NORTH VALLEY | 3.4776 | 49.9174 | 84.98% | 0 | 1 | 100% | 0% | 0 | 0.038241 | 1 | 0.038241 | 0.010996
RESERVATION ROAD 11023030 | RESER | RESERVATION ROAD 1102 | CENTRAL COAST | 4.2831 | 56.4796 | 100% | 0 | 1 | 16.48% | 0% | 0 | 0.038229 | 1 | 0.038229 | 0.0089254
POSO MOUNTAIN 21033988 | POSO | POSO MOUNTAIN 2103 | KERN | 17.2368 | 49.5955 | 64.44% | 0 | 0 | 92.36% | 0% | 0 | 0.038161 | 1 | 0.038161 | 0.0022139
DIAMOND SPRINGS 110676088 | DIAMO | DIAMOND SPRINGS 1106 | SIERRA | 11.0713 | 10.8319 | 90.75% | 3 | 3 | 100% | 0% | 0 | 0.038075 | 1 | 0.038075 | 0.0034391
PACIFICA 110311153 | PACIF | PACIFICA 1103 | PENINSULA | 0.48816 | 27.9974 | 36.15% | 0 | 1 | 5.373% | 100% | 0 | 0.038047 | 1 | 0.038047 | 0.077939
PARADISE 110343008 | PARAD | PARADISE 1103 | NORTH VALLEY | 12.9696 | 10 | 78.07% | 7 | 5 | 99.92% | 17.25% | 1 | 0.037995 | 1 | 0.037995 | 0.0029295
CLARK ROAD 110247006 | CLARK | CLARK ROAD 1102 | NORTH VALLEY | 4.5495 | 10 | 42.4% | 2 | 3 | 100% | 41.72% | 0 | 0.037887 | 1 | 0.037887 | 0.0083277
PEORIA 1701CB | PEORI | PEORIA 1701 | YOSEMITE | 8.8374 | 31.1758 | 54.24% | 0 | 6 | 100% | 0% | 0 | 0.037882 | 1 | 0.037882 | 0.0042865
SUMMIT 110148632 | SUMMI | SUMMIT 1101 | SIERRA | 2.7291 | 10 | 63.45% | 5 | 6 | 100% | 0% | 0 | 0.037786 | 1 | 0.037786 | 0.013846
GARBERVILLE 1101CB | GARBE | GARBERVILLE 1101 | HUMBOLDT | 6.497 | 63.3643 | 74.83% | 4 | 3 | 74.77% | 0% | 0 | 0.037653 | 1 | 0.037653 | 0.0057955
BROWNS VALLEY 110193870 | BROWN | BROWNS VALLEY 1101 | SIERRA | 16.0223 | 22.1517 | 92.34% | 3 | 17 | 47.1% | 0% | 0 | 0.037632 | 1 | 0.037632 | 0.0023487
BIG MEADOWS 21012586 | BIG M | BIG MEADOWS 2101 | NORTH VALLEY | 9.5691 | 78.6746 | 93% | 0 | 0 | 87.41% | 0% | 0 | 0.037594 | 1 | 0.037594 | 0.0039286
FRENCH GULCH 11012905 | FRENC | FRENCH GULCH 1101 | NORTH VALLEY | 9.7071 | 49.4271 | 100% | 1 | 0 | 100% | 0% | 0 | 0.037487 | 1 | 0.037487 | 0.0038618
OLEMA 1101602 | OLEMA | OLEMA 1101 | NORTH BAY | 15.0972 | 65.987 | 1.264% | 8 | 10 | 59.79% | 0% | 0 | 0.037469 | 1 | 0.037469 | 0.0024819
DUNLAP 11027849F | DUNLA | DUNLAP 1102 | FRESNO | 8.6653 | 17.4771 | 100% | 3 | 9 | 100% | 0% | 0 | 0.037371 | 1 | 0.037371 | 0.0043127
TEMPLETON 2110R94 | TEMPL | TEMPLETON 2110 | LOS PADRES | 13.9551 | 53.972 | 81.64% | 0 | 3 | 66.74% | 0% | 0 | 0.037368 | 1 | 0.037368 | 0.0026777
DEL MONTE 21032000 | DEL M | DEL MONTE 2103 | CENTRAL COAST | 8.9713 | 10 | 21.71% | 13 | 11 | 98.79% | 0% | 0 | 0.037343 | 1 | 0.037343 | 0.0041624
ELECTRA 110161816 | ELECT | ELECTRA 1101 | STOCKTON | 12.191 | 16.1858 | 89% | 5 | 6 | 100% | 0% | 0 | 0.03728 | 1 | 0.03728 | 0.003058
RED BLUFF 11041302 | RED B | RED BLUFF 1104 | NORTH VALLEY | 14.0918 | 39.8066 | 84.84% | 0 | 4 | 98.04% | 0% | 0 | 0.03726 | 1 | 0.03726 | 0.0026441
AUBERRY 1102R902 | AUBER | AUBERRY 1102 | FRESNO | 15.0447 | 11.5312 | 82.04% | 0 | 7 | 100% | 0% | 0 | 0.037249 | 1 | 0.037249 | 0.0024759
TASSAJARA 2112D514R | TASSA | TASSAJARA 2112 | DIABLO | 3.458 | 10.5192 | 20.09% | 0 | 5 | 72.43% | 34.87% | 0 | 0.03721 | 1 | 0.03721 | 0.010761
HIGGINS 1109CB | HIGGI | HIGGINS 1109 | SIERRA | 22.2012 | 22.658 | 81.89% | 2 | 4 | 95.77% | 0% | 0 | 0.037105 | 1 | 0.037105 | 0.0016713
CALAVERAS CEMENT 110136880 | CALAV | CALAVERAS CEMENT 1101 | STOCKTON | 7.22 | 30.9732 | 81.65% | 0 | 2 | 83.77% | 0% | 0 | 0.037097 | 1 | 0.037097 | 0.0051381
RACETRACK 17036014 | RACET | RACETRACK 1703 | YOSEMITE | 6.8384 | 27.2462 | 64.22% | 2 | 1 | 100% | 0% | 0 | 0.037053 | 1 | 0.037053 | 0.0054184
ALLEGHANY 1101978 | ALLEG | ALLEGHANY 1101 | SIERRA | 13.0219 | 53.8471 | 100% | 3 | 4 | 44.63% | 0% | 0 | 0.037002 | 1 | 0.037002 | 0.0028415
LAKEWOOD 2224D522R | LAKEW | LAKEWOOD 2224 | DIABLO | 0.67815 | 10 | 23.16% | 0 | 1 | 25.38% | 100% | 0 | 0.036972 | 1 | 0.036972 | 0.054519
EDES 1112CR312 | EDES | EDES 1112 | EAST BAY | 3.6853 | 22.7087 | 18.65% | 2 | 11 | 99.92% | 20.18% | 0 | 0.036955 | 1 | 0.036955 | 0.010028
GUALALA 1111445166 | GUALA | GUALALA 1111 | HUMBOLDT | 7.5421 | 19.2895 | 4.143% | 11 | 12 | 79.44% | 0% | 0 | 0.036855 | 1 | 0.036855 | 0.0048865
CLOVERDALE 1101112 | CLOVE | CLOVERDALE 1101 | SONOMA | 19.0544 | 64.0868 | 84.08% | 2 | 8 | 69.85% | 0% | 0 | 0.036824 | 1 | 0.036824 | 0.0019326
TEMPLETON 2113R82 | TEMPL | TEMPLETON 2113 | LOS PADRES | 34.6176 | 62.3861 | 93.76% | 0 | 4 | 50.19% | 6.458% | 0 | 0.03681 | 1 | 0.03681 | 0.0010633
PEORIA 17056697 | PEORI | PEORIA 1705 | YOSEMITE | 4.1363 | 14.6236 | 100% | 1 | 4 | 100% | 0% | 0 | 0.036751 | 1 | 0.036751 | 0.0088851
CURTIS 170565908 | CURTI | CURTIS 1705 | YOSEMITE | 12.8972 | 32.2499 | 79.87% | 2 | 10 | 77.15% | 0% | 0 | 0.036689 | 1 | 0.036689 | 0.0028447
WYANDOTTE 110777578 | WYAND | WYANDOTTE 1107 | NORTH VALLEY | 21.5731 | 10.2179 | 61.38% | 5 | 2 | 66.83% | 0% | 0 | 0.036666 | 1 | 0.036666 | 0.0016996
MORGAN HILL 2104XR018 | MORGA | MORGAN HILL 2104 | SAN JOSE | 4.9492 | 19.6923 | 100% | 0 | 3 | 46.16% | 0% | 0 | 0.03658 | 1 | 0.03658 | 0.0073911
FORT BRAGG A 11041316 | FORT | FORT BRAGG A 1104 | HUMBOLDT | 13.2223 | 12.9501 | 11.54% | 9 | 10 | 96.48% | 0% | 0 | 0.036376 | 1 | 0.036376 | 0.0027511
OLETA 11021204 | OLETA | OLETA 1102 | STOCKTON | 24.7673 | 19.1315 | 95.37% | 0 | 4 | 83.58% | 2.402% | 0 | 0.036314 | 1 | 0.036314 | 0.0014662
CURTIS 170210940 | CURTI | CURTIS 1702 | YOSEMITE | 9.3161 | 16.9626 | 82.71% | 2 | 8 | 88.08% | 0% | 0 | 0.036211 | 1 | 0.036211 | 0.0038869
ROB ROY 210410960 | ROB R | ROB ROY 2104 | CENTRAL COAST | 17.8204 | 13.6401 | 49.6% | 26 | 6 | 63.39% | 0% | 0 | 0.03619 | 1 | 0.03619 | 0.0020308
FORT ROSS 1121CB | FORT | FORT ROSS 1121 | SONOMA | 13.6368 | 88.1189 | 22.5% | 13 | 2 | 100% | 0% | 0 | 0.036054 | 1 | 0.036054 | 0.0026439
LUCERNE 1103CB | LUCER | LUCERNE 1103 | HUMBOLDT | 4.1876 | 10 | 56.07% | 0 | 12 | 95.22% | 0% | 0 | 0.036043 | 1 | 0.036043 | 0.008607
WYANDOTTE 110979932 | WYAND | WYANDOTTE 1109 | NORTH VALLEY | 19.2875 | 10.6134 | 90.79% | 1 | 2 | 59.11% | 0% | 0 | 0.036019 | 1 | 0.036019 | 0.0018675
CALISTOGA 1101CB | CALIS | CALISTOGA 1101 | NORTH BAY | 2.6498 | 39.1806 | 43.07% | 2 | 0 | 27.62% | 49.7% | 0 | 0.036018 | 1 | 0.036018 | 0.013592
SAN MIGUEL 1106CB | SAN M | SAN MIGUEL 1106 | LOS PADRES | 36.8861 | 40.1614 | 99.45% | 1 | 6 | 63.1% | 0% | 0 | 0.035909 | 1 | 0.035909 | 0.0009735
ELECTRA 110136816 | ELECT | ELECTRA 1101 | STOCKTON | 16.3224 | 14.0317 | 85.78% | 2 | 8 | 100% | 0% | 0 | 0.035905 | 1 | 0.035905 | 0.0021997
SANTA YNEZ 1102Y18 | SANTA | SANTA YNEZ 1102 | LOS PADRES | 4.6184 | 77.519 | 99.57% | 1 | 1 | 61.2% | 0% | 0 | 0.035874 | 1 | 0.035874 | 0.0077676
HOPLAND 1101768 | HOPLA | HOPLAND 1101 | HUMBOLDT | 16.1128 | 49.9055 | 90.85% | 1 | 4 | 80.79% | 0% | 0 | 0.03582 | 1 | 0.03582 | 0.0022231
CURTIS 1704CB | CURTI | CURTIS 1704 | YOSEMITE | 13.7734 | 18.3001 | 79.09% | 1 | 5 | 96.53% | 0% | 0 | 0.035785 | 1 | 0.035785 | 0.0025981
HIGHLANDS 1102CB | HIGHL | HIGHLANDS 1102 | HUMBOLDT | 7.3244 | 28.1149 | 80.17% | 1 | 6 | 100% | 0% | 0 | 0.035726 | 1 | 0.035726 | 0.0048776
WYANDOTTE 110913052 | WYAND | WYANDOTTE 1109 | NORTH VALLEY | 19.6896 | 23.3384 | 63.11% | 1 | 2 | 99.03% | 0% | 0 | 0.035725 | 1 | 0.035725 | 0.0018144
GARBERVILLE 11028189 | GARBE | GARBERVILLE 1102 | HUMBOLDT | 1.0385 | 78.4457 | 65.35% | 2 | 1 | 100% | 0% | 0 | 0.035613 | 1 | 0.035613 | 0.034292
AUBERRY 1101R2839 | AUBER | AUBERRY 1101 | FRESNO | 12.6224 | 16.271 | 63.89% | 0 | 4 | 100% | 0% | 0 | 0.035608 | 1 | 0.035608 | 0.002821
SAN LUIS OBISPO 1107V18 | SAN L | SAN LUIS OBISPO 1107 | LOS PADRES | 3.3731 | 28.9632 | 4.194% | 1 | 0 | 84.27% | 30.63% | 0 | 0.035557 | 1 | 0.035557 | 0.010541
PEORIA 17019250 | PEORI | PEORIA 1701 | YOSEMITE | 8.3271 | 28.832 | 87.97% | 0 | 3 | 100% | 0% | 0 | 0.035488 | 1 | 0.035488 | 0.0042618
DESCHUTES 11011652 | DESCH | DESCHUTES 1101 | NORTH VALLEY | 22.782 | 45.1857 | 96.26% | 0 | 4 | 93.2% | 0% | 0 | 0.035474 | 1 | 0.035474 | 0.0015571
BIG RIVER 11015065 | BIG R | BIG RIVER 1101 | HUMBOLDT | 2.2025 | 10 | 42.78% | 5 | 11 | 100% | 0% | 0 | 0.035469 | 1 | 0.035469 | 0.016104
MONTICELLO 11014360 | MONTI | MONTICELLO 1101 | NORTH BAY | 7.4298 | 66.0263 | 57.84% | 4 | 3 | 80.69% | 0% | 0 | 0.035448 | 1 | 0.035448 | 0.004771
BEAR VALLEY 21059570 | BEAR | BEAR VALLEY 2105 | YOSEMITE | 8.0469 | 57.8177 | 84.85% | 0 | 1 | 100% | 0% | 0 | 0.035385 | 1 | 0.035385 | 0.0043973
SAND CREEK 110397354 | SAND | SAND CREEK 1103 | FRESNO | 8.1104 | 10 | 100% | 0 | 1 | 80.11% | 0% | 0 | 0.035362 | 1 | 0.035362 | 0.0043601
PALO SECO 0401CB | PALO | PALO SECO 0401 | EAST BAY | 4.7078 | 10 | 0% | 4 | 1 | 100% | 18.75% | 0 | 0.035354 | 1 | 0.035354 | 0.0075096
BALCH NO 1 1101R372 | BALCH | BALCH NO 1 1101 | FRESNO | 6.0973 | 42.1008 | 100% | 0 | 0 | 100% | 0% | 0 | 0.035267 | 1 | 0.035267 | 0.005784
BOGARD 1101CB | BOGAR | BOGARD 1101 | NORTH VALLEY | 0.51623 | 20.4818 | 100% | 1 | 0 | 100% | 0% | 0 | 0.03523 | 1 | 0.03523 | 0.068244
RED BLUFF 11041566 | RED B | RED BLUFF 1104 | NORTH VALLEY | 11.3669 | 45.5787 | 76.5% | 0 | 1 | 74.23% | 0% | 0 | 0.03504 | 1 | 0.03504 | 0.0030827
CRESCENT MILLS 21012562 | CRESC | CRESCENT MILLS 2101 | NORTH VALLEY | 17.3839 | 76.7012 | 88.81% | 4 | 1 | 50.76% | 0% | 0 | 0.034993 | 1 | 0.034993 | 0.002013
TEJON 11023751 | TEJON | TEJON 1102 | KERN | 20.1546 | 14.4086 | 57.09% | 0 | 4 | 78.15% | 0% | 0 | 0.034903 | 1 | 0.034903 | 0.0017318
WILDWOOD 11011454 | WILDW | WILDWOOD 1101 | NORTH VALLEY | 7.7462 | 36.802 | 100% | 0 | 1 | 100% | 0% | 0 | 0.034751 | 1 | 0.034751 | 0.0044862
ELK CREEK 110193504 | ELK C | ELK CREEK 1101 | NORTH VALLEY | 2.2601 | 54.3949 | 100% | 0 | 0 | 90.07% | 0% | 0 | 0.034745 | 1 | 0.034745 | 0.015373
SILVERADO 2102CB | SILVE | SILVERADO 2102 | NORTH BAY | 0.45935 | 10 | 0% | 0 | 0 | 26.76% | 100% | 0 | 0.034737 | 1 | 0.034737 | 0.075621
DUNBAR 1101CB | DUNBA | DUNBAR 1101 | SONOMA | 2.1801 | 23.6947 | 93.6% | 0 | 2 | 14.87% | 59.74% | 0 | 0.034709 | 1 | 0.034709 | 0.015921
HIGHLANDS 1103568 | HIGHL | HIGHLANDS 1103 | HUMBOLDT | 7.7314 | 14.5235 | 84.3% | 1 | 2 | 84.45% | 0% | 0 | 0.034657 | 1 | 0.034657 | 0.0044826
DUNLAP 1102CB | DUNLA | DUNLAP 1102 | FRESNO | 6.506 | 11.6092 | 99.83% | 1 | 2 | 100% | 0% | 0 | 0.034553 | 1 | 0.034553 | 0.0053109
VACAVILLE 11046542 | VACAV | VACAVILLE 1104 | SACRAMENTO | 14.768 | 37.9322 | 37.99% | 1 | 5 | 100% | 0% | 0 | 0.034546 | 1 | 0.034546 | 0.0023393
HIGGINS 1104533648 | HIGGI | HIGGINS 1104 | SIERRA | 6.7529 | 10 | 96.99% | 2 | 3 | 100% | 0% | 0 | 0.034544 | 1 | 0.034544 | 0.0051155
HOLLISTER 21054048 | HOLLI | HOLLISTER 2105 | CENTRAL COAST | 15.0102 | 85.5727 | 83.97% | 1 | 0 | 53.3% | 0% | 0 | 0.034508 | 1 | 0.034508 | 0.002299
OTTER 110298036 | OTTER | OTTER 1102 | CENTRAL COAST | 9.353 | 32.3159 | 7.526% | 0 | 13 | 100% | 0% | 0 | 0.034494 | 1 | 0.034494 | 0.003688
RACETRACK 170311270 | RACET | RACETRACK 1703 | YOSEMITE | 12.3885 | 27.441 | 56.51% | 3 | 6 | 100% | 0% | 0 | 0.03438 | 1 | 0.03438 | 0.0027751
HIGHLANDS 1103CB | HIGHL | HIGHLANDS 1103 | HUMBOLDT | 10.5045 | 18.0278 | 65.06% | 2 | 6 | 87.07% | 0% | 0 | 0.034275 | 1 | 0.034275 | 0.0032629
ELK CREEK 11012004 | ELK C | ELK CREEK 1101 | NORTH VALLEY | 14.9707 | 82.0149 | 100% | 0 | 1 | 27.7% | 0% | 0 | 0.034268 | 1 | 0.034268 | 0.002289
FRUITLAND 114137410 | FRUIT | FRUITLAND 1141 | HUMBOLDT | 3.8197 | 75.1023 | 57.88% | 10 | 0 | 69.23% | 0% | 0 | 0.034236 | 1 | 0.034236 | 0.008963
FOOTHILL 1102CB | FOOTH | FOOTHILL 1102 | LOS PADRES | 8.141 | 51.8091 | 56.43% | 3 | 6 | 82.95% | 0% | 0 | 0.034219 | 1 | 0.034219 | 0.0042033
MARTELL 11033152 | MARTE | MARTELL 1103 | STOCKTON | 16.8696 | 31.4572 | 87.03% | 0 | 1 | 99.4% | 0% | 0 | 0.034215 | 1 | 0.034215 | 0.0020282
IONE 1101L3141 | IONE | IONE 1101 | STOCKTON | 13.6703 | 41.1561 | 100% | 0 | 0 | 97.4% | 0% | 0 | 0.034177 | 1 | 0.034177 | 0.0025001
MONTICELLO 11011589 | MONTI | MONTICELLO 1101 | NORTH BAY | 4.3101 | 10 | 98.73% | 0 | 3 | 100% | 0% | 0 | 0.034141 | 1 | 0.034141 | 0.0079213
CHOLAME 2102X06 | CHOLA | CHOLAME 2102 | LOS PADRES | 33.5233 | 47.8201 | 99.99% | 1 | 7 | 63.4% | 0% | 0 | 0.034127 | 1 | 0.034127 | 0.001018
WOODACRE 11021280 | WOODA | WOODACRE 1102 | NORTH BAY | 10.5964 | 14.7487 | 31.13% | 2 | 14 | 100% | 0% | 0 | 0.034114 | 1 | 0.034114 | 0.0032194
RACETRACK 17039190 | RACET | RACETRACK 1703 | YOSEMITE | 8.9165 | 23.5588 | 27.68% | 2 | 6 | 100% | 0% | 0 | 0.034029 | 1 | 0.034029 | 0.0038164
FRENCH GULCH 1102CB | FRENC | FRENCH GULCH 1102 | NORTH VALLEY | 1.6951 | 33.4949 | 100% | 0 | 1 | 100% | 0% | 0 | 0.034 | 1 | 0.034 | 0.020057
JESSUP 11019752 | JESSU | JESSUP 1101 | NORTH VALLEY | 3.8979 | 33.5364 | 99.93% | 0 | 1 | 100% | 0% | 0 | 0.033991 | 1 | 0.033991 | 0.0087205
MOUNTAIN QUARRIES 210151584 | MOUNT | MOUNTAIN QUARRIES 2101 | SIERRA | 21.6351 | 34.2949 | 99.29% | 0 | 1 | 100% | 0% | 0 | 0.033987 | 1 | 0.033987 | 0.0015709
MERCED FALLS 110238748 | MERCE | MERCED FALLS 1102 | YOSEMITE | 15.288 | 16.9529 | 100% | 0 | 0 | 100% | 0% | 0 | 0.033981 | 1 | 0.033981 | 0.0022227
FROGTOWN 170211212 | FROGT | FROGTOWN 1702 | STOCKTON | 22.4074 | 27.4478 | 70.17% | 2 | 7 | 100% | 0% | 0 | 0.033949 | 1 | 0.033949 | 0.0015151
BANGOR 11011806 | BANGO | BANGOR 1101 | NORTH VALLEY | 8.946 | 12.2309 | 77.62% | 0 | 5 | 97.6% | 0% | 0 | 0.033897 | 1 | 0.033897 | 0.003789
WILLOW CREEK 110191926 | WILLO | WILLOW CREEK 1101 | HUMBOLDT | 5.6211 | 81.2548 | 100% | 2 | 0 | 52.92% | 0% | 0 | 0.033802 | 1 | 0.033802 | 0.0060134
LOS GATOS 1108LB86 | LOS G | LOS GATOS 1108 | DE ANZA | 4.2689 | 10 | 37.07% | 3 | 5 | 80.57% | 12.91% | 0 | 0.033788 | 1 | 0.033788 | 0.007915
UKIAH 11143606 | UKIAH | UKIAH 1114 | HUMBOLDT | 9.6068 | 79.0327 | 97.2% | 3 | 5 | 58.23% | 0% | 0 | 0.033786 | 1 | 0.033786 | 0.0035169
OILFIELDS 11032757 | OILFI | OILFIELDS 1103 | CENTRAL COAST | 2.6282 | 37.5918 | 90.66% | 0 | 3 | 100% | 0% | 0 | 0.033768 | 1 | 0.033768 | 0.012849
APPLE HILL 210212025 | APPLE | APPLE HILL 2102 | SIERRA | 9.1227 | 10 | 100% | 3 | 0 | 100% | 0% | 0 | 0.033724 | 1 | 0.033724 | 0.0036967
BEAR VALLEY 21054609 | BEAR | BEAR VALLEY 2105 | YOSEMITE | 4.5488 | 18.0167 | 100% | 1 | 5 | 100% | 0% | 0 | 0.033715 | 1 | 0.033715 | 0.0074118
WYANDOTTE 110796390 | WYAND | WYANDOTTE 1107 | NORTH VALLEY | 8.1841 | 10 | 71.02% | 4 | 1 | 80.42% | 0% | 0 | 0.033709 | 1 | 0.033709 | 0.0041188
CAROLANDS 04049024 | CAROL | CAROLANDS 0404 | PENINSULA | 3.5964 | 10 | 16.66% | 1 | 9 | 99.05% | 0% | 0 | 0.033705 | 1 | 0.033705 | 0.0093718
COARSEGOLD 21046210 | COARS | COARSEGOLD 2104 | YOSEMITE | 10.6712 | 44.0621 | 48.52% | 0 | 11 | 100% | 0% | 0 | 0.033703 | 1 | 0.033703 | 0.0031583
ELECTRA 1101L3849 | ELECT | ELECTRA 1101 | STOCKTON | 5.7652 | 16.1295 | 95.19% | 1 | 1 | 100% | 0% | 0 | 0.033619 | 1 | 0.033619 | 0.0058313
HIGGINS 11094189 | HIGGI | HIGGINS 1109 | SIERRA | 3.326 | 25.4516 | 99.91% | 0 | 3 | 100% | 0% | 0 | 0.033551 | 1 | 0.033551 | 0.010087
KONOCTI 1102716 | KONOC | KONOCTI 1102 | HUMBOLDT | 12.6002 | 59.2136 | 49.34% | 2 | 6 | 73.82% | 22.04% | 1 | 0.033546 | 1 | 0.033546 | 0.0026624
REDBUD 1101CB | REDBU | REDBUD 1101 | HUMBOLDT | 4.9191 | 32.5631 | 40.27% | 2 | 12 | 69.43% | 0% | 0 | 0.033542 | 1 | 0.033542 | 0.0068187
PIT NO 3 21011360 | PIT N | PIT NO 3 2101 | NORTH VALLEY | 21.8208 | 46.6037 | 72.84% | 2 | 7 | 96.78% | 0% | 0 | 0.033534 | 1 | 0.033534 | 0.0015368
PIT NO 5 11011660 | PIT N | PIT NO 5 1101 | NORTH VALLEY | 4.8851 | 10 | 71.19% | 4 | 4 | 100% | 0% | 0 | 0.033496 | 1 | 0.033496 | 0.0068568
UPPER LAKE 110175370 | UPPER | UPPER LAKE 1101 | HUMBOLDT | 11.9492 | 35.1291 | 70.43% | 2 | 8 | 80.82% | 6.214% | 1 | 0.033449 | 1 | 0.033449 | 0.0027993
SAND CREEK 1103CB | SAND | SAND CREEK 1103 | FRESNO | 12.8175 | 20.9724 | 70.85% | 0 | 3 | 100% | 0% | 0 | 0.033442 | 1 | 0.033442 | 0.0026091
PLACERVILLE 210623190 | PLACE | PLACERVILLE 2106 | SIERRA | 3.6751 | 24.4138 | 66.27% | 0 | 8 | 100% | 2.399% | 0 | 0.033321 | 1 | 0.033321 | 0.0090667
MARIPOSA 210190180 | MARIP | MARIPOSA 2101 | YOSEMITE | 4.7841 | 52.2474 | 63.07% | 0 | 2 | 100% | 0% | 0 | 0.033288 | 1 | 0.033288 | 0.006958
AUBERRY 1101R322 | AUBER | AUBERRY 1101 | FRESNO | 7.483 | 34.3076 | 99.18% | 0 | 0 | 100% | 0% | 0 | 0.033278 | 1 | 0.033278 | 0.0044471
TEMPLETON 2113A20 | TEMPL | TEMPLETON 2113 | LOS PADRES | 7.0532 | 26.1549 | 66.41% | 2 | 0 | 89.65% | 0% | 0 | 0.033191 | 1 | 0.033191 | 0.0047059
PEORIA 170587222 | PEORI | PEORIA 1705 | YOSEMITE | 5.2686 | 10 | 76.37% | 0 | 4 | 100% | 0% | 0 | 0.03317 | 1 | 0.03317 | 0.0062957
PLACERVILLE 1111CB | PLACE | PLACERVILLE 1111 | SIERRA | 5.5179 | 10 | 61.74% | 2 | 10 | 83.46% | 0% | 0 | 0.033153 | 1 | 0.033153 | 0.0060082
BIG RIVER 110169032 | BIG R | BIG RIVER 1101 | HUMBOLDT | 8.4667 | 31.9768 | 17.96% | 7 | 9 | 100% | 0% | 0 | 0.033152 | 1 | 0.033152 | 0.0039155
RISING RIVER 11019032 | RISIN | RISING RIVER 1101 | NORTH VALLEY | 23.4901 | 16.8815 | 99.94% | 5 | 2 | 100% | 0% | 0 | 0.033124 | 1 | 0.033124 | 0.0014101
ANTLER 11011520 | ANTLE | ANTLER 1101 | NORTH VALLEY | 8.8735 | 30.8958 | 71.85% | 2 | 4 | 100% | 0% | 0 | 0.033121 | 1 | 0.033121 | 0.0037326
TIVY VALLEY 11077380 | TIVY | TIVY VALLEY 1107 | FRESNO | 12.8078 | 20.0234 | 100% | 1 | 4 | 45.52% | 0% | 0 | 0.033102 | 1 | 0.033102 | 0.0025845
PETALUMA C 1108632 | PETAL | PETALUMA C 1108 | SONOMA | 14.7325 | 83.7221 | 19.94% | 0 | 2 | 100% | 0% | 0 | 0.033063 | 1 | 0.033063 | 0.0022442
SAN RAFAEL 110991742 | SAN R | SAN RAFAEL 1109 | NORTH BAY | 5.7363 | 10 | 72.58% | 2 | 1 | 66.36% | 0% | 0 | 0.033036 | 1 | 0.033036 | 0.0057591
STANISLAUS 1701CB | STANI | STANISLAUS 1701 | YOSEMITE | 6.8255 | 50.7734 | 38.45% | 1 | 4 | 100% | 0.8907% | 0 | 0.032969 | 1 | 0.032969 | 0.0048302
WYANDOTTE 11031504 | WYAND | WYANDOTTE 1103 | NORTH VALLEY | 11.3639 | 10 | 55.8% | 3 | 8 | 77.24% | 0% | 0 | 0.032944 | 1 | 0.032944 | 0.002899
OREGON TRAIL 11021382 | OREGO | OREGON TRAIL 1102 | NORTH VALLEY | 5.4732 | 13.8429 | 96.06% | 0 | 1 | 100% | 0% | 0 | 0.03292 | 1 | 0.03292 | 0.0060148
POINT MORETTI 11015104 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 1.8713 | 40.903 | 21.17% | 4 | 0 | 100% | 0% | 0 | 0.032915 | 1 | 0.032915 | 0.017589
PLACERVILLE 1110CB | PLACE | PLACERVILLE 1110 | SIERRA | 11.9057 | 10.8465 | 38.55% | 4 | 14 | 94.9% | 13.5% | 1 | 0.032906 | 1 | 0.032906 | 0.0027639
KERCKHOFF 1101CB | KERCK | KERCKHOFF 1101 | YOSEMITE | 16.9469 | 19.3199 | 39.66% | 0 | 15 | 100% | 0% | 0 | 0.032903 | 1 | 0.032903 | 0.0019415
CALAVERAS CEMENT 110111188 | CALAV | CALAVERAS CEMENT 1101 | STOCKTON | 6.2741 | 29.7373 | 82.62% | 0 | 1 | 100% | 0% | 0 | 0.032851 | 1 | 0.032851 | 0.005236
HALF MOON BAY 11022032 | HALF | HALF MOON BAY 1102 | PENINSULA | 3.27 | 24.2985 | 27.09% | 1 | 0 | 29.71% | 73.93% | 0 | 0.032761 | 1 | 0.032761 | 0.010019
BEAR VALLEY 21014160 | BEAR | BEAR VALLEY 2101 | YOSEMITE | 22.75 | 19.66 | 91.43% | 0 | 7 | 99.99% | 0% | 0 | 0.032723 | 1 | 0.032723 | 0.0014384
HALSEY 1102CB | HALSE | HALSEY 1102 | SIERRA | 8.0128 | 10 | 41.48% | 9 | 5 | 100% | 0% | 0 | 0.032715 | 1 | 0.032715 | 0.0040829
SMARTVILLE 1101CB | SMART | SMARTVILLE 1101 | SIERRA | 15.8868 | 12.1904 | 82.07% | 1 | 6 | 100% | 0% | 0 | 0.032648 | 1 | 0.032648 | 0.0020551
RINCON 1102CB | RINCO | RINCON 1102 | SONOMA | 3.4953 | 21.5241 | 28.33% | 2 | 6 | 98.07% | 7.215% | 1 | 0.032618 | 1 | 0.032618 | 0.0093318
HIGGINS 1104842642 | HIGGI | HIGGINS 1104 | SIERRA | 5.4882 | 10 | 100% | 3 | 1 | 94.43% | 0% | 0 | 0.032606 | 1 | 0.032606 | 0.0059411
HOPLAND 110194006 | HOPLA | HOPLAND 1101 | HUMBOLDT | 13.3558 | 51.6995 | 99.02% | 0 | 1 | 84.05% | 0% | 0 | 0.032603 | 1 | 0.032603 | 0.0024411
CLARK ROAD 110292622 | CLARK | CLARK ROAD 1102 | NORTH VALLEY | 30.8948 | 14.2994 | 87.09% | 2 | 9 | 100% | 0% | 0 | 0.032599 | 1 | 0.032599 | 0.0010552
PLACERVILLE 111219742 | PLACE | PLACERVILLE 1112 | SIERRA | 7.3806 | 10 | 51.29% | 2 | 12 | 99.39% | 0% | 0 | 0.032573 | 1 | 0.032573 | 0.0044133
BIG MEADOWS 21012260 | BIG M | BIG MEADOWS 2101 | NORTH VALLEY | 17.1948 | 71.2696 | 55.9% | 4 | 0 | 76.22% | 0% | 0 | 0.032561 | 1 | 0.032561 | 0.0018937
DESCHUTES 11011380 | DESCH | DESCHUTES 1101 | NORTH VALLEY | 17.936 | 29.5967 | 86.99% | 0 | 4 | 75.95% | 0% | 0 | 0.032554 | 1 | 0.032554 | 0.001815
WYANDOTTE 11071026 | WYAND | WYANDOTTE 1107 | NORTH VALLEY | 21.2978 | 26.1479 | 94.57% | 0 | 2 | 76.21% | 0% | 0 | 0.032543 | 1 | 0.032543 | 0.001528
WYANDOTTE 110366146 | WYAND | WYANDOTTE 1103 | NORTH VALLEY | 0.1568 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.032454 | 1 | 0.032454 | 0.20698
HIGGINS 1107746082 | HIGGI | HIGGINS 1107 | SIERRA | 0.84187 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.032454 | 1 | 0.032454 | 0.03855
CURTIS 17029111 | CURTI | CURTIS 1702 | YOSEMITE | 5.6752 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.032454 | 1 | 0.032454 | 0.0057185
RED BLUFF 110585632 | RED B | RED BLUFF 1105 | NORTH VALLEY | 13.6331 | 10 | 81.59% | 1 | 4 | 91.86% | 0% | 0 | 0.032365 | 1 | 0.032365 | 0.002374
TAR FLAT 04023144 | TAR F | TAR FLAT 0402 | YOSEMITE | 4.9761 | 11.3882 | 27.07% | 0 | 3 | 96.83% | 26.03% | 1 | 0.032346 | 1 | 0.032346 | 0.0065003
TEMPLETON 2113A08 | TEMPL | TEMPLETON 2113 | LOS PADRES | 9.9198 | 65.213 | 45.79% | 1 | 2 | 40.4% | 37.28% | 0 | 0.032324 | 1 | 0.032324 | 0.0032585
ARCATA 11224218 | ARCAT | ARCATA 1122 | HUMBOLDT | 4.9191 | 35.3774 | 67.92% | 2 | 3 | 99.74% | 0% | 0 | 0.032319 | 1 | 0.032319 | 0.0065701
TEMPLETON 2111R86 | TEMPL | TEMPLETON 2111 | LOS PADRES | 10.174 | 35.046 | 79.62% | 2 | 6 | 70.64% | 0% | 0 | 0.032293 | 1 | 0.032293 | 0.003174
WOODSIDE 110411555 | WOODS | WOODSIDE 1104 | PENINSULA | 0.85806 | 10 | 96.59% | 0 | 1 | 100% | 0% | 0 | 0.032229 | 1 | 0.032229 | 0.03756
HIGGINS 11044281 | HIGGI | HIGGINS 1104 | SIERRA | 13.3205 | 11.5983 | 77.05% | 5 | 5 | 100% | 0% | 0 | 0.032224 | 1 | 0.032224 | 0.0024191
BRENTWOOD 21056512 | BRENT | BRENTWOOD 2105 | DIABLO | 0.65133 | 10 | 96.38% | 0 | 1 | 100% | 0% | 0 | 0.032177 | 1 | 0.032177 | 0.049401
BEAR VALLEY 210190550 | BEAR | BEAR VALLEY 2101 | YOSEMITE | 8.0073 | 10 | 99.83% | 0 | 6 | 100% | 0% | 0 | 0.032169 | 1 | 0.032169 | 0.0040175
PIT NO 1 11013312 | PIT N | PIT NO 1 1101 | NORTH VALLEY | 7.449 | 11.3541 | 100% | 0 | 1 | 82.66% | 0% | 0 | 0.032143 | 1 | 0.032143 | 0.0043151
SUMMIT 1102CB | SUMMI | SUMMIT 1102 | SIERRA | 1.0104 | 10 | 73.24% | 1 | 3 | 100% | 0% | 0 | 0.032108 | 1 | 0.032108 | 0.031777
SARATOGA 1107LC26 | SARAT | SARATOGA 1107 | DE ANZA | 5.6494 | 10 | 35.72% | 5 | 4 | 100% | 14.43% | 1 | 0.032092 | 1 | 0.032092 | 0.0056807
ELK 11018779 | ELK 1 | ELK 1101 | HUMBOLDT | 4.2672 | 21.5207 | 21.57% | 6 | 10 | 100% | 0% | 0 | 0.032081 | 1 | 0.032081 | 0.007518
LAKEVILLE 110287432 | LAKEV | LAKEVILLE 1102 | SONOMA | 8.9371 | 82.9673 | 68.1% | 1 | 4 | 65.45% | 0% | 0 | 0.032044 | 1 | 0.032044 | 0.0035856
MARIPOSA 21018030 | MARIP | MARIPOSA 2101 | YOSEMITE | 18.88 | 28.5381 | 67.58% | 1 | 11 | 100% | 1.019% | 0 | 0.032029 | 1 | 0.032029 | 0.0016964
OAKLAND K 1104CR210 | OAKLA | OAKLAND K 1104 | EAST BAY | 2.8215 | 10 | 11.97% | 1 | 0 | 100% | 42.91% | 0 | 0.032016 | 1 | 0.032016 | 0.011347
NARROWS 2101CB | NARRO | NARROWS 2101 | SIERRA | 15.6172 | 42.314 | 50.34% | 2 | 7 | 100% | 0% | 0 | 0.031975 | 1 | 0.031975 | 0.0020474
HAMILTON BRANCH 110187784 | HAMIL | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.4473 | 18.1172 | 99.8% | 0 | 3 | 100% | 0% | 0 | 0.031933 | 1 | 0.031933 | 0.022063
MERCED FALLS 11029460 | MERCE | MERCED FALLS 1102 | YOSEMITE | 8.5158 | 30.9683 | 53.31% | 0 | 0 | 95.4% | 0% | 0 | 0.031807 | 1 | 0.031807 | 0.003735
BRUNSWICK 1103CB | BRUNS | BRUNSWICK 1103 | SIERRA | 6.0294 | 52.8154 | 37.6% | 9 | 3 | 59.53% | 34.21% | 0 | 0.031778 | 1 | 0.031778 | 0.0052705
MARTELL 1102CB | MARTE | MARTELL 1102 | STOCKTON | 6.4004 | 24.1429 | 66.43% | 0 | 4 | 94.03% | 0% | 0 | 0.031753 | 1 | 0.031753 | 0.0049611
BURNEY 11011358 | BURNE | BURNEY 1101 | NORTH VALLEY | 7.0165 | 60.5885 | 76.98% | 1 | 3 | 74.4% | 0% | 0 | 0.0317 | 1 | 0.0317 | 0.004518
CLAY 11031230 | CLAY | CLAY 1103 | STOCKTON | 15.7057 | 29.0509 | 99.85% | 0 | 2 | 80.49% | 0% | 0 | 0.031696 | 1 | 0.031696 | 0.0020181
CURTIS 17046060 | CURTI | CURTIS 1704 | YOSEMITE | 4.0637 | 23.6511 | 61.76% | 0 | 3 | 100% | 0% | 0 | 0.031658 | 1 | 0.031658 | 0.0077904
KONOCTI 1108950 | KONOC | KONOCTI 1108 | HUMBOLDT | 6.231 | 17.4671 | 73.5% | 1 | 1 | 84.02% | 0% | 0 | 0.031636 | 1 | 0.031636 | 0.0050773
OTTER 110263868 | OTTER | OTTER 1102 | CENTRAL COAST | 15.8742 | 30.1739 | 15.67% | 12 | 5 | 100% | 0% | 0 | 0.031617 | 1 | 0.031617 | 0.0019917
FORT ROSS 112137326 | FORT | FORT ROSS 1121 | SONOMA | 5.1708 | 13.0882 | 4.203% | 4 | 1 | 100% | 0% | 0 | 0.031597 | 1 | 0.031597 | 0.0061107
PIT NO 5 11011606 | PIT N | PIT NO 5 1101 | NORTH VALLEY | 5.5302 | 10 | 89.8% | 1 | 2 | 100% | 0% | 0 | 0.031556 | 1 | 0.031556 | 0.0057061
OCEANO 1102V50 | OCEAN | OCEANO 1102 | LOS PADRES | 5.8788 | 10 | 32.53% | 6 | 4 | 56.2% | 0% | 0 | 0.031497 | 1 | 0.031497 | 0.0053577
HIGGINS 11077559 | HIGGI | HIGGINS 1107 | SIERRA | 4.3177 | 10 | 100% | 0 | 6 | 97.65% | 0% | 0 | 0.031488 | 1 | 0.031488 | 0.0072927
FORT BRAGG A 11013113 | FORT | FORT BRAGG A 1101 | HUMBOLDT | 10.0167 | 23.3659 | 35.03% | 10 | 7 | 100% | 0% | 0 | 0.031469 | 1 | 0.031469 | 0.0031416
UPPER LAKE 1101412 | UPPER | UPPER LAKE 1101 | HUMBOLDT | 11.536 | 63.7276 | 55.28% | 0 | 4 | 61.85% | 0% | 0 | 0.031441 | 1 | 0.031441 | 0.0027254
DIAMOND SPRINGS 110656026 | DIAMO | DIAMOND SPRINGS 1106 | SIERRA | 15.0808 | 21.2538 | 81.61% | 2 | 7 | 100% | 0% | 0 | 0.031374 | 1 | 0.031374 | 0.0020804
POINT ARENA 11014923 | POINT | POINT ARENA 1101 | HUMBOLDT | 2.8662 | 57.1036 | 19.76% | 5 | 5 | 100% | 0% | 0 | 0.031366 | 1 | 0.031366 | 0.010943
FORT SEWARD 11211663 | FORT | FORT SEWARD 1121 | HUMBOLDT | 1.9431 | 10 | 100% | 1 | 4 | 100% | 0% | 0 | 0.03133 | 1 | 0.03133 | 0.016124
GUALALA 1112662 | GUALA | GUALALA 1112 | HUMBOLDT | 8.3014 | 33.9068 | 0.6489% | 13 | 22 | 98.43% | 0% | 0 | 0.031273 | 1 | 0.031273 | 0.0037672
FROGTOWN 17016807 | FROGT | FROGTOWN 1701 | STOCKTON | 4.7513 | 29.5232 | 87.38% | 0 | 3 | 100% | 0% | 0 | 0.031186 | 1 | 0.031186 | 0.0065635
OREGON TRAIL 1104CB | OREGO | OREGON TRAIL 1104 | NORTH VALLEY | 10.8574 | 25.7844 | 63.12% | 2 | 12 | 74.06% | 0% | 0 | 0.031086 | 1 | 0.031086 | 0.0028631
MONTICELLO 1101654 | MONTI | MONTICELLO 1101 | NORTH BAY | 8.1004 | 46.4584 | 35.79% | 0 | 2 | 92.66% | 0% | 0 | 0.031073 | 1 | 0.031073 | 0.003836
OAKLAND K 1104CB | OAKLA | OAKLAND K 1104 | EAST BAY | 2.7076 | 10 | 13.99% | 1 | 4 | 100% | 34.6% | 0 | 0.030956 | 1 | 0.030956 | 0.011433
SOBRANTE 1103CB | SOBRA | SOBRANTE 1103 | DIABLO | 3.6739 | 50.7835 | 26.28% | 3 | 6 | 85.25% | 16.11% | 0 | 0.030947 | 1 | 0.030947 | 0.0084236
CURTIS 170411290 | CURTI | CURTIS 1704 | YOSEMITE | 7.9015 | 12.4604 | 83.91% | 5 | 0 | 100% | 0% | 0 | 0.030926 | 1 | 0.030926 | 0.003914
OREGON TRAIL 1103CB | OREGO | OREGON TRAIL 1103 | NORTH VALLEY | 2.7772 | 25.1322 | 81.43% | 2 | 1 | 95.03% | 0% | 0 | 0.030857 | 1 | 0.030857 | 0.011111
MOUNTAIN QUARRIES 210135466 | MOUNT | MOUNTAIN QUARRIES 2101 | SIERRA | 7.4036 | 10 | 90.3% | 2 | 0 | 100% | 0% | 0 | 0.030814 | 1 | 0.030814 | 0.0041621
WEIMAR 11022038 | WEIMA | WEIMAR 1102 | SIERRA | 8.1278 | 10 | 76.79% | 4 | 4 | 100% | 0% | 0 | 0.030781 | 1 | 0.030781 | 0.0037872
GARBERVILLE 1102CB | GARBE | GARBERVILLE 1102 | HUMBOLDT | 10.6146 | 34.8511 | 30.11% | 18 | 9 | 65.56% | 0% | 0 | 0.030692 | 1 | 0.030692 | 0.0028915
JESSUP 11011496 | JESSU | JESSUP 1101 | NORTH VALLEY | 14.7255 | 17.8878 | 100% | 1 | 3 | 90.72% | 1.915% | 1 | 0.030466 | 1 | 0.030466 | 0.002069
VACAVILLE 1111CB | VACAV | VACAVILLE 1111 | SACRAMENTO | 7.7902 | 19.0495 | 34.16% | 0 | 5 | 64.21% | 0% | 0 | 0.030405 | 1 | 0.030405 | 0.0039029
HIGGINS 11041374 | HIGGI | HIGGINS 1104 | SIERRA | 7.2163 | 10 | 85.17% | 5 | 6 | 86.29% | 0% | 0 | 0.030394 | 1 | 0.030394 | 0.0042118
BEAR VALLEY 210576694 | BEAR | BEAR VALLEY 2105 | YOSEMITE | 4.546 | 19.6129 | 100% | 0 | 0 | 100% | 0% | 0 | 0.030391 | 1 | 0.030391 | 0.0066851
WEIMAR 1102CB | WEIMA | WEIMAR 1102 | SIERRA | 12.1704 | 10.9563 | 65.6% | 3 | 8 | 100% | 0% | 0 | 0.030334 | 1 | 0.030334 | 0.0024924
SAN MIGUEL 1104N60 | SAN M | SAN MIGUEL 1104 | LOS PADRES | 7.3672 | 40.8154 | 100% | 0 | 1 | 83.22% | 0% | 0 | 0.030327 | 1 | 0.030327 | 0.0041165
JESSUP 11012839 | JESSU | JESSUP 1101 | NORTH VALLEY | 1.47 | 10 | 100% | 0 | 3 | 100% | 0% | 0 | 0.030308 | 1 | 0.030308 | 0.020618
FRENCH GULCH 1101CB | FRENC | FRENCH GULCH 1101 | NORTH VALLEY | 2.2975 | 10 | 100% | 0 | 3 | 100% | 0% | 0 | 0.030308 | 1 | 0.030308 | 0.013192
LAS POSITAS 2108MR182 | LAS P | LAS POSITAS 2108 | MISSION | 6.1551 | 52.1024 | 25.77% | 0 | 0 | 85.34% | 0% | 0 | 0.030304 | 1 | 0.030304 | 0.0049235
APPLE HILL 210289934 | APPLE | APPLE HILL 2102 | SIERRA | 5.6225 | 10 | 91.39% | 0 | 0 | 100% | 0% | 0 | 0.030296 | 1 | 0.030296 | 0.0053884
SAUSALITO 11021268 | SAUSA | SAUSALITO 1102 | NORTH BAY | 5.0112 | 23.3781 | 0.422% | 3 | 4 | 100% | 0% | 0 | 0.030259 | 1 | 0.030259 | 0.0060383
BALCH NO 1 1101CB | BALCH | BALCH NO 1 1101 | FRESNO | 8.601 | 30.315 | 65.14% | 0 | 10 | 100% | 0% | 0 | 0.030256 | 1 | 0.030256 | 0.0035177
LAURELES 11122142 | LAURE | LAURELES 1112 | CENTRAL COAST | 8.368 | 31.5595 | 39.83% | 4 | 4 | 87.21% | 0% | 0 | 0.030233 | 1 | 0.030233 | 0.003613
CALPELLA 11011204 | CALPE | CALPELLA 1101 | HUMBOLDT | 9.1784 | 21.5734 | 72.42% | 2 | 10 | 70.57% | 0% | 0 | 0.030223 | 1 | 0.030223 | 0.0032928
GARBERVILLE 110256048 | GARBE | GARBERVILLE 1102 | HUMBOLDT | 4.9695 | 84.598 | 7.194% | 2 | 1 | 100% | 0% | 0 | 0.030194 | 1 | 0.030194 | 0.0060759
PEORIA 1705999 | PEORI | PEORIA 1705 | YOSEMITE | 2.3082 | 18.7547 | 99.88% | 0 | 0 | 100% | 0% | 0 | 0.030188 | 1 | 0.030188 | 0.013079
CALISTOGA 1102CB | CALIS | CALISTOGA 1102 | NORTH BAY | 1.4649 | 10 | 27.88% | 0 | 0 | 51.57% | 53.48% | 0 | 0.030163 | 1 | 0.030163 | 0.020591
TIVY VALLEY 11077370 | TIVY | TIVY VALLEY 1107 | FRESNO | 11.4788 | 20.0364 | 68.04% | 0 | 4 | 63.49% | 0% | 0 | 0.030142 | 1 | 0.030142 | 0.0026259
PEORIA 1704877670 | PEORI | PEORIA 1704 | YOSEMITE | 6.3096 | 69.9259 | 47.8% | 1 | 5 | 95.84% | 0% | 0 | 0.030095 | 1 | 0.030095 | 0.0047698
ATASCADERO 11012379 | ATASC | ATASCADERO 1101 | LOS PADRES | 0.72914 | 10 | 100% | 1 | 2 | 100% | 0% | 0 | 0.030081 | 1 | 0.030081 | 0.041256
PEORIA 17013186 | PEORI | PEORIA 1701 | YOSEMITE | 10.0751 | 10 | 99.94% | 1 | 2 | 100% | 0% | 0 | 0.030068 | 1 | 0.030068 | 0.0029844
FULTON 1102CB | FULTO | FULTON 1102 | SONOMA | 1.3424 | 10 | 29.14% | 0 | 0 | 30.03% | 82.09% | 0 | 0.02998 | 1 | 0.02998 | 0.022333
SARATOGA 11075696 | SARAT | SARATOGA 1107 | DE ANZA | 4.0107 | 10 | 57.71% | 6 | 9 | 65.93% | 4.474% | 0 | 0.029972 | 1 | 0.029972 | 0.007473
SOLEDAD 210242506 | SOLED | SOLEDAD 2102 | CENTRAL COAST | 5.4144 | 74.2068 | 100% | 0 | 1 | 19.16% | 0% | 0 | 0.029952 | 1 | 0.029952 | 0.0055319
FORT ROSS 1121134 | FORT | FORT ROSS 1121 | SONOMA | 7.7066 | 23.2401 | 8.01% | 16 | 1 | 95.15% | 0% | 0 | 0.029926 | 1 | 0.029926 | 0.0038832
NARROWS 2102CB | NARRO | NARROWS 2102 | SIERRA | 22.8974 | 13.8368 | 78.07% | 2 | 5 | 93.68% | 0% | 0 | 0.029841 | 1 | 0.029841 | 0.0013032
SPENCE 11223078 | SPENC | SPENCE 1122 | CENTRAL COAST | 9.9861 | 56.9194 | 40.99% | 1 | 2 | 62.29% | 0% | 0 | 0.0298 | 1 | 0.0298 | 0.0029842
PETALUMA C 1109738866 | PETAL | PETALUMA C 1109 | SONOMA | 2.2043 | 62.3821 | 15.29% | 1 | 1 | 81.79% | 0% | 0 | 0.029792 | 1 | 0.029792 | 0.013515
BROWNS VALLEY 110117011 | BROWN | BROWNS VALLEY 1101 | SIERRA | 1.8676 | 10 | 100% | 0 | 2 | 100% | 0% | 0 | 0.029697 | 1 | 0.029697 | 0.015901
SALT SPRINGS 21014913 | SALT | SALT SPRINGS 2101 | STOCKTON | 3.8651 | 10 | 100% | 0 | 2 | 100% | 0% | 0 | 0.029697 | 1 | 0.029697 | 0.0076835
CLAY 11031821 | CLAY | CLAY 1103 | STOCKTON | 2.0901 | 61.2881 | 100% | 0 | 0 | 55.49% | 0% | 0 | 0.029593 | 1 | 0.029593 | 0.014159
WOODSIDE 11049032 | WOODS | WOODSIDE 1104 | PENINSULA | 2.5921 | 10 | 76.95% | 3 | 1 | 32.76% | 43.39% | 0 | 0.029563 | 1 | 0.029563 | 0.011405
WOODSIDE 11018522 | WOODS | WOODSIDE 1101 | PENINSULA | 0.74695 | 65.2984 | 0% | 1 | 0 | 7.949% | 85.4% | 0 | 0.029511 | 1 | 0.029511 | 0.039508
HICKS 111660050 | HICKS | HICKS 1116 | SAN JOSE | 7.9799 | 10 | 69.56% | 2 | 6 | 100% | 0% | 0 | 0.02949 | 1 | 0.02949 | 0.0036955
OREGON TRAIL 110249144 | OREGO | OREGON TRAIL 1102 | NORTH VALLEY | 16.2173 | 16.9745 | 93.48% | 1 | 0 | 76.03% | 0% | 0 | 0.029469 | 1 | 0.029469 | 0.0018172
ALHAMBRA 11058302 | ALHAM | ALHAMBRA 1105 | DIABLO | 8.2556 | 10 | 24.97% | 0 | 12 | 100% | 0% | 0 | 0.029452 | 1 | 0.029452 | 0.0035675
MOUNTAIN QUARRIES 21012422 | MOUNT | MOUNTAIN QUARRIES 2101 | SIERRA | 8.6685 | 16.1435 | 71.9% | 2 | 3 | 100% | 0% | 0 | 0.029445 | 1 | 0.029445 | 0.0033967
SALMON CREEK 110137368 | SALMO | SALMON CREEK 1101 | SONOMA | 7.013 | 10 | 3.2% | 1 | 7 | 100% | 0% | 0 | 0.029331 | 1 | 0.029331 | 0.0041824
SHINGLE SPRINGS 210511172 | SHING | SHINGLE SPRINGS 2105 | SIERRA | 2.0141 | 10 | 66.76% | 1 | 3 | 82.66% | 0% | 0 | 0.029323 | 1 | 0.029323 | 0.014559
CLARK ROAD 110281296 | CLARK | CLARK ROAD 1102 | NORTH VALLEY | 8.8512 | 53.0547 | 65.11% | 1 | 2 | 64.96% | 2.959% | 0 | 0.029241 | 1 | 0.029241 | 0.0033036
PURISIMA 1101Y44 | PURIS | PURISIMA 1101 | LOS PADRES | 10.0257 | 87.5542 | 33.95% | 0 | 2 | 86.13% | 0% | 0 | 0.029127 | 1 | 0.029127 | 0.0029053
WEIMAR 11026175 | WEIMA | WEIMAR 1102 | SIERRA | 2.7281 | 10 | 100% | 0 | 1 | 100% | 0% | 0 | 0.029099 | 1 | 0.029099 | 0.010666
SAND CREEK 11037823F | SAND | SAND CREEK 1103 | FRESNO | 4.6802 | 10 | 100% | 0 | 1 | 100% | 0% | 0 | 0.029099 | 1 | 0.029099 | 0.0062174
HAMILTON BRANCH 11012436 | HAMIL | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.2668 | 10 | 100% | 0 | 1 | 100% | 0% | 0 | 0.029099 | 1 | 0.029099 | 0.022969
HALSEY 11026129 | HALSE | HALSEY 1102 | SIERRA | 3.2034 | 10 | 99.84% | 0 | 1 | 100% | 0% | 0 | 0.029062 | 1 | 0.029062 | 0.0090722
BANGOR 1101CB | BANGO | BANGOR 1101 | NORTH VALLEY | 18.8771 | 14.9118 | 68.16% | 4 | 2 | 88.52% | 0% | 0 | 0.029011 | 1 | 0.029011 | 0.0015369
DUNBAR 110179086 | DUNBA | DUNBAR 1101 | SONOMA | 6.3052 | 21.6901 | 56.75% | 1 | 5 | 90.82% | 0% | 0 | 0.02897 | 1 | 0.02897 | 0.0045946
HIGGINS 11097863 | HIGGI | HIGGINS 1109 | SIERRA | 4.2214 | 12.2843 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028948 | 1 | 0.028948 | 0.0068574
SUNOL 1101MR650 | SUNOL | SUNOL 1101 | MISSION | 1.0325 | 10 | 30.92% | 0 | 2 | 64.08% | 55.43% | 0 | 0.028936 | 1 | 0.028936 | 0.028024
CLARK ROAD 11022070 | CLARK | CLARK ROAD 1102 | NORTH VALLEY | 9.7077 | 20.9726 | 72.7% | 1 | 4 | 86.39% | 12.56% | 0 | 0.028935 | 1 | 0.028935 | 0.0029807
CHOLAME 2102X10 | CHOLA | CHOLAME 2102 | LOS PADRES | 19.7574 | 72.3337 | 100% | 0 | 0 | 44.78% | 0% | 0 | 0.028694 | 1 | 0.028694 | 0.0014523
GUALALA 1112CB | GUALA | GUALALA 1112 | HUMBOLDT | 2.0288 | 40.2405 | 4.36% | 2 | 4 | 94.33% | 0% | 0 | 0.028665 | 1 | 0.028665 | 0.014129
SAN LUIS OBISPO 1104V40 | SAN L | SAN LUIS OBISPO 1104 | LOS PADRES | 11.8926 | 26.5582 | 47.13% | 0 | 7 | 51.44% | 0% | 0 | 0.028654 | 1 | 0.028654 | 0.0024094
WEIMAR 11012764 | WEIMA | WEIMAR 1101 | SIERRA | 6.0658 | 10 | 51% | 1 | 6 | 100% | 0% | 0 | 0.028566 | 1 | 0.028566 | 0.0047094
UKIAH 11151216 | UKIAH | UKIAH 1115 | HUMBOLDT | 13.2203 | 25.9617 | 80.05% | 1 | 10 | 70.13% | 0% | 0 | 0.028563 | 1 | 0.028563 | 0.0021605
VALLEY VIEW 1106 | VALLE | VALLEY VIEW 1106 | EAST BAY | 0.037566 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.75897
OAKLAND X 11066669 | OAKLA | OAKLAND X 1106 | EAST BAY | 0.23409 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.1218
FROGTOWN 1701L3361 | FROGT | FROGTOWN 1701 | STOCKTON | 1.8736 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.015218
SYCAMORE CREEK 1111 | SYCAM | SYCAMORE CREEK 1111 | NORTH VALLEY | 0.19166 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.14876
REEDLEY 1104 | REEDL | REEDLEY 1104 | FRESNO | 0.23841 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.11959
HIGGINS 1109 | HIGGI | HIGGINS 1109 | SIERRA | 0.056072 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.50848
CAYETANO 2111MR444 | CAYET | CAYETANO 2111 | MISSION | 0.15169 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.18796
HIGGINS 11039753 | HIGGI | HIGGINS 1103 | SIERRA | 2.1041 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.01355
OREGON TRAIL 1104 | OREGO | OREGON TRAIL 1104 | NORTH VALLEY | 0.063815 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.44678
WYANDOTTE 1110 | WYAND | WYANDOTTE 1110 | NORTH VALLEY | 0.049002 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.58184
CLOVERDALE 1102801904 | CLOVE | CLOVERDALE 1102 | SONOMA | 0.014995 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 1.9014
ECHO SUMMIT 110155262 | ECHO | ECHO SUMMIT 1101 | (blank) | 0.16554 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.17224
COARSEGOLD 2103 | COARS | COARSEGOLD 2103 | YOSEMITE | 0.14838 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.19216
SAND CREEK 1103 | SAND | SAND CREEK 1103 | FRESNO | 0.037983 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.75065
WEIMAR 1101 | WEIMA | WEIMAR 1101 | SIERRA | 0.067365 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.42324
CALAVERAS CEMENT 1101 | CALAV | CALAVERAS CEMENT 1101 | STOCKTON | 0.0029886 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 9.54
SUNOL 110148180 | SUNOL | SUNOL 1101 | MISSION | 0.015663 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 1.8204
WHITMORE 1101002 | WHITM | WHITMORE 1101 | NORTH VALLEY | 0.0042201 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 6.7562
CALPELLA 1101 | CALPE | CALPELLA 1101 | HUMBOLDT | 0.0052324 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 5.4491
LAYTONVILLE 1102220946 | LAYTO | LAYTONVILLE 1102 | HUMBOLDT | 0.040461 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.70467
CEDAR CREEK 11011362 | CEDAR | CEDAR CREEK 1101 | NORTH VALLEY | 0.015515 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 1.8377
TRIDAM POWERHOUSE 2101CB | TRIDA | TRIDAM POWERHOUSE 2101 | YOSEMITE | 0.050313 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.56668
SALT SPRINGS 21023118 | SALT | SALT SPRINGS 2102 | STOCKTON | 0.07196 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.39621
PIT NO 5 110190846 | PIT N | PIT NO 5 1101 | NORTH VALLEY | 0.092785 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.30729
ECHO SUMMIT 1101CB | ECHO | ECHO SUMMIT 1101 | (blank) | 0.03514 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.028512 | 0.81136
DUNLAP 110239190 | DUNLA | DUNLAP 1102 | FRESNO | 1.8032 | 10 | 99.73% | 0 | 0 | 100% | 0% | 0 | 0.02845 | 1 | 0.02845 | 0.015778
CLAY 110334338 | CLAY | CLAY 1103 | STOCKTON | 7.6368 | 36.5237 | 71.29% | 1 | 2 | 73.13% | 0% | 0 | 0.028445 | 1 | 0.028445 | 0.0037247
COARSEGOLD 2102CB | COARS | COARSEGOLD 2102 | YOSEMITE | 14.0621 | 38.5067 | 44.35% | 2 | 1 | 100% | 4.748% | 0 | 0.028352 | 1 | 0.028352 | 0.0020162
DESCHUTES 1104CB | DESCH | DESCHUTES 1104 | NORTH VALLEY | 12.32 | 22.7091 | 100% | 1 | 6 | 50.17% | 0% | 0 | 0.028343 | 1 | 0.028343 | 0.0023005
LLAGAS 21011451 | LLAGA | LLAGAS 2101 | SAN JOSE | 5.288 | 70.7589 | 100% | 0 | 0 | 57.46% | 0% | 0 | 0.028219 | 1 | 0.028219 | 0.0053363
HOPLAND 1101960 | HOPLA | HOPLAND 1101 | HUMBOLDT | 16.1295 | 41.2103 | 77.4% | 2 | 9 | 74.6% | 0% | 0 | 0.028177 | 1 | 0.028177 | 0.0017469
WOODWARD 210878448 | WOODW | WOODWARD 2108 | FRESNO | 18.5469 | 31.6388 | 94.91% | 1 | 5 | 62.76% | 0% | 0 | 0.028087 | 1 | 0.028087 | 0.0015143
DOBBINS 1101CB | DOBBI | DOBBINS 1101 | SIERRA | 0.67055 | 10 | 81.76% | 0 | 0 | 100% | 0% | 0 | 0.028046 | 1 | 0.028046 | 0.041825
NARROWS 21052748 | NARRO | NARROWS 2105 | SIERRA | 11.8577 | 19.7377 | 85.36% | 3 | 6 | 60.51% | 0% | 0 | 0.02804 | 1 | 0.02804 | 0.0023647
PIT NO 3 21011386 | PIT N | PIT NO 3 2101 | NORTH VALLEY | 5.8084 | 10 | 93.45% | 4 | 0 | 84.51% | 0% | 0 | 0.027889 | 1 | 0.027889 | 0.0048014
FROGTOWN 17028482 | FROGT | FROGTOWN 1702 | STOCKTON | 14.6236 | 52.3445 | 57.04% | 0 | 2 | 100% | 0% | 0 | 0.027885 | 1 | 0.027885 | 0.0019068
HARTLEY 1101698 | HARTL | HARTLEY 1101 | HUMBOLDT | 6.3129 | 57.2881 | 69.42% | 1 | 7 | 61.15% | 0% | 0 | 0.027842 | 1 | 0.027842 | 0.0044103
PLACERVILLE 1112CB | PLACE | PLACERVILLE 1112 | SIERRA | 7.6031 | 10 | 47.53% | 2 | 8 | 81.02% | 0.2042% | 0 | 0.027832 | 1 | 0.027832 | 0.0036607
JOLON 1102CB | JOLON | JOLON 1102 | CENTRAL COAST | 23.7338 | 63.1412 | 51.5% | 0 | 1 | 99.01% | 0% | 0 | 0.02781 | 1 | 0.02781 | 0.0011717
GUALALA 1111887180 | GUALA | GUALALA 1111 | HUMBOLDT | 5.4716 | 10 | 0.3119% | 7 | 8 | 100% | 0% | 0 | 0.027751 | 1 | 0.027751 | 0.0050719
LUCERNE 11034200 | LUCER | LUCERNE 1103 | HUMBOLDT | 4.2514 | 45.4735 | 81.38% | 0 | 1 | 86.14% | 0% | 0 | 0.027721 | 1 | 0.027721 | 0.0065205
OTTER 11022166 | OTTER | OTTER 1102 | CENTRAL COAST | 4.0812 | 30.3358 | 3.172% | 4 | 2 | 100% | 0% | 0 | 0.027673 | 1 | 0.027673 | 0.0067805
ELK CREEK 11012212 | ELK C | ELK CREEK 1101 | NORTH VALLEY | 10.0272 | 85.6358 | 100% | 0 | 1 | 29.79% | 0% | 0 | 0.02765 | 1 | 0.02765 | 0.0027574
STILLWATER 1101CB | STILL | STILLWATER 1101 | NORTH VALLEY | 3.671 | 10 | 87.48% | 3 | 2 | 85.62% | 0% | 0 | 0.027635 | 1 | 0.027635 | 0.0075278
REDBUD 110191960 | REDBU | REDBUD 1101 | HUMBOLDT | 7.0156 | 10 | 50% | 3 | 16 | 100% | 0% | 0 | 0.0275 | 1 | 0.0275 | 0.0039199
CLARK ROAD 11022584 | CLARK | CLARK ROAD 1102 | NORTH VALLEY | 7.9946 | 18.0642 | 99.96% | 1 | 2 | 85.31% | 0% | 0 | 0.0275 | 1 | 0.0275 | 0.0034399
CALAVERAS CEMENT 110111236 | CALAV | CALAVERAS CEMENT 1101 | STOCKTON | 20.1179 | 16.0826 | 47.9% | 0 | 4 | 100% | 0% | 0 | 0.027497 | 1 | 0.027497 | 0.0013668
PINE GROVE 110194936 | PINE | PINE GROVE 1101 | STOCKTON | 9.27 | 10 | 75.09% | 1 | 1 | 100% | 0% | 0 | 0.027484 | 1 | 0.027484 | 0.0029648
GONZALES 11013094 | GONZA | GONZALES 1101 | CENTRAL COAST | 3.5612 | 68.6689 | 100% | 1 | 1 | 39.42% | 0% | 0 | 0.027478 | 1 | 0.027478 | 0.0077159
WOODSIDE 1104CB | WOODS | WOODSIDE 1104 | PENINSULA | 0.34613 | 10 | 13.48% | 0 | 0 | 4.645% | 100% | 0 | 0.027423 | 1 | 0.027423 | 0.079227
PHILO 1102CB | PHILO | PHILO 1102 | HUMBOLDT | 5.5805 | 58.9475 | 61.62% | 10 | 11 | 44.58% | 0% | 0 | 0.027409 | 1 | 0.027409 | 0.0049116
PIT NO 3 2101CB | PIT N | PIT NO 3 2101 | NORTH VALLEY | 4.5423 | 34.7965 | 2.145% | 10 | 3 | 100% | 0% | 0 | 0.027375 | 1 | 0.027375 | 0.0060267
WOODSIDE 1104555372 | WOODS | WOODSIDE 1104 | PENINSULA | 4.1602 | 10 | 35.51% | 2 | 3 | 100% | 0% | 0 | 0.02737 | 1 | 0.02737 | 0.0065791
WHITMORE 1101CB | WHITM | WHITMORE 1101 | NORTH VALLEY | 5.8976 | 20.259 | 68.5% | 1 | 0 | 100% | 0% | 0 | 0.027347 | 1 | 0.027347 | 0.0046369
HIGGINS 11071070 | HIGGI | HIGGINS 1107 | SIERRA | 7.012 | 12.4115 | 99.96% | 1 | 4 | 84.37% | 0% | 0 | 0.027337 | 1 | 0.027337 | 0.0038986
FAIRVIEW 2207P304 | FAIRV | FAIRVIEW 2207 | DIABLO | 5.0581 | 10 | 29.34% | 0 | 2 | 82.96% | 0% | 0 | 0.027316 | 1 | 0.027316 | 0.0054004
STELLING 11109265 | STELL | STELLING 1110 | DE ANZA | 5.4699 | 10 | 92.07% | 0 | 1 | 100% | 0% | 0 | 0.027307 | 1 | 0.027307 | 0.0049922
OILFIELDS 11035175 | OILFI | OILFIELDS 1103 | CENTRAL COAST | 1.9738 | 10 | 100% | 0 | 3 | 89.15% | 0% | 0 | 0.027271 | 1 | 0.027271 | 0.013817
HALSEY 11025739 | HALSE | HALSEY 1102 | SIERRA | 6.6683 | 10 | 67.05% | 2 | 3 | 100% | 0% | 0 | 0.027187 | 1 | 0.027187 | 0.0040771
FRUITLAND 114195324 | FRUIT | FRUITLAND 1141 | HUMBOLDT | 9.0462 | 63.96 | 12.78% | 11 | 1 | 100% | 0% | 0 | 0.027146 | 1 | 0.027146 | 0.0030008
GREENBRAE 1103CB | GREEN | GREENBRAE 1103 | NORTH BAY | 0.06411 | 10 | 0% | 0 | 0 | 1.278% | 100% | 0 | 0.02712 | 1 | 0.02712 | 0.42302
DEL MONTE 21032654 | DEL M | DEL MONTE 2103 | CENTRAL COAST | 1.8437 | 10 | 36.65% | 2 | 2 | 100% | 0% | 0 | 0.027064 | 1 | 0.027064 | 0.014679
MORGAN HILL 2105XR152 | MORGA | MORGAN HILL 2105 | SAN JOSE | 8.3434 | 31.972 | 72.23% | 0 | 5 | 65.24% | 0% | 0 | 0.027024 | 1 | 0.027024 | 0.003239
PIERCY 2110XR258 | PIERC | PIERCY 2110 | SAN JOSE | 14.4387 | 60.8378 | 97.27% | 4 | 1 | 54.5% | 0% | 0 | 0.026979 | 1 | 0.026979 | 0.0018685
BIG MEADOWS 2101CB | BIG M | BIG MEADOWS 2101 | NORTH VALLEY | 2.1059 | 66.4943 | 39.01% | 1 | 2 | 100% | 0% | 0 | 0.026855 | 1 | 0.026855 | 0.012752
LAS GALLINAS A 1106CB | LAS G | LAS GALLINAS A 1106 | NORTH BAY | 4.998 | 10 | 78.22% | 0 | 1 | 31.7% | 39.74% | 0 | 0.026841 | 1 | 0.026841 | 0.0053704
EL CERRITO G 1105BR194 | EL CE | EL CERRITO G 1105 | EAST BAY | 3.0539 | 15.352 | 23.01% | 1 | 2 | 58.3% | 30.42% | 0 | 0.026764 | 1 | 0.026764 | 0.0087641
OLETA 110113478 | OLETA | OLETA 1101 | STOCKTON | 13.3756 | 25.4349 | 51.06% | 1 | 4 | 86.71% | 0% | 0 | 0.02671 | 1 | 0.02671 | 0.001997
POSO MOUNTAIN 2101CB | POSO | POSO MOUNTAIN 2101 | KERN | 4.3131 | 10 | 10.82% | 0 | 0 | 100% | 0% | 0 | 0.026686 | 1 | 0.026686 | 0.0061872
HARTLEY 11011306 | HARTL | HARTLEY 1101 | HUMBOLDT | 8.9139 | 32.0441 | 81.66% | 1 | 4 | 70.23% | 0% | 0 | 0.026684 | 1 | 0.026684 | 0.0029935
MENLO 110212249 | MENLO | MENLO 1102 | PENINSULA | 2.4062 | 33.867 | 49.86% | 2 | 1 | 100% | 0% | 0 | 0.02665 | 1 | 0.02665 | 0.011076
SOBRANTE 1101CB | SOBRA | SOBRANTE 1101 | DIABLO | 13.5487 | 10.8121 | 22.39% | 1 | 13 | 87.75% | 0% | 0 | 0.02661 | 1 | 0.02661 | 0.001964
CAMBRIA 1102CB | CAMBR | CAMBRIA 1102 | LOS PADRES | 14.9946 | 41.8579 | 39.26% | 1 | 1 | 64.1% | 0% | 0 | 0.026518 | 1 | 0.026518 | 0.0017685
PIT NO 3 21011482 | PIT N | PIT NO 3 2101 | NORTH VALLEY | 12.042 | 25.2752 | 56.98% | 0 | 2 | 100% | 0% | 0 | 0.026507 | 1 | 0.026507 | 0.0022012
PENRYN 1107346 | PENRY | PENRYN 1107 | SIERRA | 12.7652 | 20.7142 | 69.91% | 3 | 7 | 51.25% | 0% | 0 | 0.026474 | 1 | 0.026474 | 0.0020739
CASTRO VALLEY 1108MR379 | CASTR | CASTRO VALLEY 1108 | MISSION | 1.2345 | 10 | 98.65% | 0 | 0 | 78.3% | 9.302% | 0 | 0.026453 | 1 | 0.026453 | 0.021428
LUCERNE 1106526 | LUCER | LUCERNE 1106 | HUMBOLDT | 9.9941 | 16.6965 | 53.92% | 1 | 9 | 92.11% | 0% | 0 | 0.026433 | 1 | 0.026433 | 0.0026449
SAN LUIS OBISPO 1103V82 | SAN L | SAN LUIS OBISPO 1103 | LOS PADRES | 6.5219 | 24.8763 | 65.03% | 1 | 11 | 46.53% | 0% | 0 | 0.026432 | 1 | 0.026432 | 0.0040529
PENRYN 11072708 | PENRY | PENRYN 1107 | SIERRA | 8.636 | 10 | 67.69% | 3 | 4 | 79.72% | 0% | 0 | 0.026402 | 1 | 0.026402 | 0.0030572
NARROWS 21052426 | NARRO | NARROWS 2105 | SIERRA | 9.7882 | 10 | 86.21% | 2 | 2 | 56.57% | 0% | 0 | 0.026381 | 1 | 0.026381 | 0.0026951
NAPA 11121302 | NAPA | NAPA 1112 | NORTH BAY | 17.5904 | 30.9393 | 74.37% | 2 | 8 | 52.69% | 0% | 0 | 0.026355 | 1 | 0.026355 | 0.0014983
REDBUD 1102922 | REDBU | REDBUD 1102 | HUMBOLDT | 3.3 | 10 | 97% | 1 | 5 | 42.49% | 0% | 0 | 0.026319 | 1 | 0.026319 | 0.0079753
BANGOR 110131502 | BANGO | BANGOR 1101 | NORTH VALLEY | 11.8542 | 14.4917 | 60.88% | 1 | 3 | 100% | 0% | 0 | 0.026318 | 1 | 0.026318 | 0.0022201
SUMMIT 110249484 | SUMMI | SUMMIT 1102 | SIERRA | 2.6877 | 10 | 54.68% | 1 | 0 | 100% | 0% | 0 | 0.026029 | 1 | 0.026029 | 0.0096847
BAY MEADOWS 210257886 | BAY M | BAY MEADOWS 2102 | PENINSULA | 4.2245 | 10 | 28.89% | 2 | 6 | 80.67% | 0% | 0 | 0.026024 | 1 | 0.026024 | 0.0061603
HAMILTON BRANCH 110137436 | HAMIL | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.0486 | 10 | 99.62% | 2 | 5 | 51.07% | 0% | 0 | 0.025995 | 1 | 0.025995 | 0.024791
FRUITLAND 11413902 | FRUIT | FRUITLAND 1141 | HUMBOLDT | 5.0988 | 85.765 | 7.833% | 1 | 0 | 99.69% | 0% | 0 | 0.025906 | 1 | 0.025906 | 0.0050807
EL CERRITO G 1112CB | EL CE | EL CERRITO G 1112 | EAST BAY | 0.64797 | 10 | 0% | 0 | 0 | 9.809% | 100% | 0 | 0.02588 | 1 | 0.02588 | 0.03994
OCEANO 1104CB | OCEAN | OCEANO 1104 | LOS PADRES | 8.0054 | 24.7481 | 22.23% | 2 | 9 | 52.54% | 10.2% | 1 | 0.025849 | 1 | 0.025849 | 0.003229
MIDDLETOWN 1102514 | MIDDL | MIDDLETOWN 1102 | HUMBOLDT | 4.5797 | 10 | 100% | 1 | 1 | 86.53% | 0% | 0 | 0.025849 | 1 | 0.025849 | 0.0056443
LUCERNE 11062355 | LUCER | LUCERNE 1106 | HUMBOLDT | 0.92313 | 10 | 100% | 1 | 0 | 88.59% | 0% | 0 | 0.02584 | 1 | 0.02584 | 0.027992
FROGTOWN 170232556 | FROGT | FROGTOWN 1702 | STOCKTON | 4.3373 | 25.6533 | 79.39% | 0 | 0 | 69.35% | 0% | 0 | 0.025794 | 1 | 0.025794 | 0.0059469
BIG RIVER 11011286 | BIG R | BIG RIVER 1101 | HUMBOLDT | 4.4303 | 10 | 38.59% | 7 | 9 | 58.78% | 0% | 0 | 0.025767 | 1 | 0.025767 | 0.0058161
MC ARTHUR 11011546 | MC AR | MC ARTHUR 1101 | NORTH VALLEY | 13.3497 | 54.7981 | 96.53% | 1 | 1 | 58.43% | 0% | 0 | 0.025754 | 1 | 0.025754 | 0.0019292
DESCHUTES 11049718 | DESCH | DESCHUTES 1104 | NORTH VALLEY | 6.0769 | 37.0786 | 75.84% | 1 | 1 | 34.09% | 0% | 0 | 0.025713 | 1 | 0.025713 | 0.0042313
RINCON 1103472 | RINCO | RINCON 1103 | SONOMA | 3.3276 | 10 | 93.65% | 0 | 2 | 70.54% | 3.999% | 0 | 0.025694 | 1 | 0.025694 | 0.0077216
JOLON 11027002 | JOLON | JOLON 1102 | CENTRAL COAST | 7.9112 | 56.9708 | 100% | 0 | 0 | 43.93% | 0% | 0 | 0.025691 | 1 | 0.025691 | 0.0032474
POINT ARENA 110183354 | POINT | POINT ARENA 1101 | HUMBOLDT | 5.1346 | 37.1787 | 0% | 2 | 5 | 100% | 0% | 0 | 0.025688 | 1 | 0.025688 | 0.005003
PASO ROBLES 1103N52 | PASO | PASO ROBLES 1103 | LOS PADRES | 6.5425 | 67.4375 | 22.89% | 0 | 0 | 100% | 0% | 0 | 0.025622 | 1 | 0.025622 | 0.0039163
CALPELLA 1101CB | CALPE | CALPELLA 1101 | HUMBOLDT | 10.9748 | 13.9128 | 62.49% | 0 | 11 | 53.93% | 0% | 0 | 0.025545 | 1 | 0.025545 | 0.0023276
OTTER 11022002 | OTTER | OTTER 1102 | CENTRAL COAST | 8.6285 | 34.3246 | 5.086% | 6 | 1 | 100% | 0% | 0 | 0.025475 | 1 | 0.025475 | 0.0029524
CAMP EVERS 210392582 | CAMP | CAMP EVERS 2103 | CENTRAL COAST | 0.22538 | 10 | 0% | 0 | 0 | 8.037% | 100% | 0 | 0.025436 | 1 | 0.025436 | 0.11286
NORTH BRANCH 1101TS1115 | NORTH | NORTH BRANCH 1101 | STOCKTON | 17.6104 | 17.7152 | 77.63% | 1 | 0 | 100% | 0% | 0 | 0.025404 | 1 | 0.025404 | 0.0014426
OLETA 110241396 | OLETA | OLETA 1102 | STOCKTON | 7.3755 | 10 | 56.8% | 3 | 3 | 100% | 0% | 0 | 0.025362 | 1 | 0.025362 | 0.0034387
GREENBRAE 1102CB | GREEN | GREENBRAE 1102 | NORTH BAY | 0.15859 | 10 | 0% | 0 | 0 | 7.352% | 100% | 0 | 0.025266 | 1 | 0.025266 | 0.15932
PERRY 1101CB | PERRY | PERRY 1101 | LOS PADRES | 2.5037 | 27.4854 | 19.25% | 0 | 1 | 100% | 0% | 0 | 0.025246 | 1 | 0.025246 | 0.010083
RALSTON 110148936 | RALST | RALSTON 1101 | PENINSULA | 3.4057 | 10 | 32.09% | 0 | 3 | 56.99% | 0% | 0 | 0.025196 | 1 | 0.025196 | 0.0073982
MARIPOSA 210197142 | MARIP | MARIPOSA 2101 | YOSEMITE | 4.6012 | 28.8872 | 53.68% | 0 | 6 | 100% | 0% | 0 | 0.025194 | 1 | 0.025194 | 0.0054754
PEORIA 170570198 | PEORI | PEORIA 1705 | YOSEMITE | 1.5831 | 45.3965 | 98.01% | 1 | 0 | 49.77% | 0% | 0 | 0.025104 | 1 | 0.025104 | 0.015857
IGNACIO 11011300 | IGNAC | IGNACIO 1101 | NORTH BAY | 2.4856 | 23.8629 | 75.16% | 0 | 4 | 40.74% | 21.73% | 0 | 0.025064 | 1 | 0.025064 | 0.010084
JAMESON 1103CB | JAMES | JAMESON 1103 | SACRAMENTO | 3.6313 | 55.7827 | 92.07% | 0 | 1 | 33.3% | 0% | 0 | 0.025062 | 1 | 0.025062 | 0.0069017
BURNEY 110145984 | BURNE | BURNEY 1101 | NORTH VALLEY | 4.7181 | 10 | 42.42% | 2 | 3 | 98.54% | 0% | 0 | 0.025045 | 1 | 0.025045 | 0.0053082
HIGGINS 1107 | HIGGI | HIGGINS 1107 | SIERRA | 0.013093 | 10 | 100% | 0 | 0 | 86.65% | 0% | 0 | 0.025031 | 1 | 0.025031 | 1.9118
COVELO 110196896 | COVEL | COVELO 1101 | HUMBOLDT | 3.6958 | 52.7111 | 100% | 5 | 0 | 24.03% | 0% | 0 | 0.024981 | 1 | 0.024981 | 0.0067594
FROGTOWN 17027108 | FROGT | FROGTOWN 1702 | STOCKTON | 10.0437 | 39.0873 | 66.95% | 0 | 1 | 78.26% | 0% | 0 | 0.024952 | 1 | 0.024952 | 0.0024843
LLAGAS 21011449 | LLAGA | LLAGAS 2101 | SAN JOSE | 7.6142 | 50.4014 | 99.39% | 2 | 1 | 54.33% | 0% | 0 | 0.024906 | 1 | 0.024906 | 0.003271
CLAYTON 22122944 | CLAYT | CLAYTON 2212 | DIABLO | 14.8336 | 10 | 45.06% | 1 | 4 | 97.25% | 6.81% | 1 | 0.024898 | 1 | 0.024898 | 0.0016785
PERRY 1101V74 | PERRY | PERRY 1101 | LOS PADRES | 2.9727 | 10 | 2.672% | 10 | 7 | 58.33% | 0% | 0 | 0.024878 | 1 | 0.024878 | 0.0083689
LAKEWOOD 210738404 | LAKEW | LAKEWOOD 2107 | DIABLO | 6.7961 | 30.5815 | 25.31% | 5 | 8 | 68.2% | 1.158% | 0 | 0.024865 | 1 | 0.024865 | 0.0036587
GARBERVILLE 11011604 | GARBE | GARBERVILLE 1101 | HUMBOLDT | 4.3333 | 50.687 | 100% | 0 | 3 | 25.13% | 0% | 0 | 0.024833 | 1 | 0.024833 | 0.0057307
GUALALA 1111498 | GUALA | GUALALA 1111 | HUMBOLDT | 2.9971 | 32.4304 | 1.089% | 0 | 12 | 100% | 0% | 0 | 0.024787 | 1 | 0.024787 | 0.0082705
HIGGINS 1104CB | HIGGI | HIGGINS 1104 | SIERRA | 11.5789 | 10 | 38.55% | 1 | 4 | 99.62% | 0% | 0 | 0.024722 | 1 | 0.024722 | 0.0021351
ROSSMOOR 1101L503R | ROSSM | ROSSMOOR 1101 | DIABLO | 4.2657 | 11.5666 | 6.541% | 0 | 11 | 100% | 15.14% | 0 | 0.024651 | 1 | 0.024651 | 0.0057789
HIGGINS 1104498932 | HIGGI | HIGGINS 1104 | SIERRA | 3.4528 | 10 | 98.29% | 1 | 2 | 80.99% | 0% | 0 | 0.024651 | 1 | 0.024651 | 0.0071392
ZACA 1101CB | ZACA | ZACA 1101 | LOS PADRES | 7.3177 | 63.5153 | 26.01% | 0 | 1 | 67.25% | 0% | 0 | 0.024613 | 1 | 0.024613 | 0.0033635
PEORIA 170459596 | PEORI | PEORIA 1704 | YOSEMITE | 19.1476 | 35.0672 | 53.97% | 0 | 6 | 53.15% | 0% | 0 | 0.024608 | 1 | 0.024608 | 0.0012851
GARBERVILLE 1102 | GARBE | GARBERVILLE 1102 | HUMBOLDT | 0.096479 | 11.5575 | 97.17% | 0 | 0 | 86.15% | 0% | 0 | 0.024601 | 1 | 0.024601 | 0.25499
JESSUP 11021550 | JESSU | JESSUP 1102 | NORTH VALLEY | 17.7067 | 29.9161 | 71.58% | 1 | 0 | 80.02% | 0% | 0 | 0.024597 | 1 | 0.024597 | 0.0013891
WOODWARD 2108R2860 | WOODW | WOODWARD 2108 | FRESNO | 11.5924 | 40.5433 | 94.73% | 0 | 1 | 52.86% | 0% | 0 | 0.024579 | 1 | 0.024579 | 0.0021203
MARIPOSA 2102CB | MARIP | MARIPOSA 2102 | YOSEMITE | 6.6916 | 39.3684 | 36.18% | 1 | 6 | 63.39% | 0% | 0 | 0.024571 | 1 | 0.024571 | 0.0036719
HATTON 1101CB | HATTO | HATTON 1101 | CENTRAL COAST | 1.5925 | 10 | 10.22% | 4 | 0 | 100% | 0% | 0 | 0.024551 | 1 | 0.024551 | 0.015416
NORTH BRANCH 110111158 | NORTH | NORTH BRANCH 1101 | STOCKTON | 11.9363 | 47.5829 | 78.02% | 0 | 4 | 41.95% | 0% | 0 | 0.024519 | 1 | 0.024519 | 0.0020542
FITCH MOUNTAIN 111324550 | FITCH | FITCH MOUNTAIN 1113 | SONOMA | 9.0741 | 56.5036 | 70.47% | 3 | 1 | 41.6% | 1.605% | 0 | 0.024475 | 1 | 0.024475 | 0.0026972
HIGGINS 110391052 | HIGGI | HIGGINS 1103 | SIERRA | 0.64834 | 10 | 100% | 0 | 0 | 84.24% | 0% | 0 | 0.024449 | 1 | 0.024449 | 0.03771
TYLER 11051704 | TYLER | TYLER 1105 | NORTH VALLEY | 12.5832 | 29.6218 | 100% | 0 | 8 | 27.35% | 0% | 0 | 0.024427 | 1 | 0.024427 | 0.0019412
CLEAR LAKE 11011302 | CLEAR | CLEAR LAKE 1101 | HUMBOLDT | 6.3736 | 19.3133 | 67.28% | 0 | 7 | 36.56% | 0% | 0 | 0.024377 | 1 | 0.024377 | 0.0038246
CURTIS 1701CB | CURTI | CURTIS 1701 | YOSEMITE | 8.5475 | 34.1417 | 57.96% | 1 | 9 | 68.5% | 0% | 0 | 0.024359 | 1 | 0.024359 | 0.0028498
KIRKER 2104442850 | KIRKE | KIRKER 2104 | DIABLO | 5.4258 | 10 | 43.23% | 0 | 4 | 95.36% | 0% | 0 | 0.024306 | 1 | 0.024306 | 0.0044797
CORNING 110135974 | CORNI | CORNING 1101 | NORTH VALLEY | 0.83179 | 10 | 47.68% | 0 | 0 | 100% | 0% | 0 | 0.02429 | 1 | 0.02429 | 0.029202
SAN JUSTO 110136902 | SAN J | SAN JUSTO 1101 | CENTRAL COAST | 12.1218 | 14.481 | 44.84% | 5 | 5 | 82.09% | 0% | 0 | 0.024262 | 1 | 0.024262 | 0.0020015
BELL 11085703 | BELL | BELL 1108 | SIERRA | 4.5516 | 23.9501 | 96.07% | 0 | 3 | 57.44% | 0% | 0 | 0.024235 | 1 | 0.024235 | 0.0053245
LUCERNE 110693293 | LUCER | LUCERNE 1106 | HUMBOLDT | 0.10086 | 10 | 100% | 0 | 0 | 83.34% | 0% | 0 | 0.024233 | 1 | 0.024233 | 0.24028
PIT NO 1 110170952 | PIT N | PIT NO 1 1101 | NORTH VALLEY | 1.5383 | 10 | 71.41% | 1 | 1 | 89.97% | 0% | 0 | 0.024193 | 1 | 0.024193 | 0.015727
MC ARTHUR 110137388 | MC AR | MC ARTHUR 1101 | NORTH VALLEY | 8.6734 | 54.6058 | 74.62% | 0 | 2 | 69.39% | 0% | 0 | 0.024182 | 1 | 0.024182 | 0.0027881
DUNBAR 1102CB | DUNBA | DUNBAR 1102 | SONOMA | 8.263 | 20.9256 | 44.14% | 4 | 14 | 47.06% | 0% | 0 | 0.024179 | 1 | 0.024179 | 0.0029261
KONOCTI 1108CB | KONOC | KONOCTI 1108 | HUMBOLDT | 6.6517 | 32.6717 | 74.99% | 0 | 6 | 75.6% | 0% | 0 | 0.024164 | 1 | 0.024164 | 0.0036328
CAYETANO 2109CB | CAYET | CAYETANO 2109 | MISSION | 13.0515 | 49.7043 | 30.41% | 0 | 2 | 76.33% | 3.645% | 1 | 0.024131 | 1 | 0.024131 | 0.0018489
SAN RAFAEL 1105534 | SAN R | SAN RAFAEL 1105 | NORTH BAY | 1.348 | 10 | 81.92% | 3 | 4 | 85.31% | 0% | 0 | 0.024098 | 1 | 0.024098 | 0.017876
MORAGA 1104N532R | MORAG | MORAGA 1104 | DIABLO | 4.4858 | 10 | 51.34% | 1 | 5 | 97.29% | 0% | 0 | 0.023997 | 1 | 0.023997 | 0.0053495
RADUM 1105MR282 | RADUM | RADUM 1105 | MISSION | 2.1702 | 17.1089 | 66.03% | 0 | 5 | 34.07% | 37.28% | 0 | 0.023926 | 1 | 0.023926 | 0.011025
SAN LUIS OBISPO 1104V14 | SAN L | SAN LUIS OBISPO 1104 | LOS PADRES | 9.0673 | 22.9917 | 13.75% | 0 | 2 | 100% | 0% | 0 | 0.023923 | 1 | 0.023923 | 0.0026384
MORRO BAY 1102W22 | MORRO | MORRO BAY 1102 | LOS PADRES | 4.8943 | 10 | 4.74% | 0 | 3 | 47.35% | 0% | 0 | 0.023875 | 1 | 0.023875 | 0.0048782
TASSAJARA 210883368 | TASSA | TASSAJARA 2108 | DIABLO | 0.069317 | 10 | 0% | 0 | 0 | 1.551% | 100% | 0 | 0.023873 | 1 | 0.023873 | 0.3444
PINE GROVE 110152088 | PINE | PINE GROVE 1101 | STOCKTON | 2.528 | 10 | 68.63% | 1 | 3 | 100% | 0% | 0 | 0.023865 | 1 | 0.023865 | 0.0094402
OLETA 110151740 | OLETA | OLETA 1101 | STOCKTON | 9.506 | 52.4452 | 97.68% | 1 | 4 | 44.88% | 0% | 0 | 0.023833 | 1 | 0.023833 | 0.0025072
PETALUMA C 110948000 | PETAL | PETALUMA C 1109 | SONOMA | 8.7103 | 40.2232 | 37.55% | 1 | 9 | 65.59% | 0% | 0 | 0.023831 | 1 | 0.023831 | 0.0027359
LAURELES 1111CB | LAURE | LAURELES 1111 | CENTRAL COAST | 7.0885 | 26.8874 | 36.65% | 2 | 3 | 86.44% | 0% | 0 | 0.023775 | 1 | 0.023775 | 0.003354
SPRUCE 0401BR316 | SPRUC | SPRUCE 0401 | EAST BAY | 4.123 | 16.22 | 7.456% | 3 | 5 | 100% | 23.86% | 0 | 0.02375 | 1 | 0.02375 | 0.0057602
HALSEY 11012412 | HALSE | HALSEY 1101 | SIERRA | 5.321 | 10 | 60.58% | 4 | 4 | 100% | 0% | 0 | 0.023732 | 1 | 0.023732 | 0.0044601
CORRAL 110359770 | CORRA | CORRAL 1103 | STOCKTON | 4.5619 | 12.4013 | 100% | 1 | 1 | 62.81% | 0% | 0 | 0.02373 | 1 | 0.02373 | 0.0052019
CAMP EVERS 2106CB | CAMP | CAMP EVERS 2106 | CENTRAL COAST | 0.018997 | 10 | 0% | 0 | 0 | 0.8166% | 100% | 0 | 0.023702 | 1 | 0.023702 | 1.2477
DIAMOND SPRINGS 110740353 | DIAMO | DIAMOND SPRINGS 1107 | SIERRA | 2.2415 | 10 | 74.48% | 1 | 0 | 87.31% | 0% | 0 | 0.023671 | 1 | 0.023671 | 0.010561
BIG RIVER 11011052 | BIG R | BIG RIVER 1101 | HUMBOLDT | 2.9737 | 10 | 0% | 7 | 11 | 77.62% | 0% | 0 | 0.023654 | 1 | 0.023654 | 0.0079544
CLOVERDALE 1102CB | CLOVE | CLOVERDALE 1102 | SONOMA | 0.24384 | 33.3215 | 52.03% | 0 | 0 | 8.095% | 59.2% | 0 | 0.023631 | 1 | 0.023631 | 0.096911
PANOCHE 11034036 | PANOC | PANOCHE 1103 | YOSEMITE | 8.0979 | 77.6294 | 100% | 0 | 1 | 32.26% | 0% | 0 | 0.023574 | 1 | 0.023574 | 0.0029111
HIGHLANDS 1104CB | HIGHL | HIGHLANDS 1104 | HUMBOLDT | 4.6735 | 10 | 74.7% | 0 | 2 | 57.1% | 0% | 0 | 0.023554 | 1 | 0.023554 | 0.0050399
OAKLAND J 1102CR102 | OAKLA | OAKLAND J 1102 | EAST BAY | 0.53101 | 10 | 70.62% | 0 | 2 | 100% | 0% | 0 | 0.023454 | 1 | 0.023454 | 0.044169
MORGAN HILL 2105XR564 | MORGA | MORGAN HILL 2105 | SAN JOSE | 5.4316 | 26.8638 | 49.46% | 0 | 4 | 75.02% | 0% | 0 | 0.023443 | 1 | 0.023443 | 0.004316
CASTRO VALLEY 1108CB | CASTR | CASTRO VALLEY 1108 | MISSION | 1.4946 | 10 | 6.175% | 3 | 1 | 53.21% | 52.04% | 0 | 0.023442 | 1 | 0.023442 | 0.015684
POSO MOUNTAIN 21012181 | POSO | POSO MOUNTAIN 2101 | KERN | 17.1051 | 10 | 29.81% | 0 | 0 | 71.06% | 0% | 0 | 0.023433 | 1 | 0.023433 | 0.0013699
CAL WATER 1102920714 | CAL W | CAL WATER 1102 | KERN | 2.9688 | 76.5947 | 100% | 0 | 0 | 34.42% | 0% | 0 | 0.023426 | 1 | 0.023426 | 0.0078908
LUCERNE 11062327 | LUCER | LUCERNE 1106 | HUMBOLDT | 0.98526 | 10 | 100% | 0 | 1 | 77.76% | 0% | 0 | 0.02342 | 1 | 0.02342 | 0.02377
LAURELES 11122768 | LAURE | LAURELES 1112 | CENTRAL COAST | 6.6363 | 20.652 | 26.91% | 3 | 3 | 82.17% | 0% | 0 | 0.023337 | 1 | 0.023337 | 0.0035166
SUNOL 1101MR297 | SUNOL | SUNOL 1101 | MISSION | 6.0465 | 17.8817 | 28.91% | 0 | 2 | 100% | 17.46% | 0 | 0.023322 | 1 | 0.023322 | 0.0038572
PIT NO 1 11011552 | PIT N | PIT NO 1 1101 | NORTH VALLEY | 9.8425 | 12.4749 | 95.95% | 1 | 1 | 37.18% | 0% | 0 | 0.023212 | 1 | 0.023212 | 0.0023583
MC ARTHUR 11011490 | MC AR | MC ARTHUR 1101 | NORTH VALLEY | 9.1248 | 10 | 79.7% | 0 | 4 | 60.48% | 0% | 0 | 0.02318 | 1 | 0.02318 | 0.0025403
JOLON 11027070 | JOLON | JOLON 1102 | CENTRAL COAST | 4.9443 | 33.893 | 99.18% | 0 | 3 | 30.01% | 0% | 0 | 0.023132 | 1 | 0.023132 | 0.0046785
SUNOL 11018721 | SUNOL | SUNOL 1101 | MISSION | 2.3818 | 51.7237 | 49.03% | 0 | 1 | 76.51% | 0% | 0 | 0.0231 | 1 | 0.0231 | 0.0096985
HIGGINS 1103995672 | HIGGI | HIGGINS 1103 | SIERRA | 2.7769 | 10 | 100% | 1 | 1 | 48.24% | 0% | 0 | 0.02307 | 1 | 0.02307 | 0.0083081
HOLLISTER 21044403 | HOLLI | HOLLISTER 2104 | CENTRAL COAST | 5.3706 | 82.3816 | 100% | 0 | 0 | 28.45% | 0% | 0 | 0.022969 | 1 | 0.022969 | 0.0042769
GEYSERVILLE 110137454 | GEYSE | GEYSERVILLE 1101 | SONOMA | 7.5123 | 58.2774 | 62.29% | 0 | 0 | 62.62% | 0% | 0 | 0.022967 | 1 | 0.022967 | 0.0030573
DESCHUTES 11041370 | DESCH | DESCHUTES 1104 | NORTH VALLEY | 12.2362 | 19.7367 | 98.52% | 1 | 1 | 55.17% | 0% | 0 | 0.022854 | 1 | 0.022854 | 0.0018677
MENLO 11037902 | MENLO | MENLO 1103 | PENINSULA | 11.6802 | 47.4802 | 20.98% | 8 | 4 | 71.01% | 0% | 0 | 0.022804 | 1 | 0.022804 | 0.0019524
GEYSERVILLE 1101166 | GEYSE | GEYSERVILLE 1101 | SONOMA | 11.044 | 32.5571 | 62.6% | 3 | 3 | 68.81% | 0% | 0 | 0.022773 | 1 | 0.022773 | 0.002062
BANGOR 110180670 | BANGO | BANGOR 1101 | NORTH VALLEY | 14.7472 | 18.2405 | 76% | 0 | 1 | 89.02% | 0% | 0 | 0.02277 | 1 | 0.02277 | 0.0015441
PEORIA 17048040 | PEORI | PEORIA 1704 | YOSEMITE | 8.9787 | 41.627 | 97.88% | 2 | 3 | 34.87% | 0% | 0 | 0.02277 | 1 | 0.02277 | 0.002536
SISQUOC 1102M54 | SISQU | SISQUOC 1102 | LOS PADRES | 17.0931 | 11.3388 | 62.6% | 1 | 3 | 56.95% | 1.375% | 0 | 0.022753 | 1 | 0.022753 | 0.0013311
ELK 11011298 | ELK 1 | ELK 1101 | HUMBOLDT | 13.5042 | 33.0971 | 18.55% | 6 | 11 | 83.72% | 0% | 0 | 0.022711 | 1 | 0.022711 | 0.0016818
SILVERADO 2102714 | SILVE | SILVERADO 2102 | NORTH BAY | 4.37 | 45.4785 | 19.37% | 4 | 5 | 38.82% | 6.698% | 0 | 0.022688 | 1 | 0.022688 | 0.0051917
HALF MOON BAY 11036065 | HALF | HALF MOON BAY 1103 | PENINSULA | 6.2488 | 59.5208 | 36.98% | 1 | 1 | 91.2% | 0% | 0 | 0.02267 | 1 | 0.02267 | 0.0036278
PEORIA 17019811 | PEORI | PEORIA 1701 | YOSEMITE | 5.5301 | 39.6322 | 92.09% | 0 | 0 | 62.43% | 0% | 0 | 0.022586 | 1 | 0.022586 | 0.0040843
UKIAH 111129452 | UKIAH | UKIAH 1111 | HUMBOLDT | 3.6752 | 77.2683 | 100% | 0 | 0 | 30.05% | 0% | 0 | 0.022547 | 1 | 0.022547 | 0.0061348
PEORIA 170176030 | PEORI | PEORIA 1701 | YOSEMITE | 5.4729 | 32.855 | 62.69% | 0 | 1 | 88.26% | 0% | 0 | 0.022385 | 1 | 0.022385 | 0.0040901
SUMMIT 11022302 | SUMMI | SUMMIT 1102 | SIERRA | 1.4575 | 10 | 25.54% | 1 | 4 | 100% | 0% | 0 | 0.022343 | 1 | 0.022343 | 0.01533
ARCATA 11211206 | ARCAT | ARCATA 1121 | HUMBOLDT | 6.629 | 50.041 | 6.756% | 12 | 6 | 42.25% | 0% | 0 | 0.022231 | 1 | 0.022231 | 0.0033535
BIG MEADOWS 21012248 | BIG M | BIG MEADOWS 2101 | NORTH VALLEY | 9.1467 | 42.3693 | 7.268% | 0 | 1 | 100% | 0% | 0 | 0.022222 | 1 | 0.022222 | 0.0024295
STAFFORD 11021019 | STAFF | STAFFORD 1102 | NORTH BAY | 0.54264 | 10 | 100% | 0 | 0 | 74.36% | 0% | 0 | 0.022194 | 1 | 0.022194 | 0.0409
GOLDTREE 1108CB | GOLDT | GOLDTREE 1108 | LOS PADRES | 2.5563 | 36.4917 | 29.18% | 2 | 3 | 52.35% | 0% | 0 | 0.022193 | 1 | 0.022193 | 0.0086818
MC ARTHUR 11011544 | MC AR | MC ARTHUR 1101 | NORTH VALLEY | 14.33 | 61.0373 | 66.86% | 0 | 1 | 51.35% | 0% | 0 | 0.022186 | 1 | 0.022186 | 0.0015483
HALF MOON BAY 11036018 | HALF | HALF MOON BAY 1103 | PENINSULA | 14.4915 | 43.0242 | 18.48% | 5 | 3 | 79.35% | 0% | 0 | 0.022185 | 1 | 0.022185 | 0.0015309
PALMER 1101M82 | PALME | PALMER 1101 | LOS PADRES | 10.3483 | 48.0186 | 61.68% | 0 | 5 | 69.3% | 0% | 0 | 0.022153 | 1 | 0.022153 | 0.0021407
BIG RIVER 11012183 | BIG R | BIG RIVER 1101 | HUMBOLDT | 2.6396 | 37.6233 | 33.84% | 1 | 4 | 100% | 0% | 0 | 0.022133 | 1 | 0.022133 | 0.0083848
BELL 1109CB | BELL | BELL 1109 | SIERRA | 13.433 | 10 | 50.92% | 4 | 3 | 76.11% | 0% | 0 | 0.022099 | 1 | 0.022099 | 0.0016451
SOLEDAD 21027048 | SOLED | SOLEDAD 2102 | CENTRAL COAST | 16.945 | 59.8739 | 88.98% | 0 | 0 | 48.94% | 0% | 0 | 0.022097 | 1 | 0.022097 | 0.001304
KONOCTI 11084039 | KONOC | KONOCTI 1108 | HUMBOLDT | 1.6026 | 10 | 100% | 0 | 2 | 69.54% | 0% | 0 | 0.022058 | 1 | 0.022058 | 0.013764
KERCKHOFF 1101R308 | KERCK | KERCKHOFF 1101 | YOSEMITE | 3.8623 | 40.5798 | 35.11% | 0 | 3 | 100% | 0% | 0 | 0.022056 | 1 | 0.022056 | 0.0057106
LUCERNE 11031663 | LUCER | LUCERNE 1103 | HUMBOLDT | 1.2106 | 10 | 52.73% | 0 | 6 | 100% | 0% | 0 | 0.022038 | 1 | 0.022038 | 0.018204
BRUNSWICK 111061602 | BRUNS | BRUNSWICK 1110 | SIERRA | 9.4416 | 27.4436 | 52.21% | 4 | 4 | 73.99% | 0% | 0 | 0.022016 | 1 | 0.022016 | 0.0023318
MC ARTHUR 110138998 | MC AR | MC ARTHUR 1101 | NORTH VALLEY | 11.0305 | 56.1464 | 63.76% | 0 | 2 | 67.61% | 0% | 0 | 0.021999 | 1 | 0.021999 | 0.0019944
CURTIS 170356972 | CURTI | CURTIS 1703 | YOSEMITE | 8.4449 | 49.5291 | 11.99% | 0 | 2 | 100% | 0.5389% | 1 | 0.02188 | 1 | 0.02188 | 0.0025909
RIO DELL 11028852 | RIO D | RIO DELL 1102 | HUMBOLDT | 3.7546 | 61.6723 | 39.96% | 1 | 3 | 79.33% | 0% | 0 | 0.021849 | 1 | 0.021849 | 0.0058191
SAN CARLOS 11049052 | SAN C | SAN CARLOS 1104 | PENINSULA | 4.4833 | 10 | 33.62% | 0 | 5 | 90.23% | 0% | 0 | 0.021835 | 1 | 0.021835 | 0.0048704
CAYETANO 2109MR572 | CAYET | CAYETANO 2109 | MISSION | 8.1822 | 10 | 47.67% | 0 | 2 | 66.51% | 19.49% | 0 | 0.021821 | 1 | 0.021821 | 0.0026669
WOODSIDE 11049030 | WOODS | WOODSIDE 1104 | PENINSULA | 2.2354 | 10 | 77.85% | 0 | 2 | 86.64% | 0% | 0 | 0.021812 | 1 | 0.021812 | 0.0097575
VIEJO 22012064 | VIEJO | VIEJO 2201 | CENTRAL COAST | 0.87679 | 10 | 42.79% | 0 | 3 | 100% | 0% | 0 | 0.021793 | 1 | 0.021793 | 0.024856
SALT SPRINGS 21013116 | SALT | SALT SPRINGS 2101 | STOCKTON | 0.70592 | 10 | 100% | 0 | 1 | 70.33% | 0% | 0 | 0.021776 | 1 | 0.021776 | 0.030848
FOOTHILL 110299432 | FOOTH | FOOTHILL 1102 | LOS PADRES | 0.73004 | 62.5798 | 100% | 0 | 3 | 16.66% | 0% | 0 | 0.021721 | 1 | 0.021721 | 0.029753
FORT BRAGG A 11013100 | FORT | FORT BRAGG A 1101 | HUMBOLDT | 12.9058 | 10 | 7.343% | 8 | 11 | 88.01% | 0% | 0 | 0.021681 | 1 | 0.021681 | 0.0016799
JESSUP 11013383 | JESSU | JESSUP 1101 | NORTH VALLEY | 1.283 | 10 | 88.48% | 0 | 0 | 68.06% | 0% | 0 | 0.021667 | 1 | 0.021667 | 0.016887
REDBUD 1102510 | REDBU | REDBUD 1102 | HUMBOLDT | 6.0638 | 23.833 | 59.82% | 2 | 2 | 75.22% | 0% | 0 | 0.02163 | 1 | 0.02163 | 0.0035671
SAN RAFAEL 1104802 | SAN R | SAN RAFAEL 1104 | NORTH BAY | 7.826 | 10 | 18.94% | 3 | 4 | 72.62% | 0% | 0 | 0.021588 | 1 | 0.021588 | 0.0027585
CMC 1101CB | CMC 1 | CMC 1101 | LOS PADRES | 2.0609 | 25.5297 | 52.24% | 0 | 0 | 100% | 0% | 0 | 0.021532 | 1 | 0.021532 | 0.010448
MENDOCINO 1101450 | MENDO | MENDOCINO 1101 | HUMBOLDT | 5.6815 | 36.3951 | 100% | 0 | 2 | 30.28% | 3.061% | 1 | 0.021431 | 1 | 0.021431 | 0.0037721
COTATI 110361736 | COTAT | COTATI 1103 | SONOMA | 9.9372 | 78.8786 | 12.09% | 0 | 11 | 59.74% | 0% | 0 | 0.02142 | 1 | 0.02142 | 0.0021555
OTTER 1101440 | OTTER | OTTER 1101 | CENTRAL COAST | 8.556 | 21.3917 | 0.8557% | 24 | 4 | 77.84% | 0% | 0 | 0.021414 | 1 | 0.021414 | 0.0025028
SARATOGA 1106LC24 | SARAT | SARATOGA 1106 | DE ANZA | 6.2415 | 10 | 42.44% | 3 | 7 | 55.48% | 10.64% | 0 | 0.021404 | 1 | 0.021404 | 0.0034293
HIGHLANDS 110484640 | HIGHL | HIGHLANDS 1104 | HUMBOLDT | 0.56405 | 10 | 72.8% | 1 | 1 | 76.24% | 0% | 0 | 0.021388 | 1 | 0.021388 | 0.037919
PEORIA 1704CB | PEORI | PEORIA 1704 | YOSEMITE | 8.3627 | 39.95 | 39.21% | 0 | 3 | 93.61% | 0% | 0 | 0.021324 | 1 | 0.021324 | 0.0025499
RED BLUFF 1101 | RED B | RED BLUFF 1101 | NORTH VALLEY | 0.18711 | 22.4749 | 100% | 0 | 0 | 61.69% | 0% | 0 | 0.021308 | 1 | 0.021308 | 0.11388
HAMILTON BRANCH 11012082 | HAMIL | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.6281 | 32.2338 | 100% | 1 | 0 | 53.18% | 0% | 0 | 0.021199 | 1 | 0.021199 | 0.013021
OLEMA 110175686 | OLEMA | OLEMA 1101 | NORTH BAY | 3.5949 | 80.3245 | 25.14% | 0 | 0 | 69.82% | 0% | 0 | 0.021165 | 1 | 0.021165 | 0.0058874
DUNBAR 1102528 | DUNBA | DUNBAR 1102 | SONOMA | 3.4638 | 30.5853 | 54.13% | 1 | 3 | 85.5% | 0% | 0 | 0.021137 | 1 | 0.021137 | 0.0061022
PEORIA 170510580 | PEORI | PEORIA 1705 | YOSEMITE | 6.4351 | 24.7232 | 93.54% | 1 | 4 | 54.9% | 0% | 0 | 0.021125 | 1 | 0.021125 | 0.0032828
COTTONWOOD 11029026 | COTTO | COTTONWOOD 1102 | NORTH VALLEY | 14.1835 | 17.7686 | 84.41% | 1 | 2 | 58.01% | 0% | 0 | 0.021122 | 1 | 0.021122 | 0.0014892
PUTAH CREEK 11028352 | PUTAH | PUTAH CREEK 1102 | SACRAMENTO | 4.7179 | 43.9192 | 97.12% | 0 | 4 | 40.06% | 0% | 0 | 0.021102 | 1 | 0.021102 | 0.0044729
ORINDA 04013442 | ORIND | ORINDA 0401 | DIABLO | 4.9574 | 14.2459 | 5.153% | 4 | 12 | 73.89% | 0% | 0 | 0.021076 | 1 | 0.021076 | 0.0042514
BURNEY 11011322 | BURNE | BURNEY 1101 | NORTH VALLEY | 16.3381 | 29.8396 | 61.19% | 0 | 0 | 87.48% | 0% | 0 | 0.021071 | 1 | 0.021071 | 0.0012897
JOLON 11027040 | JOLON | JOLON 1102 | CENTRAL COAST | 20.3578 | 63.5106 | 29.02% | 0 | 1 | 88.79% | 0% | 0 | 0.02105 | 1 | 0.02105 | 0.001034
HATTON 11012026 | HATTO | HATTON 1101 | CENTRAL COAST | 6.3396 | 38.9334 | 46.88% | 0 | 2 | 62.03% | 0% | 0 | 0.021035 | 1 | 0.021035 | 0.003318
LAURELES 1112438 | LAURE | LAURELES 1112 | CENTRAL COAST | 5.2403 | 57.3236 | 0.9038% | 0 | 0 | 91.32% | 0% | 0 | 0.020992 | 1 | 0.020992 | 0.004006
EDES 1112CR308 | EDES | EDES 1112 | EAST BAY | 3.5907 | 10 | 15.92% | 2 | 4 | 100% | 0% | 0 | 0.020943 | 1 | 0.020943 | 0.0058324
PEORIA 170590374 | PEORI | PEORIA 1705 | YOSEMITE | 3.6064 | 10 | 81.75% | 0 | 1 | 81.35% | 0% | 0 | 0.020938 | 1 | 0.020938 | 0.0058057
CLAY 11037124 | CLAY | CLAY 1103 | STOCKTON | 8.9452 | 50.0578 | 97.24% | 0 | 1 | 27.91% | 0% | 0 | 0.020936 | 1 | 0.020936 | 0.0023405
SYCAMORE CREEK 1111CB | SYCAM | SYCAMORE CREEK 1111 | NORTH VALLEY | 8.3942 | 56.8563 | 45.31% | 1 | 3 | 47.06% | 0% | 0 | 0.020907 | 1 | 0.020907 | 0.0024907
SAN MIGUEL 1104R66 | SAN M | SAN MIGUEL 1104 | LOS PADRES | 8.3967 | 54.4532 | 99.05% | 0 | 3 | 18.97% | 0% | 0 | 0.020883 | 1 | 0.020883 | 0.002487
COVELO 110137328 | COVEL | COVELO 1101 | HUMBOLDT | 3.9213 | 85.1621 | 100% | 0 | 0 | 16.63% | 0% | 0 | 0.020839 | 1 | 0.020839 | 0.0053143
JOLON 1103CB | JOLON | JOLON 1103 | CENTRAL COAST | 14.8367 | 53.4685 | 41.31% | 0 | 2 | 82.37% | 0% | 0 | 0.020833 | 1 | 0.020833 | 0.0014042
GEYSERVILLE 110135492 | GEYSE | GEYSERVILLE 1101 | SONOMA | 8.4529 | 69.0353 | 85.9% | 0 | 0 | 39.22% | 0% | 0 | 0.020833 | 1 | 0.020833 | 0.0024646
HOLLISTER 2102855412 | HOLLI | HOLLISTER 2102 | CENTRAL COAST | 25.5091 | 59.8315 | 42.36% | 0 | 0 | 81.28% | 0% | 0 | 0.020819 | 1 | 0.020819 | 0.00081614
IGNACIO 1104450582 | IGNAC | IGNACIO 1104 | NORTH BAY | 3.8063 | 10 | 29.85% | 0 | 4 | 90.17% | 0% | 0 | 0.020738 | 1 | 0.020738 | 0.0054483
PANORAMA 11021342 | PANOR | PANORAMA 1102 | NORTH VALLEY | 11.6409 | 39.043 | 100% | 0 | 1 | 45.41% | 0% | 0 | 0.020716 | 1 | 0.020716 | 0.0017796
ELK 110191336 | ELK 1 | ELK 1101 | HUMBOLDT | 7.8266 | 12.5917 | 0% | 14 | 5 | 92.25% | 0% | 0 | 0.020708 | 1 | 0.020708 | 0.0026458
RISING RIVER 1101CB | RISIN | RISING RIVER 1101 | NORTH VALLEY | 9.43 | 10 | 88.75% | 1 | 2 | 70.58% | 0% | 0 | 0.020612 | 1 | 0.020612 | 0.0021858
COARSEGOLD 210410030 | COARS | COARSEGOLD 2104 | YOSEMITE | 15.7445 | 10.7109 | 33.01% | 0 | 3 | 88.51% | 0% | 0 | 0.020603 | 1 | 0.020603 | 0.0013086
FROGTOWN 170236870 | FROGT | FROGTOWN 1702 | STOCKTON | 2.2467 | 10 | 88.34% | 0 | 2 | 72.13% | 0% | 0 | 0.020592 | 1 | 0.020592 | 0.0091652
PANOCHE 11034016 | PANOC | PANOCHE 1103 | YOSEMITE | 2.3488 | 61.1971 | 100% | 0 | 0 | 18.31% | 0% | 0 | 0.020566 | 1 | 0.020566 | 0.0087561
JOLON 11027004 | JOLON | JOLON 1102 | CENTRAL COAST | 5.4816 | 47.887 | 100% | 0 | 0 | 27.2% | 0% | 0 | 0.020525 | 1 | 0.020525 | 0.0037443
WILLITS 1103696 | WILLI | WILLITS 1103 | HUMBOLDT | 6.5774 | 41.2479 | 62.23% | 0 | 3 | 69.69% | 0% | 0 | 0.020487 | 1 | 0.020487 | 0.0031148
RALSTON 11022028 | RALST | RALSTON 1102 | PENINSULA | 2.1344 | 10 | 38.62% | 0 | 5 | 92.94% | 0% | 0 | 0.020485 | 1 | 0.020485 | 0.0095976
NEWBURG 113190242 | NEWBU | NEWBURG 1131 | HUMBOLDT | 3.4074 | 35.576 | 50.59% | 5 | 2 | 78.12% | 0% | 0 | 0.020383 | 1 | 0.020383 | 0.0059821
CALAVERAS CEMENT 1101CB | CALAV | CALAVERAS CEMENT 1101 | STOCKTON | 11.1338 | 14.2948 | 43.85% | 0 | 4 | 60.61% | 0% | 0 | 0.02038 | 1 | 0.02038 | 0.0018305
PANORAMA 11021526 | PANOR | PANORAMA 1102 | NORTH VALLEY | 11.8848 | 23.1923 | 53.04% | 0 | 7 | 67.25% | 0% | 0 | 0.020361 | 1 | 0.020361 | 0.0017132
NEWBURG 1133CB | NEWBU | NEWBURG 1133 | HUMBOLDT | 3.7712 | 37.8079 | 38.51% | 2 | 0 | 41.21% | 0% | 0 | 0.020349 | 1 | 0.020349 | 0.0053958
LOGAN CREEK 21022226 | LOGAN | LOGAN CREEK 2102 | NORTH VALLEY | 3.7103 | 86.8404 | 100% | 0 | 1 | 10.78% | 0% | 0 | 0.020313 | 1 | 0.020313 | 0.0054747
MONTICELLO 1101CB | MONTI | MONTICELLO 1101 | NORTH BAY | 0.56293 | 10 | 41.7% | 0 | 0 | 100% | 0% | 0 | 0.020311 | 1 | 0.020311 | 0.036081
GREENBRAE 1103434 | GREEN | GREENBRAE 1103 | NORTH BAY | 0.79973 | 10 | 68.06% | 2 | 1 | 55.44% | 2.889% | 0 | 0.020293 | 1 | 0.020293 | 0.025375
KONOCTI 1102948 | KONOC | KONOCTI 1102 | HUMBOLDT | 6.065 | 30.1749 | 46.64% | 1 | 1 | 78.59% | 0% | 0 | 0.02028 | 1 | 0.02028 | 0.0033438
REDBUD 1101400 | REDBU | REDBUD 1101 | HUMBOLDT | 1.0177 | 10 | 44.91% | 0 | 5 | 100% | 0% | 0 | 0.020268 | 1 | 0.020268 | 0.019915
RIDGE 0401CB | RIDGE | RIDGE 0401 | EAST BAY | 2.662 | 10 | 10.22% | 3 | 4 | 100% | 0% | 0 | 0.02026 | 1 | 0.02026 | 0.0076108
VIEJO 2201CB | VIEJO | VIEJO 2201 | CENTRAL COAST | 4.5324 | 10 | 12.86% | 16 | 6 | 89.76% | 0% | 0 | 0.020254 | 1 | 0.020254 | 0.0044687
CLOVERDALE 1102262 | CLOVE | CLOVERDALE 1102 | SONOMA | 1.062 | 28.5735 | 25.58% | 2 | 0 | 19.75% | 47.85% | 0 | 0.020231 | 1 | 0.020231 | 0.01905
DESCHUTES 11041582 | DESCH | DESCHUTES 1104 | NORTH VALLEY | 6.3252 | 21.3729 | 99.66% | 0 | 1 | 41.84% | 0% | 0 | 0.020198 | 1 | 0.020198 | 0.0031933
BIG RIVER 1101954 | BIG R | BIG RIVER 1101 | HUMBOLDT | 7.7476 | 11.9193 | 13.02% | 4 | 10 | 95.19% | 0% | 0 | 0.020135 | 1 | 0.020135 | 0.0025988
PLACER 1103CB | PLACE | PLACER 1103 | SIERRA | 12.2492 | 28.3994 | 44.01% | 5 | 11 | 41.67% | 0% | 0 | 0.020134 | 1 | 0.020134 | 0.0016437
GARBERVILLE 110139524 | GARBE | GARBERVILLE 1101 | HUMBOLDT | 5.5428 | 59.5329 | 86.83% | 1 | 2 | 35.93% | 0% | 0 | 0.020129 | 1 | 0.020129 | 0.0036315
BURNEY 11012402 | BURNE | BURNEY 1101 | NORTH VALLEY | 1.4308 | 10 | 91.1% | 2 | 2 | 38.13% | 0% | 0 | 0.020105 | 1 | 0.020105 | 0.014051
SARATOGA 1106LC22 | SARAT | SARATOGA 1106 | DE ANZA | 7.1525 | 10 | 35.66% | 5 | 5 | 86.79% | 0% | 0 | 0.020092 | 1 | 0.020092 | 0.0028091
CUYAMA 1103622728 | CUYAM | CUYAMA 1103 | KERN | 2.3769 | 95 | 100% | 0 | 0 | 6.184% | 0% | 0 | 0.02009 | 1 | 0.02009 | 0.0084524
PUEBLO 1104640 | PUEBL | PUEBLO 1104 | NORTH BAY | 1.0277 | 10 | 45.71% | 1 | 4 | 32.52% | 0% | 0 | 0.02008 | 1 | 0.02008 | 0.01954
WISE 1101CB | WISE | WISE 1101 | SIERRA | 5.8467 | 15.7551 | 45.1% | 2 | 5 | 65.21% | 0% | 0 | 0.01999 | 1 | 0.01999 | 0.003419
OLETA 11022642 | OLETA | OLETA 1102 | STOCKTON | 4.6588 | 10 | 54.08% | 0 | 0 | 100% | 0.8976% | 1 | 0.01998 | 1 | 0.01998 | 0.0042886
NORTH DUBLIN 2101CB | NORTH | NORTH DUBLIN 2101 | MISSION | 3.6193 | 54.6377 | 4.667% | 0 | 3 | 91.94% | 0% | 0 | 0.019955 | 1 | 0.019955 | 0.0055135
HALF MOON BAY 110375550 | HALF | HALF MOON BAY 1103 | PENINSULA | 1.1869 | 54.8487 | 75.08% | 0 | 0 | 53.23% | 0% | 0 | 0.019917 | 1 | 0.019917 | 0.01678
LLAGAS 2101XR586 | LLAGA | LLAGAS 2101 | SAN JOSE | 4.744 | 52.8351 | 95.8% | 0 | 1 | 35.43% | 0% | 0 | 0.019912 | 1 | 0.019912 | 0.0041974
DIAMOND SPRINGS 110699658 | DIAMO | DIAMOND SPRINGS 1106 | SIERRA | 5.0702 | 10 | 100% | 3 | 3 | 39.71% | 0% | 0 | 0.019909 | 1 | 0.019909 | 0.0039268
PEORIA 170567898 | PEORI | PEORIA 1705 | YOSEMITE | 5.0246 | 20.73 | 47.42% | 1 | 2 | 80.37% | 0% | 0 | 0.0199 | 1 | 0.0199 | 0.0039605
CURTIS 170320240 | CURTI | CURTIS 1703 | YOSEMITE | 0.18021 | 10 | 100% | 0 | 0 | 63.08% | 0% | 0 | 0.019869 | 1 | 0.019869 | 0.11025
MC ARTHUR 11011492 | MC AR | MC ARTHUR 1101 | NORTH VALLEY | 9.6647 | 34.9258 | 100% | 1 | 0 | 31.38% | 0% | 0 | 0.019862 | 1 | 0.019862 | 0.0020551
CABRILLO 11031437 | CABRI | CABRILLO 1103 | LOS PADRES | 3.2446 | 37.9706 | 72.77% | 0 | 0 | 66.31% | 0% | 0 | 0.019849 | 1 | 0.019849 | 0.0061176
ROB ROY 210412596 | ROB R | ROB ROY 2104 | CENTRAL COAST | 7.6393 | 10 | 59% | 3 | 3 | 72.22% | 0.5428% | 0 | 0.019837 | 1 | 0.019837 | 0.0025968
OLETA 11021228 | OLETA | OLETA 1102 | STOCKTON | 8.954 | 36.1723 | 96.93% | 0 | 0 | 20.75% | 0% | 0 | 0.019803 | 1 | 0.019803 | 0.0022117
VIEJO 22019490 | VIEJO | VIEJO 2201 | CENTRAL COAST | 2.0007 | 10 | 0.3261% | 11 | 5 | 93.15% | 0% | 0 | 0.019802 | 1 | 0.019802 | 0.0098973
HALSEY 11015731 | HALSE | HALSEY 1101 | SIERRA | 3.1252 | 10 | 52.17% | 0 | 1 | 100% | 0% | 0 | 0.019797 | 1 | 0.019797 | 0.0063348
HARTLEY 11014710 | HARTL | HARTLEY 1101 | HUMBOLDT | 1.5005 | 10 | 52.07% | 1 | 0 | 100% | 0% | 0 | 0.019631 | 1 | 0.019631 | 0.013083
CURTIS 1703CB | CURTI | CURTIS 1703 | YOSEMITE | 8.4941 | 16.7987 | 53.44% | 0 | 2 | 77.88% | 0% | 0 | 0.0196 | 1 | 0.0196 | 0.0023075
MESA 1101M86 | MESA | MESA 1101 | LOS PADRES | 10.0922 | 14.4649 | 78% | 0 | 7 | 48.4% | 0% | 0 | 0.019529 | 1 | 0.019529 | 0.0019351
CLAYTON 2215W531R | CLAYT | CLAYTON 2215 | DIABLO | 5.8394 | 49.6313 | 12.81% | 0 | 3 | 54.09% | 19.44% | 0 | 0.019385 | 1 | 0.019385 | 0.0033197
PERRY 1101W12 | PERRY | PERRY 1101 | LOS PADRES | 4.7971 | 10 | 2.793% | 5 | 9 | 75.15% | 0% | 0 | 0.01938 | 1 | 0.01938 | 0.0040399
WYANDOTTE 11101954 | WYAND | WYANDOTTE 1110 | NORTH VALLEY | 13.197 | 10 | 59.13% | 1 | 2 | 48.67% | 0% | 0 | 0.019374 | 1 | 0.019374 | 0.0014681
LAURELES 11112028 | LAURE | LAURELES 1111 | CENTRAL COAST | 8.3353 | 36.2004 | 23.71% | 6 | 1 | 95.28% | 0% | 0 | 0.019345 | 1 | 0.019345 | 0.0023209
MARIPOSA 2101CB | MARIP | MARIPOSA 2101 | YOSEMITE | 6.8371 | 18.7213 | 60.25% | 1 | 4 | 63.95% | 0% | 0 | 0.019315 | 1 | 0.019315 | 0.002825
POINT MORETTI 110112122 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 6.8941 | 11.1834 | 26.23% | 14 | 1 | 86.19% | 0% | 0 | 0.019307 | 1 | 0.019307 | 0.0028005
EDENVALE 2107D80 | EDENV | EDENVALE 2107 | SAN JOSE | 0.032033 | 71.8938 | 0% | 0 | 0 | 100% | 0% | 0 | 0.019259 | 1 | 0.019259 | 0.60122
OILFIELDS 1103N64 | OILFI | OILFIELDS 1103 | CENTRAL COAST | 9.7922 | 31.0491 | 50.23% | 0 | 4 | 78.14% | 0% | 0 | 0.019257 | 1 | 0.019257 | 0.0019666
SUMMIT 110158642 | SUMMI | SUMMIT 1101 | SIERRA | 1.9126 | 10 | 32.51% | 0 | 1 | 100% | 0% | 0 | 0.019248 | 1 | 0.019248 | 0.010064
LONE TREE 210521210 | LONE | LONE TREE 2105 | DIABLO | 9.5646 | 10 | 95.6% | 0 | 2 | 59.2% | 0% | 0 | 0.019234 | 1 | 0.019234 | 0.0020109
HOLLISTER 21054724 | HOLLI | HOLLISTER 2105 | CENTRAL COAST | 3.4016 | 78.2881 | 100% | 0 | 0 | 12.91% | 0% | 0 | 0.019187 | 1 | 0.019187 | 0.0056407
NARROWS 210551582 | NARRO | NARROWS 2105 | SIERRA | 9.5263 | 10 | 48.26% | 0 | 1 | 100% | 0% | 0 | 0.019181 | 1 | 0.019181 | 0.0020135
HAMILTON BRANCH 1101CB | HAMIL | HAMILTON BRANCH 1101 | NORTH VALLEY | 4.2457 | 27.0953 | 61.17% | 1 | 2 | 74.22% | 0% | 0 | 0.019168 | 1 | 0.019168 | 0.0045147
HIGHLANDS 110275140 | HIGHL | HIGHLANDS 1102 | HUMBOLDT | 8.7915 | 33.3312 | 88.94% | 0 | 4 | 43.92% | 0% | 0 | 0.019109 | 1 | 0.019109 | 0.0021736
HOLLISTER 21064004 | HOLLI | HOLLISTER 2106 | CENTRAL COAST | 7.4093 | 64.8641 | 59.97% | 2 | 1 | 36.51% | 0% | 0 | 0.019101 | 1 | 0.019101 | 0.002578
PIT NO 1 1101CB | PIT N | PIT NO 1 1101 | NORTH VALLEY | 6.4361 | 10 | 29.8% | 1 | 2 | 98.02% | 0% | 0 | 0.019097 | 1 | 0.019097 | 0.0029672
EDES 1112CR282 | EDES | EDES 1112 | EAST BAY | 3.4204 | 10 | 46.24% | 0 | 3 | 83.7% | 0% | 0 | 0.019097 | 1 | 0.019097 | 0.0055833
GLENN 11012012 | GLENN | GLENN 1101 | NORTH VALLEY | 2.3498 | 85 | 100% | 0 | 0 | 7.814% | 0% | 0 | 0.01909 | 1 | 0.01909 | 0.0081243
DIAMOND SPRINGS 1107CB | DIAMO | DIAMOND SPRINGS 1107 | SIERRA | 7.4424 | 10 | 84.55% | 2 | 3 | 62.03% | 0.42% | 0 | 0.019073 | 1 | 0.019073 | 0.0025627
VIEJO 22029120 | VIEJO | VIEJO 2202 | CENTRAL COAST | 1.9636 | 10 | 20.08% | 9 | 3 | 26.52% | 0% | 0 | 0.019059 | 1 | 0.019059 | 0.0097064
STELLING 111060090 | STELL | STELLING 1110 | DE ANZA | 6.0088 | 10 | 51.27% | 4 | 1 | 91.55% | 0% | 0 | 0.019051 | 1 | 0.019051 | 0.0031705
MORGAN HILL 210940000 | MORGA | MORGAN HILL 2109 | SAN JOSE | 1.7684 | 10 | 99.47% | 0 | 0 | 59.08% | 0% | 0 | 0.019023 | 1 | 0.019023 | 0.010757
ALTO 11251256 | ALTO | ALTO 1125 | NORTH BAY | 1.3805 | 10 | 15.55% | 1 | 0 | 94.69% | 19.69% | 0 | 0.018993 | 1 | 0.018993 | 0.013758
CLARK ROAD 11022044 | CLARK | CLARK ROAD 1102 | NORTH VALLEY | 5.5376 | 29.0224 | 29.16% | 0 | 3 | 44.24% | 0% | 0 | 0.018991 | 1 | 0.018991 | 0.0034295
CABRILLO 110420711 | CABRI | CABRILLO 1104 | LOS PADRES | 0.18254 | 10 | 100% | 0 | 0 | 58.32% | 0% | 0 | 0.01896 | 1 | 0.01896 | 0.10387
HORSESHOE 110150140 | HORSE | HORSESHOE 1101 | SIERRA | 3.7526 | 10 | 69.76% | 1 | 4 | 60.16% | 0% | 0 | 0.018953 | 1 | 0.018953 | 0.0050507
ELECTRA 1102CB | ELECT | ELECTRA 1102 | STOCKTON | 2.62 | 68.1508 | 1.119% | 0 | 0 | 100% | 0% | 0 | 0.018952 | 1 | 0.018952 | 0.0072337
MENDOCINO 110131322 | MENDO | MENDOCINO 1101 | HUMBOLDT | 4.4175 | 35.3153 | 77.6% | 2 | 7 | 15.42% | 0% | 0 | 0.01894 | 1 | 0.01894 | 0.0042876
ELK CREEK 11012228 | ELK C | ELK CREEK 1101 | NORTH VALLEY | 3.1012 | 51.6707 | 100% | 0 | 0 | 29.46% | 0% | 0 | 0.018884 | 1 | 0.018884 | 0.0060892
FORT BRAGG A 11014698 | FORT | FORT BRAGG A 1101 | HUMBOLDT | 7.9299 | 10 | 15.57% | 8 | 8 | 100% | 0% | 0 | 0.018863 | 1 | 0.018863 | 0.0023787
POINT MORETTI 11015076 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 7.1634 | 15.8606 | 16.59% | 11 | 1 | 79.19% | 0% | 0 | 0.018862 | 1 | 0.018862 | 0.0026331
FORT BRAGG A 1102816 | FORT | FORT BRAGG A 1102 | HUMBOLDT | 2.5631 | 10 | 6.097% | 3 | 2 | 100% | 0% | 0 | 0.018806 | 1 | 0.018806 | 0.0073371
MADISON 210137082 | MADIS | MADISON 2101 | SACRAMENTO | 0.85819 | 87.1383 | 100% | 0 | 0 | 4.662% | 0% | 0 | 0.018775 | 1 | 0.018775 | 0.021878
EMERALD LAKE 04028872 | EMERA | EMERALD LAKE 0402 | PENINSULA | 4.147 | 10 | 19.14% | 0 | 11 | 74.11% | 0% | 0 | 0.018758 | 1 | 0.018758 | 0.0045232
WOODSIDE 11049116 | WOODS | WOODSIDE 1104 | PENINSULA | 1.063 | 10 | 91% | 2 | 5 | 24.81% | 0% | 0 | 0.018746 | 1 | 0.018746 | 0.017635
FITCH MOUNTAIN 1113583202 | FITCH | FITCH MOUNTAIN 1113 | SONOMA | 3.5047 | 64.5439 | 56.95% | 1 | 2 | 36.51% | 0% | 0 | 0.018742 | 1 | 0.018742 | 0.0053475
CLARKSVILLE 2109CB | CLARK | CLARKSVILLE 2109 | SIERRA | 1.031 | 10 | 7.581% | 0 | 1 | 91.6% | 7.913% | 0 | 0.018738 | 1 | 0.018738 | 0.018174
OTTER 11022012 | OTTER | OTTER 1102 | CENTRAL COAST | 9.1781 | 41.691 | 0% | 3 | 4 | 91.18% | 0% | 0 | 0.018558 | 1 | 0.018558 | 0.002022
CAMPHORA 110177978 | CAMPH | CAMPHORA 1101 | CENTRAL COAST | 1.4665 | 83.8291 | 100% | 0 | 0 | 5.721% | 0% | 0 | 0.018555 | 1 | 0.018555 | 0.012653
MAXWELL 11053008 | MAXWE | MAXWELL 1105 | SACRAMENTO | 1.6684 | 73.9154 | 100% | 0 | 0 | 12.26% | 0% | 0 | 0.018513 | 1 | 0.018513 | 0.011097
ELECTRA 11024756 | ELECT | ELECTRA 1102 | STOCKTON | 8.9008 | 26.6489 | 52.03% | 0 | 4 | 75.65% | 0% | 0 | 0.018513 | 1 | 0.018513 | 0.0020799
OAK 0401CB | OAK 0 | OAK 0401 | EAST BAY | 4.3198 | 10 | 1.236% | 2 | 7 | 79.82% | 0% | 0 | 0.018493 | 1 | 0.018493 | 0.0042811
SILVERADO 21023010 | SILVE | SILVERADO 2102 | NORTH BAY | 3.5284 | 66.7535 | 84.82% | 0 | 1 | 27.23% | 0% | 0 | 0.018454 | 1 | 0.018454 | 0.0052302
RINCON 1101CB | RINCO | RINCON 1101 | SONOMA | 2.1293 | 20.6419 | 39.27% | 1 | 4 | 43.97% | 11.03% | 0 | 0.018447 | 1 | 0.018447 | 0.0086632
ZACA 1101Y70 | ZACA | ZACA 1101 | LOS PADRES | 5.1032 | 39.0808 | 69.39% | 0 | 1 | 58.75% | 0% | 0 | 0.018441 | 1 | 0.018441 | 0.0036136
SUMMIT 11016627 | SUMMI | SUMMIT 1101 | SIERRA | 0.56142 | 10 | 45.61% | 0 | 0 | 100% | 0% | 0 | 0.01839 | 1 | 0.01839 | 0.032757
LUCERNE 110647198 | LUCER | LUCERNE 1106 | HUMBOLDT | 3.6836 | 20.6629 | 59.47% | 1 | 7 | 65.28% | 0% | 0 | 0.018382 | 1 | 0.018382 | 0.0049903
LOS OSITOS 21037468 | LOS O | LOS OSITOS 2103 | CENTRAL COAST | 1.0746 | 71.3986 | 100% | 0 | 0 | 13.23% | 0% | 0 | 0.018377 | 1 | 0.018377 | 0.017101
GREEN VALLEY 210112106 | GREEN | GREEN VALLEY 2101 | CENTRAL COAST | 6.3447 | 10 | 54.91% | 5 | 0 | 33.81% | 31.75% | 0 | 0.018337 | 1 | 0.018337 | 0.0028901
TRES PINOS 11114032 | TRES | TRES PINOS 1111 | CENTRAL COAST | 0.10269 | 70 | 100% | 0 | 0 | 0.5446% | 0% | 0 | 0.018321 | 1 | 0.018321 | 0.17842
FROGTOWN 1701CB | FROGT | FROGTOWN 1701 | STOCKTON | 9.8066 | 35.2796 | 29.68% | 0 | 4 | 86.99% | 0% | 0 | 0.018301 | 1 | 0.018301 | 0.0018662
UKIAH 1114822 | UKIAH | UKIAH 1114 | HUMBOLDT | 1.3145 | 67.0871 | 100% | 0 | 3 | 9.397% | 0% | 0 | 0.018289 | 1 | 0.018289 | 0.013913
PERRY 110185870 | PERRY | PERRY 1101 | LOS PADRES | 13.2734 | 34.8685 | 24.59% | 0 | 0 | 72.93% | 0% | 0 | 0.018257 | 1 | 0.018257 | 0.0013755
WYANDOTTE 110213044 | WYAND | WYANDOTTE 1102 | NORTH VALLEY | 3.9523 | 10 | 53.49% | 0 | 6 | 66.87% | 0% | 0 | 0.018256 | 1 | 0.018256 | 0.0046191
UKIAH 1115CB | UKIAH | UKIAH 1115 | HUMBOLDT | 4.3061 | 10 | 64.92% | 0 | 1 | 67.93% | 0% | 0 | 0.018255 | 1 | 0.018255 | 0.0042394
LAS AROMAS 0401LA401R | LAS A | LAS AROMAS 0401 | DIABLO | 3.6951 | 10 | 0.309% | 3 | 6 | 93.3% | 0% | 0 | 0.018243 | 1 | 0.018243 | 0.004937
RACETRACK 17032553 | RACET | RACETRACK 1703 | YOSEMITE | 1.2971 | 10 | 100% | 0 | 1 | 52.29% | 0% | 0 | 0.018242 | 1 | 0.018242 | 0.014064
LAMONT 11024222 | LAMON | LAMONT 1102 | KERN | 0.50063 | 85 | 100% | 0 | 0 | 3.081% | 0% | 0 | 0.018222 | 1 | 0.018222 | 0.036398
WYANDOTTE 11095607 | WYAND | WYANDOTTE 1109 | NORTH VALLEY | 3.9588 | 10 | 93.75% | 0 | 0 | 59.06% | 0% | 0 | 0.018157 | 1 | 0.018157 | 0.0045866
PEORIA 170413490 | PEORI | PEORIA 1704 | YOSEMITE | 4.0441 | 23.9004 | 44.53% | 0 | 0 | 76.49% | 0% | 0 | 0.018107 | 1 | 0.018107 | 0.0044774
SAN MIGUEL 1104R58 | SAN M | SAN MIGUEL 1104 | LOS PADRES | 9.7655 | 26.7568 | 99.18% | 0 | 1 | 40.61% | 0% | 0 | 0.018077 | 1 | 0.018077 | 0.0018511
VIEJO 22019698 | VIEJO | VIEJO 2201 | CENTRAL COAST | 0.90136 | 10 | 0% | 2 | 3 | 100% | 0% | 0 | 0.018036 | 1 | 0.018036 | 0.02001
SAN RAFAEL 110168970 | SAN R | SAN RAFAEL 1101 | NORTH BAY | 1.3404 | 10 | 17.09% | 0 | 0 | 31.9% | 46.84% | 0 | 0.018013 | 1 | 0.018013 | 0.013438
POSO MOUNTAIN 2103CB | POSO | POSO MOUNTAIN 2103 | KERN | 2.3192 | 10 | 26.74% | 0 | 0 | 100% | 0% | 0 | 0.017995 | 1 | 0.017995 | 0.0077593
FRUITLAND 11418860 | FRUIT | FRUITLAND 1141 | HUMBOLDT | 2.4992 | 72.7282 | 25.93% | 4 | 0 | 65.81% | 0% | 0 | 0.01798 | 1 | 0.01798 | 0.0071942
TAR FLAT 0401CB | TAR F | TAR FLAT 0401 | YOSEMITE | 3.4825 | 10 | 7.176% | 1 | 2 | 94.76% | 17.84% | 1 | 0.017966 | 1 | 0.017966 | 0.0051588
GIRVAN 110280726 | GIRVA | GIRVAN 1102 | NORTH VALLEY | 5.9722 | 10 | 96.6% | 0 | 5 | 31.79% | 0% | 0 | 0.017957 | 1 | 0.017957 | 0.0030067
RAWSON 110385334 | RAWSO | RAWSON 1103 | NORTH VALLEY | 2.3781 | 53.7562 | 78.76% | 0 | 1 | 24.97% | 0% | 0 | 0.017954 | 1 | 0.017954 | 0.0075499
SAUSALITO 1102410 | SAUSA | SAUSALITO 1102 | NORTH BAY | 1.0698 | 10 | 84.58% | 1 | 1 | 48.49% | 0% | 0 | 0.017913 | 1 | 0.017913 | 0.016744
TULE POWER HOUSE 1101CB | TULE | TULE POWER HOUSE 1101 | FRESNO | 4.0927 | 57.029 | 3.215% | 0 | 0 | 100% | 0% | 0 | 0.01789 | 1 | 0.01789 | 0.0043711
PEORIA 170492888 | PEORI | PEORIA 1704 | YOSEMITE | 0.24891 | 10 | 100% | 0 | 0 | 52.34% | 0% | 0 | 0.017878 | 1 | 0.017878 | 0.071825
MARTELL 1101CB | MARTE | MARTELL 1101 | STOCKTON | 6.3498 | 10 | 65.48% | 1 | 2 | 48.33% | 0% | 0 | 0.01783 | 1 | 0.01783 | 0.002808
PERRY 1101W26 | PERRY | PERRY 1101 | LOS PADRES | 2.7324 | 25.8267 | 23.85% | 3 | 0 | 100% | 0% | 0 | 0.017829 | 1 | 0.017829 | 0.0065251
EMERALD LAKE 0402CB | EMERA | EMERALD LAKE 0402 | PENINSULA | 1.9157 | 10 | 14.69% | 2 | 3 | 100% | 0% | 0 | 0.017819 | 1 | 0.017819 | 0.0093013
TOCALOMA 0241CB | TOCAL | TOCALOMA 0241 | NORTH BAY | 0.031239 | 60 | 0% | 0 | 0 | 100% | 0% | 0 | 0.017781 | 1 | 0.017781 | 0.56918
SUMMIT 110147786 | SUMMI | SUMMIT 1101 | SIERRA | 1.7732 | 10 | 6.416% | 0 | 1 | 100% | 0% | 0 | 0.017764 | 1 | 0.017764 | 0.010018
SAN LEANDRO U 1114MR545 | SAN L | SAN LEANDRO U 1114 | MISSION | 2.8053 | 10 | 16.34% | 0 | 2 | 62.83% | 0% | 0 | 0.01772 | 1 | 0.01772 | 0.0063167
VACAVILLE 1104CB | VACAV | VACAVILLE 1104 | SACRAMENTO | 0.88859 | 38.1521 | 69.79% | 0 | 1 | 28.2% | 0% | 0 | 0.017694 | 1 | 0.017694 | 0.019912
PUEBLO 21031970 | PUEBL | PUEBLO 2103 | NORTH BAY | 3.678 | 37.2305 | 48.19% | 3 | 0 | 44.65% | 0% | 0 | 0.017676 | 1 | 0.017676 | 0.0048059
BOLINAS 11011236 | BOLIN | BOLINAS 1101 | NORTH BAY | 3.0037 | 58.0295 | 0% | 0 | 0 | 73.67% | 0% | 0 | 0.017604 | 1 | 0.017604 | 0.0058609
MADISON 21017702 | MADIS | MADISON 2101 | SACRAMENTO | 2.3216 | 70.1745 | 98.98% | 0 | 0 | 10.42% | 0% | 0 | 0.017585 | 1 | 0.017585 | 0.0075745
MORRO BAY 110249632 | MORRO | MORRO BAY 1102 | LOS PADRES | 0.66912 | 10 | 0% | 0 | 3 | 100% | 0% | 0 | 0.017573 | 1 | 0.017573 | 0.026263
CASTRO VALLEY 1108MR525 | CASTR | CASTRO VALLEY 1108 | MISSION | 0.061081 | 10 | 0% | 0 | 3 | 100% | 0% | 0 | 0.017573 | 1 | 0.017573 | 0.2877
KONOCTI 11081278 | KONOC | KONOCTI 1108 | HUMBOLDT | 3.9864 | 24.8046 | 63% | 1 | 3 | 49.95% | 0% | 0 | 0.017559 | 1 | 0.017559 | 0.0044048
MORRO BAY 1101 | MORRO | MORRO BAY 1101 | LOS PADRES | 0.0056924 | 70 | 100% | 0 | 0 | 9.555% | 0% | 0 | 0.017559 | 1 | 0.017559 | 3.0847
PEORIA 17046090 | PEORI | PEORIA 1704 | YOSEMITE | 0.79834 | 10 | 4.922% | 0 | 1 | 100% | 0% | 0 | 0.01755 | 1 | 0.01755 | 0.021983
GUALALA 1111CB | GUALA | GUALALA 1111 | HUMBOLDT | 3.8671 | 10 | 20.51% | 4 | 5 | 100% | 0% | 0 | 0.017522 | 1 | 0.017522 | 0.0045311
AUBURN 11028611 | AUBUR | AUBURN 1102 | SIERRA | 1.8383 | 10 | 16.6% | 1 | 2 | 100% | 0% | 0 | 0.017498 | 1 | 0.017498 | 0.0095186
HIGGINS 111051794 | HIGGI | HIGGINS 1110 | SIERRA | 3.8902 | 22.6443 | 10.14% | 0 | 1 | 100% | 0% | 0 | 0.017481 | 1 | 0.017481 | 0.0044936
ALTO 11201214 | ALTO | ALTO 1120 | NORTH BAY | 2.1973 | 49.1379 | 3.101% | 3 | 5 | 48.69% | 0% | 0 | 0.017477 | 1 | 0.017477 | 0.0079539
SUMMIT 1101742 | SUMMI | SUMMIT 1101 | SIERRA | 0.86692 | 10 | 60.19% | 0 | 1 | 66.72% | 0% | 0 | 0.017361 | 1 | 0.017361 | 0.020026
STAFFORD 1102908 | STAFF | STAFFORD 1102 | NORTH BAY | 0.96495 | 10 | 77.17% | 0 | 3 | 21.89% | 0% | 0 | 0.01736 | 1 | 0.01736 | 0.017991
HIGGINS 1110CB | HIGGI | HIGGINS 1110 | SIERRA | 11.6416 | 10 | 74.55% | 3 | 1 | 64.03% | 0% | 0 | 0.01732 | 1 | 0.01732 | 0.0014878
GARBERVILLE 1103CB | GARBE | GARBERVILLE 1103 | HUMBOLDT | 1.3711 | 26.7284 | 20.19% | 10 | 1 | 61.39% | 0% | 0 | 0.017309 | 1 | 0.017309 | 0.012624
LOS MOLINOS 11011308 | LOS M | LOS MOLINOS 1101 | NORTH VALLEY | 0.1275 | 79.8468 | 100% | 0 | 0 | 1.055% | 0% | 0 | 0.017254 | 1 | 0.017254 | 0.13533
BIG MEADOWS 21012476 | BIG M | BIG MEADOWS 2101 | NORTH VALLEY | 4.675 | 24.1427 | 65.6% | 4 | 4 | 53.74% | 0% | 0 | 0.017254 | 1 | 0.017254 | 0.0036908
BEAR VALLEY 21014500 | BEAR | BEAR VALLEY 2101 | YOSEMITE | 27.333 | 23.9548 | 99.26% | 0 | 3 | 33.35% | 0% | 0 | 0.017222 | 1 | 0.017222 | 0.0006301
SAUSALITO 11021500 | SAUSA | SAUSALITO 1102 | NORTH BAY | 1.1513 | 69.0338 | 0% | 0 | 0 | 90.51% | 0% | 0 | 0.017208 | 1 | 0.017208 | 0.014947
SPENCE 1123CB | SPENC | SPENCE 1123 | CENTRAL COAST | 2.0801 | 71.6022 | 100% | 0 | 0 | 6.177% | 0% | 0 | 0.017169 | 1 | 0.017169 | 0.0082538
MARTELL 110368192 | MARTE | MARTELL 1103 | STOCKTON | 2.6279 | 35.8454 | 65.85% | 0 | 2 | 40.93% | 0% | 0 | 0.017124 | 1 | 0.017124 | 0.0065163
RESERVATION ROAD 1102CB | RESER | RESERVATION ROAD 1102 | CENTRAL COAST | 6.8792 | 54.6073 | 43.73% | 1 | 5 | 38.43% | 0% | 0 | 0.017073 | 1 | 0.017073 | 0.0024818
PUTAH CREEK 11058812 | PUTAH | PUTAH CREEK 1105 | SACRAMENTO | 0.75773 | 78.0828 | 100% | 0 | 0 | 1.163% | 0% | 0 | 0.017069 | 1 | 0.017069 | 0.022527
TEMPLETON 2112R98 | TEMPL | TEMPLETON 2112 | LOS PADRES | 2.5848 | 57.8675 | 88.32% | 0 | 0 | 11.06% | 0% | 0 | 0.017037 | 1 | 0.017037 | 0.0065914
JESSUP 11019002 | JESSU | JESSUP 1101 | NORTH VALLEY | 6.7893 | 16.4426 | 68.96% | 0 | 5 | 44.76% | 0% | 0 | 0.017028 | 1 | 0.017028 | 0.0025082
COARSEGOLD 21036110 | COARS | COARSEGOLD 2103 | YOSEMITE | 9.9772 | 20.6713 | 95.13% | 0 | 5 | 33.47% | 0% | 0 | 0.016997 | 1 | 0.016997 | 0.0017036
PIT NO 3 21011480 | PIT N | PIT NO 3 2101 | NORTH VALLEY | 2.2265 | 10 | 27.11% | 1 | 1 | 90.29% | 0% | 0 | 0.016964 | 1 | 0.016964 | 0.0076189
WYANDOTTE 1105CB | WYAND | WYANDOTTE 1105 | NORTH VALLEY | 12.987 | 37.2024 | 0% | 0 | 0 | 96.35% | 0.5289% | 1 | 0.016922 | 1 | 0.016922 | 0.001303
RIO DELL 11021504 | RIO D | RIO DELL 1102 | HUMBOLDT | 8.4162 | 77.8437 | 6.428% | 4 | 1 | 69.81% | 0% | 0 | 0.016871 | 1 | 0.016871 | 0.0020046
WILLITS 110434006 | WILLI | WILLITS 1104 | HUMBOLDT | 3.7731 | 21.9583 | 31.14% | 0 | 7 | 66.96% | 0% | 0 | 0.016864 | 1 | 0.016864 | 0.0044695
SUMMIT 1101CB | SUMMI | SUMMIT 1101 | SIERRA | 0.12475 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.016863 | 1 | 0.016863 | 0.13518
LINCOLN 11012310 | LINCO | LINCOLN 1101 | SIERRA | 10.0776 | 10 | 72.42% | 0 | 6 | 56.39% | 0% | 0 | 0.016835 | 1 | 0.016835 | 0.0016705
NOVATO 110455398 | NOVAT | NOVATO 1104 | NORTH BAY | 2.9149 | 74.0149 | 52.93% | 0 | 1 | 25.83% | 0% | 0 | 0.016828 | 1 | 0.016828 | 0.005773
NARROWS 210276952 | NARRO | NARROWS 2102 | SIERRA | 3.581 | 10 | 96.43% | 1 | 1 | 31.95% | 0% | 0 | 0.016756 | 1 | 0.016756 | 0.004679
MERCED FALLS 110222774 | MERCE | MERCED FALLS 1102 | YOSEMITE | 1.0091 | 37.0223 | 100% | 0 | 0 | 27.2% | 0% | 0 | 0.016738 | 1 | 0.016738 | 0.016586
SOLEDAD 21013720 | SOLED | SOLEDAD 2101 | CENTRAL COAST | 2.3505 | 51.9589 | 88.77% | 0 | 0 | 12.85% | 0% | 0 | 0.016725 | 1 | 0.016725 | 0.0071157
SOBRANTE 1101L534R | SOBRA | SOBRANTE 1101 | DIABLO | 1.5331 | 10 | 22.75% | 1 | 1 | 80.03% | 7.584% | 0 | 0.016712 | 1 | 0.016712 | 0.010901
CORRAL 110213498 | CORRA | CORRAL 1102 | STOCKTON | 0.99648 | 10 | 14.99% | 0 | 1 | 100% | 0% | 0 | 0.0167 | 1 | 0.0167 | 0.016759
STAFFORD 1101CB | STAFF | STAFFORD 1101 | NORTH BAY | 2.6576 | 10 | 64.37% | 5 | 3 | 21.89% | 0% | 0 | 0.016699 | 1 | 0.016699 | 0.0062836
PLACERVILLE 11118582 | PLACE | PLACERVILLE 1111 | SIERRA | 7.7771 | 10 | 58.12% | 5 | 4 | 64.88% | 0% | 0 | 0.016693 | 1 | 0.016693 | 0.0021464
ANDERSON 1101CB | ANDER | ANDERSON 1101 | NORTH VALLEY | 1.7524 | 42.6703 | 99.35% | 0 | 2 | 19.42% | 0% | 0 | 0.016693 | 1 | 0.016693 | 0.0095258
SOLEDAD 21017056 | SOLED | SOLEDAD 2101 | CENTRAL COAST | 1.1515 | 59.0572 | 100% | 0 | 0 | 11.67% | 0% | 0 | 0.016656 | 1 | 0.016656 | 0.014464
UPPER LAKE 1101472084 | UPPER | UPPER LAKE 1101 | HUMBOLDT | 4.5266 | 10 | 55.47% | 0 | 3 | 61.59% | 0% | 0 | 0.016554 | 1 | 0.016554 | 0.0036571
SAN CARLOS 11048942 | SAN C | SAN CARLOS 1104 | PENINSULA | 1.591 | 10 | 52.6% | 0 | 5 | 59.7% | 0% | 0 | 0.016545 | 1 | 0.016545 | 0.010399
KONOCTI 1102CB | KONOC | KONOCTI 1102 | HUMBOLDT | 6.3926 | 38.5127 | 58.33% | 0 | 0 | 42.97% | 1.842% | 0 | 0.01654 | 1 | 0.01654 | 0.0025873
LUCERNE 1106CB | LUCER | LUCERNE 1106 | HUMBOLDT | 2.483 | 10 | 34.76% | 1 | 7 | 68.8% | 0% | 0 | 0.01653 | 1 | 0.01653 | 0.0066573
SWIFT 2107XR526 | SWIFT | SWIFT 2107 | SAN JOSE | 2.6821 | 10 | 42.91% | 0 | 1 | 49.21% | 0% | 0 | 0.016512 | 1 | 0.016512 | 0.0061567
POINT ARENA 1101CB | POINT | POINT ARENA 1101 | HUMBOLDT | 2.4683 | 40.0153 | 0% | 3 | 1 | 100% | 0% | 0 | 0.016501 | 1 | 0.016501 | 0.0066852
HIGGINS 11041006 | HIGGI | HIGGINS 1104 | SIERRA | 9.9734 | 10.2486 | 72.09% | 2 | 7 | 49.68% | 0% | 0 | 0.016495 | 1 | 0.016495 | 0.0016539
EMERALD LAKE 04028858 | EMERA | EMERALD LAKE 0402 | PENINSULA | 1.9112 | 10 | 5.775% | 0 | 4 | 100% | 0% | 0 | 0.016487 | 1 | 0.016487 | 0.0086266
CLOVERDALE 1102429006 | CLOVE | CLOVERDALE 1102 | SONOMA | 2.0089 | 22.4739 | 19.1% | 0 | 1 | 100% | 0% | 0 | 0.016467 | 1 | 0.016467 | 0.0081968
HOPLAND 11011100 | HOPLA | HOPLAND 1101 | HUMBOLDT | 2.6093 | 13.3851 | 100% | 0 | 1 | 39.2% | 0% | 0 | 0.016404 | 1 | 0.016404 | 0.0062867
SPRUCE 0402BR304 | SPRUC | SPRUCE 0402 | EAST BAY | 1.905 | 10 | 5.593% | 0 | 5 | 53.05% | 19.04% | 0 | 0.016372 | 1 | 0.016372 | 0.008594
FITCH MOUNTAIN 1113352 | FITCH | FITCH MOUNTAIN 1113 | SONOMA | 7.3048 | 34.6273 | 40.22% | 1 | 0 | 61.07% | 0% | 0 | 0.016355 | 1 | 0.016355 | 0.0022389
BELL 1108CB | BELL | BELL 1108 | SIERRA | 4.1507 | 10 | 64.56% | 0 | 6 | 33.13% | 0% | 0 | 0.016334 | 1 | 0.016334 | 0.0039352
JAMESON 11059472 | JAMES | JAMESON 1105 | SACRAMENTO | 2.8377 | 36.7552 | 61.91% | 0 | 2 | 38.64% | 0% | 0 | 0.016315 | 1 | 0.016315 | 0.0057492
JESSUP 11031540 | JESSU | JESSUP 1103 | NORTH VALLEY | 2.7435 | 22.0778 | 100% | 1 | 1 | 18.03% | 0% | 0 | 0.01631 | 1 | 0.01631 | 0.005945
POTTER VALLEY P H 110495878 | POTTE | POTTER VALLEY P H 1104 | HUMBOLDT | 6.3973 | 36.9398 | 60.01% | 0 | 4 | 34.83% | 8.674% | 0 | 0.01627 | 1 | 0.01627 | 0.0025432
OILFIELDS 11037006 | OILFI | OILFIELDS 1103 | CENTRAL COAST | 2.4385 | 10 | 100% | 0 | 0 | 16.07% | 0% | 0 | 0.016263 | 1 | 0.016263 | 0.006669
MIRABEL 1101CB | MIRAB | MIRABEL 1101 | SONOMA | 2.6279 | 19.2673 | 59.3% | 0 | 2 | 31.12% | 21.2% | 0 | 0.016241 | 1 | 0.016241 | 0.00618
SAN CARLOS 11039148 | SAN C | SAN CARLOS 1103 | PENINSULA | 3.9693 | 10 | 27.37% | 0 | 9 | 43.54% | 0% | 0 | 0.016236 | 1 | 0.016236 | 0.0040905
MC KEE 110870535 | MC KE | MC KEE 1108 | SAN JOSE | 1.0836 | 23.5844 | 100% | 0 | 0 | 32.92% | 0% | 0 | 0.016178 | 1 | 0.016178 | 0.01493
SAN LEANDRO U 1114MR218 | SAN L | SAN LEANDRO U 1114 | MISSION | 6.9334 | 10 | 55.46% | 3 | 0 | 61.53% | 0% | 0 | 0.01617 | 1 | 0.01617 | 0.0023322
LLAGAS 2104XR294 | LLAGA | LLAGAS 2104 | SAN JOSE | 1.6348 | 49.1137 | 100% | 0 | 0 | 15.4% | 0% | 0 | 0.016162 | 1 | 0.016162 | 0.0098864
DUNBAR 1101234 | DUNBA | DUNBAR 1101 | SONOMA | 3.2653 | 13.7421 | 32.63% | 2 | 8 | 50.44% | 15.33% | 0 | 0.01612 | 1 | 0.01612 | 0.0049368
POSO MOUNTAIN 21013990 | POSO | POSO MOUNTAIN 2101 | KERN | 4.4819 | 10 | 34.01% | 0 | 1 | 80.62% | 0% | 0 | 0.0161 | 1 | 0.0161 | 0.0035923
LLAGAS 2106XR146 | LLAGA | LLAGAS 2106 | SAN JOSE | 1.5959 | 59.0705 | 100% | 0 | 0 | 7.634% | 0% | 0 | 0.016009 | 1 | 0.016009 | 0.010031
BURNEY 110297318 | BURNE | BURNEY 1102 | NORTH VALLEY | 0.71383 | 14.6507 | 68.47% | 0 | 0 | 50.51% | 0% | 0 | 0.015997 | 1 | 0.015997 | 0.02241
LOS OSITOS 21037082 | LOS O | LOS OSITOS 2103 | CENTRAL COAST | 0.3792 | 71.4337 | 96.62% | 0 | 0 | 1.843% | 0% | 0 | 0.015988 | 1 | 0.015988 | 0.042163
OAKLAND J 1102CR184 | OAKLA | OAKLAND J 1102 | EAST BAY | 3.4622 | 10 | 2.127% | 3 | 2 | 100% | 0% | 0 | 0.01597 | 1 | 0.01597 | 0.0046127
CAYUCOS 1102W18 | CAYUC | CAYUCOS 1102 | LOS PADRES | 1.9754 | 67.8899 | 46.98% | 0 | 0 | 8.859% | 14.04% | 0 | 0.015968 | 1 | 0.015968 | 0.0080835
ROB ROY 210512586 | ROB R | ROB ROY 2105 | CENTRAL COAST | 3.2869 | 10 | 13.9% | 3 | 2 | 50.3% | 0% | 0 | 0.015967 | 1 | 0.015967 | 0.0048578
FAIRVIEW 220799096 | FAIRV | FAIRVIEW 2207 | DIABLO | 9.9116 | 14.1017 | 19.38% | 0 | 2 | 100% | 0% | 0 | 0.015926 | 1 | 0.015926 | 0.0016068
BELL 110880680 | BELL | BELL 1108 | SIERRA | 1.2687 | 10 | 46.62% | 0 | 0 | 71.23% | 0% | 0 | 0.015926 | 1 | 0.015926 | 0.012553
COTATI 1102462 | COTAT | COTATI 1102 | SONOMA | 3.3153 | 11.8938 | 22% | 1 | 2 | 84.56% | 0% | 0 | 0.015902 | 1 | 0.015902 | 0.0047967
HIGHLANDS 11034630 | HIGHL | HIGHLANDS 1103 | HUMBOLDT | 1.4567 | 24.8899 | 80.52% | 0 | 2 | 42.07% | 0% | 0 | 0.015892 | 1 | 0.015892 | 0.010909
MORAGA 11017616 | MORAG | MORAGA 1101 | DIABLO | 1.1725 | 14.9864 | 34.86% | 0 | 4 | 82.16% | 0% | 0 | 0.015878 | 1 | 0.015878 | 0.013543
KONOCTI 11084041 | KONOC | KONOCTI 1108 | HUMBOLDT | 1.9081 | 10 | 99.47% | 0 | 0 | 40.69% | 0% | 0 | 0.015871 | 1 | 0.015871 | 0.0083179
CALPELLA 1102496 | CALPE | CALPELLA 1102 | HUMBOLDT | 4.1652 | 16.4846 | 91.99% | 0 | 2 | 24.91% | 0% | 0 | 0.015871 | 1 | 0.015871 | 0.0038104
RISING RIVER 11011530 | RISIN | RISING RIVER 1101 | NORTH VALLEY | 10.3786 | 10.5372 | 70.85% | 4 | 0 | 58.6% | 0% | 0 | 0.01587 | 1 | 0.01587 | 0.0015291
LOS GATOS 110160052 | LOS G | LOS GATOS 1101 | DE ANZA | 1.8727 | 10 | 24.39% | 0 | 1 | 100% | 0% | 0 | 0.015806 | 1 | 0.015806 | 0.0084401
HOPLAND 1101770 | HOPLA | HOPLAND 1101 | HUMBOLDT | 8.7193 | 58.1602 | 26.75% | 1 | 4 | 57.45% | 0% | 0 | 0.015784 | 1 | 0.015784 | 0.0018102
ANDERSON 11031600 | ANDER | ANDERSON 1103 | NORTH VALLEY | 2.5631 | 13.0676 | 100% | 0 | 0 | 23.83% | 0% | 0 | 0.015715 | 1 | 0.015715 | 0.0061313
SILVERADO 210298998 | SILVE | SILVERADO 2102 | NORTH BAY | 4.5559 | 48.6012 | 79.99% | 0 | 0 | 16.02% | 0% | 0 | 0.015709 | 1 | 0.015709 | 0.0034481
STAFFORD 11011298 | STAFF | STAFFORD 1101 | NORTH BAY | 2.4249 | 10 | 52.95% | 1 | 0 | 36.21% | 0% | 0 | 0.015641 | 1 | 0.015641 | 0.0064501
OILFIELDS 1103 | OILFI | OILFIELDS 1103 | CENTRAL COAST | 0.020981 | 19.5696 | 17.4% | 0 | 0 | 100% | 0% | 0 | 0.015601 | 1 | 0.015601 | 0.74357
ANDERSON 11011752 | ANDER | ANDERSON 1101 | NORTH VALLEY | 3.4624 | 22.5175 | 29.42% | 0 | 0 | 74.73% | 0% | 0 | 0.015595 | 1 | 0.015595 | 0.0045042
SHINGLE SPRINGS 210819622 | SHING | SHINGLE SPRINGS 2108 | SIERRA | 4.5627 | 12.9837 | 69.35% | 2 | 3 | 39.08% | 0% | 0 | 0.015541 | 1 | 0.015541 | 0.003406
RALSTON 1101CB | RALST | RALSTON 1101 | PENINSULA | 5.2354 | 10 | 67.13% | 0 | 1 | 62.97% | 0% | 0 | 0.015521 | 1 | 0.015521 | 0.0029646
POTTER VALLEY P H 110537476 | POTTE | POTTER VALLEY P H 1105 | HUMBOLDT | 0.5064 | 62.972 | 86.61% | 0 | 3 | 5.941% | 0% | 0 | 0.015424 | 1 | 0.015424 | 0.030459
UPPER LAKE 1101660 | UPPER | UPPER LAKE 1101 | HUMBOLDT | 7.1376 | 10 | 50.04% | 0 | 2 | 74.17% | 0% | 0 | 0.015402 | 1 | 0.015402 | 0.0021579
PENRYN 11072410 | PENRY | PENRYN 1107 | SIERRA | 2.4145 | 10 | 87.13% | 0 | 1 | 32.14% | 0% | 0 | 0.015364 | 1 | 0.015364 | 0.0063631
ROB ROY 21045304 | ROB R | ROB ROY 2104 | CENTRAL COAST | 2.975 | 10 | 39.67% | 0 | 0 | 59.8% | 0% | 0 | 0.015337 | 1 | 0.015337 | 0.0051554
SAN RAFAEL 1105344 | SAN R | SAN RAFAEL 1105 | NORTH BAY | 2.2778 | 10 | 70.24% | 0 | 2 | 30.4% | 0% | 0 | 0.015331 | 1 | 0.015331 | 0.0067303
SUMMIT 110186658 | SUMMI | SUMMIT 1101 | SIERRA | 0.66943 | 10 | 1.926% | 3 | 0 | 100% | 0% | 0 | 0.015299 | 1 | 0.015299 | 0.022854
POINT MORETTI 1101CB | POINT | POINT MORETTI 1101 | CENTRAL COAST | 0.028582 | 13.6525 | 6.641% | 0 | 0 | 100% | 6.641% | 0 | 0.015281 | 1 | 0.015281 | 0.53463
BIG RIVER 1101CB | BIG R | BIG RIVER 1101 | HUMBOLDT | 1.8594 | 10 | 0.4258% | 5 | 2 | 94.21% | 0% | 0 | 0.01527 | 1 | 0.01527 | 0.0082123
GEYSERVILLE 110289714 | GEYSE | GEYSERVILLE 1102 | SONOMA | 1.4773 | 46.3035 | 100% | 0 | 0 | 11.51% | 0% | 0 | 0.015262 | 1 | 0.015262 | 0.010331
CARLOTTA 112142896 | CARLO | CARLOTTA 1121 | HUMBOLDT | 2.183 | 31.2732 | 37.15% | 2 | 2 | 39.92% | 0% | 0 | 0.015245 | 1 | 0.015245 | 0.0069833
WILLITS 1103CB | WILLI | WILLITS 1103 | HUMBOLDT | 1.4734 | 28.6497 | 64.03% | 0 | 1 | 37.49% | 0% | 0 | 0.015222 | 1 | 0.015222 | 0.010331
BIG MEADOWS 21012510 | BIG M | BIG MEADOWS 2101 | NORTH VALLEY | 5.0492 | 32.6868 | 6.505% | 7 | 2 | 57.3% | 0% | 0 | 0.015201 | 1 | 0.015201 | 0.0030106
FRANKLIN 1104P146 | FRANK | FRANKLIN 1104 | EAST BAY | 1.1753 | 10 | 98.96% | 0 | 2 | 31.88% | 0% | 0 | 0.015101 | 1 | 0.015101 | 0.012849
SARATOGA 1115LC20 | SARAT | SARATOGA 1115 | DE ANZA | 2.7261 | 10 | 38.53% | 0 | 1 | 56.79% | 0% | 0 | 0.015057 | 1 | 0.015057 | 0.0055232
GONZALES 110422420 | GONZA | GONZALES 1104 | CENTRAL COAST | 0.060363 | 60 | 100% | 0 | 0 | 0.7167% | 0% | 0 | 0.015047 | 1 | 0.015047 | 0.24927
SAN LUIS OBISPO 1102597518 | SAN L | SAN LUIS OBISPO 1102 | LOS PADRES | 0.61698 | 17.5901 | 98.92% | 0 | 1 | 28.41% | 0% | 0 | 0.015039 | 1 | 0.015039 | 0.024375
SAN ARDO 11017094 | SAN A | SAN ARDO 1101 | CENTRAL COAST | 1.1437 | 50.6148 | 100% | 0 | 0 | 6.71% | 0% | 0 | 0.014985 | 1 | 0.014985 | 0.013103
SARATOGA 11076867 | SARAT | SARATOGA 1107 | DE ANZA | 0.24862 | 10 | 100% | 0 | 2 | 30.1% | 0% | 0 | 0.014963 | 1 | 0.014963 | 0.060185
GRASS VALLEY 1103 | GRASS | GRASS VALLEY 1103 | SIERRA | 0.021115 | 10 | 19.87% | 0 | 0 | 100% | 0% | 0 | 0.014923 | 1 | 0.014923 | 0.70677
OAKLAND X 1106CB | OAKLA | OAKLAND X 1106 | EAST BAY | 4.876 | 10 | 15.55% | 5 | 5 | 41.41% | 19.42% | 0 | 0.014897 | 1 | 0.014897 | 0.0030552
MC ARTHUR 11021324 | MC AR | MC ARTHUR 1102 | NORTH VALLEY | 0.91154 | 54.3228 | 100% | 0 | 0 | 3.568% | 0% | 0 | 0.014895 | 1 | 0.014895 | 0.016341
MERCED FALLS 1102CB | MERCE | MERCED FALLS 1102 | YOSEMITE | 8.7968 | 48.2872 | 48.16% | 0 | 1 | 34.84% | 0% | 0 | 0.014879 | 1 | 0.014879 | 0.0016914
JESSUP 1101CB | JESSU | JESSUP 1101 | NORTH VALLEY | 1.1327 | 30.8343 | 100% | 0 | 0 | 19.43% | 0% | 0 | 0.01487 | 1 | 0.01487 | 0.013128
PURISIMA 1101CB | PURIS | PURISIMA 1101 | LOS PADRES | 3.8284 | 30.5658 | 4.848% | 1 | 0 | 83.25% | 0% | 0 | 0.014861 | 1 | 0.014861 | 0.0038817
HICKS 2101XR162 | HICKS | HICKS 2101 | SAN JOSE | 2.3563 | 22.9213 | 92.08% | 0 | 3 | 24.69% | 0% | 0 | 0.014813 | 1 | 0.014813 | 0.0062866
REEDLEY 1104274990 | REEDL | REEDLEY 1104 | FRESNO | 1.6643 | 56.3701 | 98.08% | 0 | 0 | 3.167% | 0% | 0 | 0.014809 | 1 | 0.014809 | 0.008898
SAN LUIS OBISPO 1103CB | SAN L | SAN LUIS OBISPO 1103 | LOS PADRES | 2.8352 | 59.393 | 72.07% | 0 | 1 | 20.37% | 0% | 0 | 0.014802 | 1 | 0.014802 | 0.0052207
POTTER VALLEY P H 1105CB | POTTE | POTTER VALLEY P H 1105 | HUMBOLDT | 0.024417 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.014786 | 1 | 0.014786 | 0.60555
VIEJO 22022606 | VIEJO | VIEJO 2202 | CENTRAL COAST | 0.94683 | 10 | 0% | 1 | 1 | 98.67% | 0% | 0 | 0.014784 | 1 | 0.014784 | 0.015614
CORRAL 110214028 | CORRA | CORRAL 1102 | STOCKTON | 3.2845 | 10 | 84.85% | 0 | 2 | 41.18% | 0% | 0 | 0.01476 | 1 | 0.01476 | 0.0044938
COARSEGOLD 210490356 | COARS | COARSEGOLD 2104 | YOSEMITE | 4.6415 | 10 | 96.81% | 0 | 4 | 27.05% | 0% | 0 | 0.014744 | 1 | 0.014744 | 0.0031767
POTTER VALLEY P H 110564118 | POTTE | POTTER VALLEY P H 1105 | HUMBOLDT | 1.7203 | 30.1363 | 62.86% | 2 | 1 | 18.17% | 0% | 0 | 0.014734 | 1 | 0.014734 | 0.0085647
PAUL SWEET 210612828 | PAUL | PAUL SWEET 2106 | CENTRAL COAST | 1.7112 | 10 | 38.85% | 0 | 0 | 34.49% | 21.63% | 0 | 0.014721 | 1 | 0.014721 | 0.008603
COTTONWOOD 110131500 | COTTO | COTTONWOOD 1101 | NORTH VALLEY | 3.2216 | 22.5046 | 96% | 0 | 0 | 27.31% | 0% | 0 | 0.01471 | 1 | 0.01471 | 0.004566
CLARKSVILLE 210955666 | CLARK | CLARKSVILLE 2109 | SIERRA | 0.61278 | 10 | 100% | 0 | 0 | 32.55% | 0% | 0 | 0.014709 | 1 | 0.014709 | 0.024003
PERRY 1101W52 | PERRY | PERRY 1101 | LOS PADRES | 2.9028 | 10 | 12.36% | 3 | 2 | 69.83% | 0% | 0 | 0.014698 | 1 | 0.014698 | 0.0050632
CURTIS 170349746 | CURTI | CURTIS 1703 | YOSEMITE | 0.37395 | 10 | 15.4% | 0 | 1 | 100% | 0% | 0 | 0.014691 | 1 | 0.014691 | 0.039286
ANTELOPE 11011631 | ANTEL | ANTELOPE 1101 | KERN | 0.75322 | 47.1276 | 100% | 0 | 0 | 6.682% | 0% | 0 | 0.014633 | 1 | 0.014633 | 0.019427
FLINT 1102CB | FLINT | FLINT 1102 | SIERRA | 0.092844 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.014483 | 1 | 0.014483 | 0.156
AUBURN 1102 | AUBUR | AUBURN 1102 | SIERRA | 0.025464 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.014483 | 1 | 0.014483 | 0.56879
AUBURN 1101CB | AUBUR | AUBURN 1101 | SIERRA | 3.1166 | 10 | 26.2% | 0 | 7 | 63.53% | 0% | 0 | 0.014449 | 1 | 0.014449 | 0.0046359
SAN BENITO 2104CB | SAN B | SAN BENITO 2104 | CENTRAL COAST | 4.8064 | 10 | 7.992% | 0 | 0 | 52.81% | 0% | 0 | 0.014395 | 1 | 0.014395 | 0.0029949
VALLEY VIEW 1105P190 | VALLE | VALLEY VIEW 1105 | EAST BAY | 3.5037 | 10 | 43.53% | 0 | 2 | 59.31% | 0% | 0 | 0.014389 | 1 | 0.014389 | 0.0041067
LUCERNE 110676850 | LUCER | LUCERNE 1106 | HUMBOLDT | 2.0465 | 10 | 61.3% | 0 | 3 | 55.89% | 0% | 0 | 0.014386 | 1 | 0.014386 | 0.0070298
SNEATH LANE 110134438 | SNEAT | SNEATH LANE 1101 | PENINSULA | 1.6791 | 10 | 46% | 1 | 0 | 33.32% | 0% | 0 | 0.014366 | 1 | 0.014366 | 0.0085559
TULUCAY 1101628 | TULUC | TULUCAY 1101 | NORTH BAY | 4.4167 | 65.2777 | 26.9% | 0 | 1 | 50.38% | 0% | 0 | 0.014345 | 1 | 0.014345 | 0.003248
ROSSMOOR 11018132 | ROSSM | ROSSMOOR 1101 | DIABLO | 2.3517 | 13.1594 | 38.14% | 0 | 7 | 64.04% | 0% | 0 | 0.014331 | 1 | 0.014331 | 0.0060938
OAKLAND X 1104CB | OAKLA | OAKLAND X 1104 | EAST BAY | 1.3072 | 10 | 2.074% | 0 | 2 | 53.76% | 24.1% | 0 | 0.014319 | 1 | 0.014319 | 0.010954
WILLITS 11044650 | WILLI | WILLITS 1104 | HUMBOLDT | 2.8566 | 16.3398 | 61.51% | 0 | 4 | 48.68% | 0% | 0 | 0.014299 | 1 | 0.014299 | 0.0050057
OAKLAND J 1105CR256 | OAKLA | OAKLAND J 1105 | EAST BAY | 1.5352 | 10 | 0.8551% | 1 | 0 | 83.22% | 0% | 0 | 0.014281 | 1 | 0.014281 | 0.0093024
POINT MORETTI 110183716 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 2.5672 | 18.0705 | 6.579% | 5 | 0 | 94.36% | 0% | 0 | 0.014279 | 1 | 0.014279 | 0.005562
MORAGA 1103CB | MORAG | MORAGA 1103 | DIABLO | 1.341 | 16.5323 | 0% | 6 | 3 | 21.01% | 11.54% | 0 | 0.01426 | 1 | 0.01426 | 0.010633
DUNBAR 1101160 | DUNBA | DUNBAR 1101 | SONOMA | 4.1387 | 21.8951 | 29.76% | 0 | 0 | 62.23% | 10.35% | 0 | 0.01425 | 1 | 0.01425 | 0.0034432
CHESTER 1101CB | CHEST | CHESTER 1101 | NORTH VALLEY | 2.5695 | 10 | 96.88% | 0 | 0 | 31.91% | 0% | 0 | 0.01425 | 1 | 0.01425 | 0.0055458
WISE 11011404 | WISE | WISE 1101 | SIERRA | 2.2264 | 13.0264 | 54.75% | 0 | 1 | 62.41% | 0% | 0 | 0.014247 | 1 | 0.014247 | 0.006399
CLAY 110359714 | CLAY | CLAY 1103 | STOCKTON | 4.4126 | 25.7757 | 4.31% | 0 | 1 | 95.22% | 0% | 0 | 0.014243 | 1 | 0.014243 | 0.0032277
SAN CARLOS 110475210 | SAN C | SAN CARLOS 1104 | PENINSULA | 0.38485 | 10 | 11.56% | 0 | 1 | 100% | 0% | 0 | 0.01424 | 1 | 0.01424 | 0.037001
HOOPA 110193038 | HOOPA | HOOPA 1101 | HUMBOLDT | 0.1684 | 40.7085 | 100% | 0 | 1 | 6.029% | 0% | 0 | 0.014214 | 1 | 0.014214 | 0.084406
NORTH BRANCH 1101CB | NORTH | NORTH BRANCH 1101 | STOCKTON | 10.7662 | 27.7002 | 39.92% | 0 | 5 | 56% | 0% | 0 | 0.014214 | 1 | 0.014214 | 0.0013202
ECHO SUMMIT 1101344250 | ECHO | ECHO SUMMIT 1101 | (blank) | 0.80694 | 10 | 100% | 1 | 0 | 14.32% | 0% | 0 | 0.014197 | 1 | 0.014197 | 0.017594
ROSSMOOR 110845268 | ROSSM | ROSSMOOR 1108 | DIABLO | 3.7726 | 24.3862 | 31.05% | 0 | 7 | 47.92% | 0% | 0 | 0.014195 | 1 | 0.014195 | 0.0037626
HATTON 1102648928 | HATTO | HATTON 1102 | CENTRAL COAST | 2.8842 | 29.9397 | 0% | 2 | 4 | 59.99% | 0% | 0 | 0.014193 | 1 | 0.014193 | 0.0049209
ALHAMBRA 110581514 | ALHAM | ALHAMBRA 1105 | DIABLO | 2.5203 | 17.3445 | 21.67% | 2 | 3 | 52.7% | 0% | 0 | 0.014173 | 1 | 0.014173 | 0.0056236
SOLEDAD 21027562 | SOLED | SOLEDAD 2102 | CENTRAL COAST | 1.9641 | 22.7828 | 92.71% | 0 | 0 | 25.93% | 0% | 0 | 0.014154 | 1 | 0.014154 | 0.0072064
CAYETANO 2111CB | CAYET | CAYETANO 2111 | MISSION | 5.2576 | 70.3707 | 27.25% | 0 | 1 | 45% | 0% | 0 | 0.014119 | 1 | 0.014119 | 0.0026855
RALSTON 1102CB | RALST | RALSTON 1102 | PENINSULA | 1.0812 | 10 | 71.25% | 0 | 0 | 25.36% | 0% | 0 | 0.014111 | 1 | 0.014111 | 0.013051
RIDGE 0402CB | RIDGE | RIDGE 0402 | EAST BAY | 1.6674 | 10 | 31.81% | 1 | 0 | 69.66% | 0% | 0 | 0.014084 | 1 | 0.014084 | 0.0084471
HATTON 110137088 | HATTO | HATTON 1101 | CENTRAL COAST | 4.1243 | 13.8122 | 55.58% | 4 | 4 | 48.38% | 0% | 0 | 0.014072 | 1 | 0.014072 | 0.0034119
LLAGAS 2107XR188 | LLAGA | LLAGAS 2107 | SAN JOSE | 2.7329 | 20.244 | 46.06% | 0 | 0 | 43.36% | 5.395% | 0 | 0.014067 | 1 | 0.014067 | 0.0051472
LOS OSITOS 21027470 | LOS O | LOS OSITOS 2102 | CENTRAL COAST | 2.5834 | 65.4453 | 76.6% | 0 | 0 | 9.453% | 0% | 0 | 0.014067 | 1 | 0.014067 | 0.0054452
OAKLAND J 1105CR150 | OAKLA | OAKLAND J 1105 | EAST BAY | 0.4695 | 10 | 10.02% | 0 | 1 | 100% | 0% | 0 | 0.014063 | 1 | 0.014063 | 0.029953
SNEATH LANE 110796530 | SNEAT | SNEATH LANE 1107 | PENINSULA | 0.71298 | 10 | 94.87% | 0 | 0 | 32.23% | 0% | 0 | 0.014063 | 1 | 0.014063 | 0.019724
SAN RAFAEL 1109CB | SAN R | SAN RAFAEL 1109 | NORTH BAY | 0.026389 | 10 | 100% | 0 | 0 | 0.5374% | 0% | 0 | 0.013951 | 1 | 0.013951 | 0.52868
TIDEWATER 210614072 | TIDEW | TIDEWATER 2106 | DIABLO | 3.6661 | 10 | 16.78% | 0 | 0 | 95.56% | 0% | 0 | 0.013929 | 1 | 0.013929 | 0.0037995
RESERVATION ROAD 1101CB | RESER | RESERVATION ROAD 1101 | CENTRAL COAST | 3.6814 | 10 | 45.32% | 0 | 3 | 39.08% | 0% | 0 | 0.013924 | 1 | 0.013924 | 0.0037821
VALLEY VIEW 1106CB | VALLE | VALLEY VIEW 1106 | EAST BAY | 3.4767 | 45.2583 | 0.9386% | 0 | 1 | 68.92% | 0% | 0 | 0.013903 | 1 | 0.013903 | 0.0039988
IGNACIO 1101CB | IGNAC | IGNACIO 1101 | NORTH BAY | 1.394 | 10 | 18.69% | 0 | 2 | 76.2% | 0% | 0 | 0.013891 | 1 | 0.013891 | 0.0099649
MARTELL 110299214 | MARTE | MARTELL 1102 | STOCKTON | 0.5909 | 10 | 69.1% | 1 | 4 | 29.13% | 0% | 0 | 0.013885 | 1 | 0.013885 | 0.023497
VINEYARD 2110CB | VINEY | VINEYARD 2110 | MISSION | 5.8656 | 49.5436 | 17.49% | 1 | 0 | 52.96% | 0% | 0 | 0.013877 | 1 | 0.013877 | 0.0023659
BASALT 11065030 | BASAL | BASALT 1106 | NORTH BAY | 3.3103 | 53.7565 | 71.04% | 0 | 0 | 20.61% | 0% | 0 | 0.013874 | 1 | 0.013874 | 0.0041913
SUNOL 110111587 | SUNOL | SUNOL 1101 | MISSION | 0.25848 | 10 | 100% | 0 | 1 | 24.35% | 0% | 0 | 0.013849 | 1 | 0.013849 | 0.053577
VIEJO 2204CB | VIEJO | VIEJO 2204 | CENTRAL COAST | 2.2166 | 10 | 31.01% | 10 | 1 | 54.6% | 0% | 0 | 0.013845 | 1 | 0.013845 | 0.0062463
HATTON 11029642 | HATTO | HATTON 1102 | CENTRAL COAST | 1.1982 | 10 | 4.477% | 2 | 1 | 100% | 0% | 0 | 0.013798 | 1 | 0.013798 | 0.011516
PASO ROBLES 110355374 | PASO | PASO ROBLES 1103 | LOS PADRES | 2.104 | 28.3586 | 87.29% | 0 | 2 | 19.75% | 0% | 0 | 0.013788 | 1 | 0.013788 | 0.0065532
UKIAH 1114528 | UKIAH | UKIAH 1114 | HUMBOLDT | 2.0763 | 22.6279 | 79.13% | 0 | 2 | 16.87% | 0% | 0 | 0.013763 | 1 | 0.013763 | 0.0066288
COTATI 1102CB | COTAT | COTATI 1102 | SONOMA | 1.3007 | 52.8482 | 0.4591% | 0 | 0 | 64.8% | 0% | 0 | 0.013707 | 1 | 0.013707 | 0.010538
MESA 1101CB | MESA | MESA 1101 | LOS PADRES | 13.1474 | 48.8211 | 12.29% | 0 | 3 | 51.32% | 0% | 0 | 0.013679 | 1 | 0.013679 | 0.0010404
HATTON 1102CB | HATTO | HATTON 1102 | CENTRAL COAST | 2.1206 | 10 | 0.1341% | 1 | 3 | 45.47% | 0% | 0 | 0.013538 | 1 | 0.013538 | 0.006384
LAS AROMAS 04013342 | LAS A | LAS AROMAS 0401 | DIABLO | 2.2911 | 10 | 3.001% | 3 | 0 | 100% | 0% | 0 | 0.013529 | 1 | 0.013529 | 0.0059051
MORGAN HILL 2110XR326 | MORGA | MORGAN HILL 2110 | SAN JOSE | 2.054 | 29.8956 | 63.47% | 0 | 2 | 9.633% | 0% | 0 | 0.013515 | 1 | 0.013515 | 0.0065797
MENDOCINO 110137462 | MENDO | MENDOCINO 1101 | HUMBOLDT | 2.449 | 10 | 46.73% | 0 | 2 | 50.22% | 0% | 0 | 0.0135 | 1 | 0.0135 | 0.0055124
MILPITAS 1109XR374 | MILPI | MILPITAS 1109 | SAN JOSE | 0.65242 | 10 | 100% | 0 | 1 | 21.62% | 0% | 0 | 0.013479 | 1 | 0.013479 | 0.02066
MORAGA 1103E510R | MORAG | MORAGA 1103 | DIABLO | 1.3196 | 10 | 100% | 0 | 1 | 21.61% | 0% | 0 | 0.013477 | 1 | 0.013477 | 0.010213
ROB ROY 210512474 | ROB R | ROB ROY 2105 | CENTRAL COAST | 2.374 | 10 | 59.61% | 0 | 1 | 28.06% | 0% | 0 | 0.013458 | 1 | 0.013458 | 0.005669
CHESTER 1102CB | CHEST | CHESTER 1102 | NORTH VALLEY | 0.32002 | 10 | 100% | 0 | 0 | 10.17% | 0% | 0 | 0.01345 | 1 | 0.01345 | 0.042029
WYANDOTTE 110737472 | WYAND | WYANDOTTE 1107 | NORTH VALLEY | 6.2847 | 13.7184 | 63.51% | 2 | 3 | 42.06% | 0% | 0 | 0.013447 | 1 | 0.013447 | 0.0021397
OILFIELDS 1103N42 | OILFI | OILFIELDS 1103 | CENTRAL COAST | 2.2461 | 52.6729 | 47.6% | 0 | 0 | 37.49% | 0% | 0 | 0.013447 | 1 | 0.013447 | 0.0059869
ROB ROY 2105CB | ROB R | ROB ROY 2105 | CENTRAL COAST | 0.78923 | 10 | 41.07% | 2 | 0 | 55.78% | 0% | 0 | 0.013414 | 1 | 0.013414 | 0.016996
PERRY 1101W10 | PERRY | PERRY 1101 | LOS PADRES | 1.7167 | 22.2223 | 1.272% | 0 | 2 | 91.87% | 0% | 0 | 0.013398 | 1 | 0.013398 | 0.0078047
NEWBURG 1131CB | NEWBU | NEWBURG 1131 | HUMBOLDT | 3.0239 | 26.9176 | 14.49% | 0 | 2 | 24.41% | 0% | 0 | 0.013392 | 1 | 0.013392 | 0.0044285
VALLEY VIEW 1106P176 | VALLE | VALLEY VIEW 1106 | EAST BAY | 0.884 | 14.838 | 80.1% | 1 | 0 | 21.45% | 0% | 0 | 0.013387 | 1 | 0.013387 | 0.015144
CLAY 110184572 | CLAY | CLAY 1101 | STOCKTON | 1.3752 | 10 | 53.62% | 0 | 0 | 60.97% | 0% | 0 | 0.013356 | 1 | 0.013356 | 0.0097117
SUNOL 1101MR169 | SUNOL | SUNOL 1101 | MISSION | 3.8873 | 57.3439 | 37.68% | 0 | 0 | 41.76% | 0% | 0 | 0.013353 | 1 | 0.013353 | 0.003435
PURISIMA 1101Y80 | PURIS | PURISIMA 1101 | LOS PADRES | 1.0399 | 27.8619 | 91.46% | 0 | 0 | 17.5% | 0% | 0 | 0.01334 | 1 | 0.01334 | 0.012828
SHINGLE SPRINGS 1104CB | SHING | SHINGLE SPRINGS 1104 | SIERRA | 0.43321 | 10 | 56.49% | 2 | 0 | 18.41% | 23.01% | 0 | 0.013336 | 1 | 0.013336 | 0.030785
ALTO 112265474 | ALTO | ALTO 1122 | NORTH BAY | 2.1481 | 10 | 21.89% | 2 | 1 | 58.84% | 6.137% | 0 | 0.013328 | 1 | 0.013328 | 0.0062044
KONOCTI 11084037 | KONOC | KONOCTI 1108 | HUMBOLDT | 0.3878 | 10 | 100% | 0 | 0 | 22.52% | 0% | 0 | 0.013321 | 1 | 0.013321 | 0.03435
CURTIS 17019230 | CURTI | CURTIS 1701 | YOSEMITE | 2.2694 | 10 | 15.95% | 1 | 2 | 72.76% | 0% | 0 | 0.013303 | 1 | 0.013303 | 0.0058616
CORONA 11034446 | CORON | CORONA 1103 | SONOMA | 0.968 | 50.7747 | 83.54% | 0 | 0 | 7.888% | 0% | 0 | 0.013274 | 1 | 0.013274 | 0.013713
COPPERMINE 1104R755 | COPPE | COPPERMINE 1104 | FRESNO | 8.1519 | 17.5841 | 96.77% | 0 | 3 | 13.19% | 0% | 0 | 0.013252 | 1 | 0.013252 | 0.0016256
SAN RAFAEL 1109418 | SAN R | SAN RAFAEL 1109 | NORTH BAY | 4.3553 | 10 | 55.54% | 4 | 2 | 35.66% | 0% | 0 | 0.013234 | 1 | 0.013234 | 0.0030385
POINT ARENA 11013702 | POINT | POINT ARENA 1101 | HUMBOLDT | 4.3225 | 19.0711 | 4.681% | 4 | 1 | 86.66% | 0% | 0 | 0.013218 | 1 | 0.013218 | 0.003058
EDES 1112CR306 | EDES | EDES 1112 | EAST BAY | 1.0069 | 10 | 0% | 3 | 0 | 100% | 0% | 0 | 0.013203 | 1 | 0.013203 | 0.013112
LOS GATOS 1102CB | LOS G | LOS GATOS 1102 | DE ANZA | 1.1034 | 10 | 59.61% | 1 | 4 | 18.46% | 0% | 0 | 0.013194 | 1 | 0.013194 | 0.011957
MC KEE 1107XR010 | MC KE | MC KEE 1107 | SAN JOSE | 2.6945 | 34.7956 | 81.62% | 0 | 0 | 19.75% | 0% | 0 | 0.013193 | 1 | 0.013193 | 0.0048963
POSO MOUNTAIN 2104CB | POSO | POSO MOUNTAIN 2104 | KERN | 5.3916 | 10 | 6.227% | 0 | 6 | 72.59% | 0% | 0 | 0.013157 | 1 | 0.013157 | 0.0024402
PERRY 1101V72 | PERRY | PERRY 1101 | LOS PADRES | 5.7537 | 10 | 2.358% | 4 | 2 | 65.46% | 0% | 0 | 0.013146 | 1 | 0.013146 | 0.0022849
MORRO BAY 110248384 | MORRO | MORRO BAY 1102 | LOS PADRES | 0.22159 | 10 | 0% | 1 | 1 | 100% | 0% | 0 | 0.013132 | 1 | 0.013132 | 0.059259
GUALALA 1111402866 | GUALA | GUALALA 1111 | HUMBOLDT | 1.5915 | 10 | 0% | 1 | 1 | 100% | 0% | 0 | 0.013132 | 1 | 0.013132 | 0.008251
POINT ARENA 11011296 | POINT | POINT ARENA 1101 | HUMBOLDT | 2.101 | 59.6296 | 9.522% | 3 | 3 | 37.92% | 0% | 0 | 0.013105 | 1 | 0.013105 | 0.0062378
MESA 1103M68 | MESA | MESA 1103 | LOS PADRES | 0.22844 | 10 | 100% | 0 | 0 | 7.509% | 0% | 0 | 0.013101 | 1 | 0.013101 | 0.057352
RED BLUFF 11041630 | RED B | RED BLUFF 1104 | NORTH VALLEY | 2.5495 | 10 | 100% | 0 | 1 | 18.04% | 0% | 0 | 0.01301 | 1 | 0.01301 | 0.005103
LUCERNE 11031280 | LUCER | LUCERNE 1103 | HUMBOLDT | 8.886 | 18.4647 | 53.77% | 0 | 7 | 37.48% | 0% | 0 | 0.012974 | 1 | 0.012974 | 0.0014601
WYANDOTTE 1105329930 | WYAND | WYANDOTTE 1105 | NORTH VALLEY | 7.9312 | 11.1268 | 28.89% | 0 | 1 | 75.51% | 0% | 0 | 0.01297 | 1 | 0.01297 | 0.0016354
PLACERVILLE 1109CB | PLACE | PLACERVILLE 1109 | SIERRA | 0.020146 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.012961 | 1 | 0.012961 | 0.64336
GEYSERVILLE 1102756 | GEYSE | GEYSERVILLE 1102 | SONOMA | 0.58953 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.012961 | 1 | 0.012961 | 0.021986
HIGGINS 1107CB | HIGGI | HIGGINS 1107 | SIERRA | 4.6439 | 10 | 81.31% | 3 | 3 | 24.48% | 0% | 0 | 0.012908 | 1 | 0.012908 | 0.0027796
WILLITS 1102CB | WILLI | WILLITS 1102 | HUMBOLDT | 5.2584 | 15.1568 | 26.36% | 0 | 4 | 54.45% | 0% | 0 | 0.01287 | 1 | 0.01287 | 0.0024474
GEYSERVILLE 1101122 | GEYSE | GEYSERVILLE 1101 | SONOMA | 3.5712 | 48.4332 | 60.55% | 0 | 3 | 18.96% | 0% | 0 | 0.012864 | 1 | 0.012864 | 0.0036022
EDES 1112CR100 | EDES | EDES 1112 | EAST BAY | 3.3566 | 10 | 0% | 1 | 0 | 100% | 0% | 0 | 0.012862 | 1 | 0.012862 | 0.0038319
HALSEY 11022514 | HALSE | HALSEY 1102 | SIERRA | 9.2843 | 10 | 42.43% | 1 | 2 | 47.49% | 0% | 0 | 0.012855 | 1 | 0.012855 | 0.0013846
CABRILLO 1104CB | CABRI | CABRILLO 1104 | LOS PADRES | 4.9085 | 16.6076 | 47.38% | 0 | 1 | 28.73% | 0% | 0 | 0.012822 | 1 | 0.012822 | 0.0026123
SAN LUIS OBISPO 110788962 | SAN L | SAN LUIS OBISPO 1107 | LOS PADRES | 1.6209 | 48.7477 | 22.43% | 0 | 1 | 40.61% | 0% | 0 | 0.012815 | 1 | 0.012815 | 0.007906
FORT ROSS 1121560 | FORT | FORT ROSS 1121 | SONOMA | 5.3342 | 23.1043 | 0.06425% | 1 | 0 | 90.51% | 0% | 0 | 0.0128 | 1 | 0.0128 | 0.0023997
CLAY 11037142 | CLAY | CLAY 1103 | STOCKTON | 4.4879 | 10 | 67.68% | 2 | 0 | 29.1% | 0% | 0 | 0.012796 | 1 | 0.012796 | 0.0028513
DESCHUTES 1101CB | DESCH | DESCHUTES 1101 | NORTH VALLEY | 4.1985 | 15.36 | 72.74% | 0 | 0 | 36.89% | 0% | 0 | 0.012752 | 1 | 0.012752 | 0.0030371
RALSTON 11029126 | RALST | RALSTON 1102 | PENINSULA | 0.049841 | 10 | 100% | 0 | 1 | 2.638% | 0% | 0 | 0.012746 | 1 | 0.012746 | 0.25574
HICKS 2101XR548 | HICKS | HICKS 2101 | SAN JOSE | 1.763 | 53.1133 | 61.37% | 0 | 0 | 20.35% | 0% | 0 | 0.012735 | 1 | 0.012735 | 0.0072233
SAN RAFAEL 11042651 | SAN R | SAN RAFAEL 1104 | NORTH BAY | 0.79099 | 10 | 0% | 1 | 1 | 96.62% | 0% | 0 | 0.0127 | 1 | 0.0127 | 0.016056
OAKLAND K 1103CR422 | OAKLA | OAKLAND K 1103 | EAST BAY | 1.8547 | 10 | 4.055% | 0 | 3 | 90.41% | 0% | 0 | 0.0127 | 1 | 0.0127 | 0.0068473
EL CERRITO G 1110BR236 | EL CE | EL CERRITO G 1110 | EAST BAY | 0.52869 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.024013
FLORENCE 0401CR220 | FLORE | FLORENCE 0401 | EAST BAY | 0.0014212 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 8.9331
SAN CARLOS 11049048 | SAN C | SAN CARLOS 1104 | PENINSULA | 0.01529 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.83028
OAKLAND K 1104468 | OAKLA | OAKLAND K 1104 | EAST BAY | 0.0028424 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 4.4664
MORRO BAY 110298906 | MORRO | MORRO BAY 1102 | LOS PADRES | 0.034162 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.37162
MORRO BAY 110242062 | MORRO | MORRO BAY 1102 | LOS PADRES | 0.13997 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.090701
TASSAJARA 2104 | TASSA | TASSAJARA 2104 | DIABLO | 0.070201 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.18084
BERKELEY F 1105BR166 | BERKE | BERKELEY F 1105 | EAST BAY | 0.038193 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.3324
EL CERRITO G 1105BR164 | EL CE | EL CERRITO G 1105 | EAST BAY | 0.056936 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.22298
SAN RAMON 21077742 | SAN R | SAN RAMON 2107 | MISSION | 0.0028424 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 4.4665
VIEJO 220255787 | VIEJO | VIEJO 2202 | CENTRAL COAST | 0.036656 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.34633
SAN LEANDRO U 1109CR284 | SAN L | SAN LEANDRO U 1109 | MISSION | 0.93355 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.013599
CAROLANDS 0404 | CAROL | CAROLANDS 0404 | PENINSULA | 0.066741 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.19022
HIGGINS 1108CB | HIGGI | HIGGINS 1108 | SIERRA | 0.020411 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.622
BAY MEADOWS 2102 | BAY M | BAY MEADOWS 2102 | PENINSULA | 0.027395 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.46342
SAN LUIS OBISPO 110742048 | SAN L | SAN LUIS OBISPO 1107 | LOS PADRES | 0.025219 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.5034
SAN LUIS OBISPO 1107V08 | SAN L | SAN LUIS OBISPO 1107 | LOS PADRES | 0.024874 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.51038
DEL MONTE 21032204 | DEL M | DEL MONTE 2103 | CENTRAL COAST | 0.36868 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.034435
PEABODY 210818182 | PEABO | PEABODY 2108 | SACRAMENTO | 0.013085 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.9702
HIGGINS 1110 | HIGGI | HIGGINS 1110 | SIERRA | 0.035539 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.35723
MILPITAS 110962157 | MILPI | MILPITAS 1109 | SAN JOSE | 0.044828 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.2832
FORT ORD 21069658 | FORT | FORT ORD 2106 | CENTRAL COAST | 0.097044 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.13082
CMC 1102CB | CMC 1 | CMC 1102 | LOS PADRES | 0.46264 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.027441
HIGHLANDS 1101CB | HIGHL | HIGHLANDS 1101 | HUMBOLDT | 0.026418 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.48055
POINT MORETTI 110135874 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 0.27376 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.046374
PEORIA 1704 | PEORI | PEORIA 1704 | YOSEMITE | 0.12912 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.098323
MARIPOSA 210210250 | MARIP | MARIPOSA 2102 | YOSEMITE | 0.04003 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.31715
COAST RD 0401CB | COAST | COAST RD 0401 | CENTRAL COAST | 0.04709 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.2696
NARROWS 2104CB | NARRO | NARROWS 2104 | SIERRA | 0.002841 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 4.4686
HOOPA 1101 | HOOPA | HOOPA 1101 | HUMBOLDT | 0.098699 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.12863
POTTER VALLEY P H 1105990354 | POTTE | POTTER VALLEY P H 1105 | HUMBOLDT | 0.0040482 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 3.136
POTTER VALLEY PH 11054634 | POTTE | POTTER VALLEY PH 1105 | HUMBOLDT | 0.0052407 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 2.4225
POTTER VALLEY P H 1104CB | POTTE | POTTER VALLEY P H 1104 | HUMBOLDT | 0.077279 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.16428
POTTER VALLEY P H 11054634 | POTTE | POTTER VALLEY P H 1105 | HUMBOLDT | 0.13813 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.09191
CORNING 110193362 | CORNI | CORNING 1101 | NORTH VALLEY | 0.36788 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.03451
JOLON 110268034 | JOLON | JOLON 1102 | CENTRAL COAST | 0.019914 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 0.6375
PEORIA 1701 | PEORI | PEORIA 1701 | YOSEMITE | 0.00281 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.012695 | 4.5179
CASTRO VALLEY 1101MR204 | CASTR | CASTRO VALLEY 1101 | MISSION | 2.1197 | 29.3697 | 13.12% | 0 | 1 | 73.48% | 0% | 0 | 0.012645 | 1 | 0.012645 | 0.0059652
EDENVALE 2107CB | EDENV | EDENVALE 2107 | SAN JOSE | 0.73661 | 33.423 | 98.26% | 0 | 0 | 2.254% | 0% | 0 | 0.01259 | 1 | 0.01259 | 0.017092
LAS PULGAS 0401CB | LAS P | LAS PULGAS 0401 | PENINSULA | 0.063561 | 10 | 100% | 0 | 1 | 1.053% | 0% | 0 | 0.012548 | 1 | 0.012548 | 0.19742
POSO MOUNTAIN 210448268 | POSO | POSO MOUNTAIN 2104 | KERN | 4.774 | 10 | 10.21% | 0 | 0 | 90.31% | 0% | 0 | 0.012535 | 1 | 0.012535 | 0.0026258
SANTA YNEZ 1102320270 | SANTA | SANTA YNEZ 1102 | LOS PADRES | 0.55315 | 10 | 90.55% | 0 | 2 | 19.74% | 0% | 0 | 0.012507 | 1 | 0.012507 | 0.022611
OREGON TRAIL 110346860 | OREGO | OREGON TRAIL 1103 | NORTH VALLEY | 0.53541 | 10 | 100% | 0 | 0 | 16.12% | 0% | 0 | 0.012504 | 1 | 0.012504 | 0.023355
JESSUP 110338864 | JESSU | JESSUP 1103 | NORTH VALLEY | 0.59204 | 10 | 100% | 1 | 3 | 7.85% | 0% | 0 | 0.012422 | 1 | 0.012422 | 0.020981
FRANKLIN 1101P138 | FRANK | FRANKLIN 1101 | EAST BAY | 1.4993 | 10 | 0% | 0 | 0 | 97.65% | 0% | 0 | 0.012403 | 1 | 0.012403 | 0.0082724
HALF MOON BAY 11039112 | HALF | HALF MOON BAY 1103 | PENINSULA | 3.4704 | 36.5949 | 39.16% | 3 | 0 | 43.21% | 0% | 0 | 0.012394 | 1 | 0.012394 | 0.0035712
PEABODY 2106CB | PEABO | PEABODY 2106 | SACRAMENTO | 0.58049 | 10 | 53.14% | 0 | 0 | 53.74% | 0% | 0 | 0.012385 | 1 | 0.012385 | 0.021335
STONE CORRAL 11107784F | STONE | STONE CORRAL 1110 | FRESNO | 0.37155 | 63.2273 | 64.55% | 0 | 0 | 7.804% | 0% | 0 | 0.012359 | 1 | 0.012359 | 0.033264
COTATI 1102464 | COTAT | COTATI 1102 | SONOMA | 1.2747 | 26.0788 | 66.97% | 0 | 1 | 15.73% | 0% | 0 | 0.012358 | 1 | 0.012358 | 0.0096952
ELK 11014628 | ELK 1 | ELK 1101 | HUMBOLDT | 2.8486 | 10 | 0% | 0 | 7 | 69.22% | 0% | 0 | 0.012349 | 1 | 0.012349 | 0.0043351
COVELO 1101536 | COVEL | COVELO 1101 | HUMBOLDT | 0.011418 | 10 | 100% | 1 | 0 | 0.05103% | 0% | 0 | 0.012329 | 1 | 0.012329 | 1.0799
MORRO BAY 1101V66 | MORRO | MORRO BAY 1101 | LOS PADRES | 3.6398 | 32.9293 | 34.81% | 0 | 0 | 22.6% | 18.48% | 0 | 0.01232 | 1 | 0.01232 | 0.0033847
FITCH MOUNTAIN 11115060 | FITCH | FITCH MOUNTAIN 1111 | SONOMA | 2.1624 | 43.6089 | 39.41% | 0 | 3 | 35.19% | 0% | 0 | 0.012308 | 1 | 0.012308 | 0.0056917
BANGOR 110155206 | BANGO | BANGOR 1101 | NORTH VALLEY | 2.9326 | 34.2156 | 61.32% | 1 | 0 | 28.49% | 0% | 0 | 0.012304 | 1 | 0.012304 | 0.0041954
KERN OIL 11063301 | KERN | KERN OIL 1106 | KERN | 0.36257 | 10 | 100% | 0 | 0 | 1.116% | 0% | 0 | 0.012298 | 1 | 0.012298 | 0.03392
PANORAMA 1101CB | PANOR | PANORAMA 1101 | NORTH VALLEY | 1.9355 | 10 | 100% | 0 | 2 | 10.24% | 0% | 0 | 0.012297 | 1 | 0.012297 | 0.0063532
SAN RAFAEL 1104CB | SAN R | SAN RAFAEL 1104 | NORTH BAY | 2.4428 | 10 | 2.078% | 0 | 0 | 23.27% | 19.55% | 0 | 0.012295 | 1 | 0.012295 | 0.0050332
RISING RIVER 11011532 | RISIN | RISING RIVER 1101 | NORTH VALLEY | 3.0653 | 21.21 | 32.28% | 0 | 0 | 62.2% | 0% | 0 | 0.012255 | 1 | 0.012255 | 0.003998
SAN LUIS OBISPO 1105CB | SAN L | SAN LUIS OBISPO 1105 | LOS PADRES | 1.9887 | 39.9951 | 43.06% | 3 | 3 | 16.92% | 0% | 0 | 0.012254 | 1 | 0.012254 | 0.0061616
MORGAN HILL 2105XR494 | MORGA | MORGAN HILL 2105 | SAN JOSE | 0.23352 | 25.7168 | 100% | 0 | 0 | 3.179% | 0% | 0 | 0.012233 | 1 | 0.012233 | 0.052386
SNEATH LANE 11071277 | SNEAT | SNEATH LANE 1107 | PENINSULA | 0.25243 | 10 | 100% | 0 | 1 | 11.7% | 0% | 0 | 0.012219 | 1 | 0.012219 | 0.048404
BURNEY 1101CB | BURNE | BURNEY 1101 | NORTH VALLEY | 0.91927 | 10 | 59.07% | 1 | 0 | 46.14% | 0% | 0 | 0.012215 | 1 | 0.012215 | 0.013288
WYANDOTTE 11102590 | WYAND | WYANDOTTE 1110 | NORTH VALLEY | 0.10676 | 10 | 95.21% | 0 | 0 | 17.59% | 0% | 0 | 0.012201 | 1 | 0.012201 | 0.11429
CABRILLO 1103Y10 | CABRI | CABRILLO 1103 | LOS PADRES | 4.0955 | 68.6545 | 11.89% | 0 | 1 | 43.98% | 0% | 0 | 0.012191 | 1 | 0.012191 | 0.0029767
CALPELLA 1102CB | CALPE | CALPELLA 1102 | HUMBOLDT | 1.6769 | 10 | 88.62% | 0 | 2 | 18.53% | 0% | 0 | 0.012165 | 1 | 0.012165 | 0.0072547
HARTLEY 110194178 | HARTL | HARTLEY 1101 | HUMBOLDT | 1.6171 | 10 | 47.04% | 0 | 1 | 41.48% | 0% | 0 | 0.012159 | 1 | 0.012159 | 0.0075188
RACETRACK 170310850 | RACET | RACETRACK 1703 | YOSEMITE | 0.060314 | 10 | 0% | 0 | 0 | 95.5% | 0% | 0 | 0.012143 | 1 | 0.012143 | 0.20132
NORTH BRANCH 110113496 | NORTH | NORTH BRANCH 1101 | STOCKTON | 2.2189 | 10 | 62.08% | 0 | 0 | 44.24% | 0% | 0 | 0.012126 | 1 | 0.012126 | 0.0054646
RIO DELL 110270960 | RIO D | RIO DELL 1102 | HUMBOLDT | 3.7354 | 51.8564 | 33.96% | 2 | 2 | 31.94% | 0% | 0 | 0.012119 | 1 | 0.012119 | 0.0032445
REDBUD 110244119 | REDBU | REDBUD 1102 | HUMBOLDT | 0.66752 | 10 | 86.82% | 0 | 0 | 23.81% | 0% | 0 | 0.012119 | 1 | 0.012119 | 0.018155
WILLITS 1104CB | WILLI | WILLITS 1104 | HUMBOLDT | 2.2442 | 16.2086 | 22.49% | 1 | 7 | 29.86% | 0% | 0 | 0.012113 | 1 | 0.012113 | 0.0053972
CABRILLO 1104Y22 | CABRI | CABRILLO 1104 | LOS PADRES | 7.1091 | 12.8346 | 36.03% | 1 | 10 | 27.87% | 0% | 0 | 0.012091 | 1 | 0.012091 | 0.0017008
JESSUP 1102CB | JESSU | JESSUP 1102 | NORTH VALLEY | 0.20781 | 10 | 69.42% | 4 | 1 | 3.869% | 0% | 0 | 0.01209 | 1 | 0.01209 | 0.05818
COVELO 1101562360 | COVEL | COVELO 1101 | HUMBOLDT | 2.2904 | 16.1283 | 100% | 0 | 1 | 6.052% | 0% | 0 | 0.012043 | 1 | 0.012043 | 0.0052583
COTATI 1104426 | COTAT | COTATI 1104 | SONOMA | 2.1239 | 10 | 43.82% | 0 | 2 | 54.27% | 0% | 0 | 0.012029 | 1 | 0.012029 | 0.0056636
HUMBOLDT BAY 11024724 | HUMBO | HUMBOLDT BAY 1102 | HUMBOLDT | 7.0458 | 41.454 | 0.8967% | 10 | 0 | 45.74% | 0% | 0 | 0.012021 | 1 | 0.012021 | 0.0017061
OAKLAND K 1101CR172 | OAKLA | OAKLAND K 1101 | EAST BAY | 0.63886 | 10 | 27.9% | 0 | 1 | 30.68% | 23.7% | 0 | 0.011998 | 1 | 0.011998 | 0.018781
ZACA 1102Y48 | ZACA | ZACA 1102 | LOS PADRES | 4.0585 | 10 | 41.4% | 0 | 6 | 34.23% | 0% | 0 | 0.011989 | 1 | 0.011989 | 0.0029539
WISE 110163199 | WISE | WISE 1101 | SIERRA | 0.5708 | 42.4087 | 13.05% | 0 | 0 | 61.18% | 0% | 0 | 0.01197 | 1 | 0.01197 | 0.02097
GREENBRAE 110388832 | GREEN | GREENBRAE 1103 | NORTH BAY | 1.2167 | 10 | 6.453% | 0 | 0 | 88.72% | 0% | 0 | 0.011967 | 1 | 0.011967 | 0.0098361
GEYSERVILLE 1101CB | GEYSE | GEYSERVILLE 1101 | SONOMA | 0.2847 | 40.3314 | 82.04% | 0 | 1 | 3.457% | 0% | 0 | 0.011941 | 1 | 0.011941 | 0.041943
DEL MONTE 21049096 | DEL M | DEL MONTE 2104 | CENTRAL COAST | 2.1074 | 10 | 10.71% | 2 | 5 | 31.81% | 0% | 0 | 0.011931 | 1 | 0.011931 | 0.0056617
CASTRO VALLEY 1108MR341 | CASTR | CASTRO VALLEY 1108 | MISSION | 2.4534 | 10 | 13.13% | 0 | 1 | 77.41% | 2.031% | 0 | 0.011918 | 1 | 0.011918 | 0.0048576
BUTTE 11052410 | BUTTE | BUTTE 1105 | NORTH VALLEY | 1.8432 | 10 | 92.92% | 0 | 0 | 16.76% | 0% | 0 | 0.011878 | 1 | 0.011878 | 0.0064441
PALMER 1101M88 | PALME | PALMER 1101 | LOS PADRES | 2.2617 | 68.2305 | 27.53% | 0 | 1 | 14.75% | 0% | 0 | 0.011798 | 1 | 0.011798 | 0.0052164
TEJON 11032280 | TEJON | TEJON 1103 | KERN | 2.7582 | 10 | 100% | 0 | 0 | 9.965% | 0% | 0 | 0.011765 | 1 | 0.011765 | 0.0042654
ELK 1101CB | ELK 1 | ELK 1101 | HUMBOLDT | 0.88673 | 10 | 0% | 1 | 0 | 90.98% | 0% | 0 | 0.011764 | 1 | 0.011764 | 0.013267
SAN ARDO 11017632 | SAN A | SAN ARDO 1101 | CENTRAL COAST | 0.79963 | 10 | 100% | 0 | 0 | 9.729% | 0% | 0 | 0.011737 | 1 | 0.011737 | 0.014678
SOLEDAD 21027008 | SOLED | SOLEDAD 2102 | CENTRAL COAST | 1.2631 | 69.0048 | 38.01% | 0 | 0 | 6.974% | 0% | 0 | 0.011715 | 1 | 0.011715 | 0.009275
GONZALES 11033096 | GONZA | GONZALES 1103 | CENTRAL COAST | 1.0413 | 57.173 | 49.23% | 0 | 0 | 5.766% | 0% | 0 | 0.011709 | 1 | 0.011709 | 0.011245
PUEBLO 2103694 | PUEBL | PUEBLO 2103 | NORTH BAY | 0.4502 | 10 | 100% | 0 | 0 | 9.445% | 0% | 0 | 0.011704 | 1 | 0.011704 | 0.025998
KONOCTI 11022293 | KONOC | KONOCTI 1102 | HUMBOLDT | 0.16556 | 10 | 100% | 0 | 0 | 9.444% | 0% | 0 | 0.011704 | 1 | 0.011704 | 0.070692
HARTLEY 1101738 | HARTL | HARTLEY 1101 | HUMBOLDT | 3.053 | 10 | 42.13% | 1 | 2 | 37.87% | 0% | 0 | 0.011659 | 1 | 0.011659 | 0.0038189
CALAVERAS CEMENT 110113424 | CALAV | CALAVERAS CEMENT 1101 | STOCKTON | 1.1628 | 27.7873 | 54.51% | 0 | 1 | 32.26% | 0% | 0 | 0.011657 | 1 | 0.011657 | 0.010025
ANDERSON 1103CB | ANDER | ANDERSON 1103 | NORTH VALLEY | 3.2551 | 15.9196 | 80.29% | 1 | 2 | 15.59% | 0% | 0 | 0.011642 | 1 | 0.011642 | 0.0035766
GEYSERVILLE 1101480 | GEYSE | GEYSERVILLE 1101 | SONOMA | 1.4699 | 10 | 99.61% | 0 | 0 | 9.197% | 0% | 0 | 0.011639 | 1 | 0.011639 | 0.0079179
WILLOW PASS 1101CB | WILLO | WILLOW PASS 1101 | DIABLO | 0.46926 | 10 | 100% | 0 | 1 | 6.681% | 0% | 0 | 0.011627 | 1 | 0.011627 | 0.024777
CAYUCOS 11014701 | CAYUC | CAYUCOS 1101 | LOS PADRES | 2.0826 | 72.227 | 28.46% | 1 | 0 | 23.77% | 0% | 0 | 0.011613 | 1 | 0.011613 | 0.0055764
HOPLAND 1101CB | HOPLA | HOPLAND 1101 | HUMBOLDT | 0.39955 | 10 | 100% | 0 | 1 | 6.5% | 0% | 0 | 0.011606 | 1 | 0.011606 | 0.029048
MORRO BAY 110280174 | MORRO | MORRO BAY 1102 | LOS PADRES | 3.4488 | 10 | 0% | 1 | 0 | 76.14% | 0% | 0 | 0.011588 | 1 | 0.011588 | 0.0033601
GIRVAN 1102CB | GIRVA | GIRVAN 1102 | NORTH VALLEY | 4.7326 | 13.9144 | 68.55% | 4 | 1 | 22.51% | 1.048% | 1 | 0.01158 | 1 | 0.01158 | 0.0024468
RED BLUFF 1105161818 | RED B | RED BLUFF 1105 | NORTH VALLEY | 0.38337 | 10 | 100% | 0 | 0 | 8.045% | 0% | 0 | 0.011543 | 1 | 0.011543 | 0.03011
OAKHURST 110311900 | OAKHU | OAKHURST 1103 | YOSEMITE | 0.064919 | 10 | 100% | 0 | 0 | 7.722% | 0% | 0 | 0.011506 | 1 | 0.011506 | 0.17724
WYANDOTTE 110313018 | WYAND | WYANDOTTE 1103 | NORTH VALLEY | 0.12548 | 10 | 100% | 0 | 0 | 7.599% | 0% | 0 | 0.011492 | 1 | 0.011492 | 0.091583
SOLEDAD 2101CB | SOLED | SOLEDAD 2101 | CENTRAL COAST | 1.1091 | 10 | 100% | 0 | 0 | 7.451% | 0% | 0 | 0.011475 | 1 | 0.011475 | 0.010346
OCEANO 1105V44 | OCEAN | OCEANO 1105 | LOS PADRES | 0.92167 | 10 | 6.253% | 0 | 2 | 80.43% | 0% | 0 | 0.011472 | 1 | 0.011472 | 0.012447
BRENTWOOD 2105502672 | BRENT | BRENTWOOD 2105 | DIABLO | 1.383 | 10 | 100% | 0 | 0 | 7.371% | 0% | 0 | 0.011466 | 1 | 0.011466 | 0.0082912
CARLOTTA 11214045 | CARLO | CARLOTTA 1121 | HUMBOLDT | 0.14338 | 10 | 100% | 0 | 0 | 7.252% | 0% | 0 | 0.011453 | 1 | 0.011453 | 0.079879
PETALUMA C 1109270 | PETAL | PETALUMA C 1109 | SONOMA | 1.61 | 25.9839 | 62.25% | 0 | 3 | 21.02% | 0% | 0 | 0.011438 | 1 | 0.011438 | 0.0071044
BIG RIVER 11012989 | BIG R | BIG RIVER 1101 | HUMBOLDT | 0.072968 | 10 | 100% | 0 | 0 | 6.918% | 0% | 0 | 0.011415 | 1 | 0.011415 | 0.15644
BELMONT 11038958 | BELMO | BELMONT 1103 | PENINSULA | 0.46477 | 10 | 49.35% | 0 | 4 | 26.9% | 0% | 0 | 0.011413 | 1 | 0.011413 | 0.024556
SYCAMORE CREEK 1109CB | SYCAM | SYCAMORE CREEK 1109 | NORTH VALLEY | 0.58228 | 10 | 100% | 0 | 0 | 6.6% | 0% | 0 | 0.011379 | 1 | 0.011379 | 0.019542
HOLLISTER 21024780 | HOLLI | HOLLISTER 2102 | CENTRAL COAST | 2.8684 | 10 | 66.05% | 0 | 1 | 19.03% | 0% | 0 | 0.011367 | 1 | 0.011367 | 0.0039629
ROB ROY 210512584 | ROB R | ROB ROY 2105 | CENTRAL COAST | 3.0913 | 10 | 22.02% | 2 | 1 | 25.72% | 0% | 0 | 0.011337 | 1 | 0.011337 | 0.0036674
CASTRO VALLEY 1101MR359 | CASTR | CASTRO VALLEY 1101 | MISSION | 0.81851 | 10 | 96.11% | 0 | 0 | 9.323% | 0% | 0 | 0.011325 | 1 | 0.011325 | 0.013836
DUNBAR 110113481 | DUNBA | DUNBAR 1101 | SONOMA | 0.13904 | 10 | 89.93% | 1 | 0 | 12.88% | 0% | 0 | 0.011301 | 1 | 0.011301 | 0.081279
CASTRO VALLEY 1106MR205 | CASTR | CASTRO VALLEY 1106 | MISSION | 0.6704 | 10 | 69.55% | 0 | 0 | 12.34% | 11.35% | 0 | 0.01128 | 1 | 0.01128 | 0.016826
LAS GALLINAS A 11051218 | LAS G | LAS GALLINAS A 1105 | NORTH BAY | 0.13008 | 10 | 100% | 0 | 0 | 5.571% | 0% | 0 | 0.011264 | 1 | 0.011264 | 0.086592
SAN CARLOS 110479774 | SAN C | SAN CARLOS 1104 | PENINSULA | 0.48017 | 10 | 65.63% | 1 | 1 | 30.37% | 0% | 0 | 0.011253 | 1 | 0.011253 | 0.023436
SAUSALITO 11011270 | SAUSA | SAUSALITO 1101 | NORTH BAY | 0.49678 | 64.5423 | 0% | 0 | 0 | 50.41% | 0% | 0 | 0.011233 | 1 | 0.011233 | 0.022612
WYANDOTTE 11091520 | WYAND | WYANDOTTE 1109 | NORTH VALLEY | 4.1645 | 10 | 80.53% | 0 | 0 | 21.24% | 0% | 0 | 0.011222 | 1 | 0.011222 | 0.0026947
WYANDOTTE 11101952 | WYAND | WYANDOTTE 1110 | NORTH VALLEY | 0.44853 | 10 | 100% | 0 | 0 | 5.144% | 0% | 0 | 0.011216 | 1 | 0.011216 | 0.025006
MADISON 21011606 | MADIS | MADISON 2101 | SACRAMENTO | 0.66018 | 28.3427 | 86.09% | 0 | 0 | 3.933% | 0% | 0 | 0.0112 | 1 | 0.0112 | 0.016964
WILLOW PASS 2107P500R | WILLO | WILLOW PASS 2107 | DIABLO | 0.15832 | 10 | 100% | 0 | 0 | 4.986% | 0% | 0 | 0.011198 | 1 | 0.011198 | 0.070731
EL CERRITO G 1113CB | EL CE | EL CERRITO G 1113 | EAST BAY | 0.20892 | 10 | 100% | 0 | 0 | 4.98% | 0% | 0 | 0.011198 | 1 | 0.011198 | 0.053598
TASSAJARA 2103CB | TASSA | TASSAJARA 2103 | DIABLO | 1.7119 | 10 | 14.73% | 0 | 4 | 9.614% | 35.07% | 0 | 0.011177 | 1 | 0.011177 | 0.0065293
LAS POSITAS 2108MR190 | LAS P | LAS POSITAS 2108 | MISSION | 1.1924 | 39.2847 | 52.56% | 0 | 0 | 10.54% | 0% | 0 | 0.011177 | 1 | 0.011177 | 0.0093738
OLEMA 110137074 | OLEMA | OLEMA 1101 | NORTH BAY | 0.013643 | 10 | 100% | 0 | 0 | 4.337% | 0% | 0 | 0.011127 | 1 | 0.011127 | 0.81555
CLAY 1102CB | CLAY | CLAY 1102 | STOCKTON | 1.1664 | 10 | 0% | 0 | 0 | 60.02% | 0% | 0 | 0.011126 | 1 | 0.011126 | 0.0095392
MORRO BAY 1102CB | MORRO | MORRO BAY 1102 | LOS PADRES | 3.3958 | 10 | 1.002% | 0 | 0 | 71.82% | 0% | 0 | 0.011049 | 1 | 0.011049 | 0.0032539
CLAY 1103CB | CLAY | CLAY 1103 | STOCKTON | 5.7506 | 36.571 | 11.82% | 0 | 1 | 42.68% | 0% | 0 | 0.011049 | 1 | 0.011049 | 0.0019214
COTTONWOOD 1103CB | COTTO | COTTONWOOD 1103 | NORTH VALLEY | 0.091321 | 14.0615 | 100% | 0 | 0 | 0.8116% | 0% | 0 | 0.011044 | 1 | 0.011044 | 0.12094
PUEBLO 2102CB | PUEBL | PUEBLO 2102 | NORTH BAY | 0.216 | 10 | 100% | 0 | 1 | 1.423% | 0% | 0 | 0.011037 | 1 | 0.011037 | 0.051095
OROSI 11027948F | OROSI | OROSI 1102 | FRESNO | 0.26307 | 10 | 100% | 0 | 0 | 3.077% | 0% | 0 | 0.010989 | 1 | 0.010989 | 0.04177
FORT BRAGG A 1102 | FORT | FORT BRAGG A 1102 | HUMBOLDT | 0.10961 | 10 | 0% | 0 | 0 | 85.38% | 0% | 0 | 0.010984 | 1 | 0.010984 | 0.10021
SAN BERNARD 1101CB | SAN B | SAN BERNARD 1101 | KERN | 0.91753 | 10 | 100% | 0 | 0 | 2.928% | 0% | 0 | 0.010972 | 1 | 0.010972 | 0.011959
CLOVERDALE 1102670 | CLOVE | CLOVERDALE 1102 | SONOMA | 0.27521 | 10 | 95.35% | 0 | 0 | 6.733% | 0% | 0 | 0.01097 | 1 | 0.01097 | 0.03986
SARATOGA 110413314 | SARAT | SARATOGA 1104 | DE ANZA | 1.7714 | 10 | 52.47% | 2 | 5 | 15.54% | 0% | 0 | 0.010963 | 1 | 0.010963 | 0.0061886
EEL RIVER 1102530 | EEL R | EEL RIVER 1102 | HUMBOLDT | 5.0874 | 49.3959 | 37.23% | 9 | 0 | 15.69% | 0% | 0 | 0.010956 | 1 | 0.010956 | 0.0021536
ROSSMOOR 1101L501R | ROSSM | ROSSMOOR 1101 | DIABLO | 0.055455 | 10 | 100% | 0 | 0 | 2.751% | 0% | 0 | 0.010953 | 1 | 0.010953 | 0.19751
WESTLEY 11039010 | WESTL | WESTLEY 1103 | YOSEMITE | 0.92376 | 10 | 100% | 0 | 0 | 2.686% | 0% | 0 | 0.010946 | 1 | 0.010946 | 0.011849
RACETRACK 170310870 | RACET | RACETRACK 1703 | YOSEMITE | 1.0803 | 10 | 45.22% | 0 | 3 | 41.49% | 0% | 0 | 0.010943 | 1 | 0.010943 | 0.01013
SAN LEANDRO U 1114MR544 | SAN L | SAN LEANDRO U 1114 | MISSION | 2.1618 | 10 | 45.25% | 0 | 0 | 34.37% | 0% | 0 | 0.010938 | 1 | 0.010938 | 0.0050596
HOLLYWOOD 0401CB | HOLLY | HOLLYWOOD 0401 | EAST BAY | 2.9599 | 10 | 0% | 0 | 1 | 55.84% | 0% | 0 | 0.010899 | 1 | 0.010899 | 0.0036821
SUMMIT 110148636 | SUMMI | SUMMIT 1101 | SIERRA | 0.057422 | 10 | 100% | 0 | 0 | 2.116% | 0% | 0 | 0.010884 | 1 | 0.010884 | 0.18955
LOYOLA 1102LL12 | LOYOL | LOYOLA 1102 | DE ANZA | 0.10967 | 10 | 100% | 0 | 0 | 1.811% | 0% | 0 | 0.010852 | 1 | 0.010852 | 0.098947
WALDO 0402CB | WALDO | WALDO 0402 | EAST BAY | 3.0716 | 10 | 16.14% | 2 | 4 | 59.8% | 0% | 0 | 0.010847 | 1 | 0.010847 | 0.0035314
DIVIDE 110348160 | DIVID | DIVIDE 1103 | LOS PADRES | 2.2423 | 10 | 32.11% | 0 | 0 | 17.66% | 0% | 0 | 0.010844 | 1 | 0.010844 | 0.004836
HOLLISTER 210441808 | HOLLI | HOLLISTER 2104 | CENTRAL COAST | 0.1888 | 10 | 100% | 0 | 0 | 1.735% | 0% | 0 | 0.010843 | 1 | 0.010843 | 0.057433
HOPLAND 1101558 | HOPLA | HOPLAND 1101 | HUMBOLDT | 0.37929 | 10 | 97.04% | 0 | 0 | 4.114% | 0% | 0 | 0.010837 | 1 | 0.010837 | 0.028573
RIO DEL MAR 0401CB | RIO D | RIO DEL MAR 0401 | CENTRAL COAST | 1.702 | 10 | 16.67% | 5 | 1 | 48.18% | 0% | 0 | 0.010828 | 1 | 0.010828 | 0.0063618
VIEJO 220292792 | VIEJO | VIEJO 2202 | CENTRAL COAST | 0.01896 | 10 | 100% | 0 | 0 | 1.272% | 0% | 0 | 0.010794 | 1 | 0.010794 | 0.5693
MONTEREY 04022644 | MONTE | MONTEREY 0402 | CENTRAL COAST | 0.7655 | 10 | 0% | 1 | 1 | 53.52% | 0% | 0 | 0.010791 | 1 | 0.010791 | 0.014097
SAN RAFAEL 1106910 | SAN R | SAN RAFAEL 1106 | NORTH BAY | 1.5306 | 10 | 41.18% | 0 | 1 | 20.8% | 0% | 0 | 0.010777 | 1 | 0.010777 | 0.0070407
MADISON 21011943 | MADIS | MADISON 2101 | SACRAMENTO | 0.028904 | 10 | 100% | 0 | 0 | 0.9967% | 0% | 0 | 0.010764 | 1 | 0.010764 | 0.37242
LINCOLN 11042072 | LINCO | LINCOLN 1104 | SIERRA | 0.13391 | 10 | 100% | 0 | 0 | 0.7885% | 0% | 0 | 0.010742 | 1 | 0.010742 | 0.080219
SAN LEANDRO U 1107MR560 | SAN L | SAN LEANDRO U 1107 | MISSION | 0.061986 | 10 | 100% | 0 | 0 | 0.7828% | 0% | 0 | 0.010742 | 1 | 0.010742 | 0.17329
STONE CORRAL 11107320 | STONE | STONE CORRAL 1110 | FRESNO | 1.9474 | 22.4898 | 48.09% | 0 | 0 | 8.248% | 0% | 0 | 0.010731 | 1 | 0.010731 | 0.0055107
PANORAMA 1102CB | PANOR | PANORAMA 1102 | NORTH VALLEY | 0.071747 | 10 | 100% | 0 | 0 | 0.6421% | 0% | 0 | 0.010727 | 1 | 0.010727 | 0.14951
HATTON 11022070 | HATTO | HATTON 1102 | CENTRAL COAST | 0.49418 | 10 | 29.42% | 0 | 3 | 25.81% | 0% | 0 | 0.010726 | 1 | 0.010726 | 0.021705
EL CERRITO G 1112BR196 | EL CE | EL CERRITO G 1112 | EAST BAY | 0.02286 | 10 | 100% | 0 | 0 | 0.6321% | 0% | 0 | 0.010725 | 1 | 0.010725 | 0.46917
EAST MARYSVILLE 11081706 | EAST | EAST MARYSVILLE 1108 | SIERRA | 0.35809 | 10 | 100% | 0 | 0 | 0.5923% | 0% | 0 | 0.010721 | 1 | 0.010721 | 0.02994
BUELLTON 1101753644 | BUELL | BUELLTON 1101 | LOS PADRES | 0.0028488 | 10 | 100% | 0 | 0 | 0.4009% | 0% | 0 | 0.010701 | 1 | 0.010701 | 3.7563
PRUNEDALE 11103716 | PRUNE | PRUNEDALE 1110 | CENTRAL COAST | 0.046537 | 10 | 100% | 0 | 0 | 0.3534% | 0% | 0 | 0.010696 | 1 | 0.010696 | 0.22984
DOLAN ROAD 11013012 | DOLAN | DOLAN ROAD 1101 | CENTRAL COAST | 2.5496 | 10 | 65.12% | 1 | 1 | 12.08% | 0% | 0 | 0.010669 | 1 | 0.010669 | 0.0041846
BIG MEADOWS 21012016 | BIG M | BIG MEADOWS 2101 | NORTH VALLEY | 0.0028416 | 10 | 100% | 0 | 0 | 0.06646% | 0% | 0 | 0.010666 | 1 | 0.010666 | 3.7533
SUNOL 1101CB | SUNOL | SUNOL 1101 | MISSION | 3.3865 | 29.3526 | 12.99% | 0 | 0 | 58.39% | 0% | 0 | 0.010654 | 1 | 0.010654 | 0.0031459
DOLAN ROAD 110122158 | DOLAN | DOLAN ROAD 1101 | CENTRAL COAST | 1.2712 | 10 | 84.22% | 0 | 1 | 10.85% | 0% | 0 | 0.010653 | 1 | 0.010653 | 0.0083798
FAIRVIEW 2207P150 | FAIRV | FAIRVIEW 2207 | DIABLO | 1.7182 | 19.1624 | 0% | 0 | 0 | 75.67% | 0% | 0 | 0.010614 | 1 | 0.010614 | 0.0061773
SANTA YNEZ 1102CB | SANTA | SANTA YNEZ 1102 | LOS PADRES | 1.3864 | 10 | 42.97% | 0 | 2 | 15.51% | 0% | 0 | 0.010594 | 1 | 0.010594 | 0.0076415
SAN LEANDRO U 11149838 | SAN L | SAN LEANDRO U 1114 | MISSION | 1.9933 | 10 | 1.408% | 0 | 0 | 80.56% | 0% | 0 | 0.010593 | 1 | 0.010593 | 0.005314
CAMBRIA 1102W50 | CAMBR | CAMBRIA 1102 | LOS PADRES | 2.1309 | 10 | 10.45% | 0 | 0 | 58.83% | 0% | 0 | 0.010493 | 1 | 0.010493 | 0.0049243
GRASS VALLEY 1103CB | GRASS | GRASS VALLEY 1103 | SIERRA | 0.095866 | 10 | 0% | 0 | 0 | 80.7% | 0% | 0 | 0.010486 | 1 | 0.010486 | 0.10939
COTATI 1105893 | COTAT | COTATI 1105 | SONOMA | 0.50896 | 59.1092 | 51.41% | 0 | 0 | 4.828% | 0% | 0 | 0.010484 | 1 | 0.010484 | 0.0206
LAS GALLINAS A 1105904 | LAS G | LAS GALLINAS A 1105 | NORTH BAY | 2.5108 | 10 | 36.59% | 0 | 1 | 34.95% | 0% | 0 | 0.010466 | 1 | 0.010466 | 0.0041684
COTTONWOOD 1101CB | COTTO | COTTONWOOD 1101 | NORTH VALLEY | 5.2937 | 10 | 60.95% | 2 | 2 | 23.27% | 0% | 0 | 0.010444 | 1 | 0.010444 | 0.0019729
PURISIMA 1101Y42 | PURIS | PURISIMA 1101 | LOS PADRES | 0.33998 | 72.2951 | 27.05% | 0 | 0 | 2.02% | 0% | 0 | 0.010429 | 1 | 0.010429 | 0.030675
TEMPLETON 2108A40 | TEMPL | TEMPLETON 2108 | LOS PADRES | 1.2118 | 10 | 85.64% | 0 | 0 | 9.425% | 0% | 0 | 0.010408 | 1 | 0.010408 | 0.0085888
RESERVATION ROAD 11023032 | RESER | RESERVATION ROAD 1102 | CENTRAL COAST | 1.7351 | 10 | 40.39% | 0 | 1 | 17.91% | 0% | 0 | 0.010406 | 1 | 0.010406 | 0.0059972
CLEAR LAKE 11024708 | CLEAR | CLEAR LAKE 1102 | HUMBOLDT | 0.26472 | 10 | 85.61% | 0 | 0 | 9.354% | 0% | 0 | 0.010398 | 1 | 0.010398 | 0.039279
CAMBRIA 1101CB | CAMBR | CAMBRIA 1101 | LOS PADRES | 7.5504 | 30.2261 | 1.521% | 0 | 1 | 62.43% | 0% | 0 | 0.010371 | 1 | 0.010371 | 0.0013736
PACIFICA 110266732 | PACIF | PACIFICA 1102 | PENINSULA | 1.1315 | 10 | 0% | 1 | 0 | 38.02% | 24.53% | 0 | 0.010334 | 1 | 0.010334 | 0.0091329
CARLOTTA 1121CB | CARLO | CARLOTTA 1121 | HUMBOLDT | 3.8375 | 25.0692 | 63.58% | 0 | 0 | 16.59% | 0% | 0 | 0.010334 | 1 | 0.010334 | 0.002693
ATASCADERO 1101A22 | ATASC | ATASCADERO 1101 | LOS PADRES | 0.48233 | 10 | 88.74% | 0 | 1 | 3.681% | 0% | 0 | 0.010296 | 1 | 0.010296 | 0.021345
MORGAN HILL 2105XR602 | MORGA | MORGAN HILL 2105 | SAN JOSE | 0.59187 | 10 | 11.22% | 0 | 0 | 69.56% | 0% | 0 | 0.010291 | 1 | 0.010291 | 0.017387
LLAGAS 2105XR234 | LLAGA | LLAGAS 2105 | SAN JOSE | 0.40589 | 10 | 70.52% | 0 | 1 | 18.63% | 0% | 0 | 0.01029 | 1 | 0.01029 | 0.025352
WILLITS 110337504 | WILLI | WILLITS 1103 | HUMBOLDT | 0.81372 | 28.0694 | 47.51% | 0 | 2 | 22.82% | 0% | 0 | 0.010255 | 1 | 0.010255 | 0.012603
LAKEVILLE 1102530 | LAKEV | LAKEVILLE 1102 | SONOMA | 0.62549 | 57.7371 | 40.72% | 0 | 0 | 12.01% | 0% | 0 | 0.010222 | 1 | 0.010222 | 0.016342
FORT ORD 210637286 | FORT | FORT ORD 2106 | CENTRAL COAST | 1.5847 | 10 | 0% | 0 | 4 | 43% | 0% | 0 | 0.010213 | 1 | 0.010213 | 0.0064444
SAN LUIS OBISPO 1104645976 | SAN L | SAN LUIS OBISPO 1104 | LOS PADRES | 2.1274 | 42.6681 | 27.62% | 0 | 0 | 32.32% | 0% | 0 | 0.010145 | 1 | 0.010145 | 0.0047687
HARRIS 11082062 | HARRI | HARRIS 1108 | HUMBOLDT | 2.3961 | 14.4145 | 20.24% | 1 | 5 | 45.88% | 0% | 0 | 0.010144 | 1 | 0.010144 | 0.0042335
SONOMA 11054456 | SONOM | SONOMA 1105 | SONOMA | 1.6486 | 23.1811 | 52.93% | 0 | 1 | 22.31% | 0% | 0 | 0.010106 | 1 | 0.010106 | 0.0061301
BRENTWOOD 210596324 | BRENT | BRENTWOOD 2105 | DIABLO | 0.37122 | 10 | 0% | 0 | 0 | 76.98% | 0% | 0 | 0.010106 | 1 | 0.010106 | 0.027225
LINCOLN 110195756 | LINCO | LINCOLN 1101 | SIERRA | 3.5302 | 10.7023 | 65.54% | 2 | 0 | 19.54% | 0% | 0 | 0.010072 | 1 | 0.010072 | 0.002853
NARROWS 21022718 | NARRO | NARROWS 2102 | SIERRA | 0.45209 | 10 | 82.65% | 0 | 1 | 6.234% | 0% | 0 | 0.010047 | 1 | 0.010047 | 0.022224
CURTIS 170190120 | CURTI | CURTIS 1701 | YOSEMITE | 2.5983 | 10 | 28.78% | 0 | 1 | 50.57% | 0% | 0 | 0.010044 | 1 | 0.010044 | 0.0038657
MESA 1103M92 | MESA | MESA 1103 | LOS PADRES | 1.0274 | 49.2008 | 44.21% | 0 | 0 | 12.96% | 0% | 0 | 0.010021 | 1 | 0.010021 | 0.009753
TIDEWATER 210665866 | TIDEW | TIDEWATER 2106 | DIABLO | 4.2405 | 36.2821 | 12.3% | 0 | 0 | 47.54% | 0% | 0 | 0.0099699 | 1 | 0.0099699 | 0.0023511
UKIAH 111472990 | UKIAH | UKIAH 1114 | HUMBOLDT | 0.7336 | 10 | 33.42% | 1 | 5 | 22.74% | 0% | 0 | 0.0099473 | 1 | 0.0099473 | 0.013559
FITCH MOUNTAIN 1113154 | FITCH | FITCH MOUNTAIN 1113 | SONOMA | 2.1793 | 18.0666 | 70.63% | 0 | 0 | 11.51% | 0% | 0 | 0.0099274 | 1 | 0.0099274 | 0.0045554
HARTLEY 1102CB | HARTL | HARTLEY 1102 | HUMBOLDT | 2.7707 | 10 | 40.84% | 0 | 2 | 23.94% | 0% | 0 | 0.0099181 | 1 | 0.0099181 | 0.0035797
EDES 1112CB | EDES | EDES 1112 | EAST BAY | 0.77646 | 10 | 11.31% | 0 | 0 | 52.35% | 0% | 0 | 0.0099087 | 1 | 0.0099087 | 0.012761
SONOMA 1104914376 | SONOM | SONOMA 1104 | SONOMA | 0.42319 | 32.6662 | 64.75% | 0 | 0 | 6.07% | 0% | 0 | 0.0098958 | 1 | 0.0098958 | 0.023384
MENLO 11029110 | MENLO | MENLO 1102 | PENINSULA | 0.16148 | 10 | 87.04% | 1 | 0 | 1.751% | 0% | 0 | 0.0098849 | 1 | 0.0098849 | 0.061214
RACETRACK 1703332820 | RACET | RACETRACK 1703 | YOSEMITE | 1.3085 | 10 | 3.686% | 0 | 0 | 71.54% | 0% | 0 | 0.0098677 | 1 | 0.0098677 | 0.0075413
EEL RIVER 110249130 | EEL R | EEL RIVER 1102 | HUMBOLDT | 1.458 | 43.0989 | 47.28% | 0 | 1 | 10.5% | 0% | 0 | 0.0098241 | 1 | 0.0098241 | 0.0067382
SAN ARDO 110193072 | SAN A | SAN ARDO 1101 | CENTRAL COAST | 0.72134 | 10 | 63.38% | 0 | 0 | 8.566% | 0% | 0 | 0.0098197 | 1 | 0.0098197 | 0.013613
HARTLEY 1101CB | HARTL | HARTLEY 1101 | HUMBOLDT | 1.2777 | 10 | 19.8% | 0 | 1 | 42.25% | 0% | 0 | 0.0098099 | 1 | 0.0098099 | 0.0076779
BUELLTON 11016621 | BUELL | BUELLTON 1101 | LOS PADRES | 1.6446 | 36.7928 | 44.49% | 0 | 1 | 16.9% | 0% | 0 | 0.0098043 | 1 | 0.0098043 | 0.0059615
SANTA YNEZ 1104CB | SANTA | SANTA YNEZ 1104 | LOS PADRES | 0.81728 | 10 | 74.93% | 2 | 0 | 9.437% | 0% | 0 | 0.00979 | 1 | 0.00979 | 0.011979
PETALUMA C 1108630 | PETAL | PETALUMA C 1108 | SONOMA | 1.2522 | 54.3048 | 11.61% | 0 | 2 | 29.56% | 0% | 0 | 0.0097687 | 1 | 0.0097687 | 0.007801
MIRABEL 1102206 | MIRAB | MIRABEL 1102 | SONOMA | 1.6804 | 10 | 37.83% | 0 | 1 | 13.09% | 0% | 0 | 0.0097141 | 1 | 0.0097141 | 0.0057809
OAKLAND X 1101CR224 | OAKLA | OAKLAND X 1101 | EAST BAY | 0.53647 | 10 | 23.35% | 2 | 2 | 46.33% | 0% | 0 | 0.0096559 | 1 | 0.0096559 | 0.017999
GRASS VALLEY 110358498 | GRASS | GRASS VALLEY 1103 | SIERRA | 0.54343 | 10 | 37.4% | 0 | 2 | 23.91% | 0% | 0 | 0.0096407 | 1 | 0.0096407 | 0.01774
ATASCADERO 1103A46 | ATASC | ATASCADERO 1103 | LOS PADRES | 0.63104 | 65.2454 | 33.62% | 0 | 0 | 6.794% | 0% | 0 | 0.0096376 | 1 | 0.0096376 | 0.015273
STELLING 110913228 | STELL | STELLING 1109 | DE ANZA | 0.52786 | 10 | 79.39% | 0 | 0 | 6.214% | 0% | 0 | 0.0095798 | 1 | 0.0095798 | 0.018149
FORT ORD 210736596 | FORT | FORT ORD 2107 | CENTRAL COAST | 2.9621 | 10 | 1.434% | 0 | 3 | 23.77% | 0% | 0 | 0.0095449 | 1 | 0.0095449 | 0.0032224
REDBUD 1102432 | REDBU | REDBUD 1102 | HUMBOLDT | 1.3051 | 10 | 69.46% | 0 | 1 | 11.62% | 0% | 0 | 0.0095157 | 1 | 0.0095157 | 0.0072913
OAKLAND K 1101CB | OAKLA | OAKLAND K 1101 | EAST BAY | 0.35314 | 10 | 0% | 1 | 1 | 14.81% | 24.18% | 0 | 0.0095124 | 1 | 0.0095124 | 0.026937
STAFFORD 110242542 | STAFF | STAFFORD 1102 | NORTH BAY | 0.92749 | 10 | 53.57% | 0 | 0 | 26.56% | 0% | 0 | 0.0094932 | 1 | 0.0094932 | 0.010235
EL CERRITO G 1110CB | EL CE | EL CERRITO G 1110 | EAST BAY | 1.4466 | 10 | 13.89% | 0 | 3 | 52.88% | 0% | 0 | 0.0094866 | 1 | 0.0094866 | 0.0065578
BERESFORD 04039154 | BERES | BERESFORD 0403 | PENINSULA | 3.1988 | 10 | 17.34% | 4 | 1 | 48.83% | 0% | 0 | 0.0094751 | 1 | 0.0094751 | 0.0029621
LOS COCHES 1101CB | LOS C | LOS COCHES 1101 | CENTRAL COAST | 2.6219 | 75.2391 | 12.86% | 0 | 1 | 13.12% | 0% | 0 | 0.009461 | 1 | 0.009461 | 0.0036085
SAN LUIS OBISPO 1107CB | SAN L | SAN LUIS OBISPO 1107 | LOS PADRES | 0.84728 | 10 | 25.92% | 0 | 0 | 48.86% | 0% | 0 | 0.0094493 | 1 | 0.0094493 | 0.011153
SONOMA 1107126 | SONOM | SONOMA 1107 | SONOMA | 2.2583 | 59.5559 | 29.29% | 0 | 1 | 10.13% | 0% | 0 | 0.009446 | 1 | 0.009446 | 0.0041828
FLINT 110140666 | FLINT | FLINT 1101 | SIERRA | 0.79305 | 10 | 48.92% | 0 | 1 | 27.77% | 0% | 0 | 0.009443 | 1 | 0.009443 | 0.011907
JARVIS 1108MR368 | JARVI | JARVIS 1108 | MISSION | 0.80128 | 10 | 39.98% | 0 | 0 | 23.87% | 0% | 0 | 0.0094416 | 1 | 0.0094416 | 0.011783
MC ARTHUR 11011488 | MC AR | MC ARTHUR 1101 | NORTH VALLEY | 2.4985 | 10 | 70.57% | 0 | 2 | 7.462% | 0% | 0 | 0.0094078 | 1 | 0.0094078 | 0.0037653
HARTLEY 110186876 | HARTL | HARTLEY 1101 | HUMBOLDT | 2.3866 | 10 | 49.85% | 0 | 0 | 28.66% | 0% | 0 | 0.0094023 | 1 | 0.0094023 | 0.0039396
POINT MORETTI 11015074 | POINT | POINT MORETTI 1101 | CENTRAL COAST | 1.726 | 19.9026 | 1.553% | 2 | 1 | 56.7% | 0% | 0 | 0.009381 | 1 | 0.009381 | 0.005435
ROSSMOOR 110676468 | ROSSM | ROSSMOOR 1106 | DIABLO | 1.5034 | 10 | 14.83% | 1 | 2 | 51.08% | 0% | 0 | 0.0093177 | 1 | 0.0093177 | 0.0061976
ROSSMOOR 110192164 | ROSSM | ROSSMOOR 1101 | DIABLO | 0.25455 | 10 | 51.39% | 0 | 0 | 26.2% | 0% | 0 | 0.0092923 | 1 | 0.0092923 | 0.036505
ATASCADERO 1101CB | ATASC | ATASCADERO 1101 | LOS PADRES | 0.44126 | 10 | 57.34% | 0 | 0 | 21.26% | 0% | 0 | 0.0092885 | 1 | 0.0092885 | 0.02105
TEMPLETON 2113A32 | TEMPL | TEMPLETON 2113 | LOS PADRES | 0.77097 | 10 | 66.93% | 0 | 0 | 13.18% | 0% | 0 | 0.0092713 | 1 | 0.0092713 | 0.012026
SOBRANTE 110142914 | SOBRA | SOBRANTE 1101 | DIABLO | 0.83179 | 10 | 55.86% | 0 | 1 | 20.13% | 0% | 0 | 0.0092648 | 1 | 0.0092648 | 0.011138
SWIFT 2109XR300 | SWIFT | SWIFT 2109 | SAN JOSE | 0.30955 | 10 | 37.52% | 0 | 0 | 37.32% | 0% | 0 | 0.0092647 | 1 | 0.0092647 | 0.02993
OAKLAND J 1102CR254 | OAKLA | OAKLAND J 1102 | EAST BAY | 1.0198 | 10 | 0% | 1 | 0 | 66.21% | 0% | 0 | 0.0092017 | 1 | 0.0092017 | 0.0090234
FRANKLIN 1104P136 | FRANK | FRANKLIN 1104 | EAST BAY | 3.8457 | 10 | 0% | 0 | 1 | 65.24% | 0% | 0 | 0.009184 | 1 | 0.009184 | 0.0023881
DEL MONTE 210332886 | DEL M | DEL MONTE 2103 | CENTRAL COAST | 1.2598 | 10 | 0% | 5 | 1 | 31.74% | 0% | 0 | 0.0091616 | 1 | 0.0091616 | 0.0072725
OLEMA 1101320 | OLEMA | OLEMA 1101 | NORTH BAY | 0.033859 | 54.8898 | 25.18% | 0 | 1 | 0.2531% | 0% | 0 | 0.0091583 | 1 | 0.0091583 | 0.27048
OAKLAND J 1106CR330 | OAKLA | OAKLAND J 1106 | EAST BAY | 0.49535 | 10 | 40.09% | 0 | 0 | 20.57% | 0% | 0 | 0.0091449 | 1 | 0.0091449 | 0.018461
SNEATH LANE 1106CB | SNEAT | SNEATH LANE 1106 | PENINSULA | 1.101 | 10 | 47.15% | 3 | 3 | 17.83% | 0% | 0 | 0.0091441 | 1 | 0.0091441 | 0.0083051
FROGTOWN 1702CB | FROGT | FROGTOWN 1702 | STOCKTON | 2.2987 | 10 | 21.1% | 0 | 2 | 44.33% | 0% | 0 | 0.0090529 | 1 | 0.0090529 | 0.0039383
OAKLAND J 1106CR164 | OAKLA | OAKLAND J 1106 | EAST BAY | 1.4865 | 10 | 46.08% | 2 | 1 | 22.66% | 0% | 0 | 0.0090035 | 1 | 0.0090035 | 0.0060568
VALLEY VIEW 1105CB | VALLE | VALLEY VIEW 1105 | EAST BAY | 0.87089 | 10 | 56.45% | 0 | 0 | 18.73% | 0% | 0 | 0.0089925 | 1 | 0.0089925 | 0.010326
ELK 11011300 | ELK 1 | ELK 1101 | HUMBOLDT | 3.0348 | 10 | 21.85% | 10 | 1 | 31.85% | 0% | 0 | 0.0089861 | 1 | 0.0089861 | 0.002961
VALLEY VIEW 1106P128 | VALLE | VALLEY VIEW 1106 | EAST BAY | 0.72514 | 10 | 44.15% | 0 | 0 | 28.68% | 0% | 0 | 0.0089763 | 1 | 0.0089763 | 0.012379
HICKS 1116CB | HICKS | HICKS 1116 | SAN JOSE | 1.3112 | 10 | 43.95% | 1 | 3 | 7.743% | 0% | 0 | 0.0089608 | 1 | 0.0089608 | 0.0068341
GABILAN 11013034 | GABIL | GABILAN 1101 | CENTRAL COAST | 0.41092 | 10 | 76.33% | 0 | 0 | 1.978% | 0% | 0 | 0.0089581 | 1 | 0.0089581 | 0.0218
HOLLISTER 210491424 | HOLLI | HOLLISTER 2104 | CENTRAL COAST | 0.19482 | 10 | 75.59% | 0 | 0 | 2.224% | 0% | 0 | 0.0089256 | 1 | 0.0089256 | 0.045815
WYANDOTTE 110942650 | WYAND | WYANDOTTE 1109 | NORTH VALLEY | 0.71686 | 10 | 44.77% | 0 | 0 | 27.21% | 0% | 0 | 0.0088907 | 1 | 0.0088907 | 0.012402
FLORENCE 0401CB | FLORE | FLORENCE 0401 | EAST BAY | 1.7144 | 10 | 2.295% | 5 | 1 | 39.92% | 0% | 0 | 0.00887 | 1 | 0.00887 | 0.0051738
VALLEY VIEW 1105P126 | VALLE | VALLEY VIEW 1105 | EAST BAY | 0.94179 | 10 | 5.099% | 0 | 0 | 45.94% | 0% | 0 | 0.008838 | 1 | 0.008838 | 0.0093843
VINEYARD 2107CB | VINEY | VINEYARD 2107 | MISSION | 1.6942 | 13.0214 | 48.11% | 0 | 2 | 16.67% | 0% | 0 | 0.0087566 | 1 | 0.0087566 | 0.0051684
SAN CARLOS 11048846 | SAN C | SAN CARLOS 1104 | PENINSULA | 1.1188 | 10 | 42.43% | 0 | 1 | 25.48% | 0% | 0 | 0.0087545 | 1 | 0.0087545 | 0.007825
NOVATO 11041282 | NOVAT | NOVATO 1104 | NORTH BAY | 1.3064 | 10 | 9.821% | 0 | 6 | 28.52% | 0% | 0 | 0.008753 | 1 | 0.008753 | 0.0067003
ELK 1101900 | ELK 1 | ELK 1101 | HUMBOLDT | 6.0335 | 22.7757 | 2.097% | 2 | 3 | 29.53% | 0% | 0 | 0.0087294 | 1 | 0.0087294 | 0.0014468
WYANDOTTE 110213914 | WYAND | WYANDOTTE 1102 | NORTH VALLEY | 0.60739 | 10 | 33.65% | 0 | 0 | 34.43% | 0% | 0 | 0.0087222 | 1 | 0.0087222 | 0.01436
OAKLAND J 1102CR252 | OAKLA | OAKLAND J 1102 | EAST BAY | 1.1914 | 10 | 48.94% | 0 | 1 | 19.56% | 0% | 0 | 0.0087055 | 1 | 0.0087055 | 0.007307
BELMONT 1103415994 | BELMO | BELMONT 1103 | PENINSULA | 1.0684 | 10 | 38.18% | 0 | 2 | 26.01% | 0% | 0 | 0.0086782 | 1 | 0.0086782 | 0.0081228
KERN OIL 110646960 | KERN | KERN OIL 1106 | KERN | 1.1498 | 10 | 1.744% | 0 | 0 | 59.65% | 0% | 0 | 0.0086311 | 1 | 0.0086311 | 0.0075063
OAKLAND X 1105CB | OAKLA | OAKLAND X 1105 | EAST BAY | 3.475 | 10 | 21.39% | 0 | 3 | 23.79% | 0% | 0 | 0.0086247 | 1 | 0.0086247 | 0.0024819
HALF MOON BAY 11036014 | HALF | HALF MOON BAY 1103 | PENINSULA | 5.273 | 14.6725 | 1.871% | 0 | 0 | 42.92% | 0% | 0 | 0.0086216 | 1 | 0.0086216 | 0.0016351
GREEN VALLEY 210112130 | GREEN | GREEN VALLEY 2101 | CENTRAL COAST | 1.2937 | 17.054 | 59.16% | 0 | 0 | 7.411% | 0% | 0 | 0.0086186 | 1 | 0.0086186 | 0.0066621
BAYWOOD 1101CB | BAYWO | BAYWOOD 1101 | LOS PADRES | 1.4233 | 43.3041 | 38.16% | 0 | 0 | 4.9% | 0% | 0 | 0.008459 | 1 | 0.008459 | 0.0059433
FAIRVIEW 2207CB | FAIRV | FAIRVIEW 2207 | DIABLO | 0.060291 | 10 | 69.19% | 0 | 0 | 1.178% | 0% | 0 | 0.0083828 | 1 | 0.0083828 | 0.13904
FLINT 1101CB | FLINT | FLINT 1101 | SIERRA | 0.81732 | 10 | 11.07% | 0 | 2 | 31.46% | 0% | 0 | 0.008378 | 1 | 0.008378 | 0.01025
COTATI 1105616 | COTAT | COTATI 1105 | SONOMA | 0.88156 | 51.5142 | 16.32% | 0 | 0 | 2.877% | 0% | 0 | 0.0083693 | 1 | 0.0083693 | 0.0094937
ROB ROY 210410930 | ROB R | ROB ROY 2104 | CENTRAL COAST | 1.4484 | 10 | 54.81% | 0 | 0 | 12.82% | 0% | 0 | 0.0083664 | 1 | 0.0083664 | 0.0057764
FAIRVIEW 2207M501R | FAIRV | FAIRVIEW 2207 | DIABLO | 1.376 | 10 | 11.91% | 1 | 2 | 29.22% | 0% | 0 | 0.0083598 | 1 | 0.0083598 | 0.0060754
BERKELEY F 0402CB | BERKE | BERKELEY F 0402 | EAST BAY | 0.47631 | 10 | 26.87% | 0 | 0 | 22.4% | 0% | 0 | 0.0083588 | 1 | 0.0083588 | 0.017549
UKIAH 1114CB | UKIAH | UKIAH 1114 | HUMBOLDT | 1.2249 | 10 | 45.97% | 1 | 2 | 14.08% | 0% | 0 | 0.0083238 | 1 | 0.0083238 | 0.0067953
WOOD 0401CB | WOOD | WOOD 0401 | EAST BAY | 0.4018 | 10 | 54.38% | 0 | 0 | 12.06% | 0% | 0 | 0.0082741 | 1 | 0.0082741 | 0.020593
FAIRMOUNT 0401CB | FAIRM | FAIRMOUNT 0401 | EAST BAY | 1.4849 | 10 | 0% | 0 | 2 | 25.81% | 0% | 0 | 0.0082593 | 1 | 0.0082593 | 0.0055621
TEMPLETON 2113A30 | TEMPL | TEMPLETON 2113 | LOS PADRES | 0.53596 | 10 | 10.42% | 0 | 0 | 34.36% | 0% | 0 | 0.0082271 | 1 | 0.0082271 | 0.01535
KONOCTI 110264464 | KONOC | KONOCTI 1102 | HUMBOLDT | 0.53615 | 10 | 9.05% | 1 | 0 | 19.93% | 0% | 0 | 0.0081536 | 1 | 0.0081536 | 0.015208
RIO DEL MAR 0402CB | RIO D | RIO DEL MAR 0402 | CENTRAL COAST | 1.6949 | 10 | 6.344% | 2 | 0 | 47.04% | 0% | 0 | 0.0081166 | 1 | 0.0081166 | 0.004789
TASSAJARA 2109CB | TASSA | TASSAJARA 2109 | DIABLO | 0.80761 | 10 | 0% | 0 | 4 | 46.43% | 0% | 0 | 0.0081085 | 1 | 0.0081085 | 0.01004
EEL RIVER 11033820 | EEL R | EEL RIVER 1103 | HUMBOLDT | 2.3658 | 10 | 0% | 0 | 1 | 11.93% | 0% | 0 | 0.0080448 | 1 | 0.0080448 | 0.0034005
VIEJO 220146068 | VIEJO | VIEJO 2201 | CENTRAL COAST | 0.073762 | 10 | 0% | 0 | 0 | 53.15% | 0% | 0 | 0.0079762 | 1 | 0.0079762 | 0.10814
COAST RD 04015134 | COAST | COAST RD 0401 | CENTRAL COAST | 1.6146 | 10 | 0% | 0 | 0 | 53.13% | 0% | 0 | 0.007975 | 1 | 0.007975 | 0.0049392
IGNACIO 11041290 | IGNAC | IGNACIO 1104 | NORTH BAY | 1.6542 | 10 | 24.98% | 1 | 1 | 15.64% | 0% | 0 | 0.0079604 | 1 | 0.0079604 | 0.0048122
BERKELEY F 1105CB | BERKE | BERKELEY F 1105 | EAST BAY | 1.3653 | 10 | 33.54% | 1 | 1 | 21.32% | 0% | 0 | 0.0079134 | 1 | 0.0079134 | 0.0057963
FORT BRAGG A 1102CB | FORT | FORT BRAGG A 1102 | HUMBOLDT | 1.663 | 13.8095 | 19.07% | 2 | 1 | 29% | 0% | 0 | 0.0078888 | 1 | 0.0078888 | 0.0047438
RESERVATION ROAD 110222136 | RESER | RESERVATION ROAD 1102 | CENTRAL COAST | 1.1023 | 40.7641 | 13.41% | 0 | 0 | 19.9% | 0% | 0 | 0.0078815 | 1 | 0.0078815 | 0.0071498
ALHAMBRA 110595016 | ALHAM | ALHAMBRA 1105 | DIABLO | 0.37201 | 51.8878 | 0% | 0 | 0 | 9.208% | 0% | 0 | 0.0078178 | 1 | 0.0078178 | 0.021015
MORRO BAY 1101W20 | MORRO | MORRO BAY 1101 | LOS PADRES | 1.8981 | 10 | 0% | 0 | 1 | 48.29% | 0% | 0 | 0.0077601 | 1 | 0.0077601 | 0.0040883
PETALUMA C 1109CB | PETAL | PETALUMA C 1109 | SONOMA | 0.77473 | 10 | 39.24% | 0 | 1 | 15.77% | 0% | 0 | 0.007744 | 1 | 0.007744 | 0.0099957
LOS GATOS 1101CB | LOS G | LOS GATOS 1101 | DE ANZA | 0.83125 | 10 | 32.44% | 0 | 1 | 21.19% | 0% | 0 | 0.0077301 | 1 | 0.0077301 | 0.0092994
OAKLAND J 1118CR198 | OAKLA | OAKLAND J 1118 | EAST BAY | 0.38627 | 10 | 34.69% | 0 | 0 | 7.348% | 0% | 0 | 0.0076722 | 1 | 0.0076722 | 0.019862
ALTO 1123CB | ALTO | ALTO 1123 | NORTH BAY | 2.3955 | 10 | 3.352% | 0 | 0 | 39.61% | 4.121% | 0 | 0.0076595 | 1 | 0.0076595 | 0.0031975
LAS GALLINAS A 11041220 | LAS G | LAS GALLINAS A 1104 | NORTH BAY | 1.0215 | 10 | 17.87% | 0 | 0 | 20.99% | 0% | 0 | 0.0076561 | 1 | 0.0076561 | 0.0074948
SAN RAFAEL 110969860 | SAN R | SAN RAFAEL 1109 | NORTH BAY | 0.67004 | 10 | 27.57% | 0 | 0 | 26.27% | 0% | 0 | 0.0076522 | 1 | 0.0076522 | 0.01142
AUBURN 1102CB | AUBUR | AUBURN 1102 | SIERRA | 0.41789 | 10 | 46.75% | 0 | 2 | 6.005% | 0% | 0 | 0.0076302 | 1 | 0.0076302 | 0.018259
BOLINAS 11011064 | BOLIN | BOLINAS 1101 | NORTH BAY | 0.79432 | 10 | 14.47% | 2 | 1 | 17.88% | 0% | 0 | 0.0075676 | 1 | 0.0075676 | 0.0095272
MC KEE 1103XR028 | MC KE | MC KEE 1103 | SAN JOSE | 2.8083 | 15.9921 | 15.4% | 0 | 2 | 26.81% | 0% | 0 | 0.007561 | 1 | 0.007561 | 0.0026924
VIEJO 22029089 | VIEJO | VIEJO 2202 | CENTRAL COAST | 0.44699 | 10 | 0% | 1 | 3 | 26.75% | 0% | 0 | 0.0075545 | 1 | 0.0075545 | 0.016901
DEL MAR 2109CB | DEL M | DEL MAR 2109 | SIERRA | 1.7939 | 12.1972 | 19.79% | 0 | 1 | 27.43% | 0% | 0 | 0.0075272 | 1 | 0.0075272 | 0.0041959
SNEATH LANE 110748338 | SNEAT | SNEATH LANE 1107 | PENINSULA | 0.48719 | 10 | 2.1% | 0 | 0 | 45.41% | 0% | 0 | 0.0075134 | 1 | 0.0075134 | 0.015422
HOLLISTER 2104855412 | HOLLI | HOLLISTER 2104 | CENTRAL COAST | 0.30314 | 60 | 0% | 1 | 0 | 11.12% | 0% | 0 | 0.007471 | 1 | 0.007471 | 0.024645
VIEJO 22049540 | VIEJO | VIEJO 2204 | CENTRAL COAST | 0.84933 | 10 | 0% | 3 | 2 | 38.01% | 0% | 0 | 0.0074407 | 1 | 0.0074407 | 0.0087606
ALHAMBRA 1105CB | ALHAM | ALHAMBRA 1105 | DIABLO | 0.38371 | 10 | 15.25% | 0 | 0 | 20.22% | 0% | 0 | 0.0074366 | 1 | 0.0074366 | 0.019381
SNEATH LANE 1107CB | SNEAT | SNEATH LANE 1107 | PENINSULA | 0.3748 | 10 | 41.65% | 0 | 1 | 9.682% | 0% | 0 | 0.0074343 | 1 | 0.0074343 | 0.019835
SAN RAFAEL 1106837 | SAN R | SAN RAFAEL 1106 | NORTH BAY | 0.43527 | 10 | 0% | 0 | 2 | 28.12% | 0% | 0 | 0.0074019 | 1 | 0.0074019 | 0.017005
CLEAR LAKE 1102CB | CLEAR | CLEAR LAKE 1102 | HUMBOLDT | 0.13095 | 10 | 54.49% | 0 | 0 | 0.5805% | 0% | 0 | 0.0073882 | 1 | 0.0073882 | 0.056421
BIG RIVER 110155402 | BIG R | BIG RIVER 1101 | HUMBOLDT | 2.6094 | 10 | 0.156% | 5 | 5 | 28.18% | 0% | 0 | 0.0073839 | 1 | 0.0073839 | 0.0028297
IONE 1101CB | IONE | IONE 1101 | STOCKTON | 1.9633 | 49.7739 | 2.974% | 1 | 0 | 13.95% | 0% | 0 | 0.007346 | 1 | 0.007346 | 0.0037417
SNEATH LANE 11015311 | SNEAT | SNEATH LANE 1101 | PENINSULA | 0.49818 | 10 | 0% | 0 | 0 | 44.61% | 0% | 0 | 0.0073269 | 1 | 0.0073269 | 0.014707
IGNACIO 1104316 | IGNAC | IGNACIO 1104 | NORTH BAY | 0.5655 | 10 | 40.98% | 0 | 2 | 6.524% | 0% | 0 | 0.0073158 | 1 | 0.0073158 | 0.012937
ALHAMBRA 110213333 | ALHAM | ALHAMBRA 1102 | DIABLO | 0.074793 | 10 | 23.29% | 0 | 0 | 25.18% | 0% | 0 | 0.007309 | 1 | 0.007309 | 0.097722
OCEANO 1105V16 | OCEAN | OCEANO 1105 | LOS PADRES | 1.6064 | 10 | 0% | 0 | 0 | 44.18% | 0% | 0 | 0.0072956 | 1 | 0.0072956 | 0.0045415
SAN LUIS OBISPO 1104CB | SAN L | SAN LUIS OBISPO 1104 | LOS PADRES | 0.36018 | 63.441 | 2.835% | 0 | 0 | 5.218% | 0% | 0 | 0.007285 | 1 | 0.007285 | 0.020226
PACIFIC GROVE 04222614 | PACIF | PACIFIC GROVE 0422 | CENTRAL COAST | 0.61996 | 10 | 0% | 1 | 0 | 28.91% | 0% | 0 | 0.007251 | 1 | 0.007251 | 0.011696
CASTRO VALLEY 1104MR201 | CASTR | CASTRO VALLEY 1104 | MISSION | 1.8766 | 10 | 10.28% | 0 | 1 | 19.54% | 0% | 0 | 0.007241 | 1 | 0.007241 | 0.0038587
FRANKLIN 1104CB | FRANK | FRANKLIN 1104 | EAST BAY | 0.64777 | 10 | 0% | 0 | 2 | 12.31% | 0% | 0 | 0.0072216 | 1 | 0.0072216 | 0.011148
MC ARTHUR 110137344 | MC AR | MC ARTHUR 1101 | NORTH VALLEY | 0.26567 | 10 | 48.66% | 0 | 0 | 2.972% | 0% | 0 | 0.0072135 | 1 | 0.0072135 | 0.027152
HICKS 1116LB16 | HICKS | HICKS 1116 | SAN JOSE | 1.4512 | 10 | 12.53% | 1 | 1 | 15.83% | 0% | 0 | 0.0072028 | 1 | 0.0072028 | 0.0049633
CAROLANDS 04049026 | CAROL | CAROLANDS 0404 | PENINSULA | 0.27754 | 10 | 28.62% | 0 | 0 | 5.507% | 0% | 0 | 0.0071679 | 1 | 0.0071679 | 0.025826
WALDO 0401CB | WALDO | WALDO 0401 | EAST BAY | 1.6612 | 10 | 12.79% | 0 | 1 | 29.42% | 0% | 0 | 0.0071421 | 1 | 0.0071421 | 0.0042995
VIEJO 220285904 | VIEJO | VIEJO 2202 | CENTRAL COAST | 0.44182 | 10 | 5.103% | 1 | 0 | 22.34% | 0% | 0 | 0.007082 | 1 | 0.007082 | 0.016029
TAR FLAT 0402CB | TAR F | TAR FLAT 0402 | YOSEMITE | 0.52249 | 10 | 7.104% | 0 | 0 | 35.32% | 0% | 0 | 0.0070807 | 1 | 0.0070807 | 0.013552
LUCERNE 11034624 | LUCER | LUCERNE 1103 | HUMBOLDT | 0.73972 | 10 | 26.07% | 0 | 0 | 19.5% | 0% | 0 | 0.0070666 | 1 | 0.0070666 | 0.009553
PURISIMA 110149394 | PURIS | PURISIMA 1101 | LOS PADRES | 0.38618 | 10 | 25.81% | 1 | 0 | 4.395% | 0% | 0 | 0.0070193 | 1 | 0.0070193 | 0.018176
PUEBLO 11053022 | PUEBL | PUEBLO 1105 | NORTH BAY | 0.42768 | 10 | 42.51% | 0 | 0 | 4.687% | 0% | 0 | 0.0069771 | 1 | 0.0069771 | 0.016314
SAN CARLOS 110436864 | SAN C | SAN CARLOS 1104 | PENINSULA | 0.3154 | 10 | 0% | 0 | 1 | 37.17% | 0% | 0 | 0.0069476 | 1 | 0.0069476 | 0.022028
LAKEWOOD 210769586 | LAKEW | LAKEWOOD 2107 | DIABLO | 0.5706 | 16.4781 | 12.07% | 0 | 2 | 6.994% | 0% | 0 | 0.0069201 | 1 | 0.0069201 | 0.012128
MORGAN HILL 2105XR578 | MORGA | MORGAN HILL 2105 | SAN JOSE | 0.218 | 10 | 8.67% | 0 | 0 | 31.62% | 0% | 0 | 0.0069127 | 1 | 0.0069127 | 0.031709
FORT BRAGG A 11021226 | FORT | FORT BRAGG A 1102 | HUMBOLDT | 1.1335 | 10 | 21.46% | 0 | 3 | 14.45% | 0% | 0 | 0.0068882 | 1 | 0.0068882 | 0.0060768
POINT ARENA 1101476 | POINT | POINT ARENA 1101 | HUMBOLDT | 2.7213 | 21.4527 | 0% | 6 | 2 | 18.23% | 0% | 0 | 0.0068718 | 1 | 0.0068718 | 0.0025252
OCEANO 110376678 | OCEAN | OCEANO 1103 | LOS PADRES | 0.055262 | 10 | 22.91% | 0 | 2 | 14.84% | 0% | 0 | 0.0068538 | 1 | 0.0068538 | 0.12402
LAS GALLINAS A 1104304 | LAS G | LAS GALLINAS A 1104 | NORTH BAY | 0.14237 | 10 | 35.52% | 0 | 1 | 5.697% | 0% | 0 | 0.0067954 | 1 | 0.0067954 | 0.047729
BERESFORD 0403CB | BERES | BERESFORD 0403 | PENINSULA | 0.94707 | 10 | 19.89% | 1 | 1 | 17.08% | 0% | 0 | 0.0067843 | 1 | 0.0067843 | 0.0071635
ESTUDILLO 0401CB | ESTUD | ESTUDILLO 0401 | MISSION | 0.69789 | 10 | 26.72% | 0 | 0 | 14.78% | 0% | 0 | 0.0067781 | 1 | 0.0067781 | 0.0097123
SAN RAFAEL 11042235 | SAN R | SAN RAFAEL 1104 | NORTH BAY | 0.29854 | 10 | 0% | 0 | 1 | 34.56% | 0% | 0 | 0.0067695 | 1 | 0.0067695 | 0.022676
BRUNSWICK 111094368 | BRUNS | BRUNSWICK 1110 | SIERRA | 0.16855 | 10 | 0% | 0 | 0 | 35.28% | 0% | 0 | 0.0066771 | 1 | 0.0066771 | 0.039614
WYANDOTTE 1107CB | WYAND | WYANDOTTE 1107 | NORTH VALLEY | 1.0691 | 10 | 31.7% | 0 | 1 | 7.068% | 0% | 0 | 0.0066762 | 1 | 0.0066762 | 0.0062446
OAKLAND J 1105CR132 | OAKLA | OAKLAND J 1105 | EAST BAY | 0.28914 | 10 | 34.84% | 0 | 0 | 6.37% | 0% | 0 | 0.0066625 | 1 | 0.0066625 | 0.023043
BROWNS VALLEY 110136622 | BROWN | BROWNS VALLEY 1101 | SIERRA | 2.3766 | 10 | 8.927% | 0 | 1 | 25.35% | 0% | 0 | 0.0066455 | 1 | 0.0066455 | 0.0027962
MORRO BAY 1101CB | MORRO | MORRO BAY 1101 | LOS PADRES | 0.64776 | 10 | 6.384% | 0 | 0 | 29.39% | 0% | 0 | 0.0066355 | 1 | 0.0066355 | 0.010244
VIEJO 22049110 | VIEJO | VIEJO 2204 | CENTRAL COAST | 0.89252 | 10 | 16.91% | 0 | 0 | 20.66% | 0% | 0 | 0.0066316 | 1 | 0.0066316 | 0.0074302
MORAGA 110381146 | MORAG | MORAGA 1103 | DIABLO | 0.81099 | 10 | 24.05% | 0 | 0 | 14.46% | 0% | 0 | 0.00661 | 1 | 0.00661 | 0.0081505
PACIFICA 1104CB | PACIF | PACIFICA 1104 | PENINSULA | 0.50255 | 42.4378 | 0% | 0 | 0 | 11.92% | 0% | 0 | 0.006597 | 1 | 0.006597 | 0.013127
PLACER 110451732 | PLACE | PLACER 1104 | SIERRA | 1.3434 | 10 | 21.69% | 0 | 0 | 16.14% | 0% | 0 | 0.0065925 | 1 | 0.0065925 | 0.0049073
OCEANO 1106CB | OCEAN | OCEANO 1106 | LOS PADRES | 0.86306 | 10 | 5.571% | 1 | 4 | 19.68% | 0% | 0 | 0.0065904 | 1 | 0.0065904 | 0.007636
PENRYN 11051378 | PENRY | PENRYN 1105 | SIERRA | 0.3076 | 10 | 15.69% | 2 | 1 | 16.27% | 0% | 0 | 0.0065875 | 1 | 0.0065875 | 0.021416
SOLEDAD 111435306 | SOLED | SOLEDAD 1114 | CENTRAL COAST | 0.90872 | 10 | 9.031% | 0 | 0 | 12.56% | 0% | 0 | 0.0065483 | 1 | 0.0065483 | 0.0072062
SAN MIGUEL 1106N34 | SAN M | SAN MIGUEL 1106 | LOS PADRES | 0.29269 | 10 | 21.51% | 0 | 0 | 2.142% | 0% | 0 | 0.0065395 | 1 | 0.0065395 | 0.022343
CASTRO VALLEY 1106MR233 | CASTR | CASTRO VALLEY 1106 | MISSION | 0.14387 | 10 | 11.99% | 0 | 0 | 22.61% | 0% | 0 | 0.0064943 | 1 | 0.0064943 | 0.04514
SAN CARLOS 1103 | SAN C | SAN CARLOS 1103 | PENINSULA | 0.013694 | 10 | 0% | 0 | 0 | 32.32% | 0% | 0 | 0.0064833 | 1 | 0.0064833 | 0.47344
OCEANO 1105V48 | OCEAN | OCEANO 1105 | LOS PADRES | 0.76105 | 10 | 0% | 0 | 1 | 30.2% | 0% | 0 | 0.0064819 | 1 | 0.0064819 | 0.008517
OROVILLE 11042588 | OROVI | OROVILLE 1104 | NORTH VALLEY | 0.2392 | 13.5731 | 31.06% | 1 | 0 | 2.673% | 0% | 0 | 0.0064634 | 1 | 0.0064634 | 0.027021
VIEJO 22032634 | VIEJO | VIEJO 2203 | CENTRAL COAST | 0.37273 | 10 | 10.45% | 0 | 0 | 22.39% | 0% | 0 | 0.0063984 | 1 | 0.0063984 | 0.017166
CAYETANO 2109MR186 | CAYET | CAYETANO 2109 | MISSION | 0.10978 | 10 | 0% | 0 | 0 | 4.27% | 0% | 0 | 0.0063941 | 1 | 0.0063941 | 0.058243
CLARK ROAD 11022094 | CLARK | CLARK ROAD 1102 | NORTH VALLEY | 0.57902 | 10 | 17.05% | 0 | 0 | 16.85% | 0% | 0 | 0.0063918 | 1 | 0.0063918 | 0.011039
CASTRO VALLEY 1104MR236 | CASTR | CASTRO VALLEY 1104 | MISSION | 1.7251 | 10 | 10.02% | 0 | 1 | 20.44% | 0% | 0 | 0.0063847 | 1 | 0.0063847 | 0.003701
OCEANO 1106V28 | OCEAN | OCEANO 1106 | LOS PADRES | 1.0201 | 10 | 22.73% | 0 | 0 | 11.28% | 0% | 0 | 0.006335 | 1 | 0.006335 | 0.0062104
TEMPLETON 2108A64 | TEMPL | TEMPLETON 2108 | LOS PADRES | 1.3676 | 10 | 21.6% | 0 | 0 | 11.56% | 0% | 0 | 0.0062941 | 1 | 0.0062941 | 0.0046024
HALF MOON BAY 110265568 | HALF | HALF MOON BAY 1102 | PENINSULA | 0.079124 | 10 | 0% | 0 | 0 | 2.534% | 0% | 0 | 0.0062845 | 1 | 0.0062845 | 0.079426
SAN RAFAEL 110648752 | SAN R | SAN RAFAEL 1106 | NORTH BAY | 0.61983 | 10 | 0% | 0 | 1 | 26.76% | 0% | 0 | 0.0062637 | 1 | 0.0062637 | 0.010106
MARTELL 1103CB | MARTE | MARTELL 1103 | STOCKTON | 0.8745 | 10 | 17.84% | 0 | 0 | 13.95% | 0% | 0 | 0.0062499 | 1 | 0.0062499 | 0.0071469
CORNING 110187304 | CORNI | CORNING 1101 | NORTH VALLEY | 1.5372 | 10 | 14.41% | 0 | 3 | 10.47% | 0% | 0 | 0.0062491 | 1 | 0.0062491 | 0.0040653
PACIFICA 1103CB | PACIF | PACIFICA 1103 | PENINSULA | 0.044512 | 50.42 | 0% | 0 | 0 | 0.9046% | 0% | 0 | 0.0062412 | 1 | 0.0062412 | 0.14021
SARATOGA 1105CB | SARAT | SARATOGA 1105 | DE ANZA | 0.26967 | 10 | 28.45% | 0 | 0 | 4.984% | 0% | 0 | 0.0062358 | 1 | 0.0062358 | 0.023124
STONE CORRAL 11087100 | STONE | STONE CORRAL 1108 | FRESNO | 2.9159 | 10 | 14.41% | 0 | 0 | 15.91% | 0% | 0 | 0.0061962 | 1 | 0.0061962 | 0.002125
CLARK ROAD 1102CB | CLARK | CLARK ROAD 1102 | NORTH VALLEY | 0.16153 | 10 | 1.759% | 0 | 1 | 10.59% | 0% | 0 | 0.006177 | 1 | 0.006177 | 0.038241
PAUL SWEET 210510290 | PAUL | PAUL SWEET 2105 | CENTRAL COAST | 0.48079 | 10 | 22.97% | 0 | 0 | 8.329% | 0% | 0 | 0.0061637 | 1 | 0.0061637 | 0.01282
CLARKSVILLE 2106CB | CLARK | CLARKSVILLE 2106 | SIERRA | 0.13957 | 10 | 0% | 0 | 0 | 27.21% | 0% | 0 | 0.0061619 | 1 | 0.0061619 | 0.044149
PLACER 1101CB | PLACE | PLACER 1101 | SIERRA | 0.77573 | 10 | 3.906% | 0 | 0 | 10.24% | 0% | 0 | 0.0061355 | 1 | 0.0061355 | 0.0079092
TIDEWATER 210695842 | TIDEW | TIDEWATER 2106 | DIABLO | 0.21866 | 10 | 7.343% | 0 | 0 | 20.55% | 0% | 0 | 0.0061241 | 1 | 0.0061241 | 0.028007
MARTELL 110198374 | MARTE | MARTELL 1101 | STOCKTON | 0.48931 | 10 | 16.23% | 0 | 0 | 12.89% | 0% | 0 | 0.0061034 | 1 | 0.0061034 | 0.012474
SNEATH LANE 1101CB | SNEAT | SNEATH LANE 1101 | PENINSULA | 0.21236 | 10 | 2.867% | 0 | 1 | 21.58% | 0% | 0 | 0.0060901 | 1 | 0.0060901 | 0.028678
SAUSALITO 11021224 | SAUSA | SAUSALITO 1102 | NORTH BAY | 0.046722 | 10 | 29.73% | 0 | 0 | 1.494% | 0% | 0 | 0.0060863 | 1 | 0.0060863 | 0.13027
LAS GALLINAS A 1105CB | LAS G | LAS GALLINAS A 1105 | NORTH BAY | 0.31033 | 10 | 12.89% | 0 | 0 | 14.92% | 0% | 0 | 0.0060597 | 1 | 0.0060597 | 0.019527
PIT NO 1 11019702 | PIT N | PIT NO 1 1101 | NORTH VALLEY | 0.44484 | 10 | 24.55% | 0 | 0 | 4.849% | 0% | 0 | 0.0060315 | 1 | 0.0060315 | 0.013559
BANCROFT 0402CB | BANCR | BANCROFT 0402 | EAST BAY | 1.0716 | 10 | 1.687% | 0 | 0 | 23.45% | 0% | 0 | 0.0060178 | 1 | 0.0060178 | 0.0056159
FAIRVIEW 2207P142 | FAIRV | FAIRVIEW 2207 | DIABLO | 0.64407 | 10 | 4.931% | 0 | 0 | 20.76% | 0% | 0 | 0.0060169 | 1 | 0.0060169 | 0.009342
PAUL SWEET 210212850 | PAUL | PAUL SWEET 2102 | CENTRAL COAST | 0.99852 | 10 | 0% | 0 | 0 | 24.38% | 0% | 0 | 0.0059903 | 1 | 0.0059903 | 0.0059992
WILLOW PASS 210821196 | WILLO | WILLOW PASS 2108 | DIABLO | 0.047227 | 10 | 0% | 0 | 0 | 23.89% | 0% | 0 | 0.005961 | 1 | 0.005961 | 0.12622
OAKLAND J 1105CR130 | OAKLA | OAKLAND J 1105 | EAST BAY | 0.95094 | 10 | 5.238% | 0 | 0 | 19.42% | 0% | 0 | 0.0059522 | 1 | 0.0059522 | 0.0062593
MORRO BAY 1101V70 | MORRO | MORRO BAY 1101 | LOS PADRES | 0.13653 | 10 | 0% | 0 | 0 | 22.43% | 0% | 0 | 0.0058754 | 1 | 0.0058754 | 0.043033
ARLINGTON 0401CB | ARLIN | ARLINGTON 0401 | EAST BAY | 0.76473 | 10 | 0% | 0 | 1 | 19.15% | 0% | 0 | 0.005806 | 1 | 0.005806 | 0.0075922
CARMEL 0402CB | CARME | CARMEL 0402 | CENTRAL COAST | 0.30828 | 10 | 0% | 0 | 0 | 21.19% | 0% | 0 | 0.0058032 | 1 | 0.0058032 | 0.018825
HALF MOON BAY 1102CB | HALF | HALF MOON BAY 1102 | PENINSULA | 0.43987 | 10 | 9.941% | 0 | 1 | 10.85% | 0% | 0 | 0.0057997 | 1 | 0.0057997 | 0.013185
IGNACIO 1104 | IGNAC | IGNACIO 1104 | NORTH BAY | 0.012266 | 10 | 0% | 0 | 0 | 20.53% | 0% | 0 | 0.005765 | 1 | 0.005765 | 0.46999
FORT BRAGG A 1103588 | FORT | FORT BRAGG A 1103 | HUMBOLDT | 0.37656 | 10 | 0% | 0 | 0 | 20.3% | 0% | 0 | 0.0057518 | 1 | 0.0057518 | 0.015275
TASSAJARA 211238868 | TASSA | TASSAJARA 2112 | DIABLO | 0.17353 | 10 | 11.26% | 2 | 2 | 4.039% | 0% | 0 | 0.0057426 | 1 | 0.0057426 | 0.033094
OLEMA 110149756 | OLEMA | OLEMA 1101 | NORTH BAY | 0.14983 | 10 | 0% | 0 | 2 | 2.553% | 0% | 0 | 0.0057386 | 1 | 0.0057386 | 0.038301
LAKEWOOD 1102CB | LAKEW | LAKEWOOD 1102 | DIABLO | 0.47236 | 10 | 18.19% | 0 | 0 | 4.922% | 0% | 0 | 0.0057291 | 1 | 0.0057291 | 0.012129
OAKLAND K 1103CB | OAKLA | OAKLAND K 1103 | EAST BAY | 0.65834 | 10 | 0% | 1 | 2 | 13.28% | 0% | 0 | 0.0056661 | 1 | 0.0056661 | 0.0086066
FLINT 110138570 | FLINT | FLINT 1101 | SIERRA | 0.12622 | 10 | 17.37% | 0 | 0 | 3.673% | 0% | 0 | 0.0056203 | 1 | 0.0056203 | 0.044527
SAN RAFAEL 1105CB | SAN R | SAN RAFAEL 1105 | NORTH BAY | 0.49095 | 10 | 6.778% | 3 | 1 | 5.07% | 0% | 0 | 0.0055495 | 1 | 0.0055495 | 0.011304
SNEATH LANE 1102CB | SNEAT | SNEATH LANE 1102 | PENINSULA | 0.28247 | 10 | 3.955% | 0 | 1 | 11.21% | 0% | 0 | 0.0055412 | 1 | 0.0055412 | 0.019617
FREMONT 1104MR707 | FREMO | FREMONT 1104 | MISSION | 1.4479 | 10 | 0% | 0 | 0 | 16.1% | 0% | 0 | 0.0055159 | 1 | 0.0055159 | 0.0038095
OAKLAND J 1105153228 | OAKLA | OAKLAND J 1105 | EAST BAY | 0.47385 | 10 | 4.597% | 0 | 0 | 11.41% | 0% | 0 | 0.0054665 | 1 | 0.0054665 | 0.011536
OCEANO 1105V42 | OCEAN | OCEANO 1105 | LOS PADRES | 0.34173 | 10 | 0% | 0 | 0 | 14.57% | 0% | 0 | 0.0054323 | 1 | 0.0054323 | 0.015896
CORRAL 110175204 | CORRA | CORRAL 1101 | STOCKTON | 1.1128 | 10 | 10.09% | 0 | 0 | 5.993% | 0% | 0 | 0.0054182 | 1 | 0.0054182 | 0.0048691
VIEJO 22029488 | VIEJO | VIEJO 2202 | CENTRAL COAST | 0.18548 | 10 | 0% | 0 | 0 | 14.19% | 0% | 0 | 0.0054123 | 1 | 0.0054123 | 0.02918
POSO MOUNTAIN 21011703 | POSO | POSO MOUNTAIN 2101 | KERN | 0.0074631 | 10 | 0% | 0 | 0 | 0.304% | 0% | 0 | 0.0053821 | 1 | 0.0053821 | 0.72115
CARMEL 0405CB | CARME | CARMEL 0405 | CENTRAL COAST | 0.33684 | 10 | 0% | 0 | 1 | 10.77% | 0% | 0 | 0.0053408 | 1 | 0.0053408 | 0.015855
EL CERRITO G 1111CB | EL CE | EL CERRITO G 1111 | EAST BAY | 0.94606 | 10 | 6.246% | 0 | 0 | 7.497% | 0% | 0 | 0.0053291 | 1 | 0.0053291 | 0.0056329
GIRVAN 1101CB | GIRVA | GIRVAN 1101 | NORTH VALLEY | 0.35544 | 10 | 1.64% | 0 | 0 | 10.78% | 0% | 0 | 0.0053021 | 1 | 0.0053021 | 0.014917
ROSSMOOR 110479146 | ROSSM | ROSSMOOR 1104 | DIABLO | 0.24893 | 10 | 0% | 0 | 0 | 11.42% | 0% | 0 | 0.0052646 | 1 | 0.0052646 | 0.021149
MONTEREY 04012642 | MONTE | MONTEREY 0401 | CENTRAL COAST | 0.26645 | 10 | 0% | 0 | 0 | 10.11% | 0% | 0 | 0.0051963 | 1 | 0.0051963 | 0.019502
BOSTON 0401CR242 | BOSTO | BOSTON 0401 | EAST BAY | 0.44969 | 10 | 0% | 0 | 0 | 9.847% | 0% | 0 | 0.0051828 | 1 | 0.0051828 | 0.011525
DEL MONTE 210386496 | DEL M | DEL MONTE 2103 | CENTRAL COAST | 0.39145 | 10 | 0% | 3 | 0 | 5.331% | 0% | 0 | 0.0051542 | 1 | 0.0051542 | 0.013167
ARCATA 112233060 | ARCAT | ARCATA 1122 | HUMBOLDT | 0.34235 | 10 | 0% | 0 | 1 | 7.017% | 0% | 0 | 0.0051448 | 1 | 0.0051448 | 0.015028
SNEATH LANE 110168070 | SNEAT | SNEATH LANE 1101 | PENINSULA | 0.099639 | 10 | 0% | 0 | 2 | 4.651% | 0% | 0 | 0.0051309 | 1 | 0.0051309 | 0.051495
VIEJO 22022014 | VIEJO | VIEJO 2202 | CENTRAL COAST | 0.34884 | 10 | 0% | 0 | 0 | 8.641% | 0% | 0 | 0.0051208 | 1 | 0.0051208 | 0.01468
CLARKSVILLE 2103CB | CLARK | CLARKSVILLE 2103 | SIERRA | 0.11367 | 10 | 0% | 0 | 0 | 7.91% | 0% | 0 | 0.0050836 | 1 | 0.0050836 | 0.044724
VACAVILLE 110847860 | VACAV | VACAVILLE 1108 | SACRAMENTO | 0.28908 | 10 | 0% | 0 | 0 | 7.334% | 0% | 0 | 0.0050545 | 1 | 0.0050545 | 0.017485
SAN RAFAEL 11061230 | SAN R | SAN RAFAEL 1106 | NORTH BAY | 0.27095 | 10 | 0% | 0 | 1 | 5.214% | 0% | 0 | 0.0050532 | 1 | 0.0050532 | 0.01865
DEL MAR 210938684 | DEL M | DEL MAR 2109 | SIERRA | 0.062211 | 10 | 0% | 0 | 0 | 6.669% | 0% | 0 | 0.0050211 | 1 | 0.0050211 | 0.080711
SARATOGA 1103LC40 | SARAT | SARATOGA 1103 | DE ANZA | 0.12637 | 10 | 0% | 0 | 0 | 6.576% | 0% | 0 | 0.0050164 | 1 | 0.0050164 | 0.039697
EL CERRITO G 1108CB | EL CE | EL CERRITO G 1108 | EAST BAY | 0.47538 | 10 | 0% | 0 | 0 | 6.483% | 0% | 0 | 0.0050118 | 1 | 0.0050118 | 0.010543
FORT BRAGG A 110436526 | FORT | FORT BRAGG A 1104 | HUMBOLDT | 0.39885 | 10 | 0% | 0 | 0 | 6.124% | 0% | 0 | 0.0049939 | 1 | 0.0049939 | 0.012521
SHINGLE SPRINGS 210851474 | SHING | SHINGLE SPRINGS 2108 | SIERRA | 0.24496 | 10 | 0% | 0 | 0 | 5.255% | 0% | 0 | 0.0049508 | 1 | 0.0049508 | 0.020211
FORT BRAGG A 1101CB | FORT | FORT BRAGG A 1101 | HUMBOLDT | 0.22122 | 10 | 0% | 0 | 1 | 2.86% | 0% | 0 | 0.0049359 | 1 | 0.0049359 | 0.022312
RIO DELL 11028768 | RIO D | RIO DELL 1102 | HUMBOLDT | 0.28084 | 10 | 0% | 0 | 0 | 4.757% | 0% | 0 | 0.0049263 | 1 | 0.0049263 | 0.017541
SNEATH LANE 110275844 | SNEAT | SNEATH LANE 1102 | PENINSULA | 0.025403 | 10 | 0% | 0 | 0 | 4.723% | 0% | 0 | 0.0049246 | 1 | 0.0049246 | 0.19386
GREENBRAE 1104751 | GREEN | GREENBRAE 1104 | NORTH BAY | 0.079918 | 10 | 0% | 0 | 1 | 2.532% | 0% | 0 | 0.0049198 | 1 | 0.0049198 | 0.061561
BRUNSWICK 111095576 | BRUNS | BRUNSWICK 1110 | SIERRA | 0.15603 | 10 | 0% | 0 | 0 | 4.385% | 0% | 0 | 0.004908 | 1 | 0.004908 | 0.031456
MILPITAS 1109XR044 | MILPI | MILPITAS 1109 | SAN JOSE | 0.07893 | 10 | 0% | 0 | 0 | 4.212% | 0% | 0 | 0.0048996 | 1 | 0.0048996 | 0.062075
SAN LEANDRO U 1109CR344 | SAN L | SAN LEANDRO U 1109 | MISSION | 0.097411 | 10 | 0% | 0 | 0 | 3.929% | 0% | 0 | 0.0048858 | 1 | 0.0048858 | 0.050156
SARATOGA 1107CB | SARAT | SARATOGA 1107 | DE ANZA | 0.16938 | 10 | 0% | 0 | 1 | 1.739% | 0% | 0 | 0.0048811 | 1 | 0.0048811 | 0.028818
SAN RAFAEL 11092213 | SAN R | SAN RAFAEL 1109 | NORTH BAY | 0.014561 | 10 | 0% | 0 | 0 | 3.395% | 0% | 0 | 0.0048598 | 1 | 0.0048598 | 0.33376
FORT BRAGG A 1104CB | FORT | FORT BRAGG A 1104 | HUMBOLDT | 0.049503 | 10 | 0% | 1 | 0 | 1.775% | 0% | 0 | 0.0048453 | 1 | 0.0048453 | 0.097879
BRUNSWICK 110765574 | BRUNS | BRUNSWICK 1107 | SIERRA | 0.053599 | 10 | 0% | 0 | 0 | 3.058% | 0% | 0 | 0.0048435 | 1 | 0.0048435 | 0.090365
ALHAMBRA 1102CB | ALHAM | ALHAMBRA 1102 | DIABLO | 0.16935 | 10 | 0% | 0 | 0 | 2.96% | 0% | 0 | 0.0048388 | 1 | 0.0048388 | 0.028574
VALLEY VIEW 1105P124 | VALLE | VALLEY VIEW 1105 | EAST BAY | 0.092976 | 10 | 0% | 0 | 0 | 2.939% | 0% | 0 | 0.0048377 | 1 | 0.0048377 | 0.052032
WOODSIDE 11028862 | WOODS | WOODSIDE 1102 | PENINSULA | 0.10582 | 10 | 0% | 0 | 0 | 2.762% | 0% | 0 | 0.0048292 | 1 | 0.0048292 | 0.045638
FRANKLIN 1101P132 | FRANK | FRANKLIN 1101 | EAST BAY | 0.033203 | 10 | 0% | 0 | 0 | 2.185% | 0% | 0 | 0.0048015 | 1 | 0.0048015 | 0.14461
HORSESHOE 1104CB | HORSE | HORSESHOE 1104 | SIERRA | 0.063337 | 10 | 0% | 0 | 0 | 2.137% | 0% | 0 | 0.0047992 | 1 | 0.0047992 | 0.075774
HARRIS 11084674 | HARRI | HARRIS 1108 | HUMBOLDT | 0.15936 | 10 | 0% | 0 | 0 | 1.98% | 0% | 0 | 0.0047917 | 1 | 0.0047917 | 0.030069
CASTRO VALLEY 1101MR518 | CASTR | CASTRO VALLEY 1101 | MISSION | 0.037775 | 10 | 0% | 0 | 0 | 1.912% | 0% | 0 | 0.0047885 | 1 | 0.0047885 | 0.12677
HALF MOON BAY 11019014 | HALF | HALF MOON BAY 1101 | PENINSULA | 0.031423 | 10 | 0% | 0 | 0 | 1.737% | 0% | 0 | 0.0047801 | 1 | 0.0047801 | 0.15212
VIEJO 22039094 | VIEJO | VIEJO 2203 | CENTRAL COAST | 0.038317 | 10 | 0% | 0 | 0 | 1.572% | 0% | 0 | 0.0047723 | 1 | 0.0047723 | 0.12455
EL CERRITO G 1108BR346 | EL CE | EL CERRITO G 1108 | EAST BAY | 0.1038 | 10 | 0% | 0 | 0 | 1.483% | 0% | 0 | 0.004768 | 1 | 0.004768 | 0.045936
SUMMIT 110168706 | SUMMI | SUMMIT 1101 | SIERRA | 0.058904 | 10 | 0% | 0 | 0 | 1.149% | 0% | 0 | 0.0047522 | 1 | 0.0047522 | 0.080677
RINCON 1102640 | RINCO | RINCON 1102 | SONOMA | 0.04813 | 10 | 0% | 0 | 0 | 1.143% | 0% | 0 | 0.0047519 | 1 | 0.0047519 | 0.098729
CAROLANDS 040484797 | CAROL | CAROLANDS 0404 | PENINSULA | 0.013784 | 10 | 0% | 0 | 0 | 1.034% | 0% | 0 | 0.0047467 | 1 | 0.0047467 | 0.34435
WYANDOTTE 1103CB | WYAND | WYANDOTTE 1103 | NORTH VALLEY | 0.060864 | 10 | 0% | 0 | 0 | 0.8345% | 0% | 0 | 0.0047373 | 1 | 0.0047373 | 0.077834
LAURELES 1112CB | LAURE | LAURELES 1112 | CENTRAL COAST | 0.015644 | 10 | 0% | 0 | 0 | 0.6574% | 0% | 0 | 0.0047289 | 1 | 0.0047289 | 0.30228
ALTO 112088190 | ALTO | ALTO 1120 | NORTH BAY | 0.01959 | 10 | 0% | 0 | 0 | 0.6244% | 0% | 0 | 0.0047274 | 1 | 0.0047274 | 0.24131
OCEANO 1104Q04 | OCEAN | OCEANO 1104 | LOS PADRES | 0.015582 | 10 | 0% | 0 | 0 | 0.5987% | 0% | 0 | 0.0047262 | 1 | 0.0047262 | 0.3033
OCEANO 1105V20 | OCEAN | OCEANO 1105 | LOS PADRES | 0.031809 | 10 | 0% | 0 | 0 | 0.5465% | 0% | 0 | 0.0047237 | 1 | 0.0047237 | 0.1485
VASONA 1102CB | VASON | VASONA 1102 | DE ANZA | 0.06716 | 10 | 0% | 0 | 0 | 0.4408% | 0% | 0 | 0.0047187 | 1 | 0.0047187 | 0.070261
OAKLAND J 1116CR420 | OAKLA | OAKLAND J 1116 | EAST BAY | 0.031861 | 10 | 0% | 0 | 0 | 0.2787% | 0% | 0 | 0.0047111 | 1 | 0.0047111 | 0.14787
ALTO 1121CB | ALTO | ALTO 1121 | NORTH BAY | 0.013093 | 10 | 0% | 0 | 0 | 0.2456% | 0% | 0 | 0.0047095 | 1 | 0.0047095 | 0.35971
BRUNSWICK 1110CB | BRUNS | BRUNSWICK 1110 | SIERRA | 0.0037878 | 10 | 0% | 0 | 0 | 0.2212% | 0% | 0 | 0.0047084 | 1 | 0.0047084 | 1.2431
CAYUCOS 1101W14 | CAYUC | CAYUCOS 1101 | LOS PADRES | 0.012808 | 10 | 0% | 0 | 0 | 0.1056% | 0% | 0 | 0.004703 | 1 | 0.004703 | 0.36719
REEDLEY 11127240 | REEDL | REEDLEY 1112 | FRESNO | 0.0028032 | 10 | 0% | 0 | 0 | 0.01029% | 0% | 0 | 0.0046985 | 1 | 0.0046985 | 1.6761

## Sheet4
Row Labels | Max of Fire Risk | Average of Fire Risk | Sum of Tier 2/3 OH Miles | Count of Substation
ALHAM | 0.072547 | 0.020511 | 37.6776 | 7
ALLEG | 31.4559 | 17.4071 | 79.4609 | 7
ALTO | 13.1255 | 1.6421 | 81.078 | 22
ANDER | 0.45678 | 0.10329 | 15.6797 | 5
ANITA | 0.84484 | 0.84484 | 0.115 | 1
ANNAP | 7.8886 | 2.0299 | 51.2424 | 4
ANTEL | 0.014633 | 0.014633 | 0.75322 | 1
ANTLE | 0.08259 | 0.051689 | 60.0715 | 6
APPLE | 29.0916 | 7.203 | 487.2527 | 21
ARBUC | 0.24977 | 0.24977 | 2.0417 | 1
ARCAT | 0.061973 | 0.030417 | 27.1745 | 4
ARLIN | 0.005806 | 0.005806 | 0.76473 | 1
ATASC | 8.8937 | 1.0584 | 141.8638 | 14
AUBER | 21.8618 | 2.1784 | 371.2851 | 19
AUBUR | 0.017498 | 0.013515 | 5.3983 | 4
BALCH | 0.035267 | 0.032761 | 14.6983 | 2
BANCR | 0.0060178 | 0.0060178 | 1.0716 | 1
BANGO | 0.10317 | 0.051716 | 197.9775 | 9
BASAL | 1.1636 | 0.58876 | 4.9877 | 2
BAY M | 0.026024 | 0.01936 | 4.2519 | 2
BAYWO | 0.008459 | 0.008459 | 1.4233 | 1
BEAR | 10.8965 | 0.72222 | 241.5472 | 16
BELL | 4.0106 | 0.71383 | 122.4657 | 10
BELLE | 11.7473 | 3.1026 | 28.7757 | 5
BELMO | 0.011413 | 0.010046 | 1.5331 | 2
BEN L | 9.1195 | 3.6857 | 36.5295 | 7
BERES | 0.0094751 | 0.0081297 | 4.1458 | 2
BERKE | 4.67 | 0.95557 | 4.1144 | 5
BIG B | 35.0163 | 4.3836 | 224.4524 | 32
BIG M | 4.1128 | 0.48445 | 57.1862 | 10
BIG R | 0.19578 | 0.042524 | 71.4583 | 12
BIG T | 17.8776 | 9.036 | 16.1073 | 2
BOGAR | 0.03523 | 0.03523 | 0.51623 | 1
BOLIN | 0.94457 | 0.18508 | 36.2161 | 11
BONNI | 45.9434 | 30.9016 | 58.7779 | 3
BOSTO | 0.0051828 | 0.0051828 | 0.44969 | 1
BRENT | 0.042733 | 0.02412 | 9.8403 | 4
BRIDG | 6.6593 | 2.4181 | 55.8858 | 7
BROWN | 0.046288 | 0.031865 | 37.7491 | 5
BRUNS | 60.8822 | 12.5617 | 488.4002 | 49
BRYAN | 0.094086 | 0.094086 | 1.2282 | 1
BUCKS | 24.0095 | 7.091 | 60.7508 | 5
BUELL | 1.7718 | 0.38615 | 93.4019 | 7
BURNE | 0.048736 | 0.027573 | 52.216 | 8
BURNS | 11.7089 | 9.5881 | 1.664 | 2
BUTTE | 0.011878 | 0.011878 | 1.8432 | 1
CABRI | 9.9744 | 1.1611 | 84.1301 | 9
CAL W | 0.023426 | 0.023426 | 2.9688 | 1
CALAV | 0.10314 | 0.051424 | 190.5291 | 13
CALIS | 35.5203 | 5.9455 | 115.6256 | 15
CALPE | 0.080296 | 0.03754 | 77.8529 | 8
CALPI | 9.7937 | 3.085 | 37.4263 | 8
CAMBR | 0.039572 | 0.021739 | 44.7655 | 4
CAMP | 34.1458 | 3.988 | 292.3495 | 54
CAMPH | 0.018555 | 0.018555 | 1.4665 | 1
CARLO | 0.041044 | 0.023536 | 21.1982 | 5
CARME | 0.0058032 | 0.005572 | 0.64512 | 2
CAROL | 0.033705 | 0.014579 | 3.9545 | 4
CASTR | 6.6796 | 1.0079 | 54.5012 | 19
CAYET | 0.20657 | 0.050257 | 40.9085 | 6
CAYUC | 0.079048 | 0.027833 | 15.9947 | 4
CEDAR | 0.18445 | 0.09302 | 110.9 | 6
CENTE | 0.182 | 0.11858 | 36.3928 | 5
CHALL | 41.0501 | 28.8978 | 112.2874 | 8
CHEST | 0.047498 | 0.025066 | 4.9789 | 3
CHOLA | 0.049821 | 0.037547 | 58.4006 | 3
CLARK | 13.6054 | 1.3524 | 234.4067 | 27
CLAY | 0.059218 | 0.023246 | 76.7687 | 10
CLAYT | 9.6421 | 1.4983 | 59.8621 | 10
CLEAR | 0.78881 | 0.23395 | 21.8965 | 6
CLOVE | 3.0559 | 0.38027 | 105.0157 | 16
CMC 1 | 0.021532 | 0.017114 | 2.5236 | 2
COARS | 8.6723 | 0.78213 | 411.422 | 28
COAST | 0.012695 | 0.010335 | 1.6617 | 2
COLUM | 36.2974 | 20.8145 | 90.9452 | 6
COPPE | 0.013252 | 0.013252 | 8.1519 | 1
CORNI | 3.1042 | 0.5264 | 131.4673 | 11
CORON | 0.013274 | 0.013274 | 0.968 | 1
CORRA | 8.2388 | 1.5046 | 194.7629 | 18
CORTI | 0.6837 | 0.6837 | 1.036 | 1
COTAT | 4.0407 | 0.99668 | 143.0492 | 23
COTTO | 3.0669 | 0.67454 | 255.9289 | 14
COVEL | 0.024981 | 0.017548 | 9.9189 | 4
CRESC | 4.2473 | 1.9587 | 43.6463 | 6
CURTI | 15.6252 | 1.176 | 480.8712 | 39
CUYAM | 0.02009 | 0.02009 | 2.3769 | 1
DEL M | 1.2644 | 0.16217 | 75.6419 | 17
DESCH | 3.6179 | 0.50654 | 189.7161 | 13
DIAMO | 16.1444 | 1.0971 | 337.6856 | 19
DIVID | 0.010844 | 0.010844 | 2.2423 | 1
DOBBI | 0.17584 | 0.081719 | 80.2916 | 6
DOLAN | 0.010669 | 0.010661 | 3.8209 | 2
DOWNI | 21.9265 | 21.9265 | 0.032712 | 2
DRUM | 25.0967 | 12.7697 | 18.8373 | 2
DUNBA | 14.3001 | 2.5414 | 119.4031 | 22
DUNLA | 0.84147 | 0.10815 | 126.5617 | 14
EAST | 4.5718 | 1.8775 | 3.7247 | 3
ECHO | 0.13221 | 0.05551 | 6.1677 | 5
EDENV | 0.019259 | 0.015925 | 0.76864 | 2
EDES | 0.036955 | 0.018828 | 15.8364 | 6
EEL R | 0.42884 | 0.10027 | 41.3357 | 5
EL CE | 0.76268 | 0.11187 | 26.8925 | 16
EL DO | 70.5639 | 26.3829 | 190.5389 | 13
ELECT | 23.7964 | 2.3608 | 167.2425 | 13
ELK 1 | 0.15006 | 0.034574 | 76.2893 | 9
ELK C | 1.6829 | 0.32795 | 82.7232 | 10
EMERA | 0.11416 | 0.041806 | 23.5053 | 4
ESTUD | 0.0067781 | 0.0067781 | 0.69789 | 1
FAIRM | 0.0082593 | 0.0082593 | 1.4849 | 1
FAIRV | 0.027316 | 0.012769 | 18.7684 | 6
FELTO | 0.093336 | 0.093336 | 2.2987 | 1
FITCH | 17.8255 | 3.4693 | 74.4456 | 11
FLINT | 1.2249 | 0.25256 | 5.6839 | 5
FLORE | 0.012695 | 0.010783 | 1.7158 | 2
FOOTH | 1.061 | 0.34011 | 28.0857 | 5
FORES | 44.1076 | 25.3197 | 94.9915 | 8
FORT | 18.3292 | 1.3047 | 314.6716 | 36
FRANK | 0.015101 | 0.0097423 | 7.2013 | 5
FREMO | 0.64033 | 0.32292 | 2.6857 | 2
FRENC | 0.057283 | 0.042846 | 41.2147 | 7
FROGT | 1.0887 | 0.11554 | 308.6049 | 20
FRUIT | 5.3172 | 1.1812 | 83.4241 | 12
FULTO | 20.8046 | 4.3603 | 66.4878 | 11
GABIL | 0.7991 | 0.3284 | 6.4622 | 3
GANSN | 1.1048 | 0.42531 | 38.7574 | 4
GARBE | 8.4333 | 1.1355 | 210.6698 | 23
GARCI | 3.5484 | 3.4371 | 2.4735 | 2
GEYSE | 0.77452 | 0.15645 | 123.3345 | 15
GIRVA | 4.26 | 0.9218 | 149.8288 | 10
GLENN | 0.01909 | 0.01909 | 2.3498 | 1
GOLDT | 0.31985 | 0.14927 | 10.7884 | 4
GONZA | 0.92235 | 0.24414 | 5.5052 | 4
GRASS | 11.1047 | 1.3785 | 103.5142 | 9
GRAYS | 0.063148 | 0.063148 | 10.7057 | 1
GREEN | 1.6346 | 0.18081 | 55.5277 | 17
GUALA | 1.3517 | 0.17514 | 81.9308 | 11
HALF | 15.668 | 1.0736 | 175.9729 | 22
HALSE | 0.68906 | 0.10182 | 130.4913 | 12
HAMIL | 3.9575 | 0.73734 | 26.7473 | 9
HARRI | 0.086853 | 0.033929 | 15.6123 | 3
HARTL | 0.57017 | 0.11386 | 32.5313 | 12
HATTO | 3.5836 | 0.37983 | 25.5299 | 10
HICKS | 1.1412 | 0.18188 | 32.772 | 7
HIGGI | 0.62642 | 0.069758 | 355.1528 | 33
HIGHL | 12.9592 | 1.2019 | 159.4303 | 17
HOLLI | 0.044317 | 0.019951 | 103.1161 | 10
HOLLY | 0.010899 | 0.010899 | 2.9599 | 1
HOOPA | 4.9741 | 0.65196 | 103.3689 | 10
HOPLA | 0.36545 | 0.063539 | 82.4026 | 9
HORSE | 0.55294 | 0.17025 | 7.4678 | 5
HUMBO | 0.012021 | 0.012021 | 7.0458 | 1
IGNAC | 1.6637 | 0.24185 | 12.4082 | 8
INDIA | 0.58642 | 0.28409 | 16.7358 | 4
IONE | 0.034177 | 0.020761 | 15.6336 | 2
JAMES | 0.75514 | 0.34552 | 30.6214 | 5
JARVI | 0.54812 | 0.2237 | 3.8367 | 5
JESSU | 2.9417 | 0.46886 | 119.7612 | 17
JOLON | 0.042992 | 0.024341 | 81.1155 | 8
KANAK | 26.6692 | 11.7677 | 92.5364 | 8
KERCK | 0.039955 | 0.031638 | 34.5924 | 3
KERN | 0.012298 | 0.010465 | 1.5124 | 2
KESWI | 0.26099 | 0.14566 | 50.8481 | 6
KING | 0.058354 | 0.058354 | 17.5881 | 1
KIRKE | 0.024306 | 0.024306 | 5.4258 | 1
KONOC | 17.0951 | 2.8165 | 140.5019 | 17
LAKEV | 1.6557 | 0.4957 | 20.015 | 4
LAKEW | 0.63414 | 0.19342 | 9.2058 | 7
LAMON | 0.018222 | 0.018222 | 0.50063 | 1
LAS A | 0.018243 | 0.015886 | 5.9862 | 2
LAS G | 11.3927 | 1.4573 | 18.3609 | 8
LAS P | 0.030304 | 0.01801 | 7.411 | 3
LAURE | 2.471 | 0.3964 | 134.0382 | 13
LAYTO | 4.62 | 1.7062 | 162.3136 | 14
LINCO | 1.1219 | 0.5075 | 51.2867 | 6
LLAGA | 0.31885 | 0.1023 | 31.2751 | 12
LOGAN | 0.020313 | 0.020313 | 3.7103 | 1
LONE | 0.019234 | 0.019234 | 9.5646 | 1
LOS C | 0.009461 | 0.009461 | 2.6219 | 1
LOS G | 43.362 | 7.1816 | 180.4401 | 20
LOS M | 0.017254 | 0.017254 | 0.1275 | 1
LOS O | 0.057419 | 0.030484 | 47.1268 | 5
LOW G | 4.8093 | 2.0759 | 71.107 | 6
LOYOL | 0.010852 | 0.010852 | 0.10967 | 1
LUCER | 0.076393 | 0.028606 | 67.2011 | 16
MADIS | 1.2706 | 0.26579 | 7.647 | 5
MAPLE | 0.059846 | 0.059846 | 9.8748 | 1
MARIP | 52.4012 | 2.5808 | 506.3511 | 22
MARTE | 0.6193 | 0.099853 | 102.5301 | 11
MAXWE | 0.018513 | 0.018513 | 1.6684 | 1
MC AR | 0.025754 | 0.018742 | 69.8489 | 9
MC KE | 0.059287 | 0.024055 | 14.9596 | 4
MEADO | 3.5783 | 3.5783 | 0.20712 | 1
MENDO | 12.6646 | 2.553 | 40.8852 | 5
MENLO | 3.7456 | 0.81103 | 67.0116 | 9
MERCE | 1.585 | 0.27641 | 120.7817 | 8
MESA | 4.6108 | 0.72123 | 59.5665 | 7
MIDDL | 42.9273 | 7.4276 | 156.6438 | 18
MILPI | 0.64865 | 0.11779 | 29.7328 | 7
MIRAB | 28.8258 | 5.7792 | 65.8017 | 17
MIWUK | 81.7128 | 23.2111 | 152.9141 | 20
MOLIN | 33.7736 | 9.3026 | 147.4025 | 17
MONRO | 3.6239 | 1.2686 | 2.1875 | 3
MONTE | 30.9824 | 10.9313 | 140.6161 | 44
MONTI | 1.1518 | 0.29684 | 109.7815 | 13
MORAG | 9.4021 | 1.8473 | 51.6926 | 15
MORGA | 13.0233 | 0.79246 | 109.4127 | 18
MORRO | 0.073801 | 0.017428 | 27.7406 | 13
MOUNT | 18.2964 | 1.8661 | 224.6216 | 13
NAPA | 1.0072 | 0.51678 | 17.6226 | 2
NARRO | 0.90585 | 0.13643 | 334.7252 | 19
NEWBU | 0.15433 | 0.065865 | 12.6411 | 6
NORTH | 2.045 | 0.38751 | 82.4892 | 11
NOTRE | 0.15694 | 0.090232 | 27.4274 | 3
NOVAT | 0.016828 | 0.01279 | 4.2213 | 2
OAK 0 | 0.018493 | 0.018493 | 4.3198 | 1
OAKHU | 27.311 | 4.4668 | 233.0465 | 19
OAKLA | 11.9989 | 1.202 | 88.1874 | 47
OCEAN | 2.3277 | 0.31897 | 130.97 | 21
OILFI | 2.2153 | 0.2461 | 115.2449 | 12
OLEMA | 7.8017 | 1.6276 | 61.001 | 11
OLETA | 1.0679 | 0.25949 | 147.7517 | 12
OREGO | 0.57952 | 0.094162 | 205.4074 | 13
ORIND | 0.052555 | 0.037519 | 9.3864 | 3
ORO F | 49.3837 | 21.5628 | 155.9575 | 14
OROSI | 0.010989 | 0.010989 | 0.26307 | 1
OROVI | 0.0064634 | 0.0064634 | 0.2392 | 1
OTTER | 9.4134 | 1.0219 | 78.1108 | 10
PACIF | 2.1021 | 0.44884 | 13.0641 | 10
PALME | 0.05552 | 0.032869 | 37.0218 | 4
PALO | 0.035354 | 0.035354 | 4.7078 | 1
PANOC | 0.064167 | 0.036102 | 45.8174 | 3
PANOR | 1.1971 | 0.21687 | 43.8734 | 6
PARAD | 28.8939 | 6.0878 | 155.9722 | 35
PASO | 3.3373 | 0.95669 | 77.1144 | 13
PAUL | 12.3809 | 1.5752 | 83.5421 | 17
PEABO | 0.80125 | 0.3092 | 3.0716 | 4
PENNG | 4.2653 | 2.1875 | 19.2167 | 2
PENRY | 2.9333 | 0.53803 | 145.6861 | 20
PEORI | 1.0321 | 0.12835 | 204.5462 | 30
PERRY | 0.19088 | 0.041903 | 67.3591 | 10
PETAL | 5.1384 | 0.98177 | 121.4738 | 16
PHILO | 5.1995 | 0.69963 | 160.9847 | 8
PIERC | 0.026979 | 0.026979 | 14.4387 | 1
PIKE | 39.3662 | 24.3107 | 43.9528 | 4
PINE | 45.714 | 12.2108 | 250.7398 | 17
PINEC | 1.9469 | 1.5849 | 1.957 | 3
PIT N | 0.049074 | 0.031804 | 98.6549 | 19
PLACE | 50.479 | 3.1508 | 368.3903 | 23
POINT | 11.7089 | 1.8282 | 105.3245 | 25
POSO | 0.052745 | 0.02291 | 79.1649 | 9
POTTE | 0.078348 | 0.024921 | 52.216 | 10
PRUNE | 0.010696 | 0.010696 | 0.046537 | 1
PUEBL | 35.1362 | 3.8638 | 123.5039 | 19
PURIS | 0.2429 | 0.052947 | 15.9907 | 6
PUTAH | 2.2639 | 0.92151 | 31.2115 | 7
RACET | 5.0145 | 0.84132 | 101.8346 | 12
RADUM | 0.023926 | 0.023926 | 2.1702 | 1
RALST | 0.025196 | 0.017612 | 11.9066 | 5
RAWSO | 0.017954 | 0.017954 | 2.3781 | 1
RED B | 1.7969 | 0.27999 | 146.771 | 13
REDBU | 12.4782 | 1.5385 | 75.138 | 13
REEDL | 0.028512 | 0.016006 | 1.9056 | 3
RESEA | 3.7919 | 2.1589 | 1.2814 | 2
RESER | 1.4058 | 0.24888 | 39.5739 | 6
RIDGE | 0.02026 | 0.017172 | 4.3294 | 2
RINCO | 29.2949 | 6.0431 | 73.2051 | 13
RIO D | 0.10074 | 0.032551 | 50.4197 | 10
RISIN | 0.033124 | 0.020465 | 46.3641 | 4
ROB R | 9.3933 | 0.66388 | 144.4741 | 17
ROSSM | 9.7653 | 0.91214 | 29.951 | 13
SALMO | 4.7981 | 1.2271 | 26.7666 | 5
SALT | 63.7309 | 14.5484 | 68.8309 | 14
SAN A | 0.014985 | 0.012181 | 2.6646 | 3
SAN B | 0.24643 | 0.085872 | 32.6485 | 4
SAN C | 0.021835 | 0.012777 | 12.3718 | 9
SAN J | 0.75797 | 0.23397 | 212.4959 | 13
SAN L | 2.0859 | 0.12938 | 173.408 | 33
SAN M | 0.312 | 0.070622 | 63.6742 | 6
SAN R | 17.4483 | 1.1936 | 128.6183 | 47
SAND | 1.4014 | 0.19821 | 149.2192 | 9
SANTA | 6.4225 | 1.0461 | 207.5606 | 25
SARAT | 8.429 | 0.60557 | 65.233 | 15
SAUSA | 0.76987 | 0.14322 | 9.2313 | 7
SCE R | 9.7937 | 9.7937 | 0.29161 | 1
SCE T | 0.045873 | 0.045873 | 1.4276 | 1
SCE V | 0.13022 | 0.13022 | 0.17032 | 1
SEACL | 1.4392 | 0.55686 | 9.5384 | 3
SHADY | 12.6776 | 4.854 | 80.7269 | 7
SHEPH | 2.2604 | 2.2604 | 19.9144 | 1
SHING | 20.3908 | 3.2725 | 373.607 | 28
SIERR | 4.262 | 4.262 | 0.018511 | 2
SILVE | 27.494 | 6.2133 | 227.7736 | 29
SISQU | 0.21174 | 0.11917 | 76.2489 | 4
SMART | 0.032648 | 0.032648 | 15.8868 | 1
SNEAT | 0.20826 | 0.025168 | 6.4439 | 12
SO. C | 0.051431 | 0.045066 | 7.6021 | 2
SOBRA | 0.067265 | 0.038352 | 47.1251 | 8
SOLED | 0.029952 | 0.016165 | 31.1065 | 8
SONOM | 3.4319 | 0.46423 | 56.7951 | 14
SPANI | 2.9343 | 2.9343 | 7.9163 | 1
SPAUL | 0.13582 | 0.13582 | 20.1063 | 1
SPENC | 0.0298 | 0.023484 | 12.0662 | 2
SPRIN | 67.2336 | 15.5648 | 41.0705 | 6
SPRUC | 0.02375 | 0.020061 | 6.028 | 2
STAFF | 1.1617 | 0.39549 | 28.9258 | 14
STANI | 45.4193 | 17.9986 | 130.95 | 18
STELL | 17.8888 | 3.2557 | 37.0349 | 6
STILL | 0.10603 | 0.055269 | 112.7347 | 7
STONE | 0.012359 | 0.0097622 | 5.2348 | 3
SUMMI | 0.037786 | 0.019902 | 13.9092 | 12
SUNOL | 0.39615 | 0.08017 | 34.5067 | 11
SWIFT | 0.084233 | 0.041268 | 86.312 | 5
SYCAM | 28.0273 | 5.6316 | 54.0595 | 5
TAMAR | 0.38292 | 0.38292 | 16.4477 | 1
TAR F | 1.2311 | 0.32211 | 9.0078 | 4
TASSA | 4.8049 | 1.0844 | 25.1602 | 15
TEJON | 0.043014 | 0.032479 | 34.9641 | 4
TEMPL | 6.435 | 0.69658 | 377.6858 | 24
TIDEW | 0.013929 | 0.010008 | 8.1253 | 3
TIGER | 10.0449 | 10.0449 | 3.8998 | 1
TIVY | 2.8963 | 0.54574 | 118.6456 | 6
TOCAL | 0.017781 | 0.017781 | 0.031239 | 1
TRES | 0.018321 | 0.018321 | 0.10269 | 1
TRIDA | 0.028512 | 0.028512 | 0.050313 | 1
TULE | 0.01789 | 0.01789 | 4.0927 | 1
TULUC | 0.014345 | 0.014345 | 4.4167 | 1
TYLER | 0.075876 | 0.048229 | 60.5727 | 3
UKIAH | 1.4188 | 0.15527 | 98.3542 | 11
UPPER | 0.87287 | 0.18044 | 53.0863 | 8
VACA | 2.416 | 1.6197 | 26.9555 | 3
VACAV | 1.9532 | 0.60096 | 56.5557 | 10
VALLE | 1.2081 | 0.19522 | 14.319 | 11
VASCO | 0.73217 | 0.40819 | 41.9238 | 2
VASON | 0.0047187 | 0.0047187 | 0.06716 | 1
VIEJO | 0.37005 | 0.049487 | 37.5091 | 26
VINEY | 8.7379 | 1.9151 | 10.7648 | 5
VOLTA | 25.5745 | 6.3582 | 281.2137 | 23
WALDO | 0.010847 | 0.0089946 | 4.7327 | 2
WASHI | 13.4438 | 13.4438 | 0.016194 | 2
WEIMA | 0.080042 | 0.044137 | 97.3379 | 9
WEIME | 2.0183 | 2.0183 | 0.15676 | 1
WEST | 40.2233 | 16.5647 | 293.9265 | 25
WESTL | 0.010946 | 0.010946 | 0.92376 | 1
WHEAT | 0.67299 | 0.67299 | 9.9882 | 1
WHITM | 32.038 | 6.4449 | 92.5696 | 5
WILDW | 0.68153 | 0.1784 | 32.6037 | 5
WILLI | 32.1635 | 7.0749 | 231.7593 | 21
WILLO | 13.3065 | 3.0794 | 142.1073 | 17
WISE | 4.4121 | 0.91198 | 123.6041 | 10
WISHO | 0.074616 | 0.074616 | 7.7822 | 1
WOOD | 0.0082741 | 0.0082741 | 0.4018 | 1
WOODA | 23.3871 | 7.493 | 68.9785 | 10
WOODS | 24.0717 | 4.5573 | 56.2907 | 18
WOODW | 0.3371 | 0.12992 | 30.1544 | 3
WYAND | 46.1001 | 2.7434 | 278.7406 | 31
ZACA | 3.4068 | 0.54055 | 83.6467 | 7
Grand Total | 81.7128 | 2.7884 | 25594.7343 | 3205

## Sheet5
Sub | Max of Fire Risk | Average of Fire Risk | Sum of Tier 2/3 OH Miles
MIWUK | 81.7128 | 23.2111 | 152.9141 | 357 substations total
EL DO | 70.5639 | 26.3829 | 190.5389 | Top 10% | 36
SPRIN | 67.2336 | 15.5648 | 41.0705
SALT | 63.7309 | 14.5484 | 68.8309
BRUNS | 60.8822 | 12.5617 | 488.4002
MARIP | 52.4012 | 2.5808 | 506.3511
DOWNI | 21.9265 | 21.9265 | 0.032712
PLACE | 50.479 | 3.1508 | 368.3903
ORO F | 49.3837 | 21.5628 | 155.9575
WYAND | 46.1001 | 2.7434 | 278.7406
BONNI | 45.9434 | 30.9016 | 58.7779
PINE | 45.714 | 12.2108 | 250.7398
STANI | 45.4193 | 17.9986 | 130.95
FORES | 44.1076 | 25.3197 | 94.9915
WASHI | 13.4438 | 13.4438 | 0.016194
DRUM | 25.0967 | 12.7697 | 18.8373
LOS G | 43.362 | 7.1816 | 180.4401
MIDDL | 42.9273 | 7.4276 | 156.6438
CHALL | 41.0501 | 28.8978 | 112.2874
WEST | 40.2233 | 16.5647 | 293.9265
TIGER | 10.0449 | 10.0449 | 3.8998
SCE R | 9.7937 | 9.7937 | 0.29161
BURNS | 11.7089 | 9.5881 | 1.664
PIKE | 39.3662 | 24.3107 | 43.9528
BIG T | 17.8776 | 9.036 | 16.1073
COLUM | 36.2974 | 20.8145 | 90.9452
CALIS | 35.5203 | 5.9455 | 115.6256
PUEBL | 35.1362 | 3.8638 | 123.5039
BIG B | 35.0163 | 4.3836 | 224.4524
CAMP | 34.1458 | 3.988 | 292.3495
MOLIN | 33.7736 | 9.3026 | 147.4025
WILLI | 32.1635 | 7.0749 | 231.7593
WHITM | 32.038 | 6.4449 | 92.5696
ALLEG | 31.4559 | 17.4071 | 79.4609
MONTE | 30.9824 | 10.9313 | 140.6161
RINCO | 29.2949 | 6.0431 | 73.2051
APPLE | 29.0916 | 7.203 | 487.2527
PARAD | 28.8939 | 6.0878 | 155.9722
MIRAB | 28.8258 | 5.7792 | 65.8017
SYCAM | 28.0273 | 5.6316 | 54.0595
SILVE | 27.494 | 6.2133 | 227.7736
OAKHU | 27.311 | 4.4668 | 233.0465
KANAK | 26.6692 | 11.7677 | 92.5364
VOLTA | 25.5745 | 6.3582 | 281.2137
SIERR | 4.262 | 4.262 | 0.018511
WOODS | 24.0717 | 4.5573 | 56.2907
BUCKS | 24.0095 | 7.091 | 60.7508
ELECT | 23.7964 | 2.3608 | 167.2425
MEADO | 3.5783 | 3.5783 | 0.20712
WOODA | 23.3871 | 7.493 | 68.9785
GARCI | 3.5484 | 3.4371 | 2.4735
AUBER | 21.8618 | 2.1784 | 371.2851
FULTO | 20.8046 | 4.3603 | 66.4878
SHING | 20.3908 | 3.2725 | 373.607
FORT | 18.3292 | 1.3047 | 314.6716
MOUNT | 18.2964 | 1.8661 | 224.6216
STELL | 17.8888 | 3.2557 | 37.0349
SPANI | 2.9343 | 2.9343 | 7.9163
FITCH | 17.8255 | 3.4693 | 74.4456
SAN R | 17.4483 | 1.1936 | 128.6183
KONOC | 17.0951 | 2.8165 | 140.5019
DIAMO | 16.1444 | 1.0971 | 337.6856
HALF | 15.668 | 1.0736 | 175.9729
CURTI | 15.6252 | 1.176 | 480.8712
DUNBA | 14.3001 | 2.5414 | 119.4031
SHEPH | 2.2604 | 2.2604 | 19.9144
PENNG | 4.2653 | 2.1875 | 19.2167
CLARK | 13.6054 | 1.3524 | 234.4067
RESEA | 3.7919 | 2.1589 | 1.2814
WILLO | 13.3065 | 3.0794 | 142.1073
ALTO | 13.1255 | 1.6421 | 81.078
WEIME | 2.0183 | 2.0183 | 0.15676
MORGA | 13.0233 | 0.79246 | 109.4127
VINEY | 8.7379 | 1.9151 | 10.7648
EAST | 4.5718 | 1.8775 | 3.7247
HIGHL | 12.9592 | 1.2019 | 159.4303
SHADY | 12.6776 | 4.854 | 80.7269
MENDO | 12.6646 | 2.553 | 40.8852
REDBU | 12.4782 | 1.5385 | 75.138
PAUL | 12.3809 | 1.5752 | 83.5421
OAKLA | 11.9989 | 1.202 | 88.1874
BELLE | 11.7473 | 3.1026 | 28.7757
PINEC | 1.9469 | 1.5849 | 1.957
POINT | 11.7089 | 1.8282 | 105.3245
GRASS | 11.1047 | 1.3785 | 103.5142
BEAR | 10.8965 | 0.72222 | 241.5472
CABRI | 9.9744 | 1.1611 | 84.1301
LAS G | 11.3927 | 1.4573 | 18.3609
CALPI | 9.7937 | 3.085 | 37.4263
ROSSM | 9.7653 | 0.91214 | 29.951
CLAYT | 9.6421 | 1.4983 | 59.8621
MONRO | 3.6239 | 1.2686 | 2.1875
OTTER | 9.4134 | 1.0219 | 78.1108
MORAG | 9.4021 | 1.8473 | 51.6926
ROB R | 9.3933 | 0.66388 | 144.4741
BEN L | 9.1195 | 3.6857 | 36.5295
ATASC | 8.8937 | 1.0584 | 141.8638
COARS | 8.6723 | 0.78213 | 411.422
GARBE | 8.4333 | 1.1355 | 210.6698
SARAT | 8.429 | 0.60557 | 65.233
CORRA | 8.2388 | 1.5046 | 194.7629
ANNAP | 7.8886 | 2.0299 | 51.2424
OLEMA | 7.8017 | 1.6276 | 61.001
CASTR | 6.6796 | 1.0079 | 54.5012
BRIDG | 6.6593 | 2.4181 | 55.8858
TEMPL | 6.435 | 0.69658 | 377.6858
SANTA | 6.4225 | 1.0461 | 207.5606
FRUIT | 5.3172 | 1.1812 | 83.4241
PHILO | 5.1995 | 0.69963 | 160.9847
PETAL | 5.1384 | 0.98177 | 121.4738
BERKE | 4.67 | 0.95557 | 4.1144
RACET | 5.0145 | 0.84132 | 101.8346
HOOPA | 4.9741 | 0.65196 | 103.3689
LOW G | 4.8093 | 2.0759 | 71.107
TASSA | 4.8049 | 1.0844 | 25.1602
ANITA | 0.84484 | 0.84484 | 0.115
SALMO | 4.7981 | 1.2271 | 26.7666
LAYTO | 4.62 | 1.7062 | 162.3136
MESA | 4.6108 | 0.72123 | 59.5665
WISE | 4.4121 | 0.91198 | 123.6041
GIRVA | 4.26 | 0.9218 | 149.8288
CRESC | 4.2473 | 1.9587 | 43.6463
BIG M | 4.1128 | 0.48445 | 57.1862
COTAT | 4.0407 | 0.99668 | 143.0492
BELL | 4.0106 | 0.71383 | 122.4657
HAMIL | 3.9575 | 0.73734 | 26.7473
CORTI | 0.6837 | 0.6837 | 1.036
MENLO | 3.7456 | 0.81103 | 67.0116
WHEAT | 0.67299 | 0.67299 | 9.9882
DESCH | 3.6179 | 0.50654 | 189.7161
HATTO | 3.5836 | 0.37983 | 25.5299
SONOM | 3.4319 | 0.46423 | 56.7951
ZACA | 3.4068 | 0.54055 | 83.6467
BASAL | 1.1636 | 0.58876 | 4.9877
SEACL | 1.4392 | 0.55686 | 9.5384
PASO | 3.3373 | 0.95669 | 77.1144
CORNI | 3.1042 | 0.5264 | 131.4673
COTTO | 3.0669 | 0.67454 | 255.9289
CLOVE | 3.0559 | 0.38027 | 105.0157
NAPA | 1.0072 | 0.51678 | 17.6226
JESSU | 2.9417 | 0.46886 | 119.7612
PENRY | 2.9333 | 0.53803 | 145.6861
LAKEV | 1.6557 | 0.4957 | 20.015
TIVY | 2.8963 | 0.54574 | 118.6456
LAURE | 2.471 | 0.3964 | 134.0382
VACA | 2.416 | 1.6197 | 26.9555
PACIF | 2.1021 | 0.44884 | 13.0641
OCEAN | 2.3277 | 0.31897 | 130.97
PUTAH | 2.2639 | 0.92151 | 31.2115
OILFI | 2.2153 | 0.2461 | 115.2449
SAN L | 2.0859 | 0.12938 | 173.408
NORTH | 2.045 | 0.38751 | 82.4892
VACAV | 1.9532 | 0.60096 | 56.5557
TAMAR | 0.38292 | 0.38292 | 16.4477
RED B | 1.7969 | 0.27999 | 146.771
BUELL | 1.7718 | 0.38615 | 93.4019
ELK C | 1.6829 | 0.32795 | 82.7232
GREEN | 1.6346 | 0.18081 | 55.5277
GABIL | 0.7991 | 0.3284 | 6.4622
MERCE | 1.585 | 0.27641 | 120.7817
FREMO | 0.64033 | 0.32292 | 2.6857
TAR F | 1.2311 | 0.32211 | 9.0078
UKIAH | 1.4188 | 0.15527 | 98.3542
PEABO | 0.80125 | 0.3092 | 3.0716
RESER | 1.4058 | 0.24888 | 39.5739
INDIA | 0.58642 | 0.28409 | 16.7358
SAND | 1.4014 | 0.19821 | 149.2192
GUALA | 1.3517 | 0.17514 | 81.9308
MADIS | 1.2706 | 0.26579 | 7.647
DEL M | 1.2644 | 0.16217 | 75.6419
FLINT | 1.2249 | 0.25256 | 5.6839
ARBUC | 0.24977 | 0.24977 | 2.0417
PANOR | 1.1971 | 0.21687 | 43.8734
STAFF | 1.1617 | 0.39549 | 28.9258
GONZA | 0.92235 | 0.24414 | 5.5052
IGNAC | 1.6637 | 0.24185 | 12.4082
MONTI | 1.1518 | 0.29684 | 109.7815
CLEAR | 0.78881 | 0.23395 | 21.8965
JARVI | 0.54812 | 0.2237 | 3.8367
HICKS | 1.1412 | 0.18188 | 32.772
LINCO | 1.1219 | 0.5075 | 51.2867
VALLE | 1.2081 | 0.19522 | 14.319
LAKEW | 0.63414 | 0.19342 | 9.2058
GANSN | 1.1048 | 0.42531 | 38.7574
FROGT | 1.0887 | 0.11554 | 308.6049
OLETA | 1.0679 | 0.25949 | 147.7517
FOOTH | 1.061 | 0.34011 | 28.0857
PEORI | 1.0321 | 0.12835 | 204.5462
BOLIN | 0.94457 | 0.18508 | 36.2161
HORSE | 0.55294 | 0.17025 | 7.4678
NARRO | 0.90585 | 0.13643 | 334.7252
UPPER | 0.87287 | 0.18044 | 53.0863
DUNLA | 0.84147 | 0.10815 | 126.5617
GOLDT | 0.31985 | 0.14927 | 10.7884
GEYSE | 0.77452 | 0.15645 | 123.3345
SAUSA | 0.76987 | 0.14322 | 9.2313
EL CE | 0.76268 | 0.11187 | 26.8925
SPAUL | 0.13582 | 0.13582 | 20.1063
SCE V | 0.13022 | 0.13022 | 0.17032
SAN J | 0.75797 | 0.23397 | 212.4959
JAMES | 0.75514 | 0.34552 | 30.6214
VASCO | 0.73217 | 0.40819 | 41.9238
HALSE | 0.68906 | 0.10182 | 130.4913
WILDW | 0.68153 | 0.1784 | 32.6037
MILPI | 0.64865 | 0.11779 | 29.7328
HIGGI | 0.62642 | 0.069758 | 355.1528
MARTE | 0.6193 | 0.099853 | 102.5301
OREGO | 0.57952 | 0.094162 | 205.4074
HARTL | 0.57017 | 0.11386 | 32.5313
ANDER | 0.45678 | 0.10329 | 15.6797
EEL R | 0.42884 | 0.10027 | 41.3357
SUNOL | 0.39615 | 0.08017 | 34.5067
VIEJO | 0.37005 | 0.049487 | 37.5091
HOPLA | 0.36545 | 0.063539 | 82.4026
WOODW | 0.3371 | 0.12992 | 30.1544
BRYAN | 0.094086 | 0.094086 | 1.2282
FELTO | 0.093336 | 0.093336 | 2.2987
LLAGA | 0.31885 | 0.1023 | 31.2751
SAN M | 0.312 | 0.070622 | 63.6742
KESWI | 0.26099 | 0.14566 | 50.8481
SAN B | 0.24643 | 0.085872 | 32.6485
SISQU | 0.21174 | 0.11917 | 76.2489
WISHO | 0.074616 | 0.074616 | 7.7822
CAYET | 0.20657 | 0.050257 | 40.9085
BIG R | 0.19578 | 0.042524 | 71.4583
NEWBU | 0.15433 | 0.065865 | 12.6411
PERRY | 0.19088 | 0.041903 | 67.3591
GRAYS | 0.063148 | 0.063148 | 10.7057
MAPLE | 0.059846 | 0.059846 | 9.8748
KING | 0.058354 | 0.058354 | 17.5881
ECHO | 0.13221 | 0.05551 | 6.1677
CEDAR | 0.18445 | 0.09302 | 110.9
PURIS | 0.2429 | 0.052947 | 15.9907
CENTE | 0.182 | 0.11858 | 36.3928
DOBBI | 0.17584 | 0.081719 | 80.2916
NOTRE | 0.15694 | 0.090232 | 27.4274
ELK 1 | 0.15006 | 0.034574 | 76.2893
STILL | 0.10603 | 0.055269 | 112.7347
BANGO | 0.10317 | 0.051716 | 197.9775
SCE T | 0.045873 | 0.045873 | 1.4276
SO. C | 0.051431 | 0.045066 | 7.6021
CALAV | 0.10314 | 0.051424 | 190.5291
RIO D | 0.10074 | 0.032551 | 50.4197
SWIFT | 0.084233 | 0.041268 | 86.312
ANTLE | 0.08259 | 0.051689 | 60.0715
EMERA | 0.11416 | 0.041806 | 23.5053
CALPE | 0.080296 | 0.03754 | 77.8529
WEIMA | 0.080042 | 0.044137 | 97.3379
POTTE | 0.078348 | 0.024921 | 52.216
LUCER | 0.076393 | 0.028606 | 67.2011
ORIND | 0.052555 | 0.037519 | 9.3864
TYLER | 0.075876 | 0.048229 | 60.5727
PALO | 0.035354 | 0.035354 | 4.7078
BOGAR | 0.03523 | 0.03523 | 0.51623
MORRO | 0.073801 | 0.017428 | 27.7406
HARRI | 0.086853 | 0.033929 | 15.6123
ALHAM | 0.072547 | 0.020511 | 37.6776
BALCH | 0.035267 | 0.032761 | 14.6983
SMART | 0.032648 | 0.032648 | 15.8868
SOBRA | 0.067265 | 0.038352 | 47.1251
PANOC | 0.064167 | 0.036102 | 45.8174
ARCAT | 0.061973 | 0.030417 | 27.1745
CLAY | 0.059218 | 0.023246 | 76.7687
LOS O | 0.057419 | 0.030484 | 47.1268
FRENC | 0.057283 | 0.042846 | 41.2147
PALME | 0.05552 | 0.032869 | 37.0218
POSO | 0.052745 | 0.02291 | 79.1649
TRIDA | 0.028512 | 0.028512 | 0.050313
CAYUC | 0.079048 | 0.027833 | 15.9947
CHOLA | 0.049821 | 0.037547 | 58.4006
PIERC | 0.026979 | 0.026979 | 14.4387
SNEAT | 0.20826 | 0.025168 | 6.4439
CHEST | 0.047498 | 0.025066 | 4.9789
PIT N | 0.049074 | 0.031804 | 98.6549
BURNE | 0.048736 | 0.027573 | 52.216
KIRKE | 0.024306 | 0.024306 | 5.4258
BRENT | 0.042733 | 0.02412 | 9.8403
MC KE | 0.059287 | 0.024055 | 14.9596
RADUM | 0.023926 | 0.023926 | 2.1702
CARLO | 0.041044 | 0.023536 | 21.1982
SPENC | 0.0298 | 0.023484 | 12.0662
CAL W | 0.023426 | 0.023426 | 2.9688
BROWN | 0.046288 | 0.031865 | 37.7491
HOLLI | 0.044317 | 0.019951 | 103.1161
TEJON | 0.043014 | 0.032479 | 34.9641
IONE | 0.034177 | 0.020761 | 15.6336
JOLON | 0.042992 | 0.024341 | 81.1155
KERCK | 0.039955 | 0.031638 | 34.5924
LOGAN | 0.020313 | 0.020313 | 3.7103
CUYAM | 0.02009 | 0.02009 | 2.3769
SPRUC | 0.02375 | 0.020061 | 6.028
CAMBR | 0.039572 | 0.021739 | 44.7655
SUMMI | 0.037786 | 0.019902 | 13.9092
BAY M | 0.026024 | 0.01936 | 4.2519
LONE | 0.019234 | 0.019234 | 9.5646
GLENN | 0.01909 | 0.01909 | 2.3498
EDES | 0.036955 | 0.018828 | 15.8364
RISIN | 0.033124 | 0.020465 | 46.3641
CAMPH | 0.018555 | 0.018555 | 1.4665
MAXWE | 0.018513 | 0.018513 | 1.6684
OAK 0 | 0.018493 | 0.018493 | 4.3198
TRES | 0.018321 | 0.018321 | 0.10269
LAMON | 0.018222 | 0.018222 | 0.50063
LAS P | 0.030304 | 0.01801 | 7.411
RAWSO | 0.017954 | 0.017954 | 2.3781
TULE | 0.01789 | 0.01789 | 4.0927
TOCAL | 0.017781 | 0.017781 | 0.031239
RALST | 0.025196 | 0.017612 | 11.9066
COVEL | 0.024981 | 0.017548 | 9.9189
SOLED | 0.029952 | 0.016165 | 31.1065
LOS M | 0.017254 | 0.017254 | 0.1275
RIDGE | 0.02026 | 0.017172 | 4.3294
CMC 1 | 0.021532 | 0.017114 | 2.5236
MC AR | 0.025754 | 0.018742 | 69.8489
REEDL | 0.028512 | 0.016006 | 1.9056
EDENV | 0.019259 | 0.015925 | 0.76864
LAS A | 0.018243 | 0.015886 | 5.9862
ANTEL | 0.014633 | 0.014633 | 0.75322
CAROL | 0.033705 | 0.014579 | 3.9545
TULUC | 0.014345 | 0.014345 | 4.4167
AUBUR | 0.017498 | 0.013515 | 5.3983
CORON | 0.013274 | 0.013274 | 0.968
COPPE | 0.013252 | 0.013252 | 8.1519
NOVAT | 0.016828 | 0.01279 | 4.2213
SAN C | 0.021835 | 0.012777 | 12.3718
FAIRV | 0.027316 | 0.012769 | 18.7684
SAN A | 0.014985 | 0.012181 | 2.6646
HUMBO | 0.012021 | 0.012021 | 7.0458
BUTTE | 0.011878 | 0.011878 | 1.8432
OROSI | 0.010989 | 0.010989 | 0.26307
WESTL | 0.010946 | 0.010946 | 0.92376
HOLLY | 0.010899 | 0.010899 | 2.9599
LOYOL | 0.010852 | 0.010852 | 0.10967
DIVID | 0.010844 | 0.010844 | 2.2423
FLORE | 0.012695 | 0.010783 | 1.7158
PRUNE | 0.010696 | 0.010696 | 0.046537
DOLAN | 0.010669 | 0.010661 | 3.8209
KERN | 0.012298 | 0.010465 | 1.5124
COAST | 0.012695 | 0.010335 | 1.6617
BELMO | 0.011413 | 0.010046 | 1.5331
TIDEW | 0.013929 | 0.010008 | 8.1253
STONE | 0.012359 | 0.0097622 | 5.2348
FRANK | 0.015101 | 0.0097423 | 7.2013
LOS C | 0.009461 | 0.009461 | 2.6219
WALDO | 0.010847 | 0.0089946 | 4.7327
BAYWO | 0.008459 | 0.008459 | 1.4233
WOOD | 0.0082741 | 0.0082741 | 0.4018
FAIRM | 0.0082593 | 0.0082593 | 1.4849
BERES | 0.0094751 | 0.0081297 | 4.1458
ESTUD | 0.0067781 | 0.0067781 | 0.69789
OROVI | 0.0064634 | 0.0064634 | 0.2392
BANCR | 0.0060178 | 0.0060178 | 1.0716
ARLIN | 0.005806 | 0.005806 | 0.76473
CARME | 0.0058032 | 0.005572 | 0.64512
BOSTO | 0.0051828 | 0.0051828 | 0.44969
VASON | 0.0047187 | 0.0047187 | 0.06716

## REFCL + SH
Sub | Max of Fire Risk | Average of Fire Risk | Sum of Tier 2/3 OH Miles | Exposure (Avg Risk * Miles) | NOTES
BRUNSWICK | 60.8822 | 12.5617 | 488.4002 | 6135.1544 | 2 bank
EL DORADO PH | 70.5639 | 26.3829 | 190.5389 | 5026.9757 | 21kv, 2 bank
WEST POINT | 40.2233 | 16.5647 | 293.9265 | 4868.8037 | 2 bank
MIWUK | 81.7128 | 23.2111 | 152.9141 | 3549.3066 | 17kv
APPLE HILL | 29.0916 | 7.203 | 487.2527 | 3509.6702 | 12 and 21kv bks – 3wire 21kv.
ORO FINO | 49.3837 | 21.5628 | 155.9575 | 3362.8734
CHALLENGE | 41.0501 | 28.8978 | 112.2874 | 3244.861
PINE GROVE | 45.714 | 12.2108 | 250.7398 | 3061.7314 | 2 bank
FORESTHILL | 44.1076 | 25.3197 | 94.9915 | 2405.1537
STANISLAUS | 45.4193 | 17.9986 | 130.95 | 2356.9182 | 17kv
COLUMBIA HILL | 36.2974 | 20.8145 | 90.9452 | 1892.9817
BONNIE NOOK | 45.9434 | 30.9016 | 58.7779 | 1816.3331
VOLTA | 25.5745 | 6.3582 | 281.2137 | 1788.0078
WILLITS | 32.1635 | 7.0749 | 231.7593 | 1639.6785
MONTE RIO | 30.9824 | 10.9313 | 140.6161 | 1537.12 | 2 bank
SILVERADO | 27.494 | 6.2133 | 227.7736 | 1415.2324 | 21kv 4-wire
ALLEGHANY | 31.4559 | 17.4071 | 79.4609 | 1383.1838
MOLINA | 33.7736 | 9.3026 | 147.4025 | 1371.2237 | 2 bank
LOS GATOS | 43.362 | 7.1816 | 180.4401 | 1295.854 | 2 bank
MIDDLETOWN | 42.9273 | 7.4276 | 156.6438 | 1163.4831
KANAKA | 26.6692 | 11.7677 | 92.5364 | 1088.9421
PIKE CITY | 39.3662 | 24.3107 | 43.9528 | 1068.5224
SALT SPRINGS | 63.7309 | 14.5484 | 68.8309 | 1001.3769 | 12kv next to sub, 21kv 3-wire from sub – 20+ miles of cable from sub to hwy4 Cabbage Patch -autotransformers 21/17kv, 17/12kv at Alpine sub.
PARADISE | 28.8939 | 6.0878 | 155.9722 | 949.5347
CALISTOGA | 35.5203 | 5.9455 | 115.6256 | 687.4536
SPRING GAP | 67.2336 | 15.5648 | 41.0705 | 639.2556 | 17kv
WHITMORE | 32.038 | 6.4449 | 92.5696 | 596.6014
WOODACRE | 23.3871 | 7.493 | 68.9785 | 516.8581
RINCON | 29.2949 | 6.0431 | 73.2051 | 442.3884 | 2 bank
BUCKS CREEK | 24.0095 | 7.091 | 60.7508 | 430.7855
MIRABEL | 28.8258 | 5.7792 | 65.8017 | 380.2789
SYCAMORE CREEK | 28.0273 | 5.6316 | 54.0595 | 304.4413