## No Egress
Dx Prioritization Output - System Hardening | [5 empty] | Planned 2019 implementation
Circuit Information |  |  |  | Independent Variables | [5 empty] | Dependent Variable | Risk Scoring |  |  |  |  | Risk Tiers
Protection Zone | Feeder Name | District | Tier 2/3 OH Miles | Env Risk Component | Material A - % of total miles | Vegetation Outages | Company Outages | HFTD Miles per Total Miles | Tier 3 per HFTD Miles | Ignition Indicator (1+ ignition occurred) | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Consolidated Risk Score | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Rank Cons Risk | Rank P*C | P*C | Total Risk
MIWUK 170110600 | MIWUK 1701 | YOSEMITE | 10.9092 | 90.0653 | 100% | 20 | 16 | 100% | 100% | 1 | 0.80002 | 102.1389 | 3.3891 | 276.9352 | High | High | High | 1 | 1 | 81.7128 | 8926.3013 | 100%
EL DORADO PH 210119752 | EL DORADO PH 2101 | SIERRA | 38.577 | 80.8747 | 99.99% | 20 | 11 | 100% | 99.16% | 1 | 0.69086 | 102.1389 | 1.6995 | 119.922 | High | High | Low | 13 | 2 | 70.5639 | 8844.5886 | 99.08%
SPRING GAP 17029690 | SPRING GAP 1702 | YOSEMITE | 17.3345 | 90.5752 | 98.76% | 12 | 12 | 100% | 100% | 0 | 0.65826 | 102.1389 | 0.67026 | 45.0638 | High | High | Low | 172 | 3 | 67.2336 | 8774.0246 | 98.29%
MIWUK 1701CB | MIWUK 1701 | YOSEMITE | 17.9054 | 91.659 | 81.59% | 16 | 15 | 100% | 100% | 0 | 0.65411 | 102.1389 | 2.9532 | 197.3013 | High | High | Medium | 2 | 4 | 66.8104 | 8706.791 | 97.54%
SALT SPRINGS 21023142 | SALT SPRINGS 2102 | STOCKTON | 16.894 | 90.205 | 100% | 15 | 9 | 100% | 100% | 0 | 0.62396 | 102.1389 | 2.0116 | 128.2018 | High | High | Low | 8 | 5 | 63.7309 | 8639.9806 | 96.79%
BRUNSWICK 11021010 | BRUNSWICK 1102 | SIERRA | 44.041 | 87.3695 | 84.93% | 12 | 13 | 100% | 98.91% | 0 | 0.59607 | 102.1389 | 2.1263 | 129.4525 | High | High | Low | 6 | 6 | 60.8822 | 8576.2497 | 96.08%
BRUNSWICK 110532536 | BRUNSWICK 1105 | SIERRA | 21.7333 | 94.8632 | 99.08% | 11 | 14 | 100% | 100% | 0 | 0.54536 | 102.1389 | 2.2664 | 126.2441 | High | High | Medium | 9 | 7 | 55.7026 | 8515.3675 | 95.4%
BRUNSWICK 110350070 | BRUNSWICK 1103 | SIERRA | 28.1191 | 94.0552 | 99.83% | 13 | 12 | 100% | 100% | 1 | 0.54169 | 102.1389 | 2.325 | 128.6353 | High | High | Medium | 7 | 8 | 55.3273 | 8459.6649 | 94.77%
BRUNSWICK 11052210 | BRUNSWICK 1105 | SIERRA | 22.8031 | 97.1876 | 99.8% | 8 | 12 | 100% | 100% | 0 | 0.53048 | 102.1389 | 1.9441 | 105.3388 | High | High | Low | 21 | 9 | 54.1827 | 8404.3376 | 94.15%
EL DORADO PH 21016852 | EL DORADO PH 2101 | SIERRA | 25.3514 | 89.3624 | 96.21% | 18 | 8 | 100% | 100% | 0 | 0.52183 | 102.1389 | 2.0051 | 106.8716 | High | High | Low | 18 | 10 | 53.299 | 8350.1549 | 93.55%
MARIPOSA 210110170 | MARIPOSA 2101 | YOSEMITE | 16.3113 | 93.2169 | 77.6% | 14 | 34 | 100% | 100% | 1 | 0.51304 | 102.1389 | 1.5869 | 83.1571 | High | High | Low | 44 | 11 | 52.4012 | 8296.8559 | 92.95%
BRUNSWICK 11052140 | BRUNSWICK 1105 | SIERRA | 34.5645 | 95.4853 | 99.76% | 25 | 10 | 100% | 100% | 0 | 0.50651 | 102.1389 | 1.9239 | 99.5327 | High | High | Low | 22 | 12 | 51.7342 | 8244.4547 | 92.36%
PLACERVILLE 21061104 | PLACERVILLE 2106 | SIERRA | 50.3628 | 96.0676 | 90.37% | 13 | 6 | 100% | 100% | 1 | 0.49422 | 102.1389 | 2.2151 | 111.8183 | High | High | Low | 16 | 13 | 50.479 | 8192.7205 | 91.78%
ORO FINO 1101CB | ORO FINO 1101 | NORTH VALLEY | 22.1887 | 87.2953 | 86.14% | 9 | 11 | 100% | 100% | 0 | 0.48349 | 102.1389 | 3.5195 | 173.8066 | High | High | High | 3 | 14 | 49.3837 | 8142.2415 | 91.22%
EL DORADO PH 210126000 | EL DORADO PH 2101 | SIERRA | 34.0468 | 93.5067 | 99.32% | 9 | 8 | 100% | 100% | 0 | 0.57184 | 85.4511 | 1.4969 | 73.1469 | High | High | Low | 67 | 15 | 48.8647 | 8092.8578 | 90.66%
WYANDOTTE 11031974 | WYANDOTTE 1103 | NORTH VALLEY | 22.8741 | 92.9076 | 99.55% | 6 | 6 | 100% | 100% | 1 | 0.45135 | 102.1389 | 2.7281 | 125.7679 | High | High | Medium | 11 | 16 | 46.1001 | 8043.9931 | 90.12%
BONNIE NOOK 1102CB | BONNIE NOOK 1102 | SIERRA | 34.3352 | 94.488 | 85.18% | 18 | 16 | 100% | 100% | 0 | 0.44981 | 102.1389 | 1.5484 | 71.1385 | High | High | Low | 71 | 17 | 45.9434 | 7997.893 | 89.6%
PINE GROVE 110245292 | PINE GROVE 1102 | STOCKTON | 10.8778 | 85.9329 | 100% | 1 | 11 | 100% | 99.38% | 0 | 0.44757 | 102.1389 | 2.8406 | 129.855 | High | High | Medium | 5 | 18 | 45.714 | 7951.9496 | 89.08%
STANISLAUS 17021888 | STANISLAUS 1702 | YOSEMITE | 18.9533 | 77.9476 | 99.71% | 9 | 14 | 100% | 100% | 0 | 0.44468 | 102.1389 | 2.9998 | 136.2467 | High | High | Medium | 4 | 19 | 45.4193 | 7906.2355 | 88.57%
FORESTHILL 110150486 | FORESTHILL 1101 | SIERRA | 11.6566 | 81.112 | 97.86% | 4 | 8 | 100% | 100% | 0 | 0.43184 | 102.1389 | 1.9713 | 86.9475 | High | High | Low | 42 | 20 | 44.1076 | 7860.8162 | 88.06%
LOS GATOS 110760114 | LOS GATOS 1107 | DE ANZA | 24.3274 | 75.5493 | 92.99% | 9 | 3 | 100% | 100% | 1 | 0.66312 | 65.3912 | 2.5859 | 112.1303 | High | High | Medium | 15 | 21 | 43.362 | 7816.7086 | 87.57%
MIDDLETOWN 1101548 | MIDDLETOWN 1101 | HUMBOLDT | 22.1669 | 84.1532 | 73.95% | 13 | 16 | 88.6% | 97.32% | 1 | 0.42028 | 102.1389 | 2.2085 | 94.8039 | High | High | Low | 30 | 22 | 42.9273 | 7773.3466 | 87.08%
MIWUK 17018060 | MIWUK 1701 | YOSEMITE | 11.8537 | 93.2164 | 72.89% | 5 | 17 | 100% | 100% | 0 | 0.41847 | 102.1389 | 2.916 | 124.6332 | High | High | Medium | 12 | 23 | 42.7418 | 7730.4193 | 86.6%
BRUNSWICK 110651486 | BRUNSWICK 1106 | SIERRA | 56.6992 | 84.1552 | 88.14% | 22 | 15 | 100% | 87.68% | 1 | 0.49605 | 85.4511 | 2.1451 | 90.9285 | High | High | Low | 35 | 24 | 42.3883 | 7687.6774 | 86.12%
CHALLENGE 1102CB | CHALLENGE 1102 | NORTH VALLEY | 15.5217 | 96.52 | 90.77% | 6 | 5 | 100% | 100% | 0 | 0.4019 | 102.1389 | 1.7913 | 73.5318 | High | High | Low | 65 | 25 | 41.0501 | 7645.2891 | 85.65%
FORESTHILL 11011802 | FORESTHILL 1101 | SIERRA | 22.1758 | 72.9192 | 91.83% | 12 | 21 | 100% | 100% | 0 | 0.40081 | 102.1389 | 2.3329 | 95.5024 | High | High | Medium | 29 | 26 | 40.9378 | 7604.239 | 85.19%
WEST POINT 110136674 | WEST POINT 1101 | STOCKTON | 9.4896 | 86.8002 | 98.6% | 2 | 6 | 100% | 100% | 0 | 0.39381 | 102.1389 | 2.2058 | 88.7227 | High | High | Low | 38 | 27 | 40.2233 | 7563.3012 | 84.73%
PIKE CITY 1101CB | PIKE CITY 1101 | SIERRA | 19.8554 | 96.0592 | 99.76% | 13 | 13 | 100% | 100% | 1 | 0.38542 | 102.1389 | 1.982 | 78.0243 | High | High | Low | 56 | 28 | 39.3662 | 7523.0779 | 84.28%
STANISLAUS 17021804 | STANISLAUS 1702 | YOSEMITE | 8.3693 | 84.6121 | 100% | 9 | 6 | 100% | 100% | 0 | 0.38328 | 102.1389 | 2.7274 | 106.7718 | High | High | Medium | 19 | 29 | 39.1474 | 7483.7117 | 83.84%
PINE GROVE 110213438 | PINE GROVE 1102 | STOCKTON | 16.4176 | 84.6476 | 100% | 6 | 6 | 100% | 85.87% | 0 | 0.38268 | 102.1389 | 2.1023 | 82.1729 | High | High | Low | 49 | 30 | 39.087 | 7444.5643 | 83.4%
CHALLENGE 1101CB | CHALLENGE 1101 | NORTH VALLEY | 16.6203 | 96.135 | 99.73% | 4 | 3 | 100% | 100% | 0 | 0.37094 | 102.1389 | 2.1782 | 82.5265 | High | High | Low | 47 | 31 | 37.8874 | 7405.4772 | 82.96%
WEST POINT 11014706 | WEST POINT 1101 | STOCKTON | 11.5214 | 90.5528 | 100% | 4 | 4 | 100% | 100% | 0 | 0.36745 | 102.1389 | 2.5195 | 94.5581 | High | High | Medium | 31 | 32 | 37.5307 | 7367.5898 | 82.54%
ORO FINO 110276008 | ORO FINO 1102 | NORTH VALLEY | 15.9665 | 80.1873 | 99.98% | 4 | 7 | 100% | 100% | 1 | 0.36557 | 102.1389 | 2.5923 | 96.7928 | High | High | Medium | 27 | 33 | 37.3387 | 7330.0591 | 82.12%
WYANDOTTE 11031976 | WYANDOTTE 1103 | NORTH VALLEY | 23.9896 | 86.4323 | 100% | 4 | 6 | 100% | 100% | 0 | 0.43481 | 85.4511 | 2.2058 | 81.9573 | High | High | Low | 51 | 34 | 37.155 | 7292.7204 | 81.7%
ORO FINO 11012022 | ORO FINO 1101 | NORTH VALLEY | 24.1719 | 81.0032 | 94.33% | 6 | 13 | 100% | 100% | 1 | 0.36043 | 102.1389 | 3.4228 | 126.0056 | High | High | High | 10 | 35 | 36.814 | 7255.5655 | 81.28%
PINE GROVE 11021222 | PINE GROVE 1102 | STOCKTON | 17.2284 | 80.3851 | 88.79% | 6 | 14 | 100% | 93.15% | 0 | 0.35881 | 102.1389 | 2.8894 | 105.8932 | High | High | Medium | 20 | 36 | 36.6489 | 7218.7515 | 80.87%
COLUMBIA HILL 11012212 | COLUMBIA HILL 1101 | SIERRA | 9.1875 | 95.8225 | 100% | 9 | 3 | 100% | 100% | 0 | 0.35537 | 102.1389 | 1.1517 | 41.805 | High | High | Low | 198 | 37 | 36.2974 | 7182.1026 | 80.46%
CALISTOGA 1101736 | CALISTOGA 1101 | NORTH BAY | 33.5094 | 79.1543 | 66.69% | 16 | 14 | 100% | 100% | 1 | 0.74565 | 47.6367 | 2.7749 | 98.5658 | High | High | Medium | 24 | 38 | 35.5203 | 7145.8052 | 80.05%
SALT SPRINGS 21024796 | SALT SPRINGS 2102 | STOCKTON | 7.1845 | 85.6584 | 100% | 4 | 1 | 100% | 100% | 0 | 0.34533 | 102.1389 | 1.4356 | 50.6348 | High | High | Low | 133 | 39 | 35.2718 | 7110.2849 | 79.66%
PUEBLO 2102792 | PUEBLO 2102 | NORTH BAY | 17.9619 | 85.883 | 96.12% | 13 | 4 | 86.21% | 100% | 0 | 0.41118 | 85.4511 | 2.4971 | 87.7383 | High | High | Medium | 40 | 40 | 35.1362 | 7075.0131 | 79.26%
BIG BEND 11021972 | BIG BEND 1102 | NORTH VALLEY | 21.0549 | 95.6632 | 96.1% | 4 | 6 | 100% | 100% | 0 | 0.40978 | 85.4511 | 2.086 | 73.0443 | High | High | Low | 68 | 41 | 35.0163 | 7039.8769 | 78.87%
EL DORADO PH 210219562 | EL DORADO PH 2102 | SIERRA | 14.8519 | 89.5871 | 100% | 10 | 7 | 100% | 100% | 0 | 0.33748 | 102.1389 | 2.3227 | 80.0616 | High | High | Medium | 52 | 42 | 34.4696 | 7004.8606 | 78.47%
CHALLENGE 11021064 | CHALLENGE 1102 | NORTH VALLEY | 19.9876 | 84.0327 | 100% | 6 | 2 | 100% | 94.93% | 0 | 0.33496 | 102.1389 | 1.8763 | 64.191 | High | High | Low | 88 | 43 | 34.2124 | 6970.3909 | 78.09%
CAMP EVERS 21065020 | CAMP EVERS 2106 | CENTRAL COAST | 15.2094 | 69.3374 | 87.56% | 19 | 11 | 100% | 100% | 1 | 0.52218 | 65.3912 | 2.4231 | 82.7401 | High | High | Medium | 46 | 44 | 34.1458 | 6936.1785 | 77.7%
MOLINO 1102318 | MOLINO 1102 | SONOMA | 19.2803 | 89.5364 | 61.35% | 11 | 8 | 100% | 100% | 1 | 0.39524 | 85.4511 | 2.6124 | 88.2297 | High | High | Medium | 39 | 45 | 33.7736 | 6902.0328 | 77.32%
WEST POINT 110113444 | WEST POINT 1101 | STOCKTON | 16.633 | 82.1566 | 100% | 5 | 15 | 100% | 100% | 0 | 0.31924 | 102.1389 | 2.2583 | 73.6364 | High | High | Medium | 63 | 46 | 32.6072 | 6868.2591 | 76.94%
EL DORADO PH 2101CB | EL DORADO PH 2101 | SIERRA | 16.7983 | 90.3781 | 74.43% | 12 | 5 | 100% | 100% | 0 | 0.3182 | 102.1389 | 2.1319 | 69.2868 | High | High | Low | 76 | 47 | 32.5001 | 6835.6519 | 76.58%
CAMP EVERS 210660124 | CAMP EVERS 2106 | CENTRAL COAST | 22.5394 | 63.6568 | 80.34% | 20 | 3 | 100% | 100% | 1 | 0.4923 | 65.3912 | 2.4068 | 77.4809 | High | High | Medium | 57 | 48 | 32.1923 | 6803.1518 | 76.21%
WILLITS 110434008 | WILLITS 1104 | HUMBOLDT | 22.9278 | 77.1143 | 100% | 14 | 12 | 100% | 97.76% | 0 | 0.3764 | 85.4511 | 2.5543 | 82.1564 | High | High | Medium | 50 | 49 | 32.1635 | 6770.9595 | 75.85%
WHITMORE 11011598 | WHITMORE 1101 | NORTH VALLEY | 33.6511 | 71.823 | 81.12% | 6 | 5 | 100% | 75.5% | 0 | 0.37493 | 85.4511 | 0.69773 | 22.3538 | High | High | Low | 344 | 50 | 32.038 | 6738.796 | 75.49%
CHALLENGE 11015460 | CHALLENGE 1101 | NORTH VALLEY | 11.8115 | 93.9312 | 100% | 4 | 4 | 100% | 100% | 0 | 0.31277 | 102.1389 | 1.2968 | 41.4261 | High | High | Low | 200 | 51 | 31.9457 | 6706.758 | 75.13%
EL DORADO PH 210219542 | EL DORADO PH 2102 | SIERRA | 9.4332 | 77.5631 | 77.77% | 6 | 4 | 100% | 100% | 0 | 0.31239 | 102.1389 | 2.74 | 87.4241 | High | High | Medium | 41 | 52 | 31.907 | 6674.8123 | 74.78%
ALLEGHANY 1102CB | ALLEGHANY 1102 | SIERRA | 18.0939 | 92.7974 | 39.16% | 4 | 24 | 100% | 100% | 1 | 0.48104 | 65.3912 | 1.4 | 44.0392 | High | High | Low | 183 | 53 | 31.4559 | 6642.9053 | 74.42%
COLUMBIA HILL 1101764 | COLUMBIA HILL 1101 | SIERRA | 14.8572 | 87.6214 | 100% | 5 | 10 | 100% | 100% | 1 | 0.36409 | 85.4511 | 1.8603 | 57.8773 | High | High | Low | 105 | 54 | 31.1119 | 6611.4494 | 74.07%
MONTE RIO 1113524 | MONTE RIO 1113 | SONOMA | 6.2702 | 72.7249 | 28.23% | 16 | 4 | 100% | 100% | 0 | 0.30334 | 102.1389 | 3.5196 | 109.0471 | High | High | High | 17 | 55 | 30.9824 | 6580.3375 | 73.72%
WEST POINT 1101L373 | WEST POINT 1101 | STOCKTON | 7.4413 | 94.6949 | 100% | 2 | 9 | 100% | 100% | 0 | 0.30215 | 102.1389 | 2.361 | 72.8632 | High | High | Medium | 69 | 56 | 30.8608 | 6549.3551 | 73.37%
STANISLAUS 170237276 | STANISLAUS 1702 | YOSEMITE | 11.7226 | 82.7291 | 100% | 8 | 9 | 100% | 100% | 0 | 0.30163 | 102.1389 | 2.8831 | 88.8242 | High | High | Medium | 37 | 57 | 30.8083 | 6518.4943 | 73.03%
BRUNSWICK 11052130 | BRUNSWICK 1105 | SIERRA | 14.272 | 96.3517 | 99.69% | 5 | 6 | 100% | 100% | 0 | 0.29909 | 102.1389 | 2.0794 | 63.5253 | High | High | Low | 90 | 58 | 30.5492 | 6487.686 | 72.68%
STANISLAUS 170275348 | STANISLAUS 1702 | YOSEMITE | 5.3962 | 93.3092 | 100% | 1 | 9 | 100% | 100% | 0 | 0.29738 | 102.1389 | 2.6132 | 79.3742 | High | High | Medium | 53 | 59 | 30.3738 | 6457.1368 | 72.34%
ALLEGHANY 1101VR816 | ALLEGHANY 1101 | SIERRA | 4.1512 | 96.2894 | 73.9% | 6 | 8 | 100% | 100% | 0 | 0.294 | 102.1389 | 2.6166 | 78.5756 | High | High | Medium | 55 | 60 | 30.0293 | 6426.763 | 72%
CHALLENGE 110198174 | CHALLENGE 1101 | NORTH VALLEY | 12.1176 | 88.3942 | 100% | 4 | 1 | 100% | 100% | 0 | 0.34958 | 85.4511 | 0.74174 | 22.157 | High | High | Low | 346 | 61 | 29.8716 | 6396.7337 | 71.66%
BIG BEND 1101CB | BIG BEND 1101 | NORTH VALLEY | 23.102 | 80.4105 | 77.16% | 7 | 10 | 100% | 100% | 1 | 0.34627 | 85.4511 | 2.2328 | 66.0668 | High | High | Medium | 81 | 62 | 29.5895 | 6366.8621 | 71.33%
BONNIE NOOK 1101CB | BONNIE NOOK 1101 | SIERRA | 14.7401 | 89.8232 | 47.01% | 8 | 12 | 100% | 100% | 0 | 0.28941 | 102.1389 | 1.4893 | 44.0242 | High | High | Low | 184 | 63 | 29.5604 | 6337.2726 | 71%
MIWUK 17026018 | MIWUK 1702 | YOSEMITE | 19.5117 | 86.3615 | 100% | 3 | 8 | 100% | 100% | 0 | 0.28867 | 102.1389 | 3.358 | 99.0086 | High | High | High | 23 | 64 | 29.4843 | 6307.7123 | 70.66%
MIWUK 1702CB | MIWUK 1702 | YOSEMITE | 10.2382 | 90.3115 | 82.25% | 5 | 6 | 100% | 100% | 0 | 0.28839 | 102.1389 | 3.3177 | 97.7246 | High | High | High | 25 | 65 | 29.4558 | 6278.228 | 70.33%
COLUMBIA HILL 110135424 | COLUMBIA HILL 1101 | SIERRA | 13.9113 | 71.6588 | 100% | 8 | 11 | 100% | 100% | 1 | 0.44882 | 65.3912 | 2.5252 | 74.113 | High | High | Medium | 62 | 66 | 29.3488 | 6248.7722 | 70%
RINCON 1103474 | RINCON 1103 | SONOMA | 18.561 | 87.2265 | 99.41% | 8 | 6 | 100% | 100% | 0 | 0.44799 | 65.3912 | 2.5873 | 75.7944 | High | High | Medium | 60 | 67 | 29.2949 | 6219.4234 | 69.68%
APPLE HILL 110497086 | APPLE HILL 1104 | SIERRA | 25.6232 | 83.1632 | 99.98% | 8 | 5 | 100% | 100% | 1 | 0.28482 | 102.1389 | 1.6526 | 48.0777 | High | High | Low | 148 | 68 | 29.0916 | 6190.1285 | 69.35%
PARADISE 11062084 | PARADISE 1106 | NORTH VALLEY | 11.3566 | 77.2193 | 100% | 4 | 9 | 100% | 100% | 1 | 0.28289 | 102.1389 | 4.0673 | 117.5206 | High | High | High | 14 | 69 | 28.8939 | 6161.0369 | 69.02%
MIRABEL 1101298 | MIRABEL 1101 | SONOMA | 12.8273 | 89.1513 | 37.51% | 16 | 9 | 99.59% | 100% | 0 | 0.33734 | 85.4511 | 2.9749 | 85.7551 | High | High | Medium | 43 | 70 | 28.8258 | 6132.143 | 68.7%
PIKE CITY 11011730 | PIKE CITY 1101 | SIERRA | 8.599 | 94.8581 | 99.91% | 4 | 2 | 100% | 100% | 0 | 0.33402 | 85.4511 | 1.6102 | 45.9608 | High | High | Low | 166 | 71 | 28.5428 | 6103.3172 | 68.37%
MONTE RIO 1112120 | MONTE RIO 1112 | SONOMA | 6.8692 | 90.5188 | 64.49% | 17 | 9 | 100% | 100% | 0 | 0.33336 | 85.4511 | 2.7822 | 79.2535 | High | High | Medium | 54 | 72 | 28.4857 | 6074.7744 | 68.05%
CALISTOGA 110143924 | CALISTOGA 1101 | NORTH BAY | 4.45 | 80.4513 | 94.31% | 6 | 6 | 47.81% | 100% | 0 | 0.32892 | 85.4511 | 3.2727 | 91.9855 | High | High | High | 34 | 73 | 28.1068 | 6046.2887 | 67.74%
BRUNSWICK 11041020 | BRUNSWICK 1104 | SIERRA | 28.7777 | 77.1 | 87.63% | 9 | 9 | 100% | 83.4% | 1 | 0.27484 | 102.1389 | 2.4581 | 69.005 | High | High | Medium | 77 | 74 | 28.0721 | 6018.1818 | 67.42%
SYCAMORE CREEK 11112268 | SYCAMORE CREEK 1111 | NORTH VALLEY | 22.2352 | 96.7379 | 99.96% | 3 | 8 | 100% | 99.53% | 1 | 0.2744 | 102.1389 | 2.495 | 69.9295 | High | High | Medium | 74 | 75 | 28.0273 | 5990.1097 | 67.11%
APPLE HILL 110413512 | APPLE HILL 1104 | SIERRA | 27.848 | 80.8375 | 86.09% | 15 | 14 | 89.98% | 77.01% | 0 | 0.27338 | 102.1389 | 2.12 | 59.1969 | High | High | Low | 99 | 76 | 27.9228 | 5962.0824 | 66.79%
COLUMBIA HILL 11018233 | COLUMBIA HILL 1101 | SIERRA | 5.0061 | 92.4069 | 99.94% | 1 | 3 | 100% | 100% | 0 | 0.27044 | 102.1389 | 1.5103 | 41.7175 | High | High | Low | 199 | 77 | 27.6227 | 5934.1596 | 66.48%
SILVERADO 2104632 | SILVERADO 2104 | NORTH BAY | 18.1239 | 77.5447 | 73.72% | 15 | 5 | 96.09% | 100% | 1 | 0.42045 | 65.3912 | 3.2929 | 90.5343 | High | High | High | 36 | 78 | 27.494 | 5906.5369 | 66.17%
MIWUK 170238218 | MIWUK 1702 | YOSEMITE | 10.8246 | 77.698 | 74.49% | 4 | 9 | 100% | 100% | 0 | 0.26818 | 102.1389 | 3.4335 | 94.0487 | High | High | High | 32 | 79 | 27.3914 | 5879.043 | 65.86%
OAKHURST 110310190 | OAKHURST 1103 | YOSEMITE | 11.5271 | 95.517 | 27.67% | 12 | 10 | 100% | 100% | 1 | 0.26739 | 102.1389 | 1.9347 | 52.8379 | High | High | Low | 123 | 80 | 27.311 | 5851.6516 | 65.56%
ORO FINO 11022560 | ORO FINO 1102 | NORTH VALLEY | 16.7196 | 97.5242 | 100% | 5 | 6 | 100% | 81.54% | 1 | 0.26733 | 102.1389 | 2.775 | 75.7698 | High | High | Medium | 61 | 81 | 27.3045 | 5824.3406 | 65.25%
ALLEGHANY 1101806 | ALLEGHANY 1101 | SIERRA | 11.8065 | 97.171 | 100% | 0 | 7 | 100% | 100% | 0 | 0.2646 | 102.1389 | 1.7958 | 48.5336 | High | High | Low | 143 | 82 | 27.0262 | 5797.0361 | 64.94%
LOS GATOS 110760118 | LOS GATOS 1107 | DE ANZA | 20.0923 | 57.6089 | 83.76% | 25 | 2 | 100% | 100% | 1 | 0.5667 | 47.6367 | 1.6789 | 45.3221 | High | High | Low | 169 | 83 | 26.9958 | 5770.0098 | 64.64%
KANAKA 110183288 | KANAKA 1101 | NORTH VALLEY | 17.5828 | 90.1927 | 100% | 7 | 4 | 100% | 100% | 0 | 0.26111 | 102.1389 | 2.1087 | 56.2379 | High | High | Low | 111 | 84 | 26.6692 | 5743.014 | 64.34%
MIWUK 17018050 | MIWUK 1701 | YOSEMITE | 12.1253 | 91.2725 | 97.35% | 8 | 4 | 100% | 100% | 1 | 0.26086 | 102.1389 | 3.1093 | 82.8459 | High | High | High | 45 | 85 | 26.6441 | 5716.3448 | 64.04%
FORESTHILL 11022106 | FORESTHILL 1102 | SIERRA | 28.0974 | 67.1045 | 99.85% | 8 | 14 | 100% | 71.38% | 1 | 0.26076 | 102.1389 | 1.936 | 51.5625 | High | High | Low | 130 | 86 | 26.6336 | 5689.7007 | 63.74%
PARADISE 11062234 | PARADISE 1106 | NORTH VALLEY | 8.8367 | 79.1592 | 100% | 3 | 8 | 100% | 100% | 0 | 0.30628 | 85.4511 | 3.6642 | 95.9005 | High | High | High | 28 | 87 | 26.1721 | 5663.0671 | 63.44%
ORO FINO 110265932 | ORO FINO 1102 | NORTH VALLEY | 4.3114 | 96.8708 | 92.73% | 3 | 5 | 100% | 100% | 0 | 0.25228 | 102.1389 | 2.5076 | 64.6157 | High | High | Medium | 87 | 88 | 25.7678 | 5636.895 | 63.15%
KANAKA 110165606 | KANAKA 1101 | NORTH VALLEY | 12.8238 | 91.9272 | 96.33% | 13 | 4 | 100% | 100% | 1 | 0.30035 | 85.4511 | 2.5523 | 65.5039 | High | High | Medium | 84 | 89 | 25.6651 | 5611.1271 | 62.86%
VOLTA 110253130 | VOLTA 1102 | NORTH VALLEY | 13.8858 | 76.696 | 100% | 3 | 7 | 100% | 92.09% | 0 | 0.29929 | 85.4511 | 2.2396 | 57.2769 | High | High | Medium | 107 | 90 | 25.5745 | 5585.462 | 62.57%
STANISLAUS 17024905 | STANISLAUS 1702 | YOSEMITE | 2.3422 | 97.8548 | 99.88% | 2 | 2 | 100% | 100% | 0 | 0.25032 | 102.1389 | 2.5717 | 65.75 | High | High | Medium | 82 | 91 | 25.567 | 5559.8875 | 62.29%
MONTE RIO 1113202 | MONTE RIO 1113 | SONOMA | 5.2496 | 89.4483 | 68.59% | 13 | 9 | 100% | 100% | 0 | 0.2988 | 85.4511 | 3.0343 | 77.4749 | High | High | Medium | 58 | 92 | 25.5328 | 5534.3205 | 62%
MOLINO 1102104 | MOLINO 1102 | SONOMA | 21.7365 | 84.6047 | 53.29% | 22 | 10 | 100% | 100% | 1 | 0.38423 | 65.3912 | 2.69 | 67.5877 | High | High | Medium | 78 | 93 | 25.1255 | 5508.7876 | 61.71%
DRUM 1101CB | DRUM 1101 | SIERRA | 2.1059 | 96.8742 | 100% | 2 | 0 | 100% | 100% | 0 | 0.2937 | 85.4511 | 0.83984 | 21.0773 | High | High | Low | 353 | 94 | 25.0967 | 5483.6622 | 61.43%
MIWUK 1702S1547 | MIWUK 1702 | YOSEMITE | 2.7688 | 85.4231 | 100% | 1 | 5 | 100% | 100% | 0 | 0.24392 | 102.1389 | 3.3077 | 82.4079 | High | High | High | 48 | 95 | 24.9141 | 5458.5655 | 61.15%
ORO FINO 11022096 | ORO FINO 1102 | NORTH VALLEY | 14.098 | 93.7734 | 100% | 8 | 2 | 100% | 100% | 0 | 0.28682 | 85.4511 | 2.1974 | 53.8569 | High | High | Low | 122 | 96 | 24.5089 | 5433.6514 | 60.87%
FORESTHILL 11011820 | FORESTHILL 1101 | SIERRA | 5.5828 | 97.995 | 99.82% | 0 | 0 | 100% | 100% | 1 | 0.23777 | 102.1389 | 1.9221 | 46.6794 | High | High | Low | 158 | 97 | 24.2855 | 5409.1425 | 60.6%
WEST POINT 11021303 | WEST POINT 1102 | STOCKTON | 15.8188 | 90.4672 | 99.8% | 4 | 11 | 100% | 100% | 0 | 0.28235 | 85.4511 | 2.2984 | 55.4538 | High | High | Medium | 114 | 98 | 24.1273 | 5384.857 | 60.33%
WOODSIDE 11018974 | WOODSIDE 1101 | PENINSULA | 13.435 | 54.2631 | 29.29% | 40 | 16 | 100% | 100% | 0 | 0.50532 | 47.6367 | 3.1586 | 76.0338 | High | High | High | 59 | 99 | 24.0717 | 5360.7296 | 60.06%
BUCKS CREEK 11032414 | BUCKS CREEK 1103 | NORTH VALLEY | 6.1362 | 87.0222 | 100% | 6 | 5 | 76.6% | 80.44% | 0 | 0.28097 | 85.4511 | 0.98592 | 23.6715 | High | High | Low | 332 | 100 | 24.0095 | 5336.6579 | 59.79%
ELECTRA 110277204 | ELECTRA 1102 | STOCKTON | 18.6351 | 80.9647 | 100% | 2 | 8 | 100% | 100% | 0 | 0.27848 | 85.4511 | 1.9943 | 47.458 | High | High | Low | 150 | 101 | 23.7964 | 5312.6484 | 59.52%
APPLE HILL 210297982 | APPLE HILL 2102 | SIERRA | 10.1443 | 88.7232 | 100% | 1 | 1 | 100% | 100% | 0 | 0.23278 | 102.1389 | 1.3898 | 33.0445 | High | High | Low | 255 | 102 | 23.7764 | 5288.8521 | 59.25%
STANISLAUS 1702L611 | STANISLAUS 1702 | YOSEMITE | 2.9906 | 79.5104 | 100% | 2 | 2 | 100% | 100% | 0 | 0.27802 | 85.4511 | 2.9655 | 70.4504 | High | High | Medium | 73 | 103 | 23.757 | 5265.0757 | 58.98%
SALT SPRINGS 2102L485 | SALT SPRINGS 2102 | STOCKTON | 0.82893 | 87.1462 | 100% | 0 | 2 | 100% | 100% | 0 | 0.23224 | 102.1389 | 1.9664 | 46.6444 | High | High | Low | 159 | 104 | 23.721 | 5241.3187 | 58.72%
EL DORADO PH 21026645 | EL DORADO PH 2102 | SIERRA | 4.2976 | 91.6097 | 86.84% | 4 | 3 | 100% | 100% | 0 | 0.23151 | 102.1389 | 2.2842 | 54.0125 | High | High | Medium | 121 | 105 | 23.6465 | 5217.5977 | 58.45%
MIWUK 1702S2247 | MIWUK 1702 | YOSEMITE | 1.4764 | 81.7159 | 100% | 2 | 2 | 100% | 100% | 0 | 0.23034 | 102.1389 | 4.1204 | 96.9423 | High | High | High | 26 | 106 | 23.5271 | 5193.9512 | 58.19%
WOODACRE 1101404 | WOODACRE 1101 | NORTH BAY | 12.4182 | 78.1166 | 26.88% | 20 | 20 | 100% | 92.07% | 0 | 0.22897 | 102.1389 | 3.9584 | 92.5757 | High | High | High | 33 | 107 | 23.3871 | 5170.424 | 57.92%
MIDDLETOWN 11011079 | MIDDLETOWN 1101 | HUMBOLDT | 3.6508 | 95.1699 | 100% | 2 | 3 | 100% | 100% | 1 | 0.22672 | 102.1389 | 2.2574 | 52.2754 | High | High | Medium | 127 | 108 | 23.1571 | 5147.0369 | 57.66%
SPRING GAP 170210720 | SPRING GAP 1702 | YOSEMITE | 4.7512 | 90.1119 | 100% | 2 | 3 | 100% | 100% | 0 | 0.27005 | 85.4511 | 1.0152 | 23.4266 | High | High | Low | 337 | 109 | 23.076 | 5123.8798 | 57.4%
BRUNSWICK 11053611 | BRUNSWICK 1105 | SIERRA | 1.6138 | 98 | 100% | 0 | 3 | 100% | 100% | 0 | 0.22548 | 102.1389 | 1.4025 | 32.3002 | High | High | Low | 258 | 110 | 23.03 | 5100.8037 | 57.14%
BRUNSWICK 11032200 | BRUNSWICK 1103 | SIERRA | 5.571 | 90.9239 | 99.7% | 2 | 4 | 100% | 100% | 0 | 0.22488 | 102.1389 | 2.3873 | 54.8339 | High | High | Medium | 117 | 111 | 22.9688 | 5077.7737 | 56.89%
MONTE RIO 111164758 | MONTE RIO 1111 | SONOMA | 10.5474 | 85.3267 | 35.52% | 9 | 6 | 100% | 100% | 0 | 0.26838 | 85.4511 | 2.5622 | 58.7581 | High | High | Medium | 101 | 112 | 22.933 | 5054.8049 | 56.63%
WEST POINT 11024790 | WEST POINT 1102 | STOCKTON | 28.9338 | 75.0976 | 91.62% | 9 | 12 | 100% | 75.46% | 1 | 0.35051 | 65.3912 | 2.0584 | 47.1793 | High | High | Low | 154 | 113 | 22.92 | 5031.8719 | 56.37%
ORO FINO 110239154 | ORO FINO 1102 | NORTH VALLEY | 0.88251 | 98 | 100% | 3 | 0 | 100% | 100% | 1 | 0.22144 | 102.1389 | 2.7583 | 62.3862 | High | High | Medium | 93 | 114 | 22.618 | 5008.9519 | 56.11%
FORESTHILL 110137238 | FORESTHILL 1101 | SIERRA | 11.5057 | 97.4901 | 100% | 2 | 5 | 100% | 100% | 1 | 0.26202 | 85.4511 | 1.7672 | 39.5663 | High | High | Low | 215 | 115 | 22.3899 | 4986.3339 | 55.86%
BRUNSWICK 1105 | BRUNSWICK 1105 | SIERRA | 0.032568 | 98 | 100% | 2 | 0 | 100% | 100% | 0 | 0.21917 | 102.1389 | 2.3469 | 52.5372 | High | High | Medium | 124 | 116 | 22.3858 | 4963.944 | 55.61%
WEST POINT 1101L2219 | WEST POINT 1101 | STOCKTON | 3.4094 | 90.8965 | 100% | 0 | 2 | 100% | 100% | 0 | 0.26183 | 85.4511 | 2.2217 | 49.7088 | High | High | Low | 137 | 117 | 22.3739 | 4941.5583 | 55.36%
WILLITS 1104504 | WILLITS 1104 | HUMBOLDT | 22.5336 | 70.0895 | 92.93% | 13 | 8 | 100% | 60.82% | 1 | 0.2605 | 85.4511 | 2.1292 | 47.3973 | High | High | Low | 151 | 118 | 22.2602 | 4919.1844 | 55.11%
WEST POINT 110112256 | WEST POINT 1101 | STOCKTON | 6.5157 | 90.9675 | 74.92% | 4 | 4 | 100% | 100% | 0 | 0.21727 | 102.1389 | 2.7434 | 60.8819 | High | High | Medium | 96 | 119 | 22.192 | 4896.9242 | 54.86%
CHALLENGE 110113026 | CHALLENGE 1101 | NORTH VALLEY | 7.8248 | 63.8642 | 100% | 1 | 1 | 97.67% | 96.11% | 0 | 0.25947 | 85.4511 | 0.3778 | 8.3764 | High | High | Low | 506 | 120 | 22.1717 | 4874.7321 | 54.61%
WILLITS 110391810 | WILLITS 1103 | HUMBOLDT | 29.3984 | 69.6626 | 100% | 19 | 14 | 100% | 85.03% | 1 | 0.25809 | 85.4511 | 2.0026 | 44.1654 | High | High | Low | 181 | 121 | 22.0543 | 4852.5604 | 54.36%
SALT SPRINGS 2102L491 | SALT SPRINGS 2102 | STOCKTON | 2.2143 | 88.9765 | 100% | 2 | 2 | 100% | 100% | 0 | 0.21581 | 102.1389 | 1.5318 | 33.7654 | High | High | Low | 251 | 122 | 22.0423 | 4830.5061 | 54.12%
DOWNIEVILLE DIESEL 1101CB | DOWNIEVILLE DIESEL 1101 | SIERRA | 0.022979 | 98 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21467 | 102.1389 | 2.9787 | 65.3131 | High | High | Medium | 85 | 123 | 21.9265 | 4808.4638 | 53.87%
DOWNIEVILLE DIESEL 11011101/2 | DOWNIEVILLE DIESEL 1101 | SIERRA | 0.0097328 | 98 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21467 | 102.1389 | 2.9743 | 65.2163 | High | High | Medium | 86 | 124 | 21.9265 | 4786.5373 | 53.62%
WILLITS 1103 | WILLITS 1103 | HUMBOLDT | 0.065999 | 98 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21467 | 102.1389 | 1.6051 | 35.1936 | High | High | Low | 245 | 124 | 21.9265 | 4764.6109 | 53.38%
SILVERADO 210478268 | SILVERADO 2104 | NORTH BAY | 11.9793 | 67.2464 | 60.11% | 10 | 4 | 100% | 100% | 0 | 0.3351 | 65.3912 | 3.3562 | 73.5434 | High | High | High | 64 | 126 | 21.9127 | 4742.6844 | 53.13%
VOLTA 11029742 | VOLTA 1102 | NORTH VALLEY | 9.1189 | 78.986 | 100% | 1 | 2 | 100% | 94.08% | 0 | 0.25585 | 85.4511 | 1.7244 | 37.6993 | High | High | Low | 229 | 127 | 21.8624 | 4720.7717 | 52.89%
AUBERRY 1101R324 | AUBERRY 1101 | FRESNO | 10.7908 | 83.7222 | 99.89% | 3 | 1 | 100% | 100% | 0 | 0.25584 | 85.4511 | 1.6256 | 35.538 | High | High | Low | 243 | 128 | 21.8618 | 4698.9093 | 52.64%
PUEBLO 21033583 | PUEBLO 2103 | NORTH BAY | 9.4952 | 94.4646 | 44.31% | 6 | 11 | 100% | 100% | 1 | 0.25545 | 85.4511 | 2.5196 | 54.9993 | High | High | Medium | 116 | 129 | 21.8289 | 4677.0476 | 52.4%
FORESTHILL 1101CB | FORESTHILL 1101 | SIERRA | 9.3514 | 78.4608 | 92.08% | 4 | 4 | 100% | 100% | 0 | 0.33375 | 65.3912 | 2.3144 | 50.5099 | High | High | Medium | 134 | 130 | 21.8245 | 4655.2187 | 52.15%
WEST POINT 11021535 | WEST POINT 1102 | STOCKTON | 3.0651 | 85.9665 | 100% | 1 | 1 | 100% | 100% | 0 | 0.2539 | 85.4511 | 2.4158 | 52.4127 | High | High | Medium | 126 | 131 | 21.6957 | 4633.3942 | 51.91%
OAKHURST 110310723 | OAKHURST 1103 | YOSEMITE | 0.0026429 | 95 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21123 | 102.1389 | 2.2385 | 48.2953 | High | High | Medium | 146 | 132 | 21.5751 | 4611.6985 | 51.66%
MONTE RIO 11138299 | MONTE RIO 1113 | SONOMA | 1.1981 | 94.52 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21069 | 102.1389 | 2.9055 | 62.524 | High | High | Medium | 92 | 133 | 21.5193 | 4590.1233 | 51.42%
LOS GATOS 1107LA60 | LOS GATOS 1107 | DE ANZA | 8.6011 | 90.5119 | 96.22% | 1 | 0 | 100% | 100% | 0 | 0.24993 | 85.4511 | 1.9634 | 41.9315 | High | High | Low | 197 | 134 | 21.3565 | 4568.604 | 51.18%
STANISLAUS 17021850 | STANISLAUS 1702 | YOSEMITE | 13.465 | 54.7158 | 83.98% | 13 | 14 | 100% | 100% | 0 | 0.32626 | 65.3912 | 3.431 | 73.1995 | High | High | High | 66 | 135 | 21.3346 | 4547.2476 | 50.94%
STANISLAUS 1702L5381 | STANISLAUS 1702 | YOSEMITE | 1.2094 | 89.7596 | 100% | 0 | 1 | 100% | 100% | 0 | 0.20877 | 102.1389 | 2.9893 | 63.7424 | High | High | Medium | 89 | 136 | 21.3233 | 4525.9129 | 50.7%
STANISLAUS 170237278 | STANISLAUS 1702 | YOSEMITE | 6.8063 | 74.4331 | 100% | 1 | 5 | 100% | 100% | 0 | 0.2075 | 102.1389 | 2.9637 | 62.8122 | High | High | Medium | 91 | 137 | 21.1942 | 4504.5897 | 50.46%
APPLE HILL 21027502 | APPLE HILL 2102 | SIERRA | 23.0839 | 77.5827 | 99.99% | 4 | 7 | 100% | 82.95% | 0 | 0.24712 | 85.4511 | 1.8048 | 38.1112 | High | High | Low | 226 | 138 | 21.1165 | 4483.3955 | 50.23%
SALT SPRINGS 2102L7283 | SALT SPRINGS 2102 | STOCKTON | 0.66272 | 87.1614 | 100% | 0 | 1 | 100% | 100% | 0 | 0.20585 | 102.1389 | 1.3967 | 29.3663 | High | High | Low | 277 | 139 | 21.0249 | 4462.279 | 49.99%
STANISLAUS 1702 | STANISLAUS 1702 | YOSEMITE | 0.0021222 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 102.1389 | 2.8405 | 59.6463 | High | High | Medium | 98 | 140 | 20.9988 | 4441.254 | 49.75%
WEST POINT 1101L3355 | WEST POINT 1101 | STOCKTON | 2.2225 | 89.0928 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20458 | 102.1389 | 2.1399 | 44.7134 | High | High | Low | 176 | 141 | 20.8954 | 4420.2553 | 49.52%
FULTON 1107214 | FULTON 1107 | SONOMA | 12.2376 | 47.3525 | 63.1% | 7 | 19 | 100% | 100% | 0 | 0.43673 | 47.6367 | 2.1422 | 44.5667 | High | High | Low | 178 | 142 | 20.8046 | 4399.3598 | 49.29%
WEST POINT 1101L1969 | WEST POINT 1101 | STOCKTON | 1.0816 | 86.0606 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20122 | 102.1389 | 2.8277 | 58.1165 | High | High | Medium | 103 | 143 | 20.5528 | 4378.5552 | 49.05%
SHINGLE SPRINGS 210912392 | SHINGLE SPRINGS 2109 | SIERRA | 14.9169 | 46.1952 | 91.69% | 7 | 8 | 100% | 100% | 0 | 0.31183 | 65.3912 | 2.7319 | 55.7055 | High | High | Medium | 112 | 144 | 20.3908 | 4358.0024 | 48.82%
ALLEGHANY 1101CB | ALLEGHANY 1101 | SIERRA | 4.3289 | 94.1851 | 45.96% | 2 | 2 | 100% | 100% | 0 | 0.23753 | 85.4511 | 1.9061 | 38.6887 | High | High | Low | 224 | 145 | 20.2969 | 4337.6117 | 48.59%
MONTE RIO 11131991 | MONTE RIO 1113 | SONOMA | 7.0583 | 93.2573 | 64.98% | 0 | 4 | 100% | 100% | 0 | 0.19767 | 102.1389 | 2.7908 | 56.3455 | High | High | Medium | 110 | 146 | 20.1896 | 4317.3147 | 48.37%
CHALLENGE 11025462 | CHALLENGE 1102 | NORTH VALLEY | 23.3648 | 66.9386 | 100% | 8 | 5 | 100% | 97.29% | 1 | 0.30821 | 65.3912 | 1.8735 | 37.7585 | High | High | Low | 228 | 147 | 20.154 | 4297.1251 | 48.14%
FORESTHILL 110175340 | FORESTHILL 1101 | SIERRA | 4.974 | 93.375 | 69.57% | 0 | 2 | 100% | 100% | 0 | 0.19715 | 102.1389 | 2.1578 | 43.4515 | High | High | Low | 190 | 148 | 20.1366 | 4276.9711 | 47.91%
VOLTA 11021504 | VOLTA 1102 | NORTH VALLEY | 8.3043 | 82.9659 | 100% | 2 | 3 | 100% | 100% | 0 | 0.23562 | 85.4511 | 2.2543 | 45.389 | High | High | Medium | 168 | 149 | 20.1342 | 4256.8345 | 47.69%
VOLTA 110280982 | VOLTA 1102 | NORTH VALLEY | 0.52007 | 92.783 | 99.45% | 2 | 0 | 100% | 100% | 1 | 0.23557 | 85.4511 | 2.084 | 41.9505 | High | High | Low | 196 | 150 | 20.1294 | 4236.7003 | 47.46%
ORO FINO 11022090 | ORO FINO 1102 | NORTH VALLEY | 14.7385 | 94.0575 | 68.97% | 5 | 5 | 100% | 100% | 1 | 0.1964 | 102.1389 | 3.5409 | 71.0314 | High | High | High | 72 | 151 | 20.0604 | 4216.5709 | 47.24%
WOODSIDE 11018884 | WOODSIDE 1101 | PENINSULA | 7.7125 | 85.1128 | 91.16% | 13 | 3 | 100% | 100% | 0 | 0.30526 | 65.3912 | 2.4202 | 48.3096 | High | High | Medium | 145 | 152 | 19.9613 | 4196.5105 | 47.01%
EL DORADO PH 2102CB | EL DORADO PH 2102 | SIERRA | 5.6703 | 93.9988 | 79.03% | 2 | 2 | 100% | 100% | 0 | 0.19325 | 102.1389 | 2.2785 | 44.974 | High | High | Medium | 174 | 153 | 19.7388 | 4176.5492 | 46.79%
PINE GROVE 11023172 | PINE GROVE 1102 | STOCKTON | 36.8095 | 74.2107 | 73.54% | 9 | 20 | 100% | 71.26% | 1 | 0.23027 | 85.4511 | 3.4298 | 67.4865 | High | High | High | 80 | 154 | 19.6764 | 4156.8104 | 46.57%
EL DORADO PH 210119612 | EL DORADO PH 2101 | SIERRA | 9.1713 | 87.7197 | 45.56% | 7 | 1 | 100% | 100% | 0 | 0.19221 | 102.1389 | 1.8339 | 36.0017 | High | High | Low | 238 | 155 | 19.6316 | 4137.134 | 46.35%
SALT SPRINGS 210297924 | SALT SPRINGS 2102 | STOCKTON | 5.0873 | 68.1168 | 100% | 5 | 4 | 100% | 100% | 0 | 0.22834 | 85.4511 | 1.4445 | 28.1851 | High | High | Low | 290 | 156 | 19.5118 | 4117.5023 | 46.13%
WILLITS 1104934 | WILLITS 1104 | HUMBOLDT | 30.5846 | 72.5028 | 89.66% | 17 | 12 | 100% | 39.29% | 1 | 0.29588 | 65.3912 | 1.8491 | 35.7756 | High | High | Low | 241 | 157 | 19.3479 | 4097.9906 | 45.91%
KANAKA 11011034 | KANAKA 1101 | NORTH VALLEY | 13.1567 | 96.9359 | 65.02% | 4 | 2 | 100% | 100% | 0 | 0.22603 | 85.4511 | 1.9382 | 37.4363 | High | High | Low | 230 | 158 | 19.3146 | 4078.6427 | 45.69%
PINE GROVE 110235576 | PINE GROVE 1102 | STOCKTON | 7.978 | 78.3459 | 100% | 3 | 1 | 100% | 100% | 0 | 0.22493 | 85.4511 | 2.6836 | 51.5795 | High | High | Medium | 129 | 159 | 19.2204 | 4059.3281 | 45.48%
MIWUK 17028130 | MIWUK 1702 | YOSEMITE | 9.8769 | 52.0925 | 100% | 2 | 8 | 100% | 100% | 0 | 0.29268 | 65.3912 | 3.427 | 65.5898 | High | High | High | 83 | 160 | 19.1389 | 4040.1077 | 45.26%
CAMP EVERS 210510214 | CAMP EVERS 2105 | CENTRAL COAST | 14.0274 | 70.1914 | 71.02% | 31 | 1 | 100% | 100% | 0 | 0.29021 | 65.3912 | 3.1151 | 59.1158 | High | High | High | 100 | 161 | 18.9774 | 4020.9688 | 45.05%
SILVERADO 2105658898 | SILVERADO 2105 | NORTH BAY | 17.239 | 89.5362 | 92.68% | 6 | 3 | 99.53% | 97.17% | 1 | 0.28431 | 65.3912 | 3.1133 | 57.8818 | High | High | High | 104 | 162 | 18.5917 | 4001.9914 | 44.83%
STANISLAUS 17026028 | STANISLAUS 1702 | YOSEMITE | 5.3481 | 47.3801 | 91.01% | 3 | 4 | 100% | 100% | 0 | 0.28374 | 65.3912 | 3.0384 | 56.3747 | High | High | Medium | 109 | 163 | 18.5544 | 3983.3997 | 44.63%
BIG BASIN 110110720 | BIG BASIN 1101 | CENTRAL COAST | 4.6838 | 66.6097 | 31.56% | 7 | 1 | 100% | 100% | 0 | 0.21501 | 85.4511 | 3.3585 | 61.7049 | High | High | High | 95 | 164 | 18.3729 | 3964.8454 | 44.42%
FORT ROSS 112170288 | FORT ROSS 1121 | SONOMA | 11.744 | 93.8091 | 82.61% | 5 | 5 | 100% | 100% | 0 | 0.2145 | 85.4511 | 1.9739 | 36.1799 | High | High | Low | 237 | 165 | 18.3292 | 3946.4725 | 44.21%
MOUNTAIN QUARRIES 21011184 | MOUNTAIN QUARRIES 2101 | SIERRA | 11.7903 | 85.233 | 82.22% | 1 | 4 | 100% | 100% | 0 | 0.21412 | 85.4511 | 2.9723 | 54.3825 | High | High | Medium | 119 | 166 | 18.2964 | 3928.1433 | 44.01%
PARADISE 11011155 | PARADISE 1101 | NORTH VALLEY | 0.42051 | 84.3729 | 100% | 5 | 1 | 100% | 100% | 0 | 0.21365 | 85.4511 | 3.701 | 67.5683 | High | High | High | 79 | 167 | 18.257 | 3909.8469 | 43.8%
MONTE RIO 111153477 | MONTE RIO 1111 | SONOMA | 2.1403 | 90.336 | 44.25% | 6 | 1 | 100% | 100% | 0 | 0.21276 | 85.4511 | 1.9244 | 34.9877 | High | High | Low | 247 | 168 | 18.1807 | 3891.59 | 43.6%
WILLITS 1103968 | WILLITS 1103 | HUMBOLDT | 24.6966 | 68.3381 | 85.93% | 14 | 10 | 88.86% | 68.54% | 1 | 0.21234 | 85.4511 | 1.8563 | 33.6814 | High | High | Low | 253 | 169 | 18.1447 | 3873.4092 | 43.39%
SALT SPRINGS 210237300 | SALT SPRINGS 2102 | STOCKTON | 6.9933 | 87.6909 | 82.66% | 1 | 2 | 100% | 100% | 0 | 0.21052 | 85.4511 | 2.1022 | 37.8154 | High | High | Low | 227 | 170 | 17.9888 | 3855.2645 | 43.19%
MOLINO 1102396 | MOLINO 1102 | SONOMA | 16.1282 | 58.4363 | 35.51% | 9 | 10 | 100% | 100% | 0 | 0.275 | 65.3912 | 2.5855 | 46.494 | High | High | Medium | 161 | 171 | 17.9823 | 3837.2757 | 42.99%
STELLING 111060094 | STELLING 1110 | DE ANZA | 13.9579 | 79.5 | 89.71% | 7 | 6 | 100% | 94.63% | 1 | 0.27357 | 65.3912 | 3.1124 | 55.6768 | High | High | High | 113 | 172 | 17.8888 | 3819.2934 | 42.79%
BIG TREES 04025300 | BIG TREES 0402 | CENTRAL COAST | 9.8017 | 22.3436 | 42.94% | 37 | 4 | 100% | 100% | 1 | 0.37529 | 47.6367 | 3.9078 | 69.8624 | High | High | High | 75 | 173 | 17.8776 | 3801.4046 | 42.59%
FITCH MOUNTAIN 111324918 | FITCH MOUNTAIN 1113 | SONOMA | 5.4494 | 96.6209 | 46.61% | 13 | 1 | 100% | 100% | 0 | 0.17452 | 102.1389 | 2.2832 | 40.6989 | High | High | Medium | 209 | 174 | 17.8255 | 3783.527 | 42.39%
AUBERRY 1101D4982 | AUBERRY 1101 | FRESNO | 2.6789 | 91.9989 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20783 | 85.4511 | 1.8789 | 33.3678 | High | High | Low | 254 | 175 | 17.7595 | 3765.7015 | 42.19%
MOLINO 1102658 | MOLINO 1102 | SONOMA | 10.901 | 83.5071 | 77.94% | 19 | 4 | 100% | 73.87% | 0 | 0.26881 | 65.3912 | 2.8576 | 50.2302 | High | High | Medium | 135 | 176 | 17.5775 | 3747.942 | 41.99%
WEST POINT 11021391 | WEST POINT 1102 | STOCKTON | 3.974 | 89.103 | 100% | 2 | 3 | 100% | 100% | 0 | 0.26869 | 65.3912 | 1.4346 | 25.2057 | High | High | Low | 317 | 177 | 17.57 | 3730.3644 | 41.79%
WEST POINT 1101 | WEST POINT 1101 | STOCKTON | 0.004924 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 85.4511 | 2.4491 | 43.0255 | High | High | Medium | 192 | 178 | 17.5679 | 3712.7944 | 41.59%
MONTE RIO 1113678 | MONTE RIO 1113 | SONOMA | 1.8444 | 89.0499 | 49.28% | 0 | 1 | 100% | 100% | 0 | 0.20505 | 85.4511 | 2.7668 | 48.4785 | High | High | Medium | 144 | 179 | 17.5214 | 3695.2265 | 41.4%
SAN RAFAEL 11081250 | SAN RAFAEL 1108 | NORTH BAY | 3.5796 | 93.2481 | 59.75% | 1 | 1 | 100% | 100% | 1 | 0.20419 | 85.4511 | 4.1107 | 71.7241 | High | High | High | 70 | 180 | 17.4483 | 3677.7051 | 41.2%
BRUNSWICK 110584480 | BRUNSWICK 1105 | SIERRA | 4.5786 | 96.5256 | 65.31% | 1 | 0 | 100% | 100% | 0 | 0.17078 | 102.1389 | 2.4965 | 43.5454 | High | High | Medium | 188 | 181 | 17.4429 | 3660.2568 | 41.01%
MONTE RIO 1113320 | MONTE RIO 1113 | SONOMA | 2.745 | 95.3298 | 21.97% | 16 | 1 | 100% | 100% | 1 | 0.16899 | 102.1389 | 2.8782 | 49.6792 | High | High | Medium | 138 | 182 | 17.2604 | 3642.8139 | 40.81%
BRUNSWICK 11052204 | BRUNSWICK 1105 | SIERRA | 7.2073 | 87.5526 | 78.12% | 3 | 0 | 100% | 100% | 0 | 0.2017 | 85.4511 | 2.3292 | 40.1437 | High | High | Medium | 211 | 183 | 17.2351 | 3625.5534 | 40.62%
BONNIE NOOK 110186696 | BONNIE NOOK 1101 | SIERRA | 9.7026 | 94.616 | 77.04% | 2 | 5 | 100% | 100% | 0 | 0.2013 | 85.4511 | 0.64933 | 11.1691 | High | High | Low | 456 | 184 | 17.2011 | 3608.3183 | 40.42%
MONTE RIO 11111703 | MONTE RIO 1111 | SONOMA | 1.2714 | 84.0743 | 95.02% | 2 | 1 | 100% | 100% | 0 | 0.20007 | 85.4511 | 2.5488 | 43.5738 | High | High | Medium | 187 | 185 | 17.096 | 3591.1172 | 40.23%
KONOCTI 1102532 | KONOCTI 1102 | HUMBOLDT | 9.613 | 73.4923 | 78.9% | 8 | 7 | 100% | 100% | 1 | 0.20006 | 85.4511 | 2.7651 | 47.2701 | High | High | Medium | 153 | 186 | 17.0951 | 3574.0212 | 40.04%
MONTE RIO 1113652 | MONTE RIO 1113 | SONOMA | 1.6252 | 74.26 | 59.28% | 4 | 0 | 100% | 100% | 0 | 0.16674 | 102.1389 | 3.2389 | 55.1604 | High | High | High | 115 | 187 | 17.0307 | 3556.9261 | 39.85%
MIDDLETOWN 11014646 | MIDDLETOWN 1101 | HUMBOLDT | 18.5612 | 85.1867 | 99.86% | 4 | 10 | 100% | 100% | 0 | 0.35694 | 47.6367 | 2.1685 | 36.8721 | High | High | Low | 235 | 188 | 17.0035 | 3539.8955 | 39.66%
MOLINO 110266006 | MOLINO 1102 | SONOMA | 9.0487 | 82.4735 | 54.27% | 8 | 4 | 100% | 100% | 1 | 0.25799 | 65.3912 | 3.052 | 51.4882 | High | High | Medium | 131 | 189 | 16.8704 | 3522.8919 | 39.47%
BRUNSWICK 11062796 | BRUNSWICK 1106 | SIERRA | 19.8739 | 59.7898 | 71.67% | 4 | 4 | 100% | 99.1% | 0 | 0.19738 | 85.4511 | 2.6385 | 44.5007 | High | High | Medium | 180 | 190 | 16.8661 | 3506.0215 | 39.28%
MIDDLETOWN 1101614 | MIDDLETOWN 1101 | HUMBOLDT | 1.393 | 87.6673 | 76.7% | 0 | 1 | 100% | 100% | 0 | 0.19696 | 85.4511 | 2.8133 | 47.348 | High | High | Medium | 152 | 191 | 16.8302 | 3489.1554 | 39.09%
MONTE RIO 111215401 | MONTE RIO 1112 | SONOMA | 0.86292 | 85.2793 | 87.8% | 1 | 3 | 100% | 100% | 0 | 0.19647 | 85.4511 | 2.4508 | 41.1456 | High | High | Medium | 204 | 192 | 16.7884 | 3472.3253 | 38.9%
PINE GROVE 11029145 | PINE GROVE 1102 | STOCKTON | 2.9225 | 81.0955 | 99.74% | 0 | 0 | 100% | 100% | 0 | 0.19549 | 85.4511 | 2.812 | 46.973 | High | High | Medium | 156 | 193 | 16.7046 | 3455.5368 | 38.71%
WEST POINT 110234416 | WEST POINT 1102 | STOCKTON | 10.524 | 86.8553 | 100% | 7 | 3 | 100% | 100% | 1 | 0.25274 | 65.3912 | 2.5592 | 42.2967 | High | High | Medium | 194 | 194 | 16.5271 | 3438.8322 | 38.52%
WEST POINT 1102L3733 | WEST POINT 1102 | STOCKTON | 1.754 | 90.0843 | 100% | 0 | 0 | 100% | 94.99% | 0 | 0.19267 | 85.4511 | 2.5527 | 42.0286 | High | High | Medium | 195 | 195 | 16.464 | 3422.3051 | 38.34%
ORO FINO 11022556 | ORO FINO 1102 | NORTH VALLEY | 6.6623 | 79.6419 | 97.8% | 0 | 4 | 100% | 100% | 0 | 0.25169 | 65.3912 | 2.4528 | 40.3695 | High | High | Medium | 210 | 196 | 16.4582 | 3405.8411 | 38.16%
MONTE RIO 1113180 | MONTE RIO 1113 | SONOMA | 1.9463 | 80.579 | 66.84% | 3 | 0 | 100% | 100% | 0 | 0.1611 | 102.1389 | 2.9572 | 48.6589 | High | High | Medium | 142 | 197 | 16.4543 | 3389.3828 | 37.97%
WOODACRE 11011238 | WOODACRE 1101 | NORTH BAY | 3.6828 | 94.4368 | 22.55% | 16 | 2 | 100% | 100% | 0 | 0.19161 | 85.4511 | 3.808 | 62.3489 | High | High | High | 94 | 198 | 16.373 | 3372.9285 | 37.79%
PIKE CITY 11011720 | PIKE CITY 1101 | SIERRA | 6.0835 | 93.4602 | 100% | 4 | 2 | 100% | 100% | 0 | 0.24982 | 65.3912 | 1.4389 | 23.5061 | High | High | Low | 335 | 199 | 16.3363 | 3356.5555 | 37.6%
FITCH MOUNTAIN 11136751 | FITCH MOUNTAIN 1113 | SONOMA | 22.3305 | 96.8838 | 61.93% | 21 | 1 | 100% | 75.68% | 1 | 0.19015 | 85.4511 | 2.409 | 39.1424 | High | High | Medium | 218 | 200 | 16.2482 | 3340.2192 | 37.42%
STANISLAUS 17011331 | STANISLAUS 1701 | YOSEMITE | 4.3931 | 65.9467 | 100% | 5 | 0 | 100% | 100% | 0 | 0.18999 | 85.4511 | 2.846 | 46.2045 | High | High | Medium | 164 | 201 | 16.2348 | 3323.971 | 37.24%
DIAMOND SPRINGS 11071402 | DIAMOND SPRINGS 1107 | SIERRA | 44.1487 | 51.2712 | 86.92% | 1 | 21 | 100% | 76.75% | 0 | 0.24689 | 65.3912 | 2.1929 | 35.4032 | High | High | Low | 244 | 202 | 16.1444 | 3307.7362 | 37.06%
PARADISE 110195728 | PARADISE 1101 | NORTH VALLEY | 5.026 | 85.7627 | 38.06% | 1 | 6 | 100% | 100% | 0 | 0.18459 | 85.4511 | 3.6211 | 57.1177 | High | High | High | 108 | 203 | 15.7736 | 3291.5919 | 36.88%
MIWUK 17028090 | MIWUK 1702 | YOSEMITE | 4.0244 | 68.0843 | 40.03% | 1 | 7 | 100% | 100% | 0 | 0.1541 | 102.1389 | 3.6986 | 58.2148 | High | High | High | 102 | 204 | 15.7396 | 3275.8183 | 36.7%
WEST POINT 110236676 | WEST POINT 1102 | STOCKTON | 16.994 | 84.9293 | 78.04% | 3 | 4 | 100% | 93.46% | 0 | 0.24051 | 65.3912 | 2.1683 | 34.1012 | High | High | Low | 249 | 205 | 15.7272 | 3260.0787 | 36.52%
MONTE RIO 1113CB | MONTE RIO 1113 | SONOMA | 4.5623 | 78.3408 | 32.43% | 11 | 4 | 100% | 100% | 0 | 0.18356 | 85.4511 | 2.9514 | 46.2948 | High | High | Medium | 163 | 206 | 15.6855 | 3244.3515 | 36.35%
HALF MOON BAY 11012500 | HALF MOON BAY 1101 | PENINSULA | 5.7745 | 85.7148 | 84.59% | 4 | 6 | 82.94% | 96.61% | 1 | 0.2396 | 65.3912 | 3.6617 | 57.3712 | High | High | High | 106 | 207 | 15.668 | 3228.666 | 36.17%
FULTON 1107604 | FULTON 1107 | SONOMA | 17.5324 | 71.8219 | 64.8% | 2 | 17 | 100% | 100% | 0 | 0.3284 | 47.6367 | 2.4442 | 38.2377 | High | High | Medium | 225 | 208 | 15.6441 | 3212.998 | 35.99%
CURTIS 1705843 | CURTIS 1705 | YOSEMITE | 6.6016 | 54.6165 | 100% | 2 | 2 | 100% | 93.53% | 0 | 0.18286 | 85.4511 | 3.052 | 47.6886 | High | High | Medium | 149 | 209 | 15.6252 | 3197.3539 | 35.82%
RINCON 1103568 | RINCON 1103 | SONOMA | 12.8289 | 71.6958 | 48.67% | 11 | 11 | 100% | 100% | 0 | 0.32682 | 47.6367 | 2.5697 | 40.0064 | High | High | Medium | 212 | 210 | 15.5685 | 3181.7287 | 35.64%
MONTE RIO 111137520 | MONTE RIO 1111 | SONOMA | 2.1617 | 88.6545 | 55.37% | 6 | 0 | 100% | 100% | 0 | 0.18002 | 85.4511 | 1.984 | 30.52 | High | High | Low | 273 | 211 | 15.383 | 3166.1602 | 35.47%
BRUNSWICK 11062104 | BRUNSWICK 1106 | SIERRA | 9.719 | 86.4087 | 57.37% | 4 | 1 | 100% | 100% | 0 | 0.17938 | 85.4511 | 2.5365 | 38.8801 | High | High | Medium | 222 | 212 | 15.3282 | 3150.7772 | 35.3%
MIRABEL 11027347 | MIRABEL 1102 | SONOMA | 0.81707 | 70.8306 | 59.55% | 4 | 1 | 100% | 100% | 0 | 0.14897 | 102.1389 | 2.8575 | 43.4787 | High | High | Medium | 189 | 213 | 15.2154 | 3135.449 | 35.13%
LOS GATOS 11072917 | LOS GATOS 1107 | DE ANZA | 7.7152 | 64.4105 | 89.16% | 10 | 1 | 100% | 100% | 0 | 0.23223 | 65.3912 | 1.7943 | 27.2488 | High | High | Low | 299 | 214 | 15.1861 | 3120.2336 | 34.96%
SILVERADO 2104645 | SILVERADO 2104 | NORTH BAY | 1.0113 | 86.4283 | 53.43% | 4 | 2 | 100% | 100% | 0 | 0.17771 | 85.4511 | 3.9922 | 60.6227 | High | High | High | 97 | 215 | 15.1851 | 3105.0475 | 34.79%
CALISTOGA 11011085 | CALISTOGA 1101 | NORTH BAY | 2.0832 | 81.9335 | 72.65% | 1 | 1 | 100% | 100% | 0 | 0.23189 | 65.3912 | 2.6122 | 39.6091 | High | High | Medium | 214 | 216 | 15.1634 | 3089.8623 | 34.62%
PARADISE 11052214 | PARADISE 1105 | NORTH VALLEY | 9.8398 | 58.7584 | 53.2% | 6 | 6 | 86.04% | 100% | 1 | 0.14771 | 102.1389 | 3.4298 | 51.746 | High | High | High | 128 | 217 | 15.0873 | 3074.699 | 34.45%
APPLE HILL 2102CB | APPLE HILL 2102 | SIERRA | 41.3043 | 54.0794 | 88.14% | 11 | 9 | 100% | 60.25% | 1 | 0.23023 | 65.3912 | 1.9699 | 29.6561 | High | High | Low | 275 | 218 | 15.0548 | 3059.6117 | 34.28%
SHINGLE SPRINGS 210961892 | SHINGLE SPRINGS 2109 | SIERRA | 30.1835 | 48.4981 | 100% | 2 | 8 | 100% | 100% | 0 | 0.31574 | 47.6367 | 2.5856 | 38.8898 | High | High | Medium | 221 | 219 | 15.0409 | 3044.5569 | 34.11%
SILVERADO 21051421 | SILVERADO 2105 | NORTH BAY | 9.2052 | 85.2373 | 78.89% | 5 | 4 | 92.75% | 100% | 1 | 0.22901 | 65.3912 | 3.5009 | 52.427 | High | High | High | 125 | 220 | 14.9751 | 3029.516 | 33.94%
ORO FINO 1102CB | ORO FINO 1102 | NORTH VALLEY | 2.0939 | 90.4736 | 31.39% | 1 | 0 | 100% | 100% | 0 | 0.1458 | 102.1389 | 3.0047 | 44.7473 | High | High | Medium | 175 | 221 | 14.8924 | 3014.5409 | 33.77%
CURTIS 17048140 | CURTIS 1704 | YOSEMITE | 26.2498 | 65.6672 | 76.6% | 12 | 12 | 100% | 76.04% | 0 | 0.17401 | 85.4511 | 2.7756 | 41.2728 | High | High | Medium | 202 | 222 | 14.8696 | 2999.6485 | 33.6%
MIWUK 170193062 | MIWUK 1701 | YOSEMITE | 8.21 | 73.287 | 98.21% | 5 | 3 | 100% | 79.03% | 0 | 0.17366 | 85.4511 | 3.1781 | 47.1632 | High | High | High | 155 | 223 | 14.8399 | 2984.7789 | 33.44%
SILVERADO 2104722 | SILVERADO 2104 | NORTH BAY | 7.8999 | 65.7561 | 63.09% | 2 | 4 | 100% | 100% | 0 | 0.17105 | 85.4511 | 3.1898 | 46.6231 | High | High | High | 160 | 224 | 14.6165 | 2969.939 | 33.27%
MOLINO 1101322 | MOLINO 1101 | SONOMA | 15.8907 | 58.1086 | 71.61% | 14 | 10 | 100% | 44.47% | 0 | 0.22351 | 65.3912 | 2.4422 | 35.6935 | High | High | Medium | 242 | 225 | 14.6154 | 2955.3226 | 33.11%
APPLE HILL 110412832 | APPLE HILL 1104 | SIERRA | 15.3272 | 73.0049 | 95.88% | 8 | 6 | 99.79% | 19.25% | 1 | 0.22229 | 65.3912 | 1.9946 | 28.9929 | High | High | Low | 281 | 226 | 14.536 | 2940.7072 | 32.94%
DUNBAR 1101343 | DUNBAR 1101 | SONOMA | 4.4643 | 78.5129 | 81.48% | 1 | 3 | 100% | 97.94% | 0 | 0.21869 | 65.3912 | 2.7227 | 38.9349 | High | High | Medium | 220 | 227 | 14.3001 | 2926.1712 | 32.78%
PINE GROVE 110283098 | PINE GROVE 1102 | STOCKTON | 8.0988 | 80.2841 | 100% | 2 | 7 | 100% | 98.1% | 0 | 0.21828 | 65.3912 | 3.1987 | 45.6583 | High | High | High | 167 | 228 | 14.2738 | 2911.8711 | 32.62%
MIWUK 170219772 | MIWUK 1702 | YOSEMITE | 3.8508 | 59.5505 | 82.54% | 2 | 3 | 100% | 100% | 0 | 0.16594 | 85.4511 | 3.4321 | 48.6675 | High | High | High | 141 | 229 | 14.1801 | 2897.5973 | 32.46%
KANAKA 110175744 | KANAKA 1101 | NORTH VALLEY | 10.5898 | 74.5656 | 100% | 3 | 3 | 100% | 74.87% | 0 | 0.16375 | 85.4511 | 1.9254 | 26.9403 | High | High | Low | 304 | 230 | 13.9922 | 2883.4172 | 32.3%
CHALLENGE 11021902 | CHALLENGE 1102 | NORTH VALLEY | 5.0391 | 84.0879 | 100% | 3 | 2 | 100% | 100% | 0 | 0.21241 | 65.3912 | 2.2968 | 31.9012 | High | High | Medium | 259 | 231 | 13.8896 | 2869.4249 | 32.15%
VOLTA 11021648 | VOLTA 1102 | NORTH VALLEY | 4.8649 | 85.7622 | 100% | 2 | 2 | 100% | 79.51% | 0 | 0.16163 | 85.4511 | 2.0849 | 28.7959 | High | High | Low | 283 | 232 | 13.8114 | 2855.5354 | 31.99%
CAMP EVERS 210611533 | CAMP EVERS 2106 | CENTRAL COAST | 2.6563 | 88.3756 | 100% | 3 | 0 | 100% | 100% | 0 | 0.2103 | 65.3912 | 2.1282 | 29.2669 | High | High | Low | 279 | 233 | 13.7518 | 2841.724 | 31.84%
MONTE RIO 11131989 | MONTE RIO 1113 | SONOMA | 0.72387 | 90 | 37.43% | 0 | 0 | 100% | 100% | 0 | 0.13376 | 102.1389 | 3.26 | 44.5399 | High | High | High | 179 | 234 | 13.6625 | 2827.9722 | 31.68%
DUNBAR 1103534 | DUNBAR 1103 | SONOMA | 15.5924 | 79.0775 | 96.69% | 3 | 12 | 89.43% | 96.98% | 1 | 0.28566 | 47.6367 | 2.69 | 36.606 | High | High | Medium | 236 | 235 | 13.6079 | 2814.3096 | 31.53%
CLARKSVILLE 210419772 | CLARKSVILLE 2104 | SIERRA | 18.3365 | 58.7112 | 99.97% | 3 | 3 | 99.31% | 100% | 1 | 0.20806 | 65.3912 | 3.04 | 41.3598 | High | High | Medium | 201 | 236 | 13.6054 | 2800.7017 | 31.38%
KONOCTI 11024300 | KONOCTI 1102 | HUMBOLDT | 26.3294 | 77.3617 | 62.75% | 9 | 28 | 97.14% | 84.42% | 1 | 0.28482 | 47.6367 | 2.1132 | 28.6726 | High | High | Low | 287 | 237 | 13.5681 | 2787.0963 | 31.22%
LOS GATOS 110712041 | LOS GATOS 1107 | DE ANZA | 6.3296 | 61.8932 | 100% | 5 | 1 | 100% | 100% | 0 | 0.28444 | 47.6367 | 2.2717 | 30.7809 | High | High | Medium | 269 | 238 | 13.5499 | 2773.5282 | 31.07%
MIWUK 170111800 | MIWUK 1701 | YOSEMITE | 9.4843 | 50.073 | 65.97% | 8 | 9 | 100% | 100% | 0 | 0.20689 | 65.3912 | 3.6538 | 49.4316 | High | High | High | 139 | 239 | 13.5287 | 2759.9783 | 30.92%
LOS GATOS 110760024 | LOS GATOS 1107 | DE ANZA | 3.9994 | 92.5853 | 100% | 0 | 0 | 100% | 100% | 0 | 0.28225 | 47.6367 | 1.6969 | 22.8161 | High | High | Low | 342 | 240 | 13.4456 | 2746.4497 | 30.77%
WASHINGTON CITY GEN. 1101CB | WASHINGTON CITY GEN. 1101 | SIERRA | 0.012645 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 65.3912 | 1.3761 | 18.5003 | High | High | Low | 378 | 241 | 13.4438 | 2733.0041 | 30.62%
WASHINGTON CITY GEN. 11011101/2 | WASHINGTON CITY GEN. 1101 | SIERRA | 0.0035486 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 65.3912 | 1.3746 | 18.4792 | High | High | Low | 379 | 241 | 13.4438 | 2719.5602 | 30.47%
RINCON 1101578 | RINCON 1101 | SONOMA | 17.3381 | 67.0315 | 100% | 2 | 9 | 93.38% | 92.03% | 0 | 0.20486 | 65.3912 | 2.768 | 37.0801 | High | High | Medium | 233 | 243 | 13.3958 | 2706.1164 | 30.32%
RINCON 1103198 | RINCON 1103 | SONOMA | 6.4573 | 72.5696 | 80.26% | 6 | 3 | 100% | 100% | 0 | 0.20459 | 65.3912 | 3.0723 | 41.1018 | High | High | Medium | 205 | 244 | 13.3782 | 2692.7206 | 30.17%
WILLOW CREEK 11013050 | WILLOW CREEK 1101 | HUMBOLDT | 2.7741 | 81.978 | 100% | 0 | 2 | 100% | 100% | 1 | 0.20349 | 65.3912 | 0.83142 | 11.0633 | High | High | Low | 460 | 245 | 13.3065 | 2679.3423 | 30.02%
CAMP EVERS 210660120 | CAMP EVERS 2106 | CENTRAL COAST | 4.3678 | 67.866 | 79.91% | 12 | 0 | 100% | 100% | 0 | 0.20157 | 65.3912 | 2.0826 | 27.4498 | High | High | Low | 296 | 246 | 13.1807 | 2666.0359 | 29.87%
ALTO 11243121 | ALTO 1124 | NORTH BAY | 2.756 | 78.1169 | 17.87% | 3 | 11 | 100% | 100% | 0 | 0.1536 | 85.4511 | 4.1251 | 54.1442 | High | High | High | 120 | 247 | 13.1255 | 2652.8551 | 29.72%
MONTE RIO 111123916 | MONTE RIO 1111 | SONOMA | 5.2149 | 69.8916 | 48.27% | 12 | 5 | 100% | 100% | 0 | 0.20017 | 65.3912 | 1.981 | 25.9302 | High | High | Low | 312 | 248 | 13.0895 | 2639.7297 | 29.57%
MORGAN HILL 21114461 | MORGAN HILL 2111 | SAN JOSE | 2.2769 | 88.7487 | 84.71% | 4 | 2 | 100% | 100% | 0 | 0.19916 | 65.3912 | 2.6877 | 35.0025 | High | High | Medium | 246 | 249 | 13.0233 | 2626.6402 | 29.43%
VOLTA 110254932 | VOLTA 1102 | NORTH VALLEY | 4.3783 | 73.0618 | 100% | 0 | 1 | 100% | 95.18% | 0 | 0.19916 | 65.3912 | 1.937 | 25.2264 | High | High | Low | 316 | 250 | 13.0232 | 2613.6169 | 29.28%
PIKE CITY 1102CB | PIKE CITY 1102 | SIERRA | 9.4149 | 96.7439 | 75.24% | 4 | 3 | 100% | 100% | 0 | 0.19876 | 65.3912 | 1.1735 | 15.2521 | High | High | Low | 410 | 251 | 12.9975 | 2600.5938 | 29.13%
SILVERADO 2103CB | SILVERADO 2103 | NORTH BAY | 8.6664 | 84.0044 | 89.49% | 1 | 4 | 46.48% | 100% | 0 | 0.27216 | 47.6367 | 3.3783 | 43.8001 | High | High | High | 186 | 252 | 12.965 | 2587.5963 | 28.99%
HIGHLANDS 1103520 | HIGHLANDS 1103 | HUMBOLDT | 46.4816 | 67.4675 | 99% | 5 | 17 | 100% | 0% | 0 | 0.27204 | 47.6367 | 2.7667 | 35.8548 | High | High | Medium | 240 | 253 | 12.9592 | 2574.6313 | 28.84%
CAMP EVERS 210574170 | CAMP EVERS 2105 | CENTRAL COAST | 3.5599 | 43.1898 | 71.52% | 10 | 5 | 100% | 100% | 0 | 0.19742 | 65.3912 | 4.2334 | 54.6522 | High | High | High | 118 | 254 | 12.9096 | 2561.6721 | 28.7%
WEST POINT 1102CB | WEST POINT 1102 | STOCKTON | 17.7809 | 76.7324 | 62.09% | 5 | 4 | 100% | 79.61% | 1 | 0.19732 | 65.3912 | 2.8754 | 37.101 | High | High | Medium | 232 | 255 | 12.9027 | 2548.7625 | 28.55%
ALLEGHANY 1101804 | ALLEGHANY 1101 | SIERRA | 21.9183 | 93.3631 | 99.35% | 2 | 14 | 100% | 31.47% | 0 | 0.15061 | 85.4511 | 1.7753 | 22.8471 | High | High | Low | 341 | 256 | 12.8696 | 2535.8597 | 28.41%
MONTE RIO 111264682 | MONTE RIO 1112 | SONOMA | 1.7634 | 73.4411 | 19.23% | 8 | 4 | 100% | 100% | 0 | 0.12546 | 102.1389 | 3.654 | 46.8247 | High | High | High | 157 | 257 | 12.8145 | 2522.9901 | 28.26%
SHADY GLEN 11022232 | SHADY GLEN 1102 | SIERRA | 10.57 | 94.8997 | 90.23% | 5 | 11 | 100% | 60.37% | 0 | 0.14836 | 85.4511 | 1.2808 | 16.2381 | High | High | Low | 398 | 258 | 12.6776 | 2510.1757 | 28.12%
MENDOCINO 110148750 | MENDOCINO 1101 | HUMBOLDT | 17.302 | 87.2326 | 98.93% | 5 | 5 | 100% | 70.23% | 0 | 0.19367 | 65.3912 | 1.5047 | 19.056 | High | High | Low | 369 | 259 | 12.6646 | 2497.4981 | 27.98%
CURTIS 17022123 | CURTIS 1702 | YOSEMITE | 1.861 | 56.934 | 100% | 1 | 0 | 100% | 100% | 0 | 0.19293 | 65.3912 | 4.0222 | 50.7428 | High | High | High | 132 | 260 | 12.6157 | 2484.8334 | 27.84%
WOODACRE 110196844 | WOODACRE 1101 | NORTH BAY | 5.9237 | 87.2691 | 22.46% | 5 | 8 | 100% | 88.33% | 0 | 0.12278 | 102.1389 | 3.7061 | 46.4791 | High | High | High | 162 | 261 | 12.5411 | 2472.2178 | 27.7%
MONTE RIO 11131313 | MONTE RIO 1113 | SONOMA | 1.2316 | 65.332 | 67.8% | 0 | 1 | 100% | 100% | 0 | 0.14614 | 85.4511 | 3.5696 | 44.576 | High | High | High | 177 | 262 | 12.4876 | 2459.6767 | 27.56%
REDBUD 1101323962 | REDBUD 1101 | HUMBOLDT | 18.9728 | 78.4739 | 90.21% | 1 | 14 | 68.24% | 71.99% | 0 | 0.19082 | 65.3912 | 1.8051 | 22.5244 | High | High | Low | 343 | 263 | 12.4782 | 2447.189 | 27.42%
CAMP EVERS 210510294 | CAMP EVERS 2105 | CENTRAL COAST | 8.3995 | 27.1368 | 59.21% | 34 | 11 | 100% | 100% | 0 | 0.26177 | 47.6367 | 3.864 | 48.1828 | High | High | High | 147 | 264 | 12.4698 | 2434.7108 | 27.28%
WOODACRE 11011456 | WOODACRE 1101 | NORTH BAY | 3.8267 | 75.1652 | 37.76% | 1 | 5 | 100% | 88.56% | 0 | 0.14581 | 85.4511 | 2.0696 | 25.7865 | High | High | Low | 313 | 265 | 12.4595 | 2422.241 | 27.14%
PAUL SWEET 2104 | PAUL SWEET 2104 | CENTRAL COAST | 0.043661 | 75 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18934 | 65.3912 | 3.5423 | 43.8565 | High | High | High | 185 | 266 | 12.3809 | 2409.7815 | 27%
MOLINO 11026917 | MOLINO 1102 | SONOMA | 7.1386 | 86.8229 | 45.11% | 6 | 1 | 100% | 100% | 0 | 0.18864 | 65.3912 | 2.3255 | 28.6861 | High | High | Medium | 286 | 267 | 12.3355 | 2397.4006 | 26.86%
SAN RAFAEL 110863598 | SAN RAFAEL 1108 | NORTH BAY | 1.9128 | 87.2214 | 45.64% | 1 | 1 | 100% | 100% | 0 | 0.14368 | 85.4511 | 4.0853 | 50.1574 | High | High | High | 136 | 268 | 12.2776 | 2385.0651 | 26.72%
CAMP EVERS 210510225 | CAMP EVERS 2105 | CENTRAL COAST | 0.18205 | 47.7189 | 100% | 3 | 0 | 100% | 100% | 0 | 0.1873 | 65.3912 | 3.6862 | 45.1466 | High | High | High | 170 | 269 | 12.2475 | 2372.7875 | 26.58%
SHADY GLEN 1102CB | SHADY GLEN 1102 | SIERRA | 20.4139 | 69.5808 | 89.02% | 6 | 13 | 95.14% | 27.66% | 0 | 0.14313 | 85.4511 | 1.7682 | 21.6268 | High | High | Low | 349 | 270 | 12.231 | 2360.54 | 26.44%
OAKHURST 11015490 | OAKHURST 1101 | YOSEMITE | 24.9631 | 65.8497 | 73.62% | 1 | 51 | 100% | 0% | 0 | 0.18555 | 65.3912 | 2.5688 | 31.1673 | High | High | Medium | 266 | 271 | 12.1331 | 2348.309 | 26.31%
ALTO 1125510 | ALTO 1125 | NORTH BAY | 7.3822 | 55.9602 | 19.39% | 13 | 14 | 100% | 100% | 0 | 0.45487 | 26.5534 | 4.0428 | 48.8305 | High | High | High | 140 | 272 | 12.0783 | 2336.1759 | 26.17%
APPLE HILL 110412842 | APPLE HILL 1104 | SIERRA | 15.4186 | 86.4877 | 86.23% | 1 | 6 | 91.92% | 56.31% | 0 | 0.11821 | 102.1389 | 2.0647 | 24.9288 | High | High | Low | 320 | 273 | 12.0736 | 2324.0976 | 26.04%
PAUL SWEET 21045394 | PAUL SWEET 2104 | CENTRAL COAST | 14.2856 | 38.4642 | 72.86% | 5 | 2 | 93.82% | 100% | 0 | 0.25339 | 47.6367 | 3.5996 | 43.4504 | High | High | High | 191 | 274 | 12.0708 | 2312.024 | 25.9%
WILLOW CREEK 11015002 | WILLOW CREEK 1101 | HUMBOLDT | 12.8071 | 51.1134 | 93.52% | 24 | 21 | 94.53% | 2.43% | 0 | 0.18408 | 65.3912 | 1.5331 | 18.4537 | High | High | Low | 381 | 275 | 12.0369 | 2299.9532 | 25.77%
OAKLAND X 1106CR020 | OAKLAND X 1106 | EAST BAY | 2.4457 | 82.3898 | 55.47% | 10 | 1 | 100% | 99.48% | 0 | 0.18349 | 65.3912 | 3.4295 | 41.1503 | High | High | High | 203 | 276 | 11.9989 | 2287.9163 | 25.63%
CAMP EVERS 21061625 | CAMP EVERS 2106 | CENTRAL COAST | 0.904 | 67.0004 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18108 | 65.3912 | 3.8121 | 45.1386 | High | High | High | 171 | 277 | 11.841 | 2275.9174 | 25.5%
BELLEVUE 2103646 | BELLEVUE 2103 | SONOMA | 9.4191 | 67.7942 | 94.53% | 3 | 3 | 77.28% | 93.12% | 0 | 0.17965 | 65.3912 | 2.4439 | 28.7093 | High | High | Medium | 285 | 278 | 11.7473 | 2264.0765 | 25.36%
BURNS 2101 | BURNS 2101 | CENTRAL COAST | 0.0053489 | 65 | 100% | 0 | 0 | 100% | 100% | 0 | 0.17906 | 65.3912 | 3.488 | 40.84 | High | High | High | 207 | 279 | 11.7089 | 2252.3292 | 25.23%
POINT MORETTI 1101 | POINT MORETTI 1101 | CENTRAL COAST | 0.0096753 | 65 | 100% | 0 | 0 | 100% | 100% | 0 | 0.17906 | 65.3912 | 3.4875 | 40.8347 | High | High | High | 208 | 279 | 11.7089 | 2240.6204 | 25.1%
SHINGLE SPRINGS 210519522 | SHINGLE SPRINGS 2105 | SIERRA | 9.9042 | 70.9474 | 99.53% | 2 | 6 | 96.11% | 80.98% | 0 | 0.17524 | 65.3912 | 2.9822 | 34.1738 | High | High | Medium | 248 | 281 | 11.4593 | 2228.9115 | 24.97%
SILVERADO 210258626 | SILVERADO 2102 | NORTH BAY | 15.2462 | 83.9933 | 97.52% | 2 | 7 | 100% | 88.88% | 0 | 0.23976 | 47.6367 | 2.967 | 33.8868 | High | High | Medium | 250 | 282 | 11.4212 | 2217.4522 | 24.84%
LAS GALLINAS A 110599904 | LAS GALLINAS A 1105 | NORTH BAY | 5.5637 | 84.5434 | 55.29% | 2 | 2 | 100% | 100% | 0 | 0.17422 | 65.3912 | 3.4864 | 39.7192 | High | High | High | 213 | 283 | 11.3927 | 2206.031 | 24.71%
PARADISE 11022098 | PARADISE 1102 | NORTH VALLEY | 4.2185 | 79.6766 | 65.19% | 0 | 7 | 42.14% | 100% | 0 | 0.13292 | 85.4511 | 3.448 | 39.1629 | High | High | High | 217 | 284 | 11.3582 | 2194.6382 | 24.59%
WOODSIDE 11018972 | WOODSIDE 1101 | PENINSULA | 6.2078 | 92.0365 | 25.89% | 9 | 0 | 100% | 100% | 1 | 0.17321 | 65.3912 | 2.1359 | 24.1909 | High | High | Low | 327 | 285 | 11.3261 | 2183.28 | 24.46%
BRUNSWICK 110663124 | BRUNSWICK 1106 | SIERRA | 5.9024 | 71.9691 | 59.9% | 2 | 1 | 100% | 94.93% | 0 | 0.17164 | 65.3912 | 2.8195 | 31.6447 | High | High | Medium | 260 | 286 | 11.2236 | 2171.9539 | 24.33%
MONTE RIO 11111701 | MONTE RIO 1111 | SONOMA | 1.3661 | 76.5396 | 84.13% | 0 | 0 | 100% | 100% | 0 | 0.17154 | 65.3912 | 2.6378 | 29.5889 | High | High | Medium | 276 | 287 | 11.217 | 2160.7304 | 24.21%
MIWUK 17021808 | MIWUK 1702 | YOSEMITE | 1.8341 | 72.798 | 17.3% | 1 | 2 | 100% | 100% | 0 | 0.10942 | 102.1389 | 4.1225 | 46.0745 | High | High | High | 165 | 288 | 11.1764 | 2149.5133 | 24.08%
PARADISE 11011212 | PARADISE 1101 | NORTH VALLEY | 8.5723 | 27.6396 | 21.52% | 13 | 13 | 100% | 100% | 0 | 0.17074 | 65.3912 | 3.8308 | 42.7709 | High | High | High | 193 | 289 | 11.1651 | 2138.3369 | 23.96%
MONTE RIO 1112999 | MONTE RIO 1112 | SONOMA | 0.78347 | 81.1849 | 29.39% | 4 | 2 | 100% | 100% | 0 | 0.13014 | 85.4511 | 2.5578 | 28.4436 | High | High | Medium | 288 | 290 | 11.1202 | 2127.1718 | 23.83%
GRASS VALLEY 11012766 | GRASS VALLEY 1101 | SIERRA | 3.3601 | 83.6304 | 59.47% | 0 | 1 | 100% | 75.75% | 0 | 0.10872 | 102.1389 | 2.6373 | 29.2861 | High | High | Medium | 278 | 291 | 11.1047 | 2116.0516 | 23.71%
SAN RAFAEL 11081247 | SAN RAFAEL 1108 | NORTH BAY | 0.2757 | 81.1642 | 57.56% | 3 | 0 | 100% | 100% | 0 | 0.16951 | 65.3912 | 4.0604 | 45.007 | High | High | High | 173 | 292 | 11.0844 | 2104.9469 | 23.58%
BUCKS CREEK 11031131 | BUCKS CREEK 1103 | NORTH VALLEY | 2.7493 | 88.8735 | 99.9% | 0 | 1 | 100% | 56.92% | 0 | 0.12924 | 85.4511 | 0.34069 | 3.7624 | High | High | Low | 632 | 293 | 11.0435 | 2093.8625 | 23.46%
ORO FINO 1102127563 | ORO FINO 1102 | NORTH VALLEY | 6.9027 | 86.7717 | 100% | 0 | 2 | 100% | 100% | 1 | 0.23179 | 47.6367 | 2.1334 | 23.5558 | High | High | Low | 333 | 294 | 11.0415 | 2082.819 | 23.33%
WEST POINT 110293116 | WEST POINT 1102 | STOCKTON | 24.1031 | 66.8044 | 100% | 9 | 9 | 100% | 51.27% | 1 | 0.16857 | 65.3912 | 2.3737 | 26.1657 | High | High | Medium | 310 | 295 | 11.0231 | 2071.7775 | 23.21%
MIRABEL 11014859 | MIRABEL 1101 | SONOMA | 1.8526 | 77.0765 | 99.9% | 8 | 0 | 100% | 100% | 0 | 0.23121 | 47.6367 | 2.7808 | 30.6275 | High | High | Medium | 272 | 296 | 11.014 | 2060.7543 | 23.09%
ORO FINO 11022040 | ORO FINO 1102 | NORTH VALLEY | 9.1589 | 98 | 100% | 4 | 1 | 100% | 12.34% | 0 | 0.10744 | 102.1389 | 1.639 | 17.9858 | High | High | Low | 387 | 297 | 10.9734 | 2049.7403 | 22.96%
BEAR VALLEY 210513430 | BEAR VALLEY 2105 | YOSEMITE | 13.3191 | 78.8388 | 99.94% | 4 | 1 | 100% | 48.72% | 0 | 0.12752 | 85.4511 | 2.1818 | 23.7734 | High | High | Low | 331 | 298 | 10.8965 | 2038.7669 | 22.84%
MIRABEL 1102332 | MIRABEL 1102 | SONOMA | 5.7552 | 66.9134 | 43.76% | 9 | 11 | 100% | 100% | 1 | 0.16469 | 65.3912 | 2.8565 | 30.7615 | High | High | Medium | 270 | 299 | 10.7691 | 2027.8705 | 22.72%
OAKLAND K 110217430 | OAKLAND K 1102 | EAST BAY | 2.0764 | 84.0676 | 31.48% | 0 | 1 | 100% | 100% | 0 | 0.12601 | 85.4511 | 3.0426 | 32.7603 | High | High | Medium | 256 | 300 | 10.7674 | 2017.1014 | 22.6%
MIWUK 17029270 | MIWUK 1702 | YOSEMITE | 5.8553 | 48.3944 | 46.92% | 2 | 9 | 100% | 95.13% | 0 | 0.12583 | 85.4511 | 3.8062 | 40.9252 | High | High | High | 206 | 301 | 10.7524 | 2006.3341 | 22.48%
PARADISE 1106CB | PARADISE 1106 | NORTH VALLEY | 4.354 | 81.9365 | 3.23% | 2 | 3 | 96.39% | 100% | 0 | 0.10412 | 102.1389 | 3.6651 | 38.9782 | High | High | High | 219 | 302 | 10.6351 | 1995.5817 | 22.36%
PLACERVILLE 210692012 | PLACERVILLE 2106 | SIERRA | 18.5713 | 72.0312 | 64.51% | 6 | 1 | 100% | 92.15% | 0 | 0.22084 | 47.6367 | 2.5843 | 27.1879 | High | High | Medium | 300 | 303 | 10.5203 | 1984.9466 | 22.24%
MONTE RIO 1111240 | MONTE RIO 1111 | SONOMA | 3.0687 | 71.6003 | 66.68% | 5 | 7 | 100% | 100% | 0 | 0.21886 | 47.6367 | 2.6045 | 27.1546 | High | High | Medium | 301 | 304 | 10.4259 | 1974.4264 | 22.12%
BIG BEND 1101180398 | BIG BEND 1101 | NORTH VALLEY | 5.6176 | 75.1769 | 68.58% | 0 | 2 | 100% | 100% | 0 | 0.15837 | 65.3912 | 2.3657 | 24.4991 | High | High | Medium | 323 | 305 | 10.3561 | 1964.0005 | 22%
MIRABEL 1101116 | MIRABEL 1101 | SONOMA | 9.7562 | 60.7427 | 68.47% | 10 | 5 | 91.79% | 57.41% | 1 | 0.21711 | 47.6367 | 3.2592 | 33.7085 | High | High | High | 252 | 306 | 10.3426 | 1953.6444 | 21.89%
MONTE RIO 11131137 | MONTE RIO 1113 | SONOMA | 2.8427 | 88.9858 | 48.94% | 0 | 5 | 100% | 100% | 0 | 0.15775 | 65.3912 | 2.9968 | 30.9141 | High | High | Medium | 268 | 307 | 10.3156 | 1943.3018 | 21.77%
PARADISE 110135976 | PARADISE 1101 | NORTH VALLEY | 3.5298 | 50.3669 | 45.43% | 3 | 2 | 100% | 100% | 0 | 0.1201 | 85.4511 | 3.7758 | 38.7488 | High | High | High | 223 | 308 | 10.2625 | 1932.9862 | 21.65%
BRUNSWICK 1106CB | BRUNSWICK 1106 | SIERRA | 8.5018 | 76.2711 | 34.63% | 3 | 2 | 96.43% | 63.8% | 0 | 0.11976 | 85.4511 | 2.733 | 27.9679 | High | High | Medium | 292 | 309 | 10.2335 | 1922.7236 | 21.54%
SHINGLE SPRINGS 110419502 | SHINGLE SPRINGS 1104 | SIERRA | 42.2119 | 45.6817 | 99.02% | 5 | 5 | 73.54% | 87.16% | 0 | 0.15459 | 65.3912 | 2.57 | 25.9791 | High | High | Medium | 311 | 310 | 10.1086 | 1912.4901 | 21.43%
TIGER CREEK 0201CB | TIGER CREEK 0201 | STOCKTON | 3.8998 | 93.0419 | 100% | 1 | 1 | 100% | 66.65% | 0 | 0.15361 | 65.3912 | 2.2115 | 22.2145 | High | High | Low | 345 | 311 | 10.0449 | 1902.3816 | 21.31%
DUNBAR 11021249 | DUNBAR 1102 | SONOMA | 13.5745 | 82.3664 | 58.44% | 5 | 8 | 100% | 36.11% | 1 | 0.11715 | 85.4511 | 2.6217 | 26.2453 | High | High | Medium | 309 | 312 | 10.0108 | 1892.3367 | 21.2%
VOLTA 11021502 | VOLTA 1102 | NORTH VALLEY | 7.6156 | 84.4703 | 99.46% | 2 | 2 | 100% | 100% | 0 | 0.2099 | 47.6367 | 2.778 | 27.777 | High | High | Medium | 293 | 313 | 9.999 | 1882.3258 | 21.09%
MIRABEL 11022043 | MIRABEL 1102 | SONOMA | 0.56871 | 88.7155 | 17.22% | 0 | 1 | 100% | 100% | 0 | 0.11685 | 85.4511 | 2.8327 | 28.2828 | High | High | Medium | 289 | 314 | 9.9846 | 1872.3269 | 20.98%
CABRILLO 1103Y12 | CABRILLO 1103 | LOS PADRES | 26.1562 | 62.7349 | 69.42% | 1 | 11 | 84.42% | 0% | 0 | 0.20939 | 47.6367 | 3.1607 | 31.5264 | High | High | High | 263 | 315 | 9.9744 | 1862.3423 | 20.86%
WILLOW CREEK 1102CB | WILLOW CREEK 1102 | HUMBOLDT | 7.3308 | 78.4297 | 99.3% | 9 | 9 | 100% | 47.32% | 0 | 0.15188 | 65.3912 | 1.3937 | 13.8422 | High | High | Low | 423 | 316 | 9.9319 | 1852.3678 | 20.75%
CALPINE 1146200-G | CALPINE 1146 | SONOMA | 0.0085256 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 47.6367 | 1.8538 | 18.1558 | High | High | Low | 383 | 317 | 9.7937 | 1842.436 | 20.64%
CALPINE 1146394G | CALPINE 1146 | SONOMA | 0.011293 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 47.6367 | 1.8534 | 18.1516 | High | High | Low | 384 | 317 | 9.7937 | 1832.6423 | 20.53%
SCE REFUGIO 1101CB | SCE REFUGIO 1101 | LOS PADRES | 0.29161 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 47.6367 | 1.5755 | 15.4297 | High | High | Low | 408 | 317 | 9.7937 | 1822.8487 | 20.42%
MONTE RIO 11113891 | MONTE RIO 1111 | SONOMA | 3.5454 | 89.5117 | 50.47% | 2 | 0 | 100% | 100% | 1 | 0.14965 | 65.3912 | 2.2281 | 21.8036 | High | High | Low | 347 | 320 | 9.7859 | 1813.055 | 20.31%
PARADISE 11042472 | PARADISE 1104 | NORTH VALLEY | 7.3384 | 31.16 | 42.96% | 7 | 6 | 100% | 100% | 0 | 0.14941 | 65.3912 | 3.8266 | 37.3865 | High | High | High | 231 | 321 | 9.7702 | 1803.2691 | 20.2%
ROSSMOOR 110837848 | ROSSMOOR 1108 | DIABLO | 5.9561 | 79.6593 | 23.72% | 0 | 5 | 100% | 88.12% | 0 | 0.14934 | 65.3912 | 4.0336 | 39.3891 | High | High | High | 216 | 322 | 9.7653 | 1793.4989 | 20.09%
CLAYTON 22122951 | CLAYTON 2212 | DIABLO | 10.1032 | 61.4187 | 78.88% | 4 | 1 | 100% | 100% | 0 | 0.27294 | 35.3263 | 3.2196 | 31.0433 | High | High | High | 267 | 323 | 9.6421 | 1783.7335 | 19.98%
CLARKSVILLE 210413352 | CLARKSVILLE 2104 | SIERRA | 32.6724 | 49.7642 | 94.33% | 3 | 19 | 89.71% | 64.9% | 0 | 0.20162 | 47.6367 | 3.1662 | 30.4103 | High | High | High | 274 | 324 | 9.6046 | 1774.0915 | 19.87%
PLACERVILLE 21062224 | PLACERVILLE 2106 | SIERRA | 10.4972 | 65.7358 | 76.35% | 3 | 1 | 100% | 100% | 0 | 0.2002 | 47.6367 | 3.3086 | 31.5533 | High | High | High | 262 | 325 | 9.5368 | 1764.4869 | 19.77%
OAKHURST 11035120 | OAKHURST 1103 | YOSEMITE | 6.3491 | 97.3123 | 0.04473% | 0 | 2 | 100% | 100% | 0 | 0.11061 | 85.4511 | 1.6703 | 15.7864 | High | High | Low | 404 | 326 | 9.4514 | 1754.9501 | 19.66%
MONTE RIO 1113532 | MONTE RIO 1113 | SONOMA | 0.51993 | 90.7851 | 10.39% | 0 | 0 | 100% | 100% | 0 | 0.11048 | 85.4511 | 2.896 | 27.3401 | High | High | Medium | 298 | 327 | 9.4408 | 1745.4987 | 19.55%
OTTER 11012052 | OTTER 1101 | CENTRAL COAST | 4.8416 | 80.234 | 20.15% | 9 | 2 | 100% | 100% | 0 | 0.14395 | 65.3912 | 1.7174 | 16.1669 | High | High | Low | 399 | 328 | 9.4134 | 1736.0579 | 19.45%
MORAGA 1105CB | MORAGA 1105 | DIABLO | 7.1365 | 67.7298 | 20.75% | 5 | 12 | 65.86% | 77.06% | 1 | 0.092052 | 102.1389 | 3.9271 | 36.9227 | High | High | High | 234 | 329 | 9.4021 | 1726.6446 | 19.34%
ROB ROY 21055166 | ROB ROY 2105 | CENTRAL COAST | 5.4938 | 45.154 | 99.95% | 6 | 2 | 100% | 100% | 0 | 0.19719 | 47.6367 | 3.3223 | 31.2078 | High | High | High | 264 | 330 | 9.3933 | 1717.2425 | 19.24%
MIDDLETOWN 110148212 | MIDDLETOWN 1101 | HUMBOLDT | 10.2049 | 74.7586 | 62.81% | 5 | 4 | 94.29% | 99.65% | 0 | 0.19647 | 47.6367 | 1.9845 | 18.5737 | High | High | Low | 375 | 331 | 9.3592 | 1707.8492 | 19.13%
MONTE RIO 1112212 | MONTE RIO 1112 | SONOMA | 2.2491 | 44.7156 | 75.38% | 4 | 1 | 100% | 100% | 0 | 0.14298 | 65.3912 | 2.8824 | 26.9492 | High | High | Medium | 303 | 332 | 9.3496 | 1698.49 | 19.03%
BRUNSWICK 11052102 | BRUNSWICK 1105 | SIERRA | 3.6478 | 67.9602 | 63.58% | 1 | 3 | 100% | 48.36% | 1 | 0.091021 | 102.1389 | 2.6251 | 24.4045 | High | High | Medium | 325 | 333 | 9.2968 | 1689.1404 | 18.92%
SILVERADO 2104563322 | SILVERADO 2104 | NORTH BAY | 3.653 | 77.3083 | 48.88% | 3 | 1 | 100% | 100% | 1 | 0.14188 | 65.3912 | 2.9772 | 27.6225 | High | High | Medium | 295 | 334 | 9.2779 | 1679.8436 | 18.82%
WOODSIDE 11018601 | WOODSIDE 1101 | PENINSULA | 0.59795 | 81.8692 | 48.65% | 2 | 0 | 100% | 100% | 0 | 0.14129 | 65.3912 | 3.8817 | 35.8642 | High | High | High | 239 | 335 | 9.2392 | 1670.5657 | 18.72%
MONTE RIO 1111 | MONTE RIO 1111 | SONOMA | 0.032125 | 95 | 0% | 0 | 1 | 100% | 100% | 0 | 0.107 | 85.4511 | 2.6749 | 24.4578 | High | High | Medium | 324 | 336 | 9.1434 | 1661.3264 | 18.61%
BEN LOMOND 04015144 | BEN LOMOND 0401 | CENTRAL COAST | 3.9861 | 45.8832 | 59.52% | 1 | 1 | 100% | 100% | 0 | 0.13946 | 65.3912 | 3.5854 | 32.6969 | High | High | High | 257 | 337 | 9.1195 | 1652.1831 | 18.51%
BIG BASIN 1101CB | BIG BASIN 1101 | CENTRAL COAST | 4.7811 | 77.9416 | 33.87% | 2 | 0 | 100% | 100% | 0 | 0.13944 | 65.3912 | 2.9497 | 26.897 | High | High | Medium | 305 | 338 | 9.1184 | 1643.0635 | 18.41%
WILLOW CREEK 110237374 | WILLOW CREEK 1102 | HUMBOLDT | 2.2967 | 96.0041 | 99.34% | 1 | 0 | 100% | 68.24% | 0 | 0.13938 | 65.3912 | 1.2034 | 10.9677 | High | High | Low | 463 | 339 | 9.1142 | 1633.9451 | 18.3%
WOODACRE 1102851 | WOODACRE 1102 | NORTH BAY | 1.2766 | 60.3664 | 19.35% | 1 | 3 | 100% | 100% | 0 | 0.10492 | 85.4511 | 4.9245 | 44.1492 | High | High | High | 182 | 340 | 8.9652 | 1624.8309 | 18.2%
ATASCADERO 1103A06 | ATASCADERO 1103 | LOS PADRES | 34.0507 | 59.0569 | 96.54% | 3 | 5 | 91.06% | 64.46% | 1 | 0.13601 | 65.3912 | 2.647 | 23.5413 | High | High | Medium | 334 | 341 | 8.8937 | 1615.8656 | 18.1%
VINEYARD 2108MR172 | VINEYARD 2108 | MISSION | 3.1156 | 86.4654 | 47.06% | 1 | 2 | 35.54% | 100% | 1 | 0.13362 | 65.3912 | 3.178 | 27.7695 | High | High | High | 294 | 342 | 8.7379 | 1606.9719 | 18%
STANISLAUS 1702L3151 | STANISLAUS 1702 | YOSEMITE | 0.9933 | 86.9694 | 85.25% | 0 | 0 | 100% | 100% | 0 | 0.1833 | 47.6367 | 2.8637 | 25.0046 | High | High | Medium | 318 | 343 | 8.7317 | 1598.234 | 17.9%
KONOCTI 11024421 | KONOCTI 1102 | HUMBOLDT | 0.36385 | 69.0599 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18318 | 47.6367 | 2.1152 | 18.4571 | High | High | Low | 380 | 344 | 8.726 | 1589.5024 | 17.81%
MOLINO 1102178 | MOLINO 1102 | SONOMA | 13.3443 | 48.7979 | 52.24% | 13 | 10 | 88.89% | 58.63% | 0 | 0.18298 | 47.6367 | 2.8177 | 24.5608 | High | High | Medium | 321 | 345 | 8.7167 | 1580.7764 | 17.71%
COARSEGOLD 21045310 | COARSEGOLD 2104 | YOSEMITE | 17.6177 | 41.6297 | 82.56% | 2 | 60 | 100% | 0% | 0 | 0.18205 | 47.6367 | 2.2493 | 19.5069 | High | High | Medium | 364 | 346 | 8.6723 | 1572.0597 | 17.61%
BRUNSWICK 11051030 | BRUNSWICK 1105 | SIERRA | 4.9418 | 79.0296 | 79.8% | 3 | 3 | 100% | 45.4% | 0 | 0.084675 | 102.1389 | 2.4972 | 21.5975 | High | High | Medium | 351 | 347 | 8.6486 | 1563.3874 | 17.51%
SHINGLE SPRINGS 21092679 | SHINGLE SPRINGS 2109 | SIERRA | 7.0526 | 59.0742 | 100% | 0 | 2 | 100% | 100% | 1 | 0.17927 | 47.6367 | 2.7934 | 23.8549 | High | High | Medium | 330 | 348 | 8.5398 | 1554.7389 | 17.42%
PARADISE 11015185 | PARADISE 1101 | NORTH VALLEY | 0.8075 | 38.303 | 73.08% | 0 | 1 | 100% | 100% | 0 | 0.12937 | 65.3912 | 3.7374 | 31.6174 | High | High | High | 261 | 349 | 8.4598 | 1546.199 | 17.32%
POINT MORETTI 110136516 | POINT MORETTI 1101 | CENTRAL COAST | 4.1652 | 32.5436 | 68.9% | 12 | 2 | 100% | 100% | 0 | 0.17749 | 47.6367 | 3.4455 | 29.1317 | High | High | High | 280 | 350 | 8.4551 | 1537.7393 | 17.23%
GARBERVILLE 11022500 | GARBERVILLE 1102 | HUMBOLDT | 16.0185 | 91.6655 | 50.61% | 18 | 6 | 100% | 0% | 0 | 0.098692 | 85.4511 | 1.4185 | 11.9622 | High | High | Low | 446 | 351 | 8.4333 | 1529.2842 | 17.13%
SARATOGA 1107167792 | SARATOGA 1107 | DE ANZA | 4.6876 | 89.4882 | 89.82% | 13 | 1 | 100% | 18.23% | 0 | 0.1289 | 65.3912 | 3.2524 | 27.4146 | High | High | High | 297 | 352 | 8.429 | 1520.8509 | 17.04%
MIWUK 170236888 | MIWUK 1702 | YOSEMITE | 0.61573 | 72.472 | 39.92% | 0 | 2 | 100% | 100% | 0 | 0.12726 | 65.3912 | 3.3823 | 28.1466 | High | High | High | 291 | 353 | 8.3216 | 1512.4218 | 16.94%
FULTON 110777670 | FULTON 1107 | SONOMA | 6.8809 | 26.8333 | 74.89% | 3 | 6 | 100% | 100% | 0 | 0.17389 | 47.6367 | 2.3868 | 19.7715 | High | High | Medium | 361 | 354 | 8.2837 | 1504.1002 | 16.85%
KANAKA 11011044 | KANAKA 1101 | NORTH VALLEY | 6.134 | 63.1535 | 33.69% | 2 | 5 | 100% | 70.49% | 0 | 0.080757 | 102.1389 | 2.2945 | 18.9261 | High | High | Medium | 370 | 355 | 8.2484 | 1495.8165 | 16.76%
CORRAL 1101CB | CORRAL 1101 | STOCKTON | 26.1508 | 58.878 | 76.15% | 2 | 13 | 95.28% | 0% | 0 | 0.12599 | 65.3912 | 2.1911 | 18.0518 | High | High | Low | 385 | 356 | 8.2388 | 1487.5681 | 16.67%
MONTE RIO 11125040 | MONTE RIO 1112 | SONOMA | 3.9901 | 73.555 | 15.29% | 9 | 5 | 100% | 100% | 1 | 0.12574 | 65.3912 | 2.5232 | 20.7454 | High | High | Medium | 355 | 357 | 8.222 | 1479.3293 | 16.57%
PARADISE 11022206 | PARADISE 1102 | NORTH VALLEY | 5.1983 | 53.3962 | 55.37% | 4 | 4 | 89% | 100% | 0 | 0.12523 | 65.3912 | 3.7528 | 30.7318 | High | High | High | 271 | 358 | 8.1891 | 1471.1073 | 16.48%
VOLTA 110237350 | VOLTA 1102 | NORTH VALLEY | 24.2981 | 64.1392 | 95.8% | 2 | 5 | 100% | 58.24% | 1 | 0.17108 | 47.6367 | 1.7111 | 13.9446 | High | High | Low | 422 | 359 | 8.1495 | 1462.9181 | 16.39%
SHINGLE SPRINGS 21092053 | SHINGLE SPRINGS 2109 | SIERRA | 5.7202 | 32.6339 | 100% | 0 | 1 | 100% | 100% | 0 | 0.16944 | 47.6367 | 2.343 | 18.912 | High | High | Medium | 371 | 360 | 8.0716 | 1454.7686 | 16.3%
MONTE RIO 1111256 | MONTE RIO 1111 | SONOMA | 7.2865 | 62.779 | 22.47% | 12 | 6 | 100% | 100% | 1 | 0.22703 | 35.3263 | 3.0231 | 24.2464 | High | High | Medium | 326 | 361 | 8.0203 | 1446.697 | 16.21%
CLARKSVILLE 210419632 | CLARKSVILLE 2104 | SIERRA | 5.4715 | 65.8905 | 97.91% | 0 | 0 | 60.07% | 97.91% | 1 | 0.12258 | 65.3912 | 2.9244 | 23.441 | High | High | Medium | 336 | 362 | 8.0156 | 1438.6768 | 16.12%
ALTO 11221212 | ALTO 1122 | NORTH BAY | 1.5919 | 41.9573 | 53.59% | 1 | 4 | 67.44% | 92.64% | 0 | 0.09288 | 85.4511 | 3.6174 | 28.7098 | High | High | High | 284 | 363 | 7.9367 | 1430.6612 | 16.03%
CORRAL 110112608 | CORRAL 1101 | STOCKTON | 35.0176 | 52.1044 | 87.04% | 0 | 19 | 100% | 0% | 0 | 0.16618 | 47.6367 | 1.4909 | 11.8026 | High | High | Low | 447 | 364 | 7.9163 | 1422.7245 | 15.94%
ANNAPOLIS 1101554 | ANNAPOLIS 1101 | HUMBOLDT | 27.1366 | 85.1288 | 100% | 26 | 12 | 100% | 0% | 0 | 0.1656 | 47.6367 | 1.6533 | 13.0418 | High | High | Low | 431 | 365 | 7.8886 | 1414.8082 | 15.85%
FORT ROSS 11212987 | FORT ROSS 1121 | SONOMA | 2.0798 | 87.0149 | 100% | 0 | 1 | 100% | 83.64% | 0 | 0.16552 | 47.6367 | 2.0189 | 15.9187 | High | High | Low | 402 | 366 | 7.8847 | 1406.9196 | 15.76%
OLEMA 110150396 | OLEMA 1101 | NORTH BAY | 12.5505 | 59.0331 | 35.48% | 29 | 15 | 95.94% | 0% | 0 | 0.11931 | 65.3912 | 2.6117 | 20.3759 | High | High | Medium | 357 | 367 | 7.8017 | 1399.0349 | 15.67%
OAKLAND K 1102CB | OAKLAND K 1102 | EAST BAY | 3.0081 | 48.3984 | 19.08% | 4 | 5 | 100% | 100% | 0 | 0.11788 | 65.3912 | 4.048 | 31.203 | High | High | High | 265 | 368 | 7.7083 | 1391.2332 | 15.59%
BRUNSWICK 1105CB | BRUNSWICK 1105 | SIERRA | 2.0209 | 50.1126 | 64.77% | 1 | 2 | 85.09% | 53.11% | 0 | 0.075406 | 102.1389 | 2.6516 | 20.4226 | High | High | Medium | 356 | 369 | 7.7019 | 1383.5249 | 15.5%
BRUNSWICK 11052100 | BRUNSWICK 1105 | SIERRA | 3.9656 | 82.5395 | 61.98% | 2 | 1 | 100% | 39.89% | 0 | 0.074817 | 102.1389 | 2.5653 | 19.6029 | High | High | Medium | 362 | 370 | 7.6417 | 1375.823 | 15.41%
BRUNSWICK 11032784 | BRUNSWICK 1103 | SIERRA | 14.361 | 51.6275 | 64.59% | 9 | 6 | 93.84% | 32.3% | 0 | 0.11661 | 65.3912 | 2.7674 | 21.1031 | High | High | Medium | 352 | 371 | 7.6256 | 1368.1813 | 15.33%
PARADISE 110136042 | PARADISE 1101 | NORTH VALLEY | 2.7098 | 42.4595 | 41.3% | 5 | 3 | 86.87% | 100% | 0 | 0.11607 | 65.3912 | 3.8047 | 28.8767 | High | High | High | 282 | 372 | 7.5898 | 1360.5557 | 15.24%
WOODSIDE 11018912 | WOODSIDE 1101 | PENINSULA | 3.8497 | 42.1497 | 27.37% | 5 | 2 | 96.59% | 100% | 0 | 0.15841 | 47.6367 | 3.5396 | 26.7098 | High | High | High | 306 | 373 | 7.5459 | 1352.966 | 15.16%
PUEBLO 2103 | PUEBLO 2103 | NORTH BAY | 0.012243 | 90 | 0% | 0 | 0 | 100% | 100% | 0 | 0.11472 | 65.3912 | 2.8801 | 21.6062 | High | High | Medium | 350 | 374 | 7.502 | 1345.42 | 15.07%
BURNS 2101CB | BURNS 2101 | CENTRAL COAST | 1.6587 | 56.6807 | 25.38% | 1 | 0 | 100% | 100% | 0 | 0.11419 | 65.3912 | 3.5716 | 26.6705 | High | High | High | 308 | 375 | 7.4673 | 1337.9181 | 14.99%
LOS GATOS 1106LA46 | LOS GATOS 1106 | DE ANZA | 1.5345 | 25.7114 | 95.32% | 1 | 0 | 100% | 100% | 0 | 0.15665 | 47.6367 | 2.6204 | 19.5546 | High | High | Medium | 363 | 376 | 7.4623 | 1330.4507 | 14.9%
WILLITS 1103826 | WILLITS 1103 | HUMBOLDT | 7.7428 | 68.4696 | 97.36% | 4 | 8 | 100% | 35.78% | 0 | 0.11113 | 65.3912 | 2.1617 | 15.7088 | High | High | Low | 407 | 377 | 7.267 | 1322.9884 | 14.82%
FORT ROSS 1121204 | FORT ROSS 1121 | SONOMA | 18.7577 | 93.0498 | 90.41% | 0 | 2 | 100% | 39.05% | 1 | 0.10967 | 65.3912 | 1.5385 | 11.0336 | High | High | Low | 461 | 378 | 7.1716 | 1315.7214 | 14.74%
VOLTA 11021646 | VOLTA 1102 | NORTH VALLEY | 22.2648 | 70.368 | 99.98% | 0 | 4 | 92.24% | 75.72% | 0 | 0.14906 | 47.6367 | 1.9175 | 13.6151 | High | High | Low | 427 | 379 | 7.1006 | 1308.5498 | 14.66%
BIG BASIN 11015000 | BIG BASIN 1101 | CENTRAL COAST | 1.9973 | 72.3321 | 15.8% | 2 | 1 | 100% | 100% | 0 | 0.10717 | 65.3912 | 3.5025 | 24.5467 | High | High | High | 322 | 380 | 7.0083 | 1301.4493 | 14.58%
MONTE RIO 1112CB | MONTE RIO 1112 | SONOMA | 3.7135 | 57.2951 | 17.86% | 14 | 2 | 100% | 100% | 0 | 0.14693 | 47.6367 | 3.2898 | 23.026 | High | High | High | 339 | 381 | 6.9992 | 1294.4409 | 14.5%
WOODSIDE 11011922 | WOODSIDE 1101 | PENINSULA | 3.7722 | 56.2856 | 79.83% | 3 | 6 | 79.05% | 92.98% | 1 | 0.14505 | 47.6367 | 2.5025 | 17.2916 | High | High | Medium | 393 | 382 | 6.9098 | 1287.4418 | 14.42%
SILVERADO 2102 | SILVERADO 2102 | NORTH BAY | 0.0045192 | 80 | 100% | 0 | 0 | 100% | 100% | 0 | 0.19464 | 35.3263 | 2.7872 | 19.1644 | High | High | Medium | 365 | 383 | 6.876 | 1280.532 | 14.35%
BIG BASIN 110110296 | BIG BASIN 1101 | CENTRAL COAST | 14.4399 | 15.6542 | 52.28% | 39 | 5 | 100% | 100% | 0 | 0.45917 | 14.9507 | 3.0498 | 20.9366 | High | High | Medium | 354 | 384 | 6.8649 | 1273.656 | 14.27%
MORAGA 1101108540 | MORAGA 1101 | DIABLO | 4.7825 | 66.0707 | 6.533% | 0 | 5 | 99.19% | 93.66% | 1 | 0.10343 | 65.3912 | 3.6968 | 25.0018 | High | High | High | 319 | 385 | 6.7632 | 1266.7911 | 14.19%
OAKLAND X 1106CR266 | OAKLAND X 1106 | EAST BAY | 1.1822 | 88.5589 | 1.895% | 0 | 0 | 100% | 100% | 0 | 0.10237 | 65.3912 | 3.4355 | 22.9974 | High | High | High | 340 | 386 | 6.6941 | 1260.0279 | 14.12%
CASTRO VALLEY 110810315 | CASTRO VALLEY 1108 | MISSION | 5.494 | 83.0408 | 14.23% | 2 | 0 | 100% | 100% | 0 | 0.14022 | 47.6367 | 3.6086 | 24.1042 | High | High | High | 329 | 387 | 6.6796 | 1253.3338 | 14.04%
CAMP EVERS 21059031 | CAMP EVERS 2105 | CENTRAL COAST | 1.0934 | 18.456 | 18.86% | 2 | 2 | 100% | 100% | 0 | 0.10201 | 65.3912 | 4.0458 | 26.9866 | High | High | High | 302 | 388 | 6.6703 | 1246.6542 | 13.97%
BRIDGEVILLE 1101CB | BRIDGEVILLE 1101 | HUMBOLDT | 8.4707 | 94.1626 | 99.27% | 7 | 0 | 100% | 9.505% | 1 | 0.10184 | 65.3912 | 0.31236 | 2.0801 | High | High | Low | 757 | 389 | 6.6593 | 1239.9838 | 13.89%
GARBERVILLE 110135706 | GARBERVILLE 1101 | HUMBOLDT | 9.7846 | 69.4909 | 86.47% | 18 | 6 | 100% | 0% | 0 | 0.099644 | 65.3912 | 0.74027 | 4.8235 | High | High | Low | 594 | 390 | 6.5159 | 1233.3246 | 13.82%
SILVERADO 2104 | SILVERADO 2104 | NORTH BAY | 0.061489 | 85 | 0% | 0 | 0 | 100% | 100% | 0 | 0.098754 | 65.3912 | 2.8976 | 18.7118 | High | High | Medium | 373 | 391 | 6.4577 | 1226.8087 | 13.74%
TEMPLETON 21136055 | TEMPLETON 2113 | LOS PADRES | 39.7266 | 74.9616 | 83.37% | 3 | 5 | 100% | 12.3% | 1 | 0.24234 | 26.5534 | 0.51413 | 3.3084 | High | High | Low | 655 | 392 | 6.435 | 1220.351 | 13.67%
SANTA ROSA A 1104642 | SANTA ROSA A 1104 | SONOMA | 13.3386 | 23.4287 | 85.18% | 3 | 22 | 100% | 84.73% | 0 | 0.24187 | 26.5534 | 2.5097 | 16.1186 | High | High | Medium | 400 | 393 | 6.4225 | 1213.9161 | 13.6%
CASTRO VALLEY 1108MR748 | CASTRO VALLEY 1108 | MISSION | 6.2273 | 76.3747 | 18.01% | 3 | 1 | 100% | 95.99% | 0 | 0.13481 | 47.6367 | 3.945 | 25.335 | High | High | High | 315 | 394 | 6.422 | 1207.4936 | 13.53%
MIRABEL 11021139 | MIRABEL 1102 | SONOMA | 2.0153 | 64.752 | 50.11% | 2 | 2 | 100% | 100% | 0 | 0.1338 | 47.6367 | 2.9996 | 19.1194 | High | High | Medium | 366 | 395 | 6.374 | 1201.0715 | 13.46%
OAKLAND X 1104CR214 | OAKLAND X 1104 | EAST BAY | 2.8836 | 10 | 25.8% | 4 | 2 | 100% | 100% | 0 | 0.13215 | 47.6367 | 4.2427 | 26.7088 | High | High | High | 307 | 396 | 6.2952 | 1194.6975 | 13.38%
MIDDLETOWN 11011325 | MIDDLETOWN 1101 | HUMBOLDT | 8.5949 | 66.5337 | 99.94% | 1 | 2 | 100% | 100% | 0 | 0.23318 | 26.5534 | 1.9402 | 12.0132 | High | High | Low | 444 | 397 | 6.1918 | 1188.4023 | 13.31%
SAN RAMON 2108CB | SAN RAMON 2108 | MISSION | 8.6488 | 65.614 | 48.13% | 2 | 4 | 90.54% | 100% | 0 | 0.12664 | 47.6367 | 3.1076 | 18.7479 | High | High | High | 372 | 398 | 6.0329 | 1182.2105 | 13.24%
PARADISE 1101CB | PARADISE 1101 | NORTH VALLEY | 2.6336 | 51.0801 | 25.12% | 2 | 4 | 70.38% | 100% | 0 | 0.092062 | 65.3912 | 4.0044 | 24.1067 | High | High | High | 328 | 399 | 6.02 | 1176.1776 | 13.18%
BEN LOMOND 1101BL 1101 | BEN LOMOND 1101 | CENTRAL COAST | 8.6011 | 33.9399 | 41.85% | 31 | 2 | 100% | 100% | 0 | 0.22644 | 26.5534 | 4.227 | 25.4156 | High | High | High | 314 | 400 | 6.0127 | 1170.1576 | 13.11%
OAKHURST 11035470 | OAKHURST 1103 | YOSEMITE | 9.6183 | 65.532 | 32.55% | 7 | 21 | 100% | 20.07% | 0 | 0.090249 | 65.3912 | 2.5209 | 14.8769 | High | High | Medium | 415 | 401 | 5.9015 | 1164.1449 | 13.04%
POINT MORETTI 11015401 | POINT MORETTI 1101 | CENTRAL COAST | 2.5449 | 35.7837 | 49.53% | 3 | 0 | 100% | 100% | 0 | 0.12284 | 47.6367 | 3.0798 | 18.0223 | High | High | High | 386 | 402 | 5.8517 | 1158.2434 | 12.98%
TEMPLETON 2113A10 | TEMPLETON 2113 | LOS PADRES | 30.9401 | 69.101 | 70.57% | 5 | 5 | 100% | 93.66% | 0 | 0.21943 | 26.5534 | 1.2694 | 7.3966 | High | High | Low | 527 | 403 | 5.8266 | 1152.3916 | 12.91%
SILVERADO 21038401 | SILVERADO 2103 | NORTH BAY | 0.63211 | 87.9301 | 93.73% | 0 | 0 | 9.105% | 100% | 0 | 0.088787 | 65.3912 | 2.1595 | 12.5377 | High | High | Low | 439 | 404 | 5.8059 | 1146.565 | 12.84%
BRUNSWICK 110750010 | BRUNSWICK 1107 | SIERRA | 4.0845 | 61.0721 | 60.14% | 3 | 2 | 43.91% | 47.61% | 1 | 0.056677 | 102.1389 | 3.1817 | 18.4187 | Medium | Medium | High | 382 | 405 | 5.789 | 1140.7591 | 12.78%
MIDDLETOWN 1101CB | MIDDLETOWN 1101 | HUMBOLDT | 8.5904 | 74.5605 | 79.65% | 0 | 4 | 45.66% | 67.1% | 0 | 0.067737 | 85.4511 | 2.5869 | 14.9736 | High | High | Medium | 413 | 406 | 5.7882 | 1134.9702 | 12.71%
BEN LOMOND 110196738 | BEN LOMOND 1101 | CENTRAL COAST | 6.8007 | 19.3556 | 74.88% | 14 | 2 | 100% | 100% | 0 | 0.21743 | 26.5534 | 3.7528 | 21.6668 | High | High | High | 348 | 407 | 5.7735 | 1129.1819 | 12.65%
CAMP EVERS 210510786 | CAMP EVERS 2105 | CENTRAL COAST | 4.5287 | 29.7458 | 98.51% | 7 | 0 | 100% | 100% | 1 | 0.21707 | 26.5534 | 4.044 | 23.3096 | High | High | High | 338 | 408 | 5.764 | 1123.4084 | 12.59%
SHINGLE SPRINGS 210551738 | SHINGLE SPRINGS 2105 | SIERRA | 0.38011 | 59.0013 | 92.98% | 0 | 0 | 33.17% | 96.59% | 0 | 0.087308 | 65.3912 | 3.0193 | 17.2376 | High | High | Medium | 394 | 409 | 5.7091 | 1117.6445 | 12.52%
CAMP EVERS 210533542 | CAMP EVERS 2105 | CENTRAL COAST | 2.4779 | 18.5991 | 43.01% | 16 | 2 | 100% | 100% | 0 | 0.1603 | 35.3263 | 3.5621 | 20.1718 | High | High | High | 358 | 410 | 5.6629 | 1111.9353 | 12.46%
CALISTOGA 1102706 | CALISTOGA 1102 | NORTH BAY | 0.14479 | 80 | 100% | 0 | 1 | 2.91% | 100% | 0 | 0.085322 | 65.3912 | 3.5861 | 20.0081 | High | High | High | 359 | 411 | 5.5793 | 1106.2724 | 12.39%
PUEBLO 2102618 | PUEBLO 2102 | NORTH BAY | 2.0485 | 88.1559 | 93.93% | 0 | 0 | 12.3% | 100% | 0 | 0.11649 | 47.6367 | 3.1658 | 17.5673 | High | High | High | 390 | 412 | 5.5491 | 1100.6931 | 12.33%
SAN RAMON 210853732 | SAN RAMON 2108 | MISSION | 7.923 | 73.3065 | 51.9% | 0 | 2 | 100% | 100% | 0 | 0.15613 | 35.3263 | 3.1822 | 17.5521 | High | High | High | 391 | 413 | 5.5156 | 1095.144 | 12.27%
CASTRO VALLEY 11068971 | CASTRO VALLEY 1106 | MISSION | 7.918 | 68.6499 | 16.36% | 0 | 1 | 100% | 100% | 0 | 0.11574 | 47.6367 | 3.3887 | 18.6837 | High | High | High | 374 | 414 | 5.5135 | 1089.6284 | 12.21%
VOLTA 1102CB | VOLTA 1102 | NORTH VALLEY | 3.2998 | 84.686 | 16.79% | 3 | 0 | 100% | 100% | 0 | 0.11557 | 47.6367 | 2.3012 | 12.6696 | High | High | Medium | 434 | 415 | 5.5056 | 1084.1149 | 12.15%
GARBERVILLE 11028652 | GARBERVILLE 1102 | HUMBOLDT | 13.0139 | 91.1649 | 97.21% | 18 | 2 | 100% | 0% | 0 | 0.11424 | 47.6367 | 1.5713 | 8.5506 | High | High | Low | 500 | 416 | 5.4418 | 1078.6093 | 12.08%
KONOCTI 110275382 | KONOCTI 1102 | HUMBOLDT | 21.8665 | 65.7136 | 85.11% | 11 | 7 | 94.25% | 84.3% | 0 | 0.27016 | 19.9979 | 2.0627 | 11.1439 | High | High | Low | 457 | 417 | 5.4025 | 1073.1675 | 12.02%
POINT MORETTI 11015078 | POINT MORETTI 1101 | CENTRAL COAST | 14.6844 | 28.4071 | 32.64% | 18 | 2 | 100% | 99.93% | 1 | 0.2007 | 26.5534 | 3.3009 | 17.5911 | High | High | High | 389 | 418 | 5.3293 | 1067.7649 | 11.96%
DUNBAR 1101302 | DUNBAR 1101 | SONOMA | 7.7166 | 55.3691 | 64.87% | 1 | 11 | 75.08% | 68.56% | 0 | 0.15076 | 35.3263 | 2.7974 | 14.8986 | High | High | Medium | 414 | 419 | 5.3259 | 1062.4357 | 11.9%
FRUITLAND 114293234 | FRUITLAND 1142 | HUMBOLDT | 11.3813 | 94.4975 | 76.78% | 16 | 5 | 100% | 0% | 0 | 0.081313 | 65.3912 | 1.4517 | 7.7189 | High | High | Low | 522 | 420 | 5.3172 | 1057.1098 | 11.84%
FORT ROSS 11214947 | FORT ROSS 1121 | SONOMA | 10.2762 | 93.0727 | 99.97% | 4 | 1 | 100% | 8.448% | 0 | 0.11096 | 47.6367 | 1.71 | 9.0384 | High | High | Low | 491 | 421 | 5.2856 | 1051.7926 | 11.78%
PHILO 11022600 | PHILO 1102 | HUMBOLDT | 19.2386 | 94.0358 | 55.52% | 12 | 3 | 96.16% | 0% | 0 | 0.060847 | 85.4511 | 1.2847 | 6.6795 | Medium | Medium | Low | 545 | 422 | 5.1995 | 1046.5069 | 11.72%
PETALUMA C 1108208 | PETALUMA C 1108 | SONOMA | 12.4029 | 84.7631 | 33.65% | 1 | 1 | 100% | 0% | 0 | 0.07858 | 65.3912 | 2.287 | 11.7516 | High | High | Medium | 450 | 423 | 5.1384 | 1041.3075 | 11.67%
MIDDLETOWN 1101622 | MIDDLETOWN 1101 | HUMBOLDT | 15.6831 | 77.1942 | 76.84% | 4 | 8 | 78.63% | 70.55% | 1 | 0.1922 | 26.5534 | 2.3118 | 11.7983 | High | High | Medium | 448 | 424 | 5.1034 | 1036.169 | 11.61%
BIG BASIN 11029741 | BIG BASIN 1102 | CENTRAL COAST | 0.65144 | 10 | 32.18% | 5 | 0 | 100% | 100% | 0 | 0.10666 | 47.6367 | 2.8083 | 14.2687 | High | High | Medium | 419 | 425 | 5.0809 | 1031.0656 | 11.55%
SANTA ROSA A 1104716 | SANTA ROSA A 1104 | SONOMA | 8.9162 | 55.6538 | 91.58% | 1 | 3 | 100% | 100% | 0 | 0.19056 | 26.5534 | 2.7943 | 14.1391 | High | High | Medium | 420 | 426 | 5.06 | 1025.9847 | 11.49%
PARADISE 1105CB | PARADISE 1105 | NORTH VALLEY | 3.6905 | 42.5038 | 17.46% | 4 | 4 | 44.69% | 100% | 0 | 0.058684 | 85.4511 | 3.9436 | 19.7758 | Medium | Medium | High | 360 | 427 | 5.0146 | 1020.9247 | 11.44%
RACETRACK 1704CB | RACETRACK 1704 | YOSEMITE | 22.0312 | 55.84 | 32.56% | 4 | 25 | 99.99% | 0% | 0 | 0.18885 | 26.5534 | 2.0435 | 10.2471 | High | High | Low | 470 | 428 | 5.0145 | 1015.91 | 11.38%
APPLE HILL 110412947 | APPLE HILL 1104 | SIERRA | 3.4561 | 89.425 | 100% | 0 | 1 | 100% | 0% | 0 | 0.04907 | 102.1389 | 2.1335 | 10.6933 | Medium | Medium | Low | 466 | 429 | 5.012 | 1010.8955 | 11.32%
RINCON 11035152 | RINCON 1103 | SONOMA | 1.5925 | 84.6014 | 46.06% | 2 | 0 | 100% | 100% | 0 | 0.14097 | 35.3263 | 2.5132 | 12.5158 | High | High | Medium | 440 | 430 | 4.9799 | 1005.8835 | 11.27%
HOOPA 11017468 | HOOPA 1101 | HUMBOLDT | 5.6936 | 54.3189 | 96.19% | 3 | 8 | 47.51% | 49.77% | 1 | 0.076067 | 65.3912 | 1.7487 | 8.6983 | High | High | Low | 499 | 431 | 4.9741 | 1000.9036 | 11.21%
MONTE RIO 1111140 | MONTE RIO 1111 | SONOMA | 2.6327 | 49.961 | 28.63% | 14 | 1 | 100% | 100% | 0 | 0.18634 | 26.5534 | 3.3089 | 16.3721 | High | High | High | 397 | 432 | 4.9479 | 995.9295 | 11.16%
PINE GROVE 11021765 | PINE GROVE 1102 | STOCKTON | 1.4479 | 48.9693 | 100% | 0 | 0 | 100% | 66.6% | 0 | 0.10186 | 47.6367 | 3.2382 | 15.7126 | High | High | High | 406 | 433 | 4.8523 | 990.9816 | 11.1%
PINE GROVE 1102CB | PINE GROVE 1102 | STOCKTON | 10.707 | 66.221 | 86.49% | 3 | 11 | 100% | 3.567% | 1 | 0.074056 | 65.3912 | 3.6625 | 17.7359 | High | High | High | 388 | 434 | 4.8426 | 986.1293 | 11.05%
MORAGA 110118216 | MORAGA 1101 | DIABLO | 5.0361 | 38.4811 | 22.22% | 5 | 16 | 100% | 100% | 0 | 0.24183 | 19.9979 | 3.1723 | 15.3416 | High | High | High | 409 | 435 | 4.8362 | 981.2867 | 10.99%
POINT MORETTI 110110726 | POINT MORETTI 1101 | CENTRAL COAST | 10.5855 | 11.8484 | 44.34% | 15 | 5 | 100% | 100% | 1 | 0.18125 | 26.5534 | 3.2767 | 15.7704 | High | High | High | 405 | 436 | 4.8128 | 976.4505 | 10.94%
LOW GAP 1101CB | LOW GAP 1101 | HUMBOLDT | 2.17 | 82.2052 | 100% | 6 | 1 | 100% | 0% | 0 | 0.073547 | 65.3912 | 2.01 | 9.6669 | High | High | Low | 478 | 437 | 4.8093 | 971.6377 | 10.89%
TASSAJARA 21126392 | TASSAJARA 2112 | DIABLO | 5.4625 | 75.7434 | 2.892% | 0 | 3 | 100% | 100% | 0 | 0.10087 | 47.6367 | 3.5168 | 16.8979 | High | High | High | 395 | 438 | 4.8049 | 966.8283 | 10.83%
SALMON CREEK 110188998 | SALMON CREEK 1101 | SONOMA | 8.1183 | 72.1541 | 32.11% | 1 | 1 | 59.97% | 96.61% | 1 | 0.10072 | 47.6367 | 2.6582 | 12.7544 | High | High | Medium | 433 | 439 | 4.7981 | 962.0234 | 10.78%
PARADISE 110476064 | PARADISE 1104 | NORTH VALLEY | 6.3823 | 13.6814 | 48.59% | 6 | 11 | 100% | 100% | 1 | 0.13538 | 35.3263 | 3.9849 | 19.0574 | High | High | High | 368 | 440 | 4.7824 | 957.2253 | 10.72%
WEST POINT 110272036 | WEST POINT 1102 | STOCKTON | 2.3575 | 87.7642 | 47.51% | 4 | 2 | 100% | 22.74% | 0 | 0.055692 | 85.4511 | 3.115 | 14.8241 | Medium | Medium | High | 416 | 441 | 4.759 | 952.4429 | 10.67%
SHINGLE SPRINGS 210851476 | SHINGLE SPRINGS 2108 | SIERRA | 2.9778 | 55.1791 | 91.84% | 0 | 4 | 47.94% | 85.32% | 1 | 0.09969 | 47.6367 | 3.0157 | 14.3213 | High | High | Medium | 418 | 442 | 4.7489 | 947.6839 | 10.62%
POINT MORETTI 110139126 | POINT MORETTI 1101 | CENTRAL COAST | 2.2477 | 14.3797 | 26.31% | 9 | 1 | 100% | 100% | 0 | 0.099437 | 47.6367 | 3.3437 | 15.8387 | High | High | High | 403 | 443 | 4.7369 | 942.935 | 10.56%
ELECTRA 11017104 | ELECTRA 1101 | STOCKTON | 12.3464 | 47.2231 | 81.14% | 1 | 3 | 100% | 0% | 0 | 0.072301 | 65.3912 | 2.8473 | 13.4619 | High | High | Medium | 428 | 444 | 4.7279 | 938.1982 | 10.51%
BERKELEY F 1103BR110 | BERKELEY F 1103 | EAST BAY | 1.8512 | 58.149 | 51.38% | 3 | 2 | 32.55% | 100% | 0 | 0.071417 | 65.3912 | 3.9728 | 18.5534 | High | High | High | 376 | 445 | 4.67 | 933.4703 | 10.46%
MONTE RIO 1111506 | MONTE RIO 1111 | SONOMA | 1.1523 | 40.8732 | 25.9% | 6 | 0 | 100% | 100% | 0 | 0.097983 | 47.6367 | 4.0934 | 19.1062 | High | High | High | 367 | 446 | 4.6676 | 928.8003 | 10.41%
LOW GAP 110186816 | LOW GAP 1101 | HUMBOLDT | 4.4169 | 87.0623 | 100% | 0 | 8 | 100% | 0% | 0 | 0.071339 | 65.3912 | 1.4627 | 6.8232 | High | High | Low | 540 | 447 | 4.6649 | 924.1327 | 10.35%
BRIDGEVILLE 110169866 | BRIDGEVILLE 1101 | HUMBOLDT | 6.5416 | 93.8748 | 99.88% | 6 | 2 | 100% | 0% | 0 | 0.071282 | 65.3912 | 0.75814 | 3.5339 | High | High | Low | 643 | 448 | 4.6612 | 919.4677 | 10.3%
BRUNSWICK 110456468 | BRUNSWICK 1104 | SIERRA | 5.7301 | 68.1683 | 52.05% | 5 | 6 | 95.81% | 0% | 0 | 0.070779 | 65.3912 | 2.7112 | 12.5481 | High | High | Medium | 438 | 449 | 4.6283 | 914.8065 | 10.25%
LAYTONVILLE 1101CB | LAYTONVILLE 1101 | HUMBOLDT | 7.0679 | 79.2729 | 100% | 10 | 7 | 78.03% | 0% | 0 | 0.054066 | 85.4511 | 1.3144 | 6.0728 | Medium | Medium | Low | 556 | 450 | 4.62 | 910.1782 | 10.2%
TASSAJARA 210865438 | TASSAJARA 2108 | DIABLO | 0.52908 | 90 | 0% | 0 | 2 | 14.01% | 100% | 0 | 0.054006 | 85.4511 | 3.2509 | 15.0026 | Medium | Medium | High | 412 | 451 | 4.6148 | 905.5582 | 10.14%
MESA 11016111 | MESA 1101 | LOS PADRES | 23.8724 | 66.2721 | 84.61% | 0 | 7 | 92.83% | 48.37% | 0 | 0.23056 | 19.9979 | 1.9723 | 9.0938 | High | High | Low | 489 | 452 | 4.6108 | 900.9433 | 10.09%
ORO FINO 110238698 | ORO FINO 1102 | NORTH VALLEY | 15.5224 | 87.0508 | 99.92% | 2 | 6 | 100% | 0% | 0 | 0.070272 | 65.3912 | 0.89227 | 4.1001 | High | High | Low | 622 | 453 | 4.5952 | 896.3326 | 10.04%
REDBUD 1101708166 | REDBUD 1101 | HUMBOLDT | 10.1809 | 81.1955 | 96.21% | 0 | 3 | 49.7% | 53.54% | 1 | 0.096142 | 47.6367 | 2.1005 | 9.6203 | High | High | Low | 480 | 454 | 4.5799 | 891.7374 | 9.99%
EAST QUINCY 11012452 | EAST QUINCY 1101 | NORTH VALLEY | 1.102 | 63.1536 | 79.93% | 0 | 1 | 13.25% | 52.23% | 1 | 0.04476 | 102.1389 | 3.0006 | 13.7179 | Medium | Medium | Medium | 426 | 455 | 4.5718 | 887.1575 | 9.939%
CAMP EVERS 210510912 | CAMP EVERS 2105 | CENTRAL COAST | 4.9849 | 57.147 | 56.28% | 17 | 4 | 100% | 100% | 0 | 0.22661 | 19.9979 | 3.8168 | 17.2965 | High | High | High | 392 | 456 | 4.5316 | 882.5857 | 9.887%
OAKLAND K 110491060 | OAKLAND K 1104 | EAST BAY | 0.36025 | 77.0512 | 0% | 0 | 0 | 100% | 100% | 0 | 0.094019 | 47.6367 | 4.1348 | 18.5187 | High | High | High | 377 | 457 | 4.4788 | 878.0541 | 9.837%
SILVERADO 210365334 | SILVERADO 2103 | NORTH BAY | 0.51221 | 90 | 100% | 0 | 0 | 7.915% | 100% | 0 | 0.093253 | 47.6367 | 2.1963 | 9.7565 | High | High | Low | 477 | 458 | 4.4422 | 873.5753 | 9.787%
BRIDGEVILLE 110137484 | BRIDGEVILLE 1101 | HUMBOLDT | 7.5279 | 94.876 | 100% | 3 | 6 | 74.55% | 0% | 0 | 0.051968 | 85.4511 | 0.80668 | 3.5822 | Medium | Medium | Low | 640 | 459 | 4.4407 | 869.1331 | 9.737%
CALPINE 1144962 | CALPINE 1144 | SONOMA | 4.058 | 94.9648 | 64.72% | 0 | 0 | 100% | 100% | 0 | 0.16674 | 26.5534 | 1.9214 | 8.5068 | High | High | Low | 502 | 460 | 4.4275 | 864.6924 | 9.687%
WISE 11022230 | WISE 1102 | SIERRA | 22.0893 | 25.2486 | 59.65% | 3 | 10 | 89.01% | 0% | 0 | 0.09262 | 47.6367 | 1.9917 | 8.7874 | High | High | Low | 497 | 461 | 4.4121 | 860.2649 | 9.637%
LAYTONVILLE 1102CB | LAYTONVILLE 1102 | HUMBOLDT | 10.2076 | 95.4582 | 95.78% | 0 | 7 | 78.57% | 0% | 0 | 0.051516 | 85.4511 | 1.2662 | 5.5739 | Medium | Medium | Low | 570 | 462 | 4.4021 | 855.8528 | 9.588%
BEN LOMOND 04015206 | BEN LOMOND 0401 | CENTRAL COAST | 7.179 | 20.3543 | 52.81% | 22 | 2 | 100% | 100% | 0 | 0.16558 | 26.5534 | 3.6563 | 16.0757 | High | High | High | 401 | 463 | 4.3967 | 851.4507 | 9.539%
CAMP EVERS 210616000 | CAMP EVERS 2106 | CENTRAL COAST | 2.1434 | 16.7013 | 23.49% | 1 | 3 | 54.85% | 97.54% | 1 | 0.067002 | 65.3912 | 3.147 | 13.7878 | High | High | High | 424 | 464 | 4.3813 | 847.054 | 9.489%
MONTE RIO 1113250 | MONTE RIO 1113 | SONOMA | 1.2254 | 74.4629 | 18.87% | 1 | 1 | 100% | 100% | 0 | 0.1235 | 35.3263 | 2.8957 | 12.6334 | High | High | Medium | 436 | 465 | 4.3628 | 842.6727 | 9.44%
CLAYTON 22127758 | CLAYTON 2212 | DIABLO | 3.2393 | 62.3034 | 85.96% | 2 | 0 | 100% | 100% | 0 | 0.16375 | 26.5534 | 3.2939 | 14.3225 | High | High | High | 417 | 466 | 4.3482 | 838.3099 | 9.391%
WEST POINT 11025357 | WEST POINT 1102 | STOCKTON | 3.286 | 83.7938 | 100% | 3 | 2 | 100% | 17.3% | 0 | 0.065365 | 65.3912 | 2.3603 | 10.0887 | High | High | Medium | 474 | 467 | 4.2743 | 833.9617 | 9.343%
PENNGROVE 1101170 | PENNGROVE 1101 | SONOMA | 18.4109 | 61.4183 | 85.26% | 5 | 17 | 81.28% | 0% | 0 | 0.065227 | 65.3912 | 2.4598 | 10.4915 | High | High | Medium | 467 | 468 | 4.2653 | 829.6874 | 9.295%
SIERRA CITY GEN 1101CB | SIERRA CITY GEN 1101 | SIERRA | 0.013222 | 95 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049877 | 85.4511 | 2.24 | 9.5471 | Medium | Medium | Medium | 481 | 469 | 4.262 | 825.4221 | 9.247%
SIERRA CITY GEN 11011101/2 | SIERRA CITY GEN 1101 | SIERRA | 0.0052893 | 95 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049877 | 85.4511 | 2.2291 | 9.5007 | Medium | Medium | Low | 482 | 469 | 4.262 | 821.1601 | 9.199%
GIRVAN 11021028 | GIRVAN 1102 | NORTH VALLEY | 17.4682 | 30.4656 | 99.97% | 3 | 19 | 100% | 100% | 1 | 0.28494 | 14.9507 | 1.8976 | 8.084 | High | High | Low | 515 | 471 | 4.26 | 816.8981 | 9.152%
CRESCENT MILLS 21013113 | CRESCENT MILLS 2101 | NORTH VALLEY | 1.193 | 94.468 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049705 | 85.4511 | 2.837 | 12.0498 | Medium | Medium | Medium | 442 | 472 | 4.2473 | 812.638 | 9.104%
POINT MORETTI 110110722 | POINT MORETTI 1101 | CENTRAL COAST | 0.60606 | 15.6405 | 41.46% | 0 | 0 | 100% | 100% | 0 | 0.087584 | 47.6367 | 3.3583 | 14.0116 | High | High | High | 421 | 473 | 4.1722 | 808.3907 | 9.056%
BIG MEADOWS 21012474 | BIG MEADOWS 2101 | NORTH VALLEY | 8.0369 | 74.0553 | 100% | 0 | 14 | 96.17% | 0% | 0 | 0.062896 | 65.3912 | 2.6243 | 10.7933 | High | High | Medium | 465 | 474 | 4.1128 | 804.2185 | 9.01%
BRUNSWICK 1104761310 | BRUNSWICK 1104 | SIERRA | 0.029625 | 37.5776 | 100% | 0 | 0 | 100% | 100% | 0 | 0.15312 | 26.5534 | 2.4455 | 9.9432 | High | High | Medium | 475 | 475 | 4.0659 | 800.1057 | 8.963%
BRUNSWICK 1102CB | BRUNSWICK 1102 | SIERRA | 6.3271 | 51.9471 | 61.35% | 4 | 0 | 99.87% | 31.38% | 0 | 0.047536 | 85.4511 | 2.763 | 11.2233 | Medium | Medium | Medium | 455 | 476 | 4.062 | 796.0398 | 8.918%
COTATI 1105CB | COTATI 1105 | SONOMA | 3.1602 | 63.5412 | 54.85% | 1 | 0 | 100% | 0% | 0 | 0.061793 | 65.3912 | 2.8768 | 11.6244 | High | High | Medium | 454 | 477 | 4.0407 | 791.9778 | 8.872%
WILLOW CREEK 1101CB | WILLOW CREEK 1101 | HUMBOLDT | 0.28035 | 73.844 | 25.25% | 2 | 0 | 100% | 100% | 0 | 0.11379 | 35.3263 | 1.829 | 7.3523 | High | High | Low | 529 | 478 | 4.0198 | 787.9371 | 8.827%
BELL 11072400 | BELL 1107 | SIERRA | 24.3699 | 40.733 | 58.06% | 2 | 11 | 87.78% | 0% | 0 | 0.061332 | 65.3912 | 2.7006 | 10.8308 | Medium | Medium | Medium | 464 | 479 | 4.0106 | 783.9173 | 8.782%
OAKLAND K 1104CR326 | OAKLAND K 1104 | EAST BAY | 1.3049 | 10 | 98.1% | 3 | 0 | 100% | 100% | 0 | 0.14914 | 26.5534 | 4.2299 | 16.7511 | High | High | High | 396 | 480 | 3.9602 | 779.9067 | 8.737%
HAMILTON BRANCH 110190334 | HAMILTON BRANCH 1101 | NORTH VALLEY | 3.3715 | 83.9014 | 99.76% | 0 | 0 | 100% | 0% | 0 | 0.046313 | 85.4511 | 2.8026 | 11.0913 | Medium | Medium | Medium | 459 | 481 | 3.9575 | 775.9466 | 8.693%
MONTE RIO 11135024 | MONTE RIO 1113 | SONOMA | 0.33932 | 27.3622 | 58.73% | 2 | 0 | 100% | 100% | 0 | 0.10965 | 35.3263 | 3.0239 | 11.7136 | High | High | Medium | 452 | 482 | 3.8736 | 771.989 | 8.648%
PARADISE 1103CB | PARADISE 1103 | NORTH VALLEY | 2.4339 | 10 | 32.27% | 5 | 0 | 48.95% | 100% | 0 | 0.058983 | 65.3912 | 3.9165 | 15.1058 | Medium | Medium | High | 411 | 483 | 3.857 | 768.1154 | 8.605%
OLEMA 11011318 | OLEMA 1101 | NORTH BAY | 6.3563 | 77.6358 | 7.161% | 18 | 6 | 61.46% | 0% | 0 | 0.045105 | 85.4511 | 2.535 | 9.7705 | Medium | Medium | Medium | 476 | 484 | 3.8543 | 764.2584 | 8.562%
SANTA YNEZ 1104Y66 | SANTA YNEZ 1104 | LOS PADRES | 16.6796 | 85.1619 | 76.69% | 1 | 3 | 92.13% | 26.5% | 0 | 0.10816 | 35.3263 | 2.1886 | 8.3621 | High | High | Low | 508 | 485 | 3.8208 | 760.4042 | 8.519%
LAYTONVILLE 1102572 | LAYTONVILLE 1102 | HUMBOLDT | 21.4369 | 82.6922 | 96.68% | 7 | 18 | 100% | 0% | 0 | 0.14346 | 26.5534 | 1.3283 | 5.0602 | High | High | Low | 584 | 486 | 3.8094 | 756.5834 | 8.476%
RESEARCH 21029746 | RESEARCH 2102 | DIABLO | 0.70252 | 57.1565 | 2.503% | 0 | 3 | 24.99% | 100% | 0 | 0.044375 | 85.4511 | 3.091 | 11.7205 | Medium | Medium | High | 451 | 487 | 3.7919 | 752.774 | 8.433%
SHADY GLEN 11012768 | SHADY GLEN 1101 | SIERRA | 7.6983 | 67.5569 | 97.78% | 0 | 5 | 95.39% | 10.27% | 0 | 0.057683 | 65.3912 | 1.9636 | 7.4066 | Medium | Medium | Low | 526 | 488 | 3.7719 | 748.9821 | 8.391%
MENLO 11038512 | MENLO 1103 | PENINSULA | 16.8652 | 73.7343 | 67.92% | 14 | 5 | 100% | 0% | 0 | 0.10603 | 35.3263 | 2.3875 | 8.9425 | High | High | Medium | 495 | 489 | 3.7456 | 745.2102 | 8.348%
MOUNTAIN QUARRIES 2101CB | MOUNTAIN QUARRIES 2101 | SIERRA | 24.9741 | 44.4478 | 67.2% | 2 | 3 | 100% | 0% | 0 | 0.056988 | 65.3912 | 2.4457 | 9.1138 | Medium | Medium | Medium | 488 | 490 | 3.7265 | 741.4646 | 8.307%
MONTE RIO 1111CB | MONTE RIO 1111 | SONOMA | 0.26962 | 44.4262 | 0% | 0 | 1 | 100% | 100% | 0 | 0.078152 | 47.6367 | 3.5806 | 13.3304 | High | High | High | 429 | 491 | 3.7229 | 737.7381 | 8.265%
CAMP EVERS 21045096 | CAMP EVERS 2104 | CENTRAL COAST | 20.6359 | 43.5028 | 64.15% | 34 | 7 | 100% | 100% | 0 | 0.33163 | 11.2183 | 3.3817 | 12.581 | High | High | High | 437 | 492 | 3.7203 | 734.0152 | 8.223%
FORT ROSS 1121124 | FORT ROSS 1121 | SONOMA | 18.5728 | 86.0744 | 76.02% | 1 | 2 | 100% | 0% | 0 | 0.077065 | 47.6367 | 1.2649 | 4.6437 | High | High | Low | 601 | 493 | 3.6711 | 730.2948 | 8.181%
OLEMA 11011252 | OLEMA 1101 | NORTH BAY | 4.0529 | 83.346 | 14.42% | 10 | 5 | 98.65% | 0% | 0 | 0.042756 | 85.4511 | 3.0154 | 11.0171 | Medium | Medium | Medium | 462 | 494 | 3.6535 | 726.6237 | 8.14%
FRUITLAND 11426064 | FRUITLAND 1142 | HUMBOLDT | 6.4216 | 80.9642 | 100% | 2 | 4 | 77.51% | 0% | 0 | 0.076552 | 47.6367 | 0.47828 | 1.7441 | High | High | Low | 786 | 495 | 3.6467 | 722.9702 | 8.099%
FORT SEWARD 11211690 | FORT SEWARD 1121 | HUMBOLDT | 10.4929 | 86.5731 | 100% | 15 | 3 | 64.42% | 0% | 0 | 0.055586 | 65.3912 | 2.046 | 7.4369 | Medium | Medium | Low | 524 | 496 | 3.6348 | 719.3235 | 8.058%
BRUNSWICK 11042112 | BRUNSWICK 1104 | SIERRA | 19.306 | 55.1614 | 89% | 4 | 7 | 100% | 25.18% | 0 | 0.10285 | 35.3263 | 2.4774 | 9.0016 | High | High | Medium | 493 | 497 | 3.6335 | 715.6886 | 8.018%
MONROE 2103CB | MONROE 2103 | SONOMA | 0.73533 | 61.5712 | 100% | 0 | 0 | 5.132% | 100% | 0 | 0.076074 | 47.6367 | 2.2963 | 8.3215 | High | High | Medium | 509 | 498 | 3.6239 | 712.0552 | 7.977%
DESCHUTES 110449024 | DESCHUTES 1104 | NORTH VALLEY | 16.4286 | 33.9792 | 100% | 0 | 7 | 97.93% | 0% | 0 | 0.055326 | 65.3912 | 2.4946 | 9.0253 | Medium | Medium | Medium | 492 | 499 | 3.6179 | 708.4313 | 7.936%
HATTON 1101 | HATTON 1101 | CENTRAL COAST | 0.058169 | 90 | 100% | 0 | 0 | 100% | 0% | 0 | 0.054802 | 65.3912 | 2.5228 | 9.0405 | Medium | Medium | Medium | 490 | 500 | 3.5836 | 704.8134 | 7.896%
MEADOW LANE 2106C558R | MEADOW LANE 2106 | DIABLO | 0.20712 | 95 | 0% | 0 | 0 | 1.459% | 100% | 0 | 0.041876 | 85.4511 | 3.36 | 12.0232 | Medium | Medium | High | 443 | 501 | 3.5783 | 701.2298 | 7.856%
GARBERVILLE 11012026 | GARBERVILLE 1101 | HUMBOLDT | 6.3529 | 96.5509 | 100% | 5 | 1 | 100% | 0% | 0 | 0.05472 | 65.3912 | 0.23353 | 0.83563 | Medium | Medium | Low | 935 | 502 | 3.5782 | 697.6515 | 7.816%
OAKHURST 110363334 | OAKHURST 1103 | YOSEMITE | 17.2522 | 47.378 | 100% | 1 | 11 | 100% | 10.77% | 0 | 0.054511 | 65.3912 | 2.871 | 10.2339 | Medium | Medium | Medium | 471 | 503 | 3.5646 | 694.0733 | 7.776%
GARCIA 0401666 | GARCIA 0401 | HUMBOLDT | 2.4311 | 97.9965 | 100% | 2 | 2 | 100% | 0% | 0 | 0.054265 | 65.3912 | 1.3953 | 4.9513 | Medium | Medium | Low | 588 | 504 | 3.5484 | 690.5087 | 7.736%
DUNBAR 11021285 | DUNBAR 1102 | SONOMA | 4.061 | 83.8717 | 58.26% | 1 | 2 | 100% | 27.24% | 1 | 0.053737 | 65.3912 | 3.3515 | 11.7769 | Medium | Medium | High | 449 | 505 | 3.5139 | 686.9603 | 7.696%
FITCH MOUNTAIN 1113356 | FITCH MOUNTAIN 1113 | SONOMA | 9.9757 | 80.7752 | 75.25% | 5 | 1 | 65.83% | 51.2% | 1 | 0.073371 | 47.6367 | 2.443 | 8.5386 | High | High | Medium | 501 | 506 | 3.4951 | 683.4464 | 7.657%
MIWUK 170179118 | MIWUK 1701 | YOSEMITE | 0.019355 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 26.5534 | 3.7802 | 13.0713 | High | High | High | 430 | 507 | 3.4578 | 679.9513 | 7.617%
SONOMA 1106376 | SONOMA 1106 | SONOMA | 0.6618 | 42.582 | 100% | 0 | 0 | 12.23% | 100% | 0 | 0.072044 | 47.6367 | 3.7402 | 12.8361 | High | High | High | 432 | 508 | 3.4319 | 676.4934 | 7.579%
CRESCENT MILLS 21012232 | CRESCENT MILLS 2101 | NORTH VALLEY | 17.0798 | 82.544 | 99.96% | 2 | 0 | 84.55% | 0% | 0 | 0.052465 | 65.3912 | 1.3664 | 4.6879 | Medium | Medium | Low | 600 | 509 | 3.4308 | 673.0615 | 7.54%
ZACA 1102CB | ZACA 1102 | LOS PADRES | 15.8871 | 63.476 | 75.75% | 0 | 4 | 76.4% | 37.44% | 0 | 0.096438 | 35.3263 | 1.7385 | 5.9226 | High | High | Low | 562 | 510 | 3.4068 | 669.6307 | 7.502%
FRUITLAND 1142CB | FRUITLAND 1142 | HUMBOLDT | 10.4822 | 87.3271 | 88.71% | 7 | 4 | 68.32% | 0% | 0 | 0.071375 | 47.6367 | 0.91967 | 3.1269 | High | High | Low | 671 | 511 | 3.4 | 666.2239 | 7.464%
MIDDLETOWN 11011314 | MIDDLETOWN 1101 | HUMBOLDT | 0.82482 | 85.7951 | 100% | 0 | 0 | 88.81% | 5.14% | 1 | 0.051914 | 65.3912 | 2.3199 | 7.8754 | Medium | Medium | Medium | 519 | 512 | 3.3947 | 662.8239 | 7.426%
LAYTONVILLE 1102682 | LAYTONVILLE 1102 | HUMBOLDT | 14.8214 | 90.6873 | 91.3% | 5 | 3 | 100% | 0% | 0 | 0.051212 | 65.3912 | 0.7707 | 2.5809 | Medium | Medium | Low | 717 | 513 | 3.3488 | 659.4292 | 7.387%
PASO ROBLES 1103N04 | PASO ROBLES 1103 | LOS PADRES | 0.58532 | 54.1264 | 3.167% | 0 | 8 | 100% | 0% | 0 | 0.051036 | 65.3912 | 3.1021 | 10.3524 | Medium | Medium | High | 469 | 514 | 3.3373 | 656.0803 | 7.35%
GARCIA 0401CB | GARCIA 0401 | HUMBOLDT | 0.042407 | 98 | 100% | 0 | 0 | 100% | 0% | 0 | 0.050859 | 65.3912 | 1.4156 | 4.7078 | Medium | Medium | Low | 598 | 515 | 3.3257 | 652.7431 | 7.313%
SILVERADO 21051306 | SILVERADO 2105 | NORTH BAY | 2.7442 | 84.7075 | 83.99% | 0 | 2 | 34.98% | 54.43% | 0 | 0.068801 | 47.6367 | 2.8813 | 9.4434 | High | High | Medium | 485 | 516 | 3.2775 | 649.4174 | 7.275%
PINE GROVE 1101CB | PINE GROVE 1101 | STOCKTON | 4.2594 | 78.3336 | 50.63% | 0 | 5 | 100% | 0% | 0 | 0.038055 | 85.4511 | 3.1345 | 10.1928 | Medium | Medium | High | 472 | 517 | 3.2518 | 646.1399 | 7.239%
BIG BASIN 110165444 | BIG BASIN 1101 | CENTRAL COAST | 0.47094 | 48.0736 | 0% | 2 | 0 | 100% | 100% | 0 | 0.090816 | 35.3263 | 3.743 | 12.0083 | High | High | High | 445 | 518 | 3.2082 | 642.8881 | 7.202%
SHINGLE SPRINGS 21099372 | SHINGLE SPRINGS 2109 | SIERRA | 17.5824 | 48.8833 | 68.76% | 2 | 5 | 100% | 52.97% | 0 | 0.1201 | 26.5534 | 1.9275 | 6.147 | High | High | Low | 554 | 519 | 3.1891 | 639.6799 | 7.166%
TASSAJARA 210812712 | TASSAJARA 2108 | DIABLO | 0.60405 | 70.6966 | 76.13% | 0 | 2 | 18.42% | 100% | 0 | 0.089254 | 35.3263 | 3.2876 | 10.366 | High | High | High | 468 | 520 | 3.153 | 636.4908 | 7.131%
CORNING 110185152 | CORNING 1101 | NORTH VALLEY | 23.0821 | 26.0719 | 100% | 2 | 8 | 100% | 0% | 0 | 0.11691 | 26.5534 | 2.6425 | 8.2029 | High | High | Medium | 511 | 521 | 3.1042 | 633.3378 | 7.095%
COTATI 110379140 | COTATI 1103 | SONOMA | 9.8425 | 61.4372 | 48.82% | 7 | 2 | 79.77% | 0% | 0 | 0.047459 | 65.3912 | 2.5749 | 7.9908 | Medium | Medium | Medium | 517 | 522 | 3.1034 | 630.2335 | 7.06%
DIAMOND SPRINGS 110518935 | DIAMOND SPRINGS 1105 | SIERRA | 6.6942 | 21.2209 | 100% | 2 | 4 | 100% | 72.5% | 0 | 0.11646 | 26.5534 | 2.6792 | 8.2855 | High | High | Medium | 510 | 523 | 3.0925 | 627.1301 | 7.026%
CALISTOGA 11011087 | CALISTOGA 1101 | NORTH BAY | 1.9847 | 74.7271 | 70.51% | 0 | 0 | 100% | 100% | 0 | 0.15452 | 19.9979 | 2.4735 | 7.6433 | High | High | Medium | 523 | 524 | 3.0901 | 624.0376 | 6.991%
RACETRACK 170455798 | RACETRACK 1704 | YOSEMITE | 15.7881 | 56.8107 | 46.06% | 3 | 13 | 100% | 0% | 0 | 0.064582 | 47.6367 | 2.1973 | 6.7599 | High | High | Low | 543 | 525 | 3.0765 | 620.9475 | 6.956%
CAMP EVERS 210511010 | CAMP EVERS 2105 | CENTRAL COAST | 2.2251 | 32.8132 | 34.55% | 4 | 3 | 100% | 100% | 0 | 0.11572 | 26.5534 | 3.9822 | 12.2369 | High | High | High | 441 | 526 | 3.0729 | 617.871 | 6.922%
DUNBAR 11014817 | DUNBAR 1101 | SONOMA | 3.1798 | 21.7127 | 52.45% | 3 | 3 | 100% | 100% | 0 | 0.15344 | 19.9979 | 2.6498 | 8.1309 | High | High | Medium | 514 | 527 | 3.0685 | 614.7982 | 6.887%
COTTONWOOD 11039072 | COTTONWOOD 1103 | NORTH VALLEY | 28.4061 | 60.3164 | 100% | 4 | 3 | 99.13% | 0% | 0 | 0.06438 | 47.6367 | 1.3689 | 4.1983 | High | High | Low | 619 | 528 | 3.0669 | 611.7297 | 6.853%
CLOVERDALE 1101 | CLOVERDALE 1101 | SONOMA | 0.067026 | 85 | 100% | 0 | 0 | 100% | 0% | 0 | 0.046733 | 65.3912 | 2.4317 | 7.4312 | Medium | Medium | Medium | 525 | 529 | 3.0559 | 608.6628 | 6.819%
TASSAJARA 21123202 | TASSAJARA 2112 | DIABLO | 0.99352 | 84.671 | 60.56% | 0 | 0 | 100% | 100% | 0 | 0.15269 | 19.9979 | 3.1551 | 9.6344 | High | High | High | 479 | 530 | 3.0536 | 605.6069 | 6.785%
ATASCADERO 11012537 | ATASCADERO 1101 | LOS PADRES | 15.4143 | 42.2463 | 87.6% | 5 | 1 | 100% | 82.31% | 1 | 0.15256 | 19.9979 | 2.6276 | 8.0166 | High | High | Medium | 516 | 531 | 3.0509 | 602.5533 | 6.75%
OAKLAND X 1104CR022 | OAKLAND X 1104 | EAST BAY | 5.946 | 14.8032 | 44.25% | 8 | 4 | 100% | 100% | 0 | 0.14986 | 19.9979 | 4.2262 | 12.6657 | High | High | High | 435 | 532 | 2.997 | 599.5024 | 6.716%
WILLOW CREEK 11037514 | WILLOW CREEK 1103 | HUMBOLDT | 9.2339 | 70.9692 | 70.67% | 10 | 14 | 91.91% | 2.029% | 1 | 0.062494 | 47.6367 | 1.4859 | 4.4235 | High | High | Low | 610 | 533 | 2.977 | 596.5054 | 6.683%
SANTA ROSA A 1104220 | SANTA ROSA A 1104 | SONOMA | 9.5297 | 27.599 | 64.91% | 1 | 14 | 100% | 64.31% | 0 | 0.11149 | 26.5534 | 3.1942 | 9.4563 | High | High | High | 483 | 534 | 2.9604 | 593.5284 | 6.649%
CAMP EVERS 210511384 | CAMP EVERS 2105 | CENTRAL COAST | 4.1064 | 10 | 25.57% | 1 | 1 | 100% | 100% | 0 | 0.11123 | 26.5534 | 4.6612 | 13.7668 | High | High | High | 425 | 535 | 2.9535 | 590.5679 | 6.616%
WILLITS 110337506 | WILLITS 1103 | HUMBOLDT | 11.4286 | 90.7952 | 60.25% | 4 | 3 | 100% | 0% | 0 | 0.04503 | 65.3912 | 1.5483 | 4.5592 | Medium | Medium | Low | 608 | 536 | 2.9446 | 587.6145 | 6.583%
JESSUP 110276068 | JESSUP 1102 | NORTH VALLEY | 15.5129 | 23.0172 | 100% | 2 | 4 | 80.72% | 0% | 0 | 0.061753 | 47.6367 | 2.125 | 6.2511 | High | High | Low | 552 | 537 | 2.9417 | 584.6699 | 6.55%
SPANISH CREEK 4401CB | SPANISH CREEK 4401 | NORTH VALLEY | 7.9163 | 94.7918 | 10.89% | 2 | 9 | 99.83% | 0% | 0 | 0.034339 | 85.4511 | 2.2893 | 6.7174 | Medium | Medium | Medium | 544 | 538 | 2.9343 | 581.7282 | 6.517%
PENRYN 1103604 | PENRYN 1103 | SIERRA | 26.4899 | 35.3404 | 72.55% | 7 | 11 | 100% | 0% | 0 | 0.061577 | 47.6367 | 2.8611 | 8.3925 | High | High | Medium | 505 | 539 | 2.9333 | 578.7939 | 6.484%
PARADISE 110181966 | PARADISE 1101 | NORTH VALLEY | 0.1834 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 47.6367 | 3.9719 | 11.6474 | High | High | High | 453 | 540 | 2.9325 | 575.8606 | 6.451%
TIVY VALLEY 1107869946 | TIVY VALLEY 1107 | FRESNO | 29.8533 | 31.5996 | 100% | 0 | 2 | 100% | 0% | 0 | 0.044292 | 65.3912 | 1.6429 | 4.7585 | Medium | Medium | Low | 596 | 541 | 2.8963 | 572.9281 | 6.418%
GIRVAN 11019732 | GIRVAN 1101 | NORTH VALLEY | 21.139 | 36.4737 | 100% | 2 | 6 | 100% | 100% | 0 | 0.1928 | 14.9507 | 1.6805 | 4.844 | High | High | Low | 593 | 542 | 2.8825 | 570.0318 | 6.386%
CORRAL 1101 | CORRAL 1101 | STOCKTON | 0.001152 | 75 | 100% | 0 | 0 | 100% | 0% | 0 | 0.043778 | 65.3912 | 1.0736 | 3.0735 | Medium | Medium | Low | 677 | 543 | 2.8627 | 567.1493 | 6.354%
BIG BASIN 11026219 | BIG BASIN 1102 | CENTRAL COAST | 0.89903 | 23.7161 | 100% | 1 | 0 | 100% | 100% | 0 | 0.14284 | 19.9979 | 2.4506 | 6.9999 | High | High | Medium | 536 | 544 | 2.8564 | 564.2866 | 6.322%
PINE GROVE 11011021 | PINE GROVE 1101 | STOCKTON | 4.1934 | 79.4355 | 93.37% | 0 | 1 | 100% | 0% | 0 | 0.043638 | 65.3912 | 2.9314 | 8.3647 | Medium | Medium | Medium | 507 | 545 | 2.8535 | 561.4302 | 6.29%
MIRABEL 110213597 | MIRABEL 1102 | SONOMA | 0.47204 | 30.1701 | 51.63% | 3 | 0 | 100% | 100% | 0 | 0.10712 | 26.5534 | 2.9615 | 8.4237 | High | High | Medium | 503 | 546 | 2.8444 | 558.5766 | 6.258%
KONOCTI 110264664 | KONOCTI 1102 | HUMBOLDT | 27.2111 | 54.3183 | 71% | 3 | 9 | 94.13% | 22.47% | 0 | 0.10647 | 26.5534 | 2.7454 | 7.7618 | High | High | Medium | 521 | 547 | 2.8272 | 555.7322 | 6.226%
COTATI 110599720 | COTATI 1105 | SONOMA | 7.8564 | 53.7004 | 71.89% | 3 | 7 | 63.87% | 0% | 0 | 0.042996 | 65.3912 | 2.5058 | 7.0451 | Medium | Medium | Medium | 535 | 548 | 2.8115 | 552.905 | 6.194%
BRUNSWICK 11102664 | BRUNSWICK 1110 | SIERRA | 9.7807 | 42.9965 | 66.17% | 2 | 0 | 90.12% | 0% | 0 | 0.042278 | 65.3912 | 2.8403 | 7.8524 | Medium | Medium | Medium | 520 | 549 | 2.7646 | 550.0934 | 6.163%
LOW GAP 11012094 | LOW GAP 1101 | HUMBOLDT | 15.318 | 83.9747 | 100% | 2 | 4 | 90.42% | 0% | 0 | 0.077716 | 35.3263 | 1.4008 | 3.8459 | High | High | Low | 629 | 550 | 2.7454 | 547.3288 | 6.132%
COTTONWOOD 11031616 | COTTONWOOD 1103 | NORTH VALLEY | 45.6614 | 47.3529 | 99.79% | 2 | 10 | 92.93% | 0% | 0 | 0.10209 | 26.5534 | 1.3519 | 3.6648 | High | High | Low | 637 | 551 | 2.7109 | 544.5834 | 6.101%
PARADISE 110236656 | PARADISE 1102 | NORTH VALLEY | 3.3309 | 17.0477 | 19.52% | 3 | 5 | 87.51% | 100% | 0 | 0.076178 | 35.3263 | 4.1355 | 11.129 | High | High | High | 458 | 552 | 2.6911 | 541.8725 | 6.071%
BRUNSWICK 1102940 | BRUNSWICK 1102 | SIERRA | 0.6541 | 82.3173 | 27.04% | 0 | 0 | 18.81% | 100% | 0 | 0.056253 | 47.6367 | 2.7437 | 7.3523 | Medium | Medium | Medium | 528 | 553 | 2.6797 | 539.1814 | 6.04%
BRUNSWICK 11047181 | BRUNSWICK 1104 | SIERRA | 0.77307 | 57.8754 | 100% | 1 | 1 | 100% | 0% | 0 | 0.040435 | 65.3912 | 2.6834 | 7.0953 | Medium | Medium | Medium | 531 | 554 | 2.6441 | 536.5017 | 6.01%
MIDDLETOWN 1102998 | MIDDLETOWN 1102 | HUMBOLDT | 14.694 | 30.2565 | 100% | 0 | 1 | 86% | 0% | 0 | 0.055128 | 47.6367 | 3.5751 | 9.3887 | Medium | Medium | High | 486 | 555 | 2.6261 | 533.8576 | 5.981%
SANTA ROSA A 1111114 | SANTA ROSA A 1111 | SONOMA | 5.593 | 82.824 | 61.55% | 3 | 5 | 48.78% | 0.05081% | 0 | 0.039882 | 65.3912 | 3.2275 | 8.4172 | Medium | Medium | High | 504 | 556 | 2.608 | 531.2315 | 5.951%
MENLO 11028952 | MENLO 1102 | PENINSULA | 6.6194 | 37.3674 | 79.3% | 6 | 6 | 97.26% | 0% | 0 | 0.07359 | 35.3263 | 3.5512 | 9.2318 | High | High | High | 487 | 557 | 2.5996 | 528.6235 | 5.922%
COTATI 110536536 | COTATI 1105 | SONOMA | 14.0222 | 66.9943 | 49.66% | 3 | 4 | 71.19% | 0% | 0 | 0.039741 | 65.3912 | 2.6116 | 6.7868 | Medium | Medium | Medium | 542 | 558 | 2.5987 | 526.0239 | 5.893%
BIG BASIN 110112838 | BIG BASIN 1101 | CENTRAL COAST | 2.3481 | 22.8055 | 19.65% | 7 | 1 | 100% | 100% | 0 | 0.097327 | 26.5534 | 3.3758 | 8.7244 | High | High | High | 498 | 559 | 2.5844 | 523.4252 | 5.864%
MORAGA 110183424 | MORAGA 1101 | DIABLO | 1.6164 | 79.1593 | 0% | 0 | 0 | 100% | 62.3% | 0 | 0.053892 | 47.6367 | 3.4366 | 8.8227 | Medium | Medium | High | 496 | 560 | 2.5672 | 520.8408 | 5.835%
SHADY GLEN 110248894 | SHADY GLEN 1102 | SIERRA | 8.076 | 49.6205 | 67.94% | 0 | 5 | 80.69% | 16.07% | 0 | 0.038596 | 65.3912 | 1.7515 | 4.4204 | Medium | Medium | Low | 611 | 561 | 2.5239 | 518.2736 | 5.806%
HALF MOON BAY 11038894 | HALF MOON BAY 1103 | PENINSULA | 11.2938 | 71.3584 | 49.24% | 24 | 2 | 100% | 0% | 0 | 0.052113 | 47.6367 | 2.1795 | 5.4107 | Medium | Medium | Low | 574 | 562 | 2.4825 | 515.7497 | 5.778%
COTATI 1105634 | COTATI 1105 | SONOMA | 6.9392 | 85.5117 | 61.91% | 2 | 3 | 100% | 0% | 0 | 0.037803 | 65.3912 | 2.0438 | 5.0522 | Medium | Medium | Low | 585 | 563 | 2.472 | 513.2672 | 5.75%
LAURELES 111110141 | LAURELES 1111 | CENTRAL COAST | 2.922 | 83.2816 | 100% | 0 | 0 | 100% | 100% | 0 | 0.22027 | 11.2183 | 1.8674 | 4.6144 | High | High | Low | 603 | 564 | 2.471 | 510.7952 | 5.722%
COARSEGOLD 2104570682 | COARSEGOLD 2104 | YOSEMITE | 2.0271 | 37.4462 | 79.77% | 2 | 5 | 100% | 0% | 0 | 0.037588 | 65.3912 | 2.2997 | 5.6525 | Medium | Medium | Medium | 566 | 565 | 2.4579 | 508.3242 | 5.695%
PETALUMA C 1108296 | PETALUMA C 1108 | SONOMA | 14.7729 | 78.7625 | 21.22% | 3 | 7 | 100% | 0% | 0 | 0.037166 | 65.3912 | 2.8405 | 6.9034 | Medium | Medium | Medium | 538 | 566 | 2.4303 | 505.8662 | 5.667%
MOLINO 110279306 | MOLINO 1102 | SONOMA | 3.6243 | 55.9348 | 57.2% | 3 | 2 | 44.33% | 48.34% | 1 | 0.037109 | 65.3912 | 2.3082 | 5.6012 | Medium | Medium | Medium | 567 | 567 | 2.4266 | 503.4359 | 5.64%
LAYTONVILLE 110268436 | LAYTONVILLE 1102 | HUMBOLDT | 9.1013 | 91.8828 | 93.46% | 1 | 2 | 100% | 32.77% | 1 | 0.091162 | 26.5534 | 1.4538 | 3.5192 | High | High | Low | 644 | 568 | 2.4207 | 501.0093 | 5.613%
VACA DIXON 110540092 | VACA DIXON 1105 | SACRAMENTO | 23.831 | 65.7788 | 89.52% | 2 | 6 | 55.42% | 0% | 0 | 0.036947 | 65.3912 | 2.1635 | 5.227 | Medium | Medium | Low | 580 | 569 | 2.416 | 498.5886 | 5.586%
BIG BASIN 110212758 | BIG BASIN 1102 | CENTRAL COAST | 6.1262 | 42.4144 | 40.92% | 12 | 2 | 100% | 100% | 0 | 0.21481 | 11.2183 | 2.8889 | 6.9619 | High | High | Medium | 537 | 570 | 2.4099 | 496.1727 | 5.559%
HALF MOON BAY 11038089 | HALF MOON BAY 1103 | PENINSULA | 2.9815 | 77.4451 | 41.57% | 4 | 4 | 100% | 0% | 0 | 0.036303 | 65.3912 | 1.9337 | 4.5903 | Medium | Medium | Low | 604 | 571 | 2.3739 | 493.7628 | 5.532%
COARSEGOLD 2104369777 | COARSEGOLD 2104 | YOSEMITE | 18.4298 | 46.1002 | 90.43% | 1 | 34 | 100% | 0% | 0 | 0.066997 | 35.3263 | 1.9853 | 4.6987 | High | High | Low | 599 | 572 | 2.3668 | 491.3889 | 5.505%
SHADY GLEN 1101CB | SHADY GLEN 1101 | SIERRA | 4.4237 | 59.4195 | 32.95% | 0 | 5 | 80.65% | 0% | 0 | 0.027502 | 85.4511 | 2.2374 | 5.2579 | Medium | Medium | Medium | 579 | 573 | 2.3501 | 489.0221 | 5.478%
PETALUMA C 1108636 | PETALUMA C 1108 | SONOMA | 9.2277 | 74.6783 | 45.5% | 1 | 1 | 100% | 0% | 0 | 0.048927 | 47.6367 | 2.3419 | 5.4583 | Medium | Medium | Medium | 573 | 574 | 2.3307 | 486.6721 | 5.452%
CAMP EVERS 210595394 | CAMP EVERS 2105 | CENTRAL COAST | 0.49589 | 10 | 8.806% | 0 | 0 | 100% | 100% | 0 | 0.065893 | 35.3263 | 3.8628 | 8.9916 | High | High | High | 494 | 575 | 2.3278 | 484.3414 | 5.426%
OCEANO 1104Q10 | OCEANO 1104 | LOS PADRES | 23.5484 | 28.2238 | 59% | 7 | 3 | 100% | 0% | 0 | 0.065893 | 35.3263 | 3.0376 | 7.0708 | High | High | Medium | 533 | 576 | 2.3277 | 482.0136 | 5.4%
COTTONWOOD 11031344 | COTTONWOOD 1103 | NORTH VALLEY | 7.7962 | 44.5024 | 98.83% | 0 | 5 | 62.89% | 0% | 0 | 0.035503 | 65.3912 | 1.8686 | 4.338 | Medium | Medium | Low | 615 | 577 | 2.3216 | 479.6859 | 5.374%
LAYTONVILLE 1102500 | LAYTONVILLE 1102 | HUMBOLDT | 20.1821 | 81.3832 | 99.67% | 9 | 6 | 69.04% | 0% | 0 | 0.048589 | 47.6367 | 1.2335 | 2.855 | Medium | Medium | Low | 692 | 578 | 2.3146 | 477.3643 | 5.348%
MOLINO 1101338 | MOLINO 1101 | SONOMA | 7.3596 | 75.7123 | 66.21% | 4 | 4 | 51.47% | 0% | 0 | 0.035347 | 65.3912 | 3.0506 | 7.0511 | Medium | Medium | Medium | 534 | 579 | 2.3114 | 475.0497 | 5.322%
REDBUD 1102CB | REDBUD 1102 | HUMBOLDT | 15.5011 | 65.2981 | 72.86% | 2 | 2 | 77.01% | 9.757% | 0 | 0.048504 | 47.6367 | 2.492 | 5.7579 | Medium | Medium | Medium | 564 | 580 | 2.3106 | 472.7383 | 5.296%
PASO ROBLES 1103N54 | PASO ROBLES 1103 | LOS PADRES | 19.5682 | 48.3867 | 60.55% | 1 | 29 | 90.91% | 0% | 0 | 0.065373 | 35.3263 | 1.33 | 3.0715 | High | High | Low | 678 | 581 | 2.3094 | 470.4277 | 5.27%
PENRYN 11032198 | PENRYN 1103 | SIERRA | 19.8234 | 39.0911 | 53.27% | 4 | 16 | 94.86% | 0% | 0 | 0.048469 | 47.6367 | 2.1684 | 5.0067 | Medium | Medium | Low | 586 | 582 | 2.3089 | 468.1183 | 5.244%
DUNBAR 1102246 | DUNBAR 1102 | SONOMA | 14.7102 | 40.7068 | 52.1% | 6 | 13 | 100% | 1.558% | 0 | 0.064871 | 35.3263 | 2.8342 | 6.495 | High | High | Medium | 548 | 583 | 2.2917 | 465.8094 | 5.218%
PETALUMA C 1108628 | PETALUMA C 1108 | SONOMA | 9.0995 | 58.7807 | 34.73% | 0 | 3 | 82.01% | 0% | 0 | 0.035008 | 65.3912 | 2.6389 | 6.041 | Medium | Medium | Medium | 559 | 584 | 2.2892 | 463.5178 | 5.193%
COARSEGOLD 210210207 | COARSEGOLD 2102 | YOSEMITE | 3.5762 | 10 | 99.5% | 3 | 11 | 100% | 100% | 0 | 0.20336 | 11.2183 | 1.996 | 4.5536 | High | High | Low | 609 | 585 | 2.2814 | 461.2285 | 5.167%
OCEANO 1104V36 | OCEANO 1104 | LOS PADRES | 8.9209 | 45.6964 | 61.88% | 2 | 5 | 67.02% | 0% | 0 | 0.047581 | 47.6367 | 2.9332 | 6.6484 | Medium | Medium | Medium | 546 | 586 | 2.2666 | 458.9472 | 5.142%
PUTAH CREEK 11033851 | PUTAH CREEK 1103 | SACRAMENTO | 3.6658 | 82.0611 | 100% | 0 | 0 | 70.81% | 0% | 0 | 0.034621 | 65.3912 | 1.8797 | 4.2555 | Medium | Medium | Low | 616 | 587 | 2.2639 | 456.6806 | 5.116%
SHEPHERD 2111R1400 | SHEPHERD 2111 | FRESNO | 19.9144 | 43.3803 | 100% | 0 | 4 | 86.57% | 0% | 0 | 0.063987 | 35.3263 | 1.487 | 3.3613 | High | High | Low | 653 | 588 | 2.2604 | 454.4167 | 5.091%
FORESTHILL 1102CB | FORESTHILL 1102 | SIERRA | 1.6478 | 87.6992 | 97.59% | 0 | 0 | 100% | 100% | 0 | 0.19983 | 11.2183 | 2.3825 | 5.3411 | High | High | Medium | 576 | 589 | 2.2418 | 452.1562 | 5.065%
OILFIELDS 1103N46 | OILFIELDS 1103 | CENTRAL COAST | 5.8257 | 79.2916 | 67.5% | 0 | 4 | 100% | 0% | 0 | 0.062709 | 35.3263 | 2.1379 | 4.736 | High | High | Low | 597 | 590 | 2.2153 | 449.9145 | 5.04%
COTATI 1103CB | COTATI 1103 | SONOMA | 12.0212 | 77.6953 | 26.01% | 1 | 5 | 100% | 0% | 0 | 0.046374 | 47.6367 | 2.5255 | 5.5791 | Medium | Medium | Medium | 569 | 591 | 2.2091 | 447.6992 | 5.016%
CAMP EVERS 21055188 | CAMP EVERS 2105 | CENTRAL COAST | 1.985 | 10 | 58.42% | 1 | 0 | 100% | 100% | 0 | 0.10955 | 19.9979 | 3.3123 | 7.2566 | High | High | High | 530 | 592 | 2.1908 | 445.4901 | 4.991%
CORNING 110164090 | CORNING 1101 | NORTH VALLEY | 13.6992 | 19.4323 | 100% | 1 | 9 | 100% | 0% | 0 | 0.061365 | 35.3263 | 2.2782 | 4.9386 | Medium | Medium | Medium | 589 | 593 | 2.1678 | 443.2993 | 4.966%
SILVERADO 21051308 | SILVERADO 2105 | NORTH BAY | 0.01945 | 80.9995 | 16% | 3 | 1 | 0.3576% | 100% | 0 | 0.045462 | 47.6367 | 3.7584 | 8.1396 | Medium | Medium | High | 513 | 594 | 2.1657 | 441.1315 | 4.942%
CAMP EVERS 21055577 | CAMP EVERS 2105 | CENTRAL COAST | 1.1615 | 10 | 45.86% | 6 | 1 | 100% | 100% | 0 | 0.10796 | 19.9979 | 4.695 | 10.1361 | High | High | High | 473 | 595 | 2.1589 | 438.9658 | 4.918%
PARADISE 11041571 | PARADISE 1104 | NORTH VALLEY | 0.64266 | 10 | 49.69% | 2 | 2 | 100% | 100% | 0 | 0.10792 | 19.9979 | 4.3768 | 9.4463 | High | High | High | 484 | 596 | 2.1582 | 436.8069 | 4.893%
HIGHLANDS 1103828 | HIGHLANDS 1103 | HUMBOLDT | 6.7375 | 63.3162 | 90.74% | 0 | 3 | 64.07% | 0% | 0 | 0.032181 | 65.3912 | 2.8231 | 5.9408 | Medium | Medium | Medium | 561 | 597 | 2.1043 | 434.6487 | 4.869%
PACIFICA 1101CB | PACIFICA 1101 | PENINSULA | 1.1754 | 10 | 25.99% | 0 | 0 | 43.55% | 100% | 0 | 0.044128 | 47.6367 | 3.8732 | 8.142 | Medium | Medium | High | 512 | 598 | 2.1021 | 432.5444 | 4.846%
SAN LUIS OBISPO 110342344 | SAN LUIS OBISPO 1103 | LOS PADRES | 7.6647 | 51.698 | 64.08% | 0 | 1 | 70.58% | 0% | 0 | 0.031898 | 65.3912 | 2.5342 | 5.286 | Medium | Medium | Medium | 578 | 599 | 2.0859 | 430.4422 | 4.822%
CAMP EVERS 21035753 | CAMP EVERS 2103 | CENTRAL COAST | 2.4228 | 18.1993 | 27.31% | 10 | 4 | 100% | 100% | 0 | 0.13875 | 14.9507 | 3.8491 | 7.9846 | High | High | High | 518 | 600 | 2.0744 | 428.3564 | 4.799%
NORTH BRANCH 110111206 | NORTH BRANCH 1101 | STOCKTON | 17.2475 | 65.0034 | 87.98% | 1 | 4 | 96.4% | 0% | 0 | 0.057888 | 35.3263 | 3.4658 | 7.0874 | Medium | Medium | High | 532 | 601 | 2.045 | 426.282 | 4.776%
WEIMER 1101 | WEIMER 1101 | (blank) | 0.15676 | 70 | 100% | 0 | 0 | 100% | 0% | 0 | 0.042368 | 47.6367 | 1.6634 | 3.3572 | Medium | Medium | Low | 654 | 602 | 2.0183 | 424.237 | 4.753%
PASO ROBLES 1103N50 | PASO ROBLES 1103 | LOS PADRES | 2.1383 | 48.485 | 34.16% | 0 | 1 | 100% | 0% | 0 | 0.042301 | 47.6367 | 3.2748 | 6.599 | Medium | Medium | High | 547 | 603 | 2.0151 | 422.2187 | 4.73%
CRESCENT MILLS 2101CB | CRESCENT MILLS 2101 | NORTH VALLEY | 4.0564 | 89.8056 | 75.4% | 0 | 1 | 71.09% | 0% | 0 | 0.030639 | 65.3912 | 2.6018 | 5.2128 | Medium | Medium | Medium | 581 | 604 | 2.0035 | 420.2036 | 4.707%
MOLINO 11015042 | MOLINO 1101 | SONOMA | 5.4336 | 70.9721 | 53.86% | 5 | 2 | 79.32% | 0% | 0 | 0.030542 | 65.3912 | 3.0912 | 6.1735 | Medium | Medium | High | 553 | 605 | 1.9971 | 418.2001 | 4.685%
DUNBAR 11022359 | DUNBAR 1102 | SONOMA | 4.5098 | 82.5925 | 84.36% | 0 | 1 | 100% | 0% | 0 | 0.041489 | 47.6367 | 3.4865 | 6.8907 | Medium | Medium | High | 539 | 606 | 1.9764 | 416.203 | 4.663%
BRUNSWICK 111063100 | BRUNSWICK 1110 | SIERRA | 4.1271 | 39.6111 | 66.99% | 1 | 2 | 100% | 0% | 0 | 0.041392 | 47.6367 | 2.706 | 5.3357 | Medium | Medium | Medium | 577 | 607 | 1.9718 | 414.2266 | 4.641%
HALF MOON BAY 110398440 | HALF MOON BAY 1103 | PENINSULA | 8.1037 | 78.0886 | 41.99% | 8 | 1 | 100% | 0% | 0 | 0.041193 | 47.6367 | 2.3386 | 4.589 | Medium | Medium | Medium | 605 | 608 | 1.9623 | 412.2548 | 4.618%
COTATI 1103132 | COTATI 1103 | SONOMA | 25.3022 | 74.6812 | 24.81% | 4 | 9 | 100% | 0% | 0 | 0.073801 | 26.5534 | 2.0508 | 4.0188 | High | High | Low | 624 | 609 | 1.9597 | 410.2925 | 4.596%
VACAVILLE 1108 | VACAVILLE 1108 | SACRAMENTO | 0.027876 | 65 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041002 | 47.6367 | 1.5966 | 3.1185 | Medium | Medium | Low | 672 | 610 | 1.9532 | 408.3329 | 4.574%
BIG BASIN 11019773 | BIG BASIN 1101 | CENTRAL COAST | 0.4507 | 10 | 17.07% | 7 | 0 | 100% | 100% | 0 | 0.097654 | 19.9979 | 3.1187 | 6.0905 | High | High | High | 555 | 611 | 1.9529 | 406.3796 | 4.553%
PINECREST 0401CB | PINECREST 0401 | YOSEMITE | 0.021247 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 14.9507 | 0.97713 | 1.9024 | High | High | Low | 768 | 612 | 1.9469 | 404.4268 | 4.531%
PINECREST 0401 | PINECREST 0401 | YOSEMITE | 0.0016115 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 14.9507 | 0.97537 | 1.899 | High | High | Low | 769 | 612 | 1.9469 | 402.4798 | 4.509%
SILVERADO 2104726 | SILVERADO 2104 | NORTH BAY | 29.6312 | 77.5719 | 85.35% | 3 | 1 | 83.81% | 20.91% | 0 | 0.072604 | 26.5534 | 2.6935 | 5.1927 | High | High | Medium | 582 | 614 | 1.9279 | 400.5329 | 4.487%
BELLEVUE 2103478 | BELLEVUE 2103 | SONOMA | 7.8213 | 71.5626 | 88.7% | 0 | 2 | 38.92% | 0% | 0 | 0.02921 | 65.3912 | 3.3117 | 6.3256 | Medium | Medium | High | 550 | 615 | 1.9101 | 398.6051 | 4.466%
MIRABEL 11027401 | MIRABEL 1102 | SONOMA | 1.0644 | 17.3394 | 6.536% | 3 | 1 | 100% | 100% | 0 | 0.071799 | 26.5534 | 2.9335 | 5.5928 | High | High | Medium | 568 | 616 | 1.9065 | 396.695 | 4.444%
HIGHLANDS 1102628 | HIGHLANDS 1102 | HUMBOLDT | 14.1896 | 81.6211 | 32.89% | 0 | 6 | 100% | 58.23% | 1 | 0.095308 | 19.9979 | 2.6661 | 5.0814 | High | High | Medium | 583 | 617 | 1.906 | 394.7885 | 4.423%
CLARKSVILLE 2104CB | CLARKSVILLE 2104 | SIERRA | 9.4695 | 34.2727 | 54.5% | 0 | 3 | 89.57% | 0% | 0 | 0.028962 | 65.3912 | 3.5993 | 6.8166 | Medium | Medium | High | 541 | 618 | 1.8939 | 392.8825 | 4.401%
CORRAL 110136652 | CORRAL 1101 | STOCKTON | 18.0317 | 36.0873 | 87.44% | 1 | 8 | 100% | 0% | 0 | 0.053562 | 35.3263 | 1.4501 | 2.7438 | Medium | Medium | Low | 703 | 619 | 1.8922 | 390.9886 | 4.38%
VACAVILLE 110838316 | VACAVILLE 1108 | SACRAMENTO | 14.7024 | 65.6281 | 99.57% | 1 | 4 | 63.02% | 0% | 0 | 0.052621 | 35.3263 | 1.6146 | 3.0014 | Medium | Medium | Low | 684 | 620 | 1.8589 | 389.0965 | 4.359%
BRUNSWICK 110378862 | BRUNSWICK 1103 | SIERRA | 0.84386 | 75.0835 | 56.54% | 0 | 0 | 62.09% | 0% | 0 | 0.021418 | 85.4511 | 3.1475 | 5.7606 | Low | Low | High | 563 | 621 | 1.8302 | 387.2376 | 4.338%
RED BLUFF 110451238 | RED BLUFF 1104 | NORTH VALLEY | 39.381 | 43.7242 | 96.09% | 3 | 21 | 100% | 0% | 0 | 0.089857 | 19.9979 | 1.2852 | 2.3095 | High | High | Low | 744 | 622 | 1.7969 | 385.4074 | 4.318%
HIGHLANDS 11031282 | HIGHLANDS 1103 | HUMBOLDT | 15.0139 | 42.6416 | 99.84% | 3 | 8 | 89.98% | 0% | 0 | 0.050585 | 35.3263 | 2.5601 | 4.5749 | Medium | Medium | Medium | 606 | 623 | 1.787 | 383.6104 | 4.298%
BUELLTON 1102Y50 | BUELLTON 1102 | LOS PADRES | 11.1963 | 40.402 | 55.79% | 1 | 7 | 87.11% | 0% | 0 | 0.037194 | 47.6367 | 2.389 | 4.2328 | Medium | Medium | Medium | 617 | 624 | 1.7718 | 381.8235 | 4.278%
PUTAH CREEK 110267858 | PUTAH CREEK 1102 | SACRAMENTO | 11.5068 | 51.7319 | 80.2% | 2 | 0 | 99.07% | 0% | 0 | 0.037122 | 47.6367 | 1.5751 | 2.7854 | Medium | Medium | Low | 700 | 625 | 1.7684 | 380.0517 | 4.258%
RACETRACK 170423195 | RACETRACK 1704 | YOSEMITE | 7.7484 | 59.3101 | 42.51% | 0 | 0 | 100% | 0% | 0 | 0.036794 | 47.6367 | 1.973 | 3.4581 | Medium | Medium | Low | 649 | 626 | 1.7528 | 378.2833 | 4.238%
OLEMA 11011200 | OLEMA 1101 | NORTH BAY | 2.8963 | 61.7343 | 11.72% | 2 | 7 | 100% | 0% | 0 | 0.026697 | 65.3912 | 2.5297 | 4.4162 | Medium | Medium | Medium | 612 | 627 | 1.7458 | 376.5305 | 4.218%
PACIFICA 11015001 | PACIFICA 1101 | PENINSULA | 1.7299 | 13.6047 | 57.13% | 0 | 0 | 33.8% | 76.31% | 0 | 0.036346 | 47.6367 | 3.6453 | 6.3114 | Medium | Medium | High | 551 | 628 | 1.7314 | 374.7848 | 4.199%
LAYTONVILLE 110189606 | LAYTONVILLE 1101 | HUMBOLDT | 11.3479 | 67.7426 | 99.65% | 4 | 7 | 95.33% | 0% | 0 | 0.048183 | 35.3263 | 1.5294 | 2.6033 | Medium | Medium | Low | 715 | 629 | 1.7021 | 373.0534 | 4.179%
ELK CREEK 1101CB | ELK CREEK 1101 | NORTH VALLEY | 0.084247 | 80 | 68.8% | 0 | 0 | 100% | 0% | 0 | 0.035328 | 47.6367 | 1.406 | 2.3661 | Medium | Medium | Low | 735 | 630 | 1.6829 | 371.3513 | 4.16%
VACA DIXON 110118292 | VACA DIXON 1101 | SACRAMENTO | 0.82637 | 74.5954 | 100% | 0 | 2 | 13.83% | 0% | 0 | 0.019682 | 85.4511 | 2.9566 | 4.9725 | Low | Low | Medium | 587 | 631 | 1.6818 | 369.6684 | 4.141%
COARSEGOLD 21046288 | COARSEGOLD 2104 | YOSEMITE | 10.4247 | 64.6171 | 98.8% | 1 | 30 | 100% | 0% | 0 | 0.084064 | 19.9979 | 1.84 | 3.0932 | High | High | Low | 675 | 632 | 1.6811 | 367.9866 | 4.122%
MORAGA 110531512 | MORAGA 1105 | DIABLO | 1.6381 | 82.7006 | 6.913% | 0 | 1 | 35.45% | 68.16% | 0 | 0.035075 | 47.6367 | 3.886 | 6.493 | Medium | Medium | High | 549 | 633 | 1.6709 | 366.3055 | 4.104%
IGNACIO 11042447 | IGNACIO 1104 | NORTH BAY | 0.96609 | 32.7068 | 67.19% | 4 | 5 | 90.01% | 0% | 0 | 0.034924 | 47.6367 | 2.9164 | 4.852 | Medium | Medium | Medium | 592 | 634 | 1.6637 | 364.6346 | 4.085%
LAKEVILLE 11023341 | LAKEVILLE 1102 | SONOMA | 8.3809 | 81.4101 | 63.14% | 2 | 0 | 66.79% | 0% | 0 | 0.02532 | 65.3912 | 2.4798 | 4.1058 | Medium | Medium | Medium | 620 | 635 | 1.6557 | 362.9709 | 4.066%
WISE 1102307494 | WISE 1102 | SIERRA | 32.9312 | 34.3215 | 79.46% | 1 | 9 | 98.67% | 0% | 0 | 0.082577 | 19.9979 | 2.2151 | 3.6579 | High | High | Low | 638 | 636 | 1.6514 | 361.3152 | 4.048%
SPRING GAP 17029280 | SPRING GAP 1702 | YOSEMITE | 6.3606 | 34.7112 | 42.89% | 5 | 5 | 100% | 100% | 0 | 0.14642 | 11.2183 | 1.7184 | 2.8225 | High | High | Low | 695 | 637 | 1.6426 | 359.6639 | 4.029%
CAMP EVERS 2105BL 2101 | CAMP EVERS 2105 | CENTRAL COAST | 0.0032282 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 26.5534 | 3.7013 | 6.0502 | High | High | High | 557 | 638 | 1.6346 | 358.0213 | 4.011%
GREENBRAE 1103 | GREENBRAE 1103 | NORTH BAY | 0.019268 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 26.5534 | 3.6958 | 6.0412 | High | High | High | 558 | 638 | 1.6346 | 356.3867 | 3.993%
LAURELES 111184523 | LAURELES 1111 | CENTRAL COAST | 1.2223 | 80.6528 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045426 | 35.3263 | 1.8947 | 3.0405 | Medium | Medium | Low | 680 | 640 | 1.6047 | 354.7521 | 3.974%
MERCED FALLS 110285002 | MERCED FALLS 1102 | YOSEMITE | 35.632 | 29.6878 | 97.17% | 0 | 6 | 100% | 0% | 0 | 0.059691 | 26.5534 | 0.55157 | 0.87425 | Medium | Medium | Low | 922 | 641 | 1.585 | 353.1473 | 3.956%
BELL 111056214 | BELL 1110 | SIERRA | 0.30639 | 85 | 100% | 0 | 0 | 4.593% | 0% | 0 | 0.018495 | 85.4511 | 2.9334 | 4.636 | Low | Low | Medium | 602 | 642 | 1.5804 | 351.5623 | 3.938%
VACAVILLE 111113652 | VACAVILLE 1111 | SACRAMENTO | 4.3673 | 25.6376 | 64.23% | 1 | 3 | 100% | 0% | 0 | 0.033137 | 47.6367 | 3.0974 | 4.8893 | Medium | Medium | High | 590 | 643 | 1.5785 | 349.9819 | 3.921%
APPLE HILL 1104CB | APPLE HILL 1104 | SIERRA | 4.2262 | 51.4608 | 51.9% | 3 | 4 | 100% | 0% | 0 | 0.03278 | 47.6367 | 2.5597 | 3.9971 | Medium | Medium | Medium | 625 | 644 | 1.5616 | 348.4034 | 3.903%
ROSSMOOR 1102CB | ROSSMOOR 1102 | DIABLO | 0.0028423 | 10 | 0% | 0 | 0 | 0.1985% | 100% | 0 | 0.023559 | 65.3912 | 3.8658 | 5.9555 | Medium | Medium | High | 560 | 645 | 1.5406 | 346.8418 | 3.886%
STELLING 11102243 | STELLING 1110 | DE ANZA | 1.8981 | 73.5691 | 46.49% | 9 | 0 | 100% | 0% | 0 | 0.031796 | 47.6367 | 3.2106 | 4.8628 | Medium | Medium | High | 591 | 646 | 1.5146 | 345.3012 | 3.868%
JESSUP 11011993 | JESSUP 1101 | NORTH VALLEY | 2.9672 | 23.0128 | 100% | 0 | 1 | 100% | 0% | 0 | 0.031722 | 47.6367 | 2.0979 | 3.1701 | Medium | Medium | Low | 667 | 647 | 1.5111 | 343.7866 | 3.851%
TEMPLETON 2113A70 | TEMPLETON 2113 | LOS PADRES | 22.5502 | 49.7318 | 87.96% | 0 | 9 | 33.69% | 0% | 0 | 0.03134 | 47.6367 | 2.3941 | 3.5742 | Medium | Medium | Medium | 642 | 648 | 1.4929 | 342.2755 | 3.834%
CORRAL 110112612 | CORRAL 1101 | STOCKTON | 18.7862 | 47.6011 | 68.25% | 0 | 10 | 93.49% | 0% | 0 | 0.042229 | 35.3263 | 2.2608 | 3.3727 | Medium | Medium | Medium | 652 | 649 | 1.4918 | 340.7826 | 3.818%
NORTH DUBLIN 210311101 | NORTH DUBLIN 2103 | MISSION | 3.6926 | 66.2488 | 89.68% | 0 | 0 | 100% | 0% | 0 | 0.05582 | 26.5534 | 3.6138 | 5.3564 | Medium | Medium | High | 575 | 650 | 1.4822 | 339.2908 | 3.801%
BIG BASIN 1102 | BIG BASIN 1102 | CENTRAL COAST | 0.014511 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 11.2183 | 2.3875 | 3.4878 | High | High | Medium | 645 | 651 | 1.4609 | 337.8086 | 3.784%
GIRVAN 1102 | GIRVAN 1102 | NORTH VALLEY | 0.038598 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 11.2183 | 1.7778 | 2.5971 | High | High | Low | 716 | 651 | 1.4609 | 336.3477 | 3.768%
SEACLIFF 0402CB | SEACLIFF 0402 | CENTRAL COAST | 0.96395 | 10 | 24.34% | 2 | 0 | 62.04% | 63.7% | 0 | 0.030212 | 47.6367 | 3.8167 | 5.4929 | Medium | Medium | High | 572 | 653 | 1.4392 | 334.8868 | 3.752%
WISE 11022054 | WISE 1102 | SIERRA | 12.9562 | 34.6019 | 54.65% | 2 | 5 | 100% | 0% | 0 | 0.030193 | 47.6367 | 2.4077 | 3.463 | Medium | Medium | Medium | 646 | 654 | 1.4383 | 333.4476 | 3.736%
CRESCENT MILLS 21012056 | CRESCENT MILLS 2101 | NORTH VALLEY | 2.8566 | 93.184 | 33.06% | 0 | 0 | 44.02% | 0% | 0 | 0.016743 | 85.4511 | 2.3025 | 3.2941 | Low | Low | Medium | 658 | 655 | 1.4307 | 332.0093 | 3.719%
FULTON 1107CB | FULTON 1107 | SONOMA | 0.65239 | 10 | 62.57% | 2 | 0 | 4.947% | 100% | 0 | 0.053816 | 26.5534 | 2.4231 | 3.4626 | Medium | Medium | Medium | 647 | 656 | 1.429 | 330.5786 | 3.703%
OCEANO 1104Q08 | OCEANO 1104 | LOS PADRES | 12.4392 | 24.3462 | 67.44% | 7 | 8 | 100% | 0% | 0 | 0.040257 | 35.3263 | 3.0746 | 4.3725 | Medium | Medium | Medium | 614 | 657 | 1.4221 | 329.1496 | 3.687%
UKIAH 1113CB | UKIAH 1113 | HUMBOLDT | 6.3928 | 56.8513 | 87.48% | 1 | 9 | 40.25% | 0% | 0 | 0.040164 | 35.3263 | 2.6035 | 3.694 | Medium | Medium | Medium | 635 | 658 | 1.4188 | 327.7275 | 3.671%
CORRAL 110112606 | CORRAL 1101 | STOCKTON | 22.4607 | 31.7729 | 96.48% | 1 | 4 | 100% | 0% | 0 | 0.040006 | 35.3263 | 2.252 | 3.1827 | Medium | Medium | Medium | 665 | 659 | 1.4133 | 326.3087 | 3.656%
RESERVATION ROAD 11013026 | RESERVATION ROAD 1101 | CENTRAL COAST | 21.8928 | 54.2364 | 36.93% | 7 | 8 | 96.87% | 0% | 0 | 0.070296 | 19.9979 | 1.6766 | 2.3569 | High | High | Low | 737 | 660 | 1.4058 | 324.8954 | 3.64%
SAND CREEK 11037140 | SAND CREEK 1103 | FRESNO | 26.314 | 18.5001 | 91.83% | 0 | 4 | 100% | 0% | 0 | 0.03967 | 35.3263 | 2.47 | 3.4614 | Medium | Medium | Medium | 648 | 661 | 1.4014 | 323.4896 | 3.624%
GUALALA 11124431 | GUALALA 1112 | HUMBOLDT | 1.4123 | 70.1709 | 0% | 0 | 4 | 100% | 0% | 0 | 0.02067 | 65.3912 | 1.946 | 2.6304 | Low | Low | Low | 712 | 662 | 1.3517 | 322.0883 | 3.608%
ALTO 1125935 | ALTO 1125 | NORTH BAY | 3.0231 | 20.8124 | 24.9% | 7 | 7 | 94.09% | 0% | 0 | 0.038197 | 35.3263 | 2.7615 | 3.7263 | Medium | Medium | Medium | 634 | 663 | 1.3494 | 320.7366 | 3.593%
PARADISE 110299226 | PARADISE 1102 | NORTH VALLEY | 0.94174 | 38.0724 | 24.71% | 0 | 0 | 9.702% | 100% | 0 | 0.037935 | 35.3263 | 4.1275 | 5.5313 | Medium | Medium | High | 571 | 664 | 1.3401 | 319.3872 | 3.578%
MOUNTAIN QUARRIES 21016953 | MOUNTAIN QUARRIES 2101 | SIERRA | 5.7089 | 53.1337 | 100% | 0 | 0 | 100% | 0% | 0 | 0.037926 | 35.3263 | 3.1367 | 4.2025 | Medium | Medium | High | 618 | 665 | 1.3398 | 318.0471 | 3.563%
SHINGLE SPRINGS 211051800 | SHINGLE SPRINGS 2110 | SIERRA | 9.4169 | 11.4226 | 65.37% | 2 | 2 | 96.5% | 41.26% | 0 | 0.049018 | 26.5534 | 2.9295 | 3.813 | Medium | Medium | Medium | 630 | 666 | 1.3016 | 316.7073 | 3.548%
HAMILTON BRANCH 11012046 | HAMILTON BRANCH 1101 | NORTH VALLEY | 9.1511 | 77.8147 | 51.04% | 2 | 2 | 99.57% | 0% | 0 | 0.036581 | 35.3263 | 2.517 | 3.2527 | Medium | Medium | Medium | 659 | 667 | 1.2923 | 315.4057 | 3.533%
WOODSIDE 1101 | WOODSIDE 1101 | PENINSULA | 0.091557 | 33.2557 | 52.71% | 3 | 2 | 100% | 100% | 0 | 0.1142 | 11.2183 | 2.2665 | 2.9039 | High | High | Medium | 688 | 668 | 1.2812 | 314.1134 | 3.519%
PAUL SWEET 2102 | PAUL SWEET 2102 | CENTRAL COAST | 0.085046 | 10 | 0% | 3 | 0 | 100% | 100% | 0 | 0.063894 | 19.9979 | 3.0738 | 3.9275 | High | High | Medium | 626 | 669 | 1.2777 | 312.8323 | 3.505%
ELK CREEK 11012008 | ELK CREEK 1101 | NORTH VALLEY | 2.1575 | 78.9163 | 100% | 0 | 1 | 11.89% | 0% | 0 | 0.019472 | 65.3912 | 1.9305 | 2.4581 | Low | Low | Low | 725 | 670 | 1.2733 | 311.5545 | 3.49%
MADISON 210113372 | MADISON 2101 | SACRAMENTO | 3.7782 | 89.8591 | 100% | 0 | 0 | 99.16% | 0% | 0 | 0.047853 | 26.5534 | 1.0386 | 1.3197 | Medium | Medium | Low | 838 | 671 | 1.2706 | 310.2812 | 3.476%
DEL MAR 210975802 | DEL MAR 2109 | SIERRA | 0.35089 | 17.4936 | 85.01% | 0 | 1 | 84.46% | 0% | 0 | 0.026543 | 47.6367 | 2.444 | 3.0902 | Medium | Medium | Medium | 676 | 672 | 1.2644 | 309.0106 | 3.462%
MONTE RIO 1113477 | MONTE RIO 1113 | SONOMA | 1.8187 | 34.6297 | 52.03% | 0 | 3 | 100% | 100% | 0 | 0.11271 | 11.2183 | 2.8387 | 3.5893 | High | High | Medium | 639 | 673 | 1.2644 | 307.7461 | 3.448%
DESCHUTES 11049726 | DESCHUTES 1104 | NORTH VALLEY | 14.9653 | 23.7872 | 88.61% | 1 | 3 | 89% | 0% | 0 | 0.03574 | 35.3263 | 2.837 | 3.5819 | Medium | Medium | Medium | 641 | 674 | 1.2626 | 306.4817 | 3.433%
WILLITS 1103538 | WILLITS 1103 | HUMBOLDT | 6.4253 | 81.3489 | 100% | 3 | 1 | 100% | 27.62% | 0 | 0.083475 | 14.9507 | 1.7136 | 2.1386 | High | High | Low | 753 | 675 | 1.248 | 305.2191 | 3.419%
TAR FLAT 0401 | TAR FLAT 0401 | YOSEMITE | 0.026649 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 19.9979 | 3.0633 | 3.771 | High | High | Medium | 631 | 676 | 1.2311 | 303.9711 | 3.405%
BELL 110750172 | BELL 1107 | SIERRA | 17.5892 | 13.0992 | 68.99% | 0 | 6 | 94.29% | 0% | 0 | 0.046234 | 26.5534 | 2.5016 | 3.0712 | Medium | Medium | Medium | 679 | 677 | 1.2277 | 302.7401 | 3.392%
FLINT 1101750 | FLINT 1101 | SIERRA | 3.8545 | 52.6304 | 83.81% | 0 | 0 | 41.31% | 0% | 0 | 0.018732 | 65.3912 | 2.5792 | 3.1593 | Low | Low | Medium | 669 | 678 | 1.2249 | 301.5124 | 3.378%
RINCON 1103CB | RINCON 1103 | SONOMA | 2.6796 | 27.7294 | 25.63% | 1 | 1 | 89.08% | 47% | 0 | 0.034549 | 35.3263 | 3.169 | 3.8678 | Medium | Medium | High | 628 | 679 | 1.2205 | 300.2875 | 3.364%
HAMILTON BRANCH 11013049 | HAMILTON BRANCH 1101 | NORTH VALLEY | 0.54973 | 41.4686 | 100% | 0 | 1 | 32.98% | 0% | 0 | 0.018634 | 65.3912 | 2.1667 | 2.6401 | Low | Low | Low | 710 | 680 | 1.2185 | 299.067 | 3.35%
COARSEGOLD 2104CB | COARSEGOLD 2104 | YOSEMITE | 2.4475 | 54.0073 | 41.51% | 0 | 3 | 100% | 0% | 0 | 0.025403 | 47.6367 | 2.1019 | 2.5435 | Medium | Medium | Low | 721 | 681 | 1.2101 | 297.8485 | 3.337%
VALLEY VIEW 1103CB | VALLEY VIEW 1103 | EAST BAY | 0.06028 | 65 | 0% | 0 | 0 | 0.9308% | 100% | 0 | 0.034198 | 35.3263 | 4.6903 | 5.6663 | Medium | Medium | High | 565 | 682 | 1.2081 | 296.6384 | 3.323%
PUTAH CREEK 1102CB | PUTAH CREEK 1102 | SACRAMENTO | 4.8366 | 82.2611 | 100% | 0 | 0 | 37.85% | 0% | 0 | 0.025161 | 47.6367 | 2.1795 | 2.6123 | Medium | Medium | Low | 714 | 683 | 1.1986 | 295.4303 | 3.31%
PANORAMA 11019092 | PANORAMA 1101 | NORTH VALLEY | 9.7913 | 10 | 99.08% | 0 | 8 | 48.48% | 0% | 0 | 0.033887 | 35.3263 | 1.6659 | 1.9943 | Medium | Medium | Low | 761 | 684 | 1.1971 | 294.2317 | 3.296%
OAKHURST 110348842 | OAKHURST 1103 | YOSEMITE | 2.3666 | 32.8421 | 100% | 0 | 9 | 82.85% | 0% | 0 | 0.033725 | 35.3263 | 2.6913 | 3.2064 | Medium | Medium | Medium | 663 | 685 | 1.1914 | 293.0347 | 3.283%
SILVERADO 2104CB | SILVERADO 2104 | NORTH BAY | 1.8059 | 23.2702 | 84.92% | 2 | 1 | 36.1% | 66.89% | 0 | 0.044573 | 26.5534 | 3.6993 | 4.3783 | Medium | Medium | High | 613 | 686 | 1.1836 | 291.8433 | 3.269%
SANTA YNEZ 1104Y04 | SANTA YNEZ 1104 | LOS PADRES | 15.3206 | 51.8152 | 75.91% | 0 | 12 | 68.36% | 0% | 0 | 0.033153 | 35.3263 | 2.4224 | 2.837 | Medium | Medium | Medium | 694 | 687 | 1.1712 | 290.6597 | 3.256%
BASALT 11065039 | BASALT 1106 | NORTH BAY | 1.6775 | 85.8937 | 60.16% | 0 | 1 | 30.77% | 0% | 0 | 0.017795 | 65.3912 | 3.2158 | 3.7421 | Low | Low | High | 633 | 688 | 1.1636 | 289.4885 | 3.243%
STAFFORD 1102524 | STAFFORD 1102 | NORTH BAY | 3.4472 | 66.1749 | 51.31% | 1 | 2 | 26.91% | 0% | 0 | 0.024387 | 47.6367 | 2.779 | 3.2285 | Medium | Medium | Medium | 660 | 689 | 1.1617 | 288.3249 | 3.23%
CORRAL 110214026 | CORRAL 1102 | STOCKTON | 10.1342 | 44.5079 | 47.19% | 1 | 3 | 100% | 0% | 0 | 0.03277 | 35.3263 | 2.6188 | 3.0316 | Medium | Medium | Medium | 682 | 690 | 1.1576 | 287.1632 | 3.217%
MONTICELLO 1101720 | MONTICELLO 1101 | NORTH BAY | 7.5573 | 64.5271 | 99.74% | 1 | 2 | 90.69% | 0% | 0 | 0.057594 | 19.9979 | 2.4222 | 2.7897 | Medium | Medium | Medium | 697 | 691 | 1.1518 | 286.0055 | 3.204%
HICKS 2101XR250 | HICKS 2101 | SAN JOSE | 7.0147 | 55.6197 | 44.17% | 2 | 7 | 53.71% | 28.46% | 0 | 0.042978 | 26.5534 | 3.5951 | 4.1027 | Medium | Medium | High | 621 | 692 | 1.1412 | 284.8538 | 3.191%
STAFFORD 11021202 | STAFFORD 1102 | NORTH BAY | 7.2996 | 85.3549 | 21.22% | 0 | 3 | 92.36% | 0% | 0 | 0.031995 | 35.3263 | 2.1233 | 2.3999 | Medium | Medium | Low | 732 | 693 | 1.1303 | 283.7125 | 3.178%
JESSUP 11023105 | JESSUP 1102 | NORTH VALLEY | 5.7601 | 31.7951 | 100% | 0 | 2 | 92.48% | 0% | 0 | 0.031899 | 35.3263 | 2.1459 | 2.4181 | Medium | Medium | Low | 729 | 694 | 1.1269 | 282.5823 | 3.166%
LINCOLN 11042070 | LINCOLN 1104 | SIERRA | 21.0429 | 49.8208 | 65.19% | 5 | 11 | 72.52% | 0% | 0 | 0.042249 | 26.5534 | 2.4592 | 2.7588 | Medium | Medium | Medium | 701 | 695 | 1.1219 | 281.4554 | 3.153%
GARBERVILLE 11022124 | GARBERVILLE 1102 | HUMBOLDT | 3.1243 | 97.624 | 0% | 0 | 1 | 100% | 0% | 0 | 0.023355 | 47.6367 | 1.6787 | 1.8676 | Medium | Medium | Low | 774 | 696 | 1.1125 | 280.3335 | 3.141%
PASO ROBLES 110359763 | PASO ROBLES 1103 | LOS PADRES | 2.8193 | 65.7222 | 66.01% | 0 | 0 | 100% | 0% | 0 | 0.031437 | 35.3263 | 2.0367 | 2.2619 | Medium | Medium | Low | 748 | 697 | 1.1106 | 279.221 | 3.128%
MORAGA 110518396 | MORAGA 1105 | DIABLO | 0.21093 | 45.5725 | 100% | 0 | 2 | 18.41% | 0% | 0 | 0.016943 | 65.3912 | 4.3309 | 4.7983 | Low | Low | High | 595 | 698 | 1.1079 | 278.1104 | 3.116%
GANSNER 110199388 | GANSNER 1101 | NORTH VALLEY | 2.0835 | 75.9591 | 98.87% | 1 | 0 | 93.65% | 0% | 0 | 0.041605 | 26.5534 | 3.0558 | 3.3759 | Medium | Medium | Medium | 651 | 699 | 1.1048 | 277.0025 | 3.103%
PARADISE 1104CB | PARADISE 1104 | NORTH VALLEY | 0.54287 | 10 | 13.72% | 1 | 1 | 13.43% | 100% | 0 | 0.030938 | 35.3263 | 4.1742 | 4.5621 | Medium | Medium | High | 607 | 700 | 1.0929 | 275.8978 | 3.091%
MOLINO 1101891 | MOLINO 1101 | SONOMA | 3.0063 | 38.1554 | 45.65% | 1 | 1 | 95.38% | 41.51% | 0 | 0.054529 | 19.9979 | 2.4796 | 2.7039 | Medium | Medium | Medium | 707 | 701 | 1.0905 | 274.8049 | 3.079%
FROGTOWN 1702 | FROGTOWN 1702 | STOCKTON | 0.0028747 | 65 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041002 | 26.5534 | 2.6562 | 2.8919 | Medium | Medium | Medium | 689 | 702 | 1.0887 | 273.7144 | 3.066%
SHINGLE SPRINGS 210935598 | SHINGLE SPRINGS 2109 | SIERRA | 10.9289 | 31.2867 | 70.52% | 1 | 5 | 100% | 42.6% | 0 | 0.072647 | 14.9507 | 2.2274 | 2.4192 | High | High | Low | 728 | 703 | 1.0861 | 272.6256 | 3.054%
MOLINO 110241392 | MOLINO 1102 | SONOMA | 3.7264 | 58.0945 | 65.77% | 1 | 0 | 25.48% | 0% | 0 | 0.016595 | 65.3912 | 2.9568 | 3.2086 | Low | Low | Medium | 662 | 704 | 1.0852 | 271.5395 | 3.042%
PUEBLO 11042802 | PUEBLO 1104 | NORTH BAY | 9.7765 | 58.2394 | 48.14% | 0 | 5 | 89.72% | 0% | 0 | 0.072026 | 14.9507 | 3.0683 | 3.3041 | High | High | Medium | 656 | 705 | 1.0768 | 270.4543 | 3.03%
OLETA 11011217 | OLETA 1101 | STOCKTON | 14.427 | 60.7702 | 100% | 1 | 3 | 83.71% | 43.16% | 1 | 0.071429 | 14.9507 | 2.1108 | 2.2542 | High | High | Low | 749 | 706 | 1.0679 | 269.3775 | 3.018%
OAKHURST 1101CB | OAKHURST 1101 | YOSEMITE | 2.8974 | 35.5621 | 74.52% | 0 | 12 | 97.3% | 1.934% | 0 | 0.040153 | 26.5534 | 2.8286 | 3.0158 | Medium | Medium | Medium | 683 | 707 | 1.0662 | 268.3096 | 3.006%
FOOTHILL 1101CB | FOOTHILL 1101 | LOS PADRES | 10.7012 | 70.0715 | 52.58% | 0 | 2 | 48.74% | 0% | 0 | 0.039956 | 26.5534 | 2.9872 | 3.1694 | Medium | Medium | Medium | 668 | 708 | 1.061 | 267.2434 | 2.994%
PETALUMA C 1108618 | PETALUMA C 1108 | SONOMA | 8.1405 | 67.3719 | 25.14% | 5 | 1 | 74.64% | 0% | 0 | 0.022157 | 47.6367 | 3.0104 | 3.1775 | Medium | Medium | Medium | 666 | 709 | 1.0555 | 266.1824 | 2.982%
BRUNSWICK 1106 | BRUNSWICK 1106 | SIERRA | 0.037997 | 60 | 100% | 0 | 0 | 100% | 0% | 0 | 0.039678 | 26.5534 | 2.6004 | 2.7397 | Medium | Medium | Medium | 705 | 710 | 1.0536 | 265.1269 | 2.97%
EAST QUINCY 1101CB | EAST QUINCY 1101 | NORTH VALLEY | 2.2646 | 54.1438 | 97.01% | 0 | 2 | 28.47% | 0% | 0 | 0.022042 | 47.6367 | 3.0485 | 3.2009 | Medium | Medium | Medium | 664 | 711 | 1.05 | 264.0733 | 2.958%
LINCOLN 11045391 | LINCOLN 1104 | SIERRA | 0.95086 | 68.8646 | 19.08% | 0 | 0 | 100% | 0% | 0 | 0.022019 | 47.6367 | 2.7141 | 2.8468 | Medium | Medium | Medium | 693 | 712 | 1.0489 | 263.0233 | 2.947%
ELECTRA 1101L1697 | ELECTRA 1101 | STOCKTON | 5.4545 | 12.0564 | 100% | 1 | 2 | 100% | 0% | 0 | 0.039464 | 26.5534 | 2.6165 | 2.7419 | Medium | Medium | Medium | 704 | 713 | 1.0479 | 261.9745 | 2.935%
CAMP EVERS 2106834583 | CAMP EVERS 2106 | CENTRAL COAST | 0.60497 | 39.087 | 36.91% | 0 | 0 | 100% | 69.26% | 0 | 0.069915 | 14.9507 | 3.9087 | 4.0857 | High | High | High | 623 | 714 | 1.0453 | 260.9265 | 2.923%
PEORIA 170411232 | PEORIA 1704 | YOSEMITE | 13.0063 | 19.4612 | 87.58% | 0 | 2 | 75.44% | 0% | 0 | 0.029217 | 35.3263 | 3.195 | 3.2976 | Medium | Medium | High | 657 | 715 | 1.0321 | 259.8813 | 2.911%
BRUNSWICK 11038918 | BRUNSWICK 1103 | SIERRA | 0.62743 | 83.4132 | 18.44% | 0 | 0 | 29.2% | 0% | 0 | 0.012022 | 85.4511 | 2.7121 | 2.7862 | Low | Low | Medium | 699 | 716 | 1.0273 | 258.8492 | 2.9%
NAPA 1112 | NAPA 1112 | NORTH BAY | 0.032215 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 35.3263 | 3.0858 | 3.108 | Medium | Medium | High | 673 | 717 | 1.0072 | 257.8218 | 2.888%
TEMPLETON 21132949 | TEMPLETON 2113 | LOS PADRES | 0.47714 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 35.3263 | 2.6464 | 2.6655 | Medium | Medium | Medium | 709 | 717 | 1.0072 | 256.8146 | 2.877%
CLOVERDALE 110247214 | CLOVERDALE 1102 | SONOMA | 0.027332 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 35.3263 | 2.4417 | 2.4593 | Medium | Medium | Medium | 723 | 717 | 1.0072 | 255.8074 | 2.866%
HOOPA 1101561116 | HOOPA 1101 | HUMBOLDT | 0.012979 | 85 | 0% | 0 | 0 | 100% | 0% | 0 | 0.021028 | 47.6367 | 1.0757 | 1.0775 | Low | Low | Low | 880 | 720 | 1.0017 | 254.8002 | 2.854%
CLARKSVILLE 210575884 | CLARKSVILLE 2105 | SIERRA | 10.3522 | 19.5403 | 73.75% | 1 | 8 | 92.27% | 38.69% | 1 | 0.049935 | 19.9979 | 3.4349 | 3.4301 | Medium | Medium | High | 650 | 721 | 0.9986 | 253.7985 | 2.843%
BRUNSWICK 110633050 | BRUNSWICK 1106 | SIERRA | 1.709 | 18.2327 | 78.9% | 2 | 0 | 44.77% | 0% | 0 | 0.015167 | 65.3912 | 2.9867 | 2.9622 | Low | Low | Medium | 686 | 722 | 0.99181 | 252.7999 | 2.832%
SANTA YNEZ 110477098 | SANTA YNEZ 1104 | LOS PADRES | 10.6194 | 59.0619 | 89.18% | 0 | 4 | 81.31% | 0% | 0 | 0.037257 | 26.5534 | 2.7174 | 2.6883 | Medium | Medium | Medium | 708 | 723 | 0.98931 | 251.8081 | 2.821%
SPRING GAP 170286032 | SPRING GAP 1702 | YOSEMITE | 1.0066 | 66.0059 | 100% | 0 | 0 | 34.72% | 25.18% | 0 | 0.037122 | 26.5534 | 0.83455 | 0.82263 | Medium | Medium | Low | 937 | 724 | 0.98571 | 250.8188 | 2.81%
PETALUMA C 1108600 | PETALUMA C 1108 | SONOMA | 4.0703 | 32.8182 | 38.32% | 2 | 6 | 47.11% | 0% | 0 | 0.020667 | 47.6367 | 2.3993 | 2.3621 | Low | Low | Medium | 736 | 725 | 0.98451 | 249.8331 | 2.799%
OLETA 1101CB | OLETA 1101 | STOCKTON | 3.1205 | 69.4789 | 19.21% | 0 | 0 | 92.33% | 0% | 0 | 0.02053 | 47.6367 | 2.9528 | 2.8878 | Low | Low | Medium | 690 | 726 | 0.97799 | 248.8486 | 2.788%
GRASS VALLEY 1101CB | GRASS VALLEY 1101 | SIERRA | 1.7504 | 55.588 | 24.73% | 1 | 1 | 65.41% | 2.088% | 0 | 0.027071 | 35.3263 | 2.9159 | 2.7885 | Medium | Medium | Medium | 698 | 727 | 0.9563 | 247.8706 | 2.777%
CLOVERDALE 110254760 | CLOVERDALE 1102 | SONOMA | 0.13003 | 10 | 100% | 0 | 0 | 93.87% | 0% | 0 | 0.026858 | 35.3263 | 2.4446 | 2.3195 | Medium | Medium | Medium | 742 | 728 | 0.94881 | 246.9143 | 2.766%
BOLINAS 11011232 | BOLINAS 1101 | NORTH BAY | 2.4469 | 73.1714 | 0% | 0 | 1 | 100% | 0% | 0 | 0.019829 | 47.6367 | 3.3269 | 3.1425 | Low | Low | High | 670 | 729 | 0.94457 | 245.9655 | 2.756%
BELLEVUE 2103648 | BELLEVUE 2103 | SONOMA | 2.2962 | 73.8161 | 100% | 0 | 2 | 14.14% | 0% | 0 | 0.019638 | 47.6367 | 2.9986 | 2.8051 | Low | Low | Medium | 696 | 730 | 0.93548 | 245.0209 | 2.745%
PASO ROBLES 1104R56 | PASO ROBLES 1104 | LOS PADRES | 11.0427 | 56.2868 | 57.45% | 0 | 4 | 89.88% | 0% | 0 | 0.035115 | 26.5534 | 1.8717 | 1.7452 | Medium | Medium | Low | 785 | 731 | 0.93242 | 244.0854 | 2.734%
MORAGA 11058354 | MORAGA 1105 | DIABLO | 0.25208 | 83.2522 | 100% | 0 | 0 | 8.053% | 20.65% | 0 | 0.026277 | 35.3263 | 3.9671 | 3.6826 | Medium | Medium | High | 636 | 732 | 0.92827 | 243.153 | 2.724%
GONZALES 110422418 | GONZALES 1104 | CENTRAL COAST | 0.8424 | 88.5066 | 100% | 0 | 0 | 6.858% | 0% | 0 | 0.019362 | 47.6367 | 1.4832 | 1.368 | Low | Low | Low | 831 | 733 | 0.92235 | 242.2247 | 2.714%
MARIPOSA 210190130 | MARIPOSA 2101 | YOSEMITE | 0.091387 | 70 | 0% | 0 | 0 | 100% | 0% | 0 | 0.019016 | 47.6367 | 2.6983 | 2.4443 | Low | Low | Medium | 726 | 734 | 0.90585 | 241.3024 | 2.703%
NARROWS 21052214 | NARROWS 2105 | SIERRA | 0.0028409 | 70 | 0% | 0 | 0 | 100% | 0% | 0 | 0.019016 | 47.6367 | 2.5602 | 2.3192 | Low | Low | Medium | 743 | 734 | 0.90585 | 240.3965 | 2.693%
PENRYN 11051342 | PENRYN 1105 | SIERRA | 20.5672 | 12.393 | 56.11% | 3 | 12 | 53.03% | 0% | 0 | 0.025263 | 35.3263 | 1.9483 | 1.7388 | Medium | Medium | Low | 787 | 736 | 0.89244 | 239.4907 | 2.683%
FRUITLAND 1141CB | FRUITLAND 1141 | HUMBOLDT | 3.1926 | 94.3084 | 31.06% | 2 | 0 | 100% | 0% | 0 | 0.03355 | 26.5534 | 0.81784 | 0.72859 | Medium | Medium | Low | 966 | 737 | 0.89086 | 238.5982 | 2.673%
COTATI 1102282 | COTATI 1102 | SONOMA | 4.4441 | 39.13 | 50.31% | 2 | 2 | 88.16% | 0% | 0 | 0.025185 | 35.3263 | 2.6402 | 2.349 | Medium | Medium | Medium | 738 | 738 | 0.8897 | 237.7074 | 2.663%
PENRYN 110550548 | PENRYN 1105 | SIERRA | 4.6613 | 28.5134 | 63.43% | 0 | 1 | 38.43% | 0% | 0 | 0.013391 | 65.3912 | 2.1096 | 1.8472 | Low | Low | Low | 776 | 739 | 0.87563 | 236.8177 | 2.653%
UPPER LAKE 11016663 | UPPER LAKE 1101 | HUMBOLDT | 2.3336 | 74.5453 | 100% | 0 | 0 | 100% | 0% | 0 | 0.043648 | 19.9979 | 1.2971 | 1.1322 | Medium | Medium | Low | 871 | 740 | 0.87287 | 235.9421 | 2.643%
MONTICELLO 110165454 | MONTICELLO 1101 | NORTH BAY | 0.17975 | 75.7164 | 100% | 0 | 0 | 9.577% | 0% | 0 | 0.018251 | 47.6367 | 2.4012 | 2.0876 | Low | Low | Medium | 756 | 741 | 0.8694 | 235.0692 | 2.633%
DESCHUTES 11019722 | DESCHUTES 1101 | NORTH VALLEY | 2.8886 | 47.2823 | 92.43% | 0 | 2 | 60.75% | 0% | 0 | 0.024427 | 35.3263 | 2.3843 | 2.0574 | Medium | Medium | Medium | 758 | 742 | 0.8629 | 234.1998 | 2.624%
PINECREST 04011818 | PINECREST 0401 | YOSEMITE | 1.9342 | 47.9328 | 100% | 2 | 2 | 61.15% | 48.76% | 0 | 0.057579 | 14.9507 | 0.83639 | 0.72 | Medium | Medium | Low | 971 | 743 | 0.86084 | 233.3369 | 2.614%
CORRAL 110336680 | CORRAL 1103 | STOCKTON | 9.9701 | 19.0488 | 89.57% | 1 | 2 | 49.8% | 0% | 0 | 0.017976 | 47.6367 | 3.438 | 2.944 | Low | Low | High | 687 | 744 | 0.85633 | 232.476 | 2.604%
ANITA 1106CB | ANITA 1106 | NORTH VALLEY | 0.115 | 85 | 100% | 0 | 0 | 0.3281% | 0% | 0 | 0.017735 | 47.6367 | 1.6583 | 1.401 | Low | Low | Low | 828 | 745 | 0.84484 | 231.6197 | 2.595%
LINCOLN 110451756 | LINCOLN 1104 | SIERRA | 15.5512 | 62.1844 | 61.25% | 0 | 6 | 27.35% | 0% | 0 | 0.031506 | 26.5534 | 1.3793 | 1.1539 | Medium | Medium | Low | 865 | 746 | 0.8366 | 230.7749 | 2.585%
PEORIA 170413494 | PEORIA 1704 | YOSEMITE | 3.2575 | 18.8459 | 98.09% | 0 | 1 | 43.79% | 0% | 0 | 0.017531 | 47.6367 | 3.0588 | 2.5544 | Low | Low | Medium | 719 | 747 | 0.8351 | 229.9383 | 2.576%
ATASCADERO 1103A18 | ATASCADERO 1103 | LOS PADRES | 8.0258 | 28.4878 | 70.03% | 3 | 2 | 44.28% | 0% | 0 | 0.023538 | 35.3263 | 1.9037 | 1.583 | Medium | Medium | Low | 806 | 748 | 0.8315 | 229.1032 | 2.567%
WOODSIDE 11012299 | WOODSIDE 1101 | PENINSULA | 1.6209 | 33.6689 | 6.985% | 2 | 3 | 88.38% | 100% | 0 | 0.073666 | 11.2183 | 3.6727 | 3.0352 | High | High | High | 681 | 749 | 0.82641 | 228.2717 | 2.557%
BELLEVUE 2103552 | BELLEVUE 2103 | SONOMA | 9.102 | 59.5579 | 60.22% | 2 | 0 | 60.99% | 9.086% | 0 | 0.023335 | 35.3263 | 3.2018 | 2.6393 | Medium | Medium | High | 711 | 750 | 0.82433 | 227.4452 | 2.548%
BIG BEND 11011704 | BIG BEND 1101 | NORTH VALLEY | 2.999 | 64.818 | 100% | 0 | 0 | 100% | 0% | 0 | 0.040953 | 19.9979 | 1.7926 | 1.4681 | Medium | Medium | Low | 817 | 751 | 0.81898 | 226.6209 | 2.539%
PASO ROBLES 1103N02 | PASO ROBLES 1103 | LOS PADRES | 0.044146 | 10 | 36.23% | 0 | 0 | 100% | 0% | 0 | 0.017045 | 47.6367 | 3.1571 | 2.5634 | Low | Low | High | 718 | 752 | 0.81194 | 225.8019 | 2.53%
JESSUP 110296554 | JESSUP 1102 | NORTH VALLEY | 6.2214 | 43.1199 | 99.72% | 1 | 1 | 41.3% | 0% | 0 | 0.030545 | 26.5534 | 2.0694 | 1.6784 | Medium | Medium | Low | 794 | 753 | 0.81106 | 224.99 | 2.521%
PEABODY 2113CB | PEABODY 2113 | SACRAMENTO | 1.6686 | 58.5758 | 80.04% | 0 | 1 | 27.33% | 0% | 0 | 0.01682 | 47.6367 | 2.9585 | 2.3705 | Low | Low | Medium | 734 | 754 | 0.80125 | 224.1789 | 2.511%
GABILAN 11013090 | GABILAN 1101 | CENTRAL COAST | 1.8466 | 75 | 100% | 0 | 0 | 5.274% | 0% | 0 | 0.02262 | 35.3263 | 2.8398 | 2.2693 | Medium | Medium | Medium | 747 | 755 | 0.7991 | 223.3777 | 2.502%
OLETA 110163500 | OLETA 1101 | STOCKTON | 4.0006 | 22.1026 | 38.92% | 0 | 1 | 53.39% | 0% | 0 | 0.012178 | 65.3912 | 2.271 | 1.8085 | Low | Low | Medium | 779 | 756 | 0.79634 | 222.5786 | 2.494%
MOLINO 1101152 | MOLINO 1101 | SONOMA | 2.0022 | 35.0368 | 46.62% | 3 | 1 | 17.51% | 2.1% | 0 | 0.012176 | 65.3912 | 2.6304 | 2.0944 | Low | Low | Medium | 754 | 757 | 0.79623 | 221.7822 | 2.485%
PASO ROBLES 1107CB | PASO ROBLES 1107 | LOS PADRES | 0.069192 | 75 | 100% | 0 | 0 | 0.6192% | 0% | 0 | 0.016629 | 47.6367 | 1.2733 | 1.0086 | Low | Low | Low | 894 | 758 | 0.79217 | 220.986 | 2.476%
WOODACRE 110191900 | WOODACRE 1101 | NORTH BAY | 7.6804 | 74.1444 | 47.27% | 4 | 8 | 55.53% | 8.222% | 1 | 0.029825 | 26.5534 | 2.176 | 1.7233 | Medium | Medium | Low | 789 | 759 | 0.79194 | 220.1938 | 2.467%
CLEAR LAKE 110192870 | CLEAR LAKE 1101 | HUMBOLDT | 1.0943 | 58.4315 | 90.41% | 0 | 0 | 6.07% | 0% | 0 | 0.016559 | 47.6367 | 2.9112 | 2.2964 | Low | Low | Medium | 746 | 760 | 0.78881 | 219.4019 | 2.458%
SANTA YNEZ 1101Y14 | SANTA YNEZ 1101 | LOS PADRES | 4.5467 | 84.753 | 58.25% | 0 | 0 | 27.67% | 0% | 0 | 0.016519 | 47.6367 | 2.6036 | 2.0488 | Low | Low | Medium | 759 | 761 | 0.78692 | 218.6131 | 2.449%
GEYSERVILLE 1102CB | GEYSERVILLE 1102 | SONOMA | 2.3641 | 61.3374 | 59.74% | 1 | 1 | 32.38% | 57.77% | 0 | 0.03873 | 19.9979 | 1.5774 | 1.2218 | Medium | Medium | Low | 854 | 762 | 0.77452 | 217.8262 | 2.44%
HIGHLANDS 110280660 | HIGHLANDS 1102 | HUMBOLDT | 5.365 | 78.0742 | 39.2% | 1 | 2 | 71.03% | 0% | 0 | 0.021888 | 35.3263 | 3.1794 | 2.4584 | Medium | Medium | High | 724 | 763 | 0.77324 | 217.0516 | 2.432%
DUNBAR 11033135 | DUNBAR 1103 | SONOMA | 0.22216 | 10 | 100% | 0 | 0 | 29.43% | 100% | 0 | 0.068741 | 11.2183 | 4.1817 | 3.2247 | High | High | High | 661 | 764 | 0.77116 | 216.2784 | 2.423%
SAUSALITO 110284278 | SAUSALITO 1102 | NORTH BAY | 1.3711 | 32.8864 | 5.777% | 0 | 2 | 90.29% | 0% | 0 | 0.021793 | 35.3263 | 3.3996 | 2.6173 | Low | Low | High | 713 | 765 | 0.76987 | 215.5073 | 2.414%
EL CERRITO G 1112BR180 | EL CERRITO G 1112 | EAST BAY | 1.3621 | 12.166 | 3.332% | 1 | 0 | 71.61% | 74.96% | 0 | 0.038138 | 19.9979 | 5.1411 | 3.9211 | Medium | Medium | High | 627 | 766 | 0.76268 | 214.7374 | 2.406%
VACA DIXON 11059792 | VACA DIXON 1105 | SACRAMENTO | 2.2981 | 58.3899 | 100% | 0 | 0 | 7.932% | 0% | 0 | 0.015982 | 47.6367 | 2.4313 | 1.8511 | Low | Low | Medium | 775 | 767 | 0.76135 | 213.9747 | 2.397%
SAN JUSTO 11014339 | SAN JUSTO 1101 | CENTRAL COAST | 8.8141 | 41.5112 | 42.23% | 1 | 1 | 80.23% | 0% | 0 | 0.021456 | 35.3263 | 2.1555 | 1.6338 | Low | Low | Low | 801 | 768 | 0.75797 | 213.2134 | 2.389%
OAKHURST 1102CB | OAKHURST 1102 | YOSEMITE | 2.1514 | 10 | 95.52% | 0 | 10 | 44.96% | 59.79% | 0 | 0.050548 | 14.9507 | 2.5632 | 1.9371 | Medium | Medium | Medium | 765 | 769 | 0.75573 | 212.4554 | 2.38%
JAMESON 11057652 | JAMESON 1105 | SACRAMENTO | 15.7797 | 54.8992 | 80.61% | 0 | 3 | 36.24% | 0% | 0 | 0.021376 | 35.3263 | 2.6329 | 1.9882 | Low | Low | Medium | 762 | 770 | 0.75514 | 211.6996 | 2.372%
FULTON 110410281 | FULTON 1104 | SONOMA | 0.51664 | 22.43 | 74.95% | 0 | 1 | 49.63% | 0% | 0 | 0.015765 | 47.6367 | 3.068 | 2.3041 | Low | Low | Medium | 745 | 771 | 0.75099 | 210.9445 | 2.363%
CAMP EVERS 210612760 | CAMP EVERS 2106 | CENTRAL COAST | 26.714 | 47.9231 | 63.13% | 29 | 6 | 100% | 100% | 0 | 0.75098 | 1 | 2.5548 | 1.9186 | High | High | Medium | 766 | 772 | 0.75098 | 210.1935 | 2.355%
MOLINO 1104380 | MOLINO 1104 | SONOMA | 2.046 | 71.2548 | 46.79% | 0 | 0 | 7.207% | 0% | 0 | 0.011223 | 65.3912 | 3.36 | 2.4657 | Low | Low | High | 722 | 773 | 0.73385 | 209.4425 | 2.346%
VASCO 110211338 | VASCO 1102 | MISSION | 3.3669 | 79.9716 | 100% | 0 | 1 | 17.52% | 0% | 0 | 0.020726 | 35.3263 | 2.7006 | 1.9773 | Low | Low | Medium | 763 | 774 | 0.73217 | 208.7087 | 2.338%
ROB ROY 21045082 | ROB ROY 2104 | CENTRAL COAST | 24.4071 | 49.5744 | 97.38% | 64 | 6 | 98.22% | 97.15% | 0 | 0.73013 | 1 | 3.1854 | 2.3258 | High | High | High | 741 | 775 | 0.73013 | 207.9765 | 2.33%
MENLO 11028896 | MENLO 1102 | PENINSULA | 0.53492 | 85.6249 | 0.9567% | 0 | 0 | 34.58% | 0% | 0 | 0.01116 | 65.3912 | 4.0778 | 2.9759 | Low | Low | High | 685 | 776 | 0.72979 | 207.2464 | 2.322%
MARIPOSA 21019400 | MARIPOSA 2101 | YOSEMITE | 62.7736 | 22.0188 | 81.32% | 9 | 129 | 100% | 40.79% | 1 | 0.72296 | 1 | 1.619 | 1.1705 | High | High | Low | 863 | 777 | 0.72296 | 206.5166 | 2.314%
COTTONWOOD 110335470 | COTTONWOOD 1103 | NORTH VALLEY | 18.2496 | 46.5174 | 67.33% | 0 | 6 | 73.33% | 0% | 0 | 0.03595 | 19.9979 | 1.7492 | 1.2576 | Medium | Medium | Low | 846 | 778 | 0.71893 | 205.7936 | 2.305%
BUELLTON 1102CB | BUELLTON 1102 | LOS PADRES | 4.428 | 55.4455 | 60.97% | 0 | 2 | 34.48% | 0% | 0 | 0.02009 | 35.3263 | 2.346 | 1.6649 | Low | Low | Medium | 796 | 779 | 0.7097 | 205.0747 | 2.297%
SALMON CREEK 1101196 | SALMON CREEK 1101 | SONOMA | 5.0547 | 72.9126 | 4.053% | 3 | 0 | 69.63% | 0% | 0 | 0.020086 | 35.3263 | 2.652 | 1.8817 | Low | Low | Medium | 771 | 780 | 0.70955 | 204.365 | 2.289%
STAFFORD 1102361952 | STAFFORD 1102 | NORTH BAY | 1.3655 | 84.7322 | 98.54% | 0 | 1 | 100% | 0% | 0 | 0.04705 | 14.9507 | 2.6948 | 1.8956 | Medium | Medium | Medium | 770 | 781 | 0.70344 | 203.6554 | 2.282%
PASO ROBLES 1103N58 | PASO ROBLES 1103 | LOS PADRES | 4.5123 | 48.6182 | 39.94% | 0 | 1 | 60.11% | 0% | 0 | 0.026481 | 26.5534 | 2.029 | 1.4267 | Medium | Medium | Low | 825 | 782 | 0.70315 | 202.952 | 2.274%
WISE 1102697216 | WISE 1102 | SIERRA | 13.1816 | 10.264 | 71.09% | 2 | 0 | 100% | 0% | 0 | 0.026461 | 26.5534 | 2.4483 | 1.7203 | Medium | Medium | Medium | 790 | 783 | 0.70264 | 202.2488 | 2.266%
PUEBLO 2103678 | PUEBLO 2103 | NORTH BAY | 25.5805 | 63.7412 | 53.4% | 28 | 21 | 98.22% | 87.3% | 1 | 0.69166 | 1 | 2.9613 | 2.0482 | High | High | Medium | 760 | 784 | 0.69166 | 201.5462 | 2.258%
PUTAH CREEK 110546162 | PUTAH CREEK 1105 | SACRAMENTO | 0.70535 | 84.6256 | 100% | 0 | 0 | 10.52% | 0% | 0 | 0.019556 | 35.3263 | 2.1866 | 1.5106 | Low | Low | Low | 812 | 785 | 0.69085 | 200.8546 | 2.25%
CAMP EVERS 210510996 | CAMP EVERS 2105 | CENTRAL COAST | 0.7626 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 4.4922 | 3.1023 | High | High | High | 674 | 786 | 0.69059 | 200.1637 | 2.242%
EL CERRITO G 1105R6998 | EL CERRITO G 1105 | EAST BAY | 0.025405 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 4.1798 | 2.8865 | High | High | High | 691 | 786 | 0.69059 | 199.4731 | 2.235%
VINEYARD 21086952 | VINEYARD 2108 | MISSION | 0.0028424 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 3.2583 | 2.2502 | High | High | High | 750 | 786 | 0.69059 | 198.7825 | 2.227%
BIG BASIN 11015479 | BIG BASIN 1101 | CENTRAL COAST | 0.17042 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 3.0984 | 2.1397 | High | High | High | 752 | 786 | 0.69059 | 198.0919 | 2.219%
HALSEY 1101 | HALSEY 1101 | SIERRA | 0.058617 | 10 | 52.88% | 0 | 0 | 100% | 0% | 0 | 0.019506 | 35.3263 | 2.1628 | 1.4903 | Low | Low | Low | 815 | 790 | 0.68906 | 197.4013 | 2.211%
TEMPLETON 2113A60 | TEMPLETON 2113 | LOS PADRES | 7.4093 | 57.7033 | 62.45% | 1 | 2 | 82.52% | 0.05121% | 0 | 0.025802 | 26.5534 | 2.47 | 1.6923 | Medium | Medium | Medium | 792 | 791 | 0.68512 | 196.7123 | 2.204%
CORTINA 1101302192 | CORTINA 1101 | SACRAMENTO | 1.036 | 90 | 100% | 0 | 0 | 5.795% | 0% | 0 | 0.019354 | 35.3263 | 1.0872 | 0.74333 | Low | Low | Low | 961 | 792 | 0.6837 | 196.0271 | 2.196%
COTATI 1102681 | COTATI 1102 | SONOMA | 3.8076 | 32.2436 | 43.14% | 1 | 3 | 100% | 0% | 0 | 0.025685 | 26.5534 | 2.6252 | 1.7904 | Medium | Medium | Medium | 782 | 793 | 0.68203 | 195.3434 | 2.188%
WILDWOOD 1101CB | WILDWOOD 1101 | NORTH VALLEY | 0.055929 | 81.1882 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045585 | 14.9507 | 1.052 | 0.71699 | Medium | Medium | Low | 972 | 794 | 0.68153 | 194.6614 | 2.181%
GEYSERVILLE 1101482 | GEYSERVILLE 1101 | SONOMA | 0.45328 | 77.9574 | 100% | 0 | 0 | 13.09% | 0% | 0 | 0.019179 | 35.3263 | 1.094 | 0.74117 | Low | Low | Low | 962 | 795 | 0.67751 | 193.9799 | 2.173%
STAFFORD 1102784704 | STAFFORD 1102 | NORTH BAY | 0.02728 | 80 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045233 | 14.9507 | 2.6732 | 1.8078 | Medium | Medium | Medium | 780 | 796 | 0.67626 | 193.3024 | 2.166%
WHEATLAND 110591170 | WHEATLAND 1105 | SIERRA | 9.9882 | 49.4424 | 100% | 0 | 0 | 18.55% | 0% | 0 | 0.019051 | 35.3263 | 1.7362 | 1.1684 | Low | Low | Low | 864 | 797 | 0.67299 | 192.6261 | 2.158%
SILVERADO 210437632 | SILVERADO 2104 | NORTH BAY | 22.9342 | 51.0024 | 44.2% | 16 | 15 | 100% | 100% | 0 | 0.67223 | 1 | 3.7875 | 2.5461 | High | High | High | 720 | 798 | 0.67223 | 191.9531 | 2.15%
SAN RAFAEL 11071415 | SAN RAFAEL 1107 | NORTH BAY | 0.70882 | 10 | 28.8% | 0 | 0 | 59.59% | 100% | 0 | 0.059639 | 11.2183 | 4.0649 | 2.7196 | Medium | Medium | High | 706 | 799 | 0.66905 | 191.2809 | 2.143%
ATASCADERO 1101A02 | ATASCADERO 1101 | LOS PADRES | 11.1355 | 10.7743 | 66.74% | 2 | 2 | 100% | 7.928% | 0 | 0.044541 | 14.9507 | 3.626 | 2.4147 | Medium | Medium | High | 730 | 800 | 0.66592 | 190.6118 | 2.135%
JESSUP 110141356 | JESSUP 1101 | NORTH VALLEY | 32.7394 | 40.1195 | 100% | 1 | 5 | 100% | 0% | 0 | 0.044331 | 14.9507 | 1.5857 | 1.051 | Medium | Medium | Low | 884 | 801 | 0.66278 | 189.9459 | 2.128%
SONOMA 1104414 | SONOMA 1104 | SONOMA | 0.58433 | 88.0945 | 100% | 0 | 0 | 3.279% | 0% | 0 | 0.018641 | 35.3263 | 2.89 | 1.9031 | Low | Low | Medium | 767 | 802 | 0.65851 | 189.2831 | 2.121%
SONOMA 110310257 | SONOMA 1103 | SONOMA | 0.24108 | 10 | 100% | 0 | 0 | 12.38% | 100% | 0 | 0.058573 | 11.2183 | 3.6175 | 2.3771 | Medium | Medium | High | 733 | 803 | 0.65709 | 188.6246 | 2.113%
FRUITLAND 11418746 | FRUITLAND 1141 | HUMBOLDT | 0.40721 | 85 | 7.434% | 0 | 0 | 50.57% | 0% | 0 | 0.013725 | 47.6367 | 0.84229 | 0.55071 | Low | Low | Low | 1058 | 804 | 0.65382 | 187.9675 | 2.106%
PENRYN 110551676 | PENRYN 1105 | SIERRA | 8.707 | 10 | 49.11% | 4 | 2 | 74.33% | 0% | 0 | 0.018392 | 35.3263 | 2.3475 | 1.5252 | Low | Low | Medium | 811 | 805 | 0.64971 | 187.3137 | 2.098%
MILPITAS 1108XR122 | MILPITAS 1108 | SAN JOSE | 0.28331 | 75 | 0% | 0 | 0 | 3.797% | 0% | 0 | 0.0075908 | 85.4511 | 3.7218 | 2.4142 | Low | Low | High | 731 | 806 | 0.64865 | 186.664 | 2.091%
COARSEGOLD 210410335 | COARSEGOLD 2104 | YOSEMITE | 5.8238 | 24.9128 | 98.65% | 0 | 10 | 100% | 0% | 0 | 0.043347 | 14.9507 | 2.3565 | 1.5272 | Medium | Medium | Medium | 810 | 807 | 0.64806 | 186.0154 | 2.084%
DEL MONTE 21049500 | DEL MONTE 2104 | CENTRAL COAST | 6.5395 | 26.3217 | 40.33% | 0 | 7 | 96.32% | 0% | 0 | 0.03234 | 19.9979 | 2.4996 | 1.6166 | Medium | Medium | Medium | 805 | 808 | 0.64673 | 185.3673 | 2.077%
FREMONT 1104MR339 | FREMONT 1104 | MISSION | 1.2378 | 84.498 | 6.265% | 0 | 0 | 17.79% | 0% | 0 | 0.0097922 | 65.3912 | 1.5544 | 0.99533 | Low | Low | Low | 897 | 809 | 0.64033 | 184.7206 | 2.069%
LAKEWOOD 2110W577R | LAKEWOOD 2110 | DIABLO | 0.42837 | 10 | 37.2% | 0 | 0 | 46.99% | 100% | 0 | 0.056527 | 11.2183 | 3.8435 | 2.4373 | Medium | Medium | High | 727 | 810 | 0.63414 | 184.0802 | 2.062%
PETALUMA C 1109373772 | PETALUMA C 1109 | SONOMA | 0.017822 | 70 | 100% | 0 | 0 | 100% | 0% | 0 | 0.042368 | 14.9507 | 2.9557 | 1.8723 | Medium | Medium | Medium | 773 | 811 | 0.63344 | 183.4461 | 2.055%
OLEMA 11011686 | OLEMA 1101 | NORTH BAY | 0.41347 | 93.229 | 0% | 4 | 1 | 8.166% | 0% | 0 | 0.0096532 | 65.3912 | 2.2884 | 1.4445 | Low | Low | Medium | 821 | 812 | 0.63124 | 182.8127 | 2.048%
HIGGINS 11032194 | HIGGINS 1103 | SIERRA | 1.6953 | 10 | 78.66% | 3 | 1 | 63.02% | 0% | 0 | 0.017732 | 35.3263 | 3.0035 | 1.8815 | Low | Low | Medium | 772 | 813 | 0.62642 | 182.1814 | 2.041%
RED BLUFF 11011334 | RED BLUFF 1101 | NORTH VALLEY | 1.7587 | 68.6115 | 100% | 0 | 0 | 11.05% | 0% | 0 | 0.017653 | 35.3263 | 1.9337 | 1.2059 | Low | Low | Low | 857 | 814 | 0.62362 | 181.555 | 2.034%
COTATI 110387402 | COTATI 1103 | SONOMA | 11.4171 | 74.8765 | 25.02% | 0 | 0 | 100% | 0% | 0 | 0.031179 | 19.9979 | 1.9793 | 1.2341 | Medium | Medium | Low | 852 | 815 | 0.62351 | 180.9314 | 2.027%
MARTELL 11016074 | MARTELL 1101 | STOCKTON | 3.6867 | 10 | 89.99% | 1 | 1 | 100% | 0% | 0 | 0.030968 | 19.9979 | 2.6262 | 1.6264 | Medium | Medium | Medium | 802 | 816 | 0.6193 | 180.3079 | 2.02%
SONOMA 1107294 | SONOMA 1107 | SONOMA | 0.1154 | 80 | 100% | 0 | 0 | 1.248% | 0% | 0 | 0.017305 | 35.3263 | 2.3851 | 1.458 | Low | Low | Medium | 819 | 817 | 0.61132 | 179.6886 | 2.013%
PEORIA 170575274 | PEORIA 1705 | YOSEMITE | 0.58699 | 10 | 100% | 0 | 0 | 18.06% | 0% | 0 | 0.012746 | 47.6367 | 3.4448 | 2.0915 | Low | Low | High | 755 | 818 | 0.60716 | 179.0773 | 2.006%
LAURELES 11116617 | LAURELES 1111 | CENTRAL COAST | 1.819 | 41.7117 | 100% | 1 | 0 | 100% | 0% | 0 | 0.040513 | 14.9507 | 1.7012 | 1.0304 | Medium | Medium | Low | 888 | 819 | 0.6057 | 178.4701 | 1.999%
CRESCENT MILLS 21012230 | CRESCENT MILLS 2101 | NORTH VALLEY | 1.0766 | 89.5687 | 97.05% | 0 | 1 | 9.699% | 0% | 0 | 0.022777 | 26.5534 | 1.8892 | 1.1426 | Medium | Medium | Low | 869 | 820 | 0.60481 | 177.8644 | 1.993%
VALLEY VIEW 1103P160 | VALLEY VIEW 1103 | EAST BAY | 0.28761 | 80 | 0% | 0 | 0 | 7.876% | 100% | 0 | 0.040365 | 14.9507 | 4.5675 | 2.7565 | Medium | Medium | High | 702 | 821 | 0.60349 | 177.2596 | 1.986%
PEORIA 1705CB | PEORIA 1705 | YOSEMITE | 7.2378 | 70.7531 | 12.14% | 0 | 3 | 100% | 0% | 0 | 0.022424 | 26.5534 | 2.0773 | 1.2369 | Medium | Medium | Low | 850 | 822 | 0.59543 | 176.6561 | 1.979%
STAFFORD 11011082 | STAFFORD 1101 | NORTH BAY | 2.5227 | 43.9762 | 98.79% | 0 | 0 | 81.83% | 0% | 0 | 0.029652 | 19.9979 | 2.7906 | 1.6547 | Medium | Medium | Medium | 799 | 823 | 0.59297 | 176.0607 | 1.972%
GREEN VALLEY 210111054 | GREEN VALLEY 2101 | CENTRAL COAST | 24.5092 | 42.4361 | 63.08% | 38 | 3 | 95.34% | 97.52% | 1 | 0.59075 | 1 | 3.087 | 1.8236 | High | High | High | 778 | 824 | 0.59075 | 175.4677 | 1.966%
JESSUP 11021314 | JESSUP 1102 | NORTH VALLEY | 5.6244 | 41.4572 | 97.17% | 0 | 1 | 39.97% | 0% | 0 | 0.022232 | 26.5534 | 2.005 | 1.1836 | Medium | Medium | Low | 861 | 825 | 0.59034 | 174.8769 | 1.959%
LAKEWOOD 2224W544R | LAKEWOOD 2224 | DIABLO | 0.041988 | 10 | 100% | 0 | 0 | 0.7884% | 100% | 0 | 0.052488 | 11.2183 | 3.9642 | 2.3342 | Medium | Medium | High | 740 | 826 | 0.58883 | 174.2866 | 1.953%
LAYTONVILLE 1101518 | LAYTONVILLE 1101 | HUMBOLDT | 1.7269 | 84.7584 | 100% | 0 | 1 | 7.655% | 0% | 0 | 0.02214 | 26.5534 | 0.53271 | 0.31317 | Medium | Medium | Low | 1215 | 827 | 0.58789 | 173.6978 | 1.946%
INDIAN FLAT 11044440 | INDIAN FLAT 1104 | YOSEMITE | 0.21912 | 58.2464 | 100% | 0 | 0 | 100% | 0% | 0 | 0.039224 | 14.9507 | 1.7987 | 1.0548 | Medium | Medium | Low | 883 | 828 | 0.58642 | 173.1099 | 1.939%
PETALUMA C 1109664732 | PETALUMA C 1109 | SONOMA | 0.8938 | 76.1937 | 84.67% | 0 | 0 | 100% | 0% | 0 | 0.039085 | 14.9507 | 2.9436 | 1.7201 | Medium | Medium | Medium | 791 | 829 | 0.58434 | 172.5235 | 1.933%
STAFFORD 11021943 | STAFFORD 1102 | NORTH BAY | 1.2184 | 10 | 29.26% | 2 | 0 | 100% | 0% | 0 | 0.016531 | 35.3263 | 3.1358 | 1.8312 | Low | Low | High | 777 | 830 | 0.58398 | 171.9391 | 1.926%
OREGON TRAIL 1102CB | OREGON TRAIL 1102 | NORTH VALLEY | 9.1345 | 24.6852 | 60.79% | 2 | 5 | 97.5% | 0% | 0 | 0.028979 | 19.9979 | 2.4938 | 1.4452 | Medium | Medium | Medium | 820 | 831 | 0.57952 | 171.3551 | 1.92%
HARTLEY 110158095 | HARTLEY 1101 | HUMBOLDT | 0.15659 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 19.9979 | 2.9173 | 1.6633 | Medium | Medium | Medium | 797 | 832 | 0.57017 | 170.7756 | 1.913%
MARIPOSA 2102 | MARIPOSA 2102 | YOSEMITE | 0.0020154 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 19.9979 | 2.0892 | 1.1912 | Medium | Medium | Low | 860 | 832 | 0.57017 | 170.2055 | 1.907%
MONTICELLO 11011780 | MONTICELLO 1101 | NORTH BAY | 0.07232 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 19.9979 | 1.5173 | 0.86511 | Medium | Medium | Low | 927 | 832 | 0.57017 | 169.6353 | 1.9%
FULTON 11024522 | FULTON 1102 | SONOMA | 7.7633 | 52.5177 | 82.8% | 0 | 6 | 63.13% | 6.863% | 0 | 0.037536 | 14.9507 | 2.8909 | 1.6223 | Medium | Medium | Medium | 804 | 835 | 0.56119 | 169.0651 | 1.894%
CLARKSVILLE 21096502 | CLARKSVILLE 2109 | SIERRA | 2.6781 | 10 | 70.1% | 1 | 1 | 48.48% | 45.39% | 0 | 0.03731 | 14.9507 | 3.0964 | 1.7272 | Medium | Medium | High | 788 | 836 | 0.55781 | 168.5039 | 1.888%
HORSESHOE 110450142 | HORSESHOE 1104 | SIERRA | 0.99943 | 10 | 98.77% | 0 | 1 | 24.44% | 0% | 0 | 0.015652 | 35.3263 | 3.9959 | 2.2095 | Low | Low | High | 751 | 837 | 0.55294 | 167.9461 | 1.881%
JARVIS 1101MR210 | JARVIS 1101 | MISSION | 0.45193 | 56.1032 | 64.09% | 0 | 0 | 5.821% | 0% | 0 | 0.011506 | 47.6367 | 3.5376 | 1.939 | Low | Low | High | 764 | 838 | 0.54812 | 167.3932 | 1.875%
SALMON CREEK 1101 | SALMON CREEK 1101 | SONOMA | 0.026066 | 45.8588 | 0% | 0 | 0 | 100% | 51.23% | 0 | 0.036485 | 14.9507 | 2.7335 | 1.4911 | Medium | Medium | Medium | 814 | 839 | 0.54548 | 166.845 | 1.869%
AUBERRY 110149122 | AUBERRY 1101 | FRESNO | 3.8865 | 26.9324 | 92.34% | 0 | 3 | 100% | 0% | 0 | 0.036287 | 14.9507 | 2.4472 | 1.3276 | Medium | Medium | Medium | 835 | 840 | 0.54251 | 166.2996 | 1.863%
SANTA YNEZ 1101CB | SANTA YNEZ 1101 | LOS PADRES | 0.10675 | 60 | 100% | 0 | 1 | 0.6877% | 0% | 0 | 0.015356 | 35.3263 | 3.2382 | 1.7567 | Low | Low | High | 784 | 841 | 0.54248 | 165.7571 | 1.857%
PENRYN 110351658 | PENRYN 1103 | SIERRA | 7.9841 | 27.4219 | 66.1% | 1 | 2 | 91.67% | 0% | 0 | 0.027021 | 19.9979 | 2.6417 | 1.4274 | Medium | Medium | Medium | 824 | 842 | 0.54036 | 165.2146 | 1.851%
RINCON 1102644 | RINCON 1102 | SONOMA | 0.010111 | 60 | 100% | 0 | 1 | 0.1009% | 0% | 0 | 0.015268 | 35.3263 | 3.2635 | 1.7602 | Low | Low | High | 783 | 843 | 0.53935 | 164.6742 | 1.845%
SHINGLE SPRINGS 21107742 | SHINGLE SPRINGS 2110 | SIERRA | 45.6192 | 28.4995 | 92.18% | 17 | 14 | 99.89% | 99.12% | 1 | 0.53387 | 1 | 2.6864 | 1.4342 | High | High | Medium | 822 | 844 | 0.53387 | 164.1349 | 1.839%
MONTICELLO 110152910 | MONTICELLO 1101 | NORTH BAY | 2.1786 | 24.2187 | 98.28% | 0 | 1 | 69.32% | 0% | 0 | 0.026641 | 19.9979 | 1.5181 | 0.80879 | Medium | Medium | Low | 940 | 845 | 0.53277 | 163.601 | 1.833%
WILLITS 110391948 | WILLITS 1103 | HUMBOLDT | 6.1069 | 55.6867 | 72.29% | 1 | 4 | 82.53% | 5.563% | 0 | 0.035629 | 14.9507 | 1.8551 | 0.98814 | Medium | Medium | Low | 899 | 846 | 0.53267 | 163.0682 | 1.827%
DESCHUTES 11043719 | DESCHUTES 1104 | NORTH VALLEY | 11.6781 | 40.3272 | 100% | 0 | 2 | 67.24% | 0% | 0 | 0.026406 | 19.9979 | 2.604 | 1.3751 | Medium | Medium | Medium | 830 | 847 | 0.52806 | 162.5356 | 1.821%
HIGGINS 110432747 | HIGGINS 1104 | SIERRA | 1.0824 | 10 | 100% | 1 | 0 | 61.76% | 0% | 0 | 0.019868 | 26.5534 | 3.124 | 1.6482 | Low | Low | High | 800 | 848 | 0.52758 | 162.0075 | 1.815%
RESEARCH 210263274 | RESEARCH 2102 | DIABLO | 0.57886 | 29.7225 | 25.19% | 0 | 1 | 5.113% | 100% | 0 | 0.035184 | 14.9507 | 3.1898 | 1.6779 | Medium | Medium | High | 795 | 849 | 0.52603 | 161.4799 | 1.809%
OAKHURST 110310140 | OAKHURST 1103 | YOSEMITE | 16.859 | 26.9049 | 99.84% | 3 | 44 | 100% | 99.31% | 0 | 0.52553 | 1 | 1.9527 | 1.0262 | High | High | Low | 889 | 850 | 0.52553 | 160.9539 | 1.803%
CLEAR LAKE 1102904 | CLEAR LAKE 1102 | HUMBOLDT | 3.3866 | 10 | 44.47% | 0 | 0 | 94.14% | 0% | 0 | 0.01961 | 26.5534 | 2.8334 | 1.4754 | Low | Low | Medium | 816 | 851 | 0.52071 | 160.4284 | 1.797%
HIGHLANDS 1102556 | HIGHLANDS 1102 | HUMBOLDT | 0.14444 | 10 | 100% | 0 | 0 | 1.909% | 0% | 0 | 0.010862 | 47.6367 | 3.2484 | 1.6809 | Low | Low | High | 793 | 852 | 0.51744 | 159.9076 | 1.791%
BRUNSWICK 11064639 | BRUNSWICK 1106 | SIERRA | 3.2486 | 31.5408 | 99.46% | 0 | 1 | 100% | 1.568% | 1 | 0.034254 | 14.9507 | 2.6487 | 1.3565 | Medium | Medium | Medium | 833 | 853 | 0.51212 | 159.3902 | 1.786%
WISE 11022234 | WISE 1102 | SIERRA | 15.1055 | 10 | 57.56% | 1 | 4 | 100% | 0% | 0 | 0.025382 | 19.9979 | 2.055 | 1.0431 | Medium | Medium | Low | 887 | 854 | 0.5076 | 158.8781 | 1.78%
WYANDOTTE 110641650 | WYANDOTTE 1106 | NORTH VALLEY | 1.9508 | 59.4004 | 100% | 0 | 0 | 12.07% | 0% | 0 | 0.01911 | 26.5534 | 2.2667 | 1.1502 | Low | Low | Medium | 866 | 855 | 0.50744 | 158.3705 | 1.774%
PACIFICA 11026783 | PACIFICA 1102 | PENINSULA | 1.5821 | 10 | 0% | 0 | 2 | 24.72% | 24.2% | 0 | 0.010579 | 47.6367 | 3.5634 | 1.7958 | Low | Low | High | 781 | 856 | 0.50395 | 157.8631 | 1.769%
LOS GATOS 1106LA64 | LOS GATOS 1106 | DE ANZA | 12.775 | 27.6673 | 77.8% | 17 | 7 | 100% | 100% | 1 | 0.50336 | 1 | 1.8673 | 0.93994 | High | High | Low | 908 | 857 | 0.50336 | 157.3591 | 1.763%
ATASCADERO 1103CB | ATASCADERO 1103 | LOS PADRES | 7.2499 | 46.2369 | 39.81% | 0 | 1 | 74.99% | 13.24% | 0 | 0.025143 | 19.9979 | 2.5685 | 1.2915 | Medium | Medium | Medium | 842 | 858 | 0.50281 | 156.8557 | 1.757%
PARADISE 11022024 | PARADISE 1102 | NORTH VALLEY | 0.64392 | 10 | 28.85% | 0 | 1 | 39.71% | 100% | 0 | 0.044388 | 11.2183 | 4.7148 | 2.3477 | Medium | Medium | High | 739 | 859 | 0.49795 | 156.3529 | 1.752%
PUTAH CREEK 110264044 | PUTAH CREEK 1102 | SACRAMENTO | 5.0213 | 75.9618 | 100% | 0 | 1 | 67.37% | 0% | 0 | 0.03282 | 14.9507 | 1.8721 | 0.91864 | Medium | Medium | Low | 913 | 860 | 0.49069 | 155.855 | 1.746%
PUEBLO 2102698 | PUEBLO 2102 | NORTH BAY | 0.45229 | 80 | 34.45% | 0 | 0 | 2.749% | 0% | 0 | 0.0103 | 47.6367 | 2.9171 | 1.4313 | Low | Low | Medium | 823 | 861 | 0.49067 | 155.3643 | 1.741%
BIG MEADOWS 2101439 | BIG MEADOWS 2101 | NORTH VALLEY | 0.034644 | 85 | 100% | 0 | 0 | 3.714% | 0% | 0 | 0.018336 | 26.5534 | 3.2474 | 1.5811 | Low | Low | High | 807 | 862 | 0.48688 | 154.8736 | 1.735%
BRUNSWICK 1104CB | BRUNSWICK 1104 | SIERRA | 1.9366 | 10 | 53.96% | 0 | 0 | 63.09% | 0% | 0 | 0.013676 | 35.3263 | 2.8083 | 1.3567 | Low | Low | Medium | 832 | 863 | 0.48311 | 154.3867 | 1.73%
CAMP EVERS 210311046 | CAMP EVERS 2103 | CENTRAL COAST | 16.2531 | 44.8404 | 64.25% | 23 | 4 | 100% | 100% | 0 | 0.47552 | 1 | 2.7899 | 1.3267 | High | High | Medium | 836 | 864 | 0.47552 | 153.9036 | 1.724%
GEYSERVILLE 1102274 | GEYSERVILLE 1102 | SONOMA | 4.0814 | 46.8618 | 69.12% | 1 | 0 | 22.13% | 0% | 0 | 0.013409 | 35.3263 | 2.6258 | 1.2438 | Low | Low | Medium | 848 | 865 | 0.47371 | 153.4281 | 1.719%
JAMESON 11028842 | JAMESON 1102 | SACRAMENTO | 0.46739 | 47.8727 | 32.07% | 0 | 0 | 8.162% | 0% | 0 | 0.0097873 | 47.6367 | 3.045 | 1.4197 | Low | Low | Medium | 826 | 866 | 0.46623 | 152.9544 | 1.714%
COLUMBIA HILL 1101CB | COLUMBIA HILL 1101 | SIERRA | 39.662 | 48.9114 | 99.72% | 21 | 18 | 100% | 77.89% | 0 | 0.46568 | 1 | 1.6227 | 0.75567 | High | High | Low | 956 | 867 | 0.46568 | 152.4882 | 1.708%
JAMESON 110265516 | JAMESON 1102 | SACRAMENTO | 7.9053 | 31.2245 | 60.83% | 1 | 6 | 69.63% | 0% | 0 | 0.023245 | 19.9979 | 2.861 | 1.3299 | Medium | Medium | Medium | 834 | 868 | 0.46484 | 152.0225 | 1.703%
MOLINO 1102344 | MOLINO 1102 | SONOMA | 1.1141 | 30.1016 | 80.53% | 0 | 2 | 18.52% | 0% | 0 | 0.013045 | 35.3263 | 2.8566 | 1.3164 | Low | Low | Medium | 839 | 869 | 0.46084 | 151.5576 | 1.698%
ANDERSON 11012051 | ANDERSON 1101 | NORTH VALLEY | 4.6467 | 13.4745 | 100% | 0 | 2 | 87.22% | 0% | 0 | 0.030553 | 14.9507 | 2.2964 | 1.0489 | Medium | Medium | Medium | 886 | 870 | 0.45678 | 151.0968 | 1.693%
WEST POINT 11024788 | WEST POINT 1102 | STOCKTON | 70.3316 | 50.1461 | 97.21% | 9 | 19 | 100% | 60.3% | 0 | 0.45673 | 1 | 2.3714 | 1.0831 | High | High | Medium | 879 | 871 | 0.45673 | 150.64 | 1.688%
ATASCADERO 1101 | ATASCADERO 1101 | LOS PADRES | 0.011512 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 35.3263 | 2.9013 | 1.3012 | Low | Low | Medium | 840 | 872 | 0.44848 | 150.1833 | 1.682%
BIG BASIN 110212992 | BIG BASIN 1102 | CENTRAL COAST | 14.2865 | 29.6471 | 74.67% | 30 | 1 | 100% | 100% | 1 | 0.44527 | 1 | 2.5494 | 1.1352 | High | High | Medium | 870 | 873 | 0.44527 | 149.7348 | 1.677%
SAN JOAQUIN #2 1103CB | SAN JOAQUIN #2 1103 | YOSEMITE | 67.7251 | 13.3684 | 94.77% | 0 | 65 | 100% | 13.79% | 0 | 0.44439 | 1 | 1.4392 | 0.63957 | High | High | Low | 1009 | 874 | 0.44439 | 149.2895 | 1.672%
DRUM 11011602 | DRUM 1101 | SIERRA | 16.7313 | 80.5912 | 98.54% | 5 | 3 | 100% | 100% | 0 | 0.44264 | 1 | 0.6215 | 0.2751 | High | High | Low | 1273 | 875 | 0.44264 | 148.8452 | 1.667%
LOS GATOS 1106LB44 | LOS GATOS 1106 | DE ANZA | 19.5005 | 14.2956 | 68.84% | 20 | 1 | 100% | 100% | 0 | 0.44075 | 1 | 2.9349 | 1.2936 | High | High | Medium | 841 | 876 | 0.44075 | 148.4025 | 1.663%
RED BLUFF 11051564 | RED BLUFF 1105 | NORTH VALLEY | 1.279 | 15.2296 | 100% | 0 | 0 | 12.04% | 0% | 0 | 0.012441 | 35.3263 | 1.4214 | 0.62469 | Low | Low | Low | 1020 | 877 | 0.43949 | 147.9618 | 1.658%
MERCED FALLS 110222772 | MERCED FALLS 1102 | YOSEMITE | 2.2922 | 12.637 | 100% | 0 | 0 | 100% | 0% | 0 | 0.029016 | 14.9507 | 0.18721 | 0.081211 | Medium | Medium | Low | 1923 | 878 | 0.4338 | 147.5223 | 1.653%
SONOMA 11045661 | SONOMA 1104 | SONOMA | 2.0903 | 69.2654 | 50.64% | 0 | 1 | 41.25% | 0% | 0 | 0.016332 | 26.5534 | 3.8269 | 1.6596 | Low | Low | High | 798 | 879 | 0.43366 | 147.0885 | 1.648%
GANSNER 110137550 | GANSNER 1101 | NORTH VALLEY | 0.5773 | 95.7309 | 100% | 0 | 0 | 12.36% | 0% | 0 | 0.021451 | 19.9979 | 2.9158 | 1.2508 | Low | Low | Medium | 847 | 880 | 0.42898 | 146.6548 | 1.643%
EEL RIVER 11024814 | EEL RIVER 1102 | HUMBOLDT | 27.3153 | 76.7361 | 63.94% | 7 | 10 | 97.55% | 0% | 0 | 0.42884 | 1 | 1.9361 | 0.83027 | High | High | Low | 936 | 881 | 0.42884 | 146.2258 | 1.638%
LAYTONVILLE 110264908 | LAYTONVILLE 1102 | HUMBOLDT | 3.5532 | 21.2702 | 61.98% | 6 | 8 | 55.85% | 0% | 0 | 0.021316 | 19.9979 | 1.9799 | 0.84396 | Low | Low | Low | 934 | 882 | 0.42627 | 145.797 | 1.633%
CURTIS 1702 | CURTIS 1702 | YOSEMITE | 0.020195 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 14.9507 | 3.8121 | 1.625 | Medium | Medium | High | 803 | 883 | 0.42627 | 145.3707 | 1.629%
INDIAN FLAT 1104 | INDIAN FLAT 1104 | YOSEMITE | 0.0039208 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 14.9507 | 1.8025 | 0.76836 | Medium | Medium | Low | 952 | 883 | 0.42627 | 144.9445 | 1.624%
PENRYN 11052406 | PENRYN 1105 | SIERRA | 3.0306 | 20.0804 | 58.87% | 1 | 0 | 24.58% | 0% | 0 | 0.012032 | 35.3263 | 2.2969 | 0.97632 | Low | Low | Medium | 901 | 885 | 0.42506 | 144.5182 | 1.619%
SAN JOAQUIN #3 110110010 | SAN JOAQUIN #3 1101 | YOSEMITE | 12.729 | 58.6534 | 88.53% | 3 | 19 | 100% | 90.16% | 0 | 0.42208 | 1 | 1.7707 | 0.74736 | High | High | Low | 958 | 886 | 0.42208 | 144.0931 | 1.614%
CORRAL 110275622 | CORRAL 1102 | STOCKTON | 0.45257 | 14.2481 | 100% | 0 | 0 | 7.908% | 0% | 0 | 0.011863 | 35.3263 | 2.9665 | 1.2432 | Low | Low | Medium | 849 | 887 | 0.41909 | 143.671 | 1.61%
ELECTRA 11011238 | ELECTRA 1101 | STOCKTON | 4.7136 | 30.1636 | 44.85% | 1 | 1 | 66.69% | 0% | 0 | 0.015593 | 26.5534 | 3.1098 | 1.2876 | Low | Low | High | 843 | 888 | 0.41404 | 143.252 | 1.605%
PEABODY 2108CB | PEABODY 2108 | SACRAMENTO | 0.80945 | 40.6035 | 58.6% | 0 | 0 | 21.91% | 0% | 0 | 0.01162 | 35.3263 | 2.9033 | 1.1917 | Low | Low | Medium | 859 | 889 | 0.41049 | 142.8379 | 1.6%
CLARKSVILLE 210551478 | CLARKSVILLE 2105 | SIERRA | 0.050363 | 10 | 0% | 0 | 0 | 89.86% | 0% | 0 | 0.011483 | 35.3263 | 3.0401 | 1.2332 | Low | Low | Medium | 853 | 890 | 0.40565 | 142.4274 | 1.596%
MARIPOSA 210237288 | MARIPOSA 2102 | YOSEMITE | 85.1145 | 35.7142 | 99.54% | 6 | 74 | 100% | 7.812% | 0 | 0.40262 | 1 | 1.5019 | 0.60469 | High | High | Low | 1034 | 891 | 0.40262 | 142.0218 | 1.591%
STAFFORD 1102CB | STAFFORD 1102 | NORTH BAY | 0.24035 | 10 | 0% | 0 | 0 | 45.06% | 0% | 0 | 0.0084029 | 47.6367 | 2.7618 | 1.1055 | Low | Low | Medium | 876 | 892 | 0.40029 | 141.6192 | 1.587%
NORTH DUBLIN 21039473 | NORTH DUBLIN 2103 | MISSION | 2.5582 | 55.4552 | 10.6% | 0 | 1 | 86.9% | 2.14% | 0 | 0.019896 | 19.9979 | 3.7737 | 1.5015 | Low | Low | High | 813 | 893 | 0.39788 | 141.2189 | 1.582%
SUNOL 1101MR196 | SUNOL 1101 | MISSION | 2.4505 | 75.1937 | 26.76% | 0 | 1 | 18.84% | 0% | 0 | 0.011214 | 35.3263 | 1.5737 | 0.6234 | Low | Low | Low | 1021 | 894 | 0.39615 | 140.821 | 1.578%
MIDDLETOWN 1102414 | MIDDLETOWN 1102 | HUMBOLDT | 5.0571 | 54.0321 | 100% | 0 | 3 | 42.26% | 0% | 0 | 0.026354 | 14.9507 | 3.0843 | 1.2153 | Medium | Medium | High | 855 | 895 | 0.39402 | 140.4248 | 1.573%
VACAVILLE 110941782 | VACAVILLE 1109 | SACRAMENTO | 0.50066 | 79.3838 | 12.32% | 0 | 0 | 29.37% | 0% | 0 | 0.011149 | 35.3263 | 3.1982 | 1.2596 | Low | Low | High | 845 | 896 | 0.39386 | 140.0308 | 1.569%
LOS GATOS 1106LB48 | LOS GATOS 1106 | DE ANZA | 14.9866 | 67.642 | 90.94% | 14 | 1 | 100% | 100% | 1 | 0.39219 | 1 | 2.0173 | 0.79115 | High | High | Low | 945 | 897 | 0.39219 | 139.637 | 1.564%
WOODSIDE 110147872 | WOODSIDE 1101 | PENINSULA | 4.1743 | 60.8207 | 75.33% | 12 | 4 | 100% | 100% | 0 | 0.39089 | 1 | 3.0893 | 1.2076 | High | High | High | 856 | 898 | 0.39089 | 139.2448 | 1.56%
CALISTOGA 1101734 | CALISTOGA 1101 | NORTH BAY | 11.7939 | 55.3179 | 62.25% | 13 | 12 | 73.13% | 81.49% | 0 | 0.39061 | 1 | 2.7018 | 1.0554 | High | High | Medium | 882 | 899 | 0.39061 | 138.8539 | 1.556%
CORRAL 110313474 | CORRAL 1103 | STOCKTON | 3.1745 | 31.5086 | 69.33% | 0 | 0 | 44.02% | 0% | 0 | 0.019295 | 19.9979 | 3.99 | 1.5396 | Low | Low | High | 809 | 900 | 0.38586 | 138.4633 | 1.551%
UPPER LAKE 1101452 | UPPER LAKE 1101 | HUMBOLDT | 1.5567 | 30.5905 | 77.99% | 1 | 7 | 7.943% | 0% | 0 | 0.019247 | 19.9979 | 1.7433 | 0.67099 | Low | Low | Low | 990 | 901 | 0.3849 | 138.0774 | 1.547%
PENRYN 110550550 | PENRYN 1105 | SIERRA | 3.146 | 23.6879 | 96.13% | 0 | 1 | 22.41% | 0% | 0 | 0.014437 | 26.5534 | 1.9281 | 0.73914 | Low | Low | Low | 964 | 902 | 0.38336 | 137.6925 | 1.543%
TAMARACK 1101CB | TAMARACK 1101 | SIERRA | 16.4477 | 32.6722 | 67.46% | 23 | 13 | 91.62% | 0% | 0 | 0.38292 | 1 | 0.95136 | 0.36429 | High | High | Low | 1169 | 903 | 0.38292 | 137.3092 | 1.538%
COTATI 1105328 | COTATI 1105 | SONOMA | 0.42542 | 48.6287 | 27.07% | 0 | 1 | 3.098% | 0% | 0 | 0.0080325 | 47.6367 | 2.617 | 1.0014 | Low | Low | Medium | 896 | 904 | 0.38264 | 136.9263 | 1.534%
SAN JOAQUIN #3 1103CB | SAN JOAQUIN #3 1103 | YOSEMITE | 28.2713 | 13.2744 | 82.63% | 4 | 63 | 100% | 35.67% | 0 | 0.37964 | 1 | 1.2383 | 0.47011 | High | High | Low | 1101 | 905 | 0.37964 | 136.5436 | 1.53%
ROB ROY 21055090 | ROB ROY 2105 | CENTRAL COAST | 21.1859 | 44.752 | 78.23% | 40 | 3 | 100% | 97.19% | 1 | 0.37924 | 1 | 3.3344 | 1.2646 | High | High | High | 844 | 906 | 0.37924 | 136.164 | 1.525%
MONTICELLO 1101666 | MONTICELLO 1101 | NORTH BAY | 10.1625 | 67.7354 | 65.91% | 1 | 1 | 73.12% | 0% | 0 | 0.025333 | 14.9507 | 2.2961 | 0.86964 | Medium | Medium | Medium | 924 | 907 | 0.37875 | 135.7847 | 1.521%
SHADY GLEN 110151696 | SHADY GLEN 1101 | SIERRA | 17.0578 | 38.8695 | 93.61% | 4 | 7 | 82.3% | 0% | 0 | 0.033526 | 11.2183 | 2.2918 | 0.86196 | Medium | Medium | Medium | 928 | 908 | 0.37611 | 135.406 | 1.517%
LOS GATOS 110660116 | LOS GATOS 1106 | DE ANZA | 12.3794 | 30.6322 | 46% | 28 | 5 | 100% | 100% | 0 | 0.37151 | 1 | 2.4062 | 0.89393 | High | High | Medium | 917 | 909 | 0.37151 | 135.0299 | 1.513%
COTATI 1104CB | COTATI 1104 | SONOMA | 2.3176 | 10.9581 | 56.63% | 1 | 1 | 30.19% | 0% | 0 | 0.010506 | 35.3263 | 3.2386 | 1.2019 | Low | Low | High | 858 | 910 | 0.37113 | 134.6584 | 1.509%
VIEJO 2202CB | VIEJO 2202 | CENTRAL COAST | 2.1755 | 10 | 21.89% | 2 | 2 | 100% | 0% | 0 | 0.018504 | 19.9979 | 3.5811 | 1.3252 | Low | Low | High | 837 | 911 | 0.37005 | 134.2872 | 1.504%
APPLE HILL 21029722 | APPLE HILL 2102 | SIERRA | 38.3357 | 63.3481 | 100% | 10 | 4 | 100% | 82.49% | 1 | 0.36946 | 1 | 1.4151 | 0.52281 | High | High | Low | 1077 | 912 | 0.36946 | 133.9172 | 1.5%
HOPLAND 110180620 | HOPLAND 1101 | HUMBOLDT | 0.61898 | 10 | 82.97% | 0 | 0 | 11.01% | 0% | 0 | 0.010345 | 35.3263 | 1.672 | 0.61103 | Low | Low | Low | 1031 | 913 | 0.36545 | 133.5477 | 1.496%
COARSEGOLD 210410110 | COARSEGOLD 2104 | YOSEMITE | 49.586 | 26.2952 | 95.51% | 5 | 92 | 100% | 6.102% | 1 | 0.36439 | 1 | 2.3299 | 0.84901 | High | High | Medium | 933 | 914 | 0.36439 | 133.1823 | 1.492%
PUEBLO 21021326 | PUEBLO 2102 | NORTH BAY | 0.81465 | 66.7263 | 75.65% | 0 | 0 | 6.742% | 0% | 0 | 0.013708 | 26.5534 | 2.9185 | 1.0623 | Low | Low | Medium | 881 | 915 | 0.364 | 132.8179 | 1.488%
BEN LOMOND 0401CB | BEN LOMOND 0401 | CENTRAL COAST | 7.8222 | 35.8204 | 30.8% | 32 | 5 | 100% | 100% | 0 | 0.3629 | 1 | 4.3533 | 1.5799 | High | High | High | 808 | 916 | 0.3629 | 132.4539 | 1.484%
SANTA ROSA A 1108626 | SANTA ROSA A 1108 | SONOMA | 0.13621 | 75 | 0% | 0 | 0 | 3.381% | 0% | 0 | 0.0075596 | 47.6367 | 3.4302 | 1.2353 | Low | Low | High | 851 | 917 | 0.36011 | 132.091 | 1.48%
FITCH MOUNTAIN 1113406 | FITCH MOUNTAIN 1113 | SONOMA | 1.4439 | 43.4794 | 97.1% | 1 | 1 | 15.43% | 0% | 0 | 0.01793 | 19.9979 | 2.6791 | 0.96064 | Low | Low | Medium | 906 | 918 | 0.35857 | 131.7309 | 1.476%
PENRYN 11072706 | PENRYN 1107 | SIERRA | 5.0792 | 12.8578 | 75.5% | 0 | 3 | 34.23% | 0% | 0 | 0.013291 | 26.5534 | 2.6628 | 0.93976 | Low | Low | Medium | 909 | 919 | 0.35292 | 131.3723 | 1.472%
BOLINAS 110146152 | BOLINAS 1101 | NORTH BAY | 0.43174 | 69.1568 | 0% | 0 | 0 | 4.254% | 0% | 0 | 0.0073288 | 47.6367 | 4.0187 | 1.403 | Low | Low | High | 827 | 920 | 0.34912 | 131.0194 | 1.468%
BRIDGEVILLE 110255612 | BRIDGEVILLE 1102 | HUMBOLDT | 22.2453 | 91.4485 | 100% | 11 | 10 | 100% | 97.29% | 1 | 0.34757 | 1 | 0.33885 | 0.11777 | High | High | Low | 1676 | 921 | 0.34757 | 130.6702 | 1.464%
DIAMOND SPRINGS 1105CB | DIAMOND SPRINGS 1105 | SIERRA | 1.4833 | 10 | 14.23% | 0 | 1 | 31.56% | 62.47% | 0 | 0.022985 | 14.9507 | 2.8916 | 0.99365 | Medium | Medium | Medium | 898 | 922 | 0.34364 | 130.3227 | 1.46%
WEST POINT 11021305 | WEST POINT 1102 | STOCKTON | 11.4284 | 52.5642 | 100% | 4 | 5 | 100% | 100% | 1 | 0.34333 | 1 | 2.218 | 0.76151 | High | High | Low | 955 | 923 | 0.34333 | 129.979 | 1.456%
SILVERADO 210234959 | SILVERADO 2102 | NORTH BAY | 24.7275 | 77.6516 | 100% | 5 | 11 | 91.78% | 69.47% | 1 | 0.34288 | 1 | 1.3442 | 0.46089 | High | High | Low | 1104 | 924 | 0.34288 | 129.6357 | 1.452%
MESA 11016113 | MESA 1101 | LOS PADRES | 1.5145 | 57.2852 | 100% | 0 | 0 | 15.55% | 0% | 0 | 0.017101 | 19.9979 | 2.5121 | 0.85911 | Low | Low | Medium | 930 | 925 | 0.34199 | 129.2928 | 1.448%
CAMP EVERS 210612518 | CAMP EVERS 2106 | CENTRAL COAST | 15.9361 | 56.9453 | 43.9% | 39 | 3 | 100% | 100% | 0 | 0.3407 | 1 | 2.3547 | 0.80224 | High | High | Medium | 941 | 926 | 0.3407 | 128.9508 | 1.445%
WEST POINT 11021341 | WEST POINT 1102 | STOCKTON | 10.0456 | 74.4483 | 100% | 1 | 5 | 100% | 100% | 0 | 0.33803 | 1 | 1.5377 | 0.51978 | High | High | Low | 1081 | 927 | 0.33803 | 128.6101 | 1.441%
MIRABEL 1101228 | MIRABEL 1101 | SONOMA | 2.2414 | 32.2817 | 68.07% | 3 | 1 | 22.76% | 0% | 0 | 0.012705 | 26.5534 | 3.0408 | 1.0258 | Low | Low | Medium | 890 | 928 | 0.33736 | 128.2721 | 1.437%
CLOVERDALE 1102672 | CLOVERDALE 1102 | SONOMA | 22.2941 | 69.8865 | 97.84% | 1 | 12 | 98.19% | 94.9% | 0 | 0.3373 | 1 | 1.9575 | 0.66027 | High | High | Low | 997 | 929 | 0.3373 | 127.9347 | 1.433%
WOODWARD 2108688294 | WOODWARD 2108 | FRESNO | 0.015135 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 26.5534 | 1.6587 | 0.55916 | Low | Low | Low | 1051 | 930 | 0.3371 | 127.5974 | 1.429%
SAN LUIS OBISPO 1108CB | SAN LUIS OBISPO 1108 | LOS PADRES | 0.74619 | 53.8272 | 22.96% | 0 | 1 | 8.668% | 0% | 0 | 0.012642 | 26.5534 | 3.3193 | 1.1142 | Low | Low | High | 875 | 931 | 0.33568 | 127.2603 | 1.426%
OAKHURST 11035480 | OAKHURST 1103 | YOSEMITE | 17.1484 | 38.4474 | 78.11% | 4 | 31 | 100% | 97.69% | 0 | 0.33517 | 1 | 1.8045 | 0.6048 | High | High | Low | 1033 | 932 | 0.33517 | 126.9247 | 1.422%
WILLOW CREEK 11014904 | WILLOW CREEK 1101 | HUMBOLDT | 18.7302 | 84.4323 | 100% | 25 | 5 | 100% | 99.66% | 0 | 0.33351 | 1 | 1.3113 | 0.43732 | High | High | Low | 1122 | 933 | 0.33351 | 126.5895 | 1.418%
DUNBAR 1103CB | DUNBAR 1103 | SONOMA | 1.9287 | 52.9434 | 74.35% | 2 | 2 | 15.81% | 20.29% | 0 | 0.029588 | 11.2183 | 3.0334 | 1.0069 | Medium | Medium | Medium | 895 | 934 | 0.33193 | 126.256 | 1.414%
OILFIELDS 1103N40 | OILFIELDS 1103 | CENTRAL COAST | 0.75328 | 20.1382 | 3.227% | 0 | 2 | 100% | 0% | 0 | 0.01659 | 19.9979 | 2.785 | 0.92399 | Low | Low | Medium | 912 | 935 | 0.33177 | 125.9241 | 1.411%
CLAYTON 22159765 | CLAYTON 2215 | DIABLO | 0.13991 | 10 | 100% | 0 | 0 | 14.93% | 0% | 0 | 0.012358 | 26.5534 | 3.3958 | 1.1143 | Low | Low | High | 874 | 936 | 0.32814 | 125.5923 | 1.407%
CAMP EVERS 210312990 | CAMP EVERS 2103 | CENTRAL COAST | 13.5574 | 33.1797 | 62.33% | 16 | 15 | 100% | 100% | 0 | 0.32668 | 1 | 2.6325 | 0.85998 | High | High | Medium | 929 | 937 | 0.32668 | 125.2641 | 1.403%
OAKHURST 1103CB | OAKHURST 1103 | YOSEMITE | 29.7308 | 28.0867 | 78.34% | 5 | 58 | 96.61% | 65.89% | 1 | 0.32601 | 1 | 2.3864 | 0.77799 | High | High | Medium | 949 | 938 | 0.32601 | 124.9375 | 1.4%
PLACERVILLE 210611132 | PLACERVILLE 2106 | SIERRA | 43.1899 | 37.6905 | 78.66% | 11 | 29 | 100% | 66.95% | 0 | 0.3241 | 1 | 1.6694 | 0.54105 | High | High | Low | 1067 | 939 | 0.3241 | 124.6115 | 1.396%
BIG BASIN 110169550 | BIG BASIN 1101 | CENTRAL COAST | 17.8925 | 32.0488 | 71.29% | 38 | 3 | 100% | 100% | 0 | 0.32055 | 1 | 2.7588 | 0.88433 | High | High | Medium | 919 | 940 | 0.32055 | 124.2874 | 1.392%
OTTER 11017611 | OTTER 1101 | CENTRAL COAST | 4.3976 | 73.491 | 75.26% | 4 | 3 | 100% | 100% | 1 | 0.3205 | 1 | 1.5238 | 0.48836 | High | High | Low | 1092 | 941 | 0.3205 | 123.9668 | 1.389%
GOLDTREE 1105551904 | GOLDTREE 1105 | LOS PADRES | 0.022237 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 2.7356 | 0.87498 | Medium | Medium | Medium | 920 | 942 | 0.31985 | 123.6463 | 1.385%
NARROWS 2105 | NARROWS 2105 | SIERRA | 0.056021 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 2.6731 | 0.85501 | Medium | Medium | Medium | 931 | 942 | 0.31985 | 123.3265 | 1.382%
ELECTRA 1101 | ELECTRA 1101 | STOCKTON | 0.02594 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 2.4984 | 0.79913 | Medium | Medium | Medium | 942 | 942 | 0.31985 | 123.0066 | 1.378%
MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 2101 | SIERRA | 0.00097812 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 2.2083 | 0.70631 | Medium | Medium | Low | 977 | 942 | 0.31985 | 122.6867 | 1.374%
WISE 1102 | WISE 1102 | SIERRA | 0.065469 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 1.9642 | 0.62826 | Medium | Medium | Low | 1015 | 942 | 0.31985 | 122.3669 | 1.371%
FOOTHILL 1101549904 | FOOTHILL 1101 | LOS PADRES | 7.1079 | 49.5665 | 45.77% | 1 | 3 | 40.61% | 0% | 0 | 0.021381 | 14.9507 | 3.5842 | 1.1457 | Low | Low | High | 867 | 947 | 0.31966 | 122.047 | 1.367%
LLAGAS 2101XR264 | LLAGAS 2101 | SAN JOSE | 0.73019 | 64.4385 | 100% | 0 | 0 | 3.559% | 0% | 0 | 0.015944 | 19.9979 | 2.4255 | 0.77337 | Low | Low | Medium | 951 | 948 | 0.31885 | 121.7274 | 1.364%
ROSSMOOR 1106L522R | ROSSMOOR 1106 | DIABLO | 1.0378 | 10 | 19.41% | 3 | 11 | 24.6% | 0% | 0 | 0.011991 | 26.5534 | 3.6777 | 1.171 | Low | Low | High | 862 | 949 | 0.31841 | 121.4085 | 1.36%
COARSEGOLD 210210040 | COARSEGOLD 2102 | YOSEMITE | 17.3327 | 15.2245 | 73.22% | 8 | 45 | 100% | 100% | 0 | 0.31716 | 1 | 2.0156 | 0.63929 | High | High | Low | 1010 | 950 | 0.31716 | 121.0901 | 1.357%
HARTLEY 1102524 | HARTLEY 1102 | HUMBOLDT | 1.3594 | 63.3777 | 100% | 0 | 1 | 30.18% | 0% | 0 | 0.020999 | 14.9507 | 2.2759 | 0.71449 | Low | Low | Medium | 973 | 951 | 0.31394 | 120.773 | 1.353%
FROGTOWN 170113412 | FROGTOWN 1701 | STOCKTON | 38.8157 | 21.4669 | 89.5% | 2 | 31 | 100% | 20.91% | 0 | 0.31378 | 1 | 2.7876 | 0.8747 | High | High | Medium | 921 | 952 | 0.31378 | 120.459 | 1.349%
RED BLUFF 110176020 | RED BLUFF 1101 | NORTH VALLEY | 8.959 | 16.3023 | 99.96% | 0 | 1 | 62.16% | 0% | 0 | 0.020958 | 14.9507 | 1.44 | 0.45121 | Low | Low | Low | 1109 | 953 | 0.31334 | 120.1452 | 1.346%
SAN MIGUEL 1105CB | SAN MIGUEL 1105 | LOS PADRES | 0.96596 | 53.2217 | 100% | 0 | 0 | 9.014% | 0% | 0 | 0.015601 | 19.9979 | 1.882 | 0.58717 | Low | Low | Low | 1040 | 954 | 0.312 | 119.8319 | 1.342%
SHINGLE SPRINGS 2109CB | SHINGLE SPRINGS 2109 | SIERRA | 27.1022 | 21.2732 | 81.89% | 8 | 12 | 97.37% | 94.72% | 0 | 0.31197 | 1 | 3.0034 | 0.93698 | High | High | Medium | 910 | 955 | 0.31197 | 119.5199 | 1.339%
SAN RAFAEL 1108516 | SAN RAFAEL 1108 | NORTH BAY | 10.7797 | 42.2809 | 10.51% | 16 | 17 | 98.34% | 99.7% | 0 | 0.30979 | 1 | 4.4882 | 1.3904 | High | High | High | 829 | 956 | 0.30979 | 119.2079 | 1.335%
PENRYN 110790970 | PENRYN 1107 | SIERRA | 0.86048 | 10 | 69.3% | 0 | 0 | 20.31% | 0% | 0 | 0.011579 | 26.5534 | 2.9455 | 0.90563 | Low | Low | Medium | 915 | 957 | 0.30746 | 118.8981 | 1.332%
SAN RAFAEL 11071166 | SAN RAFAEL 1107 | NORTH BAY | 8.1619 | 27.5709 | 35.32% | 8 | 36 | 90.61% | 87.37% | 0 | 0.30659 | 1 | 4.7682 | 1.4619 | High | High | High | 818 | 958 | 0.30659 | 118.5907 | 1.329%
AUBERRY 1101R319 | AUBERRY 1101 | FRESNO | 21.0846 | 48.2226 | 98.48% | 8 | 8 | 100% | 93.05% | 1 | 0.30543 | 1 | 1.3298 | 0.40617 | High | High | Low | 1139 | 959 | 0.30543 | 118.2841 | 1.325%
STANISLAUS 17011812 | STANISLAUS 1701 | YOSEMITE | 19.5078 | 54.4191 | 60.13% | 9 | 15 | 100% | 99.79% | 0 | 0.30454 | 1 | 2.9903 | 0.91067 | High | High | Medium | 914 | 960 | 0.30454 | 117.9787 | 1.322%
DIAMOND SPRINGS 11052102 | DIAMOND SPRINGS 1105 | SIERRA | 37.6923 | 30.2782 | 83.99% | 5 | 15 | 95.84% | 86.14% | 1 | 0.30069 | 1 | 2.5037 | 0.75284 | High | High | Medium | 957 | 961 | 0.30069 | 117.6741 | 1.318%
TEMPLETON 2110901690 | TEMPLETON 2110 | LOS PADRES | 36.531 | 44.497 | 99.02% | 7 | 6 | 93.11% | 83.54% | 1 | 0.29843 | 1 | 2.0943 | 0.625 | High | High | Low | 1019 | 962 | 0.29843 | 117.3734 | 1.315%
MONTE RIO 1113346 | MONTE RIO 1113 | SONOMA | 10.1076 | 73.6223 | 44.96% | 12 | 4 | 100% | 100% | 0 | 0.29448 | 1 | 3.2807 | 0.9661 | High | High | High | 903 | 963 | 0.29448 | 117.075 | 1.312%
HALF MOON BAY 1103H82 | HALF MOON BAY 1103 | PENINSULA | 53.0127 | 52.0051 | 39.35% | 29 | 11 | 92.34% | 3.002% | 1 | 0.29233 | 1 | 2.6229 | 0.76674 | High | High | Medium | 953 | 964 | 0.29233 | 116.7805 | 1.308%
WOODSIDE 11043583 | WOODSIDE 1104 | PENINSULA | 2.721 | 71.077 | 98.47% | 8 | 4 | 97.67% | 92.99% | 0 | 0.28756 | 1 | 2.7171 | 0.78133 | High | High | Medium | 948 | 965 | 0.28756 | 116.4882 | 1.305%
NARROWS 21052216 | NARROWS 2105 | SIERRA | 56.6943 | 15.1323 | 85.75% | 7 | 36 | 98.06% | 0% | 0 | 0.28652 | 1 | 3.1152 | 0.89257 | High | High | High | 918 | 966 | 0.28652 | 116.2006 | 1.302%
MARIPOSA 2101439030 | MARIPOSA 2101 | YOSEMITE | 19.5499 | 36.6756 | 99.56% | 7 | 29 | 100% | 98.19% | 0 | 0.28602 | 1 | 1.1748 | 0.33603 | High | High | Low | 1193 | 967 | 0.28602 | 115.9141 | 1.299%
LAKEVILLE 1102280 | LAKEVILLE 1102 | SONOMA | 2.0715 | 72.9124 | 15.25% | 0 | 2 | 23.31% | 0% | 0 | 0.010728 | 26.5534 | 2.5448 | 0.72494 | Low | Low | Medium | 969 | 968 | 0.28487 | 115.6281 | 1.295%
SAN LUIS OBISPO 1104V46 | SAN LUIS OBISPO 1104 | LOS PADRES | 18.1965 | 66.1378 | 91.34% | 1 | 13 | 87.31% | 73.08% | 1 | 0.28268 | 1 | 2.0672 | 0.58435 | High | High | Low | 1041 | 969 | 0.28268 | 115.3432 | 1.292%
TEMPLETON 2111CB | TEMPLETON 2111 | LOS PADRES | 1.8275 | 10 | 27.26% | 0 | 0 | 16.54% | 0% | 0 | 0.0079104 | 35.3263 | 2.52 | 0.70419 | Low | Low | Medium | 978 | 970 | 0.27944 | 115.0605 | 1.289%
SPRING GAP 1702693441 | SPRING GAP 1702 | YOSEMITE | 4.1995 | 35.8935 | 98.37% | 5 | 2 | 100% | 100% | 0 | 0.27702 | 1 | 1.0588 | 0.2933 | High | High | Low | 1244 | 971 | 0.27702 | 114.7811 | 1.286%
CLARKSVILLE 210619642 | CLARKSVILLE 2106 | SIERRA | 0.81481 | 10 | 0% | 0 | 0 | 51.08% | 0% | 0 | 0.007814 | 35.3263 | 3.4847 | 0.96191 | Low | Low | High | 905 | 972 | 0.27604 | 114.5041 | 1.283%
CABRILLO 1103CB | CABRILLO 1103 | LOS PADRES | 0.14089 | 80 | 0% | 0 | 0 | 3.139% | 0% | 0 | 0.0078018 | 35.3263 | 3.2473 | 0.89498 | Low | Low | High | 916 | 973 | 0.27561 | 114.228 | 1.28%
WYANDOTTE 110932586 | WYANDOTTE 1109 | NORTH VALLEY | 1.4371 | 18.342 | 79.5% | 0 | 0 | 94.84% | 0% | 0 | 0.024309 | 11.2183 | 4.1406 | 1.1292 | Medium | Medium | High | 872 | 974 | 0.27271 | 113.9524 | 1.277%
LLAGAS 2107XR178 | LLAGAS 2107 | SAN JOSE | 0.65323 | 27.1294 | 68.86% | 0 | 0 | 9.688% | 0% | 0 | 0.010217 | 26.5534 | 3.4762 | 0.94309 | Low | Low | High | 907 | 975 | 0.2713 | 113.6797 | 1.274%
COTTONWOOD 11011510 | COTTONWOOD 1101 | NORTH VALLEY | 0.7279 | 10 | 33.06% | 0 | 0 | 21.95% | 0% | 0 | 0.0076675 | 35.3263 | 1.8603 | 0.5039 | Low | Low | Low | 1085 | 976 | 0.27086 | 113.4084 | 1.27%
JARVIS 1108MR576 | JARVIS 1108 | MISSION | 1.3706 | 10 | 32.22% | 0 | 0 | 22.29% | 0% | 0 | 0.0076408 | 35.3263 | 4.1701 | 1.1256 | Low | Low | High | 873 | 977 | 0.26992 | 113.1376 | 1.267%
CURTIS 17039180 | CURTIS 1703 | YOSEMITE | 56.1725 | 23.1853 | 91.13% | 4 | 41 | 100% | 0% | 0 | 0.26987 | 1 | 2.515 | 0.67872 | High | High | Medium | 986 | 978 | 0.26987 | 112.8676 | 1.264%
PENRYN 1103660 | PENRYN 1103 | SIERRA | 10.4724 | 10.4096 | 69.5% | 2 | 4 | 53.75% | 0% | 0 | 0.018041 | 14.9507 | 2.329 | 0.62817 | Low | Low | Medium | 1016 | 979 | 0.26972 | 112.5978 | 1.261%
COARSEGOLD 210410400 | COARSEGOLD 2104 | YOSEMITE | 42.0443 | 18.5406 | 94.25% | 4 | 95 | 94% | 0% | 0 | 0.26956 | 1 | 2.4779 | 0.66794 | High | High | Medium | 993 | 980 | 0.26956 | 112.328 | 1.258%
MIWUK 170153038 | MIWUK 1701 | YOSEMITE | 6.638 | 67.6188 | 100% | 3 | 9 | 100% | 100% | 0 | 0.26716 | 1 | 2.3412 | 0.62548 | High | High | Medium | 1018 | 981 | 0.26716 | 112.0585 | 1.255%
MIDDLETOWN 1102CB | MIDDLETOWN 1102 | HUMBOLDT | 4.3813 | 57.1831 | 32.04% | 0 | 1 | 66.6% | 5.967% | 1 | 0.023754 | 11.2183 | 2.6792 | 0.71397 | Medium | Medium | Medium | 974 | 982 | 0.26649 | 111.7913 | 1.252%
COTATI 1102260 | COTATI 1102 | SONOMA | 1.6248 | 13.946 | 2.286% | 0 | 1 | 27.41% | 0% | 0 | 0.0075335 | 35.3263 | 2.9441 | 0.78353 | Low | Low | Medium | 947 | 983 | 0.26613 | 111.5248 | 1.249%
ALTO 1124430 | ALTO 1124 | NORTH BAY | 7.2931 | 30.5125 | 12.77% | 14 | 16 | 100% | 100% | 0 | 0.26455 | 1 | 4.3274 | 1.1448 | High | High | High | 868 | 984 | 0.26455 | 111.2587 | 1.246%
FOOTHILL 1102V06 | FOOTHILL 1102 | LOS PADRES | 1.4055 | 48.154 | 31.22% | 0 | 1 | 21.48% | 0% | 0 | 0.0099416 | 26.5534 | 3.2868 | 0.86767 | Low | Low | High | 925 | 985 | 0.26398 | 110.9942 | 1.243%
DEL MONTE 21042760 | DEL MONTE 2104 | CENTRAL COAST | 2.7139 | 31.1425 | 17.74% | 0 | 3 | 100% | 0% | 0 | 0.023371 | 11.2183 | 2.4707 | 0.64778 | Medium | Medium | Medium | 1005 | 986 | 0.26219 | 110.7302 | 1.24%
KESWICK 11019712 | KESWICK 1101 | NORTH VALLEY | 18.8507 | 17.0815 | 97.11% | 2 | 13 | 100% | 100% | 0 | 0.26099 | 1 | 2.4969 | 0.65166 | High | High | Medium | 1001 | 987 | 0.26099 | 110.468 | 1.238%
CAMP EVERS 210510728 | CAMP EVERS 2105 | CENTRAL COAST | 10.465 | 15.413 | 38.24% | 13 | 4 | 100% | 100% | 0 | 0.2598 | 1 | 4.1867 | 1.0877 | High | High | High | 878 | 988 | 0.2598 | 110.207 | 1.235%
CALISTOGA 1101890 | CALISTOGA 1101 | NORTH BAY | 22.5646 | 51.954 | 60.75% | 7 | 3 | 89.13% | 61.5% | 0 | 0.25974 | 1 | 2.3028 | 0.59812 | High | High | Medium | 1036 | 989 | 0.25974 | 109.9472 | 1.232%
COARSEGOLD 210210050 | COARSEGOLD 2102 | YOSEMITE | 7.18 | 18.0295 | 97.64% | 2 | 12 | 100% | 100% | 0 | 0.25905 | 1 | 2.0066 | 0.51979 | High | High | Low | 1080 | 990 | 0.25905 | 109.6875 | 1.229%
MONTE RIO 11133970 | MONTE RIO 1113 | SONOMA | 7.3428 | 62.8724 | 47.81% | 13 | 10 | 100% | 100% | 0 | 0.25889 | 1 | 3.2812 | 0.84949 | High | High | High | 932 | 991 | 0.25889 | 109.4284 | 1.226%
PLACERVILLE 21069712 | PLACERVILLE 2106 | SIERRA | 24.7737 | 54.0303 | 80.14% | 10 | 4 | 100% | 89.29% | 1 | 0.25885 | 1 | 2.0967 | 0.54273 | High | High | Low | 1065 | 992 | 0.25885 | 109.1695 | 1.223%
SARATOGA 1107413816 | SARATOGA 1107 | DE ANZA | 11.1604 | 62.8545 | 90.16% | 13 | 7 | 100% | 89.94% | 0 | 0.25675 | 1 | 3.3738 | 0.86623 | High | High | High | 926 | 993 | 0.25675 | 108.9107 | 1.22%
CLARK ROAD 110290548 | CLARK ROAD 1102 | NORTH VALLEY | 18.3619 | 41.0434 | 98.73% | 0 | 11 | 100% | 100% | 0 | 0.25625 | 1 | 2.6272 | 0.67323 | High | High | Medium | 988 | 994 | 0.25625 | 108.6539 | 1.217%
OAKHURST 110377384 | OAKHURST 1103 | YOSEMITE | 4.7334 | 12.9583 | 82.83% | 5 | 23 | 100% | 100% | 0 | 0.25524 | 1 | 2.5373 | 0.64761 | High | High | Medium | 1006 | 995 | 0.25524 | 108.3977 | 1.214%
MIRABEL 110238514 | MIRABEL 1102 | SONOMA | 10.5875 | 61.5593 | 46.21% | 16 | 8 | 100% | 100% | 0 | 0.25422 | 1 | 2.9393 | 0.74724 | High | High | Medium | 959 | 996 | 0.25422 | 108.1424 | 1.212%
CAMP EVERS 21065302 | CAMP EVERS 2106 | CENTRAL COAST | 5.9826 | 48.1403 | 77.43% | 11 | 0 | 100% | 95.97% | 0 | 0.25415 | 1 | 4.0058 | 1.0181 | High | High | High | 891 | 997 | 0.25415 | 107.8882 | 1.209%
NARROWS 21021252 | NARROWS 2102 | SIERRA | 0.0028409 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 19.9979 | 2.6386 | 0.66989 | Low | Low | Medium | 991 | 998 | 0.25388 | 107.6341 | 1.206%
MARIPOSA 21021960 | MARIPOSA 2102 | YOSEMITE | 24.6612 | 47.7521 | 99.87% | 3 | 23 | 100% | 69.1% | 1 | 0.25188 | 1 | 1.666 | 0.41964 | High | High | Low | 1134 | 999 | 0.25188 | 107.3802 | 1.203%
PLACERVILLE 21066512 | PLACERVILLE 2106 | SIERRA | 20.9994 | 19.5513 | 83.24% | 2 | 9 | 100% | 100% | 0 | 0.25186 | 1 | 1.9426 | 0.48926 | High | High | Low | 1091 | 1000 | 0.25186 | 107.1283 | 1.2%
SAN JOAQUIN #3 11035100 | SAN JOAQUIN #3 1103 | YOSEMITE | 26.246 | 20.2846 | 88.04% | 8 | 29 | 100% | 82.8% | 0 | 0.25116 | 1 | 1.3193 | 0.33134 | High | High | Low | 1197 | 1001 | 0.25116 | 106.8764 | 1.197%
ARBUCKLE 110447282 | ARBUCKLE 1104 | SACRAMENTO | 2.0417 | 83.3119 | 73.53% | 0 | 0 | 17.21% | 0% | 0 | 0.016706 | 14.9507 | 1.4871 | 0.37144 | Low | Low | Low | 1164 | 1002 | 0.24977 | 106.6253 | 1.195%
CALISTOGA 110135588 | CALISTOGA 1101 | NORTH BAY | 3.0755 | 87.0174 | 100% | 0 | 0 | 100% | 100% | 0 | 0.24881 | 1 | 2.3966 | 0.59629 | High | High | Medium | 1037 | 1003 | 0.24881 | 106.3755 | 1.192%
HALF MOON BAY 11038898 | HALF MOON BAY 1103 | PENINSULA | 0.64191 | 18.722 | 22.54% | 0 | 1 | 100% | 0% | 0 | 0.016511 | 14.9507 | 2.8619 | 0.70648 | Low | Low | Medium | 976 | 1004 | 0.24685 | 106.1267 | 1.189%
SAN BENITO 210136912 | SAN BENITO 2101 | CENTRAL COAST | 2.942 | 68.099 | 74.6% | 0 | 1 | 23.25% | 0% | 0 | 0.016483 | 14.9507 | 2.2757 | 0.5608 | Low | Low | Medium | 1050 | 1005 | 0.24643 | 105.8799 | 1.186%
JARVIS 1110CB | JARVIS 1110 | MISSION | 0.094443 | 65 | 0% | 0 | 0 | 1.965% | 0% | 0 | 0.0069643 | 35.3263 | 4.4419 | 1.0928 | Low | Low | High | 877 | 1006 | 0.24602 | 105.6334 | 1.183%
ALTO 11243745 | ALTO 1124 | NORTH BAY | 4.5809 | 48.7454 | 24.8% | 4 | 26 | 100% | 100% | 0 | 0.24571 | 1 | 4.1069 | 1.0091 | High | High | High | 893 | 1007 | 0.24571 | 105.3874 | 1.181%
MOLINO 110251788 | MOLINO 1102 | SONOMA | 5.6218 | 26.7859 | 66.33% | 10 | 1 | 38.47% | 5.373% | 0 | 0.021877 | 11.2183 | 2.8624 | 0.70251 | Medium | Medium | Medium | 979 | 1008 | 0.24543 | 105.1417 | 1.178%
BUCKS CREEK 1103CB | BUCKS CREEK 1103 | NORTH VALLEY | 2.2994 | 96.1203 | 100% | 2 | 1 | 100% | 100% | 0 | 0.24438 | 1 | 0.43068 | 0.10525 | High | High | Low | 1737 | 1009 | 0.24438 | 104.8963 | 1.175%
MORGAN HILL 2111XR398 | MORGAN HILL 2111 | SAN JOSE | 36.8919 | 62.4019 | 77.2% | 15 | 15 | 93.25% | 35.33% | 1 | 0.2433 | 1 | 2.7433 | 0.66742 | High | High | Medium | 995 | 1010 | 0.2433 | 104.6519 | 1.172%
PURISIMA 110154728 | PURISIMA 1101 | LOS PADRES | 0.37057 | 45.459 | 76.61% | 0 | 0 | 8.245% | 0% | 0 | 0.012146 | 19.9979 | 3.2328 | 0.78525 | Low | Low | High | 946 | 1011 | 0.2429 | 104.4086 | 1.17%
GUALALA 11121294 | GUALALA 1112 | HUMBOLDT | 19.9398 | 39.726 | 11.78% | 10 | 62 | 100% | 0% | 0 | 0.24042 | 1 | 2.2212 | 0.53402 | High | High | Low | 1069 | 1012 | 0.24042 | 104.1657 | 1.167%
ZACA 1102Y54 | ZACA 1102 | LOS PADRES | 34.3968 | 50.4695 | 82.24% | 0 | 23 | 99.37% | 51.02% | 1 | 0.23948 | 1 | 1.6279 | 0.38985 | High | High | Low | 1154 | 1013 | 0.23948 | 103.9253 | 1.164%
PENRYN 1103CB | PENRYN 1103 | SIERRA | 2.2673 | 10 | 57.81% | 1 | 1 | 71.12% | 0% | 0 | 0.015799 | 14.9507 | 2.4019 | 0.56734 | Low | Low | Medium | 1048 | 1014 | 0.23621 | 103.6858 | 1.162%
CLAYTON 221296224 | CLAYTON 2212 | DIABLO | 6.0784 | 53.8659 | 38.47% | 4 | 5 | 100% | 98.09% | 0 | 0.23534 | 1 | 3.3663 | 0.79223 | High | High | High | 944 | 1015 | 0.23534 | 103.4496 | 1.159%
COARSEGOLD 21025380 | COARSEGOLD 2102 | YOSEMITE | 14.1287 | 13.3143 | 99.57% | 3 | 25 | 100% | 100% | 0 | 0.23471 | 1 | 1.9542 | 0.45867 | High | High | Low | 1107 | 1016 | 0.23471 | 103.2142 | 1.156%
OAKLAND K 1102CR014 | OAKLAND K 1102 | EAST BAY | 10.5526 | 27.0866 | 16.24% | 14 | 8 | 100% | 100% | 1 | 0.23413 | 1 | 4.2072 | 0.98504 | High | High | High | 900 | 1017 | 0.23413 | 102.9795 | 1.154%
VALLEY VIEW 1106P166 | VALLEY VIEW 1106 | EAST BAY | 3.4384 | 77.0381 | 8.804% | 5 | 1 | 75.32% | 0% | 0 | 0.020855 | 11.2183 | 4.1312 | 0.96654 | Low | Low | High | 902 | 1018 | 0.23396 | 102.7454 | 1.151%
CALISTOGA 1102634 | CALISTOGA 1102 | NORTH BAY | 11.7799 | 49.1315 | 63.48% | 13 | 6 | 61.37% | 93.22% | 1 | 0.23196 | 1 | 3.0202 | 0.70058 | High | High | Medium | 982 | 1019 | 0.23196 | 102.5114 | 1.148%
SAN LUIS OBISPO 1101CB | SAN LUIS OBISPO 1101 | LOS PADRES | 6.447 | 57.4459 | 18.1% | 1 | 2 | 37.74% | 0% | 0 | 0.01156 | 19.9979 | 3.0286 | 0.70017 | Low | Low | Medium | 983 | 1020 | 0.23118 | 102.2795 | 1.146%
SAN LUIS OBISPO 1107V60 | SAN LUIS OBISPO 1107 | LOS PADRES | 16.0455 | 59.2942 | 63.57% | 4 | 4 | 100% | 91.12% | 0 | 0.23106 | 1 | 2.1951 | 0.5072 | High | High | Low | 1084 | 1021 | 0.23106 | 102.0483 | 1.143%
ALTO 11251226 | ALTO 1125 | NORTH BAY | 7.7199 | 13.4122 | 30.57% | 9 | 29 | 98.37% | 100% | 0 | 0.23095 | 1 | 4.3912 | 1.0142 | High | High | High | 892 | 1022 | 0.23095 | 101.8172 | 1.141%
WILLITS 1103964 | WILLITS 1103 | HUMBOLDT | 2.7651 | 34.3373 | 95.61% | 0 | 1 | 51.42% | 0% | 0 | 0.02055 | 11.2183 | 1.9496 | 0.44946 | Low | Low | Low | 1113 | 1023 | 0.23053 | 101.5863 | 1.138%
HARTLEY 1101658 | HARTLEY 1101 | HUMBOLDT | 2.7971 | 52.1185 | 100% | 0 | 1 | 20.57% | 0% | 0 | 0.020197 | 11.2183 | 2.3275 | 0.52735 | Low | Low | Medium | 1072 | 1024 | 0.22658 | 101.3557 | 1.135%
BIG BEND 1102CB | BIG BEND 1102 | NORTH VALLEY | 17.1238 | 77.0813 | 99.95% | 1 | 3 | 100% | 100% | 0 | 0.22606 | 1 | 2.1303 | 0.48158 | High | High | Low | 1094 | 1025 | 0.22606 | 101.1292 | 1.133%
SHINGLE SPRINGS 210913322 | SHINGLE SPRINGS 2109 | SIERRA | 41.4342 | 33.754 | 99.99% | 7 | 13 | 100% | 26.15% | 1 | 0.22465 | 1 | 1.3879 | 0.3118 | High | High | Low | 1217 | 1026 | 0.22465 | 100.9031 | 1.13%
SAN RAMON 2102CB | SAN RAMON 2102 | MISSION | 1.535 | 41.2314 | 0% | 0 | 0 | 65.73% | 0% | 0 | 0.011168 | 19.9979 | 3.898 | 0.87053 | Low | Low | High | 923 | 1027 | 0.22333 | 100.6784 | 1.128%
ALTO 1124432 | ALTO 1124 | NORTH BAY | 7.823 | 44.0512 | 43.81% | 6 | 19 | 100% | 100% | 0 | 0.22255 | 1 | 4.3312 | 0.96392 | High | High | High | 904 | 1028 | 0.22255 | 100.4551 | 1.125%
LLAGAS 2101XR244 | LLAGAS 2101 | SAN JOSE | 0.29573 | 10 | 100% | 0 | 1 | 2.088% | 0% | 0 | 0.01111 | 19.9979 | 2.6701 | 0.59322 | Low | Low | Medium | 1039 | 1029 | 0.22217 | 100.2326 | 1.123%
VIEJO 220235388 | VIEJO 2202 | CENTRAL COAST | 0.45244 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.014786 | 14.9507 | 4.2357 | 0.93635 | Low | Low | High | 911 | 1030 | 0.22106 | 100.0104 | 1.12%
KESWICK 110148480 | KESWICK 1101 | NORTH VALLEY | 10.8916 | 45.1063 | 95.79% | 1 | 7 | 100% | 100% | 0 | 0.2199 | 1 | 3.1927 | 0.70206 | High | High | High | 981 | 1031 | 0.2199 | 99.7893 | 1.118%
SANTA YNEZ 1104Y30 | SANTA YNEZ 1104 | LOS PADRES | 0.89443 | 34.2503 | 70.68% | 0 | 2 | 6.535% | 0% | 0 | 0.010995 | 19.9979 | 2.9545 | 0.64959 | Low | Low | Medium | 1003 | 1032 | 0.21987 | 99.5694 | 1.115%
SANTA MARIA 1108M18 | SANTA MARIA 1108 | LOS PADRES | 14.6945 | 77.5423 | 92.38% | 1 | 8 | 82.48% | 56.56% | 1 | 0.21976 | 1 | 2.6052 | 0.57252 | High | High | Medium | 1046 | 1033 | 0.21976 | 99.3496 | 1.113%
ALTO 1125902 | ALTO 1125 | NORTH BAY | 12.0705 | 57.5388 | 0.5919% | 9 | 8 | 100% | 85.9% | 1 | 0.21954 | 1 | 3.287 | 0.72162 | High | High | High | 970 | 1034 | 0.21954 | 99.1298 | 1.111%
FROGTOWN 170274648 | FROGTOWN 1702 | STOCKTON | 0.21722 | 10 | 30.03% | 0 | 0 | 4.115% | 0% | 0 | 0.0081651 | 26.5534 | 1.9245 | 0.41726 | Low | Low | Low | 1135 | 1035 | 0.21681 | 98.9103 | 1.108%
FULTON 11024994 | FULTON 1102 | SONOMA | 1.7055 | 60.2868 | 44.56% | 0 | 1 | 40.25% | 0% | 0 | 0.014488 | 14.9507 | 2.9503 | 0.63906 | Low | Low | Medium | 1011 | 1036 | 0.21661 | 98.6935 | 1.106%
OCEANO 110391240 | OCEANO 1103 | LOS PADRES | 0.011387 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.014483 | 14.9507 | 3.2429 | 0.7022 | Low | Low | High | 980 | 1037 | 0.21654 | 98.4768 | 1.103%
GREENBRAE 11021254 | GREENBRAE 1102 | NORTH BAY | 7.0201 | 10 | 37.52% | 8 | 16 | 74.16% | 100% | 0 | 0.21468 | 1 | 3.7891 | 0.81344 | High | High | High | 939 | 1038 | 0.21468 | 98.2603 | 1.101%
SISQUOC 1103M14 | SISQUOC 1103 | LOS PADRES | 21.2959 | 68.8259 | 69.24% | 0 | 10 | 65.02% | 94.4% | 0 | 0.21174 | 1 | 1.0317 | 0.21846 | High | High | Low | 1374 | 1039 | 0.21174 | 98.0456 | 1.098%
MIDDLETOWN 1102878 | MIDDLETOWN 1102 | HUMBOLDT | 0.98449 | 64.5076 | 97.38% | 0 | 3 | 16.45% | 0% | 0 | 0.018862 | 11.2183 | 2.9665 | 0.6277 | Low | Low | Medium | 1017 | 1040 | 0.2116 | 97.8339 | 1.096%
SAN RAFAEL 1108322 | SAN RAFAEL 1108 | NORTH BAY | 7.1088 | 25.427 | 14.01% | 10 | 9 | 95.89% | 89.81% | 0 | 0.21074 | 1 | 4.9853 | 1.0506 | High | High | High | 885 | 1041 | 0.21074 | 97.6223 | 1.094%
OTTER 1101CB | OTTER 1101 | CENTRAL COAST | 6.5139 | 35.3423 | 0.6325% | 8 | 1 | 96.47% | 87.12% | 1 | 0.20943 | 1 | 2.1919 | 0.45904 | High | High | Low | 1106 | 1042 | 0.20943 | 97.4115 | 1.091%
SNEATH LANE 110715341 | SNEATH LANE 1107 | PENINSULA | 0.71839 | 10 | 29.45% | 0 | 0 | 55.75% | 0% | 0 | 0.010414 | 19.9979 | 3.5461 | 0.73852 | Low | Low | High | 965 | 1043 | 0.20826 | 97.2021 | 1.089%
MARIPOSA 210237282 | MARIPOSA 2102 | YOSEMITE | 48.8925 | 28.6255 | 92.59% | 4 | 51 | 82.09% | 39.78% | 0 | 0.20818 | 1 | 1.7072 | 0.35541 | High | High | Low | 1181 | 1044 | 0.20818 | 96.9939 | 1.087%
CAMP EVERS 210511004 | CAMP EVERS 2105 | CENTRAL COAST | 4.2954 | 13.9666 | 78.63% | 3 | 0 | 100% | 100% | 0 | 0.2074 | 1 | 3.9293 | 0.81496 | High | High | High | 938 | 1045 | 0.2074 | 96.7857 | 1.084%
ROB ROY 2104CB | ROB ROY 2104 | CENTRAL COAST | 14.3247 | 30.9167 | 85.32% | 22 | 10 | 100% | 61.11% | 0 | 0.20721 | 1 | 3.1441 | 0.6515 | High | High | High | 1002 | 1046 | 0.20721 | 96.5783 | 1.082%
CAYETANO 21099504 | CAYETANO 2109 | MISSION | 14.1558 | 53.8418 | 95.53% | 0 | 2 | 97.78% | 75.62% | 1 | 0.20657 | 1 | 3.2662 | 0.67468 | High | High | High | 987 | 1047 | 0.20657 | 96.3711 | 1.08%
COARSEGOLD 210210330 | COARSEGOLD 2102 | YOSEMITE | 9.5583 | 29.5023 | 99.75% | 4 | 3 | 100% | 94.16% | 0 | 0.20649 | 1 | 1.5084 | 0.31146 | High | High | Low | 1219 | 1048 | 0.20649 | 96.1645 | 1.077%
SANTA MARIA 1108M80 | SANTA MARIA 1108 | LOS PADRES | 58.3414 | 79.2858 | 99.51% | 1 | 8 | 100% | 61.18% | 1 | 0.20649 | 1 | 2.0334 | 0.41988 | High | High | Low | 1133 | 1049 | 0.20649 | 95.958 | 1.075%
CLOVERDALE 1102 | CLOVERDALE 1102 | SONOMA | 0.015567 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 1 | 1.7488 | 0.35954 | High | High | Low | 1177 | 1050 | 0.20559 | 95.7515 | 1.073%
SAN RAMON 2107MR284 | SAN RAMON 2107 | MISSION | 13.084 | 58.0067 | 71.73% | 0 | 4 | 87.08% | 97.71% | 0 | 0.20548 | 1 | 3.5403 | 0.72747 | High | High | High | 967 | 1051 | 0.20548 | 95.5459 | 1.07%
LLAGAS 2101XR584 | LLAGAS 2101 | SAN JOSE | 1.1341 | 38.093 | 49.38% | 0 | 3 | 12.45% | 0% | 0 | 0.010267 | 19.9979 | 2.6623 | 0.54662 | Low | Low | Medium | 1061 | 1052 | 0.20532 | 95.3404 | 1.068%
BIG BASIN 11025066 | BIG BASIN 1102 | CENTRAL COAST | 14.538 | 30.1342 | 55.77% | 35 | 1 | 100% | 92.59% | 1 | 0.20391 | 1 | 2.3602 | 0.48127 | High | High | Medium | 1095 | 1053 | 0.20391 | 95.1351 | 1.066%
CORRAL 1103CB | CORRAL 1103 | STOCKTON | 5.566 | 15.4342 | 82.99% | 0 | 1 | 19.4% | 0% | 0 | 0.013588 | 14.9507 | 3.2433 | 0.65886 | Low | Low | High | 998 | 1054 | 0.20315 | 94.9312 | 1.063%
ROB ROY 210410298 | ROB ROY 2104 | CENTRAL COAST | 11.1938 | 57.3937 | 79.09% | 34 | 2 | 83.3% | 78.37% | 0 | 0.2019 | 1 | 3.3081 | 0.6679 | High | High | High | 994 | 1055 | 0.2019 | 94.7281 | 1.061%
SHINGLE SPRINGS 2105CB | SHINGLE SPRINGS 2105 | SIERRA | 19.4761 | 21.3342 | 76.42% | 1 | 7 | 100% | 96.24% | 0 | 0.20055 | 1 | 3.0516 | 0.612 | High | High | Medium | 1030 | 1056 | 0.20055 | 94.5262 | 1.059%
MIDDLETOWN 1101612 | MIDDLETOWN 1101 | HUMBOLDT | 3.8703 | 82.8475 | 40.87% | 13 | 3 | 100% | 100% | 1 | 0.19998 | 1 | 2.1199 | 0.42394 | High | High | Low | 1127 | 1057 | 0.19998 | 94.3256 | 1.057%
PLACERVILLE 21067522 | PLACERVILLE 2106 | SIERRA | 67.5844 | 32.7125 | 84.62% | 19 | 16 | 100% | 11.4% | 0 | 0.1992 | 1 | 1.9612 | 0.39066 | High | High | Low | 1152 | 1058 | 0.1992 | 94.1256 | 1.054%
BRUNSWICK 11062416 | BRUNSWICK 1106 | SIERRA | 28.6672 | 22.1211 | 86.48% | 10 | 9 | 92.26% | 60.33% | 1 | 0.19856 | 1 | 2.8411 | 0.56415 | High | High | Medium | 1049 | 1059 | 0.19856 | 93.9264 | 1.052%
MARTELL 110292172 | MARTELL 1102 | STOCKTON | 1.6199 | 10 | 31.25% | 0 | 0 | 49.18% | 0% | 0 | 0.0099007 | 19.9979 | 3.0995 | 0.61369 | Low | Low | High | 1028 | 1060 | 0.19799 | 93.7279 | 1.05%
GIRVAN 11011636 | GIRVAN 1101 | NORTH VALLEY | 16.6216 | 29.0593 | 66.7% | 0 | 3 | 90.3% | 84.26% | 1 | 0.19797 | 1 | 2.1383 | 0.42331 | High | High | Low | 1128 | 1061 | 0.19797 | 93.5299 | 1.048%
PENRYN 1107CB | PENRYN 1107 | SIERRA | 5.4827 | 14.0733 | 57.47% | 3 | 1 | 34.07% | 0% | 0 | 0.01315 | 14.9507 | 2.8102 | 0.55251 | Low | Low | Medium | 1057 | 1062 | 0.19661 | 93.3319 | 1.046%
BIG BASIN 110195690 | BIG BASIN 1101 | CENTRAL COAST | 3.9003 | 22.8227 | 33.75% | 15 | 4 | 100% | 100% | 0 | 0.19661 | 1 | 3.3684 | 0.66225 | High | High | High | 996 | 1063 | 0.19661 | 93.1353 | 1.043%
LAS GALLINAS A 1105532 | LAS GALLINAS A 1105 | NORTH BAY | 3.6841 | 80.5371 | 66.72% | 3 | 5 | 83.44% | 94.05% | 0 | 0.19645 | 1 | 3.3042 | 0.64912 | High | High | High | 1004 | 1064 | 0.19645 | 92.9387 | 1.041%
SONOMA 1105138 | SONOMA 1105 | SONOMA | 0.57477 | 60.5779 | 43.92% | 0 | 0 | 3.3% | 0% | 0 | 0.0098109 | 19.9979 | 3.1352 | 0.61511 | Low | Low | High | 1026 | 1065 | 0.1962 | 92.7422 | 1.039%
OREGON TRAIL 110335002 | OREGON TRAIL 1103 | NORTH VALLEY | 57.2663 | 26.028 | 93.47% | 4 | 13 | 100% | 0% | 0 | 0.19614 | 1 | 2.0644 | 0.40491 | High | High | Low | 1141 | 1066 | 0.19614 | 92.546 | 1.037%
BIG RIVER 1101952 | BIG RIVER 1101 | HUMBOLDT | 16.8032 | 42.8498 | 13.29% | 16 | 25 | 100% | 0% | 0 | 0.19578 | 1 | 1.848 | 0.36179 | High | High | Low | 1174 | 1067 | 0.19578 | 92.3499 | 1.035%
REDBUD 1101454 | REDBUD 1101 | HUMBOLDT | 5.6455 | 80.3546 | 100% | 0 | 0 | 100% | 100% | 0 | 0.19502 | 1 | 1.9323 | 0.37684 | High | High | Low | 1162 | 1068 | 0.19502 | 92.1541 | 1.032%
BOLINAS 1101530 | BOLINAS 1101 | NORTH BAY | 10.9693 | 95.0787 | 44.47% | 2 | 3 | 100% | 100% | 1 | 0.19488 | 1 | 3.6256 | 0.70654 | High | High | High | 975 | 1069 | 0.19488 | 91.9591 | 1.03%
BRUNSWICK 11103907 | BRUNSWICK 1110 | SIERRA | 0.89347 | 10 | 0% | 2 | 0 | 100% | 0% | 0 | 0.013031 | 14.9507 | 2.8579 | 0.55681 | Low | Low | Medium | 1052 | 1070 | 0.19483 | 91.7642 | 1.028%
MORGAN HILL 2105CB | MORGAN HILL 2105 | SAN JOSE | 0.38186 | 10 | 60.48% | 0 | 1 | 21.31% | 0% | 0 | 0.0097345 | 19.9979 | 3.3616 | 0.65441 | Low | Low | High | 1000 | 1071 | 0.19467 | 91.5694 | 1.026%
BIG TREES 0402CB | BIG TREES 0402 | CENTRAL COAST | 6.3055 | 27.5904 | 28.63% | 15 | 5 | 91.1% | 95.73% | 0 | 0.19443 | 1 | 4.0842 | 0.7941 | High | High | High | 943 | 1072 | 0.19443 | 91.3747 | 1.024%
ATASCADERO 1103A88 | ATASCADERO 1103 | LOS PADRES | 0.25306 | 10 | 42.36% | 0 | 0 | 9.428% | 0% | 0 | 0.0073051 | 26.5534 | 2.6184 | 0.50791 | Low | Low | Medium | 1083 | 1073 | 0.19397 | 91.1803 | 1.021%
DUNBAR 11033127 | DUNBAR 1103 | SONOMA | 8.8393 | 48.2541 | 93.29% | 0 | 4 | 91.69% | 100% | 0 | 0.19391 | 1 | 3.2038 | 0.62125 | High | High | High | 1022 | 1074 | 0.19391 | 90.9863 | 1.019%
TIVY VALLEY 110737522 | TIVY VALLEY 1107 | FRESNO | 0.51792 | 52.3595 | 87.8% | 0 | 0 | 16.67% | 0% | 0 | 0.017278 | 11.2183 | 2.1794 | 0.42243 | Low | Low | Low | 1129 | 1075 | 0.19383 | 90.7924 | 1.017%
BIG BASIN 1102CB | BIG BASIN 1102 | CENTRAL COAST | 6.2676 | 51.463 | 36.35% | 17 | 4 | 100% | 100% | 0 | 0.19295 | 1 | 2.5476 | 0.49156 | High | High | Medium | 1088 | 1076 | 0.19295 | 90.5986 | 1.015%
POINT MORETTI 110136514 | POINT MORETTI 1101 | CENTRAL COAST | 6.8197 | 17.0171 | 90.44% | 21 | 1 | 100% | 87.46% | 0 | 0.19239 | 1 | 3.4814 | 0.66979 | High | High | High | 992 | 1077 | 0.19239 | 90.4056 | 1.013%
BRUNSWICK 110750008 | BRUNSWICK 1107 | SIERRA | 3.5553 | 10 | 37.92% | 1 | 5 | 44.72% | 0% | 0 | 0.01283 | 14.9507 | 3.6273 | 0.69578 | Low | Low | High | 984 | 1078 | 0.19182 | 90.2132 | 1.011%
PERRY 1101V88 | PERRY 1101 | LOS PADRES | 1.2286 | 10 | 3.935% | 0 | 0 | 39.45% | 0% | 0 | 0.0071884 | 26.5534 | 3.1534 | 0.6019 | Low | Low | High | 1035 | 1079 | 0.19088 | 90.0214 | 1.008%
IGNACIO 11011264 | IGNACIO 1101 | NORTH BAY | 1.5242 | 13.9644 | 55.83% | 0 | 4 | 38.01% | 4.721% | 0 | 0.016971 | 11.2183 | 3.1948 | 0.60822 | Low | Low | High | 1032 | 1080 | 0.19038 | 89.8305 | 1.006%
BIG BASIN 11015028 | BIG BASIN 1101 | CENTRAL COAST | 4.9702 | 16.4741 | 66.18% | 6 | 3 | 100% | 100% | 0 | 0.1889 | 1 | 3.3403 | 0.63099 | High | High | High | 1012 | 1081 | 0.1889 | 89.6402 | 1.004%
SONOMA 11033052 | SONOMA 1103 | SONOMA | 13.4991 | 28.4052 | 91.89% | 6 | 9 | 83.64% | 100% | 0 | 0.18717 | 1 | 3.517 | 0.65829 | High | High | High | 999 | 1082 | 0.18717 | 89.4513 | 1.002%
CEDAR CREEK 11011710 | CEDAR CREEK 1101 | NORTH VALLEY | 0.076338 | 70.3009 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18445 | 1 | 0.68738 | 0.12679 | High | High | Low | 1636 | 1083 | 0.18445 | 89.2641 | 1%
CURTIS 170268380 | CURTIS 1702 | YOSEMITE | 6.6498 | 16.4166 | 99.81% | 2 | 11 | 100% | 65.93% | 0 | 0.18443 | 1 | 4.0104 | 0.73965 | High | High | High | 963 | 1084 | 0.18443 | 89.0796 | 0.9979%
COTATI 11055156 | COTATI 1105 | SONOMA | 3.6981 | 31.1041 | 18.22% | 1 | 1 | 37.15% | 0% | 0 | 0.012279 | 14.9507 | 2.8955 | 0.53156 | Low | Low | Medium | 1071 | 1085 | 0.18358 | 88.8952 | 0.9959%
GARBERVILLE 11026084 | GARBERVILLE 1102 | HUMBOLDT | 15.3135 | 81.9421 | 99.24% | 23 | 2 | 100% | 0% | 0 | 0.18331 | 1 | 1.4373 | 0.26347 | High | High | Low | 1291 | 1086 | 0.18331 | 88.7116 | 0.9938%
CALISTOGA 110189150 | CALISTOGA 1101 | NORTH BAY | 9.6361 | 72.7174 | 50.49% | 2 | 3 | 100% | 93.01% | 1 | 0.18208 | 1 | 2.6306 | 0.47897 | High | High | Medium | 1096 | 1087 | 0.18208 | 88.5283 | 0.9918%
CENTERVILLE 11012448 | CENTERVILLE 1101 | NORTH VALLEY | 24.8271 | 10 | 80.77% | 5 | 8 | 100% | 95.09% | 1 | 0.182 | 1 | 3.4115 | 0.62089 | High | High | High | 1023 | 1088 | 0.182 | 88.3462 | 0.9897%
SISQUOC 1102M52 | SISQUOC 1102 | LOS PADRES | 31.4004 | 61.3581 | 49.81% | 0 | 2 | 87.94% | 100% | 0 | 0.18147 | 1 | 0.47061 | 0.0854 | High | High | Low | 1873 | 1089 | 0.18147 | 88.1642 | 0.9877%
GIRVAN 11029012 | GIRVAN 1102 | NORTH VALLEY | 15.986 | 25.3548 | 93.5% | 4 | 4 | 100% | 96.14% | 1 | 0.18146 | 1 | 2.3257 | 0.42202 | High | High | Medium | 1131 | 1090 | 0.18146 | 87.9828 | 0.9857%
OAKLAND X 1104CR288 | OAKLAND X 1104 | EAST BAY | 2.7135 | 13.3002 | 40.68% | 11 | 2 | 100% | 100% | 0 | 0.18087 | 1 | 4.2967 | 0.77715 | High | High | High | 950 | 1091 | 0.18087 | 87.8013 | 0.9836%
PINE GROVE 11013170 | PINE GROVE 1101 | STOCKTON | 40.3025 | 15.3788 | 88.67% | 12 | 21 | 100% | 0% | 0 | 0.18 | 1 | 2.6168 | 0.47101 | High | High | Medium | 1100 | 1092 | 0.18 | 87.6204 | 0.9816%
CALISTOGA 110266730 | CALISTOGA 1102 | NORTH BAY | 1.1709 | 73.9432 | 93.25% | 0 | 0 | 100% | 100% | 0 | 0.17987 | 1 | 2.7269 | 0.49048 | High | High | Medium | 1089 | 1093 | 0.17987 | 87.4404 | 0.9796%
PASO ROBLES 11032731 | PASO ROBLES 1103 | LOS PADRES | 1.1994 | 24.9201 | 47.66% | 0 | 0 | 73.66% | 0% | 0 | 0.015948 | 11.2183 | 1.3825 | 0.24735 | Low | Low | Low | 1320 | 1094 | 0.17891 | 87.2606 | 0.9776%
CURTIS 17039330 | CURTIS 1703 | YOSEMITE | 41.1713 | 48.6933 | 100% | 9 | 13 | 100% | 41.49% | 1 | 0.1783 | 1 | 1.542 | 0.27494 | High | High | Low | 1274 | 1095 | 0.1783 | 87.0817 | 0.9756%
LOS GATOS 110760092 | LOS GATOS 1107 | DE ANZA | 9.7412 | 27.0068 | 22.28% | 14 | 2 | 100% | 100% | 0 | 0.17816 | 1 | 2.2097 | 0.39367 | High | High | Low | 1150 | 1096 | 0.17816 | 86.9034 | 0.9736%
MORAGA 1102CB | MORAGA 1102 | DIABLO | 3.3475 | 12.7577 | 17.22% | 0 | 6 | 36.14% | 35.27% | 0 | 0.015794 | 11.2183 | 3.4911 | 0.61857 | Low | Low | High | 1024 | 1097 | 0.17719 | 86.7252 | 0.9716%
GABILAN 1101579969 | GABILAN 1101 | CENTRAL COAST | 4.2047 | 48.3297 | 40.21% | 0 | 0 | 62.81% | 0% | 0 | 0.01579 | 11.2183 | 1.8809 | 0.33318 | Low | Low | Low | 1196 | 1098 | 0.17714 | 86.548 | 0.9696%
CAMP EVERS 210610718 | CAMP EVERS 2106 | CENTRAL COAST | 8.4743 | 22.3341 | 66.06% | 7 | 3 | 100% | 100% | 0 | 0.17677 | 1 | 3.2715 | 0.57831 | High | High | High | 1043 | 1099 | 0.17677 | 86.3709 | 0.9676%
DOBBINS 11011264 | DOBBINS 1101 | SIERRA | 34.6636 | 46.9951 | 96.43% | 5 | 9 | 99.16% | 60.09% | 0 | 0.17584 | 1 | 2.216 | 0.38966 | High | High | Low | 1155 | 1100 | 0.17584 | 86.1941 | 0.9656%
WYANDOTTE 11031508 | WYANDOTTE 1103 | NORTH VALLEY | 25.7036 | 27.6675 | 92.16% | 3 | 8 | 99.06% | 81.42% | 1 | 0.17558 | 1 | 2.8465 | 0.49977 | High | High | Medium | 1086 | 1101 | 0.17558 | 86.0183 | 0.9636%
PLACERVILLE 210619552 | PLACERVILLE 2106 | SIERRA | 21.1288 | 10.9472 | 81.54% | 2 | 6 | 100% | 88.4% | 1 | 0.17549 | 1 | 2.5401 | 0.44577 | High | High | Medium | 1116 | 1102 | 0.17549 | 85.8427 | 0.9617%
SAN RAMON 2119CB | SAN RAMON 2119 | MISSION | 0.46097 | 10 | 0% | 0 | 2 | 29.99% | 0% | 0 | 0.0066042 | 26.5534 | 3.8288 | 0.67144 | Low | Low | High | 989 | 1103 | 0.17536 | 85.6672 | 0.9597%
TASSAJARA 2106CB | TASSAJARA 2106 | DIABLO | 0.13696 | 51.6086 | 30.65% | 0 | 2 | 4.465% | 0% | 0 | 0.0087354 | 19.9979 | 4.2753 | 0.74685 | Low | Low | High | 960 | 1104 | 0.17469 | 85.4918 | 0.9578%
SPRING GAP 1702CB | SPRING GAP 1702 | YOSEMITE | 7.418 | 94.1072 | 60.1% | 3 | 1 | 100% | 85.76% | 0 | 0.17407 | 1 | 0.85687 | 0.14916 | High | High | Low | 1554 | 1105 | 0.17407 | 85.3171 | 0.9558%
SANTA ROSA A 1104210 | SANTA ROSA A 1104 | SONOMA | 6.8749 | 10 | 33.39% | 9 | 10 | 88.77% | 100% | 0 | 0.17303 | 1 | 3.5409 | 0.61267 | High | High | High | 1029 | 1106 | 0.17303 | 85.1431 | 0.9538%
CASTRO VALLEY 1108MR273 | CASTRO VALLEY 1108 | MISSION | 0.47624 | 26.7875 | 0% | 0 | 0 | 65.66% | 0% | 0 | 0.01155 | 14.9507 | 4.003 | 0.69126 | Low | Low | High | 985 | 1107 | 0.17268 | 84.97 | 0.9519%
CALPINE 1146400 | CALPINE 1146 | SONOMA | 3.1435 | 89.9771 | 73.48% | 0 | 0 | 100% | 100% | 0 | 0.17211 | 1 | 1.7847 | 0.30717 | High | High | Low | 1228 | 1108 | 0.17211 | 84.7973 | 0.95%
PAUL SWEET 21065178 | PAUL SWEET 2106 | CENTRAL COAST | 7.3151 | 10 | 46.38% | 7 | 0 | 100% | 100% | 0 | 0.17066 | 1 | 3.3829 | 0.57733 | High | High | High | 1044 | 1109 | 0.17066 | 84.6252 | 0.948%
BIG BASIN 110296986 | BIG BASIN 1102 | CENTRAL COAST | 5.8731 | 33.0475 | 64.84% | 22 | 1 | 100% | 100% | 0 | 0.16999 | 1 | 2.3974 | 0.40753 | High | High | Medium | 1137 | 1110 | 0.16999 | 84.4546 | 0.9461%
PLACER 1102CB | PLACER 1102 | SIERRA | 2.1407 | 10 | 18.98% | 0 | 1 | 100% | 0% | 0 | 0.015126 | 11.2183 | 3.2057 | 0.54396 | Low | Low | High | 1064 | 1111 | 0.16968 | 84.2846 | 0.9442%
NARROWS 210248484 | NARROWS 2102 | SIERRA | 41.4937 | 26.7261 | 86.16% | 7 | 18 | 100% | 0% | 0 | 0.16958 | 1 | 2.5572 | 0.43366 | High | High | Medium | 1124 | 1112 | 0.16958 | 84.1149 | 0.9423%
CALPINE 1146CB | CALPINE 1146 | SONOMA | 3.8475 | 90.2876 | 70.72% | 0 | 0 | 100% | 100% | 0 | 0.16919 | 1 | 1.9173 | 0.32438 | High | High | Low | 1204 | 1113 | 0.16919 | 83.9453 | 0.9404%
MARIPOSA 210110990 | MARIPOSA 2101 | YOSEMITE | 39.8367 | 17.0819 | 99.94% | 3 | 69 | 100% | 0% | 0 | 0.16909 | 1 | 1.36 | 0.22996 | High | High | Low | 1350 | 1114 | 0.16909 | 83.7761 | 0.9385%
COTATI 110475972 | COTATI 1104 | SONOMA | 2.7371 | 10 | 35.68% | 0 | 3 | 41.48% | 0% | 0 | 0.015037 | 11.2183 | 3.0719 | 0.51821 | Low | Low | Medium | 1082 | 1115 | 0.1687 | 83.607 | 0.9366%
WILLOW CREEK 110129362 | WILLOW CREEK 1101 | HUMBOLDT | 6.8106 | 67.3887 | 96.73% | 8 | 5 | 58.77% | 100% | 1 | 0.16769 | 1 | 0.86685 | 0.14536 | High | High | Low | 1572 | 1116 | 0.16769 | 83.4383 | 0.9347%
PUEBLO 1105716 | PUEBLO 1105 | NORTH BAY | 2.9378 | 34.7126 | 67.65% | 0 | 0 | 14.86% | 0% | 0 | 0.01121 | 14.9507 | 3.18 | 0.53295 | Low | Low | High | 1070 | 1117 | 0.16759 | 83.2707 | 0.9329%
CORNING 11021900 | CORNING 1102 | NORTH VALLEY | 0.99921 | 77.9025 | 2.304% | 0 | 2 | 5.388% | 0% | 0 | 0.0083558 | 19.9979 | 1.3171 | 0.22009 | Low | Low | Low | 1370 | 1118 | 0.1671 | 83.1031 | 0.931%
SAN LUIS OBISPO 11042293 | SAN LUIS OBISPO 1104 | LOS PADRES | 9.0237 | 83.3193 | 68.53% | 2 | 1 | 100% | 100% | 0 | 0.16663 | 1 | 1.4572 | 0.24281 | High | High | Low | 1330 | 1119 | 0.16663 | 82.936 | 0.9291%
BIG BASIN 110276752 | BIG BASIN 1102 | CENTRAL COAST | 2.6798 | 26.5426 | 60.49% | 5 | 8 | 100% | 100% | 0 | 0.1665 | 1 | 2.6319 | 0.43821 | High | High | Medium | 1121 | 1120 | 0.1665 | 82.7693 | 0.9273%
WYANDOTTE 11091040 | WYANDOTTE 1109 | NORTH VALLEY | 0.63854 | 10 | 53.93% | 1 | 0 | 10.55% | 0% | 0 | 0.0082291 | 19.9979 | 4.416 | 0.72671 | Low | Low | High | 968 | 1121 | 0.16456 | 82.6028 | 0.9254%
SUNOL 1101MR299 | SUNOL 1101 | MISSION | 4.988 | 63.7936 | 27.4% | 3 | 3 | 100% | 100% | 0 | 0.16428 | 1 | 2.4384 | 0.40057 | High | High | Medium | 1148 | 1122 | 0.16428 | 82.4383 | 0.9235%
PENRYN 11072704 | PENRYN 1107 | SIERRA | 1.9532 | 10 | 45.97% | 0 | 0 | 34.19% | 0% | 0 | 0.010983 | 14.9507 | 3.2851 | 0.53943 | Low | Low | High | 1068 | 1123 | 0.1642 | 82.274 | 0.9217%
STAFFORD 110233692 | STAFFORD 1102 | NORTH BAY | 0.31495 | 10 | 16.33% | 0 | 0 | 14.09% | 0% | 0 | 0.0061817 | 26.5534 | 3.2 | 0.52527 | Low | Low | High | 1076 | 1124 | 0.16415 | 82.1098 | 0.9199%
GOLDTREE 1105CB | GOLDTREE 1105 | LOS PADRES | 7.0823 | 62.297 | 33.11% | 0 | 1 | 49.12% | 0% | 0 | 0.014604 | 11.2183 | 2.7587 | 0.45198 | Low | Low | Medium | 1108 | 1125 | 0.16384 | 81.9456 | 0.918%
SAN JOAQUIN #3 110210342 | SAN JOAQUIN #3 1102 | YOSEMITE | 1.8206 | 16.0634 | 100% | 0 | 4 | 100% | 100% | 0 | 0.16247 | 1 | 1.436 | 0.2333 | High | High | Low | 1346 | 1126 | 0.16247 | 81.7818 | 0.9162%
PASO ROBLES 1104P02 | PASO ROBLES 1104 | LOS PADRES | 0.077403 | 10 | 100% | 0 | 0 | 1.071% | 0% | 0 | 0.010772 | 14.9507 | 1.9918 | 0.32079 | Low | Low | Low | 1207 | 1127 | 0.16105 | 81.6193 | 0.9144%
PARADISE 110445674 | PARADISE 1104 | NORTH VALLEY | 5.0463 | 10.402 | 42.33% | 2 | 14 | 100% | 100% | 0 | 0.16095 | 1 | 3.7001 | 0.59555 | High | High | High | 1038 | 1128 | 0.16095 | 81.4583 | 0.9126%
WOODACRE 1102137662 | WOODACRE 1102 | NORTH BAY | 8.5017 | 38.382 | 27.15% | 11 | 8 | 98.65% | 72.31% | 0 | 0.16033 | 1 | 4.753 | 0.76204 | High | High | High | 954 | 1129 | 0.16033 | 81.2973 | 0.9108%
SILVERADO 2104708 | SILVERADO 2104 | NORTH BAY | 4.377 | 40.803 | 65.23% | 1 | 8 | 88.72% | 99% | 0 | 0.16025 | 1 | 3.379 | 0.5415 | High | High | High | 1066 | 1130 | 0.16025 | 81.137 | 0.909%
SAN RAMON 2101CB | SAN RAMON 2101 | MISSION | 0.57317 | 10 | 0% | 0 | 0 | 53.42% | 0% | 0 | 0.0079978 | 19.9979 | 3.8395 | 0.61409 | Low | Low | High | 1027 | 1131 | 0.15994 | 80.9768 | 0.9072%
SAN JOAQUIN #3 1101CB | SAN JOAQUIN #3 1101 | YOSEMITE | 5.4085 | 45.9214 | 90.84% | 2 | 3 | 100% | 98.42% | 0 | 0.15907 | 1 | 1.4628 | 0.23269 | High | High | Low | 1347 | 1132 | 0.15907 | 80.8168 | 0.9054%
BIG BASIN 11028403 | BIG BASIN 1102 | CENTRAL COAST | 4.9235 | 33.659 | 85.64% | 2 | 1 | 100% | 100% | 0 | 0.15781 | 1 | 2.5682 | 0.40531 | High | High | Medium | 1140 | 1133 | 0.15781 | 80.6577 | 0.9036%
DIAMOND SPRINGS 110519910 | DIAMOND SPRINGS 1105 | SIERRA | 20.7681 | 27.6002 | 62.16% | 0 | 7 | 100% | 83.55% | 0 | 0.1574 | 1 | 2.0452 | 0.32192 | High | High | Low | 1206 | 1134 | 0.1574 | 80.4999 | 0.9018%
NOTRE DAME 11042028 | NOTRE DAME 1104 | NORTH VALLEY | 10.9017 | 45.9089 | 89% | 0 | 3 | 100% | 100% | 0 | 0.15694 | 1 | 2.5912 | 0.40666 | High | High | Medium | 1138 | 1135 | 0.15694 | 80.3425 | 0.9001%
MONTE RIO 111159046 | MONTE RIO 1111 | SONOMA | 2.6767 | 61.8101 | 0% | 1 | 1 | 70.69% | 0% | 0 | 0.013942 | 11.2183 | 1.5755 | 0.24642 | Low | Low | Low | 1323 | 1136 | 0.15641 | 80.1856 | 0.8983%
KESWICK 11011590 | KESWICK 1101 | NORTH VALLEY | 6.51 | 47.89 | 75.62% | 0 | 1 | 100% | 100% | 0 | 0.15625 | 1 | 3.693 | 0.57701 | High | High | High | 1045 | 1137 | 0.15625 | 80.0292 | 0.8966%
NEWBURG 11323425 | NEWBURG 1132 | HUMBOLDT | 0.9717 | 21.9962 | 41.93% | 1 | 0 | 64.08% | 0% | 0 | 0.013757 | 11.2183 | 2.8658 | 0.44227 | Low | Low | Medium | 1120 | 1138 | 0.15433 | 79.8729 | 0.8948%
HORSESHOE 1101CB | HORSESHOE 1101 | SIERRA | 1.5163 | 10 | 43.57% | 1 | 0 | 28.38% | 0% | 0 | 0.010302 | 14.9507 | 4.1553 | 0.63998 | Low | Low | High | 1008 | 1139 | 0.15402 | 79.7186 | 0.8931%
CAMP EVERS 210637210 | CAMP EVERS 2106 | CENTRAL COAST | 6.3592 | 23.8928 | 45.59% | 8 | 2 | 100% | 100% | 0 | 0.15389 | 1 | 2.9227 | 0.44978 | High | High | Medium | 1110 | 1140 | 0.15389 | 79.5646 | 0.8913%
SARATOGA 1107LC12 | SARATOGA 1107 | DE ANZA | 7.3147 | 36.5682 | 63.55% | 4 | 7 | 100% | 57.8% | 0 | 0.15388 | 1 | 3.6179 | 0.55673 | High | High | High | 1053 | 1141 | 0.15388 | 79.4107 | 0.8896%
BIG BEND 1101641808 | BIG BEND 1101 | NORTH VALLEY | 24.9976 | 36.2263 | 100% | 6 | 10 | 95.85% | 52.55% | 1 | 0.15307 | 1 | 2.3707 | 0.36288 | High | High | Medium | 1172 | 1142 | 0.15307 | 79.2568 | 0.8879%
LOS GATOS 1106LA42 | LOS GATOS 1106 | DE ANZA | 2.7943 | 10 | 80.03% | 3 | 2 | 100% | 100% | 1 | 0.15252 | 1 | 3.137 | 0.47846 | High | High | High | 1099 | 1143 | 0.15252 | 79.1037 | 0.8862%
CLARKSVILLE 210319572 | CLARKSVILLE 2103 | SIERRA | 33.5123 | 41.8595 | 99.97% | 3 | 7 | 77.35% | 59.23% | 1 | 0.15209 | 1 | 2.6524 | 0.40341 | High | High | Medium | 1144 | 1144 | 0.15209 | 78.9512 | 0.8845%
ELK 11011272 | ELK 1101 | HUMBOLDT | 22.2131 | 39.0938 | 18.17% | 28 | 27 | 99.76% | 0% | 0 | 0.15006 | 1 | 1.6636 | 0.24963 | High | High | Low | 1312 | 1145 | 0.15006 | 78.7991 | 0.8828%
SAUSALITO 1101CB | SAUSALITO 1101 | NORTH BAY | 0.084384 | 10 | 39.07% | 0 | 0 | 1.452% | 0% | 0 | 0.0074993 | 19.9979 | 3.1293 | 0.4693 | Low | Low | High | 1103 | 1146 | 0.14997 | 78.6491 | 0.8811%
WOODACRE 1102CB | WOODACRE 1102 | NORTH BAY | 12.3335 | 47.7292 | 17.58% | 11 | 6 | 98.44% | 71.03% | 1 | 0.14985 | 1 | 4.2881 | 0.64256 | High | High | High | 1007 | 1147 | 0.14985 | 78.4991 | 0.8794%
CURTIS 17028000 | CURTIS 1702 | YOSEMITE | 14.3249 | 17.4723 | 99.98% | 1 | 11 | 100% | 50.67% | 0 | 0.14933 | 1 | 3.7034 | 0.55303 | High | High | High | 1056 | 1148 | 0.14933 | 78.3493 | 0.8777%
CAMP EVERS 2105CB | CAMP EVERS 2105 | CENTRAL COAST | 8.5381 | 22.2654 | 52.34% | 18 | 3 | 83.09% | 96.05% | 0 | 0.14927 | 1 | 4.1373 | 0.61755 | High | High | High | 1025 | 1149 | 0.14927 | 78.1999 | 0.8761%
MORGAN HILL 2105XR268 | MORGAN HILL 2105 | SAN JOSE | 7.973 | 60.2912 | 70.21% | 1 | 2 | 100% | 100% | 0 | 0.14861 | 1 | 3.0893 | 0.45909 | High | High | High | 1105 | 1150 | 0.14861 | 78.0507 | 0.8744%
MORGAN HILL 210542348 | MORGAN HILL 2105 | SAN JOSE | 1.0024 | 17.5681 | 55.95% | 0 | 0 | 23.75% | 0% | 0 | 0.0099083 | 14.9507 | 3.3198 | 0.49179 | Low | Low | High | 1087 | 1151 | 0.14814 | 77.902 | 0.8727%
ELECTRA 11022646 | ELECTRA 1102 | STOCKTON | 25.2162 | 27.1707 | 98.11% | 7 | 13 | 100% | 22.04% | 1 | 0.14592 | 1 | 1.8392 | 0.26838 | High | High | Low | 1286 | 1152 | 0.14592 | 77.7539 | 0.8711%
FULTON 1107 | FULTON 1107 | SONOMA | 0.4544 | 32.639 | 77.88% | 0 | 1 | 100% | 100% | 1 | 0.14528 | 1 | 2.3437 | 0.34049 | High | High | Medium | 1189 | 1153 | 0.14528 | 77.608 | 0.8694%
WILLITS 1103966 | WILLITS 1103 | HUMBOLDT | 1.3235 | 20.8407 | 41.93% | 0 | 1 | 57.92% | 0% | 0 | 0.012942 | 11.2183 | 2.2623 | 0.32845 | Low | Low | Medium | 1200 | 1154 | 0.14519 | 77.4627 | 0.8678%
CAMP EVERS 210310946 | CAMP EVERS 2103 | CENTRAL COAST | 5.6138 | 10 | 43.31% | 5 | 3 | 66.4% | 100% | 0 | 0.14518 | 1 | 2.7721 | 0.40244 | High | High | Medium | 1145 | 1155 | 0.14518 | 77.3175 | 0.8662%
REDBUD 11022013 | REDBUD 1102 | HUMBOLDT | 0.11285 | 35.1068 | 100% | 0 | 0 | 2.449% | 0% | 0 | 0.01294 | 11.2183 | 3.0608 | 0.44433 | Low | Low | Medium | 1117 | 1156 | 0.14517 | 77.1724 | 0.8646%
CAMP EVERS 21055146 | CAMP EVERS 2105 | CENTRAL COAST | 6.0305 | 10 | 32.63% | 11 | 6 | 100% | 100% | 0 | 0.14397 | 1 | 3.8493 | 0.55419 | High | High | High | 1055 | 1157 | 0.14397 | 77.0272 | 0.8629%
CAMP EVERS 21055232 | CAMP EVERS 2105 | CENTRAL COAST | 4.5381 | 18.453 | 49.44% | 6 | 6 | 100% | 100% | 0 | 0.14357 | 1 | 3.6265 | 0.52068 | High | High | High | 1079 | 1158 | 0.14357 | 76.8832 | 0.8613%
SAN RAFAEL 1101310 | SAN RAFAEL 1101 | NORTH BAY | 1.3967 | 10 | 2.818% | 0 | 0 | 39.65% | 0% | 0 | 0.0071371 | 19.9979 | 4.4071 | 0.62902 | Low | Low | High | 1014 | 1159 | 0.14273 | 76.7396 | 0.8597%
COARSEGOLD 21025722 | COARSEGOLD 2102 | YOSEMITE | 1.9829 | 10 | 100% | 0 | 5 | 100% | 100% | 0 | 0.14258 | 1 | 2.0056 | 0.28595 | High | High | Low | 1255 | 1160 | 0.14258 | 76.5969 | 0.8581%
NORTH DUBLIN 2103 | NORTH DUBLIN 2103 | MISSION | 0.0011266 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 11.2183 | 4.0077 | 0.57078 | Low | Low | High | 1047 | 1161 | 0.14242 | 76.4543 | 0.8565%
DEL MONTE 21043066 | DEL MONTE 2104 | CENTRAL COAST | 0.016196 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 11.2183 | 3.1116 | 0.44316 | Low | Low | High | 1119 | 1161 | 0.14242 | 76.3119 | 0.8549%
PUEBLO 1104 | PUEBLO 1104 | NORTH BAY | 0.072037 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 11.2183 | 2.568 | 0.36574 | Low | Low | Medium | 1168 | 1161 | 0.14242 | 76.1695 | 0.8533%
WILLITS 11032500 | WILLITS 1103 | HUMBOLDT | 29.9853 | 83.8453 | 100% | 11 | 13 | 100% | 0% | 0 | 0.14143 | 1 | 1.453 | 0.20549 | High | High | Low | 1403 | 1164 | 0.14143 | 76.0271 | 0.8517%
BOLINAS 1101806 | BOLINAS 1101 | NORTH BAY | 3.0453 | 88.6877 | 5.762% | 0 | 3 | 100% | 100% | 0 | 0.14085 | 1 | 3.8778 | 0.54618 | High | High | High | 1062 | 1165 | 0.14085 | 75.8856 | 0.8501%
RED BLUFF 1104CB | RED BLUFF 1104 | NORTH VALLEY | 2.0518 | 10 | 96.16% | 0 | 0 | 19.48% | 0% | 0 | 0.012529 | 11.2183 | 2.2135 | 0.31112 | Low | Low | Low | 1220 | 1166 | 0.14056 | 75.7448 | 0.8486%
REDBUD 11021212 | REDBUD 1102 | HUMBOLDT | 0.436 | 23.3209 | 21.35% | 0 | 1 | 11.49% | 0% | 0 | 0.0070167 | 19.9979 | 3.0081 | 0.42209 | Low | Low | Medium | 1130 | 1167 | 0.14032 | 75.6042 | 0.847%
SUNOL 1101MR298 | SUNOL 1101 | MISSION | 5.4024 | 53.1471 | 44.07% | 1 | 5 | 100% | 100% | 0 | 0.1402 | 1 | 1.8521 | 0.25967 | High | High | Low | 1297 | 1168 | 0.1402 | 75.4639 | 0.8454%
SEACLIFF 0401CB | SEACLIFF 0401 | CENTRAL COAST | 5.8801 | 16.5923 | 59.63% | 6 | 2 | 97.46% | 83.75% | 0 | 0.13923 | 1 | 3.7795 | 0.52621 | High | High | High | 1074 | 1169 | 0.13923 | 75.3237 | 0.8438%
SALT SPRINGS 21028442 | SALT SPRINGS 2102 | STOCKTON | 12.1299 | 48.4336 | 100% | 5 | 7 | 100% | 9.936% | 1 | 0.13919 | 1 | 0.78756 | 0.10962 | High | High | Low | 1712 | 1170 | 0.13919 | 75.1845 | 0.8423%
CLAYTON 2212CB | CLAYTON 2212 | DIABLO | 1.3959 | 28.1061 | 22.31% | 0 | 2 | 11% | 15.16% | 0 | 0.01235 | 11.2183 | 3.9394 | 0.5458 | Low | Low | High | 1063 | 1171 | 0.13855 | 75.0453 | 0.8407%
MARIPOSA 21014410 | MARIPOSA 2101 | YOSEMITE | 22.8041 | 16.019 | 99.74% | 6 | 25 | 100% | 48.37% | 1 | 0.13823 | 1 | 1.1854 | 0.16386 | High | High | Low | 1513 | 1172 | 0.13823 | 74.9067 | 0.8392%
DUNBAR 110147964 | DUNBAR 1101 | SONOMA | 6.3806 | 61.1795 | 83.1% | 1 | 6 | 83.19% | 93% | 0 | 0.13803 | 1 | 2.8326 | 0.39097 | High | High | Medium | 1151 | 1173 | 0.13803 | 74.7685 | 0.8376%
MIWUK 170247143 | MIWUK 1702 | YOSEMITE | 4.8917 | 41.2668 | 100% | 1 | 8 | 100% | 79.87% | 0 | 0.13801 | 1 | 4.5597 | 0.62928 | High | High | High | 1013 | 1174 | 0.13801 | 74.6305 | 0.8361%
TASSAJARA 2113MR276 | TASSAJARA 2113 | DIABLO | 3.6023 | 62.8969 | 34.15% | 1 | 2 | 92.48% | 100% | 0 | 0.13782 | 1 | 3.251 | 0.44804 | High | High | High | 1115 | 1175 | 0.13782 | 74.4925 | 0.8345%
PAUL SWEET 2106428102 | PAUL SWEET 2106 | CENTRAL COAST | 11.5695 | 14.0231 | 80.02% | 8 | 3 | 89.09% | 75.97% | 1 | 0.13775 | 1 | 3.9916 | 0.54983 | High | High | High | 1059 | 1176 | 0.13775 | 74.3547 | 0.833%
MARIPOSA 210110240 | MARIPOSA 2101 | YOSEMITE | 21.4769 | 25.894 | 68.07% | 2 | 22 | 100% | 66.83% | 0 | 0.13718 | 1 | 2.2737 | 0.3119 | High | High | Medium | 1216 | 1177 | 0.13718 | 74.2169 | 0.8314%
DUNBAR 1101416 | DUNBAR 1101 | SONOMA | 2.8528 | 67.3035 | 61.83% | 0 | 0 | 84.79% | 100% | 0 | 0.13696 | 1 | 2.5295 | 0.34643 | High | High | Medium | 1186 | 1178 | 0.13696 | 74.0797 | 0.8299%
MARIPOSA 21029590 | MARIPOSA 2102 | YOSEMITE | 36.36 | 19.6403 | 97.41% | 1 | 52 | 100% | 0% | 0 | 0.13645 | 1 | 2.0449 | 0.27902 | High | High | Low | 1261 | 1179 | 0.13645 | 73.9428 | 0.8284%
CLARK ROAD 11022068 | CLARK ROAD 1102 | NORTH VALLEY | 10.7164 | 15.0462 | 99.79% | 0 | 2 | 100% | 90.22% | 1 | 0.13587 | 1 | 2.3575 | 0.32031 | High | High | Medium | 1208 | 1180 | 0.13587 | 73.8063 | 0.8268%
SPAULDING 1101578852 | SPAULDING 1101 | SIERRA | 20.1063 | 56.8104 | 73.09% | 2 | 12 | 82.23% | 8.84% | 1 | 0.13582 | 1 | 0.021523 | 0.0029234 | High | High | Low | 3177 | 1181 | 0.13582 | 73.6705 | 0.8253%
ALLEGHANY 1101808 | ALLEGHANY 1101 | SIERRA | 6.1403 | 95.663 | 12.49% | 0 | 2 | 100% | 100% | 0 | 0.13475 | 1 | 1.679 | 0.22625 | High | High | Low | 1357 | 1182 | 0.13475 | 73.5346 | 0.8238%
OAKHURST 110310570 | OAKHURST 1103 | YOSEMITE | 9.7802 | 19.5863 | 100% | 0 | 5 | 100% | 83.62% | 0 | 0.13448 | 1 | 2.0684 | 0.27817 | High | High | Low | 1263 | 1183 | 0.13448 | 73.3999 | 0.8223%
BEAR VALLEY 21059560 | BEAR VALLEY 2105 | YOSEMITE | 36.2873 | 45.8774 | 99.97% | 7 | 2 | 100% | 13.33% | 1 | 0.13437 | 1 | 2.3028 | 0.30942 | High | High | Medium | 1225 | 1184 | 0.13437 | 73.2654 | 0.8208%
ANNAPOLIS 1101608 | ANNAPOLIS 1101 | HUMBOLDT | 17.8008 | 87.1454 | 94.8% | 10 | 5 | 100% | 0% | 0 | 0.13339 | 1 | 1.3674 | 0.1824 | High | High | Low | 1464 | 1185 | 0.13339 | 73.131 | 0.8193%
SAN JOAQUIN #3 110110060 | SAN JOAQUIN #3 1101 | YOSEMITE | 6.5306 | 43.2657 | 65.2% | 0 | 4 | 100% | 100% | 0 | 0.133 | 1 | 1.8456 | 0.24547 | High | High | Low | 1325 | 1186 | 0.133 | 72.9977 | 0.8178%
MARIPOSA 210210880 | MARIPOSA 2102 | YOSEMITE | 39.106 | 24.6164 | 88.93% | 0 | 41 | 98.36% | 24.49% | 0 | 0.13284 | 1 | 1.875 | 0.24909 | High | High | Low | 1315 | 1187 | 0.13284 | 72.8646 | 0.8163%
COARSEGOLD 210210610 | COARSEGOLD 2102 | YOSEMITE | 1.3639 | 10 | 100% | 0 | 1 | 100% | 100% | 0 | 0.13262 | 1 | 2.2478 | 0.29809 | High | High | Medium | 1238 | 1188 | 0.13262 | 72.7318 | 0.8148%
DOBBINS 110169722 | DOBBINS 1101 | SIERRA | 6.6325 | 10 | 87.38% | 1 | 4 | 100% | 93.4% | 1 | 0.13241 | 1 | 2.5845 | 0.34221 | High | High | Medium | 1187 | 1189 | 0.13241 | 72.5992 | 0.8133%
OLEMA 1101416 | OLEMA 1101 | NORTH BAY | 15.842 | 82.0626 | 5.587% | 9 | 6 | 97.77% | 72.25% | 1 | 0.13235 | 1 | 2.6915 | 0.35623 | High | High | Medium | 1180 | 1190 | 0.13235 | 72.4668 | 0.8118%
CAMP EVERS 210612840 | CAMP EVERS 2106 | CENTRAL COAST | 4.0602 | 32.5066 | 59.36% | 5 | 0 | 100% | 100% | 0 | 0.13232 | 1 | 3.057 | 0.40448 | High | High | Medium | 1142 | 1191 | 0.13232 | 72.3344 | 0.8104%
CALPINE 1144CB | CALPINE 1144 | SONOMA | 26.2964 | 85.7305 | 55.05% | 0 | 0 | 100% | 92.09% | 0 | 0.1323 | 1 | 1.8843 | 0.24929 | High | High | Low | 1314 | 1192 | 0.1323 | 72.2021 | 0.8089%
ECHO SUMMIT 11018922 | ECHO SUMMIT 1101 | (blank) | 2.2784 | 12.8457 | 99.62% | 6 | 2 | 64% | 0% | 0 | 0.13221 | 1 | 1.3369 | 0.17676 | High | High | Low | 1477 | 1193 | 0.13221 | 72.0698 | 0.8074%
GIRVAN 11011330 | GIRVAN 1101 | NORTH VALLEY | 31.2468 | 42.7568 | 99.67% | 0 | 4 | 100% | 24.65% | 1 | 0.13164 | 1 | 1.4253 | 0.18763 | High | High | Low | 1446 | 1194 | 0.13164 | 71.9376 | 0.8059%
SAN LUIS OBISPO 1107V62 | SAN LUIS OBISPO 1107 | LOS PADRES | 6.9341 | 31.5234 | 48.48% | 0 | 11 | 100% | 70.79% | 1 | 0.1315 | 1 | 2.1877 | 0.28768 | High | High | Low | 1251 | 1195 | 0.1315 | 71.806 | 0.8044%
SAN JOAQUIN #3 1102CB | SAN JOAQUIN #3 1102 | YOSEMITE | 9.6989 | 12.3012 | 62.24% | 3 | 14 | 100% | 56.8% | 0 | 0.1304 | 1 | 1.3465 | 0.17559 | High | High | Low | 1479 | 1196 | 0.1304 | 71.6745 | 0.803%
OAKLAND X 1104 | OAKLAND X 1104 | EAST BAY | 0.11526 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 4.2748 | 0.55668 | High | High | High | 1054 | 1197 | 0.13022 | 71.5441 | 0.8015%
CENTERVILLE 1101 | CENTERVILLE 1101 | NORTH VALLEY | 0.0017292 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 3.4526 | 0.44961 | High | High | High | 1112 | 1197 | 0.13022 | 71.4138 | 0.8%
GREEN VALLEY 21011645 | GREEN VALLEY 2101 | CENTRAL COAST | 0.48374 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 3.1056 | 0.40442 | High | High | High | 1143 | 1197 | 0.13022 | 71.2836 | 0.7986%
SCE VEGAS 1701CB | SCE VEGAS 1701 | LOS PADRES | 0.17032 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 2.0729 | 0.26993 | High | High | Low | 1284 | 1197 | 0.13022 | 71.1534 | 0.7971%
WILLOW CREEK 11032936 | WILLOW CREEK 1103 | HUMBOLDT | 32.9597 | 79.3849 | 82.84% | 19 | 24 | 100% | 0% | 0 | 0.12943 | 1 | 1.1228 | 0.14532 | High | High | Low | 1574 | 1201 | 0.12943 | 71.0232 | 0.7957%
GEYSERVILLE 1102484 | GEYSERVILLE 1102 | SONOMA | 33.3601 | 63.5348 | 83.52% | 3 | 7 | 68.39% | 43.97% | 0 | 0.12892 | 1 | 1.3254 | 0.17087 | High | High | Low | 1498 | 1202 | 0.12892 | 70.8937 | 0.7942%
MORAGA 1101CB | MORAGA 1101 | DIABLO | 6.145 | 55.6277 | 5.196% | 2 | 13 | 81.97% | 88.05% | 0 | 0.12886 | 1 | 3.3628 | 0.43333 | High | High | High | 1125 | 1203 | 0.12886 | 70.7648 | 0.7928%
HALSEY 110239104 | HALSEY 1102 | SIERRA | 30.6401 | 10.3566 | 73.57% | 9 | 18 | 100% | 0% | 0 | 0.1288 | 1 | 2.0038 | 0.25809 | High | High | Low | 1301 | 1204 | 0.1288 | 70.636 | 0.7913%
HARTLEY 1101471 | HARTLEY 1101 | HUMBOLDT | 0.38585 | 10 | 33.51% | 0 | 1 | 31.01% | 0% | 0 | 0.0085975 | 14.9507 | 2.5669 | 0.32994 | Low | Low | Medium | 1198 | 1205 | 0.12854 | 70.5072 | 0.7899%
PARADISE 11032534 | PARADISE 1103 | NORTH VALLEY | 4.7177 | 10 | 61.75% | 3 | 6 | 100% | 100% | 0 | 0.12837 | 1 | 3.8138 | 0.48959 | High | High | High | 1090 | 1206 | 0.12837 | 70.3786 | 0.7884%
APPLE HILL 11038412 | APPLE HILL 1103 | SIERRA | 20.0804 | 56.3777 | 98.03% | 4 | 10 | 100% | 56.18% | 1 | 0.12834 | 1 | 1.8505 | 0.23749 | High | High | Low | 1343 | 1207 | 0.12834 | 70.2503 | 0.787%
OAKHURST 110110090 | OAKHURST 1101 | YOSEMITE | 44.1093 | 32.6301 | 93.91% | 4 | 19 | 100% | 7.446% | 0 | 0.12831 | 1 | 2.3192 | 0.29759 | High | High | Medium | 1239 | 1208 | 0.12831 | 70.1219 | 0.7856%
PAUL SWEET 210411074 | PAUL SWEET 2104 | CENTRAL COAST | 2.9891 | 10 | 96.78% | 2 | 0 | 97.58% | 100% | 0 | 0.12749 | 1 | 3.7533 | 0.47849 | High | High | High | 1098 | 1209 | 0.12749 | 69.9936 | 0.7841%
PAUL SWEET 21068091 | PAUL SWEET 2106 | CENTRAL COAST | 6.0187 | 18.6502 | 32.26% | 14 | 1 | 100% | 100% | 0 | 0.12726 | 1 | 2.9537 | 0.37589 | High | High | Medium | 1163 | 1210 | 0.12726 | 69.8661 | 0.7827%
SAN LUIS OBISPO 1107V02 | SAN LUIS OBISPO 1107 | LOS PADRES | 17.85 | 46.8397 | 49.77% | 4 | 7 | 97.96% | 39.87% | 0 | 0.12708 | 1 | 2.273 | 0.28886 | High | High | Medium | 1250 | 1211 | 0.12708 | 69.7389 | 0.7813%
VIEJO 22019704 | VIEJO 2201 | CENTRAL COAST | 1.0374 | 10 | 50.89% | 1 | 2 | 40.52% | 0% | 0 | 0.011266 | 11.2183 | 3.1826 | 0.40224 | Low | Low | High | 1146 | 1212 | 0.12638 | 69.6118 | 0.7799%
PLACERVILLE 210619732 | PLACERVILLE 2106 | SIERRA | 9.0659 | 10 | 43.47% | 3 | 13 | 100% | 82.12% | 1 | 0.12525 | 1 | 3.1037 | 0.38874 | High | High | High | 1156 | 1213 | 0.12525 | 69.4854 | 0.7784%
MONTE RIO 11131067 | MONTE RIO 1113 | SONOMA | 0.80536 | 36.8006 | 36.57% | 2 | 0 | 100% | 100% | 0 | 0.12505 | 1 | 3.1062 | 0.38843 | High | High | High | 1157 | 1214 | 0.12505 | 69.3601 | 0.777%
BELL 1107CB | BELL 1107 | SIERRA | 0.084936 | 10 | 100% | 0 | 1 | 2.211% | 0% | 0 | 0.011123 | 11.2183 | 2.8137 | 0.35111 | Low | Low | Medium | 1183 | 1215 | 0.12478 | 69.2351 | 0.7756%
DEL MONTE 21029060 | DEL MONTE 2102 | CENTRAL COAST | 0.0023123 | 10 | 0% | 0 | 0 | 0.0258% | 0% | 0 | 0.0046992 | 26.5534 | 4.6351 | 0.57837 | Low | Low | High | 1042 | 1216 | 0.12478 | 69.1103 | 0.7742%
VINEYARD 2107MR332 | VINEYARD 2107 | MISSION | 0.086505 | 10 | 100% | 1 | 0 | 2.473% | 0% | 0 | 0.011067 | 11.2183 | 3.0685 | 0.38096 | Low | Low | Medium | 1160 | 1217 | 0.12415 | 68.9855 | 0.7728%
VIEJO 22029112 | VIEJO 2202 | CENTRAL COAST | 0.78302 | 10 | 22.17% | 1 | 0 | 23.74% | 0% | 0 | 0.008258 | 14.9507 | 4.4379 | 0.54792 | Low | Low | High | 1060 | 1218 | 0.12346 | 68.8614 | 0.7714%
HIGGINS 11102408 | HIGGINS 1110 | SIERRA | 35.5285 | 10.5577 | 99.97% | 6 | 7 | 100% | 0% | 0 | 0.12315 | 1 | 2.7776 | 0.34207 | High | High | Medium | 1188 | 1219 | 0.12315 | 68.7379 | 0.7701%
SAN RAMON 2117CB | SAN RAMON 2117 | MISSION | 0.44721 | 10 | 0% | 0 | 0 | 26.74% | 0% | 0 | 0.0061326 | 19.9979 | 3.8316 | 0.46991 | Low | Low | High | 1102 | 1220 | 0.12264 | 68.6147 | 0.7687%
WYANDOTTE 1109CB | WYANDOTTE 1109 | NORTH VALLEY | 2.5841 | 10 | 31.89% | 0 | 1 | 27.38% | 0% | 0 | 0.0081836 | 14.9507 | 4.3025 | 0.52641 | Low | Low | High | 1073 | 1221 | 0.12235 | 68.4921 | 0.7673%
ORO FINO 11022236 | ORO FINO 1102 | NORTH VALLEY | 2.5402 | 88.3654 | 18.46% | 0 | 3 | 100% | 100% | 0 | 0.12209 | 1 | 2.1142 | 0.25812 | High | High | Low | 1300 | 1222 | 0.12209 | 68.3698 | 0.7659%
SAN RAFAEL 11071276 | SAN RAFAEL 1107 | NORTH BAY | 3.842 | 10 | 17.39% | 6 | 6 | 100% | 100% | 0 | 0.12189 | 1 | 4.3125 | 0.52565 | High | High | High | 1075 | 1223 | 0.12189 | 68.2477 | 0.7646%
HORSESHOE 11011682 | HORSESHOE 1101 | SIERRA | 1.1361 | 10 | 70.68% | 0 | 0 | 11.64% | 0% | 0 | 0.010746 | 11.2183 | 3.9722 | 0.47887 | Low | Low | High | 1097 | 1224 | 0.12055 | 68.1258 | 0.7632%
WILLOW CREEK 110347966 | WILLOW CREEK 1103 | HUMBOLDT | 17.0216 | 48.5214 | 76.15% | 20 | 19 | 100% | 0% | 0 | 0.11952 | 1 | 1.1197 | 0.13384 | High | High | Low | 1611 | 1225 | 0.11952 | 68.0052 | 0.7619%
CLOVERDALE 1102570 | CLOVERDALE 1102 | SONOMA | 17.3117 | 48.3271 | 69.88% | 1 | 6 | 81.35% | 95.94% | 0 | 0.11928 | 1 | 1.824 | 0.21757 | High | High | Low | 1377 | 1226 | 0.11928 | 67.8857 | 0.7605%
MIRABEL 110257840 | MIRABEL 1102 | SONOMA | 2.5892 | 51.5846 | 26.12% | 5 | 1 | 100% | 100% | 0 | 0.11884 | 1 | 3.0442 | 0.36177 | High | High | Medium | 1175 | 1227 | 0.11884 | 67.7664 | 0.7592%
GRASS VALLEY 11032180 | GRASS VALLEY 1103 | SIERRA | 44.2075 | 22.3739 | 98.77% | 3 | 16 | 100% | 0% | 0 | 0.11816 | 1 | 2.6203 | 0.30961 | High | High | Medium | 1224 | 1228 | 0.11816 | 67.6476 | 0.7578%
VOLTA 110185234 | VOLTA 1101 | NORTH VALLEY | 7.9136 | 44.4652 | 95.46% | 10 | 12 | 100% | 0% | 0 | 0.11805 | 1 | 0.16495 | 0.019472 | High | High | Low | 3018 | 1229 | 0.11805 | 67.5294 | 0.7565%
DIAMOND SPRINGS 11057722 | DIAMOND SPRINGS 1105 | SIERRA | 59.1027 | 30.4266 | 87.61% | 10 | 7 | 94.99% | 35.49% | 0 | 0.11755 | 1 | 2.1264 | 0.24995 | High | High | Low | 1311 | 1230 | 0.11755 | 67.4114 | 0.7552%
PUEBLO 210378504 | PUEBLO 2103 | NORTH BAY | 7.9718 | 44.4313 | 84.9% | 7 | 4 | 65.86% | 87.65% | 1 | 0.11699 | 1 | 3.0008 | 0.35106 | High | High | Medium | 1184 | 1231 | 0.11699 | 67.2938 | 0.7539%
OTTER 1102CB | OTTER 1102 | CENTRAL COAST | 6.6866 | 58.389 | 0% | 3 | 0 | 98.35% | 55.62% | 1 | 0.11663 | 1 | 1.6628 | 0.19393 | High | High | Low | 1425 | 1232 | 0.11663 | 67.1768 | 0.7526%
BIG BASIN 110210254 | BIG BASIN 1102 | CENTRAL COAST | 2.1303 | 79.74 | 23.5% | 0 | 1 | 100% | 100% | 1 | 0.11586 | 1 | 2.4798 | 0.28731 | High | High | Medium | 1252 | 1233 | 0.11586 | 67.0602 | 0.7513%
PARADISE 11032488 | PARADISE 1103 | NORTH VALLEY | 3.2215 | 10 | 53.79% | 1 | 2 | 100% | 95.34% | 0 | 0.11569 | 1 | 3.766 | 0.43568 | High | High | High | 1123 | 1234 | 0.11569 | 66.9443 | 0.75%
PUEBLO 1105696 | PUEBLO 1105 | NORTH BAY | 20.5418 | 62.3545 | 78.14% | 5 | 4 | 69.81% | 0% | 0 | 0.11569 | 1 | 2.755 | 0.31872 | High | High | Medium | 1210 | 1235 | 0.11569 | 66.8286 | 0.7487%
OAKLAND K 1104CR204 | OAKLAND K 1104 | EAST BAY | 3.7332 | 23.8088 | 27.59% | 6 | 1 | 100% | 100% | 0 | 0.11562 | 1 | 4.1768 | 0.48293 | High | High | High | 1093 | 1236 | 0.11562 | 66.713 | 0.7474%
APPLE HILL 21028372 | APPLE HILL 2102 | SIERRA | 56.1866 | 51.1532 | 100% | 7 | 2 | 89.5% | 31.4% | 1 | 0.11526 | 1 | 1.8245 | 0.2103 | High | High | Low | 1394 | 1237 | 0.11526 | 66.5973 | 0.7461%
TASSAJARA 2112CB | TASSAJARA 2112 | DIABLO | 0.3541 | 10 | 9.426% | 1 | 0 | 26.89% | 0% | 0 | 0.0076765 | 14.9507 | 3.8616 | 0.4432 | Low | Low | High | 1118 | 1238 | 0.11477 | 66.4821 | 0.7448%
VOLTA 110297816 | VOLTA 1102 | NORTH VALLEY | 5.2578 | 25.9131 | 100% | 2 | 2 | 100% | 80.28% | 1 | 0.11476 | 1 | 1.6244 | 0.18643 | High | High | Low | 1450 | 1239 | 0.11476 | 66.3673 | 0.7435%
MORGAN HILL 2105XR176 | MORGAN HILL 2105 | SAN JOSE | 18.5618 | 37.9512 | 61.14% | 2 | 13 | 67.38% | 10.57% | 0 | 0.11466 | 1 | 2.5892 | 0.29688 | High | High | Medium | 1242 | 1240 | 0.11466 | 66.2525 | 0.7422%
EMERALD LAKE 0401CB | EMERALD LAKE 0401 | PENINSULA | 15.5314 | 21.1198 | 27.73% | 5 | 20 | 73.41% | 27.29% | 1 | 0.11416 | 1 | 4.5679 | 0.52148 | High | High | High | 1078 | 1241 | 0.11416 | 66.1379 | 0.7409%
MONROE 210392868 | MONROE 2103 | SONOMA | 0.69734 | 10 | 73.35% | 0 | 3 | 74% | 100% | 0 | 0.11412 | 1 | 3.3766 | 0.38534 | High | High | High | 1159 | 1242 | 0.11412 | 66.0237 | 0.7397%
MIRABEL 1102841 | MIRABEL 1102 | SONOMA | 0.78827 | 21.9552 | 18.73% | 8 | 3 | 100% | 100% | 0 | 0.11386 | 1 | 2.9577 | 0.33677 | High | High | Medium | 1191 | 1243 | 0.11386 | 65.9096 | 0.7384%
HOOPA 11013174 | HOOPA 1101 | HUMBOLDT | 17.6485 | 69.5085 | 99.93% | 19 | 10 | 80.04% | 0% | 0 | 0.11313 | 1 | 1.1672 | 0.13204 | High | High | Low | 1620 | 1244 | 0.11313 | 65.7957 | 0.7371%
LAURELES 11112020 | LAURELES 1111 | CENTRAL COAST | 33.1343 | 48.734 | 70.7% | 2 | 9 | 100% | 9.9% | 1 | 0.11304 | 1 | 1.9922 | 0.2252 | High | High | Low | 1361 | 1245 | 0.11304 | 65.6826 | 0.7358%
JESSUP 1103CB | JESSUP 1103 | NORTH VALLEY | 0.3876 | 22.4131 | 79.44% | 0 | 0 | 2.712% | 0% | 0 | 0.010068 | 11.2183 | 2.4954 | 0.28184 | Low | Low | Medium | 1259 | 1246 | 0.11295 | 65.5696 | 0.7346%
KANAKA 1101CB | KANAKA 1101 | NORTH VALLEY | 4.6774 | 55.1611 | 80.24% | 0 | 1 | 100% | 79.67% | 1 | 0.11271 | 1 | 1.9968 | 0.22505 | High | High | Low | 1362 | 1247 | 0.11271 | 65.4566 | 0.7333%
HALF MOON BAY 1101CB | HALF MOON BAY 1101 | PENINSULA | 8.298 | 59.005 | 12.7% | 3 | 2 | 59.24% | 75.84% | 1 | 0.11209 | 1 | 3.754 | 0.42078 | High | High | High | 1132 | 1248 | 0.11209 | 65.3439 | 0.732%
SILVERADO 2102636 | SILVERADO 2102 | NORTH BAY | 3.9682 | 44.4482 | 89.35% | 2 | 0 | 70.53% | 80.46% | 1 | 0.11193 | 1 | 3.6989 | 0.41401 | High | High | High | 1136 | 1249 | 0.11193 | 65.2318 | 0.7308%
CURTIS 17039210 | CURTIS 1703 | YOSEMITE | 23.0078 | 62.9555 | 99.96% | 11 | 7 | 100% | 0% | 0 | 0.11179 | 1 | 2.775 | 0.3102 | High | High | Medium | 1222 | 1250 | 0.11179 | 65.1199 | 0.7295%
CENTERVILLE 11011243 | CENTERVILLE 1101 | NORTH VALLEY | 5.1549 | 10 | 65.95% | 0 | 5 | 100% | 100% | 0 | 0.11154 | 1 | 3.2195 | 0.35911 | High | High | High | 1178 | 1251 | 0.11154 | 65.0081 | 0.7283%
LAURELES 1111432 | LAURELES 1111 | CENTRAL COAST | 49.1946 | 74.7913 | 100% | 10 | 10 | 100% | 0% | 0 | 0.11153 | 1 | 1.687 | 0.18815 | High | High | Low | 1444 | 1252 | 0.11153 | 64.8966 | 0.727%
WEST POINT 1101CB | WEST POINT 1101 | STOCKTON | 4.7054 | 80.5028 | 15.54% | 1 | 1 | 100% | 100% | 0 | 0.11111 | 1 | 2.5021 | 0.27801 | High | High | Medium | 1265 | 1253 | 0.11111 | 64.785 | 0.7258%
FITCH MOUNTAIN 1111CB | FITCH MOUNTAIN 1111 | SONOMA | 0.55902 | 10 | 52% | 0 | 0 | 3.182% | 0% | 0 | 0.0074291 | 14.9507 | 2.5563 | 0.28393 | Low | Low | Medium | 1256 | 1254 | 0.11107 | 64.6739 | 0.7245%
CLARKSVILLE 2105CB | CLARKSVILLE 2105 | SIERRA | 0.54433 | 10 | 0% | 0 | 0 | 45.8% | 0% | 0 | 0.0074141 | 14.9507 | 3.5177 | 0.38992 | Low | Low | High | 1153 | 1255 | 0.11085 | 64.5629 | 0.7233%
SONOMA 1102118 | SONOMA 1102 | SONOMA | 5.4359 | 22.1228 | 81.08% | 2 | 7 | 71.73% | 100% | 0 | 0.11084 | 1 | 4.0423 | 0.44806 | High | High | High | 1114 | 1256 | 0.11084 | 64.452 | 0.722%
CORNING 11021622 | CORNING 1102 | NORTH VALLEY | 34.031 | 83.6384 | 99.67% | 1 | 6 | 100% | 0% | 0 | 0.11037 | 1 | 1.3788 | 0.15218 | High | High | Low | 1547 | 1257 | 0.11037 | 64.3412 | 0.7208%
MOUNTAIN QUARRIES 21011102 | MOUNTAIN QUARRIES 2101 | SIERRA | 44.4218 | 34.6112 | 86.6% | 0 | 15 | 100% | 0% | 0 | 0.11033 | 1 | 1.9411 | 0.21417 | High | High | Low | 1382 | 1258 | 0.11033 | 64.2308 | 0.7196%
MIDDLETOWN 1103CB | MIDDLETOWN 1103 | HUMBOLDT | 0.052982 | 70.6148 | 0% | 0 | 0 | 32.86% | 0% | 0 | 0.009835 | 11.2183 | 2.601 | 0.28698 | Low | Low | Medium | 1253 | 1259 | 0.11033 | 64.1205 | 0.7183%
PENNGROVE 1101554 | PENNGROVE 1101 | SONOMA | 0.80578 | 23.6637 | 31.41% | 1 | 1 | 6.241% | 0% | 0 | 0.0073444 | 14.9507 | 2.9765 | 0.32683 | Low | Low | Medium | 1202 | 1260 | 0.1098 | 64.0101 | 0.7171%
GARBERVILLE 11011514 | GARBERVILLE 1101 | HUMBOLDT | 14.7707 | 71.7705 | 51.17% | 15 | 7 | 100% | 0% | 0 | 0.10959 | 1 | 0.62013 | 0.067963 | High | High | Low | 2062 | 1261 | 0.10959 | 63.9003 | 0.7159%
NARROWS 21011202 | NARROWS 2101 | SIERRA | 45.5016 | 16.7658 | 94.84% | 2 | 35 | 100% | 0% | 0 | 0.10949 | 1 | 2.2156 | 0.24258 | High | High | Low | 1331 | 1262 | 0.10949 | 63.7907 | 0.7146%
CEDAR CREEK 11011608 | CEDAR CREEK 1101 | NORTH VALLEY | 33.3899 | 31.7775 | 100% | 3 | 12 | 100% | 36.09% | 1 | 0.10917 | 1 | 0.50558 | 0.055196 | High | High | Low | 2256 | 1263 | 0.10917 | 63.6812 | 0.7134%
HOOPA 110182542 | HOOPA 1101 | HUMBOLDT | 9.9783 | 60.316 | 90.42% | 13 | 6 | 65.67% | 0% | 0 | 0.10839 | 1 | 2.3143 | 0.25085 | High | High | Medium | 1309 | 1264 | 0.10839 | 63.5721 | 0.7122%
PARADISE 11042034 | PARADISE 1104 | NORTH VALLEY | 10.6989 | 15.2166 | 88.93% | 0 | 6 | 94.14% | 86.31% | 1 | 0.10808 | 1 | 3.7081 | 0.40077 | High | High | High | 1147 | 1265 | 0.10808 | 63.4637 | 0.711%
COARSEGOLD 2102383092 | COARSEGOLD 2102 | YOSEMITE | 0.3809 | 10 | 73.97% | 0 | 0 | 100% | 100% | 0 | 0.10776 | 1 | 1.874 | 0.20194 | High | High | Low | 1407 | 1266 | 0.10776 | 63.3556 | 0.7098%
BIG BASIN 110212124 | BIG BASIN 1102 | CENTRAL COAST | 4.2617 | 10 | 33.1% | 2 | 2 | 100% | 100% | 0 | 0.1076 | 1 | 2.589 | 0.27858 | High | High | Medium | 1262 | 1267 | 0.1076 | 63.2478 | 0.7086%
SHINGLE SPRINGS 211051790 | SHINGLE SPRINGS 2110 | SIERRA | 8.0868 | 16.0955 | 60.72% | 1 | 8 | 93.48% | 72.08% | 0 | 0.10718 | 1 | 3.0513 | 0.32703 | High | High | Medium | 1201 | 1268 | 0.10718 | 63.1402 | 0.7074%
STILLWATER 11011320 | STILLWATER 1101 | NORTH VALLEY | 18.8372 | 23.2893 | 80.24% | 9 | 10 | 93.78% | 0% | 0 | 0.10603 | 1 | 1.956 | 0.2074 | High | High | Low | 1400 | 1269 | 0.10603 | 63.0331 | 0.7061%
GARBERVILLE 110197300 | GARBERVILLE 1101 | HUMBOLDT | 14.1538 | 63.6884 | 85.32% | 13 | 2 | 100% | 0% | 0 | 0.1059 | 1 | 0.026166 | 0.0027709 | High | High | Low | 3178 | 1270 | 0.1059 | 62.927 | 0.705%
STANISLAUS 17017144 | STANISLAUS 1701 | YOSEMITE | 4.4552 | 18.8557 | 79.41% | 0 | 8 | 100% | 0% | 0 | 0.10581 | 1 | 3.3929 | 0.359 | High | High | High | 1179 | 1271 | 0.10581 | 62.8211 | 0.7038%
BRUNSWICK 11067099 | BRUNSWICK 1106 | SIERRA | 7.5715 | 32.7231 | 90.35% | 0 | 3 | 100% | 52.26% | 0 | 0.1055 | 1 | 2.6802 | 0.28277 | High | High | Medium | 1258 | 1272 | 0.1055 | 62.7153 | 0.7026%
SAN LUIS OBISPO 1101V12 | SAN LUIS OBISPO 1101 | LOS PADRES | 21.0121 | 75.506 | 48.74% | 1 | 1 | 99.72% | 49% | 1 | 0.10534 | 1 | 2.27 | 0.23913 | High | High | Medium | 1338 | 1273 | 0.10534 | 62.6098 | 0.7014%
AUBERRY 1101R2845 | AUBERRY 1101 | FRESNO | 17.7605 | 28.7565 | 100% | 4 | 13 | 100% | 0% | 0 | 0.10532 | 1 | 1.8477 | 0.19461 | High | High | Low | 1422 | 1274 | 0.10532 | 62.5045 | 0.7002%
MARTELL 110191216 | MARTELL 1101 | STOCKTON | 41.3413 | 10.8803 | 100% | 3 | 13 | 100% | 0% | 0 | 0.10514 | 1 | 2.4019 | 0.25253 | High | High | Medium | 1307 | 1275 | 0.10514 | 62.3992 | 0.699%
MOUNTAIN QUARRIES 210192474 | MOUNTAIN QUARRIES 2101 | SIERRA | 14.6687 | 46.984 | 70.43% | 1 | 2 | 94.19% | 51.74% | 0 | 0.10478 | 1 | 2.4996 | 0.2619 | High | High | Medium | 1293 | 1276 | 0.10478 | 62.294 | 0.6979%
MONTE RIO 11135026 | MONTE RIO 1113 | SONOMA | 1.8374 | 45.7535 | 31.21% | 4 | 1 | 100% | 100% | 0 | 0.1045 | 1 | 3.3938 | 0.35465 | High | High | High | 1182 | 1277 | 0.1045 | 62.1892 | 0.6967%
SANTA YNEZ 1101Y52 | SANTA YNEZ 1101 | LOS PADRES | 18.8234 | 75.9887 | 74.53% | 0 | 5 | 76.28% | 53.44% | 1 | 0.10447 | 1 | 2.1391 | 0.22348 | High | High | Low | 1364 | 1278 | 0.10447 | 62.0847 | 0.6955%
COARSEGOLD 21045300 | COARSEGOLD 2104 | YOSEMITE | 37.3624 | 19.4525 | 89.47% | 1 | 28 | 100% | 0% | 0 | 0.10447 | 1 | 1.9069 | 0.19922 | High | High | Low | 1417 | 1279 | 0.10447 | 61.9803 | 0.6944%
PUEBLO 11041304 | PUEBLO 1104 | NORTH BAY | 19.9743 | 65.3191 | 45.92% | 2 | 4 | 100% | 0% | 0 | 0.10431 | 1 | 2.809 | 0.29302 | High | High | Medium | 1245 | 1280 | 0.10431 | 61.8758 | 0.6932%
AUBERRY 1101R2838 | AUBERRY 1101 | FRESNO | 20.2113 | 19.1577 | 100% | 5 | 21 | 100% | 0% | 0 | 0.10363 | 1 | 2.0481 | 0.21224 | High | High | Low | 1389 | 1281 | 0.10363 | 61.7715 | 0.692%
SAN LUIS OBISPO 1108V92 | SAN LUIS OBISPO 1108 | LOS PADRES | 0.46755 | 10 | 74.28% | 0 | 0 | 6.559% | 0% | 0 | 0.0092193 | 11.2183 | 3.5147 | 0.36351 | Low | Low | High | 1171 | 1282 | 0.10343 | 61.6679 | 0.6909%
CLAYTON 2215CB | CLAYTON 2215 | DIABLO | 2.6028 | 67.9246 | 0.2184% | 0 | 2 | 23.77% | 0% | 0 | 0.0092153 | 11.2183 | 3.5872 | 0.37085 | Low | Low | High | 1165 | 1283 | 0.10338 | 61.5644 | 0.6897%
BANGOR 11011958 | BANGOR 1101 | NORTH VALLEY | 33.6731 | 10.1792 | 87.16% | 3 | 30 | 100% | 0% | 0 | 0.10317 | 1 | 2.7724 | 0.28603 | High | High | Medium | 1254 | 1284 | 0.10317 | 61.461 | 0.6885%
CALAVERAS CEMENT 1101502 | CALAVERAS CEMENT 1101 | STOCKTON | 38.3009 | 27.6645 | 90.32% | 2 | 8 | 92.84% | 0% | 0 | 0.10314 | 1 | 2.0117 | 0.20748 | High | High | Low | 1399 | 1285 | 0.10314 | 61.3579 | 0.6874%
CLARKSVILLE 2110CB | CLARKSVILLE 2110 | SIERRA | 0.17765 | 10 | 0% | 0 | 0 | 9.133% | 0% | 0 | 0.005146 | 19.9979 | 3.4965 | 0.35982 | Low | Low | High | 1176 | 1286 | 0.10291 | 61.2547 | 0.6862%
CLARK ROAD 11022582 | CLARK ROAD 1102 | NORTH VALLEY | 20.3761 | 33.4275 | 100% | 2 | 6 | 97.24% | 8.705% | 1 | 0.10279 | 1 | 3.0257 | 0.311 | High | High | Medium | 1221 | 1287 | 0.10279 | 61.1518 | 0.6851%
CALISTOGA 1102769230 | CALISTOGA 1102 | NORTH BAY | 9.3152 | 56.0979 | 70.25% | 3 | 0 | 54.25% | 96.26% | 0 | 0.10199 | 1 | 2.7108 | 0.27647 | High | High | Medium | 1270 | 1288 | 0.10199 | 61.049 | 0.6839%
CLAYTON 2212Y504R | CLAYTON 2212 | DIABLO | 11.7508 | 28.9647 | 42.97% | 1 | 6 | 100% | 29.53% | 1 | 0.10152 | 1 | 3.5819 | 0.36362 | High | High | High | 1170 | 1289 | 0.10152 | 60.9471 | 0.6828%
RED BLUFF 11011556 | RED BLUFF 1101 | NORTH VALLEY | 35.2007 | 32.6588 | 100% | 1 | 11 | 88.02% | 0% | 0 | 0.10148 | 1 | 1.7409 | 0.17666 | High | High | Low | 1478 | 1290 | 0.10148 | 60.8455 | 0.6816%
CURTIS 170390320 | CURTIS 1703 | YOSEMITE | 27.855 | 17.0394 | 100% | 4 | 21 | 100% | 0% | 0 | 0.10108 | 1 | 0.97587 | 0.098641 | High | High | Low | 1780 | 1291 | 0.10108 | 60.7441 | 0.6805%
RIO DELL 1102CB | RIO DELL 1102 | HUMBOLDT | 0.14635 | 60 | 0% | 0 | 0 | 2.061% | 0% | 0 | 0.0067382 | 14.9507 | 2.7458 | 0.27662 | Low | Low | Medium | 1269 | 1292 | 0.10074 | 60.643 | 0.6794%
DIAMOND SPRINGS 1103 | DIAMOND SPRINGS 1103 | SIERRA | 0.10469 | 10 | 100% | 0 | 0 | 70.96% | 100% | 0 | 0.10065 | 1 | 2.7444 | 0.27622 | High | High | Medium | 1271 | 1293 | 0.10065 | 60.5422 | 0.6782%
CEDAR CREEK 11011656 | CEDAR CREEK 1101 | NORTH VALLEY | 32.2585 | 60.8127 | 100% | 10 | 9 | 100% | 0% | 0 | 0.10049 | 1 | 0.70111 | 0.070453 | High | High | Low | 2039 | 1294 | 0.10049 | 60.4416 | 0.6771%
PETALUMA C 1109128 | PETALUMA C 1109 | SONOMA | 20.216 | 67.8419 | 37.87% | 1 | 18 | 85.88% | 0% | 0 | 0.1003 | 1 | 2.9612 | 0.29701 | High | High | Medium | 1241 | 1295 | 0.1003 | 60.3411 | 0.676%
CAMP EVERS 210694770 | CAMP EVERS 2106 | CENTRAL COAST | 2.6769 | 10 | 36.19% | 10 | 8 | 66.11% | 100% | 0 | 0.09995 | 1 | 2.7268 | 0.27255 | High | High | Medium | 1277 | 1296 | 0.09995 | 60.2408 | 0.6749%
CAMP EVERS 210410442 | CAMP EVERS 2104 | CENTRAL COAST | 5.2532 | 33.0345 | 51.92% | 6 | 3 | 50.36% | 93.05% | 0 | 0.099232 | 1 | 2.9332 | 0.29106 | High | High | Medium | 1246 | 1297 | 0.099232 | 60.1409 | 0.6737%
VIEJO 22029118 | VIEJO 2202 | CENTRAL COAST | 0.57077 | 10 | 0.8969% | 1 | 0 | 19.02% | 0% | 0 | 0.0066199 | 14.9507 | 4.29 | 0.42459 | Low | Low | High | 1126 | 1298 | 0.098972 | 60.0416 | 0.6726%
CALPINE 1144304 | CALPINE 1144 | SONOMA | 0.046375 | 85 | 0% | 0 | 0 | 100% | 100% | 0 | 0.098754 | 1 | 1.8471 | 0.18241 | High | High | Low | 1463 | 1299 | 0.098754 | 59.9427 | 0.6715%
BOLINAS 110137034 | BOLINAS 1101 | NORTH BAY | 4.5303 | 84.6023 | 6.363% | 1 | 1 | 100% | 94.68% | 0 | 0.098509 | 1 | 3.0991 | 0.30529 | High | High | High | 1230 | 1300 | 0.098509 | 59.8439 | 0.6704%
CENTERVILLE 11012592 | CENTERVILLE 1101 | NORTH VALLEY | 6.3933 | 51.1304 | 7.659% | 2 | 0 | 100% | 100% | 0 | 0.098005 | 1 | 3.2954 | 0.32296 | High | High | High | 1205 | 1301 | 0.098005 | 59.7454 | 0.6693%
HALF MOON BAY 11018902 | HALF MOON BAY 1101 | PENINSULA | 14.8934 | 73.1287 | 41.51% | 11 | 3 | 82.58% | 40.17% | 0 | 0.097706 | 1 | 3.3332 | 0.32568 | High | High | High | 1203 | 1302 | 0.097706 | 59.6474 | 0.6682%
KANAKA 11011406 | KANAKA 1101 | NORTH VALLEY | 26.9635 | 16.7709 | 74.27% | 2 | 6 | 97.41% | 16.93% | 0 | 0.097652 | 1 | 1.8891 | 0.18448 | High | High | Low | 1459 | 1303 | 0.097652 | 59.5497 | 0.6671%
SILVERADO 2105616 | SILVERADO 2105 | NORTH BAY | 7.7876 | 45.8077 | 54.02% | 4 | 6 | 42.79% | 95.93% | 0 | 0.097353 | 1 | 3.0537 | 0.29728 | High | High | Medium | 1240 | 1304 | 0.097353 | 59.452 | 0.666%
COTTONWOOD 11011610 | COTTONWOOD 1101 | NORTH VALLEY | 38.431 | 59.7392 | 100% | 4 | 5 | 100% | 0% | 0 | 0.097181 | 1 | 1.3016 | 0.12649 | High | High | Low | 1638 | 1305 | 0.097181 | 59.3547 | 0.6649%
NEWBURG 11313446 | NEWBURG 1131 | HUMBOLDT | 0.24063 | 10 | 0% | 0 | 0 | 2.893% | 0% | 0 | 0.0048356 | 19.9979 | 2.3426 | 0.22653 | Low | Low | Medium | 1356 | 1306 | 0.096701 | 59.2575 | 0.6639%
CORRAL 11012128 | CORRAL 1101 | STOCKTON | 0.10849 | 55.3351 | 0% | 0 | 0 | 0.5187% | 0% | 0 | 0.0064285 | 14.9507 | 2.8084 | 0.26992 | Low | Low | Medium | 1285 | 1307 | 0.09611 | 59.1608 | 0.6628%
BIG BASIN 110211062 | BIG BASIN 1102 | CENTRAL COAST | 9.0842 | 63.1207 | 47.86% | 15 | 1 | 100% | 69.62% | 1 | 0.096095 | 1 | 2.6104 | 0.25085 | High | High | Medium | 1310 | 1308 | 0.096095 | 59.0647 | 0.6617%
CURTIS 17026008 | CURTIS 1702 | YOSEMITE | 17.4763 | 49.3908 | 89.43% | 4 | 7 | 100% | 47.18% | 0 | 0.095869 | 1 | 3.2494 | 0.31152 | High | High | High | 1218 | 1309 | 0.095869 | 58.9686 | 0.6606%
BELLEVUE 1102392 | BELLEVUE 1102 | SONOMA | 0.13708 | 10 | 0% | 0 | 0 | 2.019% | 0% | 0 | 0.0047936 | 19.9979 | 2.8755 | 0.27565 | Low | Low | Medium | 1272 | 1310 | 0.095862 | 58.8727 | 0.6595%
CAMP EVERS 21067603 | CAMP EVERS 2106 | CENTRAL COAST | 0.9357 | 10 | 57.8% | 0 | 0 | 100% | 100% | 0 | 0.095589 | 1 | 2.8433 | 0.27179 | High | High | Medium | 1279 | 1311 | 0.095589 | 58.7769 | 0.6585%
AUBERRY 1102R2850 | AUBERRY 1102 | FRESNO | 25.8464 | 30.8369 | 100% | 0 | 16 | 100% | 0% | 0 | 0.095456 | 1 | 1.8012 | 0.17193 | High | High | Low | 1492 | 1312 | 0.095456 | 58.6813 | 0.6574%
VACAVILLE 111112342 | VACAVILLE 1111 | SACRAMENTO | 0.015645 | 10 | 0% | 0 | 0 | 1.482% | 0% | 0 | 0.004768 | 19.9979 | 3.3367 | 0.31815 | Low | Low | High | 1211 | 1313 | 0.095349 | 58.5858 | 0.6563%
SANTA ROSA A 1107CB | SANTA ROSA A 1107 | SONOMA | 2.9541 | 10 | 71.96% | 6 | 3 | 60.44% | 100% | 0 | 0.095269 | 1 | 3.6663 | 0.34929 | High | High | High | 1185 | 1314 | 0.095269 | 58.4905 | 0.6553%
HIGHLANDS 110439458 | HIGHLANDS 1104 | HUMBOLDT | 0.83315 | 10 | 36.61% | 0 | 0 | 15.6% | 0% | 0 | 0.0084597 | 11.2183 | 2.8556 | 0.271 | Low | Low | Medium | 1281 | 1315 | 0.094904 | 58.3952 | 0.6542%
FORT BRAGG A 110231304 | FORT BRAGG A 1102 | HUMBOLDT | 21.5206 | 61.6048 | 34.35% | 17 | 8 | 100% | 0% | 0 | 0.094856 | 1 | 2.3985 | 0.22751 | High | High | Medium | 1353 | 1316 | 0.094856 | 58.3003 | 0.6531%
SAN RAFAEL 11081262 | SAN RAFAEL 1108 | NORTH BAY | 4.0586 | 23.1286 | 14.29% | 3 | 8 | 91.28% | 100% | 0 | 0.094261 | 1 | 4.7701 | 0.44963 | High | High | High | 1111 | 1317 | 0.094261 | 58.2054 | 0.6521%
BRYANT 0402CB | BRYANT 0402 | DIABLO | 1.2282 | 10 | 3.772% | 0 | 5 | 15.75% | 0% | 0 | 0.0062931 | 14.9507 | 3.572 | 0.33607 | Low | Low | High | 1192 | 1318 | 0.094086 | 58.1112 | 0.651%
NARROWS 2105CB | NARROWS 2105 | SIERRA | 35.605 | 11.8579 | 78.33% | 4 | 9 | 98.55% | 0% | 0 | 0.094041 | 1 | 2.7962 | 0.26296 | High | High | Medium | 1292 | 1319 | 0.094041 | 58.0171 | 0.65%
PARADISE 11032486 | PARADISE 1103 | NORTH VALLEY | 6.2013 | 10 | 48.71% | 9 | 1 | 91.06% | 100% | 0 | 0.093491 | 1 | 3.8754 | 0.36232 | High | High | High | 1173 | 1320 | 0.093491 | 57.923 | 0.6489%
FELTON 0401CB | FELTON 0401 | CENTRAL COAST | 2.2987 | 17.6192 | 4.577% | 5 | 0 | 89.41% | 100% | 0 | 0.093336 | 1 | 4.1567 | 0.38797 | High | High | High | 1158 | 1321 | 0.093336 | 57.8296 | 0.6479%
APPLE HILL 2102186912 | APPLE HILL 2102 | SIERRA | 48.9257 | 16.1646 | 100% | 9 | 3 | 96.19% | 0% | 0 | 0.093311 | 1 | 1.9754 | 0.18433 | High | High | Low | 1461 | 1322 | 0.093311 | 57.7362 | 0.6468%
DIAMOND SPRINGS 11039432 | DIAMOND SPRINGS 1103 | SIERRA | 17.0625 | 19.7634 | 81.43% | 3 | 12 | 84.57% | 8.24% | 1 | 0.093192 | 1 | 2.7267 | 0.2541 | High | High | Medium | 1303 | 1323 | 0.093192 | 57.6429 | 0.6458%
CALPINE 1144276-G | CALPINE 1144 | SONOMA | 0.014761 | 75 | 0% | 0 | 0 | 100% | 100% | 0 | 0.092831 | 1 | 1.7759 | 0.16486 | High | High | Low | 1511 | 1324 | 0.092831 | 57.5497 | 0.6447%
TEMPLETON 2113A12 | TEMPLETON 2113 | LOS PADRES | 40.4505 | 77.6946 | 67.36% | 2 | 5 | 100% | 23.89% | 1 | 0.092809 | 1 | 1.1655 | 0.10817 | High | High | Low | 1720 | 1325 | 0.092809 | 57.4569 | 0.6437%
SEACLIFF 040112946 | SEACLIFF 0401 | CENTRAL COAST | 2.6944 | 41.521 | 88.42% | 0 | 1 | 83.31% | 77.78% | 0 | 0.092179 | 1 | 3.282 | 0.30253 | High | High | High | 1232 | 1326 | 0.092179 | 57.3641 | 0.6426%
CAMP EVERS 210512590 | CAMP EVERS 2105 | CENTRAL COAST | 4.822 | 13.1146 | 60.2% | 9 | 1 | 87.03% | 85.9% | 0 | 0.091772 | 1 | 3.6609 | 0.33597 | High | High | High | 1194 | 1327 | 0.091772 | 57.2719 | 0.6416%
PINE GROVE 11023168 | PINE GROVE 1102 | STOCKTON | 30.4079 | 52.9502 | 87.84% | 3 | 16 | 100% | 16.23% | 0 | 0.091596 | 1 | 2.5997 | 0.23812 | High | High | Medium | 1340 | 1328 | 0.091596 | 57.1801 | 0.6406%
BANGOR 110182350 | BANGOR 1101 | NORTH VALLEY | 20.6431 | 13.6369 | 91.07% | 2 | 31 | 93.75% | 0% | 0 | 0.091535 | 1 | 3.298 | 0.30188 | High | High | High | 1234 | 1329 | 0.091535 | 57.0885 | 0.6396%
PLACERVILLE 111019582 | PLACERVILLE 1110 | SIERRA | 22.4014 | 26.1615 | 63.31% | 2 | 22 | 100% | 0% | 0 | 0.091322 | 1 | 2.2123 | 0.20203 | High | High | Low | 1406 | 1330 | 0.091322 | 56.997 | 0.6385%
CLOVERDALE 1102156 | CLOVERDALE 1102 | SONOMA | 6.0801 | 52.6986 | 63.14% | 2 | 11 | 52.14% | 81.66% | 0 | 0.091237 | 1 | 2.2861 | 0.20858 | High | High | Medium | 1396 | 1331 | 0.091237 | 56.9057 | 0.6375%
GOLDTREE 1107CB | GOLDTREE 1107 | LOS PADRES | 1.1277 | 39.1961 | 5.234% | 0 | 0 | 30.84% | 0% | 0 | 0.008131 | 11.2183 | 2.7356 | 0.24953 | Low | Low | Medium | 1313 | 1332 | 0.091216 | 56.8144 | 0.6365%
TEMPLETON 2111A66 | TEMPLETON 2111 | LOS PADRES | 33.7371 | 15.0206 | 78.96% | 12 | 6 | 100% | 0.9159% | 0 | 0.091159 | 1 | 2.9193 | 0.26612 | High | High | Medium | 1289 | 1333 | 0.091159 | 56.7232 | 0.6355%
PAUL SWEET 21025291 | PAUL SWEET 2102 | CENTRAL COAST | 3.3045 | 10 | 22.71% | 10 | 3 | 77.46% | 100% | 0 | 0.091104 | 1 | 3.0809 | 0.28068 | High | High | High | 1260 | 1334 | 0.091104 | 56.6321 | 0.6344%
WHITMORE 11011594 | WHITMORE 1101 | NORTH VALLEY | 24.2582 | 53.3221 | 84.24% | 2 | 1 | 100% | 29.39% | 0 | 0.09099 | 1 | 1.3571 | 0.12348 | High | High | Low | 1647 | 1335 | 0.09099 | 56.541 | 0.6334%
LOW GAP 11014086 | LOW GAP 1101 | HUMBOLDT | 11.4979 | 83.0021 | 100% | 1 | 2 | 100% | 0% | 0 | 0.090624 | 1 | 1.3559 | 0.12288 | High | High | Low | 1652 | 1336 | 0.090624 | 56.45 | 0.6324%
NEWBURG 11322074 | NEWBURG 1132 | HUMBOLDT | 1.2262 | 10 | 0% | 0 | 0 | 11.58% | 0% | 0 | 0.0060224 | 14.9507 | 2.7999 | 0.2521 | Low | Low | Medium | 1308 | 1337 | 0.090039 | 56.3593 | 0.6314%
CALAVERAS CEMENT 110180930 | CALAVERAS CEMENT 1101 | STOCKTON | 18.4785 | 30.1878 | 99.81% | 1 | 6 | 100% | 0% | 0 | 0.089656 | 1 | 2.4362 | 0.21842 | High | High | Medium | 1375 | 1338 | 0.089656 | 56.2693 | 0.6304%
SAN JUSTO 11014002 | SAN JUSTO 1101 | CENTRAL COAST | 18.1183 | 71.0394 | 96.75% | 4 | 7 | 95.15% | 0% | 0 | 0.089593 | 1 | 2.061 | 0.18465 | High | High | Low | 1457 | 1339 | 0.089593 | 56.1796 | 0.6294%
AUBERRY 1102CB | AUBERRY 1102 | FRESNO | 34.5018 | 23.0923 | 82.62% | 0 | 22 | 100% | 0% | 0 | 0.089542 | 1 | 2.3016 | 0.20609 | High | High | Medium | 1402 | 1340 | 0.089542 | 56.0901 | 0.6284%
KESWICK 11011588 | KESWICK 1101 | NORTH VALLEY | 6.9485 | 28.4638 | 99.9% | 2 | 4 | 79.32% | 55.95% | 0 | 0.089394 | 1 | 2.1029 | 0.18799 | High | High | Low | 1445 | 1341 | 0.089394 | 56.0005 | 0.6274%
PINE GROVE 11026080 | PINE GROVE 1102 | STOCKTON | 34.785 | 21.8457 | 100% | 6 | 11 | 100% | 0.6625% | 0 | 0.089074 | 1 | 1.9325 | 0.17213 | High | High | Low | 1491 | 1342 | 0.089074 | 55.9111 | 0.6264%
MOUNTAIN QUARRIES 21011130 | MOUNTAIN QUARRIES 2101 | SIERRA | 20.0304 | 57.0085 | 99.98% | 8 | 6 | 100% | 22.7% | 1 | 0.088009 | 1 | 2.1946 | 0.19314 | High | High | Low | 1429 | 1343 | 0.088009 | 55.822 | 0.6254%
PARADISE 110317711 | PARADISE 1103 | NORTH VALLEY | 6.5808 | 11.9806 | 85.8% | 3 | 1 | 100% | 51.08% | 0 | 0.087993 | 1 | 3.594 | 0.31625 | High | High | High | 1212 | 1344 | 0.087993 | 55.734 | 0.6244%
OAKHURST 11035732 | OAKHURST 1103 | YOSEMITE | 3.391 | 10.7516 | 100% | 0 | 1 | 100% | 54.98% | 0 | 0.087919 | 1 | 1.6062 | 0.14122 | High | High | Low | 1578 | 1345 | 0.087919 | 55.646 | 0.6234%
CURTIS 170539256 | CURTIS 1705 | YOSEMITE | 26.4541 | 14.8561 | 72.89% | 2 | 39 | 100% | 0% | 0 | 0.087881 | 1 | 2.9559 | 0.25976 | High | High | Medium | 1296 | 1346 | 0.087881 | 55.5581 | 0.6224%
GARBERVILLE 11011770 | GARBERVILLE 1101 | HUMBOLDT | 8.6092 | 87.0246 | 95.86% | 7 | 3 | 100% | 0% | 0 | 0.087398 | 1 | 0.26991 | 0.02359 | High | High | Low | 2919 | 1347 | 0.087398 | 55.4702 | 0.6214%
VOLTA 110293418 | VOLTA 1102 | NORTH VALLEY | 2.6513 | 65.9048 | 100% | 5 | 0 | 100% | 44.92% | 0 | 0.087226 | 1 | 1.8377 | 0.1603 | High | High | Low | 1524 | 1348 | 0.087226 | 55.3828 | 0.6204%
FROGTOWN 170275252 | FROGTOWN 1702 | STOCKTON | 57.5264 | 53.766 | 80.82% | 0 | 20 | 95.14% | 0% | 0 | 0.087181 | 1 | 2.07 | 0.18046 | High | High | Low | 1470 | 1349 | 0.087181 | 55.2956 | 0.6195%
SANTA ROSA A 110464565 | SANTA ROSA A 1104 | SONOMA | 0.80928 | 10 | 22.53% | 1 | 2 | 100% | 100% | 0 | 0.087105 | 1 | 3.4851 | 0.30357 | High | High | High | 1231 | 1350 | 0.087105 | 55.2084 | 0.6185%
HARRIS 1109700 | HARRIS 1109 | HUMBOLDT | 13.0569 | 19.3799 | 29.7% | 17 | 20 | 44.54% | 0% | 0 | 0.086853 | 1 | 3.6202 | 0.31443 | High | High | High | 1213 | 1351 | 0.086853 | 55.1213 | 0.6175%
OAKLAND K 1103CR188 | OAKLAND K 1103 | EAST BAY | 3.5811 | 10 | 48.05% | 3 | 7 | 100% | 62.42% | 0 | 0.086851 | 1 | 4.3746 | 0.37994 | High | High | High | 1161 | 1352 | 0.086851 | 55.0345 | 0.6165%
HOOPA 11013304 | HOOPA 1101 | HUMBOLDT | 16.9885 | 82.5702 | 98.71% | 15 | 4 | 100% | 0% | 0 | 0.086315 | 1 | 1.6263 | 0.14037 | High | High | Low | 1582 | 1353 | 0.086315 | 54.9476 | 0.6156%
HALSEY 1101CB | HALSEY 1101 | SIERRA | 17.1561 | 10.5573 | 71.81% | 7 | 24 | 100% | 0% | 0 | 0.08631 | 1 | 2.3966 | 0.20685 | High | High | Medium | 1401 | 1354 | 0.08631 | 54.8613 | 0.6146%
CURTIS 170510590 | CURTIS 1705 | YOSEMITE | 9.8062 | 25.1511 | 99.51% | 1 | 1 | 100% | 47.11% | 0 | 0.086282 | 1 | 3.2172 | 0.27758 | High | High | High | 1267 | 1355 | 0.086282 | 54.775 | 0.6136%
GANSNER 11012006 | GANSNER 1101 | NORTH VALLEY | 17.1959 | 52.9981 | 98.77% | 5 | 5 | 100% | 2.795% | 0 | 0.086274 | 1 | 2.5916 | 0.22359 | High | High | Medium | 1363 | 1356 | 0.086274 | 54.6887 | 0.6127%
CAMP EVERS 210611006 | CAMP EVERS 2106 | CENTRAL COAST | 2.073 | 10 | 22.12% | 2 | 1 | 100% | 100% | 0 | 0.086223 | 1 | 4.2738 | 0.3685 | High | High | High | 1166 | 1357 | 0.086223 | 54.6024 | 0.6117%
HOOPA 1101CB | HOOPA 1101 | HUMBOLDT | 15.2475 | 59.0191 | 97.73% | 17 | 6 | 56.28% | 0% | 0 | 0.085954 | 1 | 2.2215 | 0.19095 | High | High | Low | 1436 | 1358 | 0.085954 | 54.5162 | 0.6107%
KESWICK 11011586 | KESWICK 1101 | NORTH VALLEY | 7.6307 | 36.5577 | 16.39% | 0 | 2 | 100% | 100% | 1 | 0.085854 | 1 | 2.7857 | 0.23916 | High | High | Medium | 1337 | 1359 | 0.085854 | 54.4303 | 0.6098%
DIAMOND SPRINGS 1103CB | DIAMOND SPRINGS 1103 | SIERRA | 16.7869 | 10 | 71.13% | 6 | 16 | 54.37% | 47.43% | 1 | 0.08564 | 1 | 2.4835 | 0.21268 | High | High | Medium | 1387 | 1360 | 0.08564 | 54.3444 | 0.6088%
HIGGINS 1103CB | HIGGINS 1103 | SIERRA | 27.5586 | 18.1402 | 77.71% | 6 | 7 | 99.3% | 0% | 0 | 0.085581 | 1 | 2.9579 | 0.25314 | High | High | Medium | 1306 | 1361 | 0.085581 | 54.2588 | 0.6079%
POINT ARENA 110137426 | POINT ARENA 1101 | HUMBOLDT | 0.081405 | 10 | 0% | 2 | 1 | 1.62% | 0% | 0 | 0.0057167 | 14.9507 | 2.9781 | 0.25453 | Low | Low | Medium | 1302 | 1362 | 0.085468 | 54.1732 | 0.6069%
ALTO 11252243 | ALTO 1125 | NORTH BAY | 2.9262 | 21.9292 | 59.4% | 1 | 4 | 100% | 22.94% | 0 | 0.085029 | 1 | 3.926 | 0.33382 | High | High | High | 1195 | 1363 | 0.085029 | 54.0877 | 0.6059%
BRUNSWICK 11062790 | BRUNSWICK 1106 | SIERRA | 8.9258 | 13.4181 | 98.75% | 0 | 3 | 81.13% | 52.78% | 0 | 0.084645 | 1 | 2.178 | 0.18435 | High | High | Low | 1460 | 1364 | 0.084645 | 54.0027 | 0.605%
VOLTA 11011516 | VOLTA 1101 | NORTH VALLEY | 25.7297 | 67.2634 | 100% | 4 | 8 | 100% | 0% | 0 | 0.084582 | 1 | 0.70197 | 0.059374 | High | High | Low | 2190 | 1365 | 0.084582 | 53.918 | 0.604%
GUALALA 111135562 | GUALALA 1111 | HUMBOLDT | 14.2585 | 63.006 | 19.44% | 12 | 36 | 100% | 0% | 0 | 0.084547 | 1 | 1.8822 | 0.15913 | High | High | Low | 1527 | 1366 | 0.084547 | 53.8335 | 0.6031%
NARROWS 21022220 | NARROWS 2102 | SIERRA | 27.523 | 12.681 | 87.5% | 7 | 17 | 97.87% | 0% | 0 | 0.084411 | 1 | 3.2946 | 0.2781 | High | High | High | 1264 | 1367 | 0.084411 | 53.7489 | 0.6021%
EL DORADO PH 210163464 | EL DORADO PH 2101 | SIERRA | 13.6531 | 63.9369 | 100% | 0 | 2 | 100% | 36.69% | 1 | 0.084238 | 1 | 1.4999 | 0.12635 | High | High | Low | 1639 | 1368 | 0.084238 | 53.6645 | 0.6012%
SWIFT 2110XR254 | SWIFT 2110 | SAN JOSE | 24.8145 | 55.7178 | 60.2% | 2 | 3 | 100% | 0% | 0 | 0.084233 | 1 | 3.6541 | 0.30779 | High | High | High | 1227 | 1369 | 0.084233 | 53.5803 | 0.6003%
VASCO 1102MR176 | VASCO 1102 | MISSION | 38.5569 | 70.5523 | 85.5% | 0 | 7 | 89.92% | 0% | 0 | 0.084198 | 1 | 2.3104 | 0.19454 | High | High | Medium | 1423 | 1370 | 0.084198 | 53.496 | 0.5993%
APPLE HILL 210277546 | APPLE HILL 2102 | SIERRA | 43.2651 | 10.0567 | 100% | 8 | 8 | 100% | 3.986% | 0 | 0.084095 | 1 | 2.293 | 0.19283 | High | High | Medium | 1430 | 1371 | 0.084095 | 53.4118 | 0.5984%
CAMP EVERS 210311056 | CAMP EVERS 2103 | CENTRAL COAST | 1.8179 | 16.722 | 18.6% | 7 | 3 | 97.69% | 100% | 0 | 0.083758 | 1 | 3.5617 | 0.29832 | High | High | High | 1237 | 1372 | 0.083758 | 53.3277 | 0.5974%
SAN RAFAEL 110839156 | SAN RAFAEL 1108 | NORTH BAY | 3.0298 | 11.0786 | 11.96% | 3 | 10 | 63.16% | 96.57% | 0 | 0.083717 | 1 | 4.762 | 0.39866 | High | High | High | 1149 | 1373 | 0.083717 | 53.244 | 0.5965%
LOS GATOS 1106CB | LOS GATOS 1106 | DE ANZA | 6.7095 | 14.253 | 23.95% | 2 | 3 | 87.56% | 91.62% | 0 | 0.083012 | 1 | 3.283 | 0.27253 | High | High | High | 1278 | 1374 | 0.083012 | 53.1603 | 0.5955%
SANTA YNEZ 1101Y16 | SANTA YNEZ 1101 | LOS PADRES | 7.1745 | 86.5871 | 96.55% | 0 | 1 | 49.62% | 51.9% | 0 | 0.082863 | 1 | 2.1114 | 0.17496 | High | High | Low | 1481 | 1375 | 0.082863 | 53.0773 | 0.5946%
ANTLER 11011384 | ANTLER 1101 | NORTH VALLEY | 8.8576 | 10 | 98.19% | 3 | 9 | 97.22% | 0% | 0 | 0.08259 | 1 | 1.0219 | 0.084396 | High | High | Low | 1880 | 1376 | 0.08259 | 52.9944 | 0.5937%
CAMP EVERS 210355638 | CAMP EVERS 2103 | CENTRAL COAST | 1.9801 | 10 | 57.05% | 1 | 0 | 56.59% | 100% | 0 | 0.082558 | 1 | 3.2291 | 0.26659 | High | High | High | 1287 | 1377 | 0.082558 | 52.9118 | 0.5928%
LOW GAP 11014160 | LOW GAP 1101 | HUMBOLDT | 21.5735 | 61.654 | 100% | 10 | 5 | 99.51% | 0% | 0 | 0.082527 | 1 | 1.298 | 0.10712 | High | High | Low | 1725 | 1378 | 0.082527 | 52.8292 | 0.5918%
BIG MEADOWS 21012246 | BIG MEADOWS 2101 | NORTH VALLEY | 1.3711 | 10 | 100% | 1 | 20 | 75.1% | 0% | 0 | 0.082406 | 1 | 1.2663 | 0.10435 | High | High | Low | 1739 | 1379 | 0.082406 | 52.7467 | 0.5909%
BOLINAS 1101504 | BOLINAS 1101 | NORTH BAY | 6.5349 | 26.1981 | 0% | 2 | 2 | 100% | 100% | 0 | 0.082308 | 1 | 3.1479 | 0.2591 | High | High | High | 1299 | 1380 | 0.082308 | 52.6643 | 0.59%
CLOVERDALE 1102674 | CLOVERDALE 1102 | SONOMA | 17.0598 | 62.482 | 68.42% | 4 | 8 | 84.92% | 25.35% | 0 | 0.082178 | 1 | 1.8325 | 0.15059 | High | High | Low | 1549 | 1381 | 0.082178 | 52.582 | 0.5891%
OCEANO 1102CB | OCEANO 1102 | LOS PADRES | 20.8775 | 11.5809 | 41.43% | 7 | 19 | 75.87% | 0% | 0 | 0.081976 | 1 | 2.9691 | 0.2434 | High | High | Medium | 1329 | 1382 | 0.081976 | 52.4998 | 0.5881%
BUELLTON 1101Y36 | BUELLTON 1101 | LOS PADRES | 33.0581 | 70.2256 | 71.54% | 1 | 11 | 92.67% | 5.931% | 1 | 0.081946 | 1 | 1.6819 | 0.13782 | High | High | Low | 1594 | 1383 | 0.081946 | 52.4179 | 0.5872%
BANGOR 11017446 | BANGOR 1101 | NORTH VALLEY | 43.441 | 11.2625 | 85.83% | 3 | 18 | 100% | 0% | 0 | 0.081818 | 1 | 2.2193 | 0.18158 | High | High | Low | 1468 | 1384 | 0.081818 | 52.3359 | 0.5863%
GEYSERVILLE 110179788 | GEYSERVILLE 1101 | SONOMA | 36.3345 | 85.553 | 97.66% | 5 | 7 | 86.55% | 0% | 0 | 0.081783 | 1 | 1.4593 | 0.11934 | High | High | Low | 1667 | 1385 | 0.081783 | 52.2541 | 0.5854%
SHINGLE SPRINGS 210911092 | SHINGLE SPRINGS 2109 | SIERRA | 22.1149 | 21.1094 | 82.77% | 7 | 7 | 100% | 0% | 0 | 0.081649 | 1 | 1.6738 | 0.13667 | High | High | Low | 1599 | 1386 | 0.081649 | 52.1723 | 0.5845%
PERRY 1101V78 | PERRY 1101 | LOS PADRES | 29.478 | 56.2687 | 60.85% | 2 | 3 | 100% | 21.68% | 1 | 0.081321 | 1 | 2.3311 | 0.18957 | High | High | Medium | 1440 | 1387 | 0.081321 | 52.0907 | 0.5836%
GARBERVILLE 11011750 | GARBERVILLE 1101 | HUMBOLDT | 14.3678 | 85.1825 | 100% | 14 | 8 | 96.86% | 0% | 0 | 0.081262 | 1 | 1.6609 | 0.13497 | High | High | Low | 1604 | 1388 | 0.081262 | 52.0093 | 0.5827%
GANSNER 11012424 | GANSNER 1101 | NORTH VALLEY | 18.9007 | 82.3071 | 77.09% | 4 | 10 | 100% | 0% | 0 | 0.081226 | 1 | 2.0492 | 0.16645 | High | High | Low | 1507 | 1389 | 0.081226 | 51.9281 | 0.5817%
MORGAN HILL 2111XR186 | MORGAN HILL 2111 | SAN JOSE | 0.89677 | 65 | 0% | 0 | 0 | 5.591% | 0% | 0 | 0.0072203 | 11.2183 | 2.834 | 0.22955 | Low | Low | Medium | 1351 | 1390 | 0.080999 | 51.8468 | 0.5808%
GRASS VALLEY 11032110 | GRASS VALLEY 1103 | SIERRA | 19.6542 | 17.5047 | 70.11% | 3 | 10 | 97.43% | 0% | 0 | 0.080807 | 1 | 2.6029 | 0.21033 | High | High | Medium | 1393 | 1391 | 0.080807 | 51.7658 | 0.5799%
MIRABEL 1102CB | MIRABEL 1102 | SONOMA | 4.5501 | 24.245 | 39.21% | 4 | 11 | 40.5% | 94.81% | 0 | 0.080685 | 1 | 3.2843 | 0.26499 | High | High | High | 1290 | 1392 | 0.080685 | 51.685 | 0.579%
SAND CREEK 11037110 | SAND CREEK 1103 | FRESNO | 19.4155 | 27.8259 | 94.86% | 5 | 7 | 100% | 0% | 0 | 0.080582 | 1 | 0.43197 | 0.034809 | High | High | Low | 2657 | 1393 | 0.080582 | 51.6044 | 0.5781%
LLAGAS 210740407 | LLAGAS 2107 | SAN JOSE | 4.4461 | 62.3794 | 79.11% | 0 | 0 | 69.99% | 65.8% | 1 | 0.080349 | 1 | 3.8574 | 0.30994 | High | High | High | 1223 | 1394 | 0.080349 | 51.5238 | 0.5772%
BUCKS CREEK 1101CB | BUCKS CREEK 1101 | NORTH VALLEY | 20.005 | 83.6146 | 6.119% | 5 | 12 | 100% | 23.08% | 0 | 0.080342 | 1 | 1.6795 | 0.13494 | High | High | Low | 1605 | 1395 | 0.080342 | 51.4434 | 0.5763%
CABRILLO 1104Y24 | CABRILLO 1104 | LOS PADRES | 18.0747 | 69.8881 | 25.08% | 0 | 8 | 92.92% | 0% | 0 | 0.080321 | 1 | 3.2604 | 0.26188 | High | High | High | 1294 | 1396 | 0.080321 | 51.3631 | 0.5754%
CALPELLA 1101600 | CALPELLA 1101 | HUMBOLDT | 20.3203 | 63.0301 | 92.94% | 2 | 3 | 76.37% | 16.27% | 1 | 0.080296 | 1 | 1.8322 | 0.14712 | High | High | Low | 1562 | 1397 | 0.080296 | 51.2828 | 0.5745%
WEIMAR 11012740 | WEIMAR 1101 | SIERRA | 19.1962 | 52.0643 | 71.74% | 1 | 4 | 100% | 0% | 0 | 0.080042 | 1 | 1.7168 | 0.13742 | High | High | Low | 1597 | 1398 | 0.080042 | 51.2025 | 0.5736%
OILFIELDS 1103N44 | OILFIELDS 1103 | CENTRAL COAST | 18.7718 | 55.8541 | 96.36% | 0 | 0 | 100% | 0% | 0 | 0.079917 | 1 | 2.3613 | 0.18871 | High | High | Medium | 1442 | 1399 | 0.079917 | 51.1224 | 0.5727%
SHINGLE SPRINGS 1103CB | SHINGLE SPRINGS 1103 | SIERRA | 6.5783 | 25.7936 | 79.81% | 1 | 6 | 56.03% | 80.43% | 1 | 0.079857 | 1 | 3.0171 | 0.24094 | High | High | Medium | 1332 | 1400 | 0.079857 | 51.0425 | 0.5718%
GREEN VALLEY 210112824 | GREEN VALLEY 2101 | CENTRAL COAST | 0.066956 | 70 | 0% | 0 | 0 | 0.5469% | 0% | 0 | 0.007104 | 11.2183 | 2.3989 | 0.19118 | Low | Low | Medium | 1434 | 1401 | 0.079695 | 50.9626 | 0.5709%
VOLTA 11021650 | VOLTA 1102 | NORTH VALLEY | 21.7066 | 54.4838 | 100% | 4 | 9 | 100% | 0% | 0 | 0.079578 | 1 | 1.4837 | 0.11807 | High | High | Low | 1675 | 1402 | 0.079578 | 50.883 | 0.57%
BUELLTON 1101Y06 | BUELLTON 1101 | LOS PADRES | 29.0172 | 49.4932 | 60.5% | 0 | 10 | 72.26% | 0% | 0 | 0.079416 | 1 | 1.7409 | 0.13826 | High | High | Low | 1591 | 1403 | 0.079416 | 50.8034 | 0.5691%
TIVY VALLEY 1107584840 | TIVY VALLEY 1107 | FRESNO | 44.9458 | 14.7533 | 99.99% | 0 | 18 | 100% | 0% | 0 | 0.079403 | 1 | 2.0582 | 0.16342 | High | High | Low | 1514 | 1404 | 0.079403 | 50.724 | 0.5683%
PARADISE 11032558 | PARADISE 1103 | NORTH VALLEY | 2.3505 | 10 | 33.28% | 3 | 2 | 78.43% | 100% | 0 | 0.079398 | 1 | 3.8466 | 0.30541 | High | High | High | 1229 | 1405 | 0.079398 | 50.6446 | 0.5674%
COARSEGOLD 210310820 | COARSEGOLD 2103 | YOSEMITE | 28.8124 | 11.1753 | 93.73% | 0 | 47 | 100% | 0% | 0 | 0.07927 | 1 | 2.4251 | 0.19224 | High | High | Medium | 1433 | 1406 | 0.07927 | 50.5652 | 0.5665%
CAYUCOS 1102CB | CAYUCOS 1102 | LOS PADRES | 11.9239 | 72.3136 | 83.3% | 3 | 2 | 41.34% | 71.02% | 0 | 0.079048 | 1 | 2.3364 | 0.18468 | High | High | Medium | 1455 | 1407 | 0.079048 | 50.4859 | 0.5656%
BERKELEY F 1105BR100 | BERKELEY F 1105 | EAST BAY | 0.38346 | 10 | 26.17% | 0 | 2 | 14.66% | 0% | 0 | 0.0070264 | 11.2183 | 4.0468 | 0.31898 | Low | Low | High | 1209 | 1408 | 0.078824 | 50.4068 | 0.5647%
POTTER VALLEY P H 11051904 | POTTER VALLEY P H 1105 | HUMBOLDT | 28.466 | 59.7756 | 95.28% | 1 | 23 | 70.74% | 17.93% | 1 | 0.078348 | 1 | 1.3548 | 0.10615 | High | High | Low | 1731 | 1409 | 0.078348 | 50.328 | 0.5638%
MARIPOSA 210110070 | MARIPOSA 2101 | YOSEMITE | 25.9306 | 26.9034 | 96.01% | 1 | 27 | 100% | 0% | 0 | 0.078332 | 1 | 2.0789 | 0.16285 | High | High | Low | 1516 | 1410 | 0.078332 | 50.2497 | 0.5629%
SHINGLE SPRINGS 2108CB | SHINGLE SPRINGS 2108 | SIERRA | 1.2634 | 35.9265 | 24.64% | 0 | 1 | 85.58% | 100% | 1 | 0.078196 | 1 | 3.1135 | 0.24347 | High | High | High | 1328 | 1411 | 0.078196 | 50.1713 | 0.5621%
GREENBRAE 11032371 | GREENBRAE 1103 | NORTH BAY | 0.40055 | 47.8608 | 0% | 1 | 4 | 90.05% | 100% | 0 | 0.078151 | 1 | 3.7079 | 0.28978 | High | High | High | 1248 | 1412 | 0.078151 | 50.0931 | 0.5612%
SAND CREEK 110345190 | SAND CREEK 1103 | FRESNO | 36.6214 | 13.3834 | 99.51% | 0 | 5 | 100% | 0% | 0 | 0.078024 | 1 | 1.9196 | 0.14977 | High | High | Low | 1552 | 1413 | 0.078024 | 50.015 | 0.5603%
HOOPA 11013290 | HOOPA 1101 | HUMBOLDT | 13.744 | 63.8622 | 97.01% | 10 | 15 | 100% | 0% | 0 | 0.077955 | 1 | 1.0027 | 0.078163 | High | High | Low | 1953 | 1414 | 0.077955 | 49.937 | 0.5594%
BOLINAS 1101CB | BOLINAS 1101 | NORTH BAY | 2.176 | 69.2661 | 1.123% | 3 | 1 | 100% | 77.9% | 0 | 0.077604 | 1 | 2.9867 | 0.23178 | High | High | Medium | 1349 | 1415 | 0.077604 | 49.859 | 0.5586%
SHINGLE SPRINGS 210819762 | SHINGLE SPRINGS 2108 | SIERRA | 4.2221 | 28.8991 | 60.1% | 3 | 6 | 78.12% | 39.2% | 0 | 0.077593 | 1 | 3.1989 | 0.24821 | High | High | High | 1317 | 1416 | 0.077593 | 49.7814 | 0.5577%
TEMPLETON 2110R90 | TEMPLETON 2110 | LOS PADRES | 27.6614 | 57.9463 | 69.12% | 2 | 5 | 77.95% | 0% | 0 | 0.077528 | 1 | 2.0934 | 0.1623 | High | High | Low | 1519 | 1417 | 0.077528 | 49.7038 | 0.5568%
BUCKS CREEK 1102CB | BUCKS CREEK 1102 | NORTH VALLEY | 29.5609 | 73.8859 | 50.06% | 3 | 10 | 100% | 23.04% | 0 | 0.077422 | 1 | 0.91112 | 0.07054 | High | High | Low | 2035 | 1418 | 0.077422 | 49.6263 | 0.556%
SAN RAFAEL 1107CB | SAN RAFAEL 1107 | NORTH BAY | 4.2653 | 10 | 28.65% | 2 | 4 | 53.65% | 97.72% | 0 | 0.077391 | 1 | 4.2548 | 0.32928 | High | High | High | 1199 | 1419 | 0.077391 | 49.5489 | 0.5551%
PARADISE 110439216 | PARADISE 1104 | NORTH VALLEY | 2.1396 | 10 | 44.98% | 1 | 0 | 59.38% | 100% | 0 | 0.07729 | 1 | 4.0674 | 0.31437 | High | High | High | 1214 | 1420 | 0.07729 | 49.4715 | 0.5542%
AUBERRY 1101R2578 | AUBERRY 1101 | FRESNO | 46.349 | 12.9087 | 87.94% | 4 | 13 | 100% | 0% | 0 | 0.077203 | 1 | 1.5016 | 0.11593 | High | High | Low | 1685 | 1421 | 0.077203 | 49.3942 | 0.5534%
NARROWS 21057203 | NARROWS 2105 | SIERRA | 17.8971 | 13.4012 | 99.97% | 2 | 5 | 95.78% | 0% | 0 | 0.077172 | 1 | 2.5133 | 0.19395 | High | High | Medium | 1424 | 1422 | 0.077172 | 49.317 | 0.5525%
PENRYN 110651674 | PENRYN 1106 | SIERRA | 0.99996 | 10 | 36.11% | 0 | 0 | 8.247% | 0% | 0 | 0.0068595 | 11.2183 | 3.3008 | 0.254 | Low | Low | High | 1304 | 1423 | 0.076952 | 49.2398 | 0.5516%
SAN LUIS OBISPO 1107V58 | SAN LUIS OBISPO 1107 | LOS PADRES | 0.84617 | 10 | 0% | 0 | 0 | 37.96% | 0% | 0 | 0.006858 | 11.2183 | 3.2113 | 0.24706 | Low | Low | High | 1321 | 1424 | 0.076935 | 49.1629 | 0.5508%
OREGON TRAIL 11031500 | OREGON TRAIL 1103 | NORTH VALLEY | 24.8639 | 16.6581 | 98.22% | 2 | 4 | 96.57% | 0% | 0 | 0.076799 | 1 | 2.7865 | 0.214 | High | High | Medium | 1383 | 1425 | 0.076799 | 49.0859 | 0.5499%
CALAVERAS CEMENT 11014786 | CALAVERAS CEMENT 1101 | STOCKTON | 18.0051 | 18.3515 | 89.75% | 0 | 8 | 100% | 55.25% | 1 | 0.076728 | 1 | 2.9429 | 0.22581 | High | High | Medium | 1358 | 1426 | 0.076728 | 49.0091 | 0.549%
MENLO 1102W80 | MENLO 1102 | PENINSULA | 17.326 | 69.2206 | 62.7% | 1 | 9 | 91.54% | 1.485% | 1 | 0.076689 | 1 | 3.3813 | 0.2593 | High | High | High | 1298 | 1427 | 0.076689 | 48.9324 | 0.5482%
PEORIA 17051834 | PEORIA 1705 | YOSEMITE | 22.9121 | 21.3201 | 69.84% | 0 | 15 | 96.15% | 0% | 0 | 0.076648 | 1 | 2.2374 | 0.17149 | High | High | Medium | 1495 | 1428 | 0.076648 | 48.8557 | 0.5473%
HIGGINS 110332120 | HIGGINS 1103 | SIERRA | 40.5815 | 16.4911 | 85.22% | 7 | 11 | 99.04% | 0% | 0 | 0.076505 | 1 | 2.9612 | 0.22655 | High | High | Medium | 1355 | 1429 | 0.076505 | 48.7791 | 0.5465%
VOLTA 110180454 | VOLTA 1101 | NORTH VALLEY | 31.4882 | 39.839 | 95.78% | 4 | 1 | 97.71% | 0.9246% | 0 | 0.076439 | 1 | 1.1851 | 0.090591 | High | High | Low | 1826 | 1430 | 0.076439 | 48.7026 | 0.5456%
LUCERNE 110638632 | LUCERNE 1106 | HUMBOLDT | 4.4543 | 54.342 | 100% | 6 | 8 | 95.13% | 0% | 0 | 0.076393 | 1 | 2.9038 | 0.22183 | High | High | Medium | 1368 | 1431 | 0.076393 | 48.6261 | 0.5448%
BIG BASIN 110212779 | BIG BASIN 1102 | CENTRAL COAST | 0.25335 | 10 | 27.94% | 0 | 0 | 100% | 100% | 0 | 0.076303 | 1 | 2.6324 | 0.20086 | High | High | Medium | 1413 | 1432 | 0.076303 | 48.5497 | 0.5439%
INDIAN FLAT 1104CB | INDIAN FLAT 1104 | YOSEMITE | 12.7115 | 39.8985 | 69.22% | 2 | 12 | 100% | 0% | 0 | 0.075983 | 1 | 1.9513 | 0.14826 | High | High | Low | 1559 | 1433 | 0.075983 | 48.4734 | 0.543%
ALTO 1124428 | ALTO 1124 | NORTH BAY | 4.8403 | 17.2865 | 1.418% | 0 | 4 | 81.37% | 100% | 0 | 0.075976 | 1 | 4.8386 | 0.36762 | High | High | High | 1167 | 1434 | 0.075976 | 48.3974 | 0.5422%
TYLER 110585132 | TYLER 1105 | NORTH VALLEY | 30.9692 | 56.9117 | 100% | 0 | 21 | 100% | 0% | 0 | 0.075876 | 1 | 1.6764 | 0.1272 | High | High | Low | 1635 | 1435 | 0.075876 | 48.3215 | 0.5413%
SHINGLE SPRINGS 210981390 | SHINGLE SPRINGS 2109 | SIERRA | 18.7493 | 21.0161 | 63.9% | 1 | 8 | 100% | 0% | 0 | 0.075764 | 1 | 2.0292 | 0.15374 | High | High | Low | 1544 | 1436 | 0.075764 | 48.2456 | 0.5405%
OILFIELDS 1103N48 | OILFIELDS 1103 | CENTRAL COAST | 47.0468 | 56.1397 | 99.69% | 2 | 26 | 100% | 0% | 0 | 0.075176 | 1 | 1.4634 | 0.11001 | High | High | Low | 1709 | 1437 | 0.075176 | 48.1698 | 0.5396%
PHILO 1102920 | PHILO 1102 | HUMBOLDT | 17.5582 | 57.0245 | 91.25% | 3 | 12 | 67.45% | 0% | 0 | 0.075007 | 1 | 1.2527 | 0.093958 | High | High | Low | 1806 | 1438 | 0.075007 | 48.0946 | 0.5388%
APPLE HILL 1103CB | APPLE HILL 1103 | SIERRA | 27.6878 | 21.3856 | 62.7% | 5 | 24 | 82.6% | 2.955% | 0 | 0.074928 | 1 | 2.43 | 0.18207 | High | High | Medium | 1467 | 1439 | 0.074928 | 48.0196 | 0.538%
SANTA ROSA A 110432180 | SANTA ROSA A 1104 | SONOMA | 2.5189 | 19.7323 | 62.59% | 0 | 1 | 99.89% | 67.69% | 0 | 0.074867 | 1 | 3.2925 | 0.2465 | High | High | High | 1322 | 1440 | 0.074867 | 47.9447 | 0.5371%
WISHON 1101CB | WISHON 1101 | YOSEMITE | 7.7822 | 34.1369 | 78.45% | 1 | 2 | 100% | 51.22% | 1 | 0.074616 | 1 | 1.7546 | 0.13092 | High | High | Low | 1625 | 1441 | 0.074616 | 47.8698 | 0.5363%
STELLING 111060080 | STELLING 1110 | DE ANZA | 9.1723 | 64.142 | 26.3% | 6 | 3 | 90.37% | 0% | 0 | 0.074583 | 1 | 3.1821 | 0.23733 | High | High | High | 1344 | 1442 | 0.074583 | 47.7952 | 0.5354%
CALAVERAS CEMENT 11011419 | CALAVERAS CEMENT 1101 | STOCKTON | 15.0795 | 14.8417 | 100% | 2 | 7 | 100% | 0% | 0 | 0.074427 | 1 | 2.3142 | 0.17224 | High | High | Medium | 1490 | 1443 | 0.074427 | 47.7206 | 0.5346%
FORT SEWARD 11211602 | FORT SEWARD 1121 | HUMBOLDT | 18.3365 | 83.3472 | 100% | 8 | 9 | 80.72% | 0% | 0 | 0.074162 | 1 | 0.96205 | 0.071347 | High | High | Low | 2030 | 1444 | 0.074162 | 47.6462 | 0.5338%
ECHO SUMMIT 11012500 | ECHO SUMMIT 1101 | (blank) | 2.8817 | 10 | 100% | 2 | 2 | 100% | 0% | 0 | 0.074119 | 1 | 2.0914 | 0.15501 | High | High | Low | 1539 | 1445 | 0.074119 | 47.5721 | 0.5329%
RED BLUFF 11031702 | RED BLUFF 1103 | NORTH VALLEY | 15.929 | 23.8535 | 100% | 1 | 4 | 87.44% | 0% | 0 | 0.073954 | 1 | 1.9176 | 0.14181 | High | High | Low | 1577 | 1446 | 0.073954 | 47.4979 | 0.5321%
MORRO BAY 110247584 | MORRO BAY 1102 | LOS PADRES | 8.6089 | 11.2458 | 21.08% | 1 | 2 | 89.3% | 46.55% | 1 | 0.073801 | 1 | 3.3695 | 0.24868 | High | High | High | 1316 | 1447 | 0.073801 | 47.424 | 0.5313%
WEST POINT 11021369 | WEST POINT 1102 | STOCKTON | 10.5051 | 72.1066 | 100% | 1 | 0 | 98.44% | 18.78% | 0 | 0.073587 | 1 | 2.7416 | 0.20175 | High | High | Medium | 1408 | 1448 | 0.073587 | 47.3502 | 0.5305%
BEN LOMOND 040116010 | BEN LOMOND 0401 | CENTRAL COAST | 1.6971 | 10 | 15.35% | 1 | 2 | 100% | 100% | 0 | 0.072945 | 1 | 4.0662 | 0.29661 | High | High | High | 1243 | 1449 | 0.072945 | 47.2766 | 0.5296%
PENRYN 1105CB | PENRYN 1105 | SIERRA | 0.038025 | 10 | 0% | 0 | 0 | 3.678% | 0% | 0 | 0.0048736 | 14.9507 | 3.0534 | 0.22248 | Low | Low | Medium | 1366 | 1450 | 0.072863 | 47.2036 | 0.5288%
SONOMA 1105404 | SONOMA 1105 | SONOMA | 12.3578 | 22.8821 | 50.06% | 1 | 16 | 68.86% | 37.07% | 0 | 0.072855 | 1 | 3.2835 | 0.23922 | High | High | High | 1336 | 1451 | 0.072855 | 47.1308 | 0.528%
VOLTA 11011568 | VOLTA 1101 | NORTH VALLEY | 23.0081 | 45.5317 | 55% | 0 | 5 | 100% | 29.05% | 0 | 0.072817 | 1 | 1.4267 | 0.10388 | High | High | Low | 1741 | 1452 | 0.072817 | 47.0579 | 0.5272%
OCEANO 1104Q06 | OCEANO 1104 | LOS PADRES | 12.4604 | 18.1576 | 68.47% | 10 | 12 | 100% | 0% | 0 | 0.07261 | 1 | 3.274 | 0.23772 | High | High | High | 1342 | 1453 | 0.07261 | 46.9851 | 0.5264%
ALHAMBRA 110582622 | ALHAMBRA 1105 | DIABLO | 25.9018 | 63.5576 | 53.56% | 4 | 18 | 100% | 1.973% | 1 | 0.072547 | 1 | 2.8047 | 0.20347 | High | High | Medium | 1405 | 1454 | 0.072547 | 46.9125 | 0.5256%
SAN RAMON 2107CB | SAN RAMON 2107 | MISSION | 0.08762 | 60 | 100% | 0 | 0 | 0.9683% | 100% | 0 | 0.072467 | 1 | 3.5047 | 0.25397 | High | High | High | 1305 | 1455 | 0.072467 | 46.84 | 0.5247%
PHILO 1101CB | PHILO 1101 | HUMBOLDT | 30.1647 | 49.3506 | 76.4% | 12 | 16 | 60.92% | 0% | 0 | 0.072449 | 1 | 2.0932 | 0.15165 | High | High | Low | 1548 | 1456 | 0.072449 | 46.7675 | 0.5239%
AUBERRY 1101R314 | AUBERRY 1101 | FRESNO | 42.3727 | 21.0608 | 99.17% | 0 | 7 | 96.03% | 0% | 0 | 0.072346 | 1 | 1.5793 | 0.11426 | High | High | Low | 1691 | 1457 | 0.072346 | 46.695 | 0.5231%
MOUNTAIN QUARRIES 21011346 | MOUNTAIN QUARRIES 2101 | SIERRA | 30.7365 | 10.3256 | 98.49% | 5 | 12 | 100% | 0% | 0 | 0.072232 | 1 | 2.3792 | 0.17186 | High | High | Medium | 1493 | 1458 | 0.072232 | 46.6227 | 0.5223%
VOLTA 11011640 | VOLTA 1101 | NORTH VALLEY | 10.4338 | 80.2423 | 83.4% | 1 | 4 | 100% | 0% | 0 | 0.072189 | 1 | 0.092106 | 0.006649 | High | High | Low | 3163 | 1459 | 0.072189 | 46.5505 | 0.5215%
COARSEGOLD 21045525 | COARSEGOLD 2104 | YOSEMITE | 13.0444 | 10.8034 | 99.82% | 2 | 45 | 100% | 0% | 0 | 0.072179 | 1 | 2.4095 | 0.17392 | High | High | Medium | 1485 | 1460 | 0.072179 | 46.4783 | 0.5207%
DESCHUTES 11011580 | DESCHUTES 1101 | NORTH VALLEY | 44.5215 | 20.6467 | 99.77% | 3 | 12 | 90.01% | 10.49% | 0 | 0.071696 | 1 | 1.5632 | 0.11207 | High | High | Low | 1702 | 1461 | 0.071696 | 46.4061 | 0.5199%
SAN BENITO 210488772 | SAN BENITO 2104 | CENTRAL COAST | 23.9825 | 25.5059 | 54.82% | 18 | 5 | 55.63% | 0% | 0 | 0.071687 | 1 | 2.854 | 0.2046 | High | High | Medium | 1404 | 1462 | 0.071687 | 46.3344 | 0.5191%
HALSEY 11011704 | HALSEY 1101 | SIERRA | 12.7864 | 10 | 79.44% | 4 | 15 | 96.8% | 0% | 0 | 0.071684 | 1 | 2.4891 | 0.17843 | High | High | Medium | 1473 | 1463 | 0.071684 | 46.2627 | 0.5183%
UKIAH 1114408 | UKIAH 1114 | HUMBOLDT | 37.0058 | 66.3521 | 67.33% | 5 | 13 | 97.48% | 0% | 0 | 0.071452 | 1 | 2.1941 | 0.15678 | High | High | Low | 1534 | 1464 | 0.071452 | 46.191 | 0.5175%
CENTERVILLE 1101CB | CENTERVILLE 1101 | NORTH VALLEY | 0.015747 | 10 | 0% | 0 | 1 | 100% | 100% | 0 | 0.071117 | 1 | 3.1314 | 0.2227 | High | High | High | 1365 | 1465 | 0.071117 | 46.1196 | 0.5167%
LAYTONVILLE 1101402 | LAYTONVILLE 1101 | HUMBOLDT | 22.8392 | 79.1892 | 99.99% | 6 | 8 | 96.88% | 0% | 0 | 0.070954 | 1 | 0.97747 | 0.069355 | High | High | Low | 2049 | 1466 | 0.070954 | 46.0485 | 0.5159%
BRUNSWICK 110651484 | BRUNSWICK 1106 | SIERRA | 20.7709 | 48.7311 | 68.62% | 4 | 3 | 82.69% | 37.09% | 0 | 0.070762 | 1 | 2.3766 | 0.16817 | High | High | Medium | 1503 | 1467 | 0.070762 | 45.9775 | 0.5151%
GREEN VALLEY 210190860 | GREEN VALLEY 2101 | CENTRAL COAST | 3.8052 | 10 | 95.69% | 0 | 0 | 20.73% | 93.04% | 0 | 0.070746 | 1 | 3.19 | 0.22568 | High | High | High | 1359 | 1468 | 0.070746 | 45.9067 | 0.5143%
WILDWOOD 11011576 | WILDWOOD 1101 | NORTH VALLEY | 8.159 | 75.9447 | 99.97% | 1 | 4 | 100% | 0% | 0 | 0.070451 | 1 | 0.98125 | 0.06913 | High | High | Low | 2050 | 1469 | 0.070451 | 45.836 | 0.5135%
GUALALA 111223444 | GUALALA 1112 | HUMBOLDT | 14.5206 | 71.4539 | 16.53% | 7 | 15 | 100% | 0% | 0 | 0.069914 | 1 | 1.7456 | 0.12204 | High | High | Low | 1655 | 1470 | 0.069914 | 45.7655 | 0.5127%
SYCAMORE CREEK 11112014 | SYCAMORE CREEK 1111 | NORTH VALLEY | 22.6561 | 53.0217 | 99.04% | 1 | 4 | 99.97% | 25.97% | 0 | 0.069882 | 1 | 2.8512 | 0.19925 | High | High | Medium | 1416 | 1471 | 0.069882 | 45.6956 | 0.5119%
PARADISE 11042470 | PARADISE 1104 | NORTH VALLEY | 5.1264 | 10.5174 | 41.48% | 3 | 8 | 44.97% | 100% | 0 | 0.069868 | 1 | 4.3221 | 0.30197 | High | High | High | 1233 | 1472 | 0.069868 | 45.6257 | 0.5111%
BIG BASIN 11022253 | BIG BASIN 1102 | CENTRAL COAST | 1.463 | 10 | 16.17% | 0 | 0 | 100% | 100% | 0 | 0.069736 | 1 | 2.4273 | 0.16927 | High | High | Medium | 1502 | 1473 | 0.069736 | 45.5559 | 0.5104%
FROGTOWN 170212282 | FROGTOWN 1702 | STOCKTON | 36.3191 | 39.3074 | 54.5% | 2 | 7 | 100% | 0% | 0 | 0.069451 | 1 | 2.557 | 0.17759 | High | High | Medium | 1475 | 1474 | 0.069451 | 45.4861 | 0.5096%
ROB ROY 210410714 | ROB ROY 2104 | CENTRAL COAST | 15.4812 | 20.2777 | 49.42% | 12 | 6 | 79.24% | 0% | 0 | 0.069343 | 1 | 2.8504 | 0.19765 | High | High | Medium | 1419 | 1475 | 0.069343 | 45.4167 | 0.5088%
CURTIS 17036064 | CURTIS 1703 | YOSEMITE | 19.198 | 23.357 | 96.92% | 3 | 15 | 97.54% | 0% | 0 | 0.069239 | 1 | 2.8169 | 0.19504 | High | High | Medium | 1421 | 1476 | 0.069239 | 45.3473 | 0.508%
PLACERVILLE 2106CB | PLACERVILLE 2106 | SIERRA | 6.6569 | 17.5661 | 15.58% | 1 | 6 | 100% | 71.65% | 0 | 0.069168 | 1 | 2.4573 | 0.16996 | High | High | Medium | 1499 | 1477 | 0.069168 | 45.2781 | 0.5072%
OAKLAND K 1101CR178 | OAKLAND K 1101 | EAST BAY | 0.32942 | 10 | 9.622% | 0 | 2 | 100% | 100% | 0 | 0.068955 | 1 | 4.1976 | 0.28945 | High | High | High | 1249 | 1478 | 0.068955 | 45.2089 | 0.5065%
GIRVAN 1101323094 | GIRVAN 1101 | NORTH VALLEY | 36.2683 | 55.5247 | 99.98% | 1 | 3 | 100% | 0% | 0 | 0.068706 | 1 | 1.1596 | 0.079672 | High | High | Low | 1937 | 1479 | 0.068706 | 45.14 | 0.5057%
PAUL SWEET 2109CB | PAUL SWEET 2109 | CENTRAL COAST | 4.2704 | 10 | 67.66% | 4 | 1 | 34.14% | 43.22% | 0 | 0.068584 | 1 | 4.0374 | 0.2769 | High | High | High | 1268 | 1480 | 0.068584 | 45.0713 | 0.5049%
FORT BRAGG A 110235592 | FORT BRAGG A 1102 | HUMBOLDT | 13.0568 | 10.5094 | 9.263% | 19 | 29 | 100% | 0% | 0 | 0.068352 | 1 | 1.999 | 0.13663 | High | High | Low | 1600 | 1481 | 0.068352 | 45.0027 | 0.5042%
HIGGINS 110950072 | HIGGINS 1109 | SIERRA | 42.3856 | 25.4799 | 92.02% | 2 | 15 | 100% | 0% | 0 | 0.068313 | 1 | 2.5573 | 0.1747 | High | High | Medium | 1482 | 1482 | 0.068313 | 44.9343 | 0.5034%
HIGGINS 110950078 | HIGGINS 1109 | SIERRA | 48.4681 | 37.033 | 99.96% | 1 | 15 | 100% | 0% | 0 | 0.068168 | 1 | 2.5691 | 0.17513 | High | High | Medium | 1480 | 1483 | 0.068168 | 44.866 | 0.5026%
WOODACRE 1101CB | WOODACRE 1101 | NORTH BAY | 2.7386 | 31.1084 | 27.17% | 14 | 8 | 96.75% | 56.15% | 0 | 0.068112 | 1 | 4.3841 | 0.29861 | High | High | High | 1236 | 1484 | 0.068112 | 44.7979 | 0.5019%
NARROWS 21052228 | NARROWS 2105 | SIERRA | 20.4861 | 37.6865 | 94.14% | 3 | 11 | 96.44% | 0% | 0 | 0.06797 | 1 | 2.8311 | 0.19243 | High | High | Medium | 1432 | 1485 | 0.06797 | 44.7298 | 0.5011%
MONROE 210765424 | MONROE 2107 | SONOMA | 0.75479 | 10 | 100% | 0 | 0 | 14.79% | 100% | 0 | 0.067899 | 1 | 3.4252 | 0.23257 | High | High | High | 1348 | 1486 | 0.067899 | 44.6618 | 0.5003%
CEDAR CREEK 1101CB | CEDAR CREEK 1101 | NORTH VALLEY | 15.4651 | 37.802 | 95.68% | 0 | 0 | 100% | 38.1% | 1 | 0.067896 | 1 | 1.0626 | 0.072148 | High | High | Low | 2014 | 1487 | 0.067896 | 44.5939 | 0.4996%
FORT SEWARD 1122CB | FORT SEWARD 1122 | HUMBOLDT | 17.3427 | 75.2963 | 100% | 3 | 11 | 79.07% | 0% | 0 | 0.067846 | 1 | 0.93948 | 0.06374 | High | High | Low | 2120 | 1488 | 0.067846 | 44.526 | 0.4988%
PAUL SWEET 210610424 | PAUL SWEET 2106 | CENTRAL COAST | 5.7029 | 19.0788 | 48.59% | 2 | 1 | 80% | 79.15% | 0 | 0.067843 | 1 | 3.6484 | 0.24751 | High | High | High | 1319 | 1489 | 0.067843 | 44.4581 | 0.4981%
CEDAR CREEK 11011664 | CEDAR CREEK 1101 | NORTH VALLEY | 29.6947 | 28.7537 | 98.78% | 0 | 12 | 100% | 0% | 0 | 0.067598 | 1 | 1.3051 | 0.088223 | High | High | Low | 1844 | 1490 | 0.067598 | 44.3903 | 0.4973%
MONTICELLO 1101718 | MONTICELLO 1101 | NORTH BAY | 26.9011 | 60.1825 | 63.96% | 4 | 11 | 90.43% | 0% | 0 | 0.067428 | 1 | 2.6725 | 0.1802 | High | High | Medium | 1471 | 1491 | 0.067428 | 44.3227 | 0.4965%
OILFIELDS 110383158 | OILFIELDS 1103 | CENTRAL COAST | 18.1787 | 60.504 | 100% | 0 | 4 | 93.79% | 0% | 0 | 0.067417 | 1 | 0.87957 | 0.059298 | High | High | Low | 2192 | 1492 | 0.067417 | 44.2553 | 0.4958%
OREGON TRAIL 11041634 | OREGON TRAIL 1104 | NORTH VALLEY | 17.7143 | 33.9199 | 93.56% | 1 | 0 | 97.56% | 0% | 0 | 0.067366 | 1 | 2.7053 | 0.18225 | High | High | Medium | 1466 | 1493 | 0.067366 | 44.1879 | 0.495%
TASSAJARA 2104CB | TASSAJARA 2104 | DIABLO | 0.10747 | 10 | 0% | 0 | 1 | 9.092% | 0% | 0 | 0.0059985 | 11.2183 | 4.1264 | 0.27768 | Low | Low | High | 1266 | 1494 | 0.067293 | 44.1205 | 0.4943%
SOBRANTE 1102L510R | SOBRANTE 1102 | DIABLO | 9.7593 | 10 | 23.81% | 5 | 6 | 100% | 0% | 0 | 0.067265 | 1 | 3.176 | 0.21364 | High | High | High | 1384 | 1495 | 0.067265 | 44.0532 | 0.4935%
FORT BRAGG A 1102956 | FORT BRAGG A 1102 | HUMBOLDT | 10.8506 | 10 | 43.99% | 19 | 14 | 88.12% | 0% | 0 | 0.067263 | 1 | 2.1825 | 0.1468 | High | High | Low | 1564 | 1496 | 0.067263 | 43.9859 | 0.4928%
ATASCADERO 1101A50 | ATASCADERO 1101 | LOS PADRES | 19.8065 | 10 | 78.19% | 4 | 9 | 94.43% | 5.217% | 1 | 0.066857 | 1 | 3.2682 | 0.2185 | High | High | High | 1373 | 1497 | 0.066857 | 43.9187 | 0.492%
COTATI 1103148 | COTATI 1103 | SONOMA | 14.0913 | 49.2874 | 1.408% | 9 | 10 | 90.64% | 0% | 0 | 0.066855 | 1 | 1.9842 | 0.13266 | High | High | Low | 1617 | 1498 | 0.066855 | 43.8518 | 0.4913%
FORT BRAGG A 11014622 | FORT BRAGG A 1101 | HUMBOLDT | 13.4572 | 19.3216 | 4.804% | 12 | 12 | 100% | 0% | 0 | 0.066763 | 1 | 1.5197 | 0.10146 | High | High | Low | 1757 | 1499 | 0.066763 | 43.785 | 0.4905%
OAKLAND K 1104CR206 | OAKLAND K 1104 | EAST BAY | 1.7925 | 10 | 7.751% | 0 | 1 | 100% | 100% | 0 | 0.066653 | 1 | 4.2537 | 0.28352 | High | High | High | 1257 | 1500 | 0.066653 | 43.7182 | 0.4898%
PARADISE 11031231 | PARADISE 1103 | NORTH VALLEY | 2.541 | 10 | 17.59% | 3 | 2 | 90.53% | 96.98% | 0 | 0.066519 | 1 | 3.6926 | 0.24563 | High | High | High | 1324 | 1501 | 0.066519 | 43.6515 | 0.489%
STILLWATER 1102CB | STILLWATER 1102 | NORTH VALLEY | 25.0709 | 15.0844 | 83.36% | 3 | 7 | 99.96% | 0% | 0 | 0.066396 | 1 | 2.0763 | 0.13786 | High | High | Low | 1593 | 1502 | 0.066396 | 43.585 | 0.4883%
PAUL SWEET 210710986 | PAUL SWEET 2107 | CENTRAL COAST | 10.6088 | 30.4341 | 52.14% | 3 | 2 | 53.14% | 44.56% | 0 | 0.066361 | 1 | 2.8689 | 0.19038 | High | High | Medium | 1438 | 1503 | 0.066361 | 43.5186 | 0.4875%
MORGAN HILL 2111CB | MORGAN HILL 2111 | SAN JOSE | 0.34374 | 10 | 12.74% | 0 | 0 | 12.6% | 0% | 0 | 0.0059141 | 11.2183 | 3.3152 | 0.21995 | Low | Low | High | 1371 | 1504 | 0.066347 | 43.4523 | 0.4868%
WEIMAR 11012084 | WEIMAR 1101 | SIERRA | 18.471 | 37.3973 | 99.11% | 2 | 13 | 100% | 0% | 0 | 0.066085 | 1 | 1.6608 | 0.10976 | High | High | Low | 1710 | 1505 | 0.066085 | 43.3859 | 0.486%
ROB ROY 210571630 | ROB ROY 2105 | CENTRAL COAST | 1.807 | 10 | 61.71% | 5 | 2 | 96.47% | 60.73% | 0 | 0.066075 | 1 | 3.2318 | 0.21354 | High | High | High | 1385 | 1506 | 0.066075 | 43.3198 | 0.4853%
SAN RAFAEL 11079532 | SAN RAFAEL 1107 | NORTH BAY | 0.83024 | 10 | 59.24% | 0 | 0 | 45.34% | 100% | 0 | 0.066016 | 1 | 4.5265 | 0.29882 | High | High | High | 1235 | 1507 | 0.066016 | 43.2538 | 0.4846%
FROGTOWN 17011623 | FROGTOWN 1701 | STOCKTON | 15.2549 | 27.6688 | 92.79% | 0 | 7 | 100% | 0% | 0 | 0.065843 | 1 | 3.0596 | 0.20145 | High | High | Medium | 1409 | 1508 | 0.065843 | 43.1877 | 0.4838%
ELK CREEK 110137334 | ELK CREEK 1101 | NORTH VALLEY | 9.7022 | 59.8583 | 100% | 0 | 0 | 100% | 0% | 0 | 0.065795 | 1 | 1.1103 | 0.073051 | High | High | Low | 2005 | 1509 | 0.065795 | 43.1219 | 0.4831%
COTTONWOOD 11031348 | COTTONWOOD 1103 | NORTH VALLEY | 25.9721 | 33.8083 | 99.17% | 2 | 10 | 81.37% | 0% | 0 | 0.065681 | 1 | 1.5413 | 0.10123 | High | High | Low | 1760 | 1510 | 0.065681 | 43.0561 | 0.4824%
CURTIS 170411300 | CURTIS 1704 | YOSEMITE | 3.6591 | 33.4299 | 41.14% | 0 | 2 | 100% | 62.71% | 0 | 0.065584 | 1 | 2.8287 | 0.18552 | High | High | Medium | 1453 | 1511 | 0.065584 | 42.9904 | 0.4816%
LAURELES 11116421 | LAURELES 1111 | CENTRAL COAST | 1.7279 | 54.1809 | 100% | 1 | 1 | 100% | 0% | 0 | 0.065512 | 1 | 2.115 | 0.13856 | High | High | Low | 1590 | 1512 | 0.065512 | 42.9248 | 0.4809%
MONTICELLO 1101630 | MONTICELLO 1101 | NORTH BAY | 17.6986 | 68.0589 | 26.54% | 2 | 4 | 90.07% | 0% | 0 | 0.065491 | 1 | 2.2846 | 0.14962 | High | High | Medium | 1553 | 1513 | 0.065491 | 42.8593 | 0.4801%
DIAMOND SPRINGS 11062100 | DIAMOND SPRINGS 1106 | SIERRA | 38.9747 | 13.5244 | 95.18% | 3 | 8 | 100% | 0% | 0 | 0.064847 | 1 | 2.1227 | 0.13765 | High | High | Low | 1595 | 1514 | 0.064847 | 42.7938 | 0.4794%
OAKLAND K 1101CR346 | OAKLAND K 1101 | EAST BAY | 0.18736 | 10 | 0% | 1 | 2 | 100% | 100% | 0 | 0.064827 | 1 | 4.1726 | 0.2705 | High | High | High | 1283 | 1515 | 0.064827 | 42.729 | 0.4787%
WILLITS 11032506 | WILLITS 1103 | HUMBOLDT | 12.7779 | 67.5224 | 88.76% | 15 | 4 | 100% | 16.88% | 0 | 0.06476 | 1 | 1.7937 | 0.11616 | High | High | Low | 1684 | 1516 | 0.06476 | 42.6642 | 0.478%
TEMPLETON 2113CB | TEMPLETON 2113 | LOS PADRES | 0.49234 | 10 | 22.58% | 0 | 0 | 1.889% | 0% | 0 | 0.0057624 | 11.2183 | 2.6278 | 0.16987 | Low | Low | Medium | 1500 | 1517 | 0.064645 | 42.5994 | 0.4772%
BANGOR 11011804 | BANGOR 1101 | NORTH VALLEY | 42.8631 | 13.9127 | 93.17% | 8 | 9 | 100% | 3.48% | 0 | 0.064625 | 1 | 2.3914 | 0.15455 | High | High | Medium | 1542 | 1518 | 0.064625 | 42.5348 | 0.4765%
PHILO 11021308 | PHILO 1102 | HUMBOLDT | 31.8312 | 64.2643 | 100% | 9 | 11 | 100% | 0% | 0 | 0.06454 | 1 | 1.3663 | 0.088181 | High | High | Low | 1847 | 1519 | 0.06454 | 42.4701 | 0.4758%
LAYTONVILLE 110237586 | LAYTONVILLE 1102 | HUMBOLDT | 13.9719 | 83.5514 | 97.33% | 7 | 7 | 100% | 0% | 0 | 0.064508 | 1 | 1.0342 | 0.066716 | High | High | Low | 2080 | 1520 | 0.064508 | 42.4056 | 0.4751%
SAN RAFAEL 11081210 | SAN RAFAEL 1108 | NORTH BAY | 3.0269 | 13.7905 | 14.91% | 3 | 2 | 55.23% | 100% | 0 | 0.064455 | 1 | 4.5091 | 0.29063 | High | High | High | 1247 | 1521 | 0.064455 | 42.3411 | 0.4743%
PAUL SWEET 2105CB | PAUL SWEET 2105 | CENTRAL COAST | 8.1216 | 24.934 | 34.71% | 10 | 1 | 52.4% | 90.68% | 0 | 0.064304 | 1 | 3.3844 | 0.21763 | High | High | High | 1376 | 1522 | 0.064304 | 42.2766 | 0.4736%
SALT SPRINGS 21011232 | SALT SPRINGS 2101 | STOCKTON | 6.1779 | 10 | 100% | 4 | 2 | 68.77% | 0% | 0 | 0.064284 | 1 | 0.80663 | 0.051853 | High | High | Low | 2312 | 1523 | 0.064284 | 42.2123 | 0.4729%
PANOCHE 11034008 | PANOCHE 1103 | YOSEMITE | 35.3708 | 69.547 | 99.82% | 0 | 2 | 100% | 0% | 0 | 0.064167 | 1 | 0.65772 | 0.042204 | High | High | Low | 2491 | 1524 | 0.064167 | 42.148 | 0.4722%
UKIAH 1111534 | UKIAH 1111 | HUMBOLDT | 18.7979 | 74.5032 | 100% | 2 | 4 | 89.62% | 0% | 0 | 0.064153 | 1 | 1.8196 | 0.11673 | High | High | Low | 1682 | 1525 | 0.064153 | 42.0839 | 0.4715%
DESCHUTES 11011654 | DESCHUTES 1101 | NORTH VALLEY | 17.3592 | 41.2096 | 100% | 1 | 5 | 100% | 6.956% | 0 | 0.063997 | 1 | 1.5357 | 0.098281 | High | High | Low | 1781 | 1526 | 0.063997 | 42.0197 | 0.4707%
GARBERVILLE 11021510 | GARBERVILLE 1102 | HUMBOLDT | 13.0211 | 67.6864 | 30.88% | 5 | 7 | 100% | 0% | 0 | 0.063582 | 1 | 2.0147 | 0.1281 | High | High | Low | 1630 | 1527 | 0.063582 | 41.9557 | 0.47%
DEL MONTE 21043088 | DEL MONTE 2104 | CENTRAL COAST | 15.4442 | 31.6262 | 48.83% | 2 | 7 | 100% | 0% | 0 | 0.063303 | 1 | 1.9688 | 0.12463 | High | High | Low | 1644 | 1528 | 0.063303 | 41.8921 | 0.4693%
HALF MOON BAY 110148868 | HALF MOON BAY 1101 | PENINSULA | 1.1515 | 26.9273 | 98.35% | 0 | 1 | 38.91% | 72.96% | 0 | 0.06326 | 1 | 4.8763 | 0.30847 | High | High | High | 1226 | 1529 | 0.06326 | 41.8288 | 0.4686%
CURTIS 17058170 | CURTIS 1705 | YOSEMITE | 7.5122 | 10 | 100% | 1 | 19 | 95.23% | 28.76% | 0 | 0.063226 | 1 | 3.7646 | 0.23802 | High | High | High | 1341 | 1530 | 0.063226 | 41.7656 | 0.4679%
CURTIS 17039240 | CURTIS 1703 | YOSEMITE | 10.9351 | 23.2344 | 88.01% | 0 | 12 | 100% | 3.336% | 0 | 0.063182 | 1 | 1.4789 | 0.093439 | High | High | Low | 1807 | 1531 | 0.063182 | 41.7024 | 0.4672%
GRAYS FLAT 0401CB | GRAYS FLAT 0401 | NORTH VALLEY | 10.7057 | 82.9815 | 68.42% | 5 | 6 | 100% | 0% | 0 | 0.063148 | 1 | 1.4254 | 0.090014 | High | High | Low | 1833 | 1532 | 0.063148 | 41.6392 | 0.4665%
CLARKSVILLE 210951744 | CLARKSVILLE 2109 | SIERRA | 0.69986 | 10 | 100% | 0 | 1 | 39% | 87.04% | 0 | 0.062946 | 1 | 3.1987 | 0.20135 | High | High | High | 1410 | 1533 | 0.062946 | 41.576 | 0.4658%
EL CERRITO G 111257953 | EL CERRITO G 1112 | EAST BAY | 0.7567 | 10 | 0% | 0 | 1 | 100% | 100% | 0 | 0.062783 | 1 | 5.378 | 0.33765 | High | High | High | 1190 | 1534 | 0.062783 | 41.5131 | 0.4651%
LOW GAP 110137498 | LOW GAP 1101 | HUMBOLDT | 16.1307 | 72.1022 | 98.67% | 6 | 3 | 100% | 0% | 0 | 0.062673 | 1 | 1.1505 | 0.072104 | High | High | Low | 2015 | 1535 | 0.062673 | 41.4503 | 0.4644%
CAMP EVERS 210611044 | CAMP EVERS 2106 | CENTRAL COAST | 6.5538 | 10.6438 | 23.66% | 12 | 2 | 52.73% | 81.08% | 0 | 0.062668 | 1 | 4.1597 | 0.26068 | High | High | High | 1295 | 1536 | 0.062668 | 41.3876 | 0.4637%
NOTRE DAME 11042537 | NOTRE DAME 1104 | NORTH VALLEY | 5.2925 | 55.6781 | 100% | 0 | 0 | 100% | 22.56% | 0 | 0.062104 | 1 | 3.2088 | 0.19928 | High | High | High | 1415 | 1537 | 0.062104 | 41.325 | 0.463%
SAN RAFAEL 1101494 | SAN RAFAEL 1101 | NORTH BAY | 4.1663 | 10 | 20.21% | 1 | 4 | 47.93% | 100% | 0 | 0.062096 | 1 | 3.6785 | 0.22842 | High | High | High | 1352 | 1538 | 0.062096 | 41.2628 | 0.4623%
TEMPLETON 2110N32 | TEMPLETON 2110 | LOS PADRES | 28.0596 | 53.4927 | 95.78% | 1 | 9 | 94.62% | 0% | 0 | 0.061984 | 1 | 2.2723 | 0.14084 | High | High | Medium | 1579 | 1539 | 0.061984 | 41.2008 | 0.4616%
ARCATA 11225384 | ARCATA 1122 | HUMBOLDT | 15.2841 | 39.9172 | 40.09% | 14 | 5 | 87.62% | 0% | 0 | 0.061973 | 1 | 2.9263 | 0.18135 | High | High | Medium | 1469 | 1540 | 0.061973 | 41.1388 | 0.4609%
SAN RAFAEL 1101CB | SAN RAFAEL 1101 | NORTH BAY | 1.7156 | 10 | 28.81% | 3 | 3 | 39.77% | 100% | 1 | 0.061788 | 1 | 4.0124 | 0.24792 | High | High | High | 1318 | 1541 | 0.061788 | 41.0768 | 0.4602%
BEN LOMOND 04015400 | BEN LOMOND 0401 | CENTRAL COAST | 0.44316 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 4.4652 | 0.27487 | High | High | High | 1275 | 1542 | 0.061559 | 41.015 | 0.4595%
OAKLAND X 1104CR101 | OAKLAND X 1104 | EAST BAY | 0.017651 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 4.4296 | 0.27268 | High | High | High | 1276 | 1542 | 0.061559 | 40.9534 | 0.4588%
CURTIS 170511790 | CURTIS 1705 | YOSEMITE | 0.014226 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.2679 | 0.20117 | High | High | High | 1412 | 1542 | 0.061559 | 40.8919 | 0.4581%
SAN RAFAEL 11073323 | SAN RAFAEL 1107 | NORTH BAY | 0.13349 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 4.4049 | 0.27117 | High | High | High | 1280 | 1545 | 0.061559 | 40.8303 | 0.4574%
CAMP EVERS 210595050 | CAMP EVERS 2105 | CENTRAL COAST | 0.13882 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.9779 | 0.24488 | High | High | High | 1326 | 1545 | 0.061559 | 40.7688 | 0.4567%
CASTRO VALLEY 1108 | CASTRO VALLEY 1108 | MISSION | 0.019583 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.6623 | 0.22545 | High | High | High | 1360 | 1545 | 0.061559 | 40.7072 | 0.456%
BOLINAS 1101 | BOLINAS 1101 | NORTH BAY | 0.01843 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.2701 | 0.2013 | High | High | High | 1411 | 1545 | 0.061559 | 40.6457 | 0.4553%
KESWICK 1101CB | KESWICK 1101 | NORTH VALLEY | 0.016582 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.2562 | 0.20045 | High | High | High | 1414 | 1545 | 0.061559 | 40.5841 | 0.4547%
CALISTOGA 1101 | CALISTOGA 1101 | NORTH BAY | 0.0027683 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 2.3953 | 0.14745 | High | High | Medium | 1561 | 1545 | 0.061559 | 40.5225 | 0.454%
BIG RIVER 110179628 | BIG RIVER 1101 | HUMBOLDT | 14.7546 | 28.3298 | 27.17% | 16 | 19 | 100% | 0% | 0 | 0.06147 | 1 | 2.8171 | 0.17317 | Medium | Medium | Medium | 1487 | 1551 | 0.06147 | 40.461 | 0.4533%
CAMP EVERS 2103CB | CAMP EVERS 2103 | CENTRAL COAST | 0.092755 | 10 | 13.07% | 0 | 0 | 75.74% | 100% | 0 | 0.061458 | 1 | 2.7937 | 0.17169 | Medium | Medium | Medium | 1494 | 1552 | 0.061458 | 40.3995 | 0.4526%
BOLINAS 1101528 | BOLINAS 1101 | NORTH BAY | 2.2652 | 10 | 0% | 1 | 5 | 74.53% | 100% | 0 | 0.061356 | 1 | 3.4025 | 0.20876 | Medium | Medium | High | 1395 | 1553 | 0.061356 | 40.338 | 0.4519%
CALAVERAS CEMENT 1101585 | CALAVERAS CEMENT 1101 | STOCKTON | 14.1114 | 60.1241 | 100% | 0 | 9 | 100% | 0% | 0 | 0.061249 | 1 | 1.6439 | 0.10069 | Medium | Medium | Low | 1764 | 1554 | 0.061249 | 40.2767 | 0.4512%
WILDWOOD 110185112 | WILDWOOD 1101 | NORTH VALLEY | 6.7175 | 80.7667 | 100% | 4 | 6 | 100% | 0% | 0 | 0.061113 | 1 | 1.0754 | 0.065723 | Medium | Medium | Low | 2090 | 1555 | 0.061113 | 40.2154 | 0.4505%
SHINGLE SPRINGS 210985766 | SHINGLE SPRINGS 2109 | SIERRA | 18.4459 | 50.1321 | 99.71% | 3 | 4 | 100% | 0% | 0 | 0.06111 | 1 | 1.6977 | 0.10374 | Medium | Medium | Low | 1743 | 1556 | 0.06111 | 40.1543 | 0.4498%
FRUITLAND 114263170 | FRUITLAND 1142 | HUMBOLDT | 12.2406 | 74.2009 | 74.01% | 12 | 5 | 90.64% | 0% | 0 | 0.061047 | 1 | 1.7809 | 0.10872 | Medium | Medium | Low | 1716 | 1557 | 0.061047 | 40.0932 | 0.4492%
SAN RAFAEL 1107714160 | SAN RAFAEL 1107 | NORTH BAY | 2.7558 | 15.5208 | 10.99% | 0 | 10 | 98.34% | 63.23% | 0 | 0.060966 | 1 | 4.37 | 0.26642 | Medium | Medium | High | 1288 | 1558 | 0.060966 | 40.0322 | 0.4485%
OAKHURST 11016220 | OAKHURST 1101 | YOSEMITE | 20.9199 | 34.4609 | 88.69% | 0 | 15 | 100% | 0% | 0 | 0.060711 | 1 | 1.9872 | 0.12065 | Medium | Medium | Low | 1660 | 1559 | 0.060711 | 39.9712 | 0.4478%
SISQUOC 1103M98 | SISQUOC 1103 | LOS PADRES | 6.4595 | 29.4274 | 100% | 0 | 1 | 65.51% | 60.21% | 1 | 0.060705 | 1 | 0.90853 | 0.055153 | Medium | Medium | Low | 2257 | 1560 | 0.060705 | 39.9105 | 0.4471%
FROGTOWN 170291134 | FROGTOWN 1702 | STOCKTON | 14.7309 | 23.5525 | 81.54% | 0 | 12 | 92.7% | 0% | 0 | 0.060562 | 1 | 1.9356 | 0.11722 | Medium | Medium | Low | 1678 | 1561 | 0.060562 | 39.8498 | 0.4464%
DIAMOND SPRINGS 110610587 | DIAMOND SPRINGS 1106 | SIERRA | 21.9902 | 32.7231 | 99.97% | 4 | 2 | 100% | 0% | 0 | 0.060422 | 1 | 2.0865 | 0.12607 | Medium | Medium | Low | 1640 | 1562 | 0.060422 | 39.7892 | 0.4458%
GREENBRAE 11031260 | GREENBRAE 1103 | NORTH BAY | 2.3256 | 16.3667 | 42.46% | 2 | 2 | 86.56% | 70.2% | 0 | 0.060164 | 1 | 4.0042 | 0.24091 | Medium | Medium | High | 1333 | 1563 | 0.060164 | 39.7288 | 0.4451%
PHILO 110137222 | PHILO 1101 | HUMBOLDT | 25.4322 | 53.3862 | 64.87% | 9 | 12 | 100% | 0% | 0 | 0.060092 | 1 | 0.9025 | 0.054233 | Medium | Medium | Low | 2270 | 1564 | 0.060092 | 39.6686 | 0.4444%
DOBBINS 11015202 | DOBBINS 1101 | SIERRA | 15.7094 | 33.0821 | 86.66% | 1 | 6 | 92.01% | 0% | 0 | 0.059877 | 1 | 1.9749 | 0.11825 | Medium | Medium | Low | 1671 | 1565 | 0.059877 | 39.6085 | 0.4437%
MAPLE CREEK 1101CB | MAPLE CREEK 1101 | HUMBOLDT | 9.8748 | 78.7819 | 78.72% | 13 | 5 | 66.88% | 0% | 0 | 0.059846 | 1 | 1.7771 | 0.10635 | Medium | Medium | Low | 1730 | 1566 | 0.059846 | 39.5487 | 0.4431%
WYANDOTTE 11071510 | WYANDOTTE 1107 | NORTH VALLEY | 25.4968 | 11.1229 | 100% | 1 | 4 | 100% | 0% | 0 | 0.05976 | 1 | 3.0899 | 0.18465 | Medium | Medium | High | 1456 | 1567 | 0.05976 | 39.4888 | 0.4424%
HATTON 11019220 | HATTON 1101 | CENTRAL COAST | 2.6965 | 89.4573 | 0% | 1 | 3 | 100% | 51.79% | 0 | 0.059721 | 1 | 1.81 | 0.10809 | Medium | Medium | Low | 1722 | 1568 | 0.059721 | 39.4291 | 0.4417%
CLOVERDALE 11024646 | CLOVERDALE 1102 | SONOMA | 14.4526 | 74.9071 | 80.61% | 2 | 4 | 97.6% | 0% | 0 | 0.059667 | 1 | 2.0674 | 0.12335 | Medium | Medium | Low | 1650 | 1569 | 0.059667 | 39.3693 | 0.441%
DIAMOND SPRINGS 1104CB | DIAMOND SPRINGS 1104 | SIERRA | 6.9541 | 10 | 49.56% | 0 | 3 | 69.41% | 79.56% | 0 | 0.059614 | 1 | 3.1336 | 0.18681 | Medium | Medium | High | 1449 | 1570 | 0.059614 | 39.3097 | 0.4404%
EL CERRITO G 1105BR160 | EL CERRITO G 1105 | EAST BAY | 7.9453 | 33.1195 | 38.34% | 5 | 6 | 69.23% | 42.93% | 0 | 0.059441 | 1 | 4.1032 | 0.2439 | Medium | Medium | High | 1327 | 1571 | 0.059441 | 39.2501 | 0.4397%
MIDDLETOWN 1103830 | MIDDLETOWN 1103 | HUMBOLDT | 23.5041 | 79 | 88.01% | 1 | 2 | 60.51% | 36.87% | 0 | 0.059437 | 1 | 2.354 | 0.13991 | Medium | Medium | Medium | 1584 | 1572 | 0.059437 | 39.1906 | 0.439%
VOLTA 1101CB | VOLTA 1101 | NORTH VALLEY | 9.2068 | 22.5796 | 72.56% | 6 | 5 | 100% | 27.96% | 0 | 0.059425 | 1 | 1.1139 | 0.066194 | Medium | Medium | Low | 2086 | 1573 | 0.059425 | 39.1312 | 0.4384%
PUEBLO 2102656 | PUEBLO 2102 | NORTH BAY | 0.064775 | 10 | 100% | 0 | 0 | 0.3672% | 100% | 0 | 0.059306 | 1 | 3.5617 | 0.21123 | Medium | Medium | High | 1391 | 1574 | 0.059306 | 39.0718 | 0.4377%
MC KEE 1111711900 | MC KEE 1111 | SAN JOSE | 8.3733 | 57.1059 | 68.22% | 0 | 5 | 66.5% | 0% | 0 | 0.059287 | 1 | 4.0165 | 0.23813 | Medium | Medium | High | 1339 | 1575 | 0.059287 | 39.0125 | 0.4371%
LAURELES 111268454 | LAURELES 1112 | CENTRAL COAST | 8.3342 | 11.1816 | 20.6% | 3 | 7 | 75.56% | 0% | 0 | 0.059265 | 1 | 2.3713 | 0.14054 | Medium | Medium | Medium | 1580 | 1576 | 0.059265 | 38.9532 | 0.4364%
CLAY 110113442 | CLAY 1101 | STOCKTON | 25.1981 | 33.4611 | 98.28% | 1 | 6 | 81.01% | 0% | 0 | 0.059218 | 1 | 2.7463 | 0.16263 | Medium | Medium | Medium | 1518 | 1577 | 0.059218 | 38.8939 | 0.4357%
FROGTOWN 1702290609 | FROGTOWN 1702 | STOCKTON | 18.0385 | 28.1983 | 98.5% | 3 | 10 | 100% | 0% | 0 | 0.059181 | 1 | 2.4612 | 0.14566 | Medium | Medium | Medium | 1571 | 1578 | 0.059181 | 38.8347 | 0.4351%
BELL 11082202 | BELL 1108 | SIERRA | 31.9475 | 20.6823 | 70.59% | 0 | 8 | 96.19% | 0% | 0 | 0.059129 | 1 | 2.7384 | 0.16192 | Medium | Medium | Medium | 1520 | 1579 | 0.059129 | 38.7755 | 0.4344%
CAMP EVERS 21035402 | CAMP EVERS 2103 | CENTRAL COAST | 2.8538 | 10 | 29.07% | 11 | 2 | 42.31% | 90.21% | 0 | 0.05912 | 1 | 3.1651 | 0.18712 | Medium | Medium | High | 1448 | 1580 | 0.05912 | 38.7164 | 0.4337%
WILLOW CREEK 11033090 | WILLOW CREEK 1103 | HUMBOLDT | 10.7823 | 82.4459 | 100% | 5 | 3 | 100% | 0% | 0 | 0.058956 | 1 | 0.99063 | 0.058403 | Medium | Medium | Low | 2204 | 1581 | 0.058956 | 38.6573 | 0.4331%
POTTER VALLEY P H 110576498 | POTTER VALLEY P H 1105 | HUMBOLDT | 14.8769 | 81.1366 | 60.61% | 2 | 8 | 100% | 0% | 0 | 0.058866 | 1 | 1.1067 | 0.065148 | Medium | Medium | Low | 2098 | 1582 | 0.058866 | 38.5983 | 0.4324%
HICKS 2103LB50 | HICKS 2103 | SAN JOSE | 10.8958 | 72.4633 | 80.45% | 3 | 2 | 82.11% | 27.73% | 0 | 0.058713 | 1 | 3.5349 | 0.20754 | Medium | Medium | High | 1398 | 1583 | 0.058713 | 38.5394 | 0.4318%
BIG RIVER 11013002 | BIG RIVER 1101 | HUMBOLDT | 6.8985 | 10 | 4.337% | 11 | 17 | 83.84% | 0% | 0 | 0.058669 | 1 | 2.6346 | 0.15457 | Medium | Medium | Medium | 1540 | 1584 | 0.058669 | 38.4807 | 0.4311%
MOUNTAIN QUARRIES 21011350 | MOUNTAIN QUARRIES 2101 | SIERRA | 21.7386 | 30.8372 | 63.86% | 7 | 7 | 100% | 0% | 0 | 0.058591 | 1 | 2.4681 | 0.14461 | Medium | Medium | Medium | 1576 | 1585 | 0.058591 | 38.422 | 0.4304%
ATASCADERO 1103A14 | ATASCADERO 1103 | LOS PADRES | 25.1166 | 61.0387 | 72.56% | 0 | 2 | 99.83% | 36.1% | 0 | 0.058565 | 1 | 1.1767 | 0.068916 | Medium | Medium | Low | 2053 | 1586 | 0.058565 | 38.3635 | 0.4298%
CURTIS 170234426 | CURTIS 1702 | YOSEMITE | 4.917 | 10 | 82.09% | 0 | 4 | 71.87% | 67.24% | 1 | 0.058493 | 1 | 3.3748 | 0.1974 | Medium | Medium | High | 1420 | 1587 | 0.058493 | 38.3049 | 0.4291%
CALPELLA 1101542 | CALPELLA 1101 | HUMBOLDT | 23.4567 | 35.4534 | 89.83% | 1 | 18 | 100% | 0% | 0 | 0.058405 | 1 | 1.4223 | 0.083068 | Medium | Medium | Low | 1897 | 1588 | 0.058405 | 38.2464 | 0.4285%
KING CITY 11037038 | KING CITY 1103 | CENTRAL COAST | 17.5881 | 72.8479 | 99.95% | 0 | 5 | 81.26% | 0% | 0 | 0.058354 | 1 | 2.1255 | 0.12403 | Medium | Medium | Low | 1645 | 1589 | 0.058354 | 38.188 | 0.4278%
SONOMA 1106CB | SONOMA 1106 | SONOMA | 0.46405 | 10 | 100% | 0 | 0 | 11.88% | 100% | 0 | 0.058298 | 1 | 3.6884 | 0.21503 | Medium | Medium | High | 1379 | 1590 | 0.058298 | 38.1296 | 0.4272%
ANTLER 11011378 | ANTLER 1101 | NORTH VALLEY | 23.3437 | 22.2502 | 87.11% | 6 | 14 | 92.94% | 12.19% | 1 | 0.058255 | 1 | 0.83529 | 0.04866 | Medium | Medium | Low | 2373 | 1591 | 0.058255 | 38.0713 | 0.4265%
PHILO 1102928 | PHILO 1102 | HUMBOLDT | 13.0575 | 61.4578 | 77.17% | 8 | 4 | 85.6% | 0% | 0 | 0.058135 | 1 | 0.90846 | 0.052813 | Medium | Medium | Low | 2294 | 1592 | 0.058135 | 38.0131 | 0.4259%
EL DORADO PH 210152456 | EL DORADO PH 2101 | SIERRA | 10.1963 | 62.6198 | 100% | 3 | 10 | 100% | 0% | 0 | 0.058118 | 1 | 1.007 | 0.058524 | Medium | Medium | Low | 2202 | 1593 | 0.058118 | 37.955 | 0.4252%
OILFIELDS 1103N62 | OILFIELDS 1103 | CENTRAL COAST | 5.5689 | 75.4181 | 98.3% | 0 | 2 | 100% | 0% | 0 | 0.05809 | 1 | 2.1974 | 0.12764 | Medium | Medium | Low | 1633 | 1594 | 0.05809 | 37.8968 | 0.4246%
FRUITLAND 11426054 | FRUITLAND 1142 | HUMBOLDT | 10.4759 | 81.7883 | 49.67% | 26 | 9 | 100% | 0% | 0 | 0.058078 | 1 | 1.5506 | 0.090055 | Medium | Medium | Low | 1832 | 1595 | 0.058078 | 37.8387 | 0.4239%
MILPITAS 1109XR082 | MILPITAS 1109 | SAN JOSE | 19.1832 | 53.2607 | 99.6% | 3 | 3 | 94.55% | 0% | 0 | 0.058023 | 1 | 3.5906 | 0.20834 | Medium | Medium | High | 1397 | 1596 | 0.058023 | 37.7807 | 0.4233%
PAUL SWEET 2106CB | PAUL SWEET 2106 | CENTRAL COAST | 5.2267 | 14.0145 | 33.08% | 1 | 5 | 37.05% | 92.49% | 0 | 0.057775 | 1 | 4.0611 | 0.23463 | Medium | Medium | High | 1345 | 1597 | 0.057775 | 37.7226 | 0.4226%
GREEN VALLEY 210136820 | GREEN VALLEY 2101 | CENTRAL COAST | 6.5982 | 36.5973 | 46.31% | 12 | 2 | 35.52% | 88.5% | 0 | 0.057708 | 1 | 3.2834 | 0.18948 | Medium | Medium | High | 1441 | 1598 | 0.057708 | 37.6649 | 0.422%
DEL MONTE 21042624 | DEL MONTE 2104 | CENTRAL COAST | 18.1708 | 31.8719 | 33.21% | 2 | 17 | 94.85% | 0% | 0 | 0.05749 | 1 | 3.2193 | 0.18508 | Medium | Medium | High | 1454 | 1599 | 0.05749 | 37.6072 | 0.4213%
LOS OSITOS 21033010 | LOS OSITOS 2103 | CENTRAL COAST | 30.8565 | 64.7553 | 97.74% | 3 | 10 | 99.12% | 0% | 0 | 0.057419 | 1 | 1.9613 | 0.11262 | Medium | Medium | Low | 1700 | 1600 | 0.057419 | 37.5497 | 0.4207%
GRASS VALLEY 11031700 | GRASS VALLEY 1103 | SIERRA | 21.5982 | 19.8547 | 93.5% | 3 | 7 | 99.55% | 0% | 0 | 0.057412 | 1 | 2.5384 | 0.14573 | Medium | Medium | Medium | 1570 | 1601 | 0.057412 | 37.4923 | 0.42%
FRENCH GULCH 11022902 | FRENCH GULCH 1102 | NORTH VALLEY | 6.9875 | 84.5854 | 100% | 0 | 4 | 100% | 0% | 0 | 0.057283 | 1 | 0.72881 | 0.041748 | Medium | Medium | Low | 2500 | 1602 | 0.057283 | 37.4348 | 0.4194%
BELL 11082226 | BELL 1108 | SIERRA | 24.7638 | 11.2765 | 87.34% | 1 | 8 | 97.2% | 0% | 0 | 0.057141 | 1 | 2.363 | 0.13503 | Medium | Medium | Medium | 1603 | 1603 | 0.057141 | 37.3776 | 0.4187%
SOBRANTE 1102L520R | SOBRANTE 1102 | DIABLO | 7.4675 | 10 | 48.68% | 1 | 16 | 100% | 8.05% | 0 | 0.05711 | 1 | 3.39 | 0.19361 | Medium | Medium | High | 1428 | 1604 | 0.05711 | 37.3204 | 0.4181%
ROSSMOOR 1106CB | ROSSMOOR 1106 | DIABLO | 1.4865 | 10 | 68.08% | 0 | 8 | 30.91% | 92.75% | 0 | 0.057048 | 1 | 3.8412 | 0.21913 | Medium | Medium | High | 1372 | 1605 | 0.057048 | 37.2633 | 0.4175%
SOBRANTE 1103N510R | SOBRANTE 1103 | DIABLO | 0.050894 | 10 | 0% | 1 | 0 | 5.822% | 0% | 0 | 0.0050449 | 11.2183 | 3.422 | 0.19367 | Low | Low | High | 1427 | 1606 | 0.056595 | 37.2063 | 0.4168%
LAKEWOOD 210964992 | LAKEWOOD 2109 | DIABLO | 0.21818 | 10 | 100% | 0 | 0 | 8.548% | 100% | 0 | 0.056493 | 1 | 4.016 | 0.22688 | Medium | Medium | High | 1354 | 1607 | 0.056493 | 37.1497 | 0.4162%
SANTA ROSA A 110439786 | SANTA ROSA A 1104 | SONOMA | 1.14 | 10 | 49.93% | 0 | 3 | 16.83% | 100% | 0 | 0.056488 | 1 | 3.7971 | 0.21449 | Medium | Medium | High | 1381 | 1608 | 0.056488 | 37.0932 | 0.4155%
CURTIS 170247488 | CURTIS 1702 | YOSEMITE | 18.0809 | 16.9513 | 84.37% | 2 | 17 | 87.6% | 0% | 0 | 0.05643 | 1 | 3.3854 | 0.19104 | Medium | Medium | High | 1435 | 1609 | 0.05643 | 37.0367 | 0.4149%
COARSEGOLD 2103CB | COARSEGOLD 2103 | YOSEMITE | 38.4222 | 32.3373 | 83.55% | 1 | 26 | 100% | 0% | 0 | 0.056308 | 1 | 1.858 | 0.10462 | Medium | Medium | Low | 1738 | 1610 | 0.056308 | 36.9803 | 0.4143%
SAN RAFAEL 11081457 | SAN RAFAEL 1108 | NORTH BAY | 0.58979 | 10 | 0% | 0 | 0 | 77.17% | 100% | 0 | 0.056282 | 1 | 4.8134 | 0.27091 | Medium | Medium | High | 1282 | 1611 | 0.056282 | 36.9239 | 0.4137%
SALT SPRINGS 21011216 | SALT SPRINGS 2101 | STOCKTON | 5.4385 | 73.7435 | 99.91% | 0 | 1 | 98.38% | 0% | 0 | 0.056184 | 1 | 0.30767 | 0.017286 | Medium | Medium | Low | 3058 | 1612 | 0.056184 | 36.8677 | 0.413%
RACETRACK 1703CB | RACETRACK 1703 | YOSEMITE | 15.5569 | 10 | 47.8% | 4 | 26 | 86.61% | 0% | 0 | 0.05588 | 1 | 2.884 | 0.16116 | Medium | Medium | Medium | 1521 | 1613 | 0.05588 | 36.8115 | 0.4124%
ANNAPOLIS 110176842 | ANNAPOLIS 1101 | HUMBOLDT | 5.647 | 81.667 | 98.52% | 2 | 3 | 100% | 0% | 0 | 0.055858 | 1 | 1.4662 | 0.0819 | Medium | Medium | Low | 1916 | 1614 | 0.055858 | 36.7556 | 0.4118%
AUBERRY 110137536 | AUBERRY 1101 | FRESNO | 5.4818 | 31.3295 | 100% | 3 | 2 | 100% | 20.77% | 1 | 0.055781 | 1 | 1.2846 | 0.071654 | Medium | Medium | Low | 2025 | 1615 | 0.055781 | 36.6997 | 0.4111%
OAKLAND K 1101CR170 | OAKLAND K 1101 | EAST BAY | 1.2514 | 10 | 10.22% | 0 | 3 | 100% | 84.34% | 0 | 0.055611 | 1 | 3.8581 | 0.21455 | Medium | Medium | High | 1380 | 1616 | 0.055611 | 36.644 | 0.4105%
PALMER 110198478 | PALMER 1101 | LOS PADRES | 4.9874 | 64.4051 | 90.52% | 0 | 0 | 100% | 0% | 0 | 0.05552 | 1 | 1.0612 | 0.058918 | Medium | Medium | Low | 2197 | 1617 | 0.05552 | 36.5883 | 0.4099%
CURTIS 17029220 | CURTIS 1702 | YOSEMITE | 11.0663 | 17.9965 | 77.35% | 2 | 13 | 99.21% | 0.02567% | 0 | 0.05548 | 1 | 3.3526 | 0.186 | Medium | Medium | High | 1451 | 1618 | 0.05548 | 36.5328 | 0.4093%
RINCON 1101576 | RINCON 1101 | SONOMA | 2.0608 | 10 | 77.6% | 0 | 6 | 19.69% | 79.16% | 0 | 0.055451 | 1 | 2.6301 | 0.14585 | Medium | Medium | Medium | 1569 | 1619 | 0.055451 | 36.4774 | 0.4087%
CALAVERAS CEMENT 110147968 | CALAVERAS CEMENT 1101 | STOCKTON | 17.4467 | 25.9867 | 99.97% | 0 | 4 | 100% | 6.1% | 1 | 0.055443 | 1 | 2.0882 | 0.11578 | Medium | Medium | Low | 1687 | 1620 | 0.055443 | 36.4219 | 0.408%
APPLE HILL 110313312 | APPLE HILL 1103 | SIERRA | 11.1165 | 24.9201 | 69.91% | 1 | 7 | 61.36% | 40.78% | 0 | 0.055379 | 1 | 2.1929 | 0.12144 | Medium | Medium | Low | 1657 | 1621 | 0.055379 | 36.3665 | 0.4074%
FULTON 110746958 | FULTON 1107 | SONOMA | 0.032131 | 10 | 100% | 0 | 0 | 6.208% | 100% | 0 | 0.055255 | 1 | 2.4591 | 0.13588 | Medium | Medium | Medium | 1601 | 1622 | 0.055255 | 36.3111 | 0.4068%
NORTH TOWER 2101CB | NORTH TOWER 2101 | NORTH BAY | 0.18972 | 10 | 0% | 0 | 0 | 4.663% | 0% | 0 | 0.0049217 | 11.2183 | 2.9474 | 0.16274 | Low | Low | Medium | 1517 | 1623 | 0.055213 | 36.2558 | 0.4062%
HOPLAND 11014626 | HOPLAND 1101 | HUMBOLDT | 24.0779 | 57.1108 | 92.12% | 0 | 5 | 79.18% | 0% | 0 | 0.055167 | 1 | 1.524 | 0.084074 | Medium | Medium | Low | 1883 | 1624 | 0.055167 | 36.2006 | 0.4055%
WEIMAR 11012058 | WEIMAR 1101 | SIERRA | 21.2651 | 19.5754 | 79.75% | 4 | 16 | 100% | 0% | 0 | 0.055164 | 1 | 1.8526 | 0.1022 | Medium | Medium | Low | 1752 | 1625 | 0.055164 | 36.1454 | 0.4049%
OAKLAND D 1112CR192 | OAKLAND D 1112 | EAST BAY | 2.6688 | 25.8444 | 29.93% | 2 | 4 | 64.82% | 77.45% | 0 | 0.054951 | 1 | 3.8636 | 0.21231 | Medium | Medium | High | 1388 | 1626 | 0.054951 | 36.0903 | 0.4043%
MONTICELLO 110137384 | MONTICELLO 1101 | NORTH BAY | 9.3433 | 47.0333 | 65.93% | 7 | 4 | 99.86% | 0% | 0 | 0.054846 | 1 | 2.4323 | 0.1334 | Medium | Medium | Medium | 1613 | 1627 | 0.054846 | 36.0353 | 0.4037%
MERCED FALLS 110287352 | MERCED FALLS 1102 | YOSEMITE | 26.2614 | 32.8974 | 99.99% | 0 | 0 | 98.93% | 0% | 0 | 0.054765 | 1 | 0.50877 | 0.027863 | Medium | Medium | Low | 2818 | 1628 | 0.054765 | 35.9805 | 0.4031%
HALF MOON BAY 11038920 | HALF MOON BAY 1103 | PENINSULA | 8.6186 | 37.4312 | 39.37% | 7 | 11 | 100% | 0% | 0 | 0.054692 | 1 | 3.3955 | 0.1857 | Medium | Medium | High | 1452 | 1629 | 0.054692 | 35.9257 | 0.4025%
OAKLAND X 1106CR006 | OAKLAND X 1106 | EAST BAY | 3.6093 | 38.5923 | 23.16% | 2 | 2 | 100% | 56.08% | 0 | 0.054619 | 1 | 3.186 | 0.17401 | Medium | Medium | High | 1484 | 1630 | 0.054619 | 35.871 | 0.4019%
OAKHURST 110210100 | OAKHURST 1102 | YOSEMITE | 9.1816 | 28.1335 | 94.5% | 4 | 24 | 77.46% | 0% | 0 | 0.054576 | 1 | 2.4338 | 0.13282 | Medium | Medium | Medium | 1616 | 1631 | 0.054576 | 35.8164 | 0.4012%
CASTRO VALLEY 1108MR243 | CASTRO VALLEY 1108 | MISSION | 5.5308 | 36.4789 | 12.29% | 0 | 3 | 99.61% | 62.99% | 0 | 0.054568 | 1 | 3.5499 | 0.19371 | Medium | Medium | High | 1426 | 1632 | 0.054568 | 35.7618 | 0.4006%
CORNING 110290036 | CORNING 1102 | NORTH VALLEY | 14.194 | 60.2901 | 81.06% | 0 | 11 | 98.89% | 0% | 0 | 0.054481 | 1 | 1.7462 | 0.095135 | Medium | Medium | Low | 1798 | 1633 | 0.054481 | 35.7073 | 0.4%
CAMP EVERS 2104CB | CAMP EVERS 2104 | CENTRAL COAST | 1.0591 | 10 | 55.62% | 0 | 2 | 23.71% | 100% | 0 | 0.05446 | 1 | 3.3876 | 0.18449 | Medium | Medium | High | 1458 | 1634 | 0.05446 | 35.6528 | 0.3994%
VIEJO 22029104 | VIEJO 2202 | CENTRAL COAST | 5.9155 | 10 | 5.95% | 8 | 7 | 99.2% | 0% | 0 | 0.054282 | 1 | 3.2793 | 0.17801 | Medium | Medium | High | 1474 | 1635 | 0.054282 | 35.5983 | 0.3988%
ROB ROY 210538430 | ROB ROY 2105 | CENTRAL COAST | 4.0485 | 27.4617 | 42.48% | 11 | 1 | 61.21% | 68.36% | 0 | 0.05425 | 1 | 3.498 | 0.18976 | Medium | Medium | High | 1439 | 1636 | 0.05425 | 35.544 | 0.3982%
DIAMOND SPRINGS 11042093 | DIAMOND SPRINGS 1104 | SIERRA | 7.2925 | 22.8545 | 79.86% | 0 | 2 | 83.65% | 44.87% | 0 | 0.053967 | 1 | 2.3806 | 0.12847 | Medium | Medium | Medium | 1628 | 1637 | 0.053967 | 35.4898 | 0.3976%
GRASS VALLEY 11012208 | GRASS VALLEY 1101 | SIERRA | 12.2835 | 20.913 | 70.74% | 4 | 7 | 96.31% | 0% | 0 | 0.053929 | 1 | 2.7592 | 0.1488 | Medium | Medium | Medium | 1557 | 1638 | 0.053929 | 35.4358 | 0.397%
FORT BRAGG A 110195294 | FORT BRAGG A 1101 | HUMBOLDT | 25.9363 | 28.0829 | 8.119% | 33 | 16 | 99.05% | 0% | 0 | 0.053875 | 1 | 0.98845 | 0.053253 | Medium | Medium | Low | 2286 | 1639 | 0.053875 | 35.3819 | 0.3964%
CAMP EVERS 210411048 | CAMP EVERS 2104 | CENTRAL COAST | 0.87487 | 10 | 18.94% | 3 | 1 | 63.94% | 100% | 0 | 0.053728 | 1 | 4.0099 | 0.21544 | Medium | Medium | High | 1378 | 1640 | 0.053728 | 35.328 | 0.3958%
FORT BRAGG A 1102418 | FORT BRAGG A 1102 | HUMBOLDT | 13.7424 | 13.0618 | 15.86% | 29 | 14 | 98.4% | 0% | 0 | 0.053533 | 1 | 3.1937 | 0.17097 | Medium | Medium | High | 1497 | 1641 | 0.053533 | 35.2743 | 0.3952%
CASTRO VALLEY 1106MR337 | CASTRO VALLEY 1106 | MISSION | 10.471 | 41.4878 | 74.2% | 2 | 2 | 55.31% | 63.23% | 0 | 0.053395 | 1 | 3.5101 | 0.18742 | Medium | Medium | High | 1447 | 1642 | 0.053395 | 35.2208 | 0.3946%
SALMON CREEK 1101194 | SALMON CREEK 1101 | SONOMA | 6.5546 | 49.1883 | 4.108% | 3 | 3 | 77.1% | 22.41% | 0 | 0.053234 | 1 | 2.5104 | 0.13364 | Medium | Medium | Medium | 1612 | 1643 | 0.053234 | 35.1674 | 0.394%
CURTIS 1702CB | CURTIS 1702 | YOSEMITE | 21.952 | 21.1187 | 82.49% | 5 | 14 | 95.73% | 0% | 0 | 0.0532 | 1 | 3.3587 | 0.17868 | Medium | Medium | High | 1472 | 1644 | 0.0532 | 35.1141 | 0.3934%
OCEANO 1104V38 | OCEANO 1104 | LOS PADRES | 12.9054 | 24.0827 | 46.82% | 5 | 8 | 68.56% | 8.41% | 1 | 0.053152 | 1 | 3.1233 | 0.16601 | Medium | Medium | High | 1508 | 1645 | 0.053152 | 35.0609 | 0.3928%
MORAGA 1104CB | MORAGA 1104 | DIABLO | 12.3977 | 11.1682 | 54.34% | 6 | 17 | 72.33% | 3.443% | 1 | 0.053103 | 1 | 3.5454 | 0.18827 | Medium | Medium | High | 1443 | 1646 | 0.053103 | 35.0078 | 0.3922%
RIO DELL 11024230 | RIO DELL 1102 | HUMBOLDT | 22.9435 | 79.495 | 27.47% | 20 | 5 | 99.94% | 0% | 0 | 0.05306 | 1 | 0.29839 | 0.015832 | Medium | Medium | Low | 3088 | 1647 | 0.05306 | 34.9547 | 0.3916%
RIO DELL 110275970 | RIO DELL 1102 | HUMBOLDT | 7.0738 | 89.4562 | 39.39% | 2 | 2 | 100% | 0% | 0 | 0.05303 | 1 | 1.3258 | 0.07031 | Medium | Medium | Low | 2042 | 1648 | 0.05303 | 34.9016 | 0.391%
CAMP EVERS 21035404 | CAMP EVERS 2103 | CENTRAL COAST | 2.6779 | 10 | 26.91% | 3 | 0 | 57.99% | 100% | 0 | 0.052978 | 1 | 2.9173 | 0.15455 | Medium | Medium | Medium | 1541 | 1649 | 0.052978 | 34.8486 | 0.3904%
CURTIS 170463502 | CURTIS 1704 | YOSEMITE | 10.4605 | 25.8863 | 57.75% | 1 | 16 | 100% | 0% | 0 | 0.052892 | 1 | 3.0037 | 0.15887 | Medium | Medium | Medium | 1528 | 1650 | 0.052892 | 34.7956 | 0.3898%
VOLTA 11011596 | VOLTA 1101 | NORTH VALLEY | 21.7972 | 45.4978 | 99.98% | 1 | 12 | 100% | 0% | 0 | 0.052789 | 1 | 0.25608 | 0.013518 | Medium | Medium | Low | 3120 | 1651 | 0.052789 | 34.7427 | 0.3892%
POSO MOUNTAIN 21014456 | POSO MOUNTAIN 2101 | KERN | 23.5359 | 61.9546 | 91.99% | 0 | 4 | 100% | 0% | 0 | 0.052745 | 1 | 2.0977 | 0.11064 | Medium | Medium | Low | 1707 | 1652 | 0.052745 | 34.6899 | 0.3886%
CASTRO VALLEY 1109MR334 | CASTRO VALLEY 1109 | MISSION | 5.7287 | 41.5825 | 24.73% | 0 | 3 | 90.6% | 49.57% | 0 | 0.052651 | 1 | 4.2098 | 0.22165 | Medium | Medium | High | 1369 | 1653 | 0.052651 | 34.6372 | 0.388%
SAN RAMON 2107MR287 | SAN RAMON 2107 | MISSION | 0.029952 | 10 | 100% | 0 | 0 | 0.9859% | 100% | 0 | 0.052586 | 1 | 3.3036 | 0.17373 | Medium | Medium | High | 1486 | 1654 | 0.052586 | 34.5845 | 0.3874%
ELK CREEK 11012106 | ELK CREEK 1101 | NORTH VALLEY | 13.2055 | 80.5547 | 100% | 0 | 1 | 100% | 0% | 0 | 0.052586 | 1 | 0.52019 | 0.027355 | Medium | Medium | Low | 2828 | 1655 | 0.052586 | 34.5319 | 0.3869%
ORINDA 0401CB | ORINDA 0401 | DIABLO | 0.11326 | 10 | 23.54% | 0 | 0 | 63.88% | 100% | 0 | 0.052555 | 1 | 3.4681 | 0.18227 | Medium | Medium | High | 1465 | 1656 | 0.052555 | 34.4794 | 0.3863%
VOLTA 110153118 | VOLTA 1101 | NORTH VALLEY | 9.6297 | 40.8133 | 100% | 0 | 1 | 100% | 0% | 0 | 0.05235 | 1 | 1.4426 | 0.075522 | Medium | Medium | Low | 1979 | 1657 | 0.05235 | 34.4268 | 0.3857%
CURTIS 1704803 | CURTIS 1704 | YOSEMITE | 9.5141 | 57.4155 | 65.91% | 1 | 6 | 100% | 27.61% | 0 | 0.05233 | 1 | 2.6661 | 0.13952 | Medium | Medium | Medium | 1585 | 1658 | 0.05233 | 34.3744 | 0.3851%
FRENCH GULCH 11021462 | FRENCH GULCH 1102 | NORTH VALLEY | 13.6588 | 44.7353 | 99.62% | 1 | 1 | 99.24% | 22.55% | 0 | 0.052153 | 1 | 1.4168 | 0.073891 | Medium | Medium | Low | 1999 | 1659 | 0.052153 | 34.3221 | 0.3845%
CLEAR LAKE 1101406 | CLEAR LAKE 1101 | HUMBOLDT | 10.6464 | 76.543 | 93.36% | 0 | 1 | 32.19% | 54.28% | 0 | 0.052045 | 1 | 2.4044 | 0.12514 | Medium | Medium | Medium | 1642 | 1660 | 0.052045 | 34.27 | 0.3839%
OCEANO 1104Q12 | OCEANO 1104 | LOS PADRES | 9.3393 | 55.4094 | 73.47% | 0 | 5 | 57.92% | 27.55% | 0 | 0.051953 | 1 | 2.3715 | 0.12321 | Medium | Medium | Medium | 1651 | 1661 | 0.051953 | 34.2179 | 0.3833%
HIGGINS 1109594 | HIGGINS 1109 | SIERRA | 14.2898 | 11.2028 | 80.24% | 1 | 11 | 100% | 0% | 0 | 0.051909 | 1 | 3.0273 | 0.15715 | Medium | Medium | Medium | 1533 | 1662 | 0.051909 | 34.166 | 0.3828%
SONOMA 110478372 | SONOMA 1104 | SONOMA | 16.4405 | 56.415 | 74.14% | 3 | 12 | 96.01% | 0% | 0 | 0.051874 | 1 | 3.4088 | 0.17683 | Medium | Medium | High | 1476 | 1663 | 0.051874 | 34.1141 | 0.3822%
HALF MOON BAY 11028848 | HALF MOON BAY 1102 | PENINSULA | 3.8931 | 27.5705 | 29.99% | 4 | 3 | 38.64% | 80.42% | 0 | 0.051782 | 1 | 4.2924 | 0.22227 | Medium | Medium | High | 1367 | 1664 | 0.051782 | 34.0622 | 0.3816%
NOTRE DAME 11042408 | NOTRE DAME 1104 | NORTH VALLEY | 11.2331 | 23.0626 | 36.02% | 1 | 3 | 81.2% | 47.16% | 1 | 0.051652 | 1 | 2.8875 | 0.14914 | Medium | Medium | Medium | 1555 | 1665 | 0.051652 | 34.0104 | 0.381%
LAYTONVILLE 11022502 | LAYTONVILLE 1102 | HUMBOLDT | 17.8026 | 72.9803 | 99.59% | 0 | 9 | 100% | 0% | 0 | 0.051556 | 1 | 0.80349 | 0.041424 | Medium | Medium | Low | 2508 | 1666 | 0.051556 | 33.9588 | 0.3804%
OAKLAND X 1106CR008 | OAKLAND X 1106 | EAST BAY | 4.2343 | 10.8634 | 21.85% | 11 | 17 | 100% | 13.39% | 0 | 0.051531 | 1 | 3.3497 | 0.17261 | Medium | Medium | High | 1488 | 1667 | 0.051531 | 33.9072 | 0.3799%
SILVERADO 2104806 | SILVERADO 2104 | NORTH BAY | 20.224 | 80.8764 | 82.09% | 0 | 5 | 59.08% | 2.927% | 0 | 0.051436 | 1 | 2.8358 | 0.14586 | Medium | Medium | Medium | 1568 | 1668 | 0.051436 | 33.8557 | 0.3793%
SO. CAL. EDISON #2 1101CB | SO. CAL. EDISON #2 1101 | YOSEMITE | 1.1766 | 10 | 100% | 0 | 0 | 100% | 37.67% | 0 | 0.051431 | 1 | 1.6243 | 0.08354 | Medium | Medium | Low | 1893 | 1669 | 0.051431 | 33.8042 | 0.3787%
ELECTRA 11026014 | ELECTRA 1102 | STOCKTON | 28.5875 | 15.0573 | 83.7% | 1 | 14 | 100% | 0% | 0 | 0.051142 | 1 | 1.9639 | 0.10044 | Medium | Medium | Low | 1766 | 1670 | 0.051142 | 33.7528 | 0.3781%
ALTO 1122CB | ALTO 1122 | NORTH BAY | 2.386 | 10 | 11.27% | 0 | 1 | 68.83% | 100% | 0 | 0.05105 | 1 | 3.5941 | 0.18348 | Medium | Medium | High | 1462 | 1671 | 0.05105 | 33.7017 | 0.3776%
STILLWATER 11021466 | STILLWATER 1102 | NORTH VALLEY | 19.2831 | 16.0387 | 100% | 1 | 10 | 94.09% | 0% | 0 | 0.051049 | 1 | 1.4241 | 0.0727 | Medium | Medium | Low | 2008 | 1672 | 0.051049 | 33.6506 | 0.377%
PEORIA 170190090 | PEORIA 1701 | YOSEMITE | 29.5241 | 42.6688 | 45.08% | 1 | 8 | 98.45% | 0% | 0 | 0.050945 | 1 | 1.0149 | 0.051705 | Medium | Medium | Low | 2317 | 1673 | 0.050945 | 33.5996 | 0.3764%
DOBBINS 110191464 | DOBBINS 1101 | SIERRA | 7.0765 | 18.3456 | 88.34% | 2 | 2 | 100% | 2.371% | 0 | 0.050871 | 1 | 2.9545 | 0.1503 | Medium | Medium | Medium | 1550 | 1674 | 0.050871 | 33.5486 | 0.3758%
ALTO 1124CB | ALTO 1124 | NORTH BAY | 3.2561 | 10 | 7.135% | 1 | 6 | 46.3% | 100% | 0 | 0.050654 | 1 | 4.7415 | 0.24018 | Medium | Medium | High | 1334 | 1675 | 0.050654 | 33.4977 | 0.3753%
ROB ROY 210410954 | ROB ROY 2104 | CENTRAL COAST | 7.1077 | 10 | 88.57% | 7 | 3 | 100% | 0% | 0 | 0.050548 | 1 | 3.1113 | 0.15727 | Medium | Medium | High | 1532 | 1676 | 0.050548 | 33.4471 | 0.3747%
OREGON TRAIL 11021584 | OREGON TRAIL 1102 | NORTH VALLEY | 13.0863 | 23.8771 | 100% | 1 | 4 | 100% | 0% | 0 | 0.050417 | 1 | 2.7558 | 0.13894 | Medium | Medium | Medium | 1586 | 1677 | 0.050417 | 33.3965 | 0.3741%
PEORIA 170488630 | PEORIA 1704 | YOSEMITE | 0.77831 | 38.0661 | 100% | 0 | 0 | 100% | 0% | 0 | 0.050412 | 1 | 0.52663 | 0.026548 | Medium | Medium | Low | 2848 | 1678 | 0.050412 | 33.3461 | 0.3736%
HALSEY 110176178 | HALSEY 1101 | SIERRA | 19.4389 | 10 | 66.26% | 6 | 14 | 96.3% | 0% | 0 | 0.050379 | 1 | 2.5491 | 0.12842 | Medium | Medium | Medium | 1629 | 1679 | 0.050379 | 33.2957 | 0.373%
FORT BRAGG A 11044690 | FORT BRAGG A 1104 | HUMBOLDT | 12.2439 | 49.0226 | 37.04% | 15 | 12 | 85.93% | 0% | 0 | 0.050332 | 1 | 3.1146 | 0.15677 | Medium | Medium | High | 1535 | 1680 | 0.050332 | 33.2453 | 0.3724%
HALSEY 11012414 | HALSEY 1101 | SIERRA | 14.7964 | 13.1515 | 76.48% | 3 | 9 | 100% | 0% | 0 | 0.050299 | 1 | 2.0384 | 0.10253 | Medium | Medium | Low | 1750 | 1681 | 0.050299 | 33.195 | 0.3719%
PEORIA 170184318 | PEORIA 1701 | YOSEMITE | 9.9103 | 10 | 99.97% | 1 | 8 | 100% | 0% | 0 | 0.049883 | 1 | 1.0313 | 0.051441 | Medium | Medium | Low | 2322 | 1682 | 0.049883 | 33.1447 | 0.3713%
CALAVERAS CEMENT 1101544800 | CALAVERAS CEMENT 1101 | STOCKTON | 23.1954 | 36.7246 | 100% | 2 | 5 | 100% | 0% | 0 | 0.049871 | 1 | 1.9083 | 0.095168 | Medium | Medium | Low | 1797 | 1683 | 0.049871 | 33.0948 | 0.3708%
CHOLAME 21025597 | CHOLAME 2102 | LOS PADRES | 5.1199 | 69.1665 | 100% | 0 | 2 | 100% | 0% | 0 | 0.049821 | 1 | 1.2615 | 0.062847 | Medium | Medium | Low | 2132 | 1684 | 0.049821 | 33.0449 | 0.3702%
ANTLER 11011376 | ANTLER 1101 | NORTH VALLEY | 9.003 | 26.8195 | 100% | 0 | 3 | 100% | 0% | 0 | 0.049747 | 1 | 0.38247 | 0.019027 | Medium | Medium | Low | 3029 | 1685 | 0.049747 | 32.9951 | 0.3696%
SWIFT 2110XR332 | SWIFT 2110 | SAN JOSE | 49.6657 | 79.4868 | 80.03% | 0 | 0 | 100% | 0% | 0 | 0.049698 | 1 | 2.4667 | 0.12259 | Medium | Medium | Medium | 1653 | 1686 | 0.049698 | 32.9454 | 0.3691%
SAND CREEK 11037070 | SAND CREEK 1103 | FRESNO | 17.8283 | 24.5064 | 100% | 1 | 3 | 100% | 0% | 0 | 0.049625 | 1 | 1.3027 | 0.064648 | Medium | Medium | Low | 2106 | 1687 | 0.049625 | 32.8957 | 0.3685%
OCEANO 1103221092 | OCEANO 1103 | LOS PADRES | 1.2243 | 45.1389 | 92.5% | 0 | 2 | 95.43% | 0% | 0 | 0.049591 | 1 | 3.9902 | 0.19788 | Medium | Medium | High | 1418 | 1688 | 0.049591 | 32.8461 | 0.368%
EL CERRITO G 1112BR178 | EL CERRITO G 1112 | EAST BAY | 1.8955 | 10 | 57.49% | 2 | 1 | 23.53% | 92.74% | 0 | 0.049573 | 1 | 4.8314 | 0.23951 | Medium | Medium | High | 1335 | 1689 | 0.049573 | 32.7965 | 0.3674%
UPPER LAKE 1101CB | UPPER LAKE 1101 | HUMBOLDT | 1.1134 | 70.0562 | 95.06% | 2 | 2 | 100% | 0% | 0 | 0.049432 | 1 | 1.7447 | 0.086245 | Medium | Medium | Low | 1866 | 1690 | 0.049432 | 32.7469 | 0.3669%
CORNING 110253184 | CORNING 1102 | NORTH VALLEY | 31.925 | 68.303 | 86.89% | 0 | 7 | 100% | 0% | 0 | 0.049388 | 1 | 1.1736 | 0.05796 | Medium | Medium | Low | 2208 | 1691 | 0.049388 | 32.6975 | 0.3663%
CALPELLA 11013419 | CALPELLA 1101 | HUMBOLDT | 8.0753 | 59.7032 | 100% | 1 | 1 | 100% | 3.769% | 0 | 0.0493 | 1 | 1.5255 | 0.075207 | Medium | Medium | Low | 1983 | 1692 | 0.0493 | 32.6481 | 0.3658%
BEAR VALLEY 210511210 | BEAR VALLEY 2105 | YOSEMITE | 17.0195 | 54.7309 | 100% | 0 | 6 | 100% | 0% | 0 | 0.049124 | 1 | 0.44607 | 0.021913 | Medium | Medium | Low | 2965 | 1693 | 0.049124 | 32.5988 | 0.3652%
PIT NO 5 11011614 | PIT NO 5 1101 | NORTH VALLEY | 1.8659 | 92.5056 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049074 | 1 | 0.16422 | 0.0080592 | Medium | Medium | Low | 3159 | 1694 | 0.049074 | 32.5496 | 0.3646%
COTTONWOOD 11021578 | COTTONWOOD 1102 | NORTH VALLEY | 28.4377 | 38.0859 | 100% | 1 | 7 | 81.08% | 0% | 0 | 0.049028 | 1 | 1.4522 | 0.0712 | Medium | Medium | Low | 2031 | 1695 | 0.049028 | 32.5006 | 0.3641%
DUNLAP 11027360 | DUNLAP 1102 | FRESNO | 8.5319 | 14.1381 | 99.93% | 0 | 0 | 100% | 0% | 0 | 0.048964 | 1 | 0.093748 | 0.0045903 | Medium | Medium | Low | 3174 | 1696 | 0.048964 | 32.4515 | 0.3635%
COARSEGOLD 21035020 | COARSEGOLD 2103 | YOSEMITE | 16.1848 | 19.8956 | 69.91% | 1 | 23 | 97.69% | 0% | 0 | 0.048835 | 1 | 1.987 | 0.097036 | Medium | Medium | Low | 1787 | 1697 | 0.048835 | 32.4026 | 0.363%
MARTELL 110111244 | MARTELL 1101 | STOCKTON | 21.6798 | 10 | 87.92% | 5 | 3 | 99.45% | 0% | 0 | 0.048788 | 1 | 2.5388 | 0.12386 | Medium | Medium | Medium | 1646 | 1698 | 0.048788 | 32.3537 | 0.3625%
BURNEY 11019042 | BURNEY 1101 | NORTH VALLEY | 3.0554 | 28.762 | 87.06% | 1 | 1 | 96.72% | 0% | 0 | 0.048736 | 1 | 2.1708 | 0.1058 | Medium | Medium | Low | 1734 | 1699 | 0.048736 | 32.305 | 0.3619%
WEIMAR 1101CB | WEIMAR 1101 | SIERRA | 9.2462 | 10 | 51.97% | 4 | 11 | 100% | 0% | 0 | 0.04865 | 1 | 1.7246 | 0.083901 | Medium | Medium | Low | 1889 | 1700 | 0.04865 | 32.2562 | 0.3614%
PARADISE 1102CB | PARADISE 1102 | NORTH VALLEY | 0.74465 | 10 | 6.716% | 2 | 0 | 53.22% | 100% | 0 | 0.048451 | 1 | 4.3681 | 0.21164 | Medium | Medium | High | 1390 | 1701 | 0.048451 | 32.2076 | 0.3608%
MORGAN HILL 2111XR292 | MORGAN HILL 2111 | SAN JOSE | 10.8242 | 23.3354 | 98.35% | 1 | 8 | 89.12% | 0% | 0 | 0.048423 | 1 | 3.0382 | 0.14712 | Medium | Medium | Medium | 1563 | 1702 | 0.048423 | 32.1591 | 0.3603%
STILLWATER 11021644 | STILLWATER 1102 | NORTH VALLEY | 22.854 | 11.5095 | 100% | 1 | 6 | 100% | 0% | 0 | 0.048415 | 1 | 1.7011 | 0.08236 | Medium | Medium | Low | 1909 | 1703 | 0.048415 | 32.1107 | 0.3597%
NARROWS 210534069 | NARROWS 2105 | SIERRA | 15.7398 | 14.9961 | 98.66% | 0 | 6 | 100% | 0% | 0 | 0.048393 | 1 | 1.8027 | 0.087238 | Medium | Medium | Low | 1854 | 1704 | 0.048393 | 32.0623 | 0.3592%
MOUNTAIN QUARRIES 21011180 | MOUNTAIN QUARRIES 2101 | SIERRA | 12.8441 | 30.3787 | 92.22% | 1 | 2 | 100% | 9.293% | 0 | 0.048359 | 1 | 2.2311 | 0.10789 | Medium | Medium | Medium | 1723 | 1705 | 0.048359 | 32.0139 | 0.3586%
AUBERRY 110237466 | AUBERRY 1102 | FRESNO | 31.5797 | 23.1987 | 95.92% | 2 | 3 | 100% | 0% | 0 | 0.048258 | 1 | 1.7115 | 0.082592 | Medium | Medium | Low | 1905 | 1706 | 0.048258 | 31.9655 | 0.3581%
WILLOW CREEK 1103CB | WILLOW CREEK 1103 | HUMBOLDT | 3.9217 | 18.1592 | 58.12% | 1 | 8 | 100% | 7.1% | 0 | 0.048009 | 1 | 1.8137 | 0.087072 | Medium | Medium | Low | 1856 | 1707 | 0.048009 | 31.9173 | 0.3576%
SAND CREEK 11037420 | SAND CREEK 1103 | FRESNO | 23.394 | 10 | 99.98% | 4 | 4 | 100% | 0% | 0 | 0.04783 | 1 | 2.3612 | 0.11293 | Medium | Medium | Medium | 1699 | 1708 | 0.04783 | 31.8693 | 0.357%
GARBERVILLE 11024744 | GARBERVILLE 1102 | HUMBOLDT | 16.8626 | 50.888 | 35.22% | 7 | 3 | 83.26% | 0% | 0 | 0.047692 | 1 | 0.60586 | 0.028895 | Medium | Medium | Low | 2801 | 1709 | 0.047692 | 31.8214 | 0.3565%
INDIAN FLAT 110410270 | INDIAN FLAT 1104 | YOSEMITE | 3.8012 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.047687 | 1 | 1.3662 | 0.065148 | Medium | Medium | Low | 2097 | 1710 | 0.047687 | 31.7737 | 0.356%
SAN RAFAEL 1108CB | SAN RAFAEL 1108 | NORTH BAY | 3.0131 | 10 | 10.73% | 6 | 1 | 40.8% | 100% | 0 | 0.047654 | 1 | 4.4645 | 0.21275 | Medium | Medium | High | 1386 | 1711 | 0.047654 | 31.7261 | 0.3554%
ROSSMOOR 110168920 | ROSSMOOR 1101 | DIABLO | 5.9925 | 29.5829 | 31.67% | 8 | 11 | 82.31% | 24.74% | 0 | 0.047645 | 1 | 3.3031 | 0.15738 | Medium | Medium | High | 1531 | 1712 | 0.047645 | 31.6784 | 0.3549%
SHADY GLEN 110132726 | SHADY GLEN 1101 | SIERRA | 12.4872 | 23.3088 | 84.95% | 3 | 6 | 100% | 0% | 0 | 0.047638 | 1 | 2.1742 | 0.10357 | Medium | Medium | Low | 1744 | 1713 | 0.047638 | 31.6308 | 0.3544%
SAN JOAQUIN #2 110310320 | SAN JOAQUIN #2 1103 | YOSEMITE | 11.8104 | 12.4719 | 98.89% | 1 | 18 | 100% | 0% | 0 | 0.047599 | 1 | 1.2459 | 0.059305 | Medium | Medium | Low | 2191 | 1714 | 0.047599 | 31.5831 | 0.3538%
FORT SEWARD 1121CB | FORT SEWARD 1121 | HUMBOLDT | 7.2358 | 72.7632 | 100% | 3 | 3 | 100% | 0% | 0 | 0.047585 | 1 | 1.5395 | 0.073259 | Medium | Medium | Low | 2002 | 1715 | 0.047585 | 31.5355 | 0.3533%
HIGHLANDS 110448262 | HIGHLANDS 1104 | HUMBOLDT | 5.8216 | 10 | 84.42% | 0 | 6 | 100% | 0% | 0 | 0.047568 | 1 | 3.314 | 0.15764 | Medium | Medium | High | 1530 | 1716 | 0.047568 | 31.4879 | 0.3528%
SHINGLE SPRINGS 2110CB | SHINGLE SPRINGS 2110 | SIERRA | 0.10881 | 10 | 92.58% | 0 | 0 | 8.524% | 92.58% | 0 | 0.047519 | 1 | 3.2729 | 0.15553 | Medium | Medium | High | 1537 | 1717 | 0.047519 | 31.4404 | 0.3522%
CHESTER 11022564 | CHESTER 1102 | NORTH VALLEY | 2.0894 | 10 | 100% | 0 | 3 | 93.3% | 0% | 0 | 0.047498 | 1 | 2.1797 | 0.10353 | Medium | Medium | Low | 1745 | 1718 | 0.047498 | 31.3928 | 0.3517%
PIT NO 5 11011618 | PIT NO 5 1101 | NORTH VALLEY | 6.0991 | 69.0036 | 93.71% | 0 | 2 | 100% | 0% | 0 | 0.047368 | 1 | 0.028548 | 0.0013523 | Medium | Medium | Low | 3179 | 1719 | 0.047368 | 31.3453 | 0.3512%
FROGTOWN 17027134 | FROGTOWN 1702 | STOCKTON | 19.267 | 44.0538 | 84.25% | 0 | 2 | 84.8% | 0% | 0 | 0.047354 | 1 | 1.8987 | 0.089911 | Medium | Medium | Low | 1834 | 1720 | 0.047354 | 31.298 | 0.3506%
MONTICELLO 110193384 | MONTICELLO 1101 | NORTH BAY | 15.2847 | 55.7693 | 100% | 0 | 3 | 88.22% | 0% | 0 | 0.047273 | 1 | 1.3315 | 0.062941 | Medium | Medium | Low | 2130 | 1721 | 0.047273 | 31.2506 | 0.3501%
BEAR VALLEY 2101CB | BEAR VALLEY 2101 | YOSEMITE | 18.7199 | 23.9906 | 55.73% | 0 | 6 | 100% | 0% | 0 | 0.047229 | 1 | 0.81463 | 0.038474 | Medium | Medium | Low | 2572 | 1722 | 0.047229 | 31.2034 | 0.3496%
OREGON TRAIL 11041574 | OREGON TRAIL 1104 | NORTH VALLEY | 16.4858 | 16.0641 | 94.5% | 2 | 4 | 88.21% | 0% | 0 | 0.04716 | 1 | 2.1636 | 0.10204 | Medium | Medium | Low | 1754 | 1723 | 0.04716 | 31.1561 | 0.349%
CORNING 110185162 | CORNING 1101 | NORTH VALLEY | 5.7561 | 60.2607 | 100% | 0 | 2 | 100% | 0% | 0 | 0.047015 | 1 | 1.9543 | 0.09188 | Medium | Medium | Low | 1819 | 1724 | 0.047015 | 31.109 | 0.3485%
MIDDLETOWN 11021312 | MIDDLETOWN 1102 | HUMBOLDT | 9.8496 | 13.9462 | 100% | 1 | 10 | 100% | 0% | 0 | 0.046919 | 1 | 3.0951 | 0.14522 | Medium | Medium | High | 1575 | 1725 | 0.046919 | 31.062 | 0.348%
MORGAN HILL 2105XR070 | MORGAN HILL 2105 | SAN JOSE | 6.67 | 37.7183 | 68.61% | 0 | 0 | 76.77% | 50.18% | 1 | 0.046839 | 1 | 3.2954 | 0.15435 | Medium | Medium | High | 1543 | 1726 | 0.046839 | 31.015 | 0.3475%
CORNING 110182846 | CORNING 1101 | NORTH VALLEY | 5.0438 | 29.0672 | 100% | 1 | 5 | 99.85% | 0% | 0 | 0.046785 | 1 | 1.9907 | 0.093136 | Medium | Medium | Low | 1810 | 1727 | 0.046785 | 30.9682 | 0.3469%
SWIFT 2110XR366 | SWIFT 2110 | SAN JOSE | 8.8402 | 27.8534 | 70.07% | 1 | 1 | 80.04% | 0% | 0 | 0.04663 | 1 | 4.5152 | 0.21055 | Medium | Medium | High | 1392 | 1728 | 0.04663 | 30.9214 | 0.3464%
LOS OSITOS 21037062 | LOS OSITOS 2103 | CENTRAL COAST | 12.2332 | 84.1604 | 73.22% | 2 | 3 | 100% | 0% | 0 | 0.046568 | 1 | 2.1004 | 0.097814 | Medium | Medium | Low | 1785 | 1729 | 0.046568 | 30.8748 | 0.3459%
CORRAL 110236666 | CORRAL 1102 | STOCKTON | 17.3526 | 23.3821 | 99.95% | 1 | 2 | 96.21% | 0% | 0 | 0.046553 | 1 | 2.4463 | 0.11388 | Medium | Medium | Medium | 1693 | 1730 | 0.046553 | 30.8282 | 0.3454%
RINCON 1104CB | RINCON 1104 | SONOMA | 2.6764 | 10 | 22.48% | 3 | 5 | 47.86% | 77.17% | 0 | 0.046471 | 1 | 3.464 | 0.16098 | Medium | Medium | High | 1522 | 1731 | 0.046471 | 30.7817 | 0.3448%
GARBERVILLE 11022540 | GARBERVILLE 1102 | HUMBOLDT | 15.3454 | 59.7556 | 6.792% | 13 | 5 | 85.73% | 0% | 0 | 0.046446 | 1 | 0.33411 | 0.015518 | Medium | Medium | Low | 3095 | 1732 | 0.046446 | 30.7352 | 0.3443%
MONTE RIO 1111292 | MONTE RIO 1111 | SONOMA | 14.6924 | 53.0276 | 14.56% | 3 | 9 | 74.19% | 33.55% | 0 | 0.046445 | 1 | 2.1476 | 0.099746 | Medium | Medium | Low | 1771 | 1733 | 0.046445 | 30.6887 | 0.3438%
MENDOCINO 1101CB | MENDOCINO 1101 | HUMBOLDT | 11.0353 | 11.0346 | 86.58% | 0 | 6 | 81.55% | 0% | 0 | 0.046385 | 1 | 2.3319 | 0.10817 | Medium | Medium | Medium | 1719 | 1734 | 0.046385 | 30.6423 | 0.3433%
HIGGINS 1104324510 | HIGGINS 1104 | SIERRA | 12.4769 | 10 | 100% | 3 | 3 | 100% | 0% | 0 | 0.046303 | 1 | 2.9958 | 0.13872 | Medium | Medium | Medium | 1588 | 1735 | 0.046303 | 30.5959 | 0.3428%
BROWNS VALLEY 11011268 | BROWNS VALLEY 1101 | SIERRA | 10.9063 | 24.7365 | 96.96% | 1 | 7 | 100% | 0% | 0 | 0.046288 | 1 | 2.7133 | 0.12559 | Medium | Medium | Medium | 1641 | 1736 | 0.046288 | 30.5496 | 0.3422%
PIT NO 7 1101CB | PIT NO 7 1101 | NORTH VALLEY | 2.7098 | 77.1247 | 100% | 0 | 2 | 100% | 0% | 0 | 0.046206 | 1 | 0.4374 | 0.02021 | Medium | Medium | Low | 3003 | 1737 | 0.046206 | 30.5033 | 0.3417%
KONOCTI 1102596 | KONOCTI 1102 | HUMBOLDT | 8.591 | 44.5897 | 35.58% | 1 | 10 | 63.73% | 0% | 0 | 0.046139 | 1 | 3.4882 | 0.16094 | Medium | Medium | High | 1523 | 1738 | 0.046139 | 30.4571 | 0.3412%
POINT ARENA 11012637 | POINT ARENA 1101 | HUMBOLDT | 4.0404 | 84.4232 | 59.73% | 1 | 2 | 100% | 0% | 0 | 0.046116 | 1 | 1.2415 | 0.057252 | Medium | Medium | Low | 2218 | 1739 | 0.046116 | 30.411 | 0.3407%
SAN LEANDRO U 1109CR182 | SAN LEANDRO U 1109 | MISSION | 4.81 | 10 | 62.88% | 5 | 1 | 100% | 19.48% | 0 | 0.046108 | 1 | 3.2168 | 0.14832 | Medium | Medium | High | 1558 | 1740 | 0.046108 | 30.3649 | 0.3402%
DUNBAR 110297160 | DUNBAR 1102 | SONOMA | 0.058569 | 82.8928 | 100% | 0 | 0 | 100% | 0% | 0 | 0.046095 | 1 | 2.8466 | 0.13122 | Medium | Medium | Medium | 1624 | 1741 | 0.046095 | 30.3188 | 0.3397%
WYANDOTTE 110738438 | WYANDOTTE 1107 | NORTH VALLEY | 16.8538 | 17.2711 | 100% | 1 | 4 | 100% | 13.33% | 1 | 0.046053 | 1 | 1.7995 | 0.082871 | Medium | Medium | Low | 1903 | 1742 | 0.046053 | 30.2727 | 0.3391%
STILLWATER 110148950 | STILLWATER 1101 | NORTH VALLEY | 12.4263 | 10 | 99.94% | 1 | 4 | 100% | 0% | 0 | 0.046041 | 1 | 1.6867 | 0.077656 | Medium | Medium | Low | 1956 | 1743 | 0.046041 | 30.2266 | 0.3386%
HIGHLANDS 1103482 | HIGHLANDS 1103 | HUMBOLDT | 23.7709 | 84.3418 | 64.96% | 1 | 10 | 92.07% | 0% | 0 | 0.046005 | 1 | 2.3829 | 0.10963 | Medium | Medium | Medium | 1711 | 1744 | 0.046005 | 30.1806 | 0.3381%
PETALUMA C 1109848654 | PETALUMA C 1109 | SONOMA | 13.3481 | 80.6017 | 79.77% | 0 | 10 | 97.01% | 0% | 0 | 0.045978 | 1 | 2.0505 | 0.094277 | Medium | Medium | Low | 1804 | 1745 | 0.045978 | 30.1346 | 0.3376%
COTTONWOOD 110168190 | COTTONWOOD 1101 | NORTH VALLEY | 22.7429 | 39.5713 | 100% | 3 | 4 | 90.15% | 0% | 0 | 0.045908 | 1 | 1.3967 | 0.064119 | Medium | Medium | Low | 2113 | 1746 | 0.045908 | 30.0886 | 0.3371%
PINE GROVE 11013166 | PINE GROVE 1101 | STOCKTON | 12.5063 | 11.3177 | 79.03% | 1 | 18 | 100% | 0% | 0 | 0.045896 | 1 | 2.919 | 0.13397 | Medium | Medium | Medium | 1609 | 1747 | 0.045896 | 30.0427 | 0.3366%
SCE TEHACHAPI 1101CB | SCE TEHACHAPI 1101 | KERN | 1.4276 | 82.1535 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045873 | 1 | 2.4463 | 0.11222 | Medium | Medium | Medium | 1701 | 1748 | 0.045873 | 29.9968 | 0.336%
SALT SPRINGS 210110416 | SALT SPRINGS 2101 | STOCKTON | 0.57657 | 81.6052 | 94.63% | 2 | 1 | 100% | 0% | 0 | 0.045848 | 1 | 0.35085 | 0.016086 | Medium | Medium | Low | 3082 | 1749 | 0.045848 | 29.9509 | 0.3355%
GARBERVILLE 110237054 | GARBERVILLE 1102 | HUMBOLDT | 8.8244 | 78.2726 | 22.8% | 0 | 2 | 95.32% | 0% | 0 | 0.04584 | 1 | 0.97592 | 0.044736 | Medium | Medium | Low | 2442 | 1750 | 0.04584 | 29.9051 | 0.335%
DUNBAR 1103440 | DUNBAR 1103 | SONOMA | 3.5573 | 21.3081 | 50.04% | 0 | 2 | 25.85% | 93.78% | 0 | 0.045809 | 1 | 3.7008 | 0.16953 | Medium | Medium | High | 1501 | 1751 | 0.045809 | 29.8592 | 0.3345%
BURNEY 11011340 | BURNEY 1101 | NORTH VALLEY | 18.024 | 21.8274 | 89.51% | 4 | 2 | 100% | 0% | 0 | 0.045714 | 1 | 1.3248 | 0.060564 | Medium | Medium | Low | 2172 | 1752 | 0.045714 | 29.8134 | 0.334%
PLACERVILLE 111219712 | PLACERVILLE 1112 | SIERRA | 12.7698 | 10 | 100% | 3 | 10 | 97.13% | 0% | 0 | 0.045629 | 1 | 2.5586 | 0.11675 | Medium | Medium | Medium | 1681 | 1753 | 0.045629 | 29.7677 | 0.3335%
PASO ROBLES 1104R12 | PASO ROBLES 1104 | LOS PADRES | 26.4117 | 63.4802 | 89.23% | 0 | 7 | 66.23% | 0% | 0 | 0.045549 | 1 | 2.2416 | 0.1021 | Medium | Medium | Medium | 1753 | 1754 | 0.045549 | 29.7221 | 0.333%
TASSAJARA 210419042 | TASSAJARA 2104 | DIABLO | 7.0796 | 47.3825 | 57.65% | 1 | 2 | 83.81% | 25.74% | 0 | 0.045532 | 1 | 3.832 | 0.17448 | Medium | Medium | High | 1483 | 1755 | 0.045532 | 29.6765 | 0.3325%
APPLE HILL 21026552 | APPLE HILL 2102 | SIERRA | 12.3732 | 14.1708 | 74.28% | 2 | 0 | 100% | 6.545% | 1 | 0.045443 | 1 | 1.5727 | 0.07147 | Medium | Medium | Low | 2028 | 1756 | 0.045443 | 29.631 | 0.332%
DUNLAP 11027060 | DUNLAP 1102 | FRESNO | 17.8164 | 21.4268 | 100% | 3 | 11 | 100% | 0% | 0 | 0.045381 | 1 | 1.1057 | 0.050176 | Medium | Medium | Low | 2348 | 1757 | 0.045381 | 29.5855 | 0.3314%
MARIPOSA 210135244 | MARIPOSA 2101 | YOSEMITE | 17.3356 | 16.4968 | 77.7% | 2 | 10 | 100% | 23.66% | 0 | 0.045381 | 1 | 2.1925 | 0.099495 | Medium | Medium | Low | 1774 | 1758 | 0.045381 | 29.5402 | 0.3309%
AUBERRY 1101R2579 | AUBERRY 1101 | FRESNO | 34.5067 | 14.4508 | 99.64% | 2 | 14 | 100% | 0% | 0 | 0.045338 | 1 | 0.99472 | 0.045098 | Medium | Medium | Low | 2437 | 1759 | 0.045338 | 29.4948 | 0.3304%
ELK CREEK 11012002 | ELK CREEK 1101 | NORTH VALLEY | 17.647 | 82.0427 | 100% | 0 | 0 | 58.67% | 0% | 0 | 0.045253 | 1 | 1.0865 | 0.049167 | Medium | Medium | Low | 2367 | 1760 | 0.045253 | 29.4494 | 0.3299%
APPLE HILL 21021532 | APPLE HILL 2102 | SIERRA | 38.7437 | 26.3677 | 83.01% | 8 | 10 | 92.13% | 0.1028% | 0 | 0.045174 | 1 | 1.6238 | 0.073353 | Medium | Medium | Low | 2001 | 1761 | 0.045174 | 29.4042 | 0.3294%
ATASCADERO 1103A16 | ATASCADERO 1103 | LOS PADRES | 18.5162 | 60.2309 | 48.27% | 0 | 1 | 91.95% | 38.05% | 0 | 0.045156 | 1 | 1.5184 | 0.068565 | Medium | Medium | Low | 2057 | 1762 | 0.045156 | 29.359 | 0.3289%
HOOPA 110137202 | HOOPA 1101 | HUMBOLDT | 23.7883 | 81.2571 | 100% | 8 | 3 | 82.1% | 0% | 0 | 0.045151 | 1 | 1.1358 | 0.051283 | Medium | Medium | Low | 2324 | 1763 | 0.045151 | 29.3139 | 0.3284%
PIT NO 5 1101CB | PIT NO 5 1101 | NORTH VALLEY | 0.72275 | 65.782 | 100% | 4 | 2 | 100% | 0% | 0 | 0.045131 | 1 | 0.11458 | 0.0051713 | Medium | Medium | Low | 3171 | 1764 | 0.045131 | 29.2687 | 0.3279%
JARVIS 1111MR121 | JARVIS 1111 | MISSION | 1.1185 | 70.124 | 6.252% | 0 | 0 | 20.83% | 100% | 0 | 0.045013 | 1 | 3.4072 | 0.15337 | Medium | Medium | High | 1545 | 1765 | 0.045013 | 29.2236 | 0.3274%
MENLO 11031721 | MENLO 1103 | PENINSULA | 6.795 | 58.431 | 89.52% | 4 | 2 | 100% | 0% | 0 | 0.044995 | 1 | 2.626 | 0.11816 | Medium | Medium | Medium | 1674 | 1766 | 0.044995 | 29.1786 | 0.3269%
FRENCH GULCH 11011464 | FRENCH GULCH 1101 | NORTH VALLEY | 3.9608 | 72.3083 | 100% | 3 | 0 | 100% | 0% | 0 | 0.044678 | 1 | 1.9188 | 0.085727 | Medium | Medium | Low | 1870 | 1767 | 0.044678 | 29.1336 | 0.3264%
LUCERNE 110638436 | LUCERNE 1106 | HUMBOLDT | 4.6279 | 61.4353 | 100% | 0 | 7 | 96.43% | 0% | 0 | 0.044553 | 1 | 3.7075 | 0.16518 | Medium | Medium | High | 1510 | 1768 | 0.044553 | 29.0889 | 0.3259%
MILPITAS 110987800 | MILPITAS 1109 | SAN JOSE | 1.61 | 77.3424 | 100% | 0 | 0 | 100% | 0% | 0 | 0.044454 | 1 | 2.8069 | 0.12478 | Medium | Medium | Medium | 1643 | 1769 | 0.044454 | 29.0443 | 0.3254%
TYLER 11051536 | TYLER 1105 | NORTH VALLEY | 17.0203 | 70.2834 | 100% | 0 | 5 | 94.18% | 0% | 0 | 0.044384 | 1 | 1.5772 | 0.070005 | Medium | Medium | Low | 2045 | 1770 | 0.044384 | 28.9999 | 0.3249%
HOLLISTER 21054018 | HOLLISTER 2105 | CENTRAL COAST | 42.8602 | 78.3807 | 68.88% | 1 | 1 | 81.19% | 0% | 0 | 0.044317 | 1 | 1.765 | 0.078218 | Medium | Medium | Low | 1951 | 1771 | 0.044317 | 28.9555 | 0.3244%
WILLOW CREEK 11035012 | WILLOW CREEK 1103 | HUMBOLDT | 10.8623 | 35.544 | 71.11% | 10 | 12 | 100% | 0% | 0 | 0.044176 | 1 | 2.0337 | 0.08984 | Medium | Medium | Low | 1835 | 1772 | 0.044176 | 28.9112 | 0.3239%
SILVERADO 2105CB | SILVERADO 2105 | NORTH BAY | 0.47706 | 10 | 63.84% | 0 | 1 | 10.39% | 100% | 0 | 0.044175 | 1 | 3.805 | 0.16809 | Medium | Medium | High | 1504 | 1773 | 0.044175 | 28.867 | 0.3234%
WILDWOOD 110198896 | WILDWOOD 1101 | NORTH VALLEY | 9.9251 | 71.2641 | 100% | 1 | 1 | 100% | 0% | 0 | 0.044142 | 1 | 0.90896 | 0.040124 | Medium | Medium | Low | 2536 | 1774 | 0.044142 | 28.8228 | 0.3229%
ELK CREEK 11012032 | ELK CREEK 1101 | NORTH VALLEY | 9.5675 | 53.63 | 100% | 0 | 1 | 99.9% | 0% | 0 | 0.044086 | 1 | 1.3752 | 0.060626 | Medium | Medium | Low | 2170 | 1775 | 0.044086 | 28.7787 | 0.3224%
MARIPOSA 21029490 | MARIPOSA 2102 | YOSEMITE | 4.2707 | 19.9086 | 45.43% | 0 | 1 | 100% | 49.91% | 0 | 0.044074 | 1 | 2.4205 | 0.10668 | Medium | Medium | Medium | 1726 | 1776 | 0.044074 | 28.7346 | 0.3219%
STANISLAUS 170179826 | STANISLAUS 1701 | YOSEMITE | 10.1928 | 54.2786 | 66.14% | 1 | 7 | 100% | 0% | 0 | 0.044036 | 1 | 3.4104 | 0.15018 | Medium | Medium | High | 1551 | 1777 | 0.044036 | 28.6905 | 0.3214%
FRENCH GULCH 11011892 | FRENCH GULCH 1101 | NORTH VALLEY | 2.9079 | 75.8107 | 100% | 0 | 0 | 100% | 0% | 0 | 0.044011 | 1 | 1.2823 | 0.056435 | Medium | Medium | Low | 2237 | 1778 | 0.044011 | 28.6465 | 0.3209%
RIO DELL 11027124 | RIO DELL 1102 | HUMBOLDT | 0.67226 | 75.6649 | 100% | 0 | 0 | 100% | 0% | 0 | 0.043969 | 1 | 1.0549 | 0.046383 | Medium | Medium | Low | 2413 | 1779 | 0.043969 | 28.6025 | 0.3204%
ELK 11011260 | ELK 1101 | HUMBOLDT | 15.6745 | 74.4455 | 25.71% | 10 | 4 | 100% | 0% | 0 | 0.043784 | 1 | 0.80153 | 0.035094 | Medium | Medium | Low | 2649 | 1780 | 0.043784 | 28.5585 | 0.3199%
COARSEGOLD 21045516 | COARSEGOLD 2104 | YOSEMITE | 18.4464 | 11.3018 | 100% | 1 | 1 | 100% | 0% | 0 | 0.043744 | 1 | 1.6156 | 0.070674 | Medium | Medium | Low | 2033 | 1781 | 0.043744 | 28.5147 | 0.3194%
EEL RIVER 11021902 | EEL RIVER 1102 | HUMBOLDT | 5.1093 | 87.5518 | 84.86% | 3 | 2 | 68.94% | 0% | 0 | 0.043714 | 1 | 1.9061 | 0.083323 | Medium | Medium | Low | 1894 | 1782 | 0.043714 | 28.471 | 0.319%
NORTH DUBLIN 2103CB | NORTH DUBLIN 2103 | MISSION | 12.6489 | 55.8047 | 31.35% | 1 | 2 | 83.95% | 0% | 0 | 0.043695 | 1 | 3.6462 | 0.15932 | Medium | Medium | High | 1526 | 1783 | 0.043695 | 28.4273 | 0.3185%
BEAR VALLEY 210521160 | BEAR VALLEY 2105 | YOSEMITE | 23.7351 | 48.0267 | 99.88% | 2 | 5 | 100% | 3.193% | 0 | 0.043692 | 1 | 1.5413 | 0.067341 | Medium | Medium | Low | 2068 | 1784 | 0.043692 | 28.3836 | 0.318%
OAKLAND K 1104CR208 | OAKLAND K 1104 | EAST BAY | 2.4051 | 10 | 34.97% | 0 | 3 | 100% | 39.7% | 0 | 0.0436 | 1 | 4.378 | 0.19088 | Medium | Medium | High | 1437 | 1785 | 0.0436 | 28.3399 | 0.3175%
ANTLER 11011612 | ANTLER 1101 | NORTH VALLEY | 8.3928 | 10 | 100% | 2 | 6 | 90.86% | 15.08% | 1 | 0.043586 | 1 | 0.69008 | 0.030078 | Medium | Medium | Low | 2773 | 1786 | 0.043586 | 28.2963 | 0.317%
POINT ARENA 110147952 | POINT ARENA 1101 | HUMBOLDT | 10.391 | 76.4518 | 10.32% | 20 | 9 | 100% | 0% | 0 | 0.043386 | 1 | 1.9987 | 0.086717 | Medium | Medium | Low | 1859 | 1787 | 0.043386 | 28.2527 | 0.3165%
CABRILLO 1103Y46 | CABRILLO 1103 | LOS PADRES | 20.218 | 55.531 | 56.98% | 1 | 5 | 42.55% | 0% | 0 | 0.043329 | 1 | 2.9259 | 0.12678 | Medium | Medium | Medium | 1637 | 1788 | 0.043329 | 28.2093 | 0.316%
VIEJO 22019114 | VIEJO 2201 | CENTRAL COAST | 6.3385 | 10 | 15.64% | 12 | 5 | 93.11% | 0% | 0 | 0.043315 | 1 | 3.8689 | 0.16758 | Medium | Medium | High | 1505 | 1789 | 0.043315 | 28.166 | 0.3155%
DOBBINS 11011808 | DOBBINS 1101 | SIERRA | 15.539 | 16.962 | 100% | 1 | 0 | 100% | 6.412% | 0 | 0.043272 | 1 | 2.1331 | 0.092302 | Medium | Medium | Low | 1816 | 1790 | 0.043272 | 28.1227 | 0.3151%
STANISLAUS 1702CB | STANISLAUS 1702 | YOSEMITE | 7.977 | 43.3363 | 28.21% | 1 | 3 | 100% | 19.55% | 0 | 0.043216 | 1 | 3.112 | 0.13449 | Medium | Medium | High | 1607 | 1791 | 0.043216 | 28.0794 | 0.3146%
MENLO 11038982 | MENLO 1103 | PENINSULA | 4.6231 | 36.5586 | 24.74% | 19 | 4 | 100% | 0% | 0 | 0.043182 | 1 | 1.8329 | 0.07915 | Medium | Medium | Low | 1943 | 1792 | 0.043182 | 28.0362 | 0.3141%
FULTON 1102287172 | FULTON 1102 | SONOMA | 17.3701 | 47.5802 | 77.47% | 4 | 10 | 64.9% | 11.1% | 0 | 0.043179 | 1 | 2.4495 | 0.10577 | Medium | Medium | Medium | 1735 | 1793 | 0.043179 | 27.993 | 0.3136%
LUCERNE 1103630 | LUCERNE 1103 | HUMBOLDT | 12.5736 | 13.6837 | 90.26% | 2 | 19 | 92.62% | 0% | 0 | 0.043155 | 1 | 3.0456 | 0.13143 | Medium | Medium | Medium | 1621 | 1794 | 0.043155 | 27.9498 | 0.3131%
HATTON 11022010 | HATTON 1102 | CENTRAL COAST | 4.0217 | 30.548 | 30.01% | 17 | 5 | 100% | 0% | 0 | 0.043055 | 1 | 2.6454 | 0.1139 | Medium | Medium | Medium | 1692 | 1795 | 0.043055 | 27.9067 | 0.3126%
CURTIS 17058110 | CURTIS 1705 | YOSEMITE | 8.154 | 12.6611 | 71.8% | 0 | 7 | 100% | 22.12% | 0 | 0.043018 | 1 | 3.3987 | 0.14621 | Medium | Medium | High | 1565 | 1796 | 0.043018 | 27.8636 | 0.3122%
TEJON 11022455 | TEJON 1102 | KERN | 6.4984 | 10 | 98.01% | 0 | 2 | 100% | 0% | 0 | 0.043014 | 1 | 1.9757 | 0.084983 | Medium | Medium | Low | 1875 | 1797 | 0.043014 | 27.8206 | 0.3117%
JOLON 11027068 | JOLON 1102 | CENTRAL COAST | 3.8301 | 72.2303 | 100% | 0 | 0 | 100% | 0% | 0 | 0.042992 | 1 | 1.1665 | 0.05015 | Medium | Medium | Low | 2349 | 1798 | 0.042992 | 27.7776 | 0.3112%
CORRAL 1102CB | CORRAL 1102 | STOCKTON | 17.6005 | 19.3826 | 70.6% | 2 | 10 | 83.31% | 0% | 0 | 0.04296 | 1 | 3.1263 | 0.13431 | Medium | Medium | High | 1608 | 1799 | 0.04296 | 27.7346 | 0.3107%
ZACA 1102Y02 | ZACA 1102 | LOS PADRES | 10.6195 | 15.4408 | 92.94% | 0 | 5 | 80.71% | 0% | 0 | 0.042959 | 1 | 1.6742 | 0.071921 | Medium | Medium | Low | 2020 | 1800 | 0.042959 | 27.6916 | 0.3102%
ELECTRA 1101CB | ELECTRA 1101 | STOCKTON | 26.464 | 31.8119 | 57.82% | 4 | 8 | 100% | 0% | 0 | 0.042866 | 1 | 2.4294 | 0.10414 | Medium | Medium | Medium | 1740 | 1801 | 0.042866 | 27.6487 | 0.3097%
SARATOGA 1103LC16 | SARATOGA 1103 | DE ANZA | 4.0893 | 10 | 47.33% | 3 | 10 | 80.63% | 0% | 0 | 0.042849 | 1 | 3.8592 | 0.16536 | Medium | Medium | High | 1509 | 1802 | 0.042849 | 27.6058 | 0.3093%
ANTLER 1101CB | ANTLER 1101 | NORTH VALLEY | 1.601 | 30.2969 | 97.79% | 1 | 1 | 100% | 0% | 0 | 0.042837 | 1 | 1.2522 | 0.053641 | Medium | Medium | Low | 2277 | 1803 | 0.042837 | 27.5629 | 0.3088%
BRENTWOOD 2105B504R | BRENTWOOD 2105 | DIABLO | 7.4348 | 10 | 79.77% | 0 | 6 | 65.97% | 0% | 0 | 0.042733 | 1 | 2.3715 | 0.10134 | Medium | Medium | Medium | 1759 | 1804 | 0.042733 | 27.5201 | 0.3083%
PAUL SWEET 2102CB | PAUL SWEET 2102 | CENTRAL COAST | 0.80988 | 10 | 58.15% | 0 | 0 | 13.51% | 100% | 0 | 0.042651 | 1 | 3.4078 | 0.14534 | Medium | Medium | High | 1573 | 1805 | 0.042651 | 27.4774 | 0.3078%
GARBERVILLE 11022010 | GARBERVILLE 1102 | HUMBOLDT | 6.6438 | 69.4132 | 9.089% | 2 | 3 | 100% | 0% | 0 | 0.042493 | 1 | 1.7903 | 0.076076 | Medium | Medium | Low | 1973 | 1806 | 0.042493 | 27.4347 | 0.3073%
POINT ARENA 1101474 | POINT ARENA 1101 | HUMBOLDT | 9.0104 | 63.6125 | 35.39% | 4 | 6 | 100% | 0% | 0 | 0.042479 | 1 | 2.1511 | 0.091377 | Medium | Medium | Low | 1821 | 1807 | 0.042479 | 27.3922 | 0.3069%
SANTA ROSA A 1104CB | SANTA ROSA A 1104 | SONOMA | 1.1731 | 10 | 48.07% | 0 | 1 | 19.25% | 100% | 0 | 0.042461 | 1 | 3.7672 | 0.15996 | Medium | Medium | High | 1525 | 1808 | 0.042461 | 27.3498 | 0.3064%
STAFFORD 11021048 | STAFFORD 1102 | NORTH BAY | 4.9722 | 28.2651 | 55.55% | 1 | 7 | 93.63% | 17.79% | 1 | 0.042409 | 1 | 3.0962 | 0.13131 | Medium | Medium | High | 1622 | 1809 | 0.042409 | 27.3073 | 0.3059%
MILPITAS 1109XR524 | MILPITAS 1109 | SAN JOSE | 7.8802 | 65.8723 | 90.15% | 0 | 1 | 82.17% | 0% | 0 | 0.042366 | 1 | 3.1206 | 0.13221 | Medium | Medium | High | 1619 | 1810 | 0.042366 | 27.2649 | 0.3054%
FROGTOWN 17021573 | FROGTOWN 1702 | STOCKTON | 18.0626 | 46.2084 | 95.86% | 0 | 3 | 100% | 0% | 0 | 0.042352 | 1 | 2.1385 | 0.090571 | Medium | Medium | Low | 1827 | 1811 | 0.042352 | 27.2225 | 0.305%
SOBRANTE 1102CB | SOBRANTE 1102 | DIABLO | 10.2599 | 28.2629 | 22.78% | 2 | 15 | 98.33% | 12.04% | 0 | 0.042314 | 1 | 3.0143 | 0.12755 | Medium | Medium | Medium | 1634 | 1812 | 0.042314 | 27.1802 | 0.3045%
AUBERRY 1101CB | AUBERRY 1101 | FRESNO | 18.1441 | 19.2243 | 60.88% | 0 | 19 | 100% | 0% | 0 | 0.042195 | 1 | 2.6192 | 0.11052 | Medium | Medium | Medium | 1708 | 1813 | 0.042195 | 27.1379 | 0.304%
FITCH MOUNTAIN 11134566 | FITCH MOUNTAIN 1113 | SONOMA | 10.4618 | 71.5628 | 83.49% | 1 | 5 | 60.29% | 0% | 0 | 0.042183 | 1 | 2.5279 | 0.10663 | Medium | Medium | Medium | 1727 | 1814 | 0.042183 | 27.0957 | 0.3035%
PACIFICA 11033907 | PACIFICA 1103 | PENINSULA | 3.5027 | 51.2022 | 0% | 4 | 0 | 72.69% | 71.75% | 0 | 0.042148 | 1 | 3.6814 | 0.15517 | Medium | Medium | High | 1538 | 1815 | 0.042148 | 27.0535 | 0.3031%
ALTO 112278672 | ALTO 1122 | NORTH BAY | 2.7277 | 18.1694 | 27.03% | 6 | 9 | 33.13% | 66.64% | 0 | 0.042144 | 1 | 3.6273 | 0.15287 | Medium | Medium | High | 1546 | 1816 | 0.042144 | 27.0113 | 0.3026%
VACAVILLE 11088762 | VACAVILLE 1108 | SACRAMENTO | 13.206 | 54.7168 | 79.67% | 1 | 3 | 78.91% | 0% | 0 | 0.042096 | 1 | 2.7832 | 0.11716 | Medium | Medium | Medium | 1679 | 1817 | 0.042096 | 26.9692 | 0.3021%
PALMER 1101M84 | PALMER 1101 | LOS PADRES | 19.4244 | 65.3938 | 31.64% | 0 | 6 | 79.33% | 0% | 0 | 0.042007 | 1 | 1.1845 | 0.049756 | Medium | Medium | Low | 2355 | 1818 | 0.042007 | 26.9271 | 0.3017%
APPLE HILL 210251792 | APPLE HILL 2102 | SIERRA | 9.3607 | 11.5456 | 100% | 6 | 2 | 100% | 0% | 0 | 0.04191 | 1 | 1.7949 | 0.075224 | Medium | Medium | Low | 1982 | 1819 | 0.04191 | 26.8851 | 0.3012%
KANAKA 11011036 | KANAKA 1101 | NORTH VALLEY | 0.60846 | 67.9249 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041796 | 1 | 2.0662 | 0.086358 | Medium | Medium | Low | 1864 | 1820 | 0.041796 | 26.8432 | 0.3007%
WISE 1102CB | WISE 1102 | SIERRA | 18.631 | 17.4842 | 45.37% | 6 | 22 | 98.52% | 0% | 0 | 0.0417 | 1 | 2.7235 | 0.11357 | Medium | Medium | Medium | 1696 | 1821 | 0.0417 | 26.8014 | 0.3003%
ANNAPOLIS 1101CB | ANNAPOLIS 1101 | HUMBOLDT | 0.65809 | 81.2301 | 84.52% | 1 | 1 | 100% | 0% | 0 | 0.041698 | 1 | 1.4144 | 0.058979 | Medium | Medium | Low | 2196 | 1822 | 0.041698 | 26.7597 | 0.2998%
BEAR VALLEY 21059480 | BEAR VALLEY 2105 | YOSEMITE | 12.4081 | 50.2702 | 94.93% | 2 | 0 | 100% | 0% | 0 | 0.041692 | 1 | 1.3091 | 0.054581 | Medium | Medium | Low | 2265 | 1823 | 0.041692 | 26.718 | 0.2993%
FRUITLAND 11422006 | FRUITLAND 1142 | HUMBOLDT | 8.3587 | 77.2327 | 73.06% | 6 | 2 | 90.12% | 0% | 0 | 0.041689 | 1 | 2.1223 | 0.088478 | Medium | Medium | Low | 1841 | 1824 | 0.041689 | 26.6763 | 0.2989%
TIVY VALLEY 1107R1817 | TIVY VALLEY 1107 | FRESNO | 19.042 | 15.3654 | 99.23% | 0 | 5 | 99.01% | 0% | 0 | 0.041647 | 1 | 1.8427 | 0.076744 | Medium | Medium | Low | 1965 | 1825 | 0.041647 | 26.6346 | 0.2984%
ALTO 11251158 | ALTO 1125 | NORTH BAY | 2.2748 | 24.9991 | 11.61% | 1 | 1 | 41.4% | 88.18% | 0 | 0.041574 | 1 | 4.1164 | 0.17113 | Medium | Medium | High | 1496 | 1826 | 0.041574 | 26.5929 | 0.2979%
OREGON TRAIL 11031448 | OREGON TRAIL 1103 | NORTH VALLEY | 30.932 | 14.1761 | 100% | 1 | 10 | 100% | 0% | 0 | 0.041357 | 1 | 1.5321 | 0.063365 | Medium | Medium | Low | 2126 | 1827 | 0.041357 | 26.5514 | 0.2975%
STILLWATER 110248952 | STILLWATER 1102 | NORTH VALLEY | 10.5922 | 15.961 | 100% | 1 | 3 | 100% | 0% | 0 | 0.041312 | 1 | 1.6325 | 0.067444 | Medium | Medium | Low | 2066 | 1828 | 0.041312 | 26.51 | 0.297%
CLAYTON 221355668 | CLAYTON 2213 | DIABLO | 3.8789 | 27.0823 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041308 | 1 | 4.0479 | 0.16721 | Medium | Medium | High | 1506 | 1829 | 0.041308 | 26.4687 | 0.2965%
BEAR VALLEY 21054170 | BEAR VALLEY 2105 | YOSEMITE | 9.5178 | 57.2029 | 100% | 3 | 1 | 100% | 0% | 0 | 0.041292 | 1 | 0.64305 | 0.026553 | Medium | Medium | Low | 2847 | 1830 | 0.041292 | 26.4274 | 0.2961%
LOS GATOS 1107CB | LOS GATOS 1107 | DE ANZA | 13.6639 | 15.4902 | 38.19% | 1 | 13 | 86.42% | 10.54% | 0 | 0.041286 | 1 | 3.2819 | 0.1355 | Medium | Medium | High | 1602 | 1831 | 0.041286 | 26.3861 | 0.2956%
LOS GATOS 1101LB40 | LOS GATOS 1101 | DE ANZA | 7.214 | 10 | 65.42% | 2 | 3 | 77.51% | 0% | 0 | 0.041155 | 1 | 3.5497 | 0.14609 | Medium | Medium | High | 1567 | 1832 | 0.041155 | 26.3448 | 0.2951%
CARLOTTA 11214914 | CARLOTTA 1121 | HUMBOLDT | 11.4615 | 25.5188 | 70.14% | 16 | 11 | 80.82% | 0% | 0 | 0.041044 | 1 | 1.8825 | 0.077265 | Medium | Medium | Low | 1961 | 1833 | 0.041044 | 26.3037 | 0.2947%
TEMPLETON 2110N30 | TEMPLETON 2110 | LOS PADRES | 20.4995 | 52.4771 | 52.2% | 1 | 3 | 100% | 0% | 0 | 0.040875 | 1 | 2.2426 | 0.091666 | Medium | Medium | Medium | 1820 | 1834 | 0.040875 | 26.2626 | 0.2942%
TEMPLETON 2110R06 | TEMPLETON 2110 | LOS PADRES | 5.1326 | 51.0168 | 86.51% | 3 | 1 | 19.81% | 33.5% | 0 | 0.040874 | 1 | 2.3652 | 0.096678 | Medium | Medium | Medium | 1789 | 1835 | 0.040874 | 26.2217 | 0.2938%
ROSSMOOR 1108CB | ROSSMOOR 1108 | DIABLO | 3.0229 | 50.0663 | 2.294% | 0 | 11 | 53.4% | 61.71% | 0 | 0.040788 | 1 | 3.9971 | 0.16304 | Medium | Medium | High | 1515 | 1836 | 0.040788 | 26.1809 | 0.2933%
OLETA 11014768 | OLETA 1101 | STOCKTON | 12.2184 | 44.115 | 100% | 0 | 5 | 89.74% | 0% | 0 | 0.040719 | 1 | 1.6733 | 0.068136 | Medium | Medium | Low | 2060 | 1837 | 0.040719 | 26.1401 | 0.2928%
COLUMBIA HILL 110190730 | COLUMBIA HILL 1101 | SIERRA | 8.3212 | 17.8031 | 100% | 1 | 4 | 100% | 5.083% | 1 | 0.040638 | 1 | 1.7208 | 0.069929 | Medium | Medium | Low | 2046 | 1838 | 0.040638 | 26.0994 | 0.2924%
GREENBRAE 11036083 | GREENBRAE 1103 | NORTH BAY | 0.34152 | 10 | 10.92% | 0 | 0 | 100% | 67.56% | 0 | 0.040594 | 1 | 3.6438 | 0.14792 | Medium | Medium | High | 1560 | 1839 | 0.040594 | 26.0587 | 0.2919%
SAN LEANDRO U 1109CR002 | SAN LEANDRO U 1109 | MISSION | 7.0761 | 10 | 24.57% | 6 | 16 | 90.45% | 0% | 0 | 0.040555 | 1 | 3.3026 | 0.13394 | Medium | Medium | High | 1610 | 1840 | 0.040555 | 26.0181 | 0.2915%
AUBERRY 1102R309 | AUBERRY 1102 | FRESNO | 8.5895 | 21.9499 | 78.92% | 1 | 2 | 100% | 0% | 0 | 0.04051 | 1 | 1.7362 | 0.070333 | Medium | Medium | Low | 2041 | 1841 | 0.04051 | 25.9776 | 0.291%
CLOVERDALE 110112719 | CLOVERDALE 1101 | SONOMA | 4.9181 | 80.6066 | 85.19% | 0 | 3 | 67.33% | 0% | 0 | 0.040502 | 1 | 2.4017 | 0.097273 | Medium | Medium | Medium | 1786 | 1842 | 0.040502 | 25.9371 | 0.2906%
GEYSERVILLE 1102350 | GEYSERVILLE 1102 | SONOMA | 3.9586 | 50.2588 | 84.68% | 0 | 1 | 20.33% | 44.47% | 1 | 0.040497 | 1 | 2.3001 | 0.093146 | Medium | Medium | Medium | 1809 | 1843 | 0.040497 | 25.8966 | 0.2901%
HAMILTON BRANCH 110118205 | HAMILTON BRANCH 1101 | NORTH VALLEY | 4.0384 | 59.6103 | 100% | 0 | 1 | 100% | 0% | 0 | 0.040382 | 1 | 1.7837 | 0.072028 | Medium | Medium | Low | 2018 | 1844 | 0.040382 | 25.8561 | 0.2897%
MERCED FALLS 11029470 | MERCED FALLS 1102 | YOSEMITE | 22.9864 | 12.6287 | 82.62% | 0 | 4 | 100% | 0% | 0 | 0.040338 | 1 | 0.22626 | 0.0091268 | Medium | Medium | Low | 3151 | 1845 | 0.040338 | 25.8157 | 0.2892%
EL CERRITO G 1105CB | EL CERRITO G 1105 | EAST BAY | 7.4165 | 22.6789 | 12.34% | 2 | 5 | 100% | 20.23% | 0 | 0.040319 | 1 | 4.7752 | 0.19253 | Medium | Medium | High | 1431 | 1846 | 0.040319 | 25.7753 | 0.2888%
SARATOGA 1105LC14 | SARATOGA 1105 | DE ANZA | 9.6151 | 10 | 69.49% | 2 | 9 | 86.08% | 0% | 0 | 0.040305 | 1 | 3.6261 | 0.14615 | Medium | Medium | High | 1566 | 1847 | 0.040305 | 25.735 | 0.2883%
SHINGLE SPRINGS 11038752 | SHINGLE SPRINGS 1103 | SIERRA | 1.8752 | 10 | 77.05% | 0 | 1 | 100% | 7.72% | 0 | 0.040295 | 1 | 3.4298 | 0.1382 | Medium | Medium | High | 1592 | 1848 | 0.040295 | 25.6947 | 0.2879%
PACIFICA 1102CB | PACIFICA 1102 | PENINSULA | 2.2873 | 19.4 | 0% | 0 | 1 | 33.56% | 100% | 0 | 0.040266 | 1 | 4.2842 | 0.17251 | Medium | Medium | High | 1489 | 1849 | 0.040266 | 25.6544 | 0.2874%
TEJON 11023760 | TEJON 1102 | KERN | 5.5529 | 84.6891 | 100% | 0 | 0 | 84.6% | 0% | 0 | 0.040235 | 1 | 0.85149 | 0.03426 | Medium | Medium | Low | 2674 | 1850 | 0.040235 | 25.6142 | 0.287%
BEAR VALLEY 2105CB | BEAR VALLEY 2105 | YOSEMITE | 3.852 | 80.717 | 62.63% | 2 | 1 | 100% | 0% | 0 | 0.040229 | 1 | 0.22311 | 0.0089755 | Medium | Medium | Low | 3153 | 1851 | 0.040229 | 25.5739 | 0.2865%
OLETA 11011208 | OLETA 1101 | STOCKTON | 32.4243 | 51.211 | 80.1% | 0 | 12 | 85.11% | 0% | 0 | 0.040132 | 1 | 1.3763 | 0.055235 | Medium | Medium | Low | 2255 | 1852 | 0.040132 | 25.5337 | 0.2861%
BEAR VALLEY 210110019 | BEAR VALLEY 2101 | YOSEMITE | 1.9804 | 23.7531 | 100% | 0 | 6 | 100% | 0% | 0 | 0.04012 | 1 | 0.35957 | 0.014426 | Medium | Medium | Low | 3109 | 1853 | 0.04012 | 25.4936 | 0.2856%
CURTIS 1705CB | CURTIS 1705 | YOSEMITE | 13.2215 | 11.2937 | 56.4% | 2 | 15 | 96.23% | 0% | 0 | 0.040107 | 1 | 3.4615 | 0.13883 | Medium | Medium | High | 1587 | 1854 | 0.040107 | 25.4534 | 0.2852%
PANORAMA 11021632 | PANORAMA 1102 | NORTH VALLEY | 8.5492 | 81.3182 | 43.52% | 0 | 3 | 100% | 0% | 0 | 0.040056 | 1 | 1.1987 | 0.048014 | Medium | Medium | Low | 2379 | 1855 | 0.040056 | 25.4133 | 0.2847%
KERCKHOFF 1101R353 | KERCKHOFF 1101 | YOSEMITE | 13.7831 | 33.1172 | 88.25% | 0 | 1 | 100% | 0% | 0 | 0.039955 | 1 | 1.6842 | 0.067293 | Medium | Medium | Low | 2069 | 1856 | 0.039955 | 25.3733 | 0.2843%
HALF MOON BAY 11036012 | HALF MOON BAY 1103 | PENINSULA | 5.8906 | 54.5639 | 76.22% | 11 | 4 | 61.12% | 0% | 0 | 0.039954 | 1 | 2.0637 | 0.082451 | Medium | Medium | Low | 1907 | 1857 | 0.039954 | 25.3333 | 0.2838%
SAN JOAQUIN #2 1103157026 | SAN JOAQUIN #2 1103 | YOSEMITE | 3.2012 | 10 | 100% | 2 | 9 | 100% | 0% | 0 | 0.039941 | 1 | 1.3059 | 0.052157 | Medium | Medium | Low | 2304 | 1858 | 0.039941 | 25.2934 | 0.2834%
PHILO 11013700 | PHILO 1101 | HUMBOLDT | 18.1219 | 64.058 | 52.24% | 7 | 7 | 100% | 0% | 0 | 0.039935 | 1 | 1.5874 | 0.063395 | Medium | Medium | Low | 2124 | 1859 | 0.039935 | 25.2534 | 0.2829%
DEL MONTE 210436720 | DEL MONTE 2104 | CENTRAL COAST | 6.1198 | 15.0991 | 78.82% | 1 | 2 | 76.61% | 0% | 0 | 0.039935 | 1 | 3.0657 | 0.12243 | Medium | Medium | Medium | 1654 | 1860 | 0.039935 | 25.2135 | 0.2825%
VOLTA 110165764 | VOLTA 1101 | NORTH VALLEY | 10.3627 | 58.9136 | 100% | 1 | 0 | 100% | 0% | 0 | 0.0399 | 1 | 0.80592 | 0.032156 | Medium | Medium | Low | 2722 | 1861 | 0.0399 | 25.1736 | 0.282%
DEL MONTE 21042762 | DEL MONTE 2104 | CENTRAL COAST | 9.4859 | 27.7626 | 17.65% | 2 | 4 | 85.79% | 0% | 0 | 0.03979 | 1 | 2.0858 | 0.082991 | Medium | Medium | Low | 1900 | 1862 | 0.03979 | 25.1337 | 0.2816%
BEAR VALLEY 210110000 | BEAR VALLEY 2101 | YOSEMITE | 29.476 | 56.7898 | 61.86% | 4 | 0 | 88.5% | 0% | 0 | 0.039743 | 1 | 0.58061 | 0.023075 | Medium | Medium | Low | 2936 | 1863 | 0.039743 | 25.0939 | 0.2811%
BUELLTON 1101Y26 | BUELLTON 1101 | LOS PADRES | 14.0549 | 47.3747 | 54.06% | 1 | 8 | 88.5% | 0% | 0 | 0.039723 | 1 | 2.0524 | 0.081528 | Medium | Medium | Low | 1919 | 1864 | 0.039723 | 25.0541 | 0.2807%
ALTO 1125CB | ALTO 1125 | NORTH BAY | 0.27217 | 10 | 45.49% | 2 | 1 | 11.73% | 100% | 0 | 0.039699 | 1 | 3.9974 | 0.15869 | Medium | Medium | High | 1529 | 1865 | 0.039699 | 25.0144 | 0.2802%
VIEJO 2203CB | VIEJO 2203 | CENTRAL COAST | 3.0922 | 10 | 21.75% | 26 | 9 | 92.05% | 0% | 0 | 0.039672 | 1 | 3.0156 | 0.11963 | Medium | Medium | Medium | 1665 | 1866 | 0.039672 | 24.9747 | 0.2798%
WHITMORE 110145262 | WHITMORE 1101 | NORTH VALLEY | 28.7585 | 25.719 | 87.63% | 2 | 2 | 100% | 0% | 0 | 0.03964 | 1 | 1.5616 | 0.061901 | Medium | Medium | Low | 2153 | 1867 | 0.03964 | 24.935 | 0.2793%
CAMBRIA 1101V76 | CAMBRIA 1101 | LOS PADRES | 20.0895 | 13.7459 | 1.828% | 1 | 2 | 100% | 0% | 0 | 0.039572 | 1 | 1.1661 | 0.046144 | Medium | Medium | Low | 2417 | 1868 | 0.039572 | 24.8954 | 0.2789%
ZACA 1101Y72 | ZACA 1101 | LOS PADRES | 6.264 | 51.6717 | 31.17% | 0 | 0 | 97.2% | 23.49% | 0 | 0.039557 | 1 | 1.2802 | 0.050641 | Medium | Medium | Low | 2341 | 1869 | 0.039557 | 24.8558 | 0.2785%
MESA 1103M72 | MESA 1103 | LOS PADRES | 9.6841 | 10 | 75.44% | 1 | 10 | 38.47% | 0% | 0 | 0.039556 | 1 | 2.326 | 0.092007 | Medium | Medium | Medium | 1818 | 1870 | 0.039556 | 24.8163 | 0.278%
RACETRACK 17038120 | RACETRACK 1703 | YOSEMITE | 8.8205 | 16.6525 | 57.46% | 3 | 10 | 100% | 16.02% | 1 | 0.03955 | 1 | 2.9886 | 0.1182 | Medium | Medium | Medium | 1672 | 1871 | 0.03955 | 24.7767 | 0.2776%
SUNOL 1101MR387 | SUNOL 1101 | MISSION | 4.657 | 55.0854 | 92.88% | 0 | 1 | 93.35% | 0% | 0 | 0.03951 | 1 | 1.6108 | 0.063643 | Medium | Medium | Low | 2122 | 1872 | 0.03951 | 24.7372 | 0.2771%
UPPER LAKE 11011276 | UPPER LAKE 1101 | HUMBOLDT | 12.9332 | 76.2596 | 54.71% | 3 | 4 | 100% | 0% | 0 | 0.039478 | 1 | 1.1564 | 0.045653 | Medium | Medium | Low | 2428 | 1873 | 0.039478 | 24.6977 | 0.2767%
PEORIA 170169124 | PEORIA 1701 | YOSEMITE | 2.706 | 13.7023 | 100% | 0 | 2 | 100% | 0% | 0 | 0.039389 | 1 | 1.3543 | 0.053345 | Medium | Medium | Low | 2285 | 1874 | 0.039389 | 24.6582 | 0.2762%
FROGTOWN 1702L5407 | FROGTOWN 1702 | STOCKTON | 17.9809 | 33.0373 | 100% | 0 | 9 | 98.72% | 0% | 0 | 0.03936 | 1 | 2.2967 | 0.090399 | Medium | Medium | Medium | 1828 | 1875 | 0.03936 | 24.6188 | 0.2758%
COTTONWOOD 1102CB | COTTONWOOD 1102 | NORTH VALLEY | 16.7139 | 23.1081 | 88.08% | 1 | 4 | 71.09% | 0% | 0 | 0.039338 | 1 | 2.1337 | 0.083935 | Medium | Medium | Low | 1888 | 1876 | 0.039338 | 24.5794 | 0.2754%
PIT NO 5 11011658 | PIT NO 5 1101 | NORTH VALLEY | 4.5542 | 60.6461 | 59.05% | 1 | 2 | 100% | 0% | 0 | 0.039255 | 1 | 0.48755 | 0.019139 | Medium | Medium | Low | 3024 | 1877 | 0.039255 | 24.5401 | 0.2749%
AUBERRY 1102R1013 | AUBERRY 1102 | FRESNO | 12.3506 | 22.637 | 85.13% | 0 | 11 | 100% | 0% | 0 | 0.039152 | 1 | 2.1117 | 0.082679 | Medium | Medium | Low | 1904 | 1878 | 0.039152 | 24.5008 | 0.2745%
SILVERADO 2102808 | SILVERADO 2102 | NORTH BAY | 1.929 | 85.4925 | 100% | 0 | 0 | 40.02% | 25.27% | 0 | 0.039111 | 1 | 2.4149 | 0.094447 | Medium | Medium | Medium | 1803 | 1879 | 0.039111 | 24.4617 | 0.274%
BROWNS VALLEY 110197188 | BROWNS VALLEY 1101 | SIERRA | 6.5763 | 19.9978 | 93.03% | 2 | 3 | 95.83% | 0% | 0 | 0.03906 | 1 | 1.6554 | 0.064659 | Medium | Medium | Low | 2105 | 1880 | 0.03906 | 24.4226 | 0.2736%
DUNLAP 11037040 | DUNLAP 1103 | FRESNO | 24.7254 | 12.3243 | 100% | 0 | 2 | 100% | 0% | 0 | 0.039034 | 1 | 1.8465 | 0.072078 | Medium | Medium | Low | 2016 | 1881 | 0.039034 | 24.3835 | 0.2732%
ORINDA 0401N545R | ORINDA 0401 | DIABLO | 4.3157 | 10 | 9.802% | 1 | 11 | 83.77% | 52.25% | 0 | 0.038927 | 1 | 3.2801 | 0.12768 | Medium | Medium | High | 1632 | 1882 | 0.038927 | 24.3445 | 0.2727%
HIGGINS 11097831 | HIGGINS 1109 | SIERRA | 5.5525 | 26.5829 | 100% | 4 | 1 | 100% | 0% | 0 | 0.038882 | 1 | 2.4524 | 0.095352 | Medium | Medium | Medium | 1796 | 1883 | 0.038882 | 24.3056 | 0.2723%
OLETA 1102CB | OLETA 1102 | STOCKTON | 12.9237 | 28.5426 | 79.87% | 0 | 5 | 85.32% | 0% | 0 | 0.038817 | 1 | 2.0783 | 0.080675 | Medium | Medium | Low | 1929 | 1884 | 0.038817 | 24.2667 | 0.2719%
OCEANO 1102V56 | OCEANO 1102 | LOS PADRES | 9.7421 | 10 | 68.41% | 1 | 15 | 98.35% | 0% | 0 | 0.03877 | 1 | 2.5506 | 0.098886 | Medium | Medium | Medium | 1779 | 1885 | 0.03877 | 24.2279 | 0.2714%
SO. CAL. EDISON #3 1101CB | SO. CAL. EDISON #3 1101 | FRESNO | 6.4255 | 72.2284 | 15.88% | 0 | 1 | 100% | 34.58% | 0 | 0.038701 | 1 | 1.4452 | 0.055932 | Medium | Medium | Low | 2247 | 1886 | 0.038701 | 24.1891 | 0.271%
HALF MOON BAY 110369412 | HALF MOON BAY 1103 | PENINSULA | 16.9285 | 23.3773 | 24.92% | 11 | 5 | 79.06% | 0% | 0 | 0.038624 | 1 | 1.6101 | 0.062188 | Medium | Medium | Low | 2142 | 1887 | 0.038624 | 24.1504 | 0.2706%
GEYSERVILLE 1102522 | GEYSERVILLE 1102 | SONOMA | 8.3806 | 11.5615 | 69.84% | 1 | 7 | 78.98% | 12.25% | 0 | 0.038533 | 1 | 1.5258 | 0.058796 | Medium | Medium | Low | 2199 | 1888 | 0.038533 | 24.1118 | 0.2701%
LUCERNE 1106664 | LUCERNE 1106 | HUMBOLDT | 6.0536 | 25.8226 | 47.99% | 4 | 24 | 54.26% | 0% | 0 | 0.038531 | 1 | 3.0381 | 0.11706 | Medium | Medium | Medium | 1680 | 1889 | 0.038531 | 24.0732 | 0.2697%
MIRABEL 1102334 | MIRABEL 1102 | SONOMA | 5.6083 | 39.7869 | 41.25% | 2 | 2 | 61.12% | 47.7% | 0 | 0.038421 | 1 | 3.0999 | 0.1191 | Medium | Medium | High | 1668 | 1890 | 0.038421 | 24.0347 | 0.2693%
DUNLAP 11037220 | DUNLAP 1103 | FRESNO | 24.8173 | 17.858 | 99.97% | 1 | 5 | 100% | 0% | 0 | 0.0383 | 1 | 1.4867 | 0.056942 | Medium | Medium | Low | 2227 | 1891 | 0.0383 | 23.9963 | 0.2688%
DIAMOND SPRINGS 110650324 | DIAMOND SPRINGS 1106 | SIERRA | 17.7246 | 10 | 70.6% | 6 | 3 | 87.05% | 0% | 0 | 0.038264 | 1 | 2.3467 | 0.089792 | Medium | Medium | Medium | 1836 | 1892 | 0.038264 | 23.958 | 0.2684%
VOLTA 110149742 | VOLTA 1101 | NORTH VALLEY | 3.4776 | 49.9174 | 84.98% | 0 | 1 | 100% | 0% | 0 | 0.038241 | 1 | 1.3857 | 0.05299 | Medium | Medium | Low | 2289 | 1893 | 0.038241 | 23.9197 | 0.268%
RESERVATION ROAD 11023030 | RESERVATION ROAD 1102 | CENTRAL COAST | 4.2831 | 56.4796 | 100% | 0 | 1 | 16.48% | 0% | 0 | 0.038229 | 1 | 1.4511 | 0.055473 | Medium | Medium | Low | 2253 | 1894 | 0.038229 | 23.8815 | 0.2675%
POSO MOUNTAIN 21033988 | POSO MOUNTAIN 2103 | KERN | 17.2368 | 49.5955 | 64.44% | 0 | 0 | 92.36% | 0% | 0 | 0.038161 | 1 | 2.6824 | 0.10236 | Medium | Medium | Medium | 1751 | 1895 | 0.038161 | 23.8432 | 0.2671%
DIAMOND SPRINGS 110676088 | DIAMOND SPRINGS 1106 | SIERRA | 11.0713 | 10.8319 | 90.75% | 3 | 3 | 100% | 0% | 0 | 0.038075 | 1 | 2.2072 | 0.08404 | Medium | Medium | Low | 1884 | 1896 | 0.038075 | 23.8051 | 0.2667%
PACIFICA 110311153 | PACIFICA 1103 | PENINSULA | 0.48816 | 27.9974 | 36.15% | 0 | 1 | 5.373% | 100% | 0 | 0.038047 | 1 | 3.4976 | 0.13307 | Medium | Medium | High | 1614 | 1897 | 0.038047 | 23.767 | 0.2663%
PARADISE 110343008 | PARADISE 1103 | NORTH VALLEY | 12.9696 | 10 | 78.07% | 7 | 5 | 99.92% | 17.25% | 1 | 0.037995 | 1 | 3.5408 | 0.13453 | Medium | Medium | High | 1606 | 1898 | 0.037995 | 23.729 | 0.2658%
CLARK ROAD 110247006 | CLARK ROAD 1102 | NORTH VALLEY | 4.5495 | 10 | 42.4% | 2 | 3 | 100% | 41.72% | 0 | 0.037887 | 1 | 3.3709 | 0.12771 | Medium | Medium | High | 1631 | 1899 | 0.037887 | 23.691 | 0.2654%
PEORIA 1701CB | PEORIA 1701 | YOSEMITE | 8.8374 | 31.1758 | 54.24% | 0 | 6 | 100% | 0% | 0 | 0.037882 | 1 | 0.69967 | 0.026505 | Medium | Medium | Low | 2851 | 1900 | 0.037882 | 23.6531 | 0.265%
SUMMIT 110148632 | SUMMIT 1101 | SIERRA | 2.7291 | 10 | 63.45% | 5 | 6 | 100% | 0% | 0 | 0.037786 | 1 | 1.8801 | 0.071043 | Medium | Medium | Low | 2032 | 1901 | 0.037786 | 23.6152 | 0.2646%
GARBERVILLE 1101CB | GARBERVILLE 1101 | HUMBOLDT | 6.497 | 63.3643 | 74.83% | 4 | 3 | 74.77% | 0% | 0 | 0.037653 | 1 | 2.3445 | 0.088278 | Medium | Medium | Medium | 1843 | 1902 | 0.037653 | 23.5774 | 0.2641%
BROWNS VALLEY 110193870 | BROWNS VALLEY 1101 | SIERRA | 16.0223 | 22.1517 | 92.34% | 3 | 17 | 47.1% | 0% | 0 | 0.037632 | 1 | 2.4175 | 0.090975 | Medium | Medium | Medium | 1824 | 1903 | 0.037632 | 23.5398 | 0.2637%
BIG MEADOWS 21012586 | BIG MEADOWS 2101 | NORTH VALLEY | 9.5691 | 78.6746 | 93% | 0 | 0 | 87.41% | 0% | 0 | 0.037594 | 1 | 2.3215 | 0.087275 | Medium | Medium | Medium | 1853 | 1904 | 0.037594 | 23.5021 | 0.2633%
FRENCH GULCH 11012905 | FRENCH GULCH 1101 | NORTH VALLEY | 9.7071 | 49.4271 | 100% | 1 | 0 | 100% | 0% | 0 | 0.037487 | 1 | 1.1218 | 0.042053 | Medium | Medium | Low | 2496 | 1905 | 0.037487 | 23.4645 | 0.2629%
OLEMA 1101602 | OLEMA 1101 | NORTH BAY | 15.0972 | 65.987 | 1.264% | 8 | 10 | 59.79% | 0% | 0 | 0.037469 | 1 | 2.0944 | 0.078477 | Medium | Medium | Low | 1948 | 1906 | 0.037469 | 23.427 | 0.2624%
DUNLAP 11027849F | DUNLAP 1102 | FRESNO | 8.6653 | 17.4771 | 100% | 3 | 9 | 100% | 0% | 0 | 0.037371 | 1 | 1.0288 | 0.038447 | Medium | Medium | Low | 2573 | 1907 | 0.037371 | 23.3896 | 0.262%
TEMPLETON 2110R94 | TEMPLETON 2110 | LOS PADRES | 13.9551 | 53.972 | 81.64% | 0 | 3 | 66.74% | 0% | 0 | 0.037368 | 1 | 2.1258 | 0.079438 | Medium | Medium | Low | 1939 | 1908 | 0.037368 | 23.3522 | 0.2616%
DEL MONTE 21032000 | DEL MONTE 2103 | CENTRAL COAST | 8.9713 | 10 | 21.71% | 13 | 11 | 98.79% | 0% | 0 | 0.037343 | 1 | 3.097 | 0.11565 | Medium | Medium | High | 1688 | 1909 | 0.037343 | 23.3148 | 0.2612%
ELECTRA 110161816 | ELECTRA 1101 | STOCKTON | 12.191 | 16.1858 | 89% | 5 | 6 | 100% | 0% | 0 | 0.03728 | 1 | 2.7215 | 0.10146 | Medium | Medium | Medium | 1758 | 1910 | 0.03728 | 23.2775 | 0.2608%
RED BLUFF 11041302 | RED BLUFF 1104 | NORTH VALLEY | 14.0918 | 39.8066 | 84.84% | 0 | 4 | 98.04% | 0% | 0 | 0.03726 | 1 | 1.6666 | 0.062097 | Medium | Medium | Low | 2144 | 1911 | 0.03726 | 23.2402 | 0.2604%
AUBERRY 1102R902 | AUBERRY 1102 | FRESNO | 15.0447 | 11.5312 | 82.04% | 0 | 7 | 100% | 0% | 0 | 0.037249 | 1 | 1.9232 | 0.071637 | Medium | Medium | Low | 2026 | 1912 | 0.037249 | 23.2029 | 0.2599%
TASSAJARA 2112D514R | TASSAJARA 2112 | DIABLO | 3.458 | 10.5192 | 20.09% | 0 | 5 | 72.43% | 34.87% | 0 | 0.03721 | 1 | 4.003 | 0.14895 | Medium | Medium | High | 1556 | 1913 | 0.03721 | 23.1657 | 0.2595%
HIGGINS 1109CB | HIGGINS 1109 | SIERRA | 22.2012 | 22.658 | 81.89% | 2 | 4 | 95.77% | 0% | 0 | 0.037105 | 1 | 2.9246 | 0.10852 | Medium | Medium | Medium | 1717 | 1914 | 0.037105 | 23.1285 | 0.2591%
CALAVERAS CEMENT 110136880 | CALAVERAS CEMENT 1101 | STOCKTON | 7.22 | 30.9732 | 81.65% | 0 | 2 | 83.77% | 0% | 0 | 0.037097 | 1 | 2.235 | 0.082911 | Medium | Medium | Medium | 1901 | 1915 | 0.037097 | 23.0914 | 0.2587%
RACETRACK 17036014 | RACETRACK 1703 | YOSEMITE | 6.8384 | 27.2462 | 64.22% | 2 | 1 | 100% | 0% | 0 | 0.037053 | 1 | 2.8715 | 0.1064 | Medium | Medium | Medium | 1728 | 1916 | 0.037053 | 23.0543 | 0.2583%
ALLEGHANY 1101978 | ALLEGHANY 1101 | SIERRA | 13.0219 | 53.8471 | 100% | 3 | 4 | 44.63% | 0% | 0 | 0.037002 | 1 | 2.0065 | 0.074244 | Medium | Medium | Low | 1996 | 1917 | 0.037002 | 23.0172 | 0.2579%
LAKEWOOD 2224D522R | LAKEWOOD 2224 | DIABLO | 0.67815 | 10 | 23.16% | 0 | 1 | 25.38% | 100% | 0 | 0.036972 | 1 | 3.2556 | 0.12036 | Medium | Medium | High | 1663 | 1918 | 0.036972 | 22.9802 | 0.2574%
EDES 1112CR312 | EDES 1112 | EAST BAY | 3.6853 | 22.7087 | 18.65% | 2 | 11 | 99.92% | 20.18% | 0 | 0.036955 | 1 | 3.2611 | 0.12051 | Medium | Medium | High | 1661 | 1919 | 0.036955 | 22.9433 | 0.257%
GUALALA 1111445166 | GUALALA 1111 | HUMBOLDT | 7.5421 | 19.2895 | 4.143% | 11 | 12 | 79.44% | 0% | 0 | 0.036855 | 1 | 1.6737 | 0.061683 | Medium | Medium | Low | 2157 | 1920 | 0.036855 | 22.9063 | 0.2566%
CLOVERDALE 1101112 | CLOVERDALE 1101 | SONOMA | 19.0544 | 64.0868 | 84.08% | 2 | 8 | 69.85% | 0% | 0 | 0.036824 | 1 | 2.0172 | 0.074281 | Medium | Medium | Low | 1995 | 1921 | 0.036824 | 22.8695 | 0.2562%
TEMPLETON 2113R82 | TEMPLETON 2113 | LOS PADRES | 34.6176 | 62.3861 | 93.76% | 0 | 4 | 50.19% | 6.458% | 0 | 0.03681 | 1 | 0.75794 | 0.0279 | Medium | Medium | Low | 2817 | 1922 | 0.03681 | 22.8326 | 0.2558%
PEORIA 17056697 | PEORIA 1705 | YOSEMITE | 4.1363 | 14.6236 | 100% | 1 | 4 | 100% | 0% | 0 | 0.036751 | 1 | 2.6171 | 0.096184 | Medium | Medium | Medium | 1790 | 1923 | 0.036751 | 22.7958 | 0.2554%
CURTIS 170565908 | CURTIS 1705 | YOSEMITE | 12.8972 | 32.2499 | 79.87% | 2 | 10 | 77.15% | 0% | 0 | 0.036689 | 1 | 2.8987 | 0.10635 | Medium | Medium | Medium | 1729 | 1924 | 0.036689 | 22.7591 | 0.255%
WYANDOTTE 110777578 | WYANDOTTE 1107 | NORTH VALLEY | 21.5731 | 10.2179 | 61.38% | 5 | 2 | 66.83% | 0% | 0 | 0.036666 | 1 | 3.8294 | 0.14041 | Medium | Medium | High | 1581 | 1925 | 0.036666 | 22.7224 | 0.2546%
MORGAN HILL 2104XR018 | MORGAN HILL 2104 | SAN JOSE | 4.9492 | 19.6923 | 100% | 0 | 3 | 46.16% | 0% | 0 | 0.03658 | 1 | 3.0953 | 0.11323 | Medium | Medium | High | 1698 | 1926 | 0.03658 | 22.6857 | 0.2541%
FORT BRAGG A 11041316 | FORT BRAGG A 1104 | HUMBOLDT | 13.2223 | 12.9501 | 11.54% | 9 | 10 | 96.48% | 0% | 0 | 0.036376 | 1 | 3.1775 | 0.11559 | Medium | Medium | High | 1689 | 1927 | 0.036376 | 22.6491 | 0.2537%
OLETA 11021204 | OLETA 1102 | STOCKTON | 24.7673 | 19.1315 | 95.37% | 0 | 4 | 83.58% | 2.402% | 0 | 0.036314 | 1 | 2.4177 | 0.087794 | Medium | Medium | Medium | 1850 | 1928 | 0.036314 | 22.6128 | 0.2533%
CURTIS 170210940 | CURTIS 1702 | YOSEMITE | 9.3161 | 16.9626 | 82.71% | 2 | 8 | 88.08% | 0% | 0 | 0.036211 | 1 | 3.6749 | 0.13307 | Medium | Medium | High | 1615 | 1929 | 0.036211 | 22.5764 | 0.2529%
ROB ROY 210410960 | ROB ROY 2104 | CENTRAL COAST | 17.8204 | 13.6401 | 49.6% | 26 | 6 | 63.39% | 0% | 0 | 0.03619 | 1 | 3.3702 | 0.12197 | Medium | Medium | High | 1656 | 1930 | 0.03619 | 22.5402 | 0.2525%
FORT ROSS 1121CB | FORT ROSS 1121 | SONOMA | 13.6368 | 88.1189 | 22.5% | 13 | 2 | 100% | 0% | 0 | 0.036054 | 1 | 1.4046 | 0.050641 | Medium | Medium | Low | 2342 | 1931 | 0.036054 | 22.504 | 0.2521%
LUCERNE 1103CB | LUCERNE 1103 | HUMBOLDT | 4.1876 | 10 | 56.07% | 0 | 12 | 95.22% | 0% | 0 | 0.036043 | 1 | 2.7667 | 0.09972 | Medium | Medium | Medium | 1772 | 1932 | 0.036043 | 22.468 | 0.2517%
WYANDOTTE 110979932 | WYANDOTTE 1109 | NORTH VALLEY | 19.2875 | 10.6134 | 90.79% | 1 | 2 | 59.11% | 0% | 0 | 0.036019 | 1 | 2.7826 | 0.10022 | Medium | Medium | Medium | 1767 | 1933 | 0.036019 | 22.4319 | 0.2513%
CALISTOGA 1101CB | CALISTOGA 1101 | NORTH BAY | 2.6498 | 39.1806 | 43.07% | 2 | 0 | 27.62% | 49.7% | 0 | 0.036018 | 1 | 2.9421 | 0.10597 | Medium | Medium | Medium | 1732 | 1934 | 0.036018 | 22.3959 | 0.2509%
SAN MIGUEL 1106CB | SAN MIGUEL 1106 | LOS PADRES | 36.8861 | 40.1614 | 99.45% | 1 | 6 | 63.1% | 0% | 0 | 0.035909 | 1 | 0.91469 | 0.032845 | Medium | Medium | Low | 2703 | 1935 | 0.035909 | 22.3599 | 0.2505%
ELECTRA 110136816 | ELECTRA 1101 | STOCKTON | 16.3224 | 14.0317 | 85.78% | 2 | 8 | 100% | 0% | 0 | 0.035905 | 1 | 2.5788 | 0.092591 | Medium | Medium | Medium | 1813 | 1936 | 0.035905 | 22.324 | 0.2501%
SANTA YNEZ 1102Y18 | SANTA YNEZ 1102 | LOS PADRES | 4.6184 | 77.519 | 99.57% | 1 | 1 | 61.2% | 0% | 0 | 0.035874 | 1 | 2.1205 | 0.076069 | Medium | Medium | Low | 1974 | 1937 | 0.035874 | 22.2881 | 0.2497%
HOPLAND 1101768 | HOPLAND 1101 | HUMBOLDT | 16.1128 | 49.9055 | 90.85% | 1 | 4 | 80.79% | 0% | 0 | 0.03582 | 1 | 1.3347 | 0.047808 | Medium | Medium | Low | 2383 | 1938 | 0.03582 | 22.2522 | 0.2493%
CURTIS 1704CB | CURTIS 1704 | YOSEMITE | 13.7734 | 18.3001 | 79.09% | 1 | 5 | 96.53% | 0% | 0 | 0.035785 | 1 | 3.3627 | 0.12033 | Medium | Medium | High | 1664 | 1939 | 0.035785 | 22.2164 | 0.2489%
HIGHLANDS 1102CB | HIGHLANDS 1102 | HUMBOLDT | 7.3244 | 28.1149 | 80.17% | 1 | 6 | 100% | 0% | 0 | 0.035726 | 1 | 3.1836 | 0.11374 | Medium | Medium | High | 1694 | 1940 | 0.035726 | 22.1806 | 0.2485%
WYANDOTTE 110913052 | WYANDOTTE 1109 | NORTH VALLEY | 19.6896 | 23.3384 | 63.11% | 1 | 2 | 99.03% | 0% | 0 | 0.035725 | 1 | 3.319 | 0.11857 | Medium | Medium | High | 1669 | 1941 | 0.035725 | 22.1449 | 0.2481%
GARBERVILLE 11028189 | GARBERVILLE 1102 | HUMBOLDT | 1.0385 | 78.4457 | 65.35% | 2 | 1 | 100% | 0% | 0 | 0.035613 | 1 | 0.5748 | 0.02047 | Medium | Medium | Low | 2992 | 1942 | 0.035613 | 22.1092 | 0.2477%
AUBERRY 1101R2839 | AUBERRY 1101 | FRESNO | 12.6224 | 16.271 | 63.89% | 0 | 4 | 100% | 0% | 0 | 0.035608 | 1 | 1.8413 | 0.065564 | Medium | Medium | Low | 2093 | 1943 | 0.035608 | 22.0736 | 0.2473%
SAN LUIS OBISPO 1107V18 | SAN LUIS OBISPO 1107 | LOS PADRES | 3.3731 | 28.9632 | 4.194% | 1 | 0 | 84.27% | 30.63% | 0 | 0.035557 | 1 | 2.2292 | 0.079264 | Medium | Medium | Low | 1942 | 1944 | 0.035557 | 22.0379 | 0.2469%
PEORIA 17019250 | PEORIA 1701 | YOSEMITE | 8.3271 | 28.832 | 87.97% | 0 | 3 | 100% | 0% | 0 | 0.035488 | 1 | 1.35 | 0.047908 | Medium | Medium | Low | 2381 | 1945 | 0.035488 | 22.0024 | 0.2465%
DESCHUTES 11011652 | DESCHUTES 1101 | NORTH VALLEY | 22.782 | 45.1857 | 96.26% | 0 | 4 | 93.2% | 0% | 0 | 0.035474 | 1 | 1.8172 | 0.064462 | Medium | Medium | Low | 2110 | 1946 | 0.035474 | 21.9669 | 0.2461%
BIG RIVER 11015065 | BIG RIVER 1101 | HUMBOLDT | 2.2025 | 10 | 42.78% | 5 | 11 | 100% | 0% | 0 | 0.035469 | 1 | 2.8348 | 0.10055 | Medium | Medium | Medium | 1765 | 1947 | 0.035469 | 21.9314 | 0.2457%
MONTICELLO 11014360 | MONTICELLO 1101 | NORTH BAY | 7.4298 | 66.0263 | 57.84% | 4 | 3 | 80.69% | 0% | 0 | 0.035448 | 1 | 2.8213 | 0.10001 | Medium | Medium | Medium | 1769 | 1948 | 0.035448 | 21.896 | 0.2453%
BEAR VALLEY 21059570 | BEAR VALLEY 2105 | YOSEMITE | 8.0469 | 57.8177 | 84.85% | 0 | 1 | 100% | 0% | 0 | 0.035385 | 1 | 0.86453 | 0.030591 | Medium | Medium | Low | 2755 | 1949 | 0.035385 | 21.8605 | 0.2449%
SAND CREEK 110397354 | SAND CREEK 1103 | FRESNO | 8.1104 | 10 | 100% | 0 | 1 | 80.11% | 0% | 0 | 0.035362 | 1 | 1.7829 | 0.063047 | Medium | Medium | Low | 2128 | 1950 | 0.035362 | 21.8251 | 0.2445%
PALO SECO 0401CB | PALO SECO 0401 | EAST BAY | 4.7078 | 10 | 0% | 4 | 1 | 100% | 18.75% | 0 | 0.035354 | 1 | 4.4285 | 0.15657 | Medium | Medium | High | 1536 | 1951 | 0.035354 | 21.7898 | 0.2441%
RED BLUFF 11041566 | RED BLUFF 1104 | NORTH VALLEY | 11.3669 | 45.5787 | 76.5% | 0 | 1 | 74.23% | 0% | 0 | 0.03504 | 1 | 1.3025 | 0.045641 | Medium | Medium | Low | 2429 | 1952 | 0.03504 | 21.7544 | 0.2437%
CRESCENT MILLS 21012562 | CRESCENT MILLS 2101 | NORTH VALLEY | 17.3839 | 76.7012 | 88.81% | 4 | 1 | 50.76% | 0% | 0 | 0.034993 | 1 | 1.5371 | 0.053789 | Medium | Medium | Low | 2273 | 1953 | 0.034993 | 21.7194 | 0.2433%
TEJON 11023751 | TEJON 1102 | KERN | 20.1546 | 14.4086 | 57.09% | 0 | 4 | 78.15% | 0% | 0 | 0.034903 | 1 | 0.99037 | 0.034567 | Medium | Medium | Low | 2662 | 1954 | 0.034903 | 21.6844 | 0.2429%
WILDWOOD 11011454 | WILDWOOD 1101 | NORTH VALLEY | 7.7462 | 36.802 | 100% | 0 | 1 | 100% | 0% | 0 | 0.034751 | 1 | 0.83154 | 0.028897 | Medium | Medium | Low | 2800 | 1955 | 0.034751 | 21.6495 | 0.2425%
ELK CREEK 110193504 | ELK CREEK 1101 | NORTH VALLEY | 2.2601 | 54.3949 | 100% | 0 | 0 | 90.07% | 0% | 0 | 0.034745 | 1 | 1.6101 | 0.055942 | Medium | Medium | Low | 2246 | 1956 | 0.034745 | 21.6147 | 0.2421%
SILVERADO 2102CB | SILVERADO 2102 | NORTH BAY | 0.45935 | 10 | 0% | 0 | 0 | 26.76% | 100% | 0 | 0.034737 | 1 | 3.7165 | 0.1291 | Medium | Medium | High | 1627 | 1957 | 0.034737 | 21.58 | 0.2418%
DUNBAR 1101CB | DUNBAR 1101 | SONOMA | 2.1801 | 23.6947 | 93.6% | 0 | 2 | 14.87% | 59.74% | 0 | 0.034709 | 1 | 3.2741 | 0.11364 | Medium | Medium | High | 1695 | 1958 | 0.034709 | 21.5452 | 0.2414%
HIGHLANDS 1103568 | HIGHLANDS 1103 | HUMBOLDT | 7.7314 | 14.5235 | 84.3% | 1 | 2 | 84.45% | 0% | 0 | 0.034657 | 1 | 2.9157 | 0.10105 | Medium | Medium | Medium | 1761 | 1959 | 0.034657 | 21.5105 | 0.241%
VACAVILLE 11046542 | VACAVILLE 1104 | SACRAMENTO | 14.768 | 37.9322 | 37.99% | 1 | 5 | 100% | 0% | 0 | 0.034546 | 1 | 2.9717 | 0.10266 | Medium | Medium | Medium | 1749 | 1960 | 0.034546 | 21.4759 | 0.2406%
HIGGINS 1104533648 | HIGGINS 1104 | SIERRA | 6.7529 | 10 | 96.99% | 2 | 3 | 100% | 0% | 0 | 0.034544 | 1 | 3.2267 | 0.11146 | Medium | Medium | High | 1704 | 1961 | 0.034544 | 21.4413 | 0.2402%
HOLLISTER 21054048 | HOLLISTER 2105 | CENTRAL COAST | 15.0102 | 85.5727 | 83.97% | 1 | 0 | 53.3% | 0% | 0 | 0.034508 | 1 | 1.9904 | 0.068686 | Medium | Medium | Low | 2056 | 1962 | 0.034508 | 21.4068 | 0.2398%
OTTER 110298036 | OTTER 1102 | CENTRAL COAST | 9.353 | 32.3159 | 7.526% | 0 | 13 | 100% | 0% | 0 | 0.034494 | 1 | 1.2921 | 0.04457 | Medium | Medium | Low | 2446 | 1963 | 0.034494 | 21.3723 | 0.2394%
RACETRACK 170311270 | RACETRACK 1703 | YOSEMITE | 12.3885 | 27.441 | 56.51% | 3 | 6 | 100% | 0% | 0 | 0.03438 | 1 | 3.0786 | 0.10584 | Medium | Medium | High | 1733 | 1964 | 0.03438 | 21.3378 | 0.239%
HIGHLANDS 1103CB | HIGHLANDS 1103 | HUMBOLDT | 10.5045 | 18.0278 | 65.06% | 2 | 6 | 87.07% | 0% | 0 | 0.034275 | 1 | 3.1863 | 0.10921 | Medium | Medium | High | 1714 | 1965 | 0.034275 | 21.3034 | 0.2387%
ELK CREEK 11012004 | ELK CREEK 1101 | NORTH VALLEY | 14.9707 | 82.0149 | 100% | 0 | 1 | 27.7% | 0% | 0 | 0.034268 | 1 | 0.68104 | 0.023338 | Medium | Medium | Low | 2928 | 1966 | 0.034268 | 21.2691 | 0.2383%
FRUITLAND 114137410 | FRUITLAND 1141 | HUMBOLDT | 3.8197 | 75.1023 | 57.88% | 10 | 0 | 69.23% | 0% | 0 | 0.034236 | 1 | 1.2527 | 0.042886 | Medium | Medium | Low | 2479 | 1967 | 0.034236 | 21.2349 | 0.2379%
FOOTHILL 1102CB | FOOTHILL 1102 | LOS PADRES | 8.141 | 51.8091 | 56.43% | 3 | 6 | 82.95% | 0% | 0 | 0.034219 | 1 | 2.9019 | 0.099302 | Medium | Medium | Medium | 1777 | 1968 | 0.034219 | 21.2006 | 0.2375%
MARTELL 11033152 | MARTELL 1103 | STOCKTON | 16.8696 | 31.4572 | 87.03% | 0 | 1 | 99.4% | 0% | 0 | 0.034215 | 1 | 2.4031 | 0.082223 | Medium | Medium | Medium | 1913 | 1969 | 0.034215 | 21.1664 | 0.2371%
IONE 1101L3141 | IONE 1101 | STOCKTON | 13.6703 | 41.1561 | 100% | 0 | 0 | 97.4% | 0% | 0 | 0.034177 | 1 | 2.7017 | 0.092334 | Medium | Medium | Medium | 1815 | 1970 | 0.034177 | 21.1322 | 0.2367%
MONTICELLO 11011589 | MONTICELLO 1101 | NORTH BAY | 4.3101 | 10 | 98.73% | 0 | 3 | 100% | 0% | 0 | 0.034141 | 1 | 2.4603 | 0.083998 | Medium | Medium | Medium | 1886 | 1971 | 0.034141 | 21.098 | 0.2364%
CHOLAME 2102X06 | CHOLAME 2102 | LOS PADRES | 33.5233 | 47.8201 | 99.99% | 1 | 7 | 63.4% | 0% | 0 | 0.034127 | 1 | 0.89797 | 0.030645 | Medium | Medium | Low | 2753 | 1972 | 0.034127 | 21.0639 | 0.236%
WOODACRE 11021280 | WOODACRE 1102 | NORTH BAY | 10.5964 | 14.7487 | 31.13% | 2 | 14 | 100% | 0% | 0 | 0.034114 | 1 | 4.0304 | 0.1375 | Medium | Medium | High | 1596 | 1973 | 0.034114 | 21.0297 | 0.2356%
RACETRACK 17039190 | RACETRACK 1703 | YOSEMITE | 8.9165 | 23.5588 | 27.68% | 2 | 6 | 100% | 0% | 0 | 0.034029 | 1 | 3.3879 | 0.11529 | Medium | Medium | High | 1690 | 1974 | 0.034029 | 20.9956 | 0.2352%
FRENCH GULCH 1102CB | FRENCH GULCH 1102 | NORTH VALLEY | 1.6951 | 33.4949 | 100% | 0 | 1 | 100% | 0% | 0 | 0.034 | 1 | 0.94898 | 0.032265 | Medium | Medium | Low | 2719 | 1975 | 0.034 | 20.9616 | 0.2348%
JESSUP 11019752 | JESSUP 1101 | NORTH VALLEY | 3.8979 | 33.5364 | 99.93% | 0 | 1 | 100% | 0% | 0 | 0.033991 | 1 | 2.4213 | 0.082304 | Medium | Medium | Medium | 1912 | 1976 | 0.033991 | 20.9276 | 0.2344%
MOUNTAIN QUARRIES 210151584 | MOUNTAIN QUARRIES 2101 | SIERRA | 21.6351 | 34.2949 | 99.29% | 0 | 1 | 100% | 0% | 0 | 0.033987 | 1 | 2.2566 | 0.076695 | Medium | Medium | Medium | 1968 | 1977 | 0.033987 | 20.8936 | 0.2341%
MERCED FALLS 110238748 | MERCED FALLS 1102 | YOSEMITE | 15.288 | 16.9529 | 100% | 0 | 0 | 100% | 0% | 0 | 0.033981 | 1 | 0.19224 | 0.0065325 | Medium | Medium | Low | 3164 | 1978 | 0.033981 | 20.8596 | 0.2337%
FROGTOWN 170211212 | FROGTOWN 1702 | STOCKTON | 22.4074 | 27.4478 | 70.17% | 2 | 7 | 100% | 0% | 0 | 0.033949 | 1 | 1.6518 | 0.056076 | Medium | Medium | Low | 2242 | 1979 | 0.033949 | 20.8256 | 0.2333%
BANGOR 11011806 | BANGOR 1101 | NORTH VALLEY | 8.946 | 12.2309 | 77.62% | 0 | 5 | 97.6% | 0% | 0 | 0.033897 | 1 | 2.4358 | 0.082565 | Medium | Medium | Medium | 1906 | 1980 | 0.033897 | 20.7917 | 0.2329%
WILLOW CREEK 110191926 | WILLOW CREEK 1101 | HUMBOLDT | 5.6211 | 81.2548 | 100% | 2 | 0 | 52.92% | 0% | 0 | 0.033802 | 1 | 1.1327 | 0.038287 | Medium | Medium | Low | 2578 | 1981 | 0.033802 | 20.7578 | 0.2325%
LOS GATOS 1108LB86 | LOS GATOS 1108 | DE ANZA | 4.2689 | 10 | 37.07% | 3 | 5 | 80.57% | 12.91% | 0 | 0.033788 | 1 | 3.8848 | 0.13126 | Medium | Medium | High | 1623 | 1982 | 0.033788 | 20.724 | 0.2322%
UKIAH 11143606 | UKIAH 1114 | HUMBOLDT | 9.6068 | 79.0327 | 97.2% | 3 | 5 | 58.23% | 0% | 0 | 0.033786 | 1 | 2.6108 | 0.088208 | Medium | Medium | Medium | 1845 | 1983 | 0.033786 | 20.6902 | 0.2318%
OILFIELDS 11032757 | OILFIELDS 1103 | CENTRAL COAST | 2.6282 | 37.5918 | 90.66% | 0 | 3 | 100% | 0% | 0 | 0.033768 | 1 | 2.1416 | 0.072319 | Medium | Medium | Low | 2013 | 1984 | 0.033768 | 20.6564 | 0.2314%
APPLE HILL 210212025 | APPLE HILL 2102 | SIERRA | 9.1227 | 10 | 100% | 3 | 0 | 100% | 0% | 0 | 0.033724 | 1 | 1.8915 | 0.063789 | Medium | Medium | Low | 2118 | 1985 | 0.033724 | 20.6227 | 0.231%
BEAR VALLEY 21054609 | BEAR VALLEY 2105 | YOSEMITE | 4.5488 | 18.0167 | 100% | 1 | 5 | 100% | 0% | 0 | 0.033715 | 1 | 1.728 | 0.058259 | Medium | Medium | Low | 2206 | 1986 | 0.033715 | 20.5889 | 0.2307%
WYANDOTTE 110796390 | WYANDOTTE 1107 | NORTH VALLEY | 8.1841 | 10 | 71.02% | 4 | 1 | 80.42% | 0% | 0 | 0.033709 | 1 | 3.6617 | 0.12343 | Medium | Medium | High | 1649 | 1987 | 0.033709 | 20.5552 | 0.2303%
CAROLANDS 04049024 | CAROLANDS 0404 | PENINSULA | 3.5964 | 10 | 16.66% | 1 | 9 | 99.05% | 0% | 0 | 0.033705 | 1 | 3.5061 | 0.11817 | Medium | Medium | High | 1673 | 1988 | 0.033705 | 20.5215 | 0.2299%
COARSEGOLD 21046210 | COARSEGOLD 2104 | YOSEMITE | 10.6712 | 44.0621 | 48.52% | 0 | 11 | 100% | 0% | 0 | 0.033703 | 1 | 1.9204 | 0.064723 | Medium | Medium | Low | 2102 | 1989 | 0.033703 | 20.4878 | 0.2295%
ELECTRA 1101L3849 | ELECTRA 1101 | STOCKTON | 5.7652 | 16.1295 | 95.19% | 1 | 1 | 100% | 0% | 0 | 0.033619 | 1 | 1.9842 | 0.066706 | Medium | Medium | Low | 2081 | 1990 | 0.033619 | 20.4541 | 0.2291%
HIGGINS 11094189 | HIGGINS 1109 | SIERRA | 3.326 | 25.4516 | 99.91% | 0 | 3 | 100% | 0% | 0 | 0.033551 | 1 | 2.4095 | 0.080842 | Medium | Medium | Medium | 1928 | 1991 | 0.033551 | 20.4205 | 0.2288%
KONOCTI 1102716 | KONOCTI 1102 | HUMBOLDT | 12.6002 | 59.2136 | 49.34% | 2 | 6 | 73.82% | 22.04% | 1 | 0.033546 | 1 | 2.6664 | 0.089449 | Medium | Medium | Medium | 1837 | 1992 | 0.033546 | 20.3869 | 0.2284%
REDBUD 1101CB | REDBUD 1101 | HUMBOLDT | 4.9191 | 32.5631 | 40.27% | 2 | 12 | 69.43% | 0% | 0 | 0.033542 | 1 | 2.6297 | 0.088206 | Medium | Medium | Medium | 1846 | 1993 | 0.033542 | 20.3534 | 0.228%
PIT NO 3 21011360 | PIT NO 3 2101 | NORTH VALLEY | 21.8208 | 46.6037 | 72.84% | 2 | 7 | 96.78% | 0% | 0 | 0.033534 | 1 | 0.24766 | 0.0083049 | Medium | Medium | Low | 3158 | 1994 | 0.033534 | 20.3198 | 0.2276%
PIT NO 5 11011660 | PIT NO 5 1101 | NORTH VALLEY | 4.8851 | 10 | 71.19% | 4 | 4 | 100% | 0% | 0 | 0.033496 | 1 | 0.50439 | 0.016895 | Medium | Medium | Low | 3066 | 1995 | 0.033496 | 20.2863 | 0.2273%
UPPER LAKE 110175370 | UPPER LAKE 1101 | HUMBOLDT | 11.9492 | 35.1291 | 70.43% | 2 | 8 | 80.82% | 6.214% | 1 | 0.033449 | 1 | 1.3516 | 0.04521 | Medium | Medium | Low | 2435 | 1996 | 0.033449 | 20.2528 | 0.2269%
SAND CREEK 1103CB | SAND CREEK 1103 | FRESNO | 12.8175 | 20.9724 | 70.85% | 0 | 3 | 100% | 0% | 0 | 0.033442 | 1 | 2.1429 | 0.071662 | Medium | Medium | Low | 2024 | 1997 | 0.033442 | 20.2194 | 0.2265%
PLACERVILLE 210623190 | PLACERVILLE 2106 | SIERRA | 3.6751 | 24.4138 | 66.27% | 0 | 8 | 100% | 2.399% | 0 | 0.033321 | 1 | 2.6363 | 0.087845 | Medium | Medium | Medium | 1849 | 1998 | 0.033321 | 20.1859 | 0.2261%
MARIPOSA 210190180 | MARIPOSA 2101 | YOSEMITE | 4.7841 | 52.2474 | 63.07% | 0 | 2 | 100% | 0% | 0 | 0.033288 | 1 | 0.62236 | 0.020717 | Medium | Medium | Low | 2986 | 1999 | 0.033288 | 20.1526 | 0.2258%
AUBERRY 1101R322 | AUBERRY 1101 | FRESNO | 7.483 | 34.3076 | 99.18% | 0 | 0 | 100% | 0% | 0 | 0.033278 | 1 | 1.9251 | 0.064062 | Medium | Medium | Low | 2114 | 2000 | 0.033278 | 20.1193 | 0.2254%
TEMPLETON 2113A20 | TEMPLETON 2113 | LOS PADRES | 7.0532 | 26.1549 | 66.41% | 2 | 0 | 89.65% | 0% | 0 | 0.033191 | 1 | 2.6768 | 0.088847 | Medium | Medium | Medium | 1838 | 2001 | 0.033191 | 20.086 | 0.225%
PEORIA 170587222 | PEORIA 1705 | YOSEMITE | 5.2686 | 10 | 76.37% | 0 | 4 | 100% | 0% | 0 | 0.03317 | 1 | 2.9599 | 0.098179 | Medium | Medium | Medium | 1782 | 2002 | 0.03317 | 20.0528 | 0.2246%
PLACERVILLE 1111CB | PLACERVILLE 1111 | SIERRA | 5.5179 | 10 | 61.74% | 2 | 10 | 83.46% | 0% | 0 | 0.033153 | 1 | 3.064 | 0.10158 | Medium | Medium | Medium | 1756 | 2003 | 0.033153 | 20.0197 | 0.2243%
BIG RIVER 110169032 | BIG RIVER 1101 | HUMBOLDT | 8.4667 | 31.9768 | 17.96% | 7 | 9 | 100% | 0% | 0 | 0.033152 | 1 | 2.3622 | 0.07831 | Medium | Medium | Medium | 1949 | 2004 | 0.033152 | 19.9865 | 0.2239%
RISING RIVER 11019032 | RISING RIVER 1101 | NORTH VALLEY | 23.4901 | 16.8815 | 99.94% | 5 | 2 | 100% | 0% | 0 | 0.033124 | 1 | 0.53301 | 0.017655 | Medium | Medium | Low | 3049 | 2005 | 0.033124 | 19.9534 | 0.2235%
ANTLER 11011520 | ANTLER 1101 | NORTH VALLEY | 8.8735 | 30.8958 | 71.85% | 2 | 4 | 100% | 0% | 0 | 0.033121 | 1 | 1.188 | 0.039347 | Medium | Medium | Low | 2552 | 2006 | 0.033121 | 19.9202 | 0.2232%
TIVY VALLEY 11077380 | TIVY VALLEY 1107 | FRESNO | 12.8078 | 20.0234 | 100% | 1 | 4 | 45.52% | 0% | 0 | 0.033102 | 1 | 2.1686 | 0.071783 | Medium | Medium | Low | 2023 | 2007 | 0.033102 | 19.8871 | 0.2228%
PETALUMA C 1108632 | PETALUMA C 1108 | SONOMA | 14.7325 | 83.7221 | 19.94% | 0 | 2 | 100% | 0% | 0 | 0.033063 | 1 | 1.6482 | 0.054496 | Medium | Medium | Low | 2266 | 2008 | 0.033063 | 19.854 | 0.2224%
SAN RAFAEL 110991742 | SAN RAFAEL 1109 | NORTH BAY | 5.7363 | 10 | 72.58% | 2 | 1 | 66.36% | 0% | 0 | 0.033036 | 1 | 3.657 | 0.12081 | Medium | Medium | High | 1658 | 2009 | 0.033036 | 19.821 | 0.2221%
STANISLAUS 1701CB | STANISLAUS 1701 | YOSEMITE | 6.8255 | 50.7734 | 38.45% | 1 | 4 | 100% | 0.8907% | 0 | 0.032969 | 1 | 3.3185 | 0.10941 | Medium | Medium | High | 1713 | 2010 | 0.032969 | 19.7879 | 0.2217%
WYANDOTTE 11031504 | WYANDOTTE 1103 | NORTH VALLEY | 11.3639 | 10 | 55.8% | 3 | 8 | 77.24% | 0% | 0 | 0.032944 | 1 | 3.7481 | 0.12348 | Medium | Medium | High | 1648 | 2011 | 0.032944 | 19.7549 | 0.2213%
OREGON TRAIL 11021382 | OREGON TRAIL 1102 | NORTH VALLEY | 5.4732 | 13.8429 | 96.06% | 0 | 1 | 100% | 0% | 0 | 0.03292 | 1 | 2.141 | 0.070481 | Medium | Medium | Low | 2037 | 2012 | 0.03292 | 19.722 | 0.2209%
POINT MORETTI 11015104 | POINT MORETTI 1101 | CENTRAL COAST | 1.8713 | 40.903 | 21.17% | 4 | 0 | 100% | 0% | 0 | 0.032915 | 1 | 2.5532 | 0.084038 | Medium | Medium | Medium | 1885 | 2013 | 0.032915 | 19.6891 | 0.2206%
PLACERVILLE 1110CB | PLACERVILLE 1110 | SIERRA | 11.9057 | 10.8465 | 38.55% | 4 | 14 | 94.9% | 13.5% | 1 | 0.032906 | 1 | 2.7626 | 0.090907 | Medium | Medium | Medium | 1825 | 2014 | 0.032906 | 19.6562 | 0.2202%
KERCKHOFF 1101CB | KERCKHOFF 1101 | YOSEMITE | 16.9469 | 19.3199 | 39.66% | 0 | 15 | 100% | 0% | 0 | 0.032903 | 1 | 2.2156 | 0.072899 | Medium | Medium | Low | 2007 | 2015 | 0.032903 | 19.6233 | 0.2198%
CALAVERAS CEMENT 110111188 | CALAVERAS CEMENT 1101 | STOCKTON | 6.2741 | 29.7373 | 82.62% | 0 | 1 | 100% | 0% | 0 | 0.032851 | 1 | 1.9023 | 0.062494 | Medium | Medium | Low | 2136 | 2016 | 0.032851 | 19.5904 | 0.2195%
HALF MOON BAY 11022032 | HALF MOON BAY 1102 | PENINSULA | 3.27 | 24.2985 | 27.09% | 1 | 0 | 29.71% | 73.93% | 0 | 0.032761 | 1 | 4.2337 | 0.1387 | Medium | Medium | High | 1589 | 2017 | 0.032761 | 19.5575 | 0.2191%
BEAR VALLEY 21014160 | BEAR VALLEY 2101 | YOSEMITE | 22.75 | 19.66 | 91.43% | 0 | 7 | 99.99% | 0% | 0 | 0.032723 | 1 | 2.1443 | 0.070169 | Medium | Medium | Low | 2043 | 2018 | 0.032723 | 19.5247 | 0.2187%
HALSEY 1102CB | HALSEY 1102 | SIERRA | 8.0128 | 10 | 41.48% | 9 | 5 | 100% | 0% | 0 | 0.032715 | 1 | 2.1959 | 0.071838 | Medium | Medium | Low | 2022 | 2019 | 0.032715 | 19.492 | 0.2184%
SMARTVILLE 1101CB | SMARTVILLE 1101 | SIERRA | 15.8868 | 12.1904 | 82.07% | 1 | 6 | 100% | 0% | 0 | 0.032648 | 1 | 2.4063 | 0.078562 | Medium | Medium | Medium | 1947 | 2020 | 0.032648 | 19.4593 | 0.218%
RINCON 1102CB | RINCON 1102 | SONOMA | 3.4953 | 21.5241 | 28.33% | 2 | 6 | 98.07% | 7.215% | 1 | 0.032618 | 1 | 3.2363 | 0.10556 | Medium | Medium | High | 1736 | 2021 | 0.032618 | 19.4267 | 0.2176%
HIGGINS 1104842642 | HIGGINS 1104 | SIERRA | 5.4882 | 10 | 100% | 3 | 1 | 94.43% | 0% | 0 | 0.032606 | 1 | 3.4791 | 0.11344 | Medium | Medium | High | 1697 | 2022 | 0.032606 | 19.394 | 0.2173%
HOPLAND 110194006 | HOPLAND 1101 | HUMBOLDT | 13.3558 | 51.6995 | 99.02% | 0 | 1 | 84.05% | 0% | 0 | 0.032603 | 1 | 1.676 | 0.054643 | Medium | Medium | Low | 2264 | 2023 | 0.032603 | 19.3614 | 0.2169%
CLARK ROAD 110292622 | CLARK ROAD 1102 | NORTH VALLEY | 30.8948 | 14.2994 | 87.09% | 2 | 9 | 100% | 0% | 0 | 0.032599 | 1 | 2.0512 | 0.066867 | Medium | Medium | Low | 2076 | 2024 | 0.032599 | 19.3288 | 0.2165%
PLACERVILLE 111219742 | PLACERVILLE 1112 | SIERRA | 7.3806 | 10 | 51.29% | 2 | 12 | 99.39% | 0% | 0 | 0.032573 | 1 | 2.6661 | 0.086842 | Medium | Medium | Medium | 1858 | 2025 | 0.032573 | 19.2962 | 0.2162%
BIG MEADOWS 21012260 | BIG MEADOWS 2101 | NORTH VALLEY | 17.1948 | 71.2696 | 55.9% | 4 | 0 | 76.22% | 0% | 0 | 0.032561 | 1 | 2.4871 | 0.080983 | Medium | Medium | Medium | 1926 | 2026 | 0.032561 | 19.2637 | 0.2158%
DESCHUTES 11011380 | DESCHUTES 1101 | NORTH VALLEY | 17.936 | 29.5967 | 86.99% | 0 | 4 | 75.95% | 0% | 0 | 0.032554 | 1 | 2.2953 | 0.07472 | Medium | Medium | Medium | 1989 | 2027 | 0.032554 | 19.2311 | 0.2154%
WYANDOTTE 11071026 | WYANDOTTE 1107 | NORTH VALLEY | 21.2978 | 26.1479 | 94.57% | 0 | 2 | 76.21% | 0% | 0 | 0.032543 | 1 | 2.3229 | 0.075594 | Medium | Medium | Medium | 1978 | 2028 | 0.032543 | 19.1985 | 0.2151%
WYANDOTTE 110366146 | WYANDOTTE 1103 | NORTH VALLEY | 0.1568 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.032454 | 1 | 3.7133 | 0.12051 | Medium | Medium | High | 1662 | 2029 | 0.032454 | 19.166 | 0.2147%
HIGGINS 1107746082 | HIGGINS 1107 | SIERRA | 0.84187 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.032454 | 1 | 3.3644 | 0.10919 | Medium | Medium | High | 1715 | 2029 | 0.032454 | 19.1336 | 0.2144%
CURTIS 17029111 | CURTIS 1702 | YOSEMITE | 5.6752 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.032454 | 1 | 3.3314 | 0.10812 | Medium | Medium | High | 1721 | 2029 | 0.032454 | 19.1011 | 0.214%
RED BLUFF 110585632 | RED BLUFF 1105 | NORTH VALLEY | 13.6331 | 10 | 81.59% | 1 | 4 | 91.86% | 0% | 0 | 0.032365 | 1 | 2.0302 | 0.065709 | Medium | Medium | Low | 2092 | 2032 | 0.032365 | 19.0686 | 0.2136%
TAR FLAT 04023144 | TAR FLAT 0402 | YOSEMITE | 4.9761 | 11.3882 | 27.07% | 0 | 3 | 96.83% | 26.03% | 1 | 0.032346 | 1 | 2.8761 | 0.093031 | Medium | Medium | Medium | 1811 | 2033 | 0.032346 | 19.0363 | 0.2133%
TEMPLETON 2113A08 | TEMPLETON 2113 | LOS PADRES | 9.9198 | 65.213 | 45.79% | 1 | 2 | 40.4% | 37.28% | 0 | 0.032324 | 1 | 1.6527 | 0.053421 | Medium | Medium | Low | 2282 | 2034 | 0.032324 | 19.0039 | 0.2129%
ARCATA 11224218 | ARCATA 1122 | HUMBOLDT | 4.9191 | 35.3774 | 67.92% | 2 | 3 | 99.74% | 0% | 0 | 0.032319 | 1 | 2.7359 | 0.088422 | Medium | Medium | Medium | 1842 | 2035 | 0.032319 | 18.9716 | 0.2125%
TEMPLETON 2111R86 | TEMPLETON 2111 | LOS PADRES | 10.174 | 35.046 | 79.62% | 2 | 6 | 70.64% | 0% | 0 | 0.032293 | 1 | 2.4827 | 0.080172 | Medium | Medium | Medium | 1932 | 2036 | 0.032293 | 18.9393 | 0.2122%
WOODSIDE 110411555 | WOODSIDE 1104 | PENINSULA | 0.85806 | 10 | 96.59% | 0 | 1 | 100% | 0% | 0 | 0.032229 | 1 | 5.0953 | 0.16422 | Medium | Medium | High | 1512 | 2037 | 0.032229 | 18.907 | 0.2118%
HIGGINS 11044281 | HIGGINS 1104 | SIERRA | 13.3205 | 11.5983 | 77.05% | 5 | 5 | 100% | 0% | 0 | 0.032224 | 1 | 2.9395 | 0.094722 | Medium | Medium | Medium | 1800 | 2038 | 0.032224 | 18.8748 | 0.2115%
BRENTWOOD 21056512 | BRENTWOOD 2105 | DIABLO | 0.65133 | 10 | 96.38% | 0 | 1 | 100% | 0% | 0 | 0.032177 | 1 | 2.6202 | 0.084309 | Medium | Medium | Medium | 1882 | 2039 | 0.032177 | 18.8425 | 0.2111%
BEAR VALLEY 210190550 | BEAR VALLEY 2101 | YOSEMITE | 8.0073 | 10 | 99.83% | 0 | 6 | 100% | 0% | 0 | 0.032169 | 1 | 0.53108 | 0.017084 | Medium | Medium | Low | 3062 | 2040 | 0.032169 | 18.8104 | 0.2107%
PIT NO 1 11013312 | PIT NO 1 1101 | NORTH VALLEY | 7.449 | 11.3541 | 100% | 0 | 1 | 82.66% | 0% | 0 | 0.032143 | 1 | 1.5906 | 0.051127 | Medium | Medium | Low | 2329 | 2041 | 0.032143 | 18.7782 | 0.2104%
SUMMIT 1102CB | SUMMIT 1102 | SIERRA | 1.0104 | 10 | 73.24% | 1 | 3 | 100% | 0% | 0 | 0.032108 | 1 | 0.63651 | 0.020437 | Medium | Medium | Low | 2994 | 2042 | 0.032108 | 18.7461 | 0.21%
SARATOGA 1107LC26 | SARATOGA 1107 | DE ANZA | 5.6494 | 10 | 35.72% | 5 | 4 | 100% | 14.43% | 1 | 0.032092 | 1 | 3.6662 | 0.11766 | Medium | Medium | High | 1677 | 2043 | 0.032092 | 18.7139 | 0.2096%
ELK 11018779 | ELK 1101 | HUMBOLDT | 4.2672 | 21.5207 | 21.57% | 6 | 10 | 100% | 0% | 0 | 0.032081 | 1 | 1.4446 | 0.046343 | Medium | Medium | Low | 2414 | 2044 | 0.032081 | 18.6819 | 0.2093%
LAKEVILLE 110287432 | LAKEVILLE 1102 | SONOMA | 8.9371 | 82.9673 | 68.1% | 1 | 4 | 65.45% | 0% | 0 | 0.032044 | 1 | 2.7702 | 0.088771 | Medium | Medium | Medium | 1839 | 2045 | 0.032044 | 18.6498 | 0.2089%
MARIPOSA 21018030 | MARIPOSA 2101 | YOSEMITE | 18.88 | 28.5381 | 67.58% | 1 | 11 | 100% | 1.019% | 0 | 0.032029 | 1 | 2.3021 | 0.073734 | Medium | Medium | Medium | 2000 | 2046 | 0.032029 | 18.6177 | 0.2086%
OAKLAND K 1104CR210 | OAKLAND K 1104 | EAST BAY | 2.8215 | 10 | 11.97% | 1 | 0 | 100% | 42.91% | 0 | 0.032016 | 1 | 4.383 | 0.14033 | Medium | Medium | High | 1583 | 2047 | 0.032016 | 18.5857 | 0.2082%
NARROWS 2101CB | NARROWS 2101 | SIERRA | 15.6172 | 42.314 | 50.34% | 2 | 7 | 100% | 0% | 0 | 0.031975 | 1 | 1.9092 | 0.061047 | Medium | Medium | Low | 2166 | 2048 | 0.031975 | 18.5537 | 0.2079%
HAMILTON BRANCH 110187784 | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.4473 | 18.1172 | 99.8% | 0 | 3 | 100% | 0% | 0 | 0.031933 | 1 | 3.7387 | 0.11939 | Medium | Medium | High | 1666 | 2049 | 0.031933 | 18.5217 | 0.2075%
MERCED FALLS 11029460 | MERCED FALLS 1102 | YOSEMITE | 8.5158 | 30.9683 | 53.31% | 0 | 0 | 95.4% | 0% | 0 | 0.031807 | 1 | 0.30868 | 0.009818 | Medium | Medium | Low | 3147 | 2050 | 0.031807 | 18.4898 | 0.2071%
BRUNSWICK 1103CB | BRUNSWICK 1103 | SIERRA | 6.0294 | 52.8154 | 37.6% | 9 | 3 | 59.53% | 34.21% | 0 | 0.031778 | 1 | 3.2375 | 0.10288 | Medium | Medium | High | 1747 | 2051 | 0.031778 | 18.458 | 0.2068%
MARTELL 1102CB | MARTELL 1102 | STOCKTON | 6.4004 | 24.1429 | 66.43% | 0 | 4 | 94.03% | 0% | 0 | 0.031753 | 1 | 2.5224 | 0.080095 | Medium | Medium | Medium | 1934 | 2052 | 0.031753 | 18.4262 | 0.2064%
BURNEY 11011358 | BURNEY 1101 | NORTH VALLEY | 7.0165 | 60.5885 | 76.98% | 1 | 3 | 74.4% | 0% | 0 | 0.0317 | 1 | 1.9333 | 0.061286 | Medium | Medium | Low | 2165 | 2053 | 0.0317 | 18.3944 | 0.2061%
CLAY 11031230 | CLAY 1103 | STOCKTON | 15.7057 | 29.0509 | 99.85% | 0 | 2 | 80.49% | 0% | 0 | 0.031696 | 1 | 2.4895 | 0.078906 | Medium | Medium | Medium | 1945 | 2054 | 0.031696 | 18.3627 | 0.2057%
CURTIS 17046060 | CURTIS 1704 | YOSEMITE | 4.0637 | 23.6511 | 61.76% | 0 | 3 | 100% | 0% | 0 | 0.031658 | 1 | 3.0016 | 0.095023 | Medium | Medium | Medium | 1799 | 2055 | 0.031658 | 18.331 | 0.2054%
KONOCTI 1108950 | KONOCTI 1108 | HUMBOLDT | 6.231 | 17.4671 | 73.5% | 1 | 1 | 84.02% | 0% | 0 | 0.031636 | 1 | 2.7401 | 0.086689 | Medium | Medium | Medium | 1860 | 2056 | 0.031636 | 18.2994 | 0.205%
OTTER 110263868 | OTTER 1102 | CENTRAL COAST | 15.8742 | 30.1739 | 15.67% | 12 | 5 | 100% | 0% | 0 | 0.031617 | 1 | 1.3086 | 0.041374 | Medium | Medium | Low | 2510 | 2057 | 0.031617 | 18.2677 | 0.2047%
FORT ROSS 112137326 | FORT ROSS 1121 | SONOMA | 5.1708 | 13.0882 | 4.203% | 4 | 1 | 100% | 0% | 0 | 0.031597 | 1 | 1.3203 | 0.04172 | Medium | Medium | Low | 2502 | 2058 | 0.031597 | 18.2361 | 0.2043%
PIT NO 5 11011606 | PIT NO 5 1101 | NORTH VALLEY | 5.5302 | 10 | 89.8% | 1 | 2 | 100% | 0% | 0 | 0.031556 | 1 | 0.39242 | 0.012383 | Medium | Medium | Low | 3133 | 2059 | 0.031556 | 18.2045 | 0.2039%
OCEANO 1102V50 | OCEANO 1102 | LOS PADRES | 5.8788 | 10 | 32.53% | 6 | 4 | 56.2% | 0% | 0 | 0.031497 | 1 | 3.4105 | 0.10742 | Medium | Medium | High | 1724 | 2060 | 0.031497 | 18.173 | 0.2036%
HIGGINS 11077559 | HIGGINS 1107 | SIERRA | 4.3177 | 10 | 100% | 0 | 6 | 97.65% | 0% | 0 | 0.031488 | 1 | 3.2282 | 0.10165 | Medium | Medium | High | 1755 | 2061 | 0.031488 | 18.1415 | 0.2032%
FORT BRAGG A 11013113 | FORT BRAGG A 1101 | HUMBOLDT | 10.0167 | 23.3659 | 35.03% | 10 | 7 | 100% | 0% | 0 | 0.031469 | 1 | 1.6795 | 0.052853 | Medium | Medium | Low | 2292 | 2062 | 0.031469 | 18.11 | 0.2029%
UPPER LAKE 1101412 | UPPER LAKE 1101 | HUMBOLDT | 11.536 | 63.7276 | 55.28% | 0 | 4 | 61.85% | 0% | 0 | 0.031441 | 1 | 1.2806 | 0.040263 | Medium | Medium | Low | 2533 | 2063 | 0.031441 | 18.0785 | 0.2025%
DIAMOND SPRINGS 110656026 | DIAMOND SPRINGS 1106 | SIERRA | 15.0808 | 21.2538 | 81.61% | 2 | 7 | 100% | 0% | 0 | 0.031374 | 1 | 2.0796 | 0.065246 | Medium | Medium | Low | 2096 | 2064 | 0.031374 | 18.0471 | 0.2022%
POINT ARENA 11014923 | POINT ARENA 1101 | HUMBOLDT | 2.8662 | 57.1036 | 19.76% | 5 | 5 | 100% | 0% | 0 | 0.031366 | 1 | 1.8015 | 0.056505 | Medium | Medium | Low | 2234 | 2065 | 0.031366 | 18.0157 | 0.2018%
FORT SEWARD 11211663 | FORT SEWARD 1121 | HUMBOLDT | 1.9431 | 10 | 100% | 1 | 4 | 100% | 0% | 0 | 0.03133 | 1 | 1.7358 | 0.054383 | Medium | Medium | Low | 2268 | 2066 | 0.03133 | 17.9843 | 0.2015%
GUALALA 1112662 | GUALALA 1112 | HUMBOLDT | 8.3014 | 33.9068 | 0.6489% | 13 | 22 | 98.43% | 0% | 0 | 0.031273 | 1 | 2.1271 | 0.06652 | Medium | Medium | Low | 2082 | 2067 | 0.031273 | 17.953 | 0.2011%
FROGTOWN 17016807 | FROGTOWN 1701 | STOCKTON | 4.7513 | 29.5232 | 87.38% | 0 | 3 | 100% | 0% | 0 | 0.031186 | 1 | 2.7121 | 0.084578 | Medium | Medium | Medium | 1878 | 2068 | 0.031186 | 17.9217 | 0.2008%
OREGON TRAIL 1104CB | OREGON TRAIL 1104 | NORTH VALLEY | 10.8574 | 25.7844 | 63.12% | 2 | 12 | 74.06% | 0% | 0 | 0.031086 | 1 | 2.6945 | 0.08376 | Medium | Medium | Medium | 1891 | 2069 | 0.031086 | 17.8906 | 0.2004%
MONTICELLO 1101654 | MONTICELLO 1101 | NORTH BAY | 8.1004 | 46.4584 | 35.79% | 0 | 2 | 92.66% | 0% | 0 | 0.031073 | 1 | 1.8356 | 0.057038 | Medium | Medium | Low | 2223 | 2070 | 0.031073 | 17.8595 | 0.2001%
OAKLAND K 1104CB | OAKLAND K 1104 | EAST BAY | 2.7076 | 10 | 13.99% | 1 | 4 | 100% | 34.6% | 0 | 0.030956 | 1 | 4.4174 | 0.13675 | Medium | Medium | High | 1598 | 2071 | 0.030956 | 17.8284 | 0.1997%
SOBRANTE 1103CB | SOBRANTE 1103 | DIABLO | 3.6739 | 50.7835 | 26.28% | 3 | 6 | 85.25% | 16.11% | 0 | 0.030947 | 1 | 3.0955 | 0.095796 | Medium | Medium | High | 1791 | 2072 | 0.030947 | 17.7974 | 0.1994%
CURTIS 170411290 | CURTIS 1704 | YOSEMITE | 7.9015 | 12.4604 | 83.91% | 5 | 0 | 100% | 0% | 0 | 0.030926 | 1 | 3.0902 | 0.095569 | Medium | Medium | High | 1795 | 2073 | 0.030926 | 17.7665 | 0.199%
OREGON TRAIL 1103CB | OREGON TRAIL 1103 | NORTH VALLEY | 2.7772 | 25.1322 | 81.43% | 2 | 1 | 95.03% | 0% | 0 | 0.030857 | 1 | 2.3184 | 0.071539 | Medium | Medium | Medium | 2027 | 2074 | 0.030857 | 17.7356 | 0.1987%
MOUNTAIN QUARRIES 210135466 | MOUNTAIN QUARRIES 2101 | SIERRA | 7.4036 | 10 | 90.3% | 2 | 0 | 100% | 0% | 0 | 0.030814 | 1 | 2.0397 | 0.062851 | Medium | Medium | Low | 2131 | 2075 | 0.030814 | 17.7047 | 0.1983%
WEIMAR 11022038 | WEIMAR 1102 | SIERRA | 8.1278 | 10 | 76.79% | 4 | 4 | 100% | 0% | 0 | 0.030781 | 1 | 2.0149 | 0.062021 | Medium | Medium | Low | 2150 | 2076 | 0.030781 | 17.6739 | 0.198%
GARBERVILLE 1102CB | GARBERVILLE 1102 | HUMBOLDT | 10.6146 | 34.8511 | 30.11% | 18 | 9 | 65.56% | 0% | 0 | 0.030692 | 1 | 2.6357 | 0.080896 | Medium | Medium | Medium | 1927 | 2077 | 0.030692 | 17.6431 | 0.1977%
JESSUP 11011496 | JESSUP 1101 | NORTH VALLEY | 14.7255 | 17.8878 | 100% | 1 | 3 | 90.72% | 1.915% | 1 | 0.030466 | 1 | 2.1149 | 0.064433 | Medium | Medium | Low | 2111 | 2078 | 0.030466 | 17.6124 | 0.1973%
VACAVILLE 1111CB | VACAVILLE 1111 | SACRAMENTO | 7.7902 | 19.0495 | 34.16% | 0 | 5 | 64.21% | 0% | 0 | 0.030405 | 1 | 3.282 | 0.099788 | Medium | Medium | High | 1770 | 2079 | 0.030405 | 17.582 | 0.197%
HIGGINS 11041374 | HIGGINS 1104 | SIERRA | 7.2163 | 10 | 85.17% | 5 | 6 | 86.29% | 0% | 0 | 0.030394 | 1 | 3.8118 | 0.11586 | Medium | Medium | High | 1686 | 2080 | 0.030394 | 17.5516 | 0.1966%
BEAR VALLEY 210576694 | BEAR VALLEY 2105 | YOSEMITE | 4.546 | 19.6129 | 100% | 0 | 0 | 100% | 0% | 0 | 0.030391 | 1 | 2.1365 | 0.064928 | Medium | Medium | Low | 2100 | 2081 | 0.030391 | 17.5212 | 0.1963%
WEIMAR 1102CB | WEIMAR 1102 | SIERRA | 12.1704 | 10.9563 | 65.6% | 3 | 8 | 100% | 0% | 0 | 0.030334 | 1 | 2.2122 | 0.067104 | Medium | Medium | Low | 2073 | 2082 | 0.030334 | 17.4908 | 0.1959%
SAN MIGUEL 1104N60 | SAN MIGUEL 1104 | LOS PADRES | 7.3672 | 40.8154 | 100% | 0 | 1 | 83.22% | 0% | 0 | 0.030327 | 1 | 1.4627 | 0.044359 | Medium | Medium | Low | 2452 | 2083 | 0.030327 | 17.4604 | 0.1956%
JESSUP 11012839 | JESSUP 1101 | NORTH VALLEY | 1.47 | 10 | 100% | 0 | 3 | 100% | 0% | 0 | 0.030308 | 1 | 2.2134 | 0.067083 | Medium | Medium | Low | 2074 | 2084 | 0.030308 | 17.4301 | 0.1953%
FRENCH GULCH 1101CB | FRENCH GULCH 1101 | NORTH VALLEY | 2.2975 | 10 | 100% | 0 | 3 | 100% | 0% | 0 | 0.030308 | 1 | 1.5093 | 0.045746 | Medium | Medium | Low | 2425 | 2085 | 0.030308 | 17.3998 | 0.1949%
LAS POSITAS 2108MR182 | LAS POSITAS 2108 | MISSION | 6.1551 | 52.1024 | 25.77% | 0 | 0 | 85.34% | 0% | 0 | 0.030304 | 1 | 2.8822 | 0.087344 | Medium | Medium | Medium | 1852 | 2086 | 0.030304 | 17.3695 | 0.1946%
APPLE HILL 210289934 | APPLE HILL 2102 | SIERRA | 5.6225 | 10 | 91.39% | 0 | 0 | 100% | 0% | 0 | 0.030296 | 1 | 1.4475 | 0.043854 | Medium | Medium | Low | 2466 | 2087 | 0.030296 | 17.3392 | 0.1942%
SAUSALITO 11021268 | SAUSALITO 1102 | NORTH BAY | 5.0112 | 23.3781 | 0.422% | 3 | 4 | 100% | 0% | 0 | 0.030259 | 1 | 2.8544 | 0.086372 | Medium | Medium | Medium | 1863 | 2088 | 0.030259 | 17.3089 | 0.1939%
BALCH NO 1 1101CB | BALCH NO 1 1101 | FRESNO | 8.601 | 30.315 | 65.14% | 0 | 10 | 100% | 0% | 0 | 0.030256 | 1 | 1.07 | 0.032375 | Medium | Medium | Low | 2715 | 2089 | 0.030256 | 17.2786 | 0.1936%
LAURELES 11122142 | LAURELES 1112 | CENTRAL COAST | 8.368 | 31.5595 | 39.83% | 4 | 4 | 87.21% | 0% | 0 | 0.030233 | 1 | 2.7544 | 0.083276 | Medium | Medium | Medium | 1895 | 2090 | 0.030233 | 17.2484 | 0.1932%
CALPELLA 11011204 | CALPELLA 1101 | HUMBOLDT | 9.1784 | 21.5734 | 72.42% | 2 | 10 | 70.57% | 0% | 0 | 0.030223 | 1 | 2.1101 | 0.063774 | Medium | Medium | Low | 2119 | 2091 | 0.030223 | 17.2181 | 0.1929%
GARBERVILLE 110256048 | GARBERVILLE 1102 | HUMBOLDT | 4.9695 | 84.598 | 7.194% | 2 | 1 | 100% | 0% | 0 | 0.030194 | 1 | 1.3096 | 0.039543 | Medium | Medium | Low | 2548 | 2092 | 0.030194 | 17.1879 | 0.1926%
PEORIA 1705999 | PEORIA 1705 | YOSEMITE | 2.3082 | 18.7547 | 99.88% | 0 | 0 | 100% | 0% | 0 | 0.030188 | 1 | 2.9134 | 0.087952 | Medium | Medium | Medium | 1848 | 2093 | 0.030188 | 17.1577 | 0.1922%
CALISTOGA 1102CB | CALISTOGA 1102 | NORTH BAY | 1.4649 | 10 | 27.88% | 0 | 0 | 51.57% | 53.48% | 0 | 0.030163 | 1 | 3.3194 | 0.10012 | Medium | Medium | High | 1768 | 2094 | 0.030163 | 17.1275 | 0.1919%
TIVY VALLEY 11077370 | TIVY VALLEY 1107 | FRESNO | 11.4788 | 20.0364 | 68.04% | 0 | 4 | 63.49% | 0% | 0 | 0.030142 | 1 | 2.0098 | 0.060577 | Medium | Medium | Low | 2171 | 2095 | 0.030142 | 17.0974 | 0.1915%
PEORIA 1704877670 | PEORIA 1704 | YOSEMITE | 6.3096 | 69.9259 | 47.8% | 1 | 5 | 95.84% | 0% | 0 | 0.030095 | 1 | 2.1572 | 0.064921 | Medium | Medium | Low | 2101 | 2096 | 0.030095 | 17.0672 | 0.1912%
ATASCADERO 11012379 | ATASCADERO 1101 | LOS PADRES | 0.72914 | 10 | 100% | 1 | 2 | 100% | 0% | 0 | 0.030081 | 1 | 3.0039 | 0.090361 | Medium | Medium | Medium | 1829 | 2097 | 0.030081 | 17.0371 | 0.1909%
PEORIA 17013186 | PEORIA 1701 | YOSEMITE | 10.0751 | 10 | 99.94% | 1 | 2 | 100% | 0% | 0 | 0.030068 | 1 | 1.1773 | 0.035399 | Medium | Medium | Low | 2643 | 2098 | 0.030068 | 17.0071 | 0.1905%
FULTON 1102CB | FULTON 1102 | SONOMA | 1.3424 | 10 | 29.14% | 0 | 0 | 30.03% | 82.09% | 0 | 0.02998 | 1 | 2.351 | 0.070482 | Medium | Medium | Medium | 2036 | 2099 | 0.02998 | 16.977 | 0.1902%
SARATOGA 11075696 | SARATOGA 1107 | DE ANZA | 4.0107 | 10 | 57.71% | 6 | 9 | 65.93% | 4.474% | 0 | 0.029972 | 1 | 3.7269 | 0.1117 | Medium | Medium | High | 1703 | 2100 | 0.029972 | 16.947 | 0.1899%
SOLEDAD 210242506 | SOLEDAD 2102 | CENTRAL COAST | 5.4144 | 74.2068 | 100% | 0 | 1 | 19.16% | 0% | 0 | 0.029952 | 1 | 2.2961 | 0.068774 | Medium | Medium | Medium | 2055 | 2101 | 0.029952 | 16.917 | 0.1895%
FORT ROSS 1121134 | FORT ROSS 1121 | SONOMA | 7.7066 | 23.2401 | 8.01% | 16 | 1 | 95.15% | 0% | 0 | 0.029926 | 1 | 1.2427 | 0.037189 | Medium | Medium | Low | 2607 | 2102 | 0.029926 | 16.8871 | 0.1892%
NARROWS 2102CB | NARROWS 2102 | SIERRA | 22.8974 | 13.8368 | 78.07% | 2 | 5 | 93.68% | 0% | 0 | 0.029841 | 1 | 3.4435 | 0.10276 | Medium | Medium | High | 1748 | 2103 | 0.029841 | 16.8572 | 0.1888%
SPENCE 11223078 | SPENCE 1122 | CENTRAL COAST | 9.9861 | 56.9194 | 40.99% | 1 | 2 | 62.29% | 0% | 0 | 0.0298 | 1 | 1.3582 | 0.040476 | Medium | Medium | Low | 2528 | 2104 | 0.0298 | 16.8273 | 0.1885%
PETALUMA C 1109738866 | PETALUMA C 1109 | SONOMA | 2.2043 | 62.3821 | 15.29% | 1 | 1 | 81.79% | 0% | 0 | 0.029792 | 1 | 3.2084 | 0.095587 | Medium | Medium | High | 1794 | 2105 | 0.029792 | 16.7975 | 0.1882%
BROWNS VALLEY 110117011 | BROWNS VALLEY 1101 | SIERRA | 1.8676 | 10 | 100% | 0 | 2 | 100% | 0% | 0 | 0.029697 | 1 | 2.4913 | 0.073986 | Medium | Medium | Medium | 1998 | 2106 | 0.029697 | 16.7677 | 0.1878%
SALT SPRINGS 21014913 | SALT SPRINGS 2101 | STOCKTON | 3.8651 | 10 | 100% | 0 | 2 | 100% | 0% | 0 | 0.029697 | 1 | 0.71504 | 0.021235 | Medium | Medium | Low | 2978 | 2107 | 0.029697 | 16.738 | 0.1875%
CLAY 11031821 | CLAY 1103 | STOCKTON | 2.0901 | 61.2881 | 100% | 0 | 0 | 55.49% | 0% | 0 | 0.029593 | 1 | 2.5933 | 0.076746 | Medium | Medium | Medium | 1964 | 2108 | 0.029593 | 16.7083 | 0.1872%
WOODSIDE 11049032 | WOODSIDE 1104 | PENINSULA | 2.5921 | 10 | 76.95% | 3 | 1 | 32.76% | 43.39% | 0 | 0.029563 | 1 | 2.6884 | 0.079475 | Medium | Medium | Medium | 1938 | 2109 | 0.029563 | 16.6787 | 0.1868%
WOODSIDE 11018522 | WOODSIDE 1101 | PENINSULA | 0.74695 | 65.2984 | 0% | 1 | 0 | 7.949% | 85.4% | 0 | 0.029511 | 1 | 3.7573 | 0.11088 | Medium | Medium | High | 1706 | 2110 | 0.029511 | 16.6492 | 0.1865%
HICKS 111660050 | HICKS 1116 | SAN JOSE | 7.9799 | 10 | 69.56% | 2 | 6 | 100% | 0% | 0 | 0.02949 | 1 | 3.3545 | 0.098924 | Medium | Medium | High | 1778 | 2111 | 0.02949 | 16.6197 | 0.1862%
OREGON TRAIL 110249144 | OREGON TRAIL 1102 | NORTH VALLEY | 16.2173 | 16.9745 | 93.48% | 1 | 0 | 76.03% | 0% | 0 | 0.029469 | 1 | 2.7862 | 0.082107 | Medium | Medium | Medium | 1914 | 2112 | 0.029469 | 16.5902 | 0.1859%
ALHAMBRA 11058302 | ALHAMBRA 1105 | DIABLO | 8.2556 | 10 | 24.97% | 0 | 12 | 100% | 0% | 0 | 0.029452 | 1 | 2.9395 | 0.086573 | Medium | Medium | Medium | 1862 | 2113 | 0.029452 | 16.5607 | 0.1855%
MOUNTAIN QUARRIES 21012422 | MOUNTAIN QUARRIES 2101 | SIERRA | 8.6685 | 16.1435 | 71.9% | 2 | 3 | 100% | 0% | 0 | 0.029445 | 1 | 2.2909 | 0.067454 | Medium | Medium | Medium | 2065 | 2114 | 0.029445 | 16.5313 | 0.1852%
SALMON CREEK 110137368 | SALMON CREEK 1101 | SONOMA | 7.013 | 10 | 3.2% | 1 | 7 | 100% | 0% | 0 | 0.029331 | 1 | 1.9591 | 0.057461 | Medium | Medium | Low | 2216 | 2115 | 0.029331 | 16.5018 | 0.1849%
SHINGLE SPRINGS 210511172 | SHINGLE SPRINGS 2105 | SIERRA | 2.0141 | 10 | 66.76% | 1 | 3 | 82.66% | 0% | 0 | 0.029323 | 1 | 3.7968 | 0.11133 | Medium | Medium | High | 1705 | 2116 | 0.029323 | 16.4725 | 0.1845%
CLARK ROAD 110281296 | CLARK ROAD 1102 | NORTH VALLEY | 8.8512 | 53.0547 | 65.11% | 1 | 2 | 64.96% | 2.959% | 0 | 0.029241 | 1 | 1.5871 | 0.046408 | Medium | Medium | Low | 2410 | 2117 | 0.029241 | 16.4432 | 0.1842%
PURISIMA 1101Y44 | PURISIMA 1101 | LOS PADRES | 10.0257 | 87.5542 | 33.95% | 0 | 2 | 86.13% | 0% | 0 | 0.029127 | 1 | 3.4151 | 0.099473 | Medium | Medium | High | 1775 | 2118 | 0.029127 | 16.4139 | 0.1839%
WEIMAR 11026175 | WEIMAR 1102 | SIERRA | 2.7281 | 10 | 100% | 0 | 1 | 100% | 0% | 0 | 0.029099 | 1 | 2.5942 | 0.075486 | Medium | Medium | Medium | 1981 | 2119 | 0.029099 | 16.3848 | 0.1836%
SAND CREEK 11037823F | SAND CREEK 1103 | FRESNO | 4.6802 | 10 | 100% | 0 | 1 | 100% | 0% | 0 | 0.029099 | 1 | 2.1489 | 0.062531 | Medium | Medium | Low | 2135 | 2119 | 0.029099 | 16.3557 | 0.1832%
HAMILTON BRANCH 11012436 | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.2668 | 10 | 100% | 0 | 1 | 100% | 0% | 0 | 0.029099 | 1 | 1.9087 | 0.055542 | Medium | Medium | Low | 2252 | 2119 | 0.029099 | 16.3266 | 0.1829%
HALSEY 11026129 | HALSEY 1102 | SIERRA | 3.2034 | 10 | 99.84% | 0 | 1 | 100% | 0% | 0 | 0.029062 | 1 | 2.1446 | 0.062326 | Medium | Medium | Low | 2139 | 2122 | 0.029062 | 16.2975 | 0.1826%
BANGOR 1101CB | BANGOR 1101 | NORTH VALLEY | 18.8771 | 14.9118 | 68.16% | 4 | 2 | 88.52% | 0% | 0 | 0.029011 | 1 | 2.802 | 0.081291 | Medium | Medium | Medium | 1922 | 2123 | 0.029011 | 16.2684 | 0.1823%
DUNBAR 110179086 | DUNBAR 1101 | SONOMA | 6.3052 | 21.6901 | 56.75% | 1 | 5 | 90.82% | 0% | 0 | 0.02897 | 1 | 2.866 | 0.083029 | Medium | Medium | Medium | 1898 | 2124 | 0.02897 | 16.2394 | 0.1819%
HIGGINS 11097863 | HIGGINS 1109 | SIERRA | 4.2214 | 12.2843 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028948 | 1 | 2.1193 | 0.06135 | Medium | Medium | Low | 2163 | 2125 | 0.028948 | 16.2104 | 0.1816%
SUNOL 1101MR650 | SUNOL 1101 | MISSION | 1.0325 | 10 | 30.92% | 0 | 2 | 64.08% | 55.43% | 0 | 0.028936 | 1 | 2.294 | 0.066379 | Medium | Medium | Medium | 2083 | 2126 | 0.028936 | 16.1815 | 0.1813%
CLARK ROAD 11022070 | CLARK ROAD 1102 | NORTH VALLEY | 9.7077 | 20.9726 | 72.7% | 1 | 4 | 86.39% | 12.56% | 0 | 0.028935 | 1 | 2.5885 | 0.0749 | Medium | Medium | Medium | 1985 | 2127 | 0.028935 | 16.1526 | 0.181%
GUALALA 1112CB | GUALALA 1112 | HUMBOLDT | 2.0288 | 40.2405 | 4.36% | 2 | 4 | 94.33% | 0% | 0 | 0.028665 | 1 | 1.6458 | 0.047177 | Medium | Medium | Low | 2395 | 2128 | 0.028665 | 16.1236 | 0.1806%
SAN LUIS OBISPO 1104V40 | SAN LUIS OBISPO 1104 | LOS PADRES | 11.8926 | 26.5582 | 47.13% | 0 | 7 | 51.44% | 0% | 0 | 0.028654 | 1 | 2.1403 | 0.061327 | Medium | Medium | Low | 2164 | 2129 | 0.028654 | 16.095 | 0.1803%
WEIMAR 11012764 | WEIMAR 1101 | SIERRA | 6.0658 | 10 | 51% | 1 | 6 | 100% | 0% | 0 | 0.028566 | 1 | 1.8747 | 0.053554 | Medium | Medium | Low | 2278 | 2130 | 0.028566 | 16.0663 | 0.18%
UKIAH 11151216 | UKIAH 1115 | HUMBOLDT | 13.2203 | 25.9617 | 80.05% | 1 | 10 | 70.13% | 0% | 0 | 0.028563 | 1 | 2.4347 | 0.069541 | Medium | Medium | Medium | 2048 | 2131 | 0.028563 | 16.0377 | 0.1797%
FROGTOWN 1701L3361 | FROGTOWN 1701 | STOCKTON | 1.8736 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.2429 | 0.092461 | Medium | Medium | High | 1814 | 2132 | 0.028512 | 16.0092 | 0.1793%
HIGGINS 1109 | HIGGINS 1109 | SIERRA | 0.056072 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.0741 | 0.087647 | Medium | Medium | Medium | 1851 | 2132 | 0.028512 | 15.9807 | 0.179%
CAYETANO 2111MR444 | CAYETANO 2111 | MISSION | 0.15169 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.0154 | 0.085973 | Medium | Medium | Medium | 1867 | 2132 | 0.028512 | 15.9522 | 0.1787%
TRIDAM POWERHOUSE 2101CB | TRIDAM POWERHOUSE 2101 | YOSEMITE | 0.050313 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.89044 | 0.025388 | Medium | Medium | Low | 2874 | 2132 | 0.028512 | 15.9236 | 0.1784%
VALLEY VIEW 1106 | VALLEY VIEW 1106 | EAST BAY | 0.037566 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 4.232 | 0.12066 | Medium | Medium | High | 1659 | 2136 | 0.028512 | 15.8951 | 0.1781%
OAKLAND X 11066669 | OAKLAND X 1106 | EAST BAY | 0.23409 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.4389 | 0.098048 | Medium | Medium | High | 1783 | 2136 | 0.028512 | 15.8666 | 0.1778%
SYCAMORE CREEK 1111 | SYCAMORE CREEK 1111 | NORTH VALLEY | 0.19166 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.1909 | 0.090978 | Medium | Medium | High | 1823 | 2136 | 0.028512 | 15.8381 | 0.1774%
REEDLEY 1104 | REEDLEY 1104 | FRESNO | 0.23841 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.1623 | 0.090163 | Medium | Medium | High | 1831 | 2136 | 0.028512 | 15.8096 | 0.1771%
HIGGINS 11039753 | HIGGINS 1103 | SIERRA | 2.1041 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.918 | 0.083198 | Medium | Medium | Medium | 1896 | 2136 | 0.028512 | 15.7811 | 0.1768%
WYANDOTTE 1110 | WYANDOTTE 1110 | NORTH VALLEY | 0.049002 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.324 | 0.066261 | Medium | Medium | Medium | 2084 | 2136 | 0.028512 | 15.7526 | 0.1765%
CLOVERDALE 1102801904 | CLOVERDALE 1102 | SONOMA | 0.014995 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.2691 | 0.064697 | Medium | Medium | Medium | 2104 | 2136 | 0.028512 | 15.7241 | 0.1762%
ECHO SUMMIT 110155262 | ECHO SUMMIT 1101 | (blank) | 0.16554 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.0866 | 0.059493 | Medium | Medium | Low | 2187 | 2136 | 0.028512 | 15.6956 | 0.1758%
COARSEGOLD 2103 | COARSEGOLD 2103 | YOSEMITE | 0.14838 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.9847 | 0.056588 | Medium | Medium | Low | 2232 | 2136 | 0.028512 | 15.667 | 0.1755%
SAND CREEK 1103 | SAND CREEK 1103 | FRESNO | 0.037983 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.9649 | 0.056022 | Medium | Medium | Low | 2244 | 2136 | 0.028512 | 15.6385 | 0.1752%
WEIMAR 1101 | WEIMAR 1101 | SIERRA | 0.067365 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.8525 | 0.052817 | Medium | Medium | Low | 2293 | 2136 | 0.028512 | 15.61 | 0.1749%
CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 1101 | STOCKTON | 0.0029886 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.8278 | 0.052113 | Medium | Medium | Low | 2306 | 2136 | 0.028512 | 15.5815 | 0.1746%
SUNOL 110148180 | SUNOL 1101 | MISSION | 0.015663 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.7365 | 0.049509 | Medium | Medium | Low | 2361 | 2136 | 0.028512 | 15.553 | 0.1742%
WHITMORE 1101002 | WHITMORE 1101 | NORTH VALLEY | 0.0042201 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.5578 | 0.044415 | Medium | Medium | Low | 2450 | 2136 | 0.028512 | 15.5245 | 0.1739%
CALPELLA 1101 | CALPELLA 1101 | HUMBOLDT | 0.0052324 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.4352 | 0.040921 | Medium | Medium | Low | 2519 | 2136 | 0.028512 | 15.496 | 0.1736%
LAYTONVILLE 1102220946 | LAYTONVILLE 1102 | HUMBOLDT | 0.040461 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.3334 | 0.038016 | Medium | Medium | Low | 2583 | 2136 | 0.028512 | 15.4675 | 0.1733%
CEDAR CREEK 11011362 | CEDAR CREEK 1101 | NORTH VALLEY | 0.015515 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.2439 | 0.035466 | Medium | Medium | Low | 2641 | 2136 | 0.028512 | 15.4389 | 0.173%
PIT NO 5 110190846 | PIT NO 5 1101 | NORTH VALLEY | 0.092785 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.31428 | 0.0089606 | Medium | Medium | Low | 3154 | 2136 | 0.028512 | 15.4104 | 0.1726%
OREGON TRAIL 1104 | OREGON TRAIL 1104 | NORTH VALLEY | 0.063815 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.6217 | 0.074749 | Medium | Medium | Medium | 1988 | 2154 | 0.028512 | 15.3819 | 0.1723%
SALT SPRINGS 21023118 | SALT SPRINGS 2102 | STOCKTON | 0.07196 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.54869 | 0.015644 | Medium | Medium | Low | 3092 | 2154 | 0.028512 | 15.3534 | 0.172%
CLAY 110334338 | CLAY 1103 | STOCKTON | 7.6368 | 36.5237 | 71.29% | 1 | 2 | 73.13% | 0% | 0 | 0.028445 | 1 | 2.6701 | 0.075951 | Medium | Medium | Medium | 1976 | 2156 | 0.028445 | 15.3249 | 0.1717%
COARSEGOLD 2102CB | COARSEGOLD 2102 | YOSEMITE | 14.0621 | 38.5067 | 44.35% | 2 | 1 | 100% | 4.748% | 0 | 0.028352 | 1 | 1.8189 | 0.051569 | Medium | Medium | Low | 2318 | 2157 | 0.028352 | 15.2965 | 0.1714%
DESCHUTES 1104CB | DESCHUTES 1104 | NORTH VALLEY | 12.32 | 22.7091 | 100% | 1 | 6 | 50.17% | 0% | 0 | 0.028343 | 1 | 3.212 | 0.091036 | Medium | Medium | High | 1822 | 2158 | 0.028343 | 15.2681 | 0.171%
LLAGAS 21011451 | LLAGAS 2101 | SAN JOSE | 5.288 | 70.7589 | 100% | 0 | 0 | 57.46% | 0% | 0 | 0.028219 | 1 | 2.4961 | 0.070438 | Medium | Medium | Medium | 2040 | 2159 | 0.028219 | 15.2398 | 0.1707%
HOPLAND 1101960 | HOPLAND 1101 | HUMBOLDT | 16.1295 | 41.2103 | 77.4% | 2 | 9 | 74.6% | 0% | 0 | 0.028177 | 1 | 1.4185 | 0.039967 | Medium | Medium | Low | 2541 | 2160 | 0.028177 | 15.2115 | 0.1704%
WOODWARD 210878448 | WOODWARD 2108 | FRESNO | 18.5469 | 31.6388 | 94.91% | 1 | 5 | 62.76% | 0% | 0 | 0.028087 | 1 | 1.6079 | 0.045161 | Medium | Medium | Low | 2436 | 2161 | 0.028087 | 15.1834 | 0.1701%
DOBBINS 1101CB | DOBBINS 1101 | SIERRA | 0.67055 | 10 | 81.76% | 0 | 0 | 100% | 0% | 0 | 0.028046 | 1 | 2.2347 | 0.062675 | Medium | Medium | Medium | 2133 | 2162 | 0.028046 | 15.1553 | 0.1698%
NARROWS 21052748 | NARROWS 2105 | SIERRA | 11.8577 | 19.7377 | 85.36% | 3 | 6 | 60.51% | 0% | 0 | 0.02804 | 1 | 3.5416 | 0.099307 | Medium | Medium | High | 1776 | 2163 | 0.02804 | 15.1272 | 0.1695%
PIT NO 3 21011386 | PIT NO 3 2101 | NORTH VALLEY | 5.8084 | 10 | 93.45% | 4 | 0 | 84.51% | 0% | 0 | 0.027889 | 1 | 0.24957 | 0.0069602 | Medium | Medium | Low | 3162 | 2164 | 0.027889 | 15.0992 | 0.1692%
FROGTOWN 17028482 | FROGTOWN 1702 | STOCKTON | 14.6236 | 52.3445 | 57.04% | 0 | 2 | 100% | 0% | 0 | 0.027885 | 1 | 1.9388 | 0.054064 | Medium | Medium | Low | 2271 | 2165 | 0.027885 | 15.0713 | 0.1688%
HARTLEY 1101698 | HARTLEY 1101 | HUMBOLDT | 6.3129 | 57.2881 | 69.42% | 1 | 7 | 61.15% | 0% | 0 | 0.027842 | 1 | 2.0226 | 0.056312 | Medium | Medium | Low | 2239 | 2166 | 0.027842 | 15.0434 | 0.1685%
PLACERVILLE 1112CB | PLACERVILLE 1112 | SIERRA | 7.6031 | 10 | 47.53% | 2 | 8 | 81.02% | 0.2042% | 0 | 0.027832 | 1 | 3.0844 | 0.085847 | Medium | Medium | High | 1868 | 2167 | 0.027832 | 15.0156 | 0.1682%
JOLON 1102CB | JOLON 1102 | CENTRAL COAST | 23.7338 | 63.1412 | 51.5% | 0 | 1 | 99.01% | 0% | 0 | 0.02781 | 1 | 0.97488 | 0.027111 | Medium | Medium | Low | 2837 | 2168 | 0.02781 | 14.9877 | 0.1679%
GUALALA 1111887180 | GUALALA 1111 | HUMBOLDT | 5.4716 | 10 | 0.3119% | 7 | 8 | 100% | 0% | 0 | 0.027751 | 1 | 2.6787 | 0.074336 | Medium | Medium | Medium | 1994 | 2169 | 0.027751 | 14.9599 | 0.1676%
LUCERNE 11034200 | LUCERNE 1103 | HUMBOLDT | 4.2514 | 45.4735 | 81.38% | 0 | 1 | 86.14% | 0% | 0 | 0.027721 | 1 | 1.9269 | 0.053416 | Medium | Medium | Low | 2283 | 2170 | 0.027721 | 14.9322 | 0.1673%
OTTER 11022166 | OTTER 1102 | CENTRAL COAST | 4.0812 | 30.3358 | 3.172% | 4 | 2 | 100% | 0% | 0 | 0.027673 | 1 | 1.3506 | 0.037374 | Medium | Medium | Low | 2598 | 2171 | 0.027673 | 14.9045 | 0.167%
ELK CREEK 11012212 | ELK CREEK 1101 | NORTH VALLEY | 10.0272 | 85.6358 | 100% | 0 | 1 | 29.79% | 0% | 0 | 0.02765 | 1 | 1.7915 | 0.049534 | Medium | Medium | Low | 2360 | 2172 | 0.02765 | 14.8768 | 0.1667%
STILLWATER 1101CB | STILLWATER 1101 | NORTH VALLEY | 3.671 | 10 | 87.48% | 3 | 2 | 85.62% | 0% | 0 | 0.027635 | 1 | 2.6197 | 0.072394 | Medium | Medium | Medium | 2012 | 2173 | 0.027635 | 14.8491 | 0.1664%
REDBUD 110191960 | REDBUD 1101 | HUMBOLDT | 7.0156 | 10 | 50% | 3 | 16 | 100% | 0% | 0 | 0.0275 | 1 | 2.2782 | 0.062653 | Medium | Medium | Medium | 2134 | 2174 | 0.0275 | 14.8215 | 0.166%
CLARK ROAD 11022584 | CLARK ROAD 1102 | NORTH VALLEY | 7.9946 | 18.0642 | 99.96% | 1 | 2 | 85.31% | 0% | 0 | 0.0275 | 1 | 2.2918 | 0.063027 | Medium | Medium | Medium | 2129 | 2175 | 0.0275 | 14.794 | 0.1657%
CALAVERAS CEMENT 110111236 | CALAVERAS CEMENT 1101 | STOCKTON | 20.1179 | 16.0826 | 47.9% | 0 | 4 | 100% | 0% | 0 | 0.027497 | 1 | 1.8952 | 0.052111 | Medium | Medium | Low | 2307 | 2176 | 0.027497 | 14.7665 | 0.1654%
PINE GROVE 110194936 | PINE GROVE 1101 | STOCKTON | 9.27 | 10 | 75.09% | 1 | 1 | 100% | 0% | 0 | 0.027484 | 1 | 2.6139 | 0.071841 | Medium | Medium | Medium | 2021 | 2177 | 0.027484 | 14.739 | 0.1651%
GONZALES 11013094 | GONZALES 1101 | CENTRAL COAST | 3.5612 | 68.6689 | 100% | 1 | 1 | 39.42% | 0% | 0 | 0.027478 | 1 | 2.2388 | 0.061516 | Medium | Medium | Medium | 2160 | 2178 | 0.027478 | 14.7115 | 0.1648%
WOODSIDE 1104CB | WOODSIDE 1104 | PENINSULA | 0.34613 | 10 | 13.48% | 0 | 0 | 4.645% | 100% | 0 | 0.027423 | 1 | 2.6038 | 0.071405 | Medium | Medium | Medium | 2029 | 2179 | 0.027423 | 14.684 | 0.1645%
PHILO 1102CB | PHILO 1102 | HUMBOLDT | 5.5805 | 58.9475 | 61.62% | 10 | 11 | 44.58% | 0% | 0 | 0.027409 | 1 | 2.3552 | 0.064554 | Medium | Medium | Medium | 2107 | 2180 | 0.027409 | 14.6566 | 0.1642%
PIT NO 3 2101CB | PIT NO 3 2101 | NORTH VALLEY | 4.5423 | 34.7965 | 2.145% | 10 | 3 | 100% | 0% | 0 | 0.027375 | 1 | 1.2188 | 0.033365 | Medium | Medium | Low | 2691 | 2181 | 0.027375 | 14.6292 | 0.1639%
WOODSIDE 1104555372 | WOODSIDE 1104 | PENINSULA | 4.1602 | 10 | 35.51% | 2 | 3 | 100% | 0% | 0 | 0.02737 | 1 | 4.8418 | 0.13252 | Medium | Medium | High | 1618 | 2182 | 0.02737 | 14.6018 | 0.1636%
WHITMORE 1101CB | WHITMORE 1101 | NORTH VALLEY | 5.8976 | 20.259 | 68.5% | 1 | 0 | 100% | 0% | 0 | 0.027347 | 1 | 1.5637 | 0.042762 | Medium | Medium | Low | 2483 | 2183 | 0.027347 | 14.5745 | 0.1633%
HIGGINS 11071070 | HIGGINS 1107 | SIERRA | 7.012 | 12.4115 | 99.96% | 1 | 4 | 84.37% | 0% | 0 | 0.027337 | 1 | 3.0898 | 0.084465 | Medium | Medium | High | 1879 | 2184 | 0.027337 | 14.5471 | 0.163%
FAIRVIEW 2207P304 | FAIRVIEW 2207 | DIABLO | 5.0581 | 10 | 29.34% | 0 | 2 | 82.96% | 0% | 0 | 0.027316 | 1 | 3.4133 | 0.093239 | Medium | Medium | High | 1808 | 2185 | 0.027316 | 14.5198 | 0.1627%
STELLING 11109265 | STELLING 1110 | DE ANZA | 5.4699 | 10 | 92.07% | 0 | 1 | 100% | 0% | 0 | 0.027307 | 1 | 2.9335 | 0.080104 | Medium | Medium | Medium | 1933 | 2186 | 0.027307 | 14.4925 | 0.1624%
OILFIELDS 11035175 | OILFIELDS 1103 | CENTRAL COAST | 1.9738 | 10 | 100% | 0 | 3 | 89.15% | 0% | 0 | 0.027271 | 1 | 2.7162 | 0.074075 | Medium | Medium | Medium | 1997 | 2187 | 0.027271 | 14.4652 | 0.1621%
HALSEY 11025739 | HALSEY 1102 | SIERRA | 6.6683 | 10 | 67.05% | 2 | 3 | 100% | 0% | 0 | 0.027187 | 1 | 1.8652 | 0.050708 | Medium | Medium | Low | 2339 | 2188 | 0.027187 | 14.4379 | 0.1617%
FRUITLAND 114195324 | FRUITLAND 1141 | HUMBOLDT | 9.0462 | 63.96 | 12.78% | 11 | 1 | 100% | 0% | 0 | 0.027146 | 1 | 1.6852 | 0.045746 | Medium | Medium | Low | 2424 | 2189 | 0.027146 | 14.4107 | 0.1614%
GREENBRAE 1103CB | GREENBRAE 1103 | NORTH BAY | 0.06411 | 10 | 0% | 0 | 0 | 1.278% | 100% | 0 | 0.02712 | 1 | 3.9968 | 0.10839 | Medium | Medium | High | 1718 | 2190 | 0.02712 | 14.3836 | 0.1611%
DEL MONTE 21032654 | DEL MONTE 2103 | CENTRAL COAST | 1.8437 | 10 | 36.65% | 2 | 2 | 100% | 0% | 0 | 0.027064 | 1 | 3.2195 | 0.087132 | Medium | Medium | High | 1855 | 2191 | 0.027064 | 14.3564 | 0.1608%
MORGAN HILL 2105XR152 | MORGAN HILL 2105 | SAN JOSE | 8.3434 | 31.972 | 72.23% | 0 | 5 | 65.24% | 0% | 0 | 0.027024 | 1 | 3.0674 | 0.082892 | Medium | Medium | Medium | 1902 | 2192 | 0.027024 | 14.3294 | 0.1605%
PIERCY 2110XR258 | PIERCY 2110 | SAN JOSE | 14.4387 | 60.8378 | 97.27% | 4 | 1 | 54.5% | 0% | 0 | 0.026979 | 1 | 2.7761 | 0.074895 | Medium | Medium | Medium | 1986 | 2193 | 0.026979 | 14.3024 | 0.1602%
BIG MEADOWS 2101CB | BIG MEADOWS 2101 | NORTH VALLEY | 2.1059 | 66.4943 | 39.01% | 1 | 2 | 100% | 0% | 0 | 0.026855 | 1 | 1.6697 | 0.04484 | Medium | Medium | Low | 2441 | 2194 | 0.026855 | 14.2754 | 0.1599%
LAS GALLINAS A 1106CB | LAS GALLINAS A 1106 | NORTH BAY | 4.998 | 10 | 78.22% | 0 | 1 | 31.7% | 39.74% | 0 | 0.026841 | 1 | 3.8683 | 0.10383 | Medium | Medium | High | 1742 | 2195 | 0.026841 | 14.2485 | 0.1596%
EL CERRITO G 1105BR194 | EL CERRITO G 1105 | EAST BAY | 3.0539 | 15.352 | 23.01% | 1 | 2 | 58.3% | 30.42% | 0 | 0.026764 | 1 | 4.423 | 0.11838 | Medium | Medium | High | 1670 | 2196 | 0.026764 | 14.2217 | 0.1593%
OLETA 110113478 | OLETA 1101 | STOCKTON | 13.3756 | 25.4349 | 51.06% | 1 | 4 | 86.71% | 0% | 0 | 0.02671 | 1 | 3.4668 | 0.092599 | Medium | Medium | High | 1812 | 2197 | 0.02671 | 14.1949 | 0.159%
POSO MOUNTAIN 2101CB | POSO MOUNTAIN 2101 | KERN | 4.3131 | 10 | 10.82% | 0 | 0 | 100% | 0% | 0 | 0.026686 | 1 | 2.722 | 0.072639 | Medium | Medium | Medium | 2009 | 2198 | 0.026686 | 14.1682 | 0.1587%
HARTLEY 11011306 | HARTLEY 1101 | HUMBOLDT | 8.9139 | 32.0441 | 81.66% | 1 | 4 | 70.23% | 0% | 0 | 0.026684 | 1 | 2.6078 | 0.069587 | Medium | Medium | Medium | 2047 | 2199 | 0.026684 | 14.1415 | 0.1584%
MENLO 110212249 | MENLO 1102 | PENINSULA | 2.4062 | 33.867 | 49.86% | 2 | 1 | 100% | 0% | 0 | 0.02665 | 1 | 2.3278 | 0.062037 | Medium | Medium | Medium | 2147 | 2200 | 0.02665 | 14.1148 | 0.1581%
SOBRANTE 1101CB | SOBRANTE 1101 | DIABLO | 13.5487 | 10.8121 | 22.39% | 1 | 13 | 87.75% | 0% | 0 | 0.02661 | 1 | 3.1685 | 0.084314 | Medium | Medium | High | 1881 | 2201 | 0.02661 | 14.0882 | 0.1578%
CAMBRIA 1102CB | CAMBRIA 1102 | LOS PADRES | 14.9946 | 41.8579 | 39.26% | 1 | 1 | 64.1% | 0% | 0 | 0.026518 | 1 | 2.3401 | 0.062055 | Medium | Medium | Medium | 2146 | 2202 | 0.026518 | 14.0616 | 0.1575%
PIT NO 3 21011482 | PIT NO 3 2101 | NORTH VALLEY | 12.042 | 25.2752 | 56.98% | 0 | 2 | 100% | 0% | 0 | 0.026507 | 1 | 0.19495 | 0.0051676 | Medium | Medium | Low | 3172 | 2203 | 0.026507 | 14.0351 | 0.1572%
PENRYN 1107346 | PENRYN 1107 | SIERRA | 12.7652 | 20.7142 | 69.91% | 3 | 7 | 51.25% | 0% | 0 | 0.026474 | 1 | 2.5635 | 0.067868 | Medium | Medium | Medium | 2063 | 2204 | 0.026474 | 14.0085 | 0.1569%
CASTRO VALLEY 1108MR379 | CASTRO VALLEY 1108 | MISSION | 1.2345 | 10 | 98.65% | 0 | 0 | 78.3% | 9.302% | 0 | 0.026453 | 1 | 3.7001 | 0.09788 | Medium | Medium | High | 1784 | 2205 | 0.026453 | 13.9821 | 0.1566%
LUCERNE 1106526 | LUCERNE 1106 | HUMBOLDT | 9.9941 | 16.6965 | 53.92% | 1 | 9 | 92.11% | 0% | 0 | 0.026433 | 1 | 2.4967 | 0.065996 | Medium | Medium | Medium | 2088 | 2206 | 0.026433 | 13.9556 | 0.1563%
SAN LUIS OBISPO 1103V82 | SAN LUIS OBISPO 1103 | LOS PADRES | 6.5219 | 24.8763 | 65.03% | 1 | 11 | 46.53% | 0% | 0 | 0.026432 | 1 | 2.2734 | 0.060091 | Medium | Medium | Medium | 2182 | 2207 | 0.026432 | 13.9292 | 0.156%
PENRYN 11072708 | PENRYN 1107 | SIERRA | 8.636 | 10 | 67.69% | 3 | 4 | 79.72% | 0% | 0 | 0.026402 | 1 | 3.2393 | 0.085524 | Medium | Medium | High | 1872 | 2208 | 0.026402 | 13.9028 | 0.1558%
NARROWS 21052426 | NARROWS 2105 | SIERRA | 9.7882 | 10 | 86.21% | 2 | 2 | 56.57% | 0% | 0 | 0.026381 | 1 | 3.2439 | 0.085575 | Medium | Medium | High | 1871 | 2209 | 0.026381 | 13.8764 | 0.1555%
NAPA 11121302 | NAPA 1112 | NORTH BAY | 17.5904 | 30.9393 | 74.37% | 2 | 8 | 52.69% | 0% | 0 | 0.026355 | 1 | 3.0997 | 0.081693 | Medium | Medium | High | 1918 | 2210 | 0.026355 | 13.85 | 0.1552%
REDBUD 1102922 | REDBUD 1102 | HUMBOLDT | 3.3 | 10 | 97% | 1 | 5 | 42.49% | 0% | 0 | 0.026319 | 1 | 2.2985 | 0.060493 | Medium | Medium | Medium | 2173 | 2211 | 0.026319 | 13.8236 | 0.1549%
BANGOR 110131502 | BANGOR 1101 | NORTH VALLEY | 11.8542 | 14.4917 | 60.88% | 1 | 3 | 100% | 0% | 0 | 0.026318 | 1 | 2.9147 | 0.076709 | Medium | Medium | Medium | 1967 | 2212 | 0.026318 | 13.7973 | 0.1546%
SUMMIT 110249484 | SUMMIT 1102 | SIERRA | 2.6877 | 10 | 54.68% | 1 | 0 | 100% | 0% | 0 | 0.026029 | 1 | 0.69298 | 0.018038 | Medium | Medium | Low | 3043 | 2213 | 0.026029 | 13.771 | 0.1543%
BAY MEADOWS 210257886 | BAY MEADOWS 2102 | PENINSULA | 4.2245 | 10 | 28.89% | 2 | 6 | 80.67% | 0% | 0 | 0.026024 | 1 | 3.0461 | 0.079274 | Medium | Medium | Medium | 1941 | 2214 | 0.026024 | 13.745 | 0.154%
HAMILTON BRANCH 110137436 | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.0486 | 10 | 99.62% | 2 | 5 | 51.07% | 0% | 0 | 0.025995 | 1 | 3.8843 | 0.10097 | Medium | Medium | High | 1762 | 2215 | 0.025995 | 13.7189 | 0.1537%
FRUITLAND 11413902 | FRUITLAND 1141 | HUMBOLDT | 5.0988 | 85.765 | 7.833% | 1 | 0 | 99.69% | 0% | 0 | 0.025906 | 1 | 0.80512 | 0.020857 | Medium | Medium | Low | 2984 | 2216 | 0.025906 | 13.6929 | 0.1534%
EL CERRITO G 1112CB | EL CERRITO G 1112 | EAST BAY | 0.64797 | 10 | 0% | 0 | 0 | 9.809% | 100% | 0 | 0.02588 | 1 | 4.9956 | 0.12929 | Medium | Medium | High | 1626 | 2217 | 0.02588 | 13.667 | 0.1531%
OCEANO 1104CB | OCEANO 1104 | LOS PADRES | 8.0054 | 24.7481 | 22.23% | 2 | 9 | 52.54% | 10.2% | 1 | 0.025849 | 1 | 3.7493 | 0.096918 | Medium | Medium | High | 1788 | 2218 | 0.025849 | 13.6411 | 0.1528%
MIDDLETOWN 1102514 | MIDDLETOWN 1102 | HUMBOLDT | 4.5797 | 10 | 100% | 1 | 1 | 86.53% | 0% | 0 | 0.025849 | 1 | 3.491 | 0.090241 | Medium | Medium | High | 1830 | 2219 | 0.025849 | 13.6153 | 0.1525%
LUCERNE 11062355 | LUCERNE 1106 | HUMBOLDT | 0.92313 | 10 | 100% | 1 | 0 | 88.59% | 0% | 0 | 0.02584 | 1 | 2.1572 | 0.055742 | Medium | Medium | Low | 2250 | 2220 | 0.02584 | 13.5894 | 0.1522%
FROGTOWN 170232556 | FROGTOWN 1702 | STOCKTON | 4.3373 | 25.6533 | 79.39% | 0 | 0 | 69.35% | 0% | 0 | 0.025794 | 1 | 1.9369 | 0.049959 | Medium | Medium | Low | 2351 | 2221 | 0.025794 | 13.5636 | 0.152%
BIG RIVER 11011286 | BIG RIVER 1101 | HUMBOLDT | 4.4303 | 10 | 38.59% | 7 | 9 | 58.78% | 0% | 0 | 0.025767 | 1 | 2.6794 | 0.06904 | Medium | Medium | Medium | 2051 | 2222 | 0.025767 | 13.5378 | 0.1517%
MC ARTHUR 11011546 | MC ARTHUR 1101 | NORTH VALLEY | 13.3497 | 54.7981 | 96.53% | 1 | 1 | 58.43% | 0% | 0 | 0.025754 | 1 | 0.91531 | 0.023572 | Medium | Medium | Low | 2921 | 2223 | 0.025754 | 13.512 | 0.1514%
DESCHUTES 11049718 | DESCHUTES 1104 | NORTH VALLEY | 6.0769 | 37.0786 | 75.84% | 1 | 1 | 34.09% | 0% | 0 | 0.025713 | 1 | 2.6812 | 0.068942 | Medium | Medium | Medium | 2052 | 2224 | 0.025713 | 13.4863 | 0.1511%
RINCON 1103472 | RINCON 1103 | SONOMA | 3.3276 | 10 | 93.65% | 0 | 2 | 70.54% | 3.999% | 0 | 0.025694 | 1 | 3.1877 | 0.081905 | Medium | Medium | High | 1915 | 2225 | 0.025694 | 13.4606 | 0.1508%
JOLON 11027002 | JOLON 1102 | CENTRAL COAST | 7.9112 | 56.9708 | 100% | 0 | 0 | 43.93% | 0% | 0 | 0.025691 | 1 | 1.1804 | 0.030327 | Medium | Medium | Low | 2767 | 2226 | 0.025691 | 13.4349 | 0.1505%
POINT ARENA 110183354 | POINT ARENA 1101 | HUMBOLDT | 5.1346 | 37.1787 | 0% | 2 | 5 | 100% | 0% | 0 | 0.025688 | 1 | 2.0227 | 0.051961 | Medium | Medium | Low | 2309 | 2227 | 0.025688 | 13.4092 | 0.1502%
PASO ROBLES 1103N52 | PASO ROBLES 1103 | LOS PADRES | 6.5425 | 67.4375 | 22.89% | 0 | 0 | 100% | 0% | 0 | 0.025622 | 1 | 2.4074 | 0.061683 | Medium | Medium | Medium | 2158 | 2228 | 0.025622 | 13.3835 | 0.1499%
CALPELLA 1101CB | CALPELLA 1101 | HUMBOLDT | 10.9748 | 13.9128 | 62.49% | 0 | 11 | 53.93% | 0% | 0 | 0.025545 | 1 | 1.6899 | 0.043167 | Medium | Medium | Low | 2473 | 2229 | 0.025545 | 13.3579 | 0.1496%
OTTER 11022002 | OTTER 1102 | CENTRAL COAST | 8.6285 | 34.3246 | 5.086% | 6 | 1 | 100% | 0% | 0 | 0.025475 | 1 | 1.2546 | 0.03196 | Medium | Medium | Low | 2728 | 2230 | 0.025475 | 13.3323 | 0.1494%
CAMP EVERS 210392582 | CAMP EVERS 2103 | CENTRAL COAST | 0.22538 | 10 | 0% | 0 | 0 | 8.037% | 100% | 0 | 0.025436 | 1 | 2.5772 | 0.065553 | Medium | Medium | Medium | 2094 | 2231 | 0.025436 | 13.3069 | 0.1491%
NORTH BRANCH 1101TS1115 | NORTH BRANCH 1101 | STOCKTON | 17.6104 | 17.7152 | 77.63% | 1 | 0 | 100% | 0% | 0 | 0.025404 | 1 | 2.3625 | 0.060018 | Medium | Medium | Medium | 2183 | 2232 | 0.025404 | 13.2814 | 0.1488%
OLETA 110241396 | OLETA 1102 | STOCKTON | 7.3755 | 10 | 56.8% | 3 | 3 | 100% | 0% | 0 | 0.025362 | 1 | 3.0576 | 0.077548 | Medium | Medium | Medium | 1958 | 2233 | 0.025362 | 13.256 | 0.1485%
GREENBRAE 1102CB | GREENBRAE 1102 | NORTH BAY | 0.15859 | 10 | 0% | 0 | 0 | 7.352% | 100% | 0 | 0.025266 | 1 | 3.3659 | 0.085044 | Medium | Medium | High | 1874 | 2234 | 0.025266 | 13.2307 | 0.1482%
PERRY 1101CB | PERRY 1101 | LOS PADRES | 2.5037 | 27.4854 | 19.25% | 0 | 1 | 100% | 0% | 0 | 0.025246 | 1 | 2.9519 | 0.074522 | Medium | Medium | Medium | 1990 | 2235 | 0.025246 | 13.2054 | 0.1479%
RALSTON 110148936 | RALSTON 1101 | PENINSULA | 3.4057 | 10 | 32.09% | 0 | 3 | 56.99% | 0% | 0 | 0.025196 | 1 | 3.2337 | 0.081477 | Medium | Medium | High | 1920 | 2236 | 0.025196 | 13.1801 | 0.1477%
MARIPOSA 210197142 | MARIPOSA 2101 | YOSEMITE | 4.6012 | 28.8872 | 53.68% | 0 | 6 | 100% | 0% | 0 | 0.025194 | 1 | 1.8808 | 0.047384 | Medium | Medium | Low | 2392 | 2237 | 0.025194 | 13.155 | 0.1474%
PEORIA 170570198 | PEORIA 1705 | YOSEMITE | 1.5831 | 45.3965 | 98.01% | 1 | 0 | 49.77% | 0% | 0 | 0.025104 | 1 | 2.6852 | 0.067408 | Medium | Medium | Medium | 2067 | 2238 | 0.025104 | 13.1298 | 0.1471%
IGNACIO 11011300 | IGNACIO 1101 | NORTH BAY | 2.4856 | 23.8629 | 75.16% | 0 | 4 | 40.74% | 21.73% | 0 | 0.025064 | 1 | 3.1191 | 0.078176 | Medium | Medium | High | 1952 | 2239 | 0.025064 | 13.1047 | 0.1468%
JAMESON 1103CB | JAMESON 1103 | SACRAMENTO | 3.6313 | 55.7827 | 92.07% | 0 | 1 | 33.3% | 0% | 0 | 0.025062 | 1 | 3.4236 | 0.085801 | Medium | Medium | High | 1869 | 2240 | 0.025062 | 13.0796 | 0.1465%
BURNEY 110145984 | BURNEY 1101 | NORTH VALLEY | 4.7181 | 10 | 42.42% | 2 | 3 | 98.54% | 0% | 0 | 0.025045 | 1 | 2.4898 | 0.062355 | Medium | Medium | Medium | 2138 | 2241 | 0.025045 | 13.0545 | 0.1462%
HIGGINS 1107 | HIGGINS 1107 | SIERRA | 0.013093 | 10 | 100% | 0 | 0 | 86.65% | 0% | 0 | 0.025031 | 1 | 3.3943 | 0.084962 | Medium | Medium | High | 1876 | 2242 | 0.025031 | 13.0295 | 0.146%
COVELO 110196896 | COVELO 1101 | HUMBOLDT | 3.6958 | 52.7111 | 100% | 5 | 0 | 24.03% | 0% | 0 | 0.024981 | 1 | 1.3246 | 0.033091 | Medium | Medium | Low | 2698 | 2243 | 0.024981 | 13.0045 | 0.1457%
FROGTOWN 17027108 | FROGTOWN 1702 | STOCKTON | 10.0437 | 39.0873 | 66.95% | 0 | 1 | 78.26% | 0% | 0 | 0.024952 | 1 | 2.4898 | 0.062125 | Medium | Medium | Medium | 2143 | 2244 | 0.024952 | 12.9795 | 0.1454%
LLAGAS 21011449 | LLAGAS 2101 | SAN JOSE | 7.6142 | 50.4014 | 99.39% | 2 | 1 | 54.33% | 0% | 0 | 0.024906 | 1 | 2.3109 | 0.057555 | Medium | Medium | Medium | 2214 | 2245 | 0.024906 | 12.9545 | 0.1451%
CLAYTON 22122944 | CLAYTON 2212 | DIABLO | 14.8336 | 10 | 45.06% | 1 | 4 | 97.25% | 6.81% | 1 | 0.024898 | 1 | 3.1713 | 0.078959 | Medium | Medium | High | 1944 | 2246 | 0.024898 | 12.9296 | 0.1448%
PERRY 1101V74 | PERRY 1101 | LOS PADRES | 2.9727 | 10 | 2.672% | 10 | 7 | 58.33% | 0% | 0 | 0.024878 | 1 | 3.4959 | 0.086972 | Medium | Medium | High | 1857 | 2247 | 0.024878 | 12.9047 | 0.1446%
LAKEWOOD 210738404 | LAKEWOOD 2107 | DIABLO | 6.7961 | 30.5815 | 25.31% | 5 | 8 | 68.2% | 1.158% | 0 | 0.024865 | 1 | 3.312 | 0.082353 | Medium | Medium | High | 1910 | 2248 | 0.024865 | 12.8798 | 0.1443%
GARBERVILLE 11011604 | GARBERVILLE 1101 | HUMBOLDT | 4.3333 | 50.687 | 100% | 0 | 3 | 25.13% | 0% | 0 | 0.024833 | 1 | 2.1532 | 0.053469 | Medium | Medium | Low | 2280 | 2249 | 0.024833 | 12.855 | 0.144%
GUALALA 1111498 | GUALALA 1111 | HUMBOLDT | 2.9971 | 32.4304 | 1.089% | 0 | 12 | 100% | 0% | 0 | 0.024787 | 1 | 1.9715 | 0.048867 | Medium | Medium | Low | 2370 | 2250 | 0.024787 | 12.8301 | 0.1437%
HIGGINS 1104CB | HIGGINS 1104 | SIERRA | 11.5789 | 10 | 38.55% | 1 | 4 | 99.62% | 0% | 0 | 0.024722 | 1 | 3.0793 | 0.076125 | Medium | Medium | High | 1971 | 2251 | 0.024722 | 12.8054 | 0.1435%
ROSSMOOR 1101L503R | ROSSMOOR 1101 | DIABLO | 4.2657 | 11.5666 | 6.541% | 0 | 11 | 100% | 15.14% | 0 | 0.024651 | 1 | 3.5968 | 0.088666 | Medium | Medium | High | 1840 | 2252 | 0.024651 | 12.7806 | 0.1432%
HIGGINS 1104498932 | HIGGINS 1104 | SIERRA | 3.4528 | 10 | 98.29% | 1 | 2 | 80.99% | 0% | 0 | 0.024651 | 1 | 3.516 | 0.086673 | Medium | Medium | High | 1861 | 2253 | 0.024651 | 12.756 | 0.1429%
ZACA 1101CB | ZACA 1101 | LOS PADRES | 7.3177 | 63.5153 | 26.01% | 0 | 1 | 67.25% | 0% | 0 | 0.024613 | 1 | 1.2436 | 0.030608 | Medium | Medium | Low | 2754 | 2254 | 0.024613 | 12.7313 | 0.1426%
PEORIA 170459596 | PEORIA 1704 | YOSEMITE | 19.1476 | 35.0672 | 53.97% | 0 | 6 | 53.15% | 0% | 0 | 0.024608 | 1 | 3.3279 | 0.081892 | Medium | Medium | High | 1917 | 2255 | 0.024608 | 12.7067 | 0.1424%
GARBERVILLE 1102 | GARBERVILLE 1102 | HUMBOLDT | 0.096479 | 11.5575 | 97.17% | 0 | 0 | 86.15% | 0% | 0 | 0.024601 | 1 | 0.65244 | 0.016051 | Medium | Medium | Low | 3083 | 2256 | 0.024601 | 12.6821 | 0.1421%
JESSUP 11021550 | JESSUP 1102 | NORTH VALLEY | 17.7067 | 29.9161 | 71.58% | 1 | 0 | 80.02% | 0% | 0 | 0.024597 | 1 | 2.3755 | 0.05843 | Medium | Medium | Medium | 2203 | 2257 | 0.024597 | 12.6575 | 0.1418%
WOODWARD 2108R2860 | WOODWARD 2108 | FRESNO | 11.5924 | 40.5433 | 94.73% | 0 | 1 | 52.86% | 0% | 0 | 0.024579 | 1 | 1.6377 | 0.040253 | Medium | Medium | Low | 2534 | 2258 | 0.024579 | 12.6329 | 0.1415%
MARIPOSA 2102CB | MARIPOSA 2102 | YOSEMITE | 6.6916 | 39.3684 | 36.18% | 1 | 6 | 63.39% | 0% | 0 | 0.024571 | 1 | 2.5225 | 0.061982 | Medium | Medium | Medium | 2152 | 2259 | 0.024571 | 12.6083 | 0.1412%
HATTON 1101CB | HATTON 1101 | CENTRAL COAST | 1.5925 | 10 | 10.22% | 4 | 0 | 100% | 0% | 0 | 0.024551 | 1 | 3.0516 | 0.074918 | Medium | Medium | Medium | 1984 | 2260 | 0.024551 | 12.5838 | 0.141%
NORTH BRANCH 110111158 | NORTH BRANCH 1101 | STOCKTON | 11.9363 | 47.5829 | 78.02% | 0 | 4 | 41.95% | 0% | 0 | 0.024519 | 1 | 2.528 | 0.061986 | Medium | Medium | Medium | 2151 | 2261 | 0.024519 | 12.5592 | 0.1407%
FITCH MOUNTAIN 111324550 | FITCH MOUNTAIN 1113 | SONOMA | 9.0741 | 56.5036 | 70.47% | 3 | 1 | 41.6% | 1.605% | 0 | 0.024475 | 1 | 2.7468 | 0.067228 | Medium | Medium | Medium | 2070 | 2262 | 0.024475 | 12.5347 | 0.1404%
HIGGINS 110391052 | HIGGINS 1103 | SIERRA | 0.64834 | 10 | 100% | 0 | 0 | 84.24% | 0% | 0 | 0.024449 | 1 | 3.3175 | 0.081108 | Medium | Medium | High | 1924 | 2263 | 0.024449 | 12.5102 | 0.1402%
TYLER 11051704 | TYLER 1105 | NORTH VALLEY | 12.5832 | 29.6218 | 100% | 0 | 8 | 27.35% | 0% | 0 | 0.024427 | 1 | 1.7997 | 0.043962 | Medium | Medium | Low | 2463 | 2264 | 0.024427 | 12.4858 | 0.1399%
CLEAR LAKE 11011302 | CLEAR LAKE 1101 | HUMBOLDT | 6.3736 | 19.3133 | 67.28% | 0 | 7 | 36.56% | 0% | 0 | 0.024377 | 1 | 3.0552 | 0.074476 | Medium | Medium | Medium | 1991 | 2265 | 0.024377 | 12.4613 | 0.1396%
CURTIS 1701CB | CURTIS 1701 | YOSEMITE | 8.5475 | 34.1417 | 57.96% | 1 | 9 | 68.5% | 0% | 0 | 0.024359 | 1 | 3.1577 | 0.076918 | Medium | Medium | High | 1963 | 2266 | 0.024359 | 12.437 | 0.1393%
KIRKER 2104442850 | KIRKER 2104 | DIABLO | 5.4258 | 10 | 43.23% | 0 | 4 | 95.36% | 0% | 0 | 0.024306 | 1 | 3.3502 | 0.081427 | Medium | Medium | High | 1921 | 2267 | 0.024306 | 12.4126 | 0.1391%
CORNING 110135974 | CORNING 1101 | NORTH VALLEY | 0.83179 | 10 | 47.68% | 0 | 0 | 100% | 0% | 0 | 0.02429 | 1 | 1.1214 | 0.027239 | Medium | Medium | Low | 2832 | 2268 | 0.02429 | 12.3883 | 0.1388%
SAN JUSTO 110136902 | SAN JUSTO 1101 | CENTRAL COAST | 12.1218 | 14.481 | 44.84% | 5 | 5 | 82.09% | 0% | 0 | 0.024262 | 1 | 2.0985 | 0.050914 | Medium | Medium | Low | 2335 | 2269 | 0.024262 | 12.364 | 0.1385%
BELL 11085703 | BELL 1108 | SIERRA | 4.5516 | 23.9501 | 96.07% | 0 | 3 | 57.44% | 0% | 0 | 0.024235 | 1 | 2.8219 | 0.068387 | Medium | Medium | Medium | 2058 | 2270 | 0.024235 | 12.3397 | 0.1382%
LUCERNE 110693293 | LUCERNE 1106 | HUMBOLDT | 0.10086 | 10 | 100% | 0 | 0 | 83.34% | 0% | 0 | 0.024233 | 1 | 2.1005 | 0.050903 | Medium | Medium | Low | 2336 | 2271 | 0.024233 | 12.3155 | 0.138%
PIT NO 1 110170952 | PIT NO 1 1101 | NORTH VALLEY | 1.5383 | 10 | 71.41% | 1 | 1 | 89.97% | 0% | 0 | 0.024193 | 1 | 2.3158 | 0.056027 | Medium | Medium | Medium | 2243 | 2272 | 0.024193 | 12.2913 | 0.1377%
DUNBAR 1102CB | DUNBAR 1102 | SONOMA | 8.263 | 20.9256 | 44.14% | 4 | 14 | 47.06% | 0% | 0 | 0.024179 | 1 | 3.2378 | 0.078286 | Medium | Medium | High | 1950 | 2273 | 0.024179 | 12.2671 | 0.1374%
KONOCTI 1108CB | KONOCTI 1108 | HUMBOLDT | 6.6517 | 32.6717 | 74.99% | 0 | 6 | 75.6% | 0% | 0 | 0.024164 | 1 | 2.5096 | 0.060644 | Medium | Medium | Medium | 2169 | 2274 | 0.024164 | 12.2429 | 0.1372%
CAYETANO 2109CB | CAYETANO 2109 | MISSION | 13.0515 | 49.7043 | 30.41% | 0 | 2 | 76.33% | 3.645% | 1 | 0.024131 | 1 | 3.2891 | 0.079369 | Medium | Medium | High | 1940 | 2275 | 0.024131 | 12.2187 | 0.1369%
SAN RAFAEL 1105534 | SAN RAFAEL 1105 | NORTH BAY | 1.348 | 10 | 81.92% | 3 | 4 | 85.31% | 0% | 0 | 0.024098 | 1 | 3.3132 | 0.079842 | Medium | Medium | High | 1935 | 2276 | 0.024098 | 12.1946 | 0.1366%
MORAGA 1104N532R | MORAGA 1104 | DIABLO | 4.4858 | 10 | 51.34% | 1 | 5 | 97.29% | 0% | 0 | 0.023997 | 1 | 3.8388 | 0.09212 | Medium | Medium | High | 1817 | 2277 | 0.023997 | 12.1705 | 0.1363%
RADUM 1105MR282 | RADUM 1105 | MISSION | 2.1702 | 17.1089 | 66.03% | 0 | 5 | 34.07% | 37.28% | 0 | 0.023926 | 1 | 3.184 | 0.076183 | Medium | Medium | High | 1970 | 2278 | 0.023926 | 12.1465 | 0.1361%
SAN LUIS OBISPO 1104V14 | SAN LUIS OBISPO 1104 | LOS PADRES | 9.0673 | 22.9917 | 13.75% | 0 | 2 | 100% | 0% | 0 | 0.023923 | 1 | 2.7612 | 0.066057 | Medium | Medium | Medium | 2087 | 2279 | 0.023923 | 12.1226 | 0.1358%
MORRO BAY 1102W22 | MORRO BAY 1102 | LOS PADRES | 4.8943 | 10 | 4.74% | 0 | 3 | 47.35% | 0% | 0 | 0.023875 | 1 | 4.2269 | 0.10092 | Medium | Medium | High | 1763 | 2280 | 0.023875 | 12.0987 | 0.1355%
TASSAJARA 210883368 | TASSAJARA 2108 | DIABLO | 0.069317 | 10 | 0% | 0 | 0 | 1.551% | 100% | 0 | 0.023873 | 1 | 3.3752 | 0.080577 | Medium | Medium | High | 1930 | 2281 | 0.023873 | 12.0748 | 0.1353%
PINE GROVE 110152088 | PINE GROVE 1101 | STOCKTON | 2.528 | 10 | 68.63% | 1 | 3 | 100% | 0% | 0 | 0.023865 | 1 | 2.3857 | 0.056935 | Medium | Medium | Medium | 2228 | 2282 | 0.023865 | 12.0509 | 0.135%
OLETA 110151740 | OLETA 1101 | STOCKTON | 9.506 | 52.4452 | 97.68% | 1 | 4 | 44.88% | 0% | 0 | 0.023833 | 1 | 2.5749 | 0.061369 | Medium | Medium | Medium | 2161 | 2283 | 0.023833 | 12.0271 | 0.1347%
PETALUMA C 110948000 | PETALUMA C 1109 | SONOMA | 8.7103 | 40.2232 | 37.55% | 1 | 9 | 65.59% | 0% | 0 | 0.023831 | 1 | 3.0235 | 0.072053 | Medium | Medium | Medium | 2017 | 2284 | 0.023831 | 12.0032 | 0.1345%
LAURELES 1111CB | LAURELES 1111 | CENTRAL COAST | 7.0885 | 26.8874 | 36.65% | 2 | 3 | 86.44% | 0% | 0 | 0.023775 | 1 | 2.8474 | 0.067697 | Medium | Medium | Medium | 2064 | 2285 | 0.023775 | 11.9794 | 0.1342%
SPRUCE 0401BR316 | SPRUCE 0401 | EAST BAY | 4.123 | 16.22 | 7.456% | 3 | 5 | 100% | 23.86% | 0 | 0.02375 | 1 | 4.8945 | 0.11624 | Medium | Medium | High | 1683 | 2286 | 0.02375 | 11.9556 | 0.1339%
HALSEY 11012412 | HALSEY 1101 | SIERRA | 5.321 | 10 | 60.58% | 4 | 4 | 100% | 0% | 0 | 0.023732 | 1 | 2.3931 | 0.056792 | Medium | Medium | Medium | 2230 | 2287 | 0.023732 | 11.9319 | 0.1337%
CORRAL 110359770 | CORRAL 1103 | STOCKTON | 4.5619 | 12.4013 | 100% | 1 | 1 | 62.81% | 0% | 0 | 0.02373 | 1 | 3.6376 | 0.086321 | Medium | Medium | High | 1865 | 2288 | 0.02373 | 11.9081 | 0.1334%
CAMP EVERS 2106CB | CAMP EVERS 2106 | CENTRAL COAST | 0.018997 | 10 | 0% | 0 | 0 | 0.8166% | 100% | 0 | 0.023702 | 1 | 3.5428 | 0.083973 | Medium | Medium | High | 1887 | 2289 | 0.023702 | 11.8844 | 0.1331%
DIAMOND SPRINGS 110740353 | DIAMOND SPRINGS 1107 | SIERRA | 2.2415 | 10 | 74.48% | 1 | 0 | 87.31% | 0% | 0 | 0.023671 | 1 | 2.5112 | 0.059443 | Medium | Medium | Medium | 2188 | 2290 | 0.023671 | 11.8607 | 0.1329%
BIG RIVER 11011052 | BIG RIVER 1101 | HUMBOLDT | 2.9737 | 10 | 0% | 7 | 11 | 77.62% | 0% | 0 | 0.023654 | 1 | 3.2182 | 0.076123 | Medium | Medium | High | 1972 | 2291 | 0.023654 | 11.837 | 0.1326%
CLOVERDALE 1102CB | CLOVERDALE 1102 | SONOMA | 0.24384 | 33.3215 | 52.03% | 0 | 0 | 8.095% | 59.2% | 0 | 0.023631 | 1 | 2.4298 | 0.05742 | Medium | Medium | Medium | 2217 | 2292 | 0.023631 | 11.8134 | 0.1323%
PANOCHE 11034036 | PANOCHE 1103 | YOSEMITE | 8.0979 | 77.6294 | 100% | 0 | 1 | 32.26% | 0% | 0 | 0.023574 | 1 | 0.7002 | 0.016507 | Medium | Medium | Low | 3072 | 2293 | 0.023574 | 11.7897 | 0.1321%
HIGHLANDS 1104CB | HIGHLANDS 1104 | HUMBOLDT | 4.6735 | 10 | 74.7% | 0 | 2 | 57.1% | 0% | 0 | 0.023554 | 1 | 3.1769 | 0.074829 | Medium | Medium | High | 1987 | 2294 | 0.023554 | 11.7662 | 0.1318%
OAKLAND J 1102CR102 | OAKLAND J 1102 | EAST BAY | 0.53101 | 10 | 70.62% | 0 | 2 | 100% | 0% | 0 | 0.023454 | 1 | 3.3241 | 0.077962 | Medium | Medium | High | 1954 | 2295 | 0.023454 | 11.7426 | 0.1316%
MORGAN HILL 2105XR564 | MORGAN HILL 2105 | SAN JOSE | 5.4316 | 26.8638 | 49.46% | 0 | 4 | 75.02% | 0% | 0 | 0.023443 | 1 | 2.4719 | 0.057948 | Medium | Medium | Medium | 2209 | 2296 | 0.023443 | 11.7192 | 0.1313%
CASTRO VALLEY 1108CB | CASTRO VALLEY 1108 | MISSION | 1.4946 | 10 | 6.175% | 3 | 1 | 53.21% | 52.04% | 0 | 0.023442 | 1 | 3.5736 | 0.083772 | Medium | Medium | High | 1890 | 2297 | 0.023442 | 11.6957 | 0.131%
POSO MOUNTAIN 21012181 | POSO MOUNTAIN 2101 | KERN | 17.1051 | 10 | 29.81% | 0 | 0 | 71.06% | 0% | 0 | 0.023433 | 1 | 2.214 | 0.051879 | Medium | Medium | Low | 2311 | 2298 | 0.023433 | 11.6723 | 0.1308%
CAL WATER 1102920714 | CAL WATER 1102 | KERN | 2.9688 | 76.5947 | 100% | 0 | 0 | 34.42% | 0% | 0 | 0.023426 | 1 | 2.1754 | 0.05096 | Medium | Medium | Low | 2330 | 2299 | 0.023426 | 11.6488 | 0.1305%
LUCERNE 11062327 | LUCERNE 1106 | HUMBOLDT | 0.98526 | 10 | 100% | 0 | 1 | 77.76% | 0% | 0 | 0.02342 | 1 | 3.2861 | 0.07696 | Medium | Medium | High | 1962 | 2300 | 0.02342 | 11.6254 | 0.1302%
LAURELES 11122768 | LAURELES 1112 | CENTRAL COAST | 6.6363 | 20.652 | 26.91% | 3 | 3 | 82.17% | 0% | 0 | 0.023337 | 1 | 2.0172 | 0.047076 | Medium | Medium | Low | 2399 | 2301 | 0.023337 | 11.602 | 0.13%
SUNOL 1101MR297 | SUNOL 1101 | MISSION | 6.0465 | 17.8817 | 28.91% | 0 | 2 | 100% | 17.46% | 0 | 0.023322 | 1 | 2.3616 | 0.055077 | Medium | Medium | Medium | 2258 | 2302 | 0.023322 | 11.5787 | 0.1297%
PIT NO 1 11011552 | PIT NO 1 1101 | NORTH VALLEY | 9.8425 | 12.4749 | 95.95% | 1 | 1 | 37.18% | 0% | 0 | 0.023212 | 1 | 1.0048 | 0.023324 | Medium | Medium | Low | 2929 | 2303 | 0.023212 | 11.5553 | 0.1295%
MC ARTHUR 11011490 | MC ARTHUR 1101 | NORTH VALLEY | 9.1248 | 10 | 79.7% | 0 | 4 | 60.48% | 0% | 0 | 0.02318 | 1 | 0.49873 | 0.01156 | Medium | Medium | Low | 3139 | 2304 | 0.02318 | 11.5321 | 0.1292%
JOLON 11027070 | JOLON 1102 | CENTRAL COAST | 4.9443 | 33.893 | 99.18% | 0 | 3 | 30.01% | 0% | 0 | 0.023132 | 1 | 1.3548 | 0.031339 | Medium | Medium | Low | 2742 | 2305 | 0.023132 | 11.5089 | 0.1289%
SUNOL 11018721 | SUNOL 1101 | MISSION | 2.3818 | 51.7237 | 49.03% | 0 | 1 | 76.51% | 0% | 0 | 0.0231 | 1 | 1.6423 | 0.037937 | Medium | Medium | Low | 2584 | 2306 | 0.0231 | 11.4858 | 0.1287%
HIGGINS 1103995672 | HIGGINS 1103 | SIERRA | 2.7769 | 10 | 100% | 1 | 1 | 48.24% | 0% | 0 | 0.02307 | 1 | 3.2961 | 0.076042 | Medium | Medium | High | 1975 | 2307 | 0.02307 | 11.4627 | 0.1284%
HOLLISTER 21044403 | HOLLISTER 2104 | CENTRAL COAST | 5.3706 | 82.3816 | 100% | 0 | 0 | 28.45% | 0% | 0 | 0.022969 | 1 | 2.2884 | 0.052563 | Medium | Medium | Medium | 2300 | 2308 | 0.022969 | 11.4396 | 0.1282%
GEYSERVILLE 110137454 | GEYSERVILLE 1101 | SONOMA | 7.5123 | 58.2774 | 62.29% | 0 | 0 | 62.62% | 0% | 0 | 0.022967 | 1 | 1.4474 | 0.033242 | Medium | Medium | Low | 2695 | 2309 | 0.022967 | 11.4167 | 0.1279%
DESCHUTES 11041370 | DESCHUTES 1104 | NORTH VALLEY | 12.2362 | 19.7367 | 98.52% | 1 | 1 | 55.17% | 0% | 0 | 0.022854 | 1 | 2.271 | 0.051901 | Medium | Medium | Medium | 2310 | 2310 | 0.022854 | 11.3937 | 0.1276%
MENLO 11037902 | MENLO 1103 | PENINSULA | 11.6802 | 47.4802 | 20.98% | 8 | 4 | 71.01% | 0% | 0 | 0.022804 | 1 | 2.779 | 0.063373 | Medium | Medium | Medium | 2125 | 2311 | 0.022804 | 11.3709 | 0.1274%
GEYSERVILLE 1101166 | GEYSERVILLE 1101 | SONOMA | 11.044 | 32.5571 | 62.6% | 3 | 3 | 68.81% | 0% | 0 | 0.022773 | 1 | 1.478 | 0.033658 | Medium | Medium | Low | 2688 | 2312 | 0.022773 | 11.3481 | 0.1271%
BANGOR 110180670 | BANGOR 1101 | NORTH VALLEY | 14.7472 | 18.2405 | 76% | 0 | 1 | 89.02% | 0% | 0 | 0.02277 | 1 | 3.21 | 0.073094 | Medium | Medium | High | 2004 | 2313 | 0.02277 | 11.3253 | 0.1269%
PEORIA 17048040 | PEORIA 1704 | YOSEMITE | 8.9787 | 41.627 | 97.88% | 2 | 3 | 34.87% | 0% | 0 | 0.02277 | 1 | 0.58079 | 0.013225 | Medium | Medium | Low | 3122 | 2314 | 0.02277 | 11.3025 | 0.1266%
SISQUOC 1102M54 | SISQUOC 1102 | LOS PADRES | 17.0931 | 11.3388 | 62.6% | 1 | 3 | 56.95% | 1.375% | 0 | 0.022753 | 1 | 0.99426 | 0.022622 | Medium | Medium | Low | 2952 | 2315 | 0.022753 | 11.2797 | 0.1264%
ELK 11011298 | ELK 1101 | HUMBOLDT | 13.5042 | 33.0971 | 18.55% | 6 | 11 | 83.72% | 0% | 0 | 0.022711 | 1 | 1.1193 | 0.025419 | Medium | Medium | Low | 2873 | 2316 | 0.022711 | 11.257 | 0.1261%
SILVERADO 2102714 | SILVERADO 2102 | NORTH BAY | 4.37 | 45.4785 | 19.37% | 4 | 5 | 38.82% | 6.698% | 0 | 0.022688 | 1 | 3.4176 | 0.077537 | Medium | Medium | High | 1959 | 2317 | 0.022688 | 11.2343 | 0.1259%
HALF MOON BAY 11036065 | HALF MOON BAY 1103 | PENINSULA | 6.2488 | 59.5208 | 36.98% | 1 | 1 | 91.2% | 0% | 0 | 0.02267 | 1 | 3.3733 | 0.076472 | Medium | Medium | High | 1969 | 2318 | 0.02267 | 11.2116 | 0.1256%
PEORIA 17019811 | PEORIA 1701 | YOSEMITE | 5.5301 | 39.6322 | 92.09% | 0 | 0 | 62.43% | 0% | 0 | 0.022586 | 1 | 1.223 | 0.027623 | Medium | Medium | Low | 2821 | 2319 | 0.022586 | 11.1889 | 0.1253%
UKIAH 111129452 | UKIAH 1111 | HUMBOLDT | 3.6752 | 77.2683 | 100% | 0 | 0 | 30.05% | 0% | 0 | 0.022547 | 1 | 2.4814 | 0.055947 | Medium | Medium | Medium | 2245 | 2320 | 0.022547 | 11.1663 | 0.1251%
PEORIA 170176030 | PEORIA 1701 | YOSEMITE | 5.4729 | 32.855 | 62.69% | 0 | 1 | 88.26% | 0% | 0 | 0.022385 | 1 | 1.0774 | 0.024117 | Medium | Medium | Low | 2906 | 2321 | 0.022385 | 11.1438 | 0.1248%
SUMMIT 11022302 | SUMMIT 1102 | SIERRA | 1.4575 | 10 | 25.54% | 1 | 4 | 100% | 0% | 0 | 0.022343 | 1 | 0.59618 | 0.01332 | Medium | Medium | Low | 3121 | 2322 | 0.022343 | 11.1214 | 0.1246%
ARCATA 11211206 | ARCATA 1121 | HUMBOLDT | 6.629 | 50.041 | 6.756% | 12 | 6 | 42.25% | 0% | 0 | 0.022231 | 1 | 2.4644 | 0.054786 | Medium | Medium | Medium | 2263 | 2323 | 0.022231 | 11.0991 | 0.1243%
BIG MEADOWS 21012248 | BIG MEADOWS 2101 | NORTH VALLEY | 9.1467 | 42.3693 | 7.268% | 0 | 1 | 100% | 0% | 0 | 0.022222 | 1 | 2.056 | 0.045688 | Medium | Medium | Low | 2427 | 2324 | 0.022222 | 11.0768 | 0.1241%
STAFFORD 11021019 | STAFFORD 1102 | NORTH BAY | 0.54264 | 10 | 100% | 0 | 0 | 74.36% | 0% | 0 | 0.022194 | 1 | 2.9612 | 0.065721 | Medium | Medium | Medium | 2091 | 2325 | 0.022194 | 11.0546 | 0.1238%
GOLDTREE 1108CB | GOLDTREE 1108 | LOS PADRES | 2.5563 | 36.4917 | 29.18% | 2 | 3 | 52.35% | 0% | 0 | 0.022193 | 1 | 2.85 | 0.063249 | Medium | Medium | Medium | 2127 | 2326 | 0.022193 | 11.0324 | 0.1236%
MC ARTHUR 11011544 | MC ARTHUR 1101 | NORTH VALLEY | 14.33 | 61.0373 | 66.86% | 0 | 1 | 51.35% | 0% | 0 | 0.022186 | 1 | 0.18317 | 0.0040638 | Medium | Medium | Low | 3175 | 2327 | 0.022186 | 11.0102 | 0.1233%
HALF MOON BAY 11036018 | HALF MOON BAY 1103 | PENINSULA | 14.4915 | 43.0242 | 18.48% | 5 | 3 | 79.35% | 0% | 0 | 0.022185 | 1 | 2.2501 | 0.049917 | Medium | Medium | Medium | 2354 | 2328 | 0.022185 | 10.988 | 0.1231%
PALMER 1101M82 | PALMER 1101 | LOS PADRES | 10.3483 | 48.0186 | 61.68% | 0 | 5 | 69.3% | 0% | 0 | 0.022153 | 1 | 1.7614 | 0.03902 | Medium | Medium | Low | 2559 | 2329 | 0.022153 | 10.9658 | 0.1228%
BIG RIVER 11012183 | BIG RIVER 1101 | HUMBOLDT | 2.6396 | 37.6233 | 33.84% | 1 | 4 | 100% | 0% | 0 | 0.022133 | 1 | 2.3018 | 0.050945 | Medium | Medium | Medium | 2331 | 2330 | 0.022133 | 10.9437 | 0.1226%
BELL 1109CB | BELL 1109 | SIERRA | 13.433 | 10 | 50.92% | 4 | 3 | 76.11% | 0% | 0 | 0.022099 | 1 | 2.7321 | 0.060377 | Medium | Medium | Medium | 2177 | 2331 | 0.022099 | 10.9216 | 0.1224%
SOLEDAD 21027048 | SOLEDAD 2102 | CENTRAL COAST | 16.945 | 59.8739 | 88.98% | 0 | 0 | 48.94% | 0% | 0 | 0.022097 | 1 | 2.316 | 0.051176 | Medium | Medium | Medium | 2327 | 2332 | 0.022097 | 10.8995 | 0.1221%
KONOCTI 11084039 | KONOCTI 1108 | HUMBOLDT | 1.6026 | 10 | 100% | 0 | 2 | 69.54% | 0% | 0 | 0.022058 | 1 | 2.6616 | 0.05871 | Medium | Medium | Medium | 2200 | 2333 | 0.022058 | 10.8774 | 0.1219%
KERCKHOFF 1101R308 | KERCKHOFF 1101 | YOSEMITE | 3.8623 | 40.5798 | 35.11% | 0 | 3 | 100% | 0% | 0 | 0.022056 | 1 | 1.9946 | 0.043992 | Medium | Medium | Low | 2462 | 2334 | 0.022056 | 10.8553 | 0.1216%
LUCERNE 11031663 | LUCERNE 1103 | HUMBOLDT | 1.2106 | 10 | 52.73% | 0 | 6 | 100% | 0% | 0 | 0.022038 | 1 | 3.735 | 0.082313 | Medium | Medium | High | 1911 | 2335 | 0.022038 | 10.8333 | 0.1214%
BRUNSWICK 111061602 | BRUNSWICK 1110 | SIERRA | 9.4416 | 27.4436 | 52.21% | 4 | 4 | 73.99% | 0% | 0 | 0.022016 | 1 | 2.7653 | 0.06088 | Medium | Medium | Medium | 2167 | 2336 | 0.022016 | 10.8112 | 0.1211%
MC ARTHUR 110138998 | MC ARTHUR 1101 | NORTH VALLEY | 11.0305 | 56.1464 | 63.76% | 0 | 2 | 67.61% | 0% | 0 | 0.021999 | 1 | 0.56625 | 0.012457 | Medium | Medium | Low | 3132 | 2337 | 0.021999 | 10.7892 | 0.1209%
CURTIS 170356972 | CURTIS 1703 | YOSEMITE | 8.4449 | 49.5291 | 11.99% | 0 | 2 | 100% | 0.5389% | 1 | 0.02188 | 1 | 1.6045 | 0.035106 | Medium | Medium | Low | 2648 | 2338 | 0.02188 | 10.7672 | 0.1206%
RIO DELL 11028852 | RIO DELL 1102 | HUMBOLDT | 3.7546 | 61.6723 | 39.96% | 1 | 3 | 79.33% | 0% | 0 | 0.021849 | 1 | 2.4325 | 0.053146 | Medium | Medium | Medium | 2287 | 2339 | 0.021849 | 10.7453 | 0.1204%
SAN CARLOS 11049052 | SAN CARLOS 1104 | PENINSULA | 4.4833 | 10 | 33.62% | 0 | 5 | 90.23% | 0% | 0 | 0.021835 | 1 | 4.3823 | 0.095688 | Medium | Medium | High | 1793 | 2340 | 0.021835 | 10.7235 | 0.1201%
CAYETANO 2109MR572 | CAYETANO 2109 | MISSION | 8.1822 | 10 | 47.67% | 0 | 2 | 66.51% | 19.49% | 0 | 0.021821 | 1 | 2.7701 | 0.060448 | Medium | Medium | Medium | 2174 | 2341 | 0.021821 | 10.7016 | 0.1199%
WOODSIDE 11049030 | WOODSIDE 1104 | PENINSULA | 2.2354 | 10 | 77.85% | 0 | 2 | 86.64% | 0% | 0 | 0.021812 | 1 | 4.57 | 0.099682 | Medium | Medium | High | 1773 | 2342 | 0.021812 | 10.6798 | 0.1196%
VIEJO 22012064 | VIEJO 2201 | CENTRAL COAST | 0.87679 | 10 | 42.79% | 0 | 3 | 100% | 0% | 0 | 0.021793 | 1 | 3.6566 | 0.079688 | Low | Low | High | 1936 | 2343 | 0.021793 | 10.658 | 0.1194%
SALT SPRINGS 21013116 | SALT SPRINGS 2101 | STOCKTON | 0.70592 | 10 | 100% | 0 | 1 | 70.33% | 0% | 0 | 0.021776 | 1 | 0.56292 | 0.012258 | Low | Low | Low | 3135 | 2344 | 0.021776 | 10.6362 | 0.1192%
FOOTHILL 110299432 | FOOTHILL 1102 | LOS PADRES | 0.73004 | 62.5798 | 100% | 0 | 3 | 16.66% | 0% | 0 | 0.021721 | 1 | 3.048 | 0.066206 | Low | Low | Medium | 2085 | 2345 | 0.021721 | 10.6144 | 0.1189%
FORT BRAGG A 11013100 | FORT BRAGG A 1101 | HUMBOLDT | 12.9058 | 10 | 7.343% | 8 | 11 | 88.01% | 0% | 0 | 0.021681 | 1 | 2.5776 | 0.055885 | Low | Low | Medium | 2248 | 2346 | 0.021681 | 10.5927 | 0.1187%
JESSUP 11013383 | JESSUP 1101 | NORTH VALLEY | 1.283 | 10 | 88.48% | 0 | 0 | 68.06% | 0% | 0 | 0.021667 | 1 | 2.2493 | 0.048737 | Low | Low | Medium | 2372 | 2347 | 0.021667 | 10.571 | 0.1184%
REDBUD 1102510 | REDBUD 1102 | HUMBOLDT | 6.0638 | 23.833 | 59.82% | 2 | 2 | 75.22% | 0% | 0 | 0.02163 | 1 | 2.6321 | 0.056933 | Low | Low | Medium | 2229 | 2348 | 0.02163 | 10.5494 | 0.1182%
SAN RAFAEL 1104802 | SAN RAFAEL 1104 | NORTH BAY | 7.826 | 10 | 18.94% | 3 | 4 | 72.62% | 0% | 0 | 0.021588 | 1 | 4.3551 | 0.094017 | Low | Low | High | 1805 | 2349 | 0.021588 | 10.5277 | 0.1179%
CMC 1101CB | CMC 1101 | LOS PADRES | 2.0609 | 25.5297 | 52.24% | 0 | 0 | 100% | 0% | 0 | 0.021532 | 1 | 2.6866 | 0.057849 | Low | Low | Medium | 2210 | 2350 | 0.021532 | 10.5061 | 0.1177%
MENDOCINO 1101450 | MENDOCINO 1101 | HUMBOLDT | 5.6815 | 36.3951 | 100% | 0 | 2 | 30.28% | 3.061% | 1 | 0.021431 | 1 | 1.8346 | 0.039318 | Low | Low | Low | 2553 | 2351 | 0.021431 | 10.4846 | 0.1175%
COTATI 110361736 | COTATI 1103 | SONOMA | 9.9372 | 78.8786 | 12.09% | 0 | 11 | 59.74% | 0% | 0 | 0.02142 | 1 | 2.3776 | 0.050928 | Low | Low | Medium | 2333 | 2352 | 0.02142 | 10.4632 | 0.1172%
OTTER 1101440 | OTTER 1101 | CENTRAL COAST | 8.556 | 21.3917 | 0.8557% | 24 | 4 | 77.84% | 0% | 0 | 0.021414 | 1 | 2.508 | 0.053708 | Low | Low | Medium | 2276 | 2353 | 0.021414 | 10.4418 | 0.117%
SARATOGA 1106LC24 | SARATOGA 1106 | DE ANZA | 6.2415 | 10 | 42.44% | 3 | 7 | 55.48% | 10.64% | 0 | 0.021404 | 1 | 3.8778 | 0.083 | Low | Low | High | 1899 | 2354 | 0.021404 | 10.4203 | 0.1167%
HIGHLANDS 110484640 | HIGHLANDS 1104 | HUMBOLDT | 0.56405 | 10 | 72.8% | 1 | 1 | 76.24% | 0% | 0 | 0.021388 | 1 | 2.8868 | 0.061742 | Low | Low | Medium | 2156 | 2355 | 0.021388 | 10.3989 | 0.1165%
PEORIA 1704CB | PEORIA 1704 | YOSEMITE | 8.3627 | 39.95 | 39.21% | 0 | 3 | 93.61% | 0% | 0 | 0.021324 | 1 | 2.0061 | 0.042779 | Low | Low | Low | 2481 | 2356 | 0.021324 | 10.3776 | 0.1163%
RED BLUFF 1101 | RED BLUFF 1101 | NORTH VALLEY | 0.18711 | 22.4749 | 100% | 0 | 0 | 61.69% | 0% | 0 | 0.021308 | 1 | 1.7689 | 0.037691 | Low | Low | Low | 2590 | 2357 | 0.021308 | 10.3562 | 0.116%
HAMILTON BRANCH 11012082 | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.6281 | 32.2338 | 100% | 1 | 0 | 53.18% | 0% | 0 | 0.021199 | 1 | 3.5753 | 0.075794 | Low | Low | High | 1977 | 2358 | 0.021199 | 10.3349 | 0.1158%
OLEMA 110175686 | OLEMA 1101 | NORTH BAY | 3.5949 | 80.3245 | 25.14% | 0 | 0 | 69.82% | 0% | 0 | 0.021165 | 1 | 1.9507 | 0.041286 | Low | Low | Low | 2511 | 2359 | 0.021165 | 10.3137 | 0.1155%
DUNBAR 1102528 | DUNBAR 1102 | SONOMA | 3.4638 | 30.5853 | 54.13% | 1 | 3 | 85.5% | 0% | 0 | 0.021137 | 1 | 3.6876 | 0.077945 | Low | Low | High | 1955 | 2360 | 0.021137 | 10.2926 | 0.1153%
PEORIA 170510580 | PEORIA 1705 | YOSEMITE | 6.4351 | 24.7232 | 93.54% | 1 | 4 | 54.9% | 0% | 0 | 0.021125 | 1 | 2.4388 | 0.051522 | Low | Low | Medium | 2320 | 2361 | 0.021125 | 10.2714 | 0.1151%
COTTONWOOD 11029026 | COTTONWOOD 1102 | NORTH VALLEY | 14.1835 | 17.7686 | 84.41% | 1 | 2 | 58.01% | 0% | 0 | 0.021122 | 1 | 1.7609 | 0.037192 | Low | Low | Low | 2606 | 2362 | 0.021122 | 10.2503 | 0.1148%
PUTAH CREEK 11028352 | PUTAH CREEK 1102 | SACRAMENTO | 4.7179 | 43.9192 | 97.12% | 0 | 4 | 40.06% | 0% | 0 | 0.021102 | 1 | 1.961 | 0.041381 | Low | Low | Low | 2509 | 2363 | 0.021102 | 10.2292 | 0.1146%
ORINDA 04013442 | ORINDA 0401 | DIABLO | 4.9574 | 14.2459 | 5.153% | 4 | 12 | 73.89% | 0% | 0 | 0.021076 | 1 | 3.2283 | 0.068041 | Low | Low | High | 2061 | 2364 | 0.021076 | 10.2081 | 0.1144%
BURNEY 11011322 | BURNEY 1101 | NORTH VALLEY | 16.3381 | 29.8396 | 61.19% | 0 | 0 | 87.48% | 0% | 0 | 0.021071 | 1 | 1.5564 | 0.032794 | Low | Low | Low | 2705 | 2365 | 0.021071 | 10.187 | 0.1141%
JOLON 11027040 | JOLON 1102 | CENTRAL COAST | 20.3578 | 63.5106 | 29.02% | 0 | 1 | 88.79% | 0% | 0 | 0.02105 | 1 | 1.5142 | 0.031874 | Low | Low | Low | 2729 | 2366 | 0.02105 | 10.1659 | 0.1139%
HATTON 11012026 | HATTON 1101 | CENTRAL COAST | 6.3396 | 38.9334 | 46.88% | 0 | 2 | 62.03% | 0% | 0 | 0.021035 | 1 | 3.1737 | 0.06676 | Low | Low | High | 2078 | 2367 | 0.021035 | 10.1449 | 0.1137%
LAURELES 1112438 | LAURELES 1112 | CENTRAL COAST | 5.2403 | 57.3236 | 0.9038% | 0 | 0 | 91.32% | 0% | 0 | 0.020992 | 1 | 2.2111 | 0.046416 | Low | Low | Low | 2408 | 2368 | 0.020992 | 10.1238 | 0.1134%
EDES 1112CR308 | EDES 1112 | EAST BAY | 3.5907 | 10 | 15.92% | 2 | 4 | 100% | 0% | 0 | 0.020943 | 1 | 3.1965 | 0.066942 | Low | Low | High | 2075 | 2369 | 0.020943 | 10.1028 | 0.1132%
PEORIA 170590374 | PEORIA 1705 | YOSEMITE | 3.6064 | 10 | 81.75% | 0 | 1 | 81.35% | 0% | 0 | 0.020938 | 1 | 2.8737 | 0.060168 | Low | Low | Medium | 2180 | 2370 | 0.020938 | 10.0819 | 0.1129%
CLAY 11037124 | CLAY 1103 | STOCKTON | 8.9452 | 50.0578 | 97.24% | 0 | 1 | 27.91% | 0% | 0 | 0.020936 | 1 | 2.4969 | 0.052275 | Low | Low | Medium | 2303 | 2371 | 0.020936 | 10.061 | 0.1127%
SYCAMORE CREEK 1111CB | SYCAMORE CREEK 1111 | NORTH VALLEY | 8.3942 | 56.8563 | 45.31% | 1 | 3 | 47.06% | 0% | 0 | 0.020907 | 1 | 2.8652 | 0.059903 | Low | Low | Medium | 2185 | 2372 | 0.020907 | 10.04 | 0.1125%
SAN MIGUEL 1104R66 | SAN MIGUEL 1104 | LOS PADRES | 8.3967 | 54.4532 | 99.05% | 0 | 3 | 18.97% | 0% | 0 | 0.020883 | 1 | 1.0549 | 0.02203 | Low | Low | Low | 2962 | 2373 | 0.020883 | 10.0191 | 0.1122%
COVELO 110137328 | COVELO 1101 | HUMBOLDT | 3.9213 | 85.1621 | 100% | 0 | 0 | 16.63% | 0% | 0 | 0.020839 | 1 | 1.2015 | 0.025038 | Low | Low | Low | 2881 | 2374 | 0.020839 | 9.9982 | 0.112%
JOLON 1103CB | JOLON 1103 | CENTRAL COAST | 14.8367 | 53.4685 | 41.31% | 0 | 2 | 82.37% | 0% | 0 | 0.020833 | 1 | 0.78084 | 0.016268 | Low | Low | Low | 3075 | 2375 | 0.020833 | 9.9774 | 0.1118%
GEYSERVILLE 110135492 | GEYSERVILLE 1101 | SONOMA | 8.4529 | 69.0353 | 85.9% | 0 | 0 | 39.22% | 0% | 0 | 0.020833 | 1 | 1.6734 | 0.034862 | Low | Low | Low | 2654 | 2376 | 0.020833 | 9.9566 | 0.1115%
HOLLISTER 2102855412 | HOLLISTER 2102 | CENTRAL COAST | 25.5091 | 59.8315 | 42.36% | 0 | 0 | 81.28% | 0% | 0 | 0.020819 | 1 | 2.4248 | 0.050482 | Low | Low | Medium | 2344 | 2377 | 0.020819 | 9.9357 | 0.1113%
IGNACIO 1104450582 | IGNACIO 1104 | NORTH BAY | 3.8063 | 10 | 29.85% | 0 | 4 | 90.17% | 0% | 0 | 0.020738 | 1 | 2.9935 | 0.062078 | Low | Low | Medium | 2145 | 2378 | 0.020738 | 9.9149 | 0.1111%
PANORAMA 11021342 | PANORAMA 1102 | NORTH VALLEY | 11.6409 | 39.043 | 100% | 0 | 1 | 45.41% | 0% | 0 | 0.020716 | 1 | 1.9444 | 0.04028 | Low | Low | Low | 2532 | 2379 | 0.020716 | 9.8942 | 0.1108%
ELK 110191336 | ELK 1101 | HUMBOLDT | 7.8266 | 12.5917 | 0% | 14 | 5 | 92.25% | 0% | 0 | 0.020708 | 1 | 1.7508 | 0.036255 | Low | Low | Low | 2624 | 2380 | 0.020708 | 9.8735 | 0.1106%
RISING RIVER 1101CB | RISING RIVER 1101 | NORTH VALLEY | 9.43 | 10 | 88.75% | 1 | 2 | 70.58% | 0% | 0 | 0.020612 | 1 | 1.5535 | 0.03202 | Low | Low | Low | 2725 | 2381 | 0.020612 | 9.8528 | 0.1104%
COARSEGOLD 210410030 | COARSEGOLD 2104 | YOSEMITE | 15.7445 | 10.7109 | 33.01% | 0 | 3 | 88.51% | 0% | 0 | 0.020603 | 1 | 1.786 | 0.036797 | Low | Low | Low | 2618 | 2382 | 0.020603 | 9.8321 | 0.1101%
FROGTOWN 170236870 | FROGTOWN 1702 | STOCKTON | 2.2467 | 10 | 88.34% | 0 | 2 | 72.13% | 0% | 0 | 0.020592 | 1 | 1.8354 | 0.037794 | Low | Low | Low | 2587 | 2383 | 0.020592 | 9.8115 | 0.1099%
PANOCHE 11034016 | PANOCHE 1103 | YOSEMITE | 2.3488 | 61.1971 | 100% | 0 | 0 | 18.31% | 0% | 0 | 0.020566 | 1 | 0.46613 | 0.0095864 | Low | Low | Low | 3149 | 2384 | 0.020566 | 9.7909 | 0.1097%
JOLON 11027004 | JOLON 1102 | CENTRAL COAST | 5.4816 | 47.887 | 100% | 0 | 0 | 27.2% | 0% | 0 | 0.020525 | 1 | 1.2884 | 0.026445 | Low | Low | Low | 2853 | 2385 | 0.020525 | 9.7704 | 0.1095%
WILLITS 1103696 | WILLITS 1103 | HUMBOLDT | 6.5774 | 41.2479 | 62.23% | 0 | 3 | 69.69% | 0% | 0 | 0.020487 | 1 | 1.7628 | 0.036115 | Low | Low | Low | 2627 | 2386 | 0.020487 | 9.7499 | 0.1092%
RALSTON 11022028 | RALSTON 1102 | PENINSULA | 2.1344 | 10 | 38.62% | 0 | 5 | 92.94% | 0% | 0 | 0.020485 | 1 | 3.746 | 0.076737 | Low | Low | High | 1966 | 2387 | 0.020485 | 9.7294 | 0.109%
NEWBURG 113190242 | NEWBURG 1131 | HUMBOLDT | 3.4074 | 35.576 | 50.59% | 5 | 2 | 78.12% | 0% | 0 | 0.020383 | 1 | 2.6054 | 0.053106 | Low | Low | Medium | 2288 | 2388 | 0.020383 | 9.7089 | 0.1088%
CALAVERAS CEMENT 1101CB | CALAVERAS CEMENT 1101 | STOCKTON | 11.1338 | 14.2948 | 43.85% | 0 | 4 | 60.61% | 0% | 0 | 0.02038 | 1 | 2.3984 | 0.048881 | Low | Low | Medium | 2369 | 2389 | 0.02038 | 9.6885 | 0.1085%
PANORAMA 11021526 | PANORAMA 1102 | NORTH VALLEY | 11.8848 | 23.1923 | 53.04% | 0 | 7 | 67.25% | 0% | 0 | 0.020361 | 1 | 1.5446 | 0.03145 | Low | Low | Low | 2736 | 2390 | 0.020361 | 9.6681 | 0.1083%
NEWBURG 1133CB | NEWBURG 1133 | HUMBOLDT | 3.7712 | 37.8079 | 38.51% | 2 | 0 | 41.21% | 0% | 0 | 0.020349 | 1 | 2.7759 | 0.056485 | Low | Low | Medium | 2235 | 2391 | 0.020349 | 9.6478 | 0.1081%
LOGAN CREEK 21022226 | LOGAN CREEK 2102 | NORTH VALLEY | 3.7103 | 86.8404 | 100% | 0 | 1 | 10.78% | 0% | 0 | 0.020313 | 1 | 0.2575 | 0.0052305 | Low | Low | Low | 3170 | 2392 | 0.020313 | 9.6274 | 0.1079%
MONTICELLO 1101CB | MONTICELLO 1101 | NORTH BAY | 0.56293 | 10 | 41.7% | 0 | 0 | 100% | 0% | 0 | 0.020311 | 1 | 2.3219 | 0.047161 | Low | Low | Medium | 2396 | 2393 | 0.020311 | 9.6071 | 0.1076%
GREENBRAE 1103434 | GREENBRAE 1103 | NORTH BAY | 0.79973 | 10 | 68.06% | 2 | 1 | 55.44% | 2.889% | 0 | 0.020293 | 1 | 5.0736 | 0.10296 | Low | Low | High | 1746 | 2394 | 0.020293 | 9.5868 | 0.1074%
KONOCTI 1102948 | KONOCTI 1102 | HUMBOLDT | 6.065 | 30.1749 | 46.64% | 1 | 1 | 78.59% | 0% | 0 | 0.02028 | 1 | 2.9925 | 0.060688 | Low | Low | Medium | 2168 | 2395 | 0.02028 | 9.5665 | 0.1072%
REDBUD 1101400 | REDBUD 1101 | HUMBOLDT | 1.0177 | 10 | 44.91% | 0 | 5 | 100% | 0% | 0 | 0.020268 | 1 | 2.632 | 0.053346 | Low | Low | Medium | 2284 | 2396 | 0.020268 | 9.5462 | 0.1069%
RIDGE 0401CB | RIDGE 0401 | EAST BAY | 2.662 | 10 | 10.22% | 3 | 4 | 100% | 0% | 0 | 0.02026 | 1 | 4.0693 | 0.082444 | Low | Low | High | 1908 | 2397 | 0.02026 | 9.5259 | 0.1067%
VIEJO 2201CB | VIEJO 2201 | CENTRAL COAST | 4.5324 | 10 | 12.86% | 16 | 6 | 89.76% | 0% | 0 | 0.020254 | 1 | 3.8798 | 0.078583 | Low | Low | High | 1946 | 2398 | 0.020254 | 9.5057 | 0.1065%
CLOVERDALE 1102262 | CLOVERDALE 1102 | SONOMA | 1.062 | 28.5735 | 25.58% | 2 | 0 | 19.75% | 47.85% | 0 | 0.020231 | 1 | 2.3861 | 0.048274 | Low | Low | Medium | 2375 | 2399 | 0.020231 | 9.4854 | 0.1063%
DESCHUTES 11041582 | DESCHUTES 1104 | NORTH VALLEY | 6.3252 | 21.3729 | 99.66% | 0 | 1 | 41.84% | 0% | 0 | 0.020198 | 1 | 2.3806 | 0.048084 | Low | Low | Medium | 2377 | 2400 | 0.020198 | 9.4652 | 0.106%
BIG RIVER 1101954 | BIG RIVER 1101 | HUMBOLDT | 7.7476 | 11.9193 | 13.02% | 4 | 10 | 95.19% | 0% | 0 | 0.020135 | 1 | 2.6074 | 0.0525 | Low | Low | Medium | 2301 | 2401 | 0.020135 | 9.445 | 0.1058%
PLACER 1103CB | PLACER 1103 | SIERRA | 12.2492 | 28.3994 | 44.01% | 5 | 11 | 41.67% | 0% | 0 | 0.020134 | 1 | 2.9879 | 0.060157 | Low | Low | Medium | 2181 | 2402 | 0.020134 | 9.4249 | 0.1056%
GARBERVILLE 110139524 | GARBERVILLE 1101 | HUMBOLDT | 5.5428 | 59.5329 | 86.83% | 1 | 2 | 35.93% | 0% | 0 | 0.020129 | 1 | 1.2425 | 0.02501 | Low | Low | Low | 2883 | 2403 | 0.020129 | 9.4047 | 0.1054%
BURNEY 11012402 | BURNEY 1101 | NORTH VALLEY | 1.4308 | 10 | 91.1% | 2 | 2 | 38.13% | 0% | 0 | 0.020105 | 1 | 1.914 | 0.038481 | Low | Low | Low | 2571 | 2404 | 0.020105 | 9.3846 | 0.1051%
SARATOGA 1106LC22 | SARATOGA 1106 | DE ANZA | 7.1525 | 10 | 35.66% | 5 | 5 | 86.79% | 0% | 0 | 0.020092 | 1 | 4.16 | 0.083584 | Low | Low | High | 1892 | 2405 | 0.020092 | 9.3645 | 0.1049%
CUYAMA 1103622728 | CUYAMA 1103 | KERN | 2.3769 | 95 | 100% | 0 | 0 | 6.184% | 0% | 0 | 0.02009 | 1 | 0.49944 | 0.010034 | Low | Low | Low | 3146 | 2406 | 0.02009 | 9.3444 | 0.1047%
PUEBLO 1104640 | PUEBLO 1104 | NORTH BAY | 1.0277 | 10 | 45.71% | 1 | 4 | 32.52% | 0% | 0 | 0.02008 | 1 | 3.1015 | 0.06228 | Low | Low | High | 2140 | 2407 | 0.02008 | 9.3243 | 0.1045%
WISE 1101CB | WISE 1101 | SIERRA | 5.8467 | 15.7551 | 45.1% | 2 | 5 | 65.21% | 0% | 0 | 0.01999 | 1 | 2.7196 | 0.054364 | Low | Low | Medium | 2269 | 2408 | 0.01999 | 9.3042 | 0.1042%
OLETA 11022642 | OLETA 1102 | STOCKTON | 4.6588 | 10 | 54.08% | 0 | 0 | 100% | 0.8976% | 1 | 0.01998 | 1 | 1.5701 | 0.031371 | Low | Low | Low | 2738 | 2409 | 0.01998 | 9.2842 | 0.104%
NORTH DUBLIN 2101CB | NORTH DUBLIN 2101 | MISSION | 3.6193 | 54.6377 | 4.667% | 0 | 3 | 91.94% | 0% | 0 | 0.019955 | 1 | 3.6341 | 0.072519 | Low | Low | High | 2011 | 2410 | 0.019955 | 9.2643 | 0.1038%
HALF MOON BAY 110375550 | HALF MOON BAY 1103 | PENINSULA | 1.1869 | 54.8487 | 75.08% | 0 | 0 | 53.23% | 0% | 0 | 0.019917 | 1 | 3.6734 | 0.073163 | Low | Low | High | 2003 | 2411 | 0.019917 | 9.2443 | 0.1036%
LLAGAS 2101XR586 | LLAGAS 2101 | SAN JOSE | 4.744 | 52.8351 | 95.8% | 0 | 1 | 35.43% | 0% | 0 | 0.019912 | 1 | 2.4913 | 0.049608 | Low | Low | Medium | 2359 | 2412 | 0.019912 | 9.2244 | 0.1033%
DIAMOND SPRINGS 110699658 | DIAMOND SPRINGS 1106 | SIERRA | 5.0702 | 10 | 100% | 3 | 3 | 39.71% | 0% | 0 | 0.019909 | 1 | 2.5296 | 0.050364 | Low | Low | Medium | 2345 | 2413 | 0.019909 | 9.2045 | 0.1031%
PEORIA 170567898 | PEORIA 1705 | YOSEMITE | 5.0246 | 20.73 | 47.42% | 1 | 2 | 80.37% | 0% | 0 | 0.0199 | 1 | 2.9757 | 0.059217 | Low | Low | Medium | 2193 | 2414 | 0.0199 | 9.1846 | 0.1029%
CURTIS 170320240 | CURTIS 1703 | YOSEMITE | 0.18021 | 10 | 100% | 0 | 0 | 63.08% | 0% | 0 | 0.019869 | 1 | 3.9035 | 0.077558 | Low | Low | High | 1957 | 2415 | 0.019869 | 9.1647 | 0.1027%
MC ARTHUR 11011492 | MC ARTHUR 1101 | NORTH VALLEY | 9.6647 | 34.9258 | 100% | 1 | 0 | 31.38% | 0% | 0 | 0.019862 | 1 | 0.62862 | 0.012486 | Low | Low | Low | 3131 | 2416 | 0.019862 | 9.1448 | 0.1024%
CABRILLO 11031437 | CABRILLO 1103 | LOS PADRES | 3.2446 | 37.9706 | 72.77% | 0 | 0 | 66.31% | 0% | 0 | 0.019849 | 1 | 1.7318 | 0.034374 | Low | Low | Low | 2671 | 2417 | 0.019849 | 9.1249 | 0.1022%
ROB ROY 210412596 | ROB ROY 2104 | CENTRAL COAST | 7.6393 | 10 | 59% | 3 | 3 | 72.22% | 0.5428% | 0 | 0.019837 | 1 | 3.2178 | 0.063833 | Low | Low | High | 2116 | 2418 | 0.019837 | 9.1051 | 0.102%
OLETA 11021228 | OLETA 1102 | STOCKTON | 8.954 | 36.1723 | 96.93% | 0 | 0 | 20.75% | 0% | 0 | 0.019803 | 1 | 2.2184 | 0.043932 | Low | Low | Low | 2464 | 2419 | 0.019803 | 9.0853 | 0.1018%
VIEJO 22019490 | VIEJO 2201 | CENTRAL COAST | 2.0007 | 10 | 0.3261% | 11 | 5 | 93.15% | 0% | 0 | 0.019802 | 1 | 3.5624 | 0.070542 | Low | Low | High | 2034 | 2420 | 0.019802 | 9.0655 | 0.1016%
HALSEY 11015731 | HALSEY 1101 | SIERRA | 3.1252 | 10 | 52.17% | 0 | 1 | 100% | 0% | 0 | 0.019797 | 1 | 2.4133 | 0.047777 | Low | Low | Medium | 2384 | 2421 | 0.019797 | 9.0457 | 0.1013%
HARTLEY 11014710 | HARTLEY 1101 | HUMBOLDT | 1.5005 | 10 | 52.07% | 1 | 0 | 100% | 0% | 0 | 0.019631 | 1 | 3.0245 | 0.059375 | Low | Low | Medium | 2189 | 2422 | 0.019631 | 9.0259 | 0.1011%
CURTIS 1703CB | CURTIS 1703 | YOSEMITE | 8.4941 | 16.7987 | 53.44% | 0 | 2 | 77.88% | 0% | 0 | 0.0196 | 1 | 3.2518 | 0.063736 | Low | Low | High | 2121 | 2423 | 0.0196 | 9.0062 | 0.1009%
MESA 1101M86 | MESA 1101 | LOS PADRES | 10.0922 | 14.4649 | 78% | 0 | 7 | 48.4% | 0% | 0 | 0.019529 | 1 | 2.0981 | 0.040973 | Low | Low | Low | 2518 | 2424 | 0.019529 | 8.9866 | 0.1007%
CLAYTON 2215W531R | CLAYTON 2215 | DIABLO | 5.8394 | 49.6313 | 12.81% | 0 | 3 | 54.09% | 19.44% | 0 | 0.019385 | 1 | 3.4465 | 0.06681 | Low | Low | High | 2077 | 2425 | 0.019385 | 8.9671 | 0.1005%
PERRY 1101W12 | PERRY 1101 | LOS PADRES | 4.7971 | 10 | 2.793% | 5 | 9 | 75.15% | 0% | 0 | 0.01938 | 1 | 3.5539 | 0.068874 | Low | Low | High | 2054 | 2426 | 0.01938 | 8.9477 | 0.1002%
WYANDOTTE 11101954 | WYANDOTTE 1110 | NORTH VALLEY | 13.197 | 10 | 59.13% | 1 | 2 | 48.67% | 0% | 0 | 0.019374 | 1 | 3.5192 | 0.068181 | Low | Low | High | 2059 | 2427 | 0.019374 | 8.9283 | 0.1%
LAURELES 11112028 | LAURELES 1111 | CENTRAL COAST | 8.3353 | 36.2004 | 23.71% | 6 | 1 | 95.28% | 0% | 0 | 0.019345 | 1 | 2.5818 | 0.049946 | Low | Low | Medium | 2352 | 2428 | 0.019345 | 8.909 | 0.09981%
MARIPOSA 2101CB | MARIPOSA 2101 | YOSEMITE | 6.8371 | 18.7213 | 60.25% | 1 | 4 | 63.95% | 0% | 0 | 0.019315 | 1 | 2.3032 | 0.044486 | Low | Low | Medium | 2449 | 2429 | 0.019315 | 8.8896 | 0.09959%
POINT MORETTI 110112122 | POINT MORETTI 1101 | CENTRAL COAST | 6.8941 | 11.1834 | 26.23% | 14 | 1 | 86.19% | 0% | 0 | 0.019307 | 1 | 1.689 | 0.03261 | Low | Low | Low | 2707 | 2430 | 0.019307 | 8.8703 | 0.09937%
EDENVALE 2107D80 | EDENVALE 2107 | SAN JOSE | 0.032033 | 71.8938 | 0% | 0 | 0 | 100% | 0% | 0 | 0.019259 | 1 | 2.7189 | 0.052363 | Low | Low | Medium | 2302 | 2431 | 0.019259 | 8.851 | 0.09916%
OILFIELDS 1103N64 | OILFIELDS 1103 | CENTRAL COAST | 9.7922 | 31.0491 | 50.23% | 0 | 4 | 78.14% | 0% | 0 | 0.019257 | 1 | 2.4471 | 0.047124 | Low | Low | Medium | 2398 | 2432 | 0.019257 | 8.8317 | 0.09894%
SUMMIT 110158642 | SUMMIT 1101 | SIERRA | 1.9126 | 10 | 32.51% | 0 | 1 | 100% | 0% | 0 | 0.019248 | 1 | 1.1597 | 0.022322 | Low | Low | Low | 2957 | 2433 | 0.019248 | 8.8125 | 0.09872%
LONE TREE 210521210 | LONE TREE 2105 | DIABLO | 9.5646 | 10 | 95.6% | 0 | 2 | 59.2% | 0% | 0 | 0.019234 | 1 | 3.2356 | 0.062233 | Low | Low | High | 2141 | 2434 | 0.019234 | 8.7932 | 0.09851%
HOLLISTER 21054724 | HOLLISTER 2105 | CENTRAL COAST | 3.4016 | 78.2881 | 100% | 0 | 0 | 12.91% | 0% | 0 | 0.019187 | 1 | 0.89991 | 0.017267 | Low | Low | Low | 3059 | 2435 | 0.019187 | 8.774 | 0.09829%
NARROWS 210551582 | NARROWS 2105 | SIERRA | 9.5263 | 10 | 48.26% | 0 | 1 | 100% | 0% | 0 | 0.019181 | 1 | 1.9413 | 0.037237 | Low | Low | Low | 2605 | 2436 | 0.019181 | 8.7548 | 0.09808%
HAMILTON BRANCH 1101CB | HAMILTON BRANCH 1101 | NORTH VALLEY | 4.2457 | 27.0953 | 61.17% | 1 | 2 | 74.22% | 0% | 0 | 0.019168 | 1 | 3.3969 | 0.065111 | Low | Low | High | 2099 | 2437 | 0.019168 | 8.7356 | 0.09786%
HIGHLANDS 110275140 | HIGHLANDS 1102 | HUMBOLDT | 8.7915 | 33.3312 | 88.94% | 0 | 4 | 43.92% | 0% | 0 | 0.019109 | 1 | 3.4168 | 0.065291 | Low | Low | High | 2095 | 2438 | 0.019109 | 8.7165 | 0.09765%
HOLLISTER 21064004 | HOLLISTER 2106 | CENTRAL COAST | 7.4093 | 64.8641 | 59.97% | 2 | 1 | 36.51% | 0% | 0 | 0.019101 | 1 | 2.6827 | 0.051242 | Low | Low | Medium | 2325 | 2439 | 0.019101 | 8.6973 | 0.09744%
PIT NO 1 1101CB | PIT NO 1 1101 | NORTH VALLEY | 6.4361 | 10 | 29.8% | 1 | 2 | 98.02% | 0% | 0 | 0.019097 | 1 | 1.7847 | 0.034083 | Low | Low | Low | 2680 | 2440 | 0.019097 | 8.6782 | 0.09722%
EDES 1112CR282 | EDES 1112 | EAST BAY | 3.4204 | 10 | 46.24% | 0 | 3 | 83.7% | 0% | 0 | 0.019097 | 1 | 3.2289 | 0.061662 | Low | Low | High | 2159 | 2441 | 0.019097 | 8.6591 | 0.09701%
GLENN 11012012 | GLENN 1101 | NORTH VALLEY | 2.3498 | 85 | 100% | 0 | 0 | 7.814% | 0% | 0 | 0.01909 | 1 | 0.59338 | 0.011328 | Low | Low | Low | 3140 | 2442 | 0.01909 | 8.64 | 0.09679%
DIAMOND SPRINGS 1107CB | DIAMOND SPRINGS 1107 | SIERRA | 7.4424 | 10 | 84.55% | 2 | 3 | 62.03% | 0.42% | 0 | 0.019073 | 1 | 2.4518 | 0.046763 | Low | Low | Medium | 2402 | 2443 | 0.019073 | 8.621 | 0.09658%
VIEJO 22029120 | VIEJO 2202 | CENTRAL COAST | 1.9636 | 10 | 20.08% | 9 | 3 | 26.52% | 0% | 0 | 0.019059 | 1 | 3.9065 | 0.074456 | Low | Low | High | 1992 | 2444 | 0.019059 | 8.6019 | 0.09637%
STELLING 111060090 | STELLING 1110 | DE ANZA | 6.0088 | 10 | 51.27% | 4 | 1 | 91.55% | 0% | 0 | 0.019051 | 1 | 3.3845 | 0.064479 | Low | Low | High | 2109 | 2445 | 0.019051 | 8.5828 | 0.09615%
MORGAN HILL 210940000 | MORGAN HILL 2109 | SAN JOSE | 1.7684 | 10 | 99.47% | 0 | 0 | 59.08% | 0% | 0 | 0.019023 | 1 | 3.095 | 0.058876 | Low | Low | High | 2198 | 2446 | 0.019023 | 8.5638 | 0.09594%
ALTO 11251256 | ALTO 1125 | NORTH BAY | 1.3805 | 10 | 15.55% | 1 | 0 | 94.69% | 19.69% | 0 | 0.018993 | 1 | 3.7099 | 0.070461 | Low | Low | High | 2038 | 2447 | 0.018993 | 8.5448 | 0.09573%
CLARK ROAD 11022044 | CLARK ROAD 1102 | NORTH VALLEY | 5.5376 | 29.0224 | 29.16% | 0 | 3 | 44.24% | 0% | 0 | 0.018991 | 1 | 1.5914 | 0.030222 | Low | Low | Low | 2768 | 2448 | 0.018991 | 8.5258 | 0.09551%
CABRILLO 110420711 | CABRILLO 1104 | LOS PADRES | 0.18254 | 10 | 100% | 0 | 0 | 58.32% | 0% | 0 | 0.01896 | 1 | 3.8254 | 0.072532 | Low | Low | High | 2010 | 2449 | 0.01896 | 8.5068 | 0.0953%
HORSESHOE 110150140 | HORSESHOE 1101 | SIERRA | 3.7526 | 10 | 69.76% | 1 | 4 | 60.16% | 0% | 0 | 0.018953 | 1 | 3.7991 | 0.072006 | Low | Low | High | 2019 | 2450 | 0.018953 | 8.4878 | 0.09509%
ELECTRA 1102CB | ELECTRA 1102 | STOCKTON | 2.62 | 68.1508 | 1.119% | 0 | 0 | 100% | 0% | 0 | 0.018952 | 1 | 1.606 | 0.030437 | Low | Low | Low | 2762 | 2451 | 0.018952 | 8.4689 | 0.09488%
MENDOCINO 110131322 | MENDOCINO 1101 | HUMBOLDT | 4.4175 | 35.3153 | 77.6% | 2 | 7 | 15.42% | 0% | 0 | 0.01894 | 1 | 2.7133 | 0.05139 | Low | Low | Medium | 2323 | 2452 | 0.01894 | 8.4499 | 0.09466%
ELK CREEK 11012228 | ELK CREEK 1101 | NORTH VALLEY | 3.1012 | 51.6707 | 100% | 0 | 0 | 29.46% | 0% | 0 | 0.018884 | 1 | 1.7101 | 0.032292 | Low | Low | Low | 2717 | 2453 | 0.018884 | 8.431 | 0.09445%
FORT BRAGG A 11014698 | FORT BRAGG A 1101 | HUMBOLDT | 7.9299 | 10 | 15.57% | 8 | 8 | 100% | 0% | 0 | 0.018863 | 1 | 2.4544 | 0.046298 | Low | Low | Medium | 2416 | 2454 | 0.018863 | 8.4121 | 0.09424%
POINT MORETTI 11015076 | POINT MORETTI 1101 | CENTRAL COAST | 7.1634 | 15.8606 | 16.59% | 11 | 1 | 79.19% | 0% | 0 | 0.018862 | 1 | 2.0481 | 0.03863 | Low | Low | Low | 2568 | 2455 | 0.018862 | 8.3932 | 0.09403%
FORT BRAGG A 1102816 | FORT BRAGG A 1102 | HUMBOLDT | 2.5631 | 10 | 6.097% | 3 | 2 | 100% | 0% | 0 | 0.018806 | 1 | 2.916 | 0.054838 | Low | Low | Medium | 2261 | 2456 | 0.018806 | 8.3744 | 0.09382%
MADISON 210137082 | MADISON 2101 | SACRAMENTO | 0.85819 | 87.1383 | 100% | 0 | 0 | 4.662% | 0% | 0 | 0.018775 | 1 | 1.0976 | 0.020608 | Low | Low | Low | 2990 | 2457 | 0.018775 | 8.3555 | 0.09361%
EMERALD LAKE 04028872 | EMERALD LAKE 0402 | PENINSULA | 4.147 | 10 | 19.14% | 0 | 11 | 74.11% | 0% | 0 | 0.018758 | 1 | 5.0483 | 0.094694 | Low | Low | High | 1801 | 2458 | 0.018758 | 8.3368 | 0.0934%
WOODSIDE 11049116 | WOODSIDE 1104 | PENINSULA | 1.063 | 10 | 91% | 2 | 5 | 24.81% | 0% | 0 | 0.018746 | 1 | 4.5156 | 0.08465 | Low | Low | High | 1877 | 2459 | 0.018746 | 8.318 | 0.09319%
FITCH MOUNTAIN 1113583202 | FITCH MOUNTAIN 1113 | SONOMA | 3.5047 | 64.5439 | 56.95% | 1 | 2 | 36.51% | 0% | 0 | 0.018742 | 1 | 2.4393 | 0.045717 | Low | Low | Medium | 2426 | 2460 | 0.018742 | 8.2993 | 0.09298%
CLARKSVILLE 2109CB | CLARKSVILLE 2109 | SIERRA | 1.031 | 10 | 7.581% | 0 | 1 | 91.6% | 7.913% | 0 | 0.018738 | 1 | 3.5876 | 0.067224 | Low | Low | High | 2071 | 2461 | 0.018738 | 8.2805 | 0.09277%
OTTER 11022012 | OTTER 1102 | CENTRAL COAST | 9.1781 | 41.691 | 0% | 3 | 4 | 91.18% | 0% | 0 | 0.018558 | 1 | 1.3664 | 0.025359 | Low | Low | Low | 2875 | 2462 | 0.018558 | 8.2618 | 0.09256%
CAMPHORA 110177978 | CAMPHORA 1101 | CENTRAL COAST | 1.4665 | 83.8291 | 100% | 0 | 0 | 5.721% | 0% | 0 | 0.018555 | 1 | 2.1797 | 0.040444 | Low | Low | Low | 2530 | 2463 | 0.018555 | 8.2432 | 0.09235%
MAXWELL 11053008 | MAXWELL 1105 | SACRAMENTO | 1.6684 | 73.9154 | 100% | 0 | 0 | 12.26% | 0% | 0 | 0.018513 | 1 | 0.80874 | 0.014972 | Low | Low | Low | 3102 | 2464 | 0.018513 | 8.2247 | 0.09214%
ELECTRA 11024756 | ELECTRA 1102 | STOCKTON | 8.9008 | 26.6489 | 52.03% | 0 | 4 | 75.65% | 0% | 0 | 0.018513 | 1 | 2.637 | 0.048818 | Low | Low | Medium | 2371 | 2465 | 0.018513 | 8.2062 | 0.09193%
OAK 0401CB | OAK 0401 | EAST BAY | 4.3198 | 10 | 1.236% | 2 | 7 | 79.82% | 0% | 0 | 0.018493 | 1 | 5.1168 | 0.094626 | Low | Low | High | 1802 | 2466 | 0.018493 | 8.1876 | 0.09172%
SILVERADO 21023010 | SILVERADO 2102 | NORTH BAY | 3.5284 | 66.7535 | 84.82% | 0 | 1 | 27.23% | 0% | 0 | 0.018454 | 1 | 1.79 | 0.033032 | Low | Low | Low | 2699 | 2467 | 0.018454 | 8.1692 | 0.09152%
RINCON 1101CB | RINCON 1101 | SONOMA | 2.1293 | 20.6419 | 39.27% | 1 | 4 | 43.97% | 11.03% | 0 | 0.018447 | 1 | 3.2011 | 0.05905 | Low | Low | High | 2194 | 2468 | 0.018447 | 8.1507 | 0.09131%
ZACA 1101Y70 | ZACA 1101 | LOS PADRES | 5.1032 | 39.0808 | 69.39% | 0 | 1 | 58.75% | 0% | 0 | 0.018441 | 1 | 1.1363 | 0.020954 | Low | Low | Low | 2983 | 2469 | 0.018441 | 8.1323 | 0.0911%
SUMMIT 11016627 | SUMMIT 1101 | SIERRA | 0.56142 | 10 | 45.61% | 0 | 0 | 100% | 0% | 0 | 0.01839 | 1 | 1.4632 | 0.026909 | Low | Low | Low | 2840 | 2470 | 0.01839 | 8.1138 | 0.0909%
LUCERNE 110647198 | LUCERNE 1106 | HUMBOLDT | 3.6836 | 20.6629 | 59.47% | 1 | 7 | 65.28% | 0% | 0 | 0.018382 | 1 | 2.2339 | 0.041063 | Low | Low | Medium | 2516 | 2471 | 0.018382 | 8.0954 | 0.09069%
LOS OSITOS 21037468 | LOS OSITOS 2103 | CENTRAL COAST | 1.0746 | 71.3986 | 100% | 0 | 0 | 13.23% | 0% | 0 | 0.018377 | 1 | 2.3508 | 0.043201 | Low | Low | Medium | 2472 | 2472 | 0.018377 | 8.077 | 0.09049%
GREEN VALLEY 210112106 | GREEN VALLEY 2101 | CENTRAL COAST | 6.3447 | 10 | 54.91% | 5 | 0 | 33.81% | 31.75% | 0 | 0.018337 | 1 | 3.5176 | 0.064501 | Low | Low | High | 2108 | 2473 | 0.018337 | 8.0587 | 0.09028%
TRES PINOS 11114032 | TRES PINOS 1111 | CENTRAL COAST | 0.10269 | 70 | 100% | 0 | 0 | 0.5446% | 0% | 0 | 0.018321 | 1 | 1.4487 | 0.026542 | Low | Low | Low | 2849 | 2474 | 0.018321 | 8.0403 | 0.09007%
FROGTOWN 1701CB | FROGTOWN 1701 | STOCKTON | 9.8066 | 35.2796 | 29.68% | 0 | 4 | 86.99% | 0% | 0 | 0.018301 | 1 | 2.3489 | 0.042988 | Low | Low | Medium | 2477 | 2475 | 0.018301 | 8.022 | 0.08987%
UKIAH 1114822 | UKIAH 1114 | HUMBOLDT | 1.3145 | 67.0871 | 100% | 0 | 3 | 9.397% | 0% | 0 | 0.018289 | 1 | 2.3374 | 0.042749 | Low | Low | Medium | 2484 | 2476 | 0.018289 | 8.0037 | 0.08966%
PERRY 110185870 | PERRY 1101 | LOS PADRES | 13.2734 | 34.8685 | 24.59% | 0 | 0 | 72.93% | 0% | 0 | 0.018257 | 1 | 2.8229 | 0.051539 | Low | Low | Medium | 2319 | 2477 | 0.018257 | 7.9854 | 0.08946%
WYANDOTTE 110213044 | WYANDOTTE 1102 | NORTH VALLEY | 3.9523 | 10 | 53.49% | 0 | 6 | 66.87% | 0% | 0 | 0.018256 | 1 | 2.4807 | 0.045288 | Low | Low | Medium | 2433 | 2478 | 0.018256 | 7.9672 | 0.08925%
UKIAH 1115CB | UKIAH 1115 | HUMBOLDT | 4.3061 | 10 | 64.92% | 0 | 1 | 67.93% | 0% | 0 | 0.018255 | 1 | 2.8014 | 0.051141 | Low | Low | Medium | 2328 | 2479 | 0.018255 | 7.9489 | 0.08905%
LAS AROMAS 0401LA401R | LAS AROMAS 0401 | DIABLO | 3.6951 | 10 | 0.309% | 3 | 6 | 93.3% | 0% | 0 | 0.018243 | 1 | 3.3031 | 0.060258 | Low | Low | High | 2179 | 2480 | 0.018243 | 7.9306 | 0.08885%
RACETRACK 17032553 | RACETRACK 1703 | YOSEMITE | 1.2971 | 10 | 100% | 0 | 1 | 52.29% | 0% | 0 | 0.018242 | 1 | 2.8066 | 0.051198 | Low | Low | Medium | 2326 | 2481 | 0.018242 | 7.9124 | 0.08864%
LAMONT 11024222 | LAMONT 1102 | KERN | 0.50063 | 85 | 100% | 0 | 0 | 3.081% | 0% | 0 | 0.018222 | 1 | 1.0005 | 0.01823 | Low | Low | Low | 3039 | 2482 | 0.018222 | 7.8942 | 0.08844%
WYANDOTTE 11095607 | WYANDOTTE 1109 | NORTH VALLEY | 3.9588 | 10 | 93.75% | 0 | 0 | 59.06% | 0% | 0 | 0.018157 | 1 | 2.7246 | 0.049471 | Low | Low | Medium | 2362 | 2483 | 0.018157 | 7.8759 | 0.08823%
PEORIA 170413490 | PEORIA 1704 | YOSEMITE | 4.0441 | 23.9004 | 44.53% | 0 | 0 | 76.49% | 0% | 0 | 0.018107 | 1 | 2.6351 | 0.047714 | Low | Low | Medium | 2385 | 2484 | 0.018107 | 7.8578 | 0.08803%
SAN MIGUEL 1104R58 | SAN MIGUEL 1104 | LOS PADRES | 9.7655 | 26.7568 | 99.18% | 0 | 1 | 40.61% | 0% | 0 | 0.018077 | 1 | 1.6551 | 0.029918 | Low | Low | Low | 2776 | 2485 | 0.018077 | 7.8397 | 0.08783%
VIEJO 22019698 | VIEJO 2201 | CENTRAL COAST | 0.90136 | 10 | 0% | 2 | 3 | 100% | 0% | 0 | 0.018036 | 1 | 3.8848 | 0.070067 | Low | Low | High | 2044 | 2486 | 0.018036 | 7.8216 | 0.08762%
SAN RAFAEL 110168970 | SAN RAFAEL 1101 | NORTH BAY | 1.3404 | 10 | 17.09% | 0 | 0 | 31.9% | 46.84% | 0 | 0.018013 | 1 | 4.4995 | 0.08105 | Low | Low | High | 1925 | 2487 | 0.018013 | 7.8036 | 0.08742%
POSO MOUNTAIN 2103CB | POSO MOUNTAIN 2103 | KERN | 2.3192 | 10 | 26.74% | 0 | 0 | 100% | 0% | 0 | 0.017995 | 1 | 2.7452 | 0.0494 | Low | Low | Medium | 2363 | 2488 | 0.017995 | 7.7856 | 0.08722%
FRUITLAND 11418860 | FRUITLAND 1141 | HUMBOLDT | 2.4992 | 72.7282 | 25.93% | 4 | 0 | 65.81% | 0% | 0 | 0.01798 | 1 | 1.5096 | 0.027143 | Low | Low | Low | 2836 | 2489 | 0.01798 | 7.7676 | 0.08702%
TAR FLAT 0401CB | TAR FLAT 0401 | YOSEMITE | 3.4825 | 10 | 7.176% | 1 | 2 | 94.76% | 17.84% | 1 | 0.017966 | 1 | 3.199 | 0.057473 | Low | Low | High | 2215 | 2490 | 0.017966 | 7.7496 | 0.08682%
GIRVAN 110280726 | GIRVAN 1102 | NORTH VALLEY | 5.9722 | 10 | 96.6% | 0 | 5 | 31.79% | 0% | 0 | 0.017957 | 1 | 2.6748 | 0.048032 | Low | Low | Medium | 2378 | 2491 | 0.017957 | 7.7316 | 0.08662%
RAWSON 110385334 | RAWSON 1103 | NORTH VALLEY | 2.3781 | 53.7562 | 78.76% | 0 | 1 | 24.97% | 0% | 0 | 0.017954 | 1 | 1.5952 | 0.028642 | Low | Low | Low | 2805 | 2492 | 0.017954 | 7.7137 | 0.08641%
SAUSALITO 1102410 | SAUSALITO 1102 | NORTH BAY | 1.0698 | 10 | 84.58% | 1 | 1 | 48.49% | 0% | 0 | 0.017913 | 1 | 3.5643 | 0.063846 | Low | Low | High | 2115 | 2493 | 0.017913 | 7.6957 | 0.08621%
TULE POWER HOUSE 1101CB | TULE POWER HOUSE 1101 | FRESNO | 4.0927 | 57.029 | 3.215% | 0 | 0 | 100% | 0% | 0 | 0.01789 | 1 | 1.3019 | 0.023291 | Low | Low | Low | 2932 | 2494 | 0.01789 | 7.6778 | 0.08601%
PEORIA 170492888 | PEORIA 1704 | YOSEMITE | 0.24891 | 10 | 100% | 0 | 0 | 52.34% | 0% | 0 | 0.017878 | 1 | 0.4954 | 0.0088569 | Low | Low | Low | 3155 | 2495 | 0.017878 | 7.6599 | 0.08581%
MARTELL 1101CB | MARTELL 1101 | STOCKTON | 6.3498 | 10 | 65.48% | 1 | 2 | 48.33% | 0% | 0 | 0.01783 | 1 | 2.7857 | 0.049671 | Low | Low | Medium | 2357 | 2496 | 0.01783 | 7.642 | 0.08561%
PERRY 1101W26 | PERRY 1101 | LOS PADRES | 2.7324 | 25.8267 | 23.85% | 3 | 0 | 100% | 0% | 0 | 0.017829 | 1 | 2.8 | 0.049922 | Low | Low | Medium | 2353 | 2497 | 0.017829 | 7.6242 | 0.08541%
EMERALD LAKE 0402CB | EMERALD LAKE 0402 | PENINSULA | 1.9157 | 10 | 14.69% | 2 | 3 | 100% | 0% | 0 | 0.017819 | 1 | 5.3744 | 0.095764 | Low | Low | High | 1792 | 2498 | 0.017819 | 7.6064 | 0.08521%
TOCALOMA 0241CB | TOCALOMA 0241 | NORTH BAY | 0.031239 | 60 | 0% | 0 | 0 | 100% | 0% | 0 | 0.017781 | 1 | 2.2908 | 0.040732 | Low | Low | Medium | 2521 | 2499 | 0.017781 | 7.5885 | 0.08501%
SUMMIT 110147786 | SUMMIT 1101 | SIERRA | 1.7732 | 10 | 6.416% | 0 | 1 | 100% | 0% | 0 | 0.017764 | 1 | 0.69667 | 0.012376 | Low | Low | Low | 3134 | 2500 | 0.017764 | 7.5708 | 0.08481%
SAN LEANDRO U 1114MR545 | SAN LEANDRO U 1114 | MISSION | 2.8053 | 10 | 16.34% | 0 | 2 | 62.83% | 0% | 0 | 0.01772 | 1 | 3.623 | 0.0642 | Low | Low | High | 2112 | 2501 | 0.01772 | 7.553 | 0.08462%
VACAVILLE 1104CB | VACAVILLE 1104 | SACRAMENTO | 0.88859 | 38.1521 | 69.79% | 0 | 1 | 28.2% | 0% | 0 | 0.017694 | 1 | 3.1813 | 0.056289 | Low | Low | High | 2240 | 2502 | 0.017694 | 7.5353 | 0.08442%
PUEBLO 21031970 | PUEBLO 2103 | NORTH BAY | 3.678 | 37.2305 | 48.19% | 3 | 0 | 44.65% | 0% | 0 | 0.017676 | 1 | 3.2222 | 0.056955 | Low | Low | High | 2226 | 2503 | 0.017676 | 7.5176 | 0.08422%
BOLINAS 11011236 | BOLINAS 1101 | NORTH BAY | 3.0037 | 58.0295 | 0% | 0 | 0 | 73.67% | 0% | 0 | 0.017604 | 1 | 3.3892 | 0.059663 | Low | Low | High | 2186 | 2504 | 0.017604 | 7.4999 | 0.08402%
MADISON 21017702 | MADISON 2101 | SACRAMENTO | 2.3216 | 70.1745 | 98.98% | 0 | 0 | 10.42% | 0% | 0 | 0.017585 | 1 | 2.2784 | 0.040066 | Low | Low | Medium | 2538 | 2505 | 0.017585 | 7.4823 | 0.08382%
MORRO BAY 110249632 | MORRO BAY 1102 | LOS PADRES | 0.66912 | 10 | 0% | 0 | 3 | 100% | 0% | 0 | 0.017573 | 1 | 4.5803 | 0.080492 | Low | Low | High | 1931 | 2506 | 0.017573 | 7.4647 | 0.08363%
CASTRO VALLEY 1108MR525 | CASTRO VALLEY 1108 | MISSION | 0.061081 | 10 | 0% | 0 | 3 | 100% | 0% | 0 | 0.017573 | 1 | 3.5299 | 0.062033 | Low | Low | High | 2149 | 2506 | 0.017573 | 7.4471 | 0.08343%
KONOCTI 11081278 | KONOCTI 1108 | HUMBOLDT | 3.9864 | 24.8046 | 63% | 1 | 3 | 49.95% | 0% | 0 | 0.017559 | 1 | 2.6217 | 0.046036 | Low | Low | Medium | 2419 | 2508 | 0.017559 | 7.4296 | 0.08323%
MORRO BAY 1101 | MORRO BAY 1101 | LOS PADRES | 0.0056924 | 70 | 100% | 0 | 0 | 9.555% | 0% | 0 | 0.017559 | 1 | 2.3749 | 0.041701 | Low | Low | Medium | 2503 | 2509 | 0.017559 | 7.412 | 0.08304%
PEORIA 17046090 | PEORIA 1704 | YOSEMITE | 0.79834 | 10 | 4.922% | 0 | 1 | 100% | 0% | 0 | 0.01755 | 1 | 2.3134 | 0.0406 | Low | Low | Medium | 2524 | 2510 | 0.01755 | 7.3945 | 0.08284%
GUALALA 1111CB | GUALALA 1111 | HUMBOLDT | 3.8671 | 10 | 20.51% | 4 | 5 | 100% | 0% | 0 | 0.017522 | 1 | 1.59 | 0.02786 | Low | Low | Low | 2819 | 2511 | 0.017522 | 7.3769 | 0.08264%
AUBURN 11028611 | AUBURN 1102 | SIERRA | 1.8383 | 10 | 16.6% | 1 | 2 | 100% | 0% | 0 | 0.017498 | 1 | 2.9798 | 0.05214 | Low | Low | Medium | 2305 | 2512 | 0.017498 | 7.3594 | 0.08245%
HIGGINS 111051794 | HIGGINS 1110 | SIERRA | 3.8902 | 22.6443 | 10.14% | 0 | 1 | 100% | 0% | 0 | 0.017481 | 1 | 3.0277 | 0.052927 | Low | Low | Medium | 2290 | 2513 | 0.017481 | 7.3419 | 0.08225%
ALTO 11201214 | ALTO 1120 | NORTH BAY | 2.1973 | 49.1379 | 3.101% | 3 | 5 | 48.69% | 0% | 0 | 0.017477 | 1 | 2.904 | 0.050753 | Low | Low | Medium | 2338 | 2514 | 0.017477 | 7.3244 | 0.08205%
SUMMIT 1101742 | SUMMIT 1101 | SIERRA | 0.86692 | 10 | 60.19% | 0 | 1 | 66.72% | 0% | 0 | 0.017361 | 1 | 0.93316 | 0.016201 | Low | Low | Low | 3077 | 2515 | 0.017361 | 7.3069 | 0.08186%
STAFFORD 1102908 | STAFFORD 1102 | NORTH BAY | 0.96495 | 10 | 77.17% | 0 | 3 | 21.89% | 0% | 0 | 0.01736 | 1 | 3.3591 | 0.058315 | Low | Low | High | 2205 | 2516 | 0.01736 | 7.2896 | 0.08166%
HIGGINS 1110CB | HIGGINS 1110 | SIERRA | 11.6416 | 10 | 74.55% | 3 | 1 | 64.03% | 0% | 0 | 0.01732 | 1 | 3.2906 | 0.056995 | Low | Low | High | 2225 | 2517 | 0.01732 | 7.2722 | 0.08147%
GARBERVILLE 1103CB | GARBERVILLE 1103 | HUMBOLDT | 1.3711 | 26.7284 | 20.19% | 10 | 1 | 61.39% | 0% | 0 | 0.017309 | 1 | 2.7282 | 0.04722 | Low | Low | Medium | 2393 | 2518 | 0.017309 | 7.2549 | 0.08128%
LOS MOLINOS 11011308 | LOS MOLINOS 1101 | NORTH VALLEY | 0.1275 | 79.8468 | 100% | 0 | 0 | 1.055% | 0% | 0 | 0.017254 | 1 | 1.9923 | 0.034377 | Low | Low | Low | 2669 | 2519 | 0.017254 | 7.2376 | 0.08108%
BIG MEADOWS 21012476 | BIG MEADOWS 2101 | NORTH VALLEY | 4.675 | 24.1427 | 65.6% | 4 | 4 | 53.74% | 0% | 0 | 0.017254 | 1 | 1.8966 | 0.032724 | Low | Low | Low | 2706 | 2520 | 0.017254 | 7.2203 | 0.08089%
BEAR VALLEY 21014500 | BEAR VALLEY 2101 | YOSEMITE | 27.333 | 23.9548 | 99.26% | 0 | 3 | 33.35% | 0% | 0 | 0.017222 | 1 | 1.9324 | 0.03328 | Low | Low | Low | 2693 | 2521 | 0.017222 | 7.2031 | 0.08069%
SAUSALITO 11021500 | SAUSALITO 1102 | NORTH BAY | 1.1513 | 69.0338 | 0% | 0 | 0 | 90.51% | 0% | 0 | 0.017208 | 1 | 3.3211 | 0.05715 | Low | Low | High | 2221 | 2522 | 0.017208 | 7.1858 | 0.0805%
SPENCE 1123CB | SPENCE 1123 | CENTRAL COAST | 2.0801 | 71.6022 | 100% | 0 | 0 | 6.177% | 0% | 0 | 0.017169 | 1 | 1.4373 | 0.024677 | Low | Low | Low | 2892 | 2523 | 0.017169 | 7.1686 | 0.08031%
MARTELL 110368192 | MARTELL 1103 | STOCKTON | 2.6279 | 35.8454 | 65.85% | 0 | 2 | 40.93% | 0% | 0 | 0.017124 | 1 | 2.9408 | 0.05036 | Low | Low | Medium | 2346 | 2524 | 0.017124 | 7.1515 | 0.08012%
RESERVATION ROAD 1102CB | RESERVATION ROAD 1102 | CENTRAL COAST | 6.8792 | 54.6073 | 43.73% | 1 | 5 | 38.43% | 0% | 0 | 0.017073 | 1 | 1.8467 | 0.031528 | Low | Low | Low | 2734 | 2525 | 0.017073 | 7.1343 | 0.07992%
PUTAH CREEK 11058812 | PUTAH CREEK 1105 | SACRAMENTO | 0.75773 | 78.0828 | 100% | 0 | 0 | 1.163% | 0% | 0 | 0.017069 | 1 | 1.8258 | 0.031165 | Low | Low | Low | 2745 | 2526 | 0.017069 | 7.1173 | 0.07973%
TEMPLETON 2112R98 | TEMPLETON 2112 | LOS PADRES | 2.5848 | 57.8675 | 88.32% | 0 | 0 | 11.06% | 0% | 0 | 0.017037 | 1 | 2.2449 | 0.038247 | Low | Low | Medium | 2579 | 2527 | 0.017037 | 7.1002 | 0.07954%
JESSUP 11019002 | JESSUP 1101 | NORTH VALLEY | 6.7893 | 16.4426 | 68.96% | 0 | 5 | 44.76% | 0% | 0 | 0.017028 | 1 | 2.2277 | 0.037935 | Low | Low | Low | 2585 | 2528 | 0.017028 | 7.0832 | 0.07935%
COARSEGOLD 21036110 | COARSEGOLD 2103 | YOSEMITE | 9.9772 | 20.6713 | 95.13% | 0 | 5 | 33.47% | 0% | 0 | 0.016997 | 1 | 1.5993 | 0.027183 | Low | Low | Low | 2835 | 2529 | 0.016997 | 7.0661 | 0.07916%
PIT NO 3 21011480 | PIT NO 3 2101 | NORTH VALLEY | 2.2265 | 10 | 27.11% | 1 | 1 | 90.29% | 0% | 0 | 0.016964 | 1 | 1.0365 | 0.017582 | Low | Low | Low | 3051 | 2530 | 0.016964 | 7.0491 | 0.07897%
WYANDOTTE 1105CB | WYANDOTTE 1105 | NORTH VALLEY | 12.987 | 37.2024 | 0% | 0 | 0 | 96.35% | 0.5289% | 1 | 0.016922 | 1 | 2.4689 | 0.041778 | Low | Low | Medium | 2499 | 2531 | 0.016922 | 7.0322 | 0.07878%
RIO DELL 11021504 | RIO DELL 1102 | HUMBOLDT | 8.4162 | 77.8437 | 6.428% | 4 | 1 | 69.81% | 0% | 0 | 0.016871 | 1 | 0.76309 | 0.012874 | Low | Low | Low | 3126 | 2532 | 0.016871 | 7.0153 | 0.07859%
WILLITS 110434006 | WILLITS 1104 | HUMBOLDT | 3.7731 | 21.9583 | 31.14% | 0 | 7 | 66.96% | 0% | 0 | 0.016864 | 1 | 2.5304 | 0.042672 | Low | Low | Medium | 2485 | 2533 | 0.016864 | 6.9984 | 0.0784%
SUMMIT 1101CB | SUMMIT 1101 | SIERRA | 0.12475 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.016863 | 1 | 1.5975 | 0.026939 | Low | Low | Low | 2838 | 2534 | 0.016863 | 6.9815 | 0.07821%
LINCOLN 11012310 | LINCOLN 1101 | SIERRA | 10.0776 | 10 | 72.42% | 0 | 6 | 56.39% | 0% | 0 | 0.016835 | 1 | 2.9232 | 0.049213 | Low | Low | Medium | 2366 | 2535 | 0.016835 | 6.9647 | 0.07802%
NOVATO 110455398 | NOVATO 1104 | NORTH BAY | 2.9149 | 74.0149 | 52.93% | 0 | 1 | 25.83% | 0% | 0 | 0.016828 | 1 | 2.8041 | 0.047187 | Low | Low | Medium | 2394 | 2536 | 0.016828 | 6.9478 | 0.07784%
NARROWS 210276952 | NARROWS 2102 | SIERRA | 3.581 | 10 | 96.43% | 1 | 1 | 31.95% | 0% | 0 | 0.016756 | 1 | 3.7233 | 0.062386 | Low | Low | High | 2137 | 2537 | 0.016756 | 6.931 | 0.07765%
MERCED FALLS 110222774 | MERCED FALLS 1102 | YOSEMITE | 1.0091 | 37.0223 | 100% | 0 | 0 | 27.2% | 0% | 0 | 0.016738 | 1 | 0.33771 | 0.0056526 | Low | Low | Low | 3166 | 2538 | 0.016738 | 6.9142 | 0.07746%
SOLEDAD 21013720 | SOLEDAD 2101 | CENTRAL COAST | 2.3505 | 51.9589 | 88.77% | 0 | 0 | 12.85% | 0% | 0 | 0.016725 | 1 | 2.3054 | 0.038559 | Low | Low | Medium | 2570 | 2539 | 0.016725 | 6.8975 | 0.07727%
SOBRANTE 1101L534R | SOBRANTE 1101 | DIABLO | 1.5331 | 10 | 22.75% | 1 | 1 | 80.03% | 7.584% | 0 | 0.016712 | 1 | 3.8056 | 0.0636 | Low | Low | High | 2123 | 2540 | 0.016712 | 6.8808 | 0.07708%
CORRAL 110213498 | CORRAL 1102 | STOCKTON | 0.99648 | 10 | 14.99% | 0 | 1 | 100% | 0% | 0 | 0.0167 | 1 | 3.3092 | 0.055263 | Low | Low | High | 2254 | 2541 | 0.0167 | 6.8641 | 0.0769%
STAFFORD 1101CB | STAFFORD 1101 | NORTH BAY | 2.6576 | 10 | 64.37% | 5 | 3 | 21.89% | 0% | 0 | 0.016699 | 1 | 2.8654 | 0.047849 | Low | Low | Medium | 2382 | 2542 | 0.016699 | 6.8474 | 0.07671%
PLACERVILLE 11118582 | PLACERVILLE 1111 | SIERRA | 7.7771 | 10 | 58.12% | 5 | 4 | 64.88% | 0% | 0 | 0.016693 | 1 | 2.7827 | 0.046451 | Low | Low | Medium | 2407 | 2543 | 0.016693 | 6.8307 | 0.07652%
ANDERSON 1101CB | ANDERSON 1101 | NORTH VALLEY | 1.7524 | 42.6703 | 99.35% | 0 | 2 | 19.42% | 0% | 0 | 0.016693 | 1 | 2.9503 | 0.049249 | Low | Low | Medium | 2365 | 2544 | 0.016693 | 6.814 | 0.07634%
SOLEDAD 21017056 | SOLEDAD 2101 | CENTRAL COAST | 1.1515 | 59.0572 | 100% | 0 | 0 | 11.67% | 0% | 0 | 0.016656 | 1 | 2.3825 | 0.039684 | Low | Low | Medium | 2545 | 2545 | 0.016656 | 6.7973 | 0.07615%
UPPER LAKE 1101472084 | UPPER LAKE 1101 | HUMBOLDT | 4.5266 | 10 | 55.47% | 0 | 3 | 61.59% | 0% | 0 | 0.016554 | 1 | 1.8437 | 0.030521 | Low | Low | Low | 2757 | 2546 | 0.016554 | 6.7806 | 0.07596%
SAN CARLOS 11048942 | SAN CARLOS 1104 | PENINSULA | 1.591 | 10 | 52.6% | 0 | 5 | 59.7% | 0% | 0 | 0.016545 | 1 | 4.0626 | 0.067215 | Low | Low | High | 2072 | 2547 | 0.016545 | 6.7641 | 0.07578%
KONOCTI 1102CB | KONOCTI 1102 | HUMBOLDT | 6.3926 | 38.5127 | 58.33% | 0 | 0 | 42.97% | 1.842% | 0 | 0.01654 | 1 | 2.4961 | 0.041284 | Low | Low | Medium | 2512 | 2548 | 0.01654 | 6.7475 | 0.07559%
LUCERNE 1106CB | LUCERNE 1106 | HUMBOLDT | 2.483 | 10 | 34.76% | 1 | 7 | 68.8% | 0% | 0 | 0.01653 | 1 | 2.1266 | 0.035153 | Low | Low | Low | 2647 | 2549 | 0.01653 | 6.731 | 0.07541%
SWIFT 2107XR526 | SWIFT 2107 | SAN JOSE | 2.6821 | 10 | 42.91% | 0 | 1 | 49.21% | 0% | 0 | 0.016512 | 1 | 4.4175 | 0.072944 | Low | Low | High | 2006 | 2550 | 0.016512 | 6.7144 | 0.07522%
POINT ARENA 1101CB | POINT ARENA 1101 | HUMBOLDT | 2.4683 | 40.0153 | 0% | 3 | 1 | 100% | 0% | 0 | 0.016501 | 1 | 2.4898 | 0.041084 | Low | Low | Medium | 2514 | 2551 | 0.016501 | 6.6979 | 0.07504%
HIGGINS 11041006 | HIGGINS 1104 | SIERRA | 9.9734 | 10.2486 | 72.09% | 2 | 7 | 49.68% | 0% | 0 | 0.016495 | 1 | 3.2059 | 0.052881 | Low | Low | High | 2291 | 2552 | 0.016495 | 6.6814 | 0.07485%
EMERALD LAKE 04028858 | EMERALD LAKE 0402 | PENINSULA | 1.9112 | 10 | 5.775% | 0 | 4 | 100% | 0% | 0 | 0.016487 | 1 | 4.6869 | 0.077272 | Low | Low | High | 1960 | 2553 | 0.016487 | 6.6649 | 0.07467%
CLOVERDALE 1102429006 | CLOVERDALE 1102 | SONOMA | 2.0089 | 22.4739 | 19.1% | 0 | 1 | 100% | 0% | 0 | 0.016467 | 1 | 2.2766 | 0.037488 | Low | Low | Medium | 2594 | 2554 | 0.016467 | 6.6485 | 0.07448%
HOPLAND 11011100 | HOPLAND 1101 | HUMBOLDT | 2.6093 | 13.3851 | 100% | 0 | 1 | 39.2% | 0% | 0 | 0.016404 | 1 | 1.8539 | 0.030412 | Low | Low | Low | 2764 | 2555 | 0.016404 | 6.632 | 0.0743%
SPRUCE 0402BR304 | SPRUCE 0402 | EAST BAY | 1.905 | 10 | 5.593% | 0 | 5 | 53.05% | 19.04% | 0 | 0.016372 | 1 | 4.6125 | 0.075515 | Low | Low | High | 1980 | 2556 | 0.016372 | 6.6156 | 0.07411%
FITCH MOUNTAIN 1113352 | FITCH MOUNTAIN 1113 | SONOMA | 7.3048 | 34.6273 | 40.22% | 1 | 0 | 61.07% | 0% | 0 | 0.016355 | 1 | 2.6925 | 0.044035 | Low | Low | Medium | 2461 | 2557 | 0.016355 | 6.5992 | 0.07393%
BELL 1108CB | BELL 1108 | SIERRA | 4.1507 | 10 | 64.56% | 0 | 6 | 33.13% | 0% | 0 | 0.016334 | 1 | 2.6182 | 0.042766 | Low | Low | Medium | 2482 | 2558 | 0.016334 | 6.5829 | 0.07375%
JAMESON 11059472 | JAMESON 1105 | SACRAMENTO | 2.8377 | 36.7552 | 61.91% | 0 | 2 | 38.64% | 0% | 0 | 0.016315 | 1 | 2.585 | 0.042175 | Low | Low | Medium | 2492 | 2559 | 0.016315 | 6.5665 | 0.07356%
JESSUP 11031540 | JESSUP 1103 | NORTH VALLEY | 2.7435 | 22.0778 | 100% | 1 | 1 | 18.03% | 0% | 0 | 0.01631 | 1 | 2.3847 | 0.038895 | Low | Low | Medium | 2563 | 2560 | 0.01631 | 6.5502 | 0.07338%
POTTER VALLEY P H 110495878 | POTTER VALLEY P H 1104 | HUMBOLDT | 6.3973 | 36.9398 | 60.01% | 0 | 4 | 34.83% | 8.674% | 0 | 0.01627 | 1 | 1.5212 | 0.024749 | Low | Low | Low | 2890 | 2561 | 0.01627 | 6.5339 | 0.0732%
MIRABEL 1101CB | MIRABEL 1101 | SONOMA | 2.6279 | 19.2673 | 59.3% | 0 | 2 | 31.12% | 21.2% | 0 | 0.016241 | 1 | 3.6316 | 0.058979 | Low | Low | High | 2195 | 2562 | 0.016241 | 6.5176 | 0.07302%
SAN CARLOS 11039148 | SAN CARLOS 1103 | PENINSULA | 3.9693 | 10 | 27.37% | 0 | 9 | 43.54% | 0% | 0 | 0.016236 | 1 | 4.5802 | 0.074366 | Low | Low | High | 1993 | 2563 | 0.016236 | 6.5014 | 0.07283%
MC KEE 110870535 | MC KEE 1108 | SAN JOSE | 1.0836 | 23.5844 | 100% | 0 | 0 | 32.92% | 0% | 0 | 0.016178 | 1 | 3.8247 | 0.061876 | Low | Low | High | 2154 | 2564 | 0.016178 | 6.4852 | 0.07265%
SAN LEANDRO U 1114MR218 | SAN LEANDRO U 1114 | MISSION | 6.9334 | 10 | 55.46% | 3 | 0 | 61.53% | 0% | 0 | 0.01617 | 1 | 3.4495 | 0.055778 | Low | Low | High | 2249 | 2565 | 0.01617 | 6.469 | 0.07247%
LLAGAS 2104XR294 | LLAGAS 2104 | SAN JOSE | 1.6348 | 49.1137 | 100% | 0 | 0 | 15.4% | 0% | 0 | 0.016162 | 1 | 2.8487 | 0.046041 | Low | Low | Medium | 2418 | 2566 | 0.016162 | 6.4528 | 0.07229%
DUNBAR 1101234 | DUNBAR 1101 | SONOMA | 3.2653 | 13.7421 | 32.63% | 2 | 8 | 50.44% | 15.33% | 0 | 0.01612 | 1 | 2.7726 | 0.044694 | Low | Low | Medium | 2444 | 2567 | 0.01612 | 6.4366 | 0.07211%
POSO MOUNTAIN 21013990 | POSO MOUNTAIN 2101 | KERN | 4.4819 | 10 | 34.01% | 0 | 1 | 80.62% | 0% | 0 | 0.0161 | 1 | 2.8327 | 0.045606 | Low | Low | Medium | 2431 | 2568 | 0.0161 | 6.4205 | 0.07193%
LLAGAS 2106XR146 | LLAGAS 2106 | SAN JOSE | 1.5959 | 59.0705 | 100% | 0 | 0 | 7.634% | 0% | 0 | 0.016009 | 1 | 2.4996 | 0.040015 | Low | Low | Medium | 2540 | 2569 | 0.016009 | 6.4044 | 0.07175%
BURNEY 110297318 | BURNEY 1102 | NORTH VALLEY | 0.71383 | 14.6507 | 68.47% | 0 | 0 | 50.51% | 0% | 0 | 0.015997 | 1 | 2.1361 | 0.034171 | Low | Low | Low | 2678 | 2570 | 0.015997 | 6.3884 | 0.07157%
LOS OSITOS 21037082 | LOS OSITOS 2103 | CENTRAL COAST | 0.3792 | 71.4337 | 96.62% | 0 | 0 | 1.843% | 0% | 0 | 0.015988 | 1 | 2.4399 | 0.03901 | Low | Low | Medium | 2561 | 2571 | 0.015988 | 6.3724 | 0.07139%
OAKLAND J 1102CR184 | OAKLAND J 1102 | EAST BAY | 3.4622 | 10 | 2.127% | 3 | 2 | 100% | 0% | 0 | 0.01597 | 1 | 3.4089 | 0.054442 | Low | Low | High | 2267 | 2572 | 0.01597 | 6.3564 | 0.07121%
CAYUCOS 1102W18 | CAYUCOS 1102 | LOS PADRES | 1.9754 | 67.8899 | 46.98% | 0 | 0 | 8.859% | 14.04% | 0 | 0.015968 | 1 | 2.4056 | 0.038413 | Low | Low | Medium | 2575 | 2573 | 0.015968 | 6.3405 | 0.07103%
ROB ROY 210512586 | ROB ROY 2105 | CENTRAL COAST | 3.2869 | 10 | 13.9% | 3 | 2 | 50.3% | 0% | 0 | 0.015967 | 1 | 2.9067 | 0.046412 | Low | Low | Medium | 2409 | 2574 | 0.015967 | 6.3245 | 0.07085%
FAIRVIEW 220799096 | FAIRVIEW 2207 | DIABLO | 9.9116 | 14.1017 | 19.38% | 0 | 2 | 100% | 0% | 0 | 0.015926 | 1 | 2.9135 | 0.046399 | Low | Low | Medium | 2411 | 2575 | 0.015926 | 6.3085 | 0.07067%
BELL 110880680 | BELL 1108 | SIERRA | 1.2687 | 10 | 46.62% | 0 | 0 | 71.23% | 0% | 0 | 0.015926 | 1 | 2.6403 | 0.042048 | Low | Low | Medium | 2497 | 2576 | 0.015926 | 6.2926 | 0.0705%
COTATI 1102462 | COTATI 1102 | SONOMA | 3.3153 | 11.8938 | 22% | 1 | 2 | 84.56% | 0% | 0 | 0.015902 | 1 | 2.7902 | 0.044371 | Low | Low | Medium | 2451 | 2577 | 0.015902 | 6.2767 | 0.07032%
HIGHLANDS 11034630 | HIGHLANDS 1103 | HUMBOLDT | 1.4567 | 24.8899 | 80.52% | 0 | 2 | 42.07% | 0% | 0 | 0.015892 | 1 | 3.3089 | 0.052584 | Low | Low | High | 2299 | 2578 | 0.015892 | 6.2608 | 0.07014%
MORAGA 11017616 | MORAGA 1101 | DIABLO | 1.1725 | 14.9864 | 34.86% | 0 | 4 | 82.16% | 0% | 0 | 0.015878 | 1 | 3.6873 | 0.058547 | Low | Low | High | 2201 | 2579 | 0.015878 | 6.2449 | 0.06996%
KONOCTI 11084041 | KONOCTI 1108 | HUMBOLDT | 1.9081 | 10 | 99.47% | 0 | 0 | 40.69% | 0% | 0 | 0.015871 | 1 | 2.4887 | 0.039499 | Low | Low | Medium | 2549 | 2580 | 0.015871 | 6.229 | 0.06978%
CALPELLA 1102496 | CALPELLA 1102 | HUMBOLDT | 4.1652 | 16.4846 | 91.99% | 0 | 2 | 24.91% | 0% | 0 | 0.015871 | 1 | 1.3046 | 0.020706 | Low | Low | Low | 2987 | 2581 | 0.015871 | 6.2131 | 0.0696%
RISING RIVER 11011530 | RISING RIVER 1101 | NORTH VALLEY | 10.3786 | 10.5372 | 70.85% | 4 | 0 | 58.6% | 0% | 0 | 0.01587 | 1 | 0.8986 | 0.014261 | Low | Low | Low | 3112 | 2582 | 0.01587 | 6.1973 | 0.06943%
LOS GATOS 110160052 | LOS GATOS 1101 | DE ANZA | 1.8727 | 10 | 24.39% | 0 | 1 | 100% | 0% | 0 | 0.015806 | 1 | 3.3394 | 0.052781 | Low | Low | High | 2295 | 2583 | 0.015806 | 6.1814 | 0.06925%
HOPLAND 1101770 | HOPLAND 1101 | HUMBOLDT | 8.7193 | 58.1602 | 26.75% | 1 | 4 | 57.45% | 0% | 0 | 0.015784 | 1 | 1.5698 | 0.024778 | Low | Low | Low | 2889 | 2584 | 0.015784 | 6.1656 | 0.06907%
ANDERSON 11031600 | ANDERSON 1103 | NORTH VALLEY | 2.5631 | 13.0676 | 100% | 0 | 0 | 23.83% | 0% | 0 | 0.015715 | 1 | 2.3807 | 0.037413 | Low | Low | Medium | 2597 | 2585 | 0.015715 | 6.1498 | 0.0689%
SILVERADO 210298998 | SILVERADO 2102 | NORTH BAY | 4.5559 | 48.6012 | 79.99% | 0 | 0 | 16.02% | 0% | 0 | 0.015709 | 1 | 1.5297 | 0.024031 | Low | Low | Low | 2910 | 2586 | 0.015709 | 6.1341 | 0.06872%
STAFFORD 11011298 | STAFFORD 1101 | NORTH BAY | 2.4249 | 10 | 52.95% | 1 | 0 | 36.21% | 0% | 0 | 0.015641 | 1 | 3.0475 | 0.047666 | Low | Low | Medium | 2388 | 2587 | 0.015641 | 6.1184 | 0.06854%
OILFIELDS 1103 | OILFIELDS 1103 | CENTRAL COAST | 0.020981 | 19.5696 | 17.4% | 0 | 0 | 100% | 0% | 0 | 0.015601 | 1 | 2.3018 | 0.035911 | Low | Low | Medium | 2629 | 2588 | 0.015601 | 6.1027 | 0.06837%
ANDERSON 11011752 | ANDERSON 1101 | NORTH VALLEY | 3.4624 | 22.5175 | 29.42% | 0 | 0 | 74.73% | 0% | 0 | 0.015595 | 1 | 2.4433 | 0.038104 | Low | Low | Medium | 2581 | 2589 | 0.015595 | 6.0871 | 0.06819%
SHINGLE SPRINGS 210819622 | SHINGLE SPRINGS 2108 | SIERRA | 4.5627 | 12.9837 | 69.35% | 2 | 3 | 39.08% | 0% | 0 | 0.015541 | 1 | 3.3954 | 0.052766 | Low | Low | High | 2296 | 2590 | 0.015541 | 6.0715 | 0.06802%
RALSTON 1101CB | RALSTON 1101 | PENINSULA | 5.2354 | 10 | 67.13% | 0 | 1 | 62.97% | 0% | 0 | 0.015521 | 1 | 2.985 | 0.04633 | Low | Low | Medium | 2415 | 2591 | 0.015521 | 6.056 | 0.06784%
POTTER VALLEY P H 110537476 | POTTER VALLEY P H 1105 | HUMBOLDT | 0.5064 | 62.972 | 86.61% | 0 | 3 | 5.941% | 0% | 0 | 0.015424 | 1 | 1.6964 | 0.026166 | Low | Low | Low | 2859 | 2592 | 0.015424 | 6.0405 | 0.06767%
UPPER LAKE 1101660 | UPPER LAKE 1101 | HUMBOLDT | 7.1376 | 10 | 50.04% | 0 | 2 | 74.17% | 0% | 0 | 0.015402 | 1 | 1.6171 | 0.024907 | Low | Low | Low | 2887 | 2593 | 0.015402 | 6.025 | 0.0675%
PENRYN 11072410 | PENRYN 1107 | SIERRA | 2.4145 | 10 | 87.13% | 0 | 1 | 32.14% | 0% | 0 | 0.015364 | 1 | 3.3713 | 0.051797 | Low | Low | High | 2315 | 2594 | 0.015364 | 6.0096 | 0.06733%
ROB ROY 21045304 | ROB ROY 2104 | CENTRAL COAST | 2.975 | 10 | 39.67% | 0 | 0 | 59.8% | 0% | 0 | 0.015337 | 1 | 3.2417 | 0.049718 | Low | Low | High | 2356 | 2595 | 0.015337 | 5.9943 | 0.06715%
SAN RAFAEL 1105344 | SAN RAFAEL 1105 | NORTH BAY | 2.2778 | 10 | 70.24% | 0 | 2 | 30.4% | 0% | 0 | 0.015331 | 1 | 4.1625 | 0.063813 | Low | Low | High | 2117 | 2596 | 0.015331 | 5.9789 | 0.06698%
SUMMIT 110186658 | SUMMIT 1101 | SIERRA | 0.66943 | 10 | 1.926% | 3 | 0 | 100% | 0% | 0 | 0.015299 | 1 | 1.3569 | 0.020759 | Low | Low | Low | 2985 | 2597 | 0.015299 | 5.9636 | 0.06681%
POINT MORETTI 1101CB | POINT MORETTI 1101 | CENTRAL COAST | 0.028582 | 13.6525 | 6.641% | 0 | 0 | 100% | 6.641% | 0 | 0.015281 | 1 | 2.6605 | 0.040655 | Low | Low | Medium | 2522 | 2598 | 0.015281 | 5.9483 | 0.06664%
BIG RIVER 1101CB | BIG RIVER 1101 | HUMBOLDT | 1.8594 | 10 | 0.4258% | 5 | 2 | 94.21% | 0% | 0 | 0.01527 | 1 | 3.6 | 0.054971 | Low | Low | High | 2259 | 2599 | 0.01527 | 5.933 | 0.06647%
GEYSERVILLE 110289714 | GEYSERVILLE 1102 | SONOMA | 1.4773 | 46.3035 | 100% | 0 | 0 | 11.51% | 0% | 0 | 0.015262 | 1 | 1.5055 | 0.022977 | Low | Low | Low | 2939 | 2600 | 0.015262 | 5.9178 | 0.0663%
CARLOTTA 112142896 | CARLOTTA 1121 | HUMBOLDT | 2.183 | 31.2732 | 37.15% | 2 | 2 | 39.92% | 0% | 0 | 0.015245 | 1 | 2.4688 | 0.037636 | Low | Low | Medium | 2592 | 2601 | 0.015245 | 5.9025 | 0.06612%
WILLITS 1103CB | WILLITS 1103 | HUMBOLDT | 1.4734 | 28.6497 | 64.03% | 0 | 1 | 37.49% | 0% | 0 | 0.015222 | 1 | 1.9923 | 0.030328 | Low | Low | Low | 2766 | 2602 | 0.015222 | 5.8873 | 0.06595%
BIG MEADOWS 21012510 | BIG MEADOWS 2101 | NORTH VALLEY | 5.0492 | 32.6868 | 6.505% | 7 | 2 | 57.3% | 0% | 0 | 0.015201 | 1 | 1.0173 | 0.015464 | Low | Low | Low | 3098 | 2603 | 0.015201 | 5.872 | 0.06578%
FRANKLIN 1104P146 | FRANKLIN 1104 | EAST BAY | 1.1753 | 10 | 98.96% | 0 | 2 | 31.88% | 0% | 0 | 0.015101 | 1 | 3.2686 | 0.049359 | Low | Low | High | 2364 | 2604 | 0.015101 | 5.8568 | 0.06561%
SARATOGA 1115LC20 | SARATOGA 1115 | DE ANZA | 2.7261 | 10 | 38.53% | 0 | 1 | 56.79% | 0% | 0 | 0.015057 | 1 | 3.5487 | 0.053432 | Low | Low | High | 2281 | 2605 | 0.015057 | 5.8417 | 0.06544%
GONZALES 110422420 | GONZALES 1104 | CENTRAL COAST | 0.060363 | 60 | 100% | 0 | 0 | 0.7167% | 0% | 0 | 0.015047 | 1 | 2.2459 | 0.033793 | Low | Low | Medium | 2686 | 2606 | 0.015047 | 5.8267 | 0.06528%
SAN LUIS OBISPO 1102597518 | SAN LUIS OBISPO 1102 | LOS PADRES | 0.61698 | 17.5901 | 98.92% | 0 | 1 | 28.41% | 0% | 0 | 0.015039 | 1 | 4.3749 | 0.065794 | Low | Low | High | 2089 | 2607 | 0.015039 | 5.8116 | 0.06511%
SAN ARDO 11017094 | SAN ARDO 1101 | CENTRAL COAST | 1.1437 | 50.6148 | 100% | 0 | 0 | 6.71% | 0% | 0 | 0.014985 | 1 | 0.52695 | 0.0078965 | Low | Low | Low | 3160 | 2608 | 0.014985 | 5.7966 | 0.06494%
SARATOGA 11076867 | SARATOGA 1107 | DE ANZA | 0.24862 | 10 | 100% | 0 | 2 | 30.1% | 0% | 0 | 0.014963 | 1 | 3.817 | 0.057115 | Low | Low | High | 2222 | 2609 | 0.014963 | 5.7816 | 0.06477%
GRASS VALLEY 1103 | GRASS VALLEY 1103 | SIERRA | 0.021115 | 10 | 19.87% | 0 | 0 | 100% | 0% | 0 | 0.014923 | 1 | 2.5027 | 0.037349 | Low | Low | Medium | 2599 | 2610 | 0.014923 | 5.7666 | 0.0646%
OAKLAND X 1106CB | OAKLAND X 1106 | EAST BAY | 4.876 | 10 | 15.55% | 5 | 5 | 41.41% | 19.42% | 0 | 0.014897 | 1 | 4.146 | 0.061764 | Low | Low | High | 2155 | 2611 | 0.014897 | 5.7517 | 0.06444%
MC ARTHUR 11021324 | MC ARTHUR 1102 | NORTH VALLEY | 0.91154 | 54.3228 | 100% | 0 | 0 | 3.568% | 0% | 0 | 0.014895 | 1 | 1.0821 | 0.016117 | Low | Low | Low | 3080 | 2612 | 0.014895 | 5.7368 | 0.06427%
MERCED FALLS 1102CB | MERCED FALLS 1102 | YOSEMITE | 8.7968 | 48.2872 | 48.16% | 0 | 1 | 34.84% | 0% | 0 | 0.014879 | 1 | 0.87183 | 0.012972 | Low | Low | Low | 3125 | 2613 | 0.014879 | 5.7219 | 0.0641%
JESSUP 1101CB | JESSUP 1101 | NORTH VALLEY | 1.1327 | 30.8343 | 100% | 0 | 0 | 19.43% | 0% | 0 | 0.01487 | 1 | 2.5003 | 0.037179 | Low | Low | Medium | 2609 | 2614 | 0.01487 | 5.707 | 0.06394%
PURISIMA 1101CB | PURISIMA 1101 | LOS PADRES | 3.8284 | 30.5658 | 4.848% | 1 | 0 | 83.25% | 0% | 0 | 0.014861 | 1 | 3.8367 | 0.057017 | Low | Low | High | 2224 | 2615 | 0.014861 | 5.6922 | 0.06377%
HICKS 2101XR162 | HICKS 2101 | SAN JOSE | 2.3563 | 22.9213 | 92.08% | 0 | 3 | 24.69% | 0% | 0 | 0.014813 | 1 | 3.2145 | 0.047617 | Low | Low | High | 2389 | 2616 | 0.014813 | 5.6773 | 0.0636%
REEDLEY 1104274990 | REEDLEY 1104 | FRESNO | 1.6643 | 56.3701 | 98.08% | 0 | 0 | 3.167% | 0% | 0 | 0.014809 | 1 | 3.2104 | 0.047544 | Low | Low | High | 2391 | 2617 | 0.014809 | 5.6625 | 0.06344%
SAN LUIS OBISPO 1103CB | SAN LUIS OBISPO 1103 | LOS PADRES | 2.8352 | 59.393 | 72.07% | 0 | 1 | 20.37% | 0% | 0 | 0.014802 | 1 | 2.3239 | 0.034398 | Low | Low | Medium | 2668 | 2618 | 0.014802 | 5.6477 | 0.06327%
POTTER VALLEY P H 1105CB | POTTER VALLEY P H 1105 | HUMBOLDT | 0.024417 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.014786 | 1 | 1.3325 | 0.019702 | Low | Low | Low | 3014 | 2619 | 0.014786 | 5.6329 | 0.0631%
VIEJO 22022606 | VIEJO 2202 | CENTRAL COAST | 0.94683 | 10 | 0% | 1 | 1 | 98.67% | 0% | 0 | 0.014784 | 1 | 3.9289 | 0.058085 | Low | Low | High | 2207 | 2620 | 0.014784 | 5.6181 | 0.06294%
CORRAL 110214028 | CORRAL 1102 | STOCKTON | 3.2845 | 10 | 84.85% | 0 | 2 | 41.18% | 0% | 0 | 0.01476 | 1 | 2.5258 | 0.03728 | Low | Low | Medium | 2603 | 2621 | 0.01476 | 5.6033 | 0.06277%
COARSEGOLD 210490356 | COARSEGOLD 2104 | YOSEMITE | 4.6415 | 10 | 96.81% | 0 | 4 | 27.05% | 0% | 0 | 0.014744 | 1 | 1.5262 | 0.022503 | Low | Low | Low | 2955 | 2622 | 0.014744 | 5.5886 | 0.06261%
POTTER VALLEY P H 110564118 | POTTER VALLEY P H 1105 | HUMBOLDT | 1.7203 | 30.1363 | 62.86% | 2 | 1 | 18.17% | 0% | 0 | 0.014734 | 1 | 1.6469 | 0.024265 | Low | Low | Low | 2902 | 2623 | 0.014734 | 5.5738 | 0.06244%
PAUL SWEET 210612828 | PAUL SWEET 2106 | CENTRAL COAST | 1.7112 | 10 | 38.85% | 0 | 0 | 34.49% | 21.63% | 0 | 0.014721 | 1 | 4.5319 | 0.066716 | Low | Low | High | 2079 | 2624 | 0.014721 | 5.5591 | 0.06228%
COTTONWOOD 110131500 | COTTONWOOD 1101 | NORTH VALLEY | 3.2216 | 22.5046 | 96% | 0 | 0 | 27.31% | 0% | 0 | 0.01471 | 1 | 1.6607 | 0.024428 | Low | Low | Low | 2898 | 2625 | 0.01471 | 5.5444 | 0.06211%
CLARKSVILLE 210955666 | CLARKSVILLE 2109 | SIERRA | 0.61278 | 10 | 100% | 0 | 0 | 32.55% | 0% | 0 | 0.014709 | 1 | 3.1023 | 0.04563 | Low | Low | High | 2430 | 2626 | 0.014709 | 5.5297 | 0.06195%
PERRY 1101W52 | PERRY 1101 | LOS PADRES | 2.9028 | 10 | 12.36% | 3 | 2 | 69.83% | 0% | 0 | 0.014698 | 1 | 3.5249 | 0.051807 | Low | Low | High | 2314 | 2627 | 0.014698 | 5.5149 | 0.06178%
CURTIS 170349746 | CURTIS 1703 | YOSEMITE | 0.37395 | 10 | 15.4% | 0 | 1 | 100% | 0% | 0 | 0.014691 | 1 | 2.8626 | 0.042055 | Low | Low | Medium | 2495 | 2628 | 0.014691 | 5.5002 | 0.06162%
ANTELOPE 11011631 | ANTELOPE 1101 | KERN | 0.75322 | 47.1276 | 100% | 0 | 0 | 6.682% | 0% | 0 | 0.014633 | 1 | 0.73269 | 0.010722 | Low | Low | Low | 3142 | 2629 | 0.014633 | 5.4856 | 0.06145%
FLINT 1102CB | FLINT 1102 | SIERRA | 0.092844 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.014483 | 1 | 3.2339 | 0.046837 | Low | Low | High | 2401 | 2630 | 0.014483 | 5.4709 | 0.06129%
AUBURN 1102 | AUBURN 1102 | SIERRA | 0.025464 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.014483 | 1 | 3.1021 | 0.044929 | Low | Low | High | 2438 | 2631 | 0.014483 | 5.4564 | 0.06113%
AUBURN 1101CB | AUBURN 1101 | SIERRA | 3.1166 | 10 | 26.2% | 0 | 7 | 63.53% | 0% | 0 | 0.014449 | 1 | 3.1752 | 0.045877 | Low | Low | High | 2423 | 2632 | 0.014449 | 5.442 | 0.06097%
SAN BENITO 2104CB | SAN BENITO 2104 | CENTRAL COAST | 4.8064 | 10 | 7.992% | 0 | 0 | 52.81% | 0% | 0 | 0.014395 | 1 | 2.1147 | 0.030441 | Low | Low | Low | 2761 | 2633 | 0.014395 | 5.4275 | 0.0608%
VALLEY VIEW 1105P190 | VALLEY VIEW 1105 | EAST BAY | 3.5037 | 10 | 43.53% | 0 | 2 | 59.31% | 0% | 0 | 0.014389 | 1 | 4.3115 | 0.062036 | Low | Low | High | 2148 | 2634 | 0.014389 | 5.4131 | 0.06064%
LUCERNE 110676850 | LUCERNE 1106 | HUMBOLDT | 2.0465 | 10 | 61.3% | 0 | 3 | 55.89% | 0% | 0 | 0.014386 | 1 | 2.5722 | 0.037005 | Low | Low | Medium | 2611 | 2635 | 0.014386 | 5.3987 | 0.06048%
SNEATH LANE 110134438 | SNEATH LANE 1101 | PENINSULA | 1.6791 | 10 | 46% | 1 | 0 | 33.32% | 0% | 0 | 0.014366 | 1 | 4.1734 | 0.059955 | Low | Low | High | 2184 | 2636 | 0.014366 | 5.3843 | 0.06032%
TULUCAY 1101628 | TULUCAY 1101 | NORTH BAY | 4.4167 | 65.2777 | 26.9% | 0 | 1 | 50.38% | 0% | 0 | 0.014345 | 1 | 3.4912 | 0.050083 | Low | Low | High | 2350 | 2637 | 0.014345 | 5.37 | 0.06016%
ROSSMOOR 11018132 | ROSSMOOR 1101 | DIABLO | 2.3517 | 13.1594 | 38.14% | 0 | 7 | 64.04% | 0% | 0 | 0.014331 | 1 | 3.0841 | 0.044197 | Low | Low | High | 2454 | 2638 | 0.014331 | 5.3556 | 0.06%
OAKLAND X 1104CB | OAKLAND X 1104 | EAST BAY | 1.3072 | 10 | 2.074% | 0 | 2 | 53.76% | 24.1% | 0 | 0.014319 | 1 | 4.5195 | 0.064715 | Low | Low | High | 2103 | 2639 | 0.014319 | 5.3413 | 0.05984%
WILLITS 11044650 | WILLITS 1104 | HUMBOLDT | 2.8566 | 16.3398 | 61.51% | 0 | 4 | 48.68% | 0% | 0 | 0.014299 | 1 | 2.3934 | 0.034224 | Low | Low | Medium | 2675 | 2640 | 0.014299 | 5.327 | 0.05968%
OAKLAND J 1105CR256 | OAKLAND J 1105 | EAST BAY | 1.5352 | 10 | 0.8551% | 1 | 0 | 83.22% | 0% | 0 | 0.014281 | 1 | 3.3396 | 0.047692 | Low | Low | High | 2386 | 2641 | 0.014281 | 5.3127 | 0.05952%
POINT MORETTI 110183716 | POINT MORETTI 1101 | CENTRAL COAST | 2.5672 | 18.0705 | 6.579% | 5 | 0 | 94.36% | 0% | 0 | 0.014279 | 1 | 1.6002 | 0.022849 | Low | Low | Low | 2943 | 2642 | 0.014279 | 5.2984 | 0.05936%
MORAGA 1103CB | MORAGA 1103 | DIABLO | 1.341 | 16.5323 | 0% | 6 | 3 | 21.01% | 11.54% | 0 | 0.01426 | 1 | 3.9729 | 0.056652 | Low | Low | High | 2231 | 2643 | 0.01426 | 5.2841 | 0.0592%
DUNBAR 1101160 | DUNBAR 1101 | SONOMA | 4.1387 | 21.8951 | 29.76% | 0 | 0 | 62.23% | 10.35% | 0 | 0.01425 | 1 | 2.486 | 0.035427 | Low | Low | Medium | 2642 | 2644 | 0.01425 | 5.2699 | 0.05904%
CHESTER 1101CB | CHESTER 1101 | NORTH VALLEY | 2.5695 | 10 | 96.88% | 0 | 0 | 31.91% | 0% | 0 | 0.01425 | 1 | 2.4772 | 0.035299 | Low | Low | Medium | 2645 | 2645 | 0.01425 | 5.2556 | 0.05888%
WISE 11011404 | WISE 1101 | SIERRA | 2.2264 | 13.0264 | 54.75% | 0 | 1 | 62.41% | 0% | 0 | 0.014247 | 1 | 2.3816 | 0.03393 | Low | Low | Medium | 2684 | 2646 | 0.014247 | 5.2414 | 0.05872%
CLAY 110359714 | CLAY 1103 | STOCKTON | 4.4126 | 25.7757 | 4.31% | 0 | 1 | 95.22% | 0% | 0 | 0.014243 | 1 | 3.1342 | 0.044639 | Low | Low | High | 2445 | 2647 | 0.014243 | 5.2271 | 0.05856%
SAN CARLOS 110475210 | SAN CARLOS 1104 | PENINSULA | 0.38485 | 10 | 11.56% | 0 | 1 | 100% | 0% | 0 | 0.01424 | 1 | 3.7871 | 0.053927 | Low | Low | High | 2272 | 2648 | 0.01424 | 5.2129 | 0.0584%
HOOPA 110193038 | HOOPA 1101 | HUMBOLDT | 0.1684 | 40.7085 | 100% | 0 | 1 | 6.029% | 0% | 0 | 0.014214 | 1 | 2.0078 | 0.028539 | Low | Low | Low | 2809 | 2649 | 0.014214 | 5.1986 | 0.05824%
NORTH BRANCH 1101CB | NORTH BRANCH 1101 | STOCKTON | 10.7662 | 27.7002 | 39.92% | 0 | 5 | 56% | 0% | 0 | 0.014214 | 1 | 2.5951 | 0.036887 | Low | Low | Medium | 2616 | 2650 | 0.014214 | 5.1844 | 0.05808%
ECHO SUMMIT 1101344250 | ECHO SUMMIT 1101 | (blank) | 0.80694 | 10 | 100% | 1 | 0 | 14.32% | 0% | 0 | 0.014197 | 1 | 2.0707 | 0.029398 | Low | Low | Low | 2789 | 2651 | 0.014197 | 5.1702 | 0.05792%
ROSSMOOR 110845268 | ROSSMOOR 1108 | DIABLO | 3.7726 | 24.3862 | 31.05% | 0 | 7 | 47.92% | 0% | 0 | 0.014195 | 1 | 4.0289 | 0.057189 | Low | Low | High | 2220 | 2652 | 0.014195 | 5.156 | 0.05776%
HATTON 1102648928 | HATTON 1102 | CENTRAL COAST | 2.8842 | 29.9397 | 0% | 2 | 4 | 59.99% | 0% | 0 | 0.014193 | 1 | 2.8013 | 0.039758 | Low | Low | Medium | 2543 | 2653 | 0.014193 | 5.1418 | 0.0576%
ALHAMBRA 110581514 | ALHAMBRA 1105 | DIABLO | 2.5203 | 17.3445 | 21.67% | 2 | 3 | 52.7% | 0% | 0 | 0.014173 | 1 | 3.0995 | 0.043928 | Low | Low | High | 2465 | 2654 | 0.014173 | 5.1276 | 0.05744%
SOLEDAD 21027562 | SOLEDAD 2102 | CENTRAL COAST | 1.9641 | 22.7828 | 92.71% | 0 | 0 | 25.93% | 0% | 0 | 0.014154 | 1 | 2.6794 | 0.037924 | Low | Low | Medium | 2586 | 2655 | 0.014154 | 5.1134 | 0.05729%
CAYETANO 2111CB | CAYETANO 2111 | MISSION | 5.2576 | 70.3707 | 27.25% | 0 | 1 | 45% | 0% | 0 | 0.014119 | 1 | 2.9536 | 0.041701 | Low | Low | Medium | 2504 | 2656 | 0.014119 | 5.0993 | 0.05713%
RALSTON 1102CB | RALSTON 1102 | PENINSULA | 1.0812 | 10 | 71.25% | 0 | 0 | 25.36% | 0% | 0 | 0.014111 | 1 | 3.4704 | 0.04897 | Low | Low | High | 2368 | 2657 | 0.014111 | 5.0852 | 0.05697%
RIDGE 0402CB | RIDGE 0402 | EAST BAY | 1.6674 | 10 | 31.81% | 1 | 0 | 69.66% | 0% | 0 | 0.014084 | 1 | 4.0946 | 0.05767 | Low | Low | High | 2211 | 2658 | 0.014084 | 5.0711 | 0.05681%
HATTON 110137088 | HATTON 1101 | CENTRAL COAST | 4.1243 | 13.8122 | 55.58% | 4 | 4 | 48.38% | 0% | 0 | 0.014072 | 1 | 2.9011 | 0.040823 | Low | Low | Medium | 2520 | 2659 | 0.014072 | 5.057 | 0.05665%
LLAGAS 2107XR188 | LLAGAS 2107 | SAN JOSE | 2.7329 | 20.244 | 46.06% | 0 | 0 | 43.36% | 5.395% | 0 | 0.014067 | 1 | 3.2148 | 0.045223 | Low | Low | High | 2434 | 2660 | 0.014067 | 5.0429 | 0.05649%
LOS OSITOS 21027470 | LOS OSITOS 2102 | CENTRAL COAST | 2.5834 | 65.4453 | 76.6% | 0 | 0 | 9.453% | 0% | 0 | 0.014067 | 1 | 2.1688 | 0.030509 | Low | Low | Low | 2758 | 2661 | 0.014067 | 5.0288 | 0.05634%
OAKLAND J 1105CR150 | OAKLAND J 1105 | EAST BAY | 0.4695 | 10 | 10.02% | 0 | 1 | 100% | 0% | 0 | 0.014063 | 1 | 3.265 | 0.045915 | Low | Low | High | 2422 | 2662 | 0.014063 | 5.0148 | 0.05618%
SNEATH LANE 110796530 | SNEATH LANE 1107 | PENINSULA | 0.71298 | 10 | 94.87% | 0 | 0 | 32.23% | 0% | 0 | 0.014063 | 1 | 3.3534 | 0.047158 | Low | Low | High | 2397 | 2663 | 0.014063 | 5.0007 | 0.05602%
SAN RAFAEL 1109CB | SAN RAFAEL 1109 | NORTH BAY | 0.026389 | 10 | 100% | 0 | 0 | 0.5374% | 0% | 0 | 0.013951 | 1 | 3.4403 | 0.047995 | Low | Low | High | 2380 | 2664 | 0.013951 | 4.9866 | 0.05586%
TIDEWATER 210614072 | TIDEWATER 2106 | DIABLO | 3.6661 | 10 | 16.78% | 0 | 0 | 95.56% | 0% | 0 | 0.013929 | 1 | 3.718 | 0.051789 | Low | Low | High | 2316 | 2665 | 0.013929 | 4.9727 | 0.05571%
RESERVATION ROAD 1101CB | RESERVATION ROAD 1101 | CENTRAL COAST | 3.6814 | 10 | 45.32% | 0 | 3 | 39.08% | 0% | 0 | 0.013924 | 1 | 1.799 | 0.025049 | Low | Low | Low | 2880 | 2666 | 0.013924 | 4.9588 | 0.05555%
VALLEY VIEW 1106CB | VALLEY VIEW 1106 | EAST BAY | 3.4767 | 45.2583 | 0.9386% | 0 | 1 | 68.92% | 0% | 0 | 0.013903 | 1 | 4.0593 | 0.056436 | Low | Low | High | 2236 | 2667 | 0.013903 | 4.9448 | 0.0554%
IGNACIO 1101CB | IGNACIO 1101 | NORTH BAY | 1.394 | 10 | 18.69% | 0 | 2 | 76.2% | 0% | 0 | 0.013891 | 1 | 3.3089 | 0.045965 | Low | Low | High | 2421 | 2668 | 0.013891 | 4.9309 | 0.05524%
MARTELL 110299214 | MARTELL 1102 | STOCKTON | 0.5909 | 10 | 69.1% | 1 | 4 | 29.13% | 0% | 0 | 0.013885 | 1 | 3.016 | 0.041876 | Low | Low | Medium | 2498 | 2669 | 0.013885 | 4.917 | 0.05508%
VINEYARD 2110CB | VINEYARD 2110 | MISSION | 5.8656 | 49.5436 | 17.49% | 1 | 0 | 52.96% | 0% | 0 | 0.013877 | 1 | 3.1806 | 0.044138 | Low | Low | High | 2455 | 2670 | 0.013877 | 4.9032 | 0.05493%
BASALT 11065030 | BASALT 1106 | NORTH BAY | 3.3103 | 53.7565 | 71.04% | 0 | 0 | 20.61% | 0% | 0 | 0.013874 | 1 | 3.1305 | 0.043433 | Low | Low | High | 2469 | 2671 | 0.013874 | 4.8893 | 0.05477%
SUNOL 110111587 | SUNOL 1101 | MISSION | 0.25848 | 10 | 100% | 0 | 1 | 24.35% | 0% | 0 | 0.013849 | 1 | 2.7479 | 0.038054 | Low | Low | Medium | 2582 | 2672 | 0.013849 | 4.8754 | 0.05462%
VIEJO 2204CB | VIEJO 2204 | CENTRAL COAST | 2.2166 | 10 | 31.01% | 10 | 1 | 54.6% | 0% | 0 | 0.013845 | 1 | 3.0559 | 0.04231 | Low | Low | Medium | 2490 | 2673 | 0.013845 | 4.8616 | 0.05446%
HATTON 11029642 | HATTON 1102 | CENTRAL COAST | 1.1982 | 10 | 4.477% | 2 | 1 | 100% | 0% | 0 | 0.013798 | 1 | 2.6508 | 0.036576 | Low | Low | Medium | 2620 | 2674 | 0.013798 | 4.8477 | 0.05431%
PASO ROBLES 110355374 | PASO ROBLES 1103 | LOS PADRES | 2.104 | 28.3586 | 87.29% | 0 | 2 | 19.75% | 0% | 0 | 0.013788 | 1 | 2.1323 | 0.0294 | Low | Low | Low | 2788 | 2675 | 0.013788 | 4.8339 | 0.05415%
UKIAH 1114528 | UKIAH 1114 | HUMBOLDT | 2.0763 | 22.6279 | 79.13% | 0 | 2 | 16.87% | 0% | 0 | 0.013763 | 1 | 2.3375 | 0.032173 | Low | Low | Medium | 2721 | 2676 | 0.013763 | 4.8201 | 0.054%
COTATI 1102CB | COTATI 1102 | SONOMA | 1.3007 | 52.8482 | 0.4591% | 0 | 0 | 64.8% | 0% | 0 | 0.013707 | 1 | 2.9311 | 0.040175 | Low | Low | Medium | 2535 | 2677 | 0.013707 | 4.8064 | 0.05385%
MESA 1101CB | MESA 1101 | LOS PADRES | 13.1474 | 48.8211 | 12.29% | 0 | 3 | 51.32% | 0% | 0 | 0.013679 | 1 | 2.5227 | 0.034509 | Low | Low | Medium | 2663 | 2678 | 0.013679 | 4.7927 | 0.05369%
HATTON 1102CB | HATTON 1102 | CENTRAL COAST | 2.1206 | 10 | 0.1341% | 1 | 3 | 45.47% | 0% | 0 | 0.013538 | 1 | 3.1114 | 0.042121 | Low | Low | High | 2493 | 2679 | 0.013538 | 4.779 | 0.05354%
LAS AROMAS 04013342 | LAS AROMAS 0401 | DIABLO | 2.2911 | 10 | 3.001% | 3 | 0 | 100% | 0% | 0 | 0.013529 | 1 | 3.2617 | 0.044129 | Low | Low | High | 2457 | 2680 | 0.013529 | 4.7654 | 0.05339%
MORGAN HILL 2110XR326 | MORGAN HILL 2110 | SAN JOSE | 2.054 | 29.8956 | 63.47% | 0 | 2 | 9.633% | 0% | 0 | 0.013515 | 1 | 2.63 | 0.035544 | Low | Low | Medium | 2639 | 2681 | 0.013515 | 4.7519 | 0.05324%
MENDOCINO 110137462 | MENDOCINO 1101 | HUMBOLDT | 2.449 | 10 | 46.73% | 0 | 2 | 50.22% | 0% | 0 | 0.0135 | 1 | 2.6397 | 0.035636 | Low | Low | Medium | 2634 | 2682 | 0.0135 | 4.7384 | 0.05308%
MILPITAS 1109XR374 | MILPITAS 1109 | SAN JOSE | 0.65242 | 10 | 100% | 0 | 1 | 21.62% | 0% | 0 | 0.013479 | 1 | 3.3325 | 0.044919 | Low | Low | High | 2439 | 2683 | 0.013479 | 4.7249 | 0.05293%
MORAGA 1103E510R | MORAGA 1103 | DIABLO | 1.3196 | 10 | 100% | 0 | 1 | 21.61% | 0% | 0 | 0.013477 | 1 | 4.475 | 0.060311 | Low | Low | High | 2178 | 2684 | 0.013477 | 4.7114 | 0.05278%
ROB ROY 210512474 | ROB ROY 2105 | CENTRAL COAST | 2.374 | 10 | 59.61% | 0 | 1 | 28.06% | 0% | 0 | 0.013458 | 1 | 3.02 | 0.040644 | Low | Low | Medium | 2523 | 2685 | 0.013458 | 4.6979 | 0.05263%
CHESTER 1102CB | CHESTER 1102 | NORTH VALLEY | 0.32002 | 10 | 100% | 0 | 0 | 10.17% | 0% | 0 | 0.01345 | 1 | 2.6792 | 0.036036 | Low | Low | Medium | 2628 | 2686 | 0.01345 | 4.6845 | 0.05248%
WYANDOTTE 110737472 | WYANDOTTE 1107 | NORTH VALLEY | 6.2847 | 13.7184 | 63.51% | 2 | 3 | 42.06% | 0% | 0 | 0.013447 | 1 | 3.6893 | 0.049612 | Low | Low | High | 2358 | 2687 | 0.013447 | 4.671 | 0.05233%
OILFIELDS 1103N42 | OILFIELDS 1103 | CENTRAL COAST | 2.2461 | 52.6729 | 47.6% | 0 | 0 | 37.49% | 0% | 0 | 0.013447 | 1 | 0.061363 | 0.00082516 | Low | Low | Low | 3180 | 2688 | 0.013447 | 4.6576 | 0.05218%
ROB ROY 2105CB | ROB ROY 2105 | CENTRAL COAST | 0.78923 | 10 | 41.07% | 2 | 0 | 55.78% | 0% | 0 | 0.013414 | 1 | 2.895 | 0.038833 | Low | Low | Medium | 2564 | 2689 | 0.013414 | 4.6441 | 0.05203%
PERRY 1101W10 | PERRY 1101 | LOS PADRES | 1.7167 | 22.2223 | 1.272% | 0 | 2 | 91.87% | 0% | 0 | 0.013398 | 1 | 3.1157 | 0.041744 | Low | Low | High | 2501 | 2690 | 0.013398 | 4.6307 | 0.05188%
NEWBURG 1131CB | NEWBURG 1131 | HUMBOLDT | 3.0239 | 26.9176 | 14.49% | 0 | 2 | 24.41% | 0% | 0 | 0.013392 | 1 | 2.916 | 0.03905 | Low | Low | Medium | 2558 | 2691 | 0.013392 | 4.6173 | 0.05173%
VALLEY VIEW 1106P176 | VALLEY VIEW 1106 | EAST BAY | 0.884 | 14.838 | 80.1% | 1 | 0 | 21.45% | 0% | 0 | 0.013387 | 1 | 4.2737 | 0.057211 | Low | Low | High | 2219 | 2692 | 0.013387 | 4.6039 | 0.05158%
CLAY 110184572 | CLAY 1101 | STOCKTON | 1.3752 | 10 | 53.62% | 0 | 0 | 60.97% | 0% | 0 | 0.013356 | 1 | 3.473 | 0.046384 | Low | Low | High | 2412 | 2693 | 0.013356 | 4.5906 | 0.05143%
SUNOL 1101MR169 | SUNOL 1101 | MISSION | 3.8873 | 57.3439 | 37.68% | 0 | 0 | 41.76% | 0% | 0 | 0.013353 | 1 | 1.6919 | 0.022592 | Low | Low | Low | 2953 | 2694 | 0.013353 | 4.5772 | 0.05128%
PURISIMA 1101Y80 | PURISIMA 1101 | LOS PADRES | 1.0399 | 27.8619 | 91.46% | 0 | 0 | 17.5% | 0% | 0 | 0.01334 | 1 | 3.819 | 0.050944 | Low | Low | High | 2332 | 2695 | 0.01334 | 4.5638 | 0.05113%
SHINGLE SPRINGS 1104CB | SHINGLE SPRINGS 1104 | SIERRA | 0.43321 | 10 | 56.49% | 2 | 0 | 18.41% | 23.01% | 0 | 0.013336 | 1 | 3.3035 | 0.044055 | Low | Low | High | 2460 | 2696 | 0.013336 | 4.5505 | 0.05098%
ALTO 112265474 | ALTO 1122 | NORTH BAY | 2.1481 | 10 | 21.89% | 2 | 1 | 58.84% | 6.137% | 0 | 0.013328 | 1 | 3.89 | 0.051845 | Low | Low | High | 2313 | 2697 | 0.013328 | 4.5372 | 0.05083%
KONOCTI 11084037 | KONOCTI 1108 | HUMBOLDT | 0.3878 | 10 | 100% | 0 | 0 | 22.52% | 0% | 0 | 0.013321 | 1 | 2.7262 | 0.036316 | Low | Low | Medium | 2623 | 2698 | 0.013321 | 4.5238 | 0.05068%
CURTIS 17019230 | CURTIS 1701 | YOSEMITE | 2.2694 | 10 | 15.95% | 1 | 2 | 72.76% | 0% | 0 | 0.013303 | 1 | 3.3462 | 0.044513 | Low | Low | High | 2448 | 2699 | 0.013303 | 4.5105 | 0.05053%
CORONA 11034446 | CORONA 1103 | SONOMA | 0.968 | 50.7747 | 83.54% | 0 | 0 | 7.888% | 0% | 0 | 0.013274 | 1 | 2.8291 | 0.037555 | Low | Low | Medium | 2593 | 2700 | 0.013274 | 4.4972 | 0.05038%
COPPERMINE 1104R755 | COPPERMINE 1104 | FRESNO | 8.1519 | 17.5841 | 96.77% | 0 | 3 | 13.19% | 0% | 0 | 0.013252 | 1 | 1.537 | 0.020367 | Low | Low | Low | 2997 | 2701 | 0.013252 | 4.4839 | 0.05023%
SAN RAFAEL 1109418 | SAN RAFAEL 1109 | NORTH BAY | 4.3553 | 10 | 55.54% | 4 | 2 | 35.66% | 0% | 0 | 0.013234 | 1 | 4.6368 | 0.061362 | Low | Low | High | 2162 | 2702 | 0.013234 | 4.4707 | 0.05008%
POINT ARENA 11013702 | POINT ARENA 1101 | HUMBOLDT | 4.3225 | 19.0711 | 4.681% | 4 | 1 | 86.66% | 0% | 0 | 0.013218 | 1 | 2.4572 | 0.03248 | Low | Low | Medium | 2712 | 2703 | 0.013218 | 4.4575 | 0.04994%
EDES 1112CR306 | EDES 1112 | EAST BAY | 1.0069 | 10 | 0% | 3 | 0 | 100% | 0% | 0 | 0.013203 | 1 | 3.2812 | 0.043321 | Low | Low | High | 2471 | 2704 | 0.013203 | 4.4442 | 0.04979%
LOS GATOS 1102CB | LOS GATOS 1102 | DE ANZA | 1.1034 | 10 | 59.61% | 1 | 4 | 18.46% | 0% | 0 | 0.013194 | 1 | 4.0562 | 0.053517 | Low | Low | High | 2279 | 2705 | 0.013194 | 4.431 | 0.04964%
MC KEE 1107XR010 | MC KEE 1107 | SAN JOSE | 2.6945 | 34.7956 | 81.62% | 0 | 0 | 19.75% | 0% | 0 | 0.013193 | 1 | 3.8599 | 0.050922 | Low | Low | High | 2334 | 2706 | 0.013193 | 4.4178 | 0.04949%
POSO MOUNTAIN 2104CB | POSO MOUNTAIN 2104 | KERN | 5.3916 | 10 | 6.227% | 0 | 6 | 72.59% | 0% | 0 | 0.013157 | 1 | 2.8181 | 0.037076 | Low | Low | Medium | 2610 | 2707 | 0.013157 | 4.4046 | 0.04934%
PERRY 1101V72 | PERRY 1101 | LOS PADRES | 5.7537 | 10 | 2.358% | 4 | 2 | 65.46% | 0% | 0 | 0.013146 | 1 | 4.0035 | 0.052631 | Low | Low | High | 2298 | 2708 | 0.013146 | 4.3915 | 0.0492%
MORRO BAY 110248384 | MORRO BAY 1102 | LOS PADRES | 0.22159 | 10 | 0% | 1 | 1 | 100% | 0% | 0 | 0.013132 | 1 | 4.1848 | 0.054953 | Low | Low | High | 2260 | 2709 | 0.013132 | 4.3783 | 0.04905%
GUALALA 1111402866 | GUALALA 1111 | HUMBOLDT | 1.5915 | 10 | 0% | 1 | 1 | 100% | 0% | 0 | 0.013132 | 1 | 1.557 | 0.020445 | Low | Low | Low | 2993 | 2709 | 0.013132 | 4.3652 | 0.0489%
POINT ARENA 11011296 | POINT ARENA 1101 | HUMBOLDT | 2.101 | 59.6296 | 9.522% | 3 | 3 | 37.92% | 0% | 0 | 0.013105 | 1 | 1.4612 | 0.019149 | Low | Low | Low | 3023 | 2711 | 0.013105 | 4.3521 | 0.04876%
MESA 1103M68 | MESA 1103 | LOS PADRES | 0.22844 | 10 | 100% | 0 | 0 | 7.509% | 0% | 0 | 0.013101 | 1 | 3.2134 | 0.042099 | Low | Low | High | 2494 | 2712 | 0.013101 | 4.339 | 0.04861%
RED BLUFF 11041630 | RED BLUFF 1104 | NORTH VALLEY | 2.5495 | 10 | 100% | 0 | 1 | 18.04% | 0% | 0 | 0.01301 | 1 | 1.715 | 0.022313 | Low | Low | Low | 2958 | 2713 | 0.01301 | 4.3259 | 0.04846%
LUCERNE 11031280 | LUCERNE 1103 | HUMBOLDT | 8.886 | 18.4647 | 53.77% | 0 | 7 | 37.48% | 0% | 0 | 0.012974 | 1 | 2.1053 | 0.027314 | Low | Low | Low | 2829 | 2714 | 0.012974 | 4.3129 | 0.04832%
WYANDOTTE 1105329930 | WYANDOTTE 1105 | NORTH VALLEY | 7.9312 | 11.1268 | 28.89% | 0 | 1 | 75.51% | 0% | 0 | 0.01297 | 1 | 2.5915 | 0.033613 | Low | Low | Medium | 2689 | 2715 | 0.01297 | 4.2999 | 0.04817%
PLACERVILLE 1109CB | PLACERVILLE 1109 | SIERRA | 0.020146 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.012961 | 1 | 2.6978 | 0.034966 | Low | Low | Medium | 2650 | 2716 | 0.012961 | 4.2869 | 0.04803%
GEYSERVILLE 1102756 | GEYSERVILLE 1102 | SONOMA | 0.58953 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.012961 | 1 | 1.2459 | 0.016148 | Low | Low | Low | 3078 | 2716 | 0.012961 | 4.274 | 0.04788%
HIGGINS 1107CB | HIGGINS 1107 | SIERRA | 4.6439 | 10 | 81.31% | 3 | 3 | 24.48% | 0% | 0 | 0.012908 | 1 | 3.3796 | 0.043625 | Low | Low | High | 2468 | 2718 | 0.012908 | 4.261 | 0.04774%
WILLITS 1102CB | WILLITS 1102 | HUMBOLDT | 5.2584 | 15.1568 | 26.36% | 0 | 4 | 54.45% | 0% | 0 | 0.01287 | 1 | 2.3959 | 0.030834 | Low | Low | Medium | 2747 | 2719 | 0.01287 | 4.2481 | 0.04759%
GEYSERVILLE 1101122 | GEYSERVILLE 1101 | SONOMA | 3.5712 | 48.4332 | 60.55% | 0 | 3 | 18.96% | 0% | 0 | 0.012864 | 1 | 2.1153 | 0.027211 | Low | Low | Low | 2833 | 2720 | 0.012864 | 4.2352 | 0.04745%
EDES 1112CR100 | EDES 1112 | EAST BAY | 3.3566 | 10 | 0% | 1 | 0 | 100% | 0% | 0 | 0.012862 | 1 | 3.2337 | 0.041593 | Low | Low | High | 2505 | 2721 | 0.012862 | 4.2224 | 0.0473%
HALSEY 11022514 | HALSEY 1102 | SIERRA | 9.2843 | 10 | 42.43% | 1 | 2 | 47.49% | 0% | 0 | 0.012855 | 1 | 2.7818 | 0.035761 | Low | Low | Medium | 2632 | 2722 | 0.012855 | 4.2095 | 0.04716%
CABRILLO 1104CB | CABRILLO 1104 | LOS PADRES | 4.9085 | 16.6076 | 47.38% | 0 | 1 | 28.73% | 0% | 0 | 0.012822 | 1 | 3.7934 | 0.048641 | Low | Low | High | 2374 | 2723 | 0.012822 | 4.1966 | 0.04701%
SAN LUIS OBISPO 110788962 | SAN LUIS OBISPO 1107 | LOS PADRES | 1.6209 | 48.7477 | 22.43% | 0 | 1 | 40.61% | 0% | 0 | 0.012815 | 1 | 2.9485 | 0.037786 | Low | Low | Medium | 2588 | 2724 | 0.012815 | 4.1838 | 0.04687%
FORT ROSS 1121560 | FORT ROSS 1121 | SONOMA | 5.3342 | 23.1043 | 0.06425% | 1 | 0 | 90.51% | 0% | 0 | 0.0128 | 1 | 1.2567 | 0.016087 | Low | Low | Low | 3081 | 2725 | 0.0128 | 4.171 | 0.04673%
CLAY 11037142 | CLAY 1103 | STOCKTON | 4.4879 | 10 | 67.68% | 2 | 0 | 29.1% | 0% | 0 | 0.012796 | 1 | 2.4498 | 0.031348 | Low | Low | Medium | 2739 | 2726 | 0.012796 | 4.1582 | 0.04658%
DESCHUTES 1101CB | DESCHUTES 1101 | NORTH VALLEY | 4.1985 | 15.36 | 72.74% | 0 | 0 | 36.89% | 0% | 0 | 0.012752 | 1 | 2.792 | 0.035602 | Low | Low | Medium | 2637 | 2727 | 0.012752 | 4.1454 | 0.04644%
RALSTON 11029126 | RALSTON 1102 | PENINSULA | 0.049841 | 10 | 100% | 0 | 1 | 2.638% | 0% | 0 | 0.012746 | 1 | 3.5205 | 0.044873 | Low | Low | High | 2440 | 2728 | 0.012746 | 4.1327 | 0.0463%
HICKS 2101XR548 | HICKS 2101 | SAN JOSE | 1.763 | 53.1133 | 61.37% | 0 | 0 | 20.35% | 0% | 0 | 0.012735 | 1 | 2.9304 | 0.037318 | Low | Low | Medium | 2602 | 2729 | 0.012735 | 4.1199 | 0.04615%
SAN RAFAEL 11042651 | SAN RAFAEL 1104 | NORTH BAY | 0.79099 | 10 | 0% | 1 | 1 | 96.62% | 0% | 0 | 0.0127 | 1 | 4.1495 | 0.0527 | Low | Low | High | 2297 | 2730 | 0.0127 | 4.1072 | 0.04601%
OAKLAND K 1103CR422 | OAKLAND K 1103 | EAST BAY | 1.8547 | 10 | 4.055% | 0 | 3 | 90.41% | 0% | 0 | 0.0127 | 1 | 4.4523 | 0.056544 | Low | Low | High | 2233 | 2731 | 0.0127 | 4.0945 | 0.04587%
CAROLANDS 0404 | CAROLANDS 0404 | PENINSULA | 0.066741 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.3793 | 0.042901 | Low | Low | High | 2478 | 2732 | 0.012695 | 4.0818 | 0.04573%
POTTER VALLEY P H 1105990354 | POTTER VALLEY P H 1105 | HUMBOLDT | 0.0040482 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.331 | 0.016897 | Low | Low | Low | 3065 | 2732 | 0.012695 | 4.0691 | 0.04559%
POTTER VALLEY PH 11054634 | POTTER VALLEY PH 1105 | HUMBOLDT | 0.0052407 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.3294 | 0.016878 | Low | Low | Low | 3067 | 2732 | 0.012695 | 4.0564 | 0.04544%
EL CERRITO G 1110BR236 | EL CERRITO G 1110 | EAST BAY | 0.52869 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.7576 | 0.0604 | Low | Low | High | 2175 | 2735 | 0.012695 | 4.0437 | 0.0453%
FLORENCE 0401CR220 | FLORENCE 0401 | EAST BAY | 0.0014212 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.5363 | 0.057589 | Low | Low | High | 2213 | 2735 | 0.012695 | 4.031 | 0.04516%
SAN CARLOS 11049048 | SAN CARLOS 1104 | PENINSULA | 0.01529 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.4369 | 0.056328 | Low | Low | High | 2238 | 2735 | 0.012695 | 4.0183 | 0.04502%
OAKLAND K 1104468 | OAKLAND K 1104 | EAST BAY | 0.0028424 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.4321 | 0.056268 | Low | Low | High | 2241 | 2735 | 0.012695 | 4.0056 | 0.04487%
MORRO BAY 110298906 | MORRO BAY 1102 | LOS PADRES | 0.034162 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.3164 | 0.054798 | Low | Low | High | 2262 | 2735 | 0.012695 | 3.9929 | 0.04473%
MORRO BAY 110242062 | MORRO BAY 1102 | LOS PADRES | 0.13997 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.236 | 0.053777 | Low | Low | High | 2274 | 2735 | 0.012695 | 3.9802 | 0.04459%
TASSAJARA 2104 | TASSAJARA 2104 | DIABLO | 0.070201 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.0947 | 0.051984 | Low | Low | High | 2308 | 2735 | 0.012695 | 3.9675 | 0.04445%
BERKELEY F 1105BR166 | BERKELEY F 1105 | EAST BAY | 0.038193 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.0059 | 0.050857 | Low | Low | High | 2337 | 2735 | 0.012695 | 3.9548 | 0.04431%
EL CERRITO G 1105BR164 | EL CERRITO G 1105 | EAST BAY | 0.056936 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.9936 | 0.0507 | Low | Low | High | 2340 | 2735 | 0.012695 | 3.9421 | 0.04416%
SAN RAMON 21077742 | SAN RAMON 2107 | MISSION | 0.0028424 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.9835 | 0.050572 | Low | Low | High | 2343 | 2735 | 0.012695 | 3.9294 | 0.04402%
VIEJO 220255787 | VIEJO 2202 | CENTRAL COAST | 0.036656 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.6721 | 0.046619 | Low | Low | High | 2404 | 2735 | 0.012695 | 3.9167 | 0.04388%
SAN LEANDRO U 1109CR284 | SAN LEANDRO U 1109 | MISSION | 0.93355 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.3989 | 0.043151 | Low | Low | High | 2474 | 2735 | 0.012695 | 3.904 | 0.04374%
BAY MEADOWS 2102 | BAY MEADOWS 2102 | PENINSULA | 0.027395 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.1881 | 0.040474 | Low | Low | High | 2529 | 2735 | 0.012695 | 3.8913 | 0.04359%
SAN LUIS OBISPO 110742048 | SAN LUIS OBISPO 1107 | LOS PADRES | 0.025219 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0883 | 0.039207 | Low | Low | High | 2554 | 2735 | 0.012695 | 3.8786 | 0.04345%
SAN LUIS OBISPO 1107V08 | SAN LUIS OBISPO 1107 | LOS PADRES | 0.024874 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0856 | 0.039173 | Low | Low | High | 2556 | 2735 | 0.012695 | 3.866 | 0.04331%
DEL MONTE 21032204 | DEL MONTE 2103 | CENTRAL COAST | 0.36868 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0732 | 0.039015 | Low | Low | Medium | 2560 | 2735 | 0.012695 | 3.8533 | 0.04317%
PEABODY 210818182 | PEABODY 2108 | SACRAMENTO | 0.013085 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0555 | 0.03879 | Low | Low | Medium | 2565 | 2735 | 0.012695 | 3.8406 | 0.04303%
HIGGINS 1110 | HIGGINS 1110 | SIERRA | 0.035539 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0246 | 0.038398 | Low | Low | Medium | 2576 | 2735 | 0.012695 | 3.8279 | 0.04288%
MILPITAS 110962157 | MILPITAS 1109 | SAN JOSE | 0.044828 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.9508 | 0.037462 | Low | Low | Medium | 2595 | 2735 | 0.012695 | 3.8152 | 0.04274%
FORT ORD 21069658 | FORT ORD 2106 | CENTRAL COAST | 0.097044 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.7847 | 0.035353 | Low | Low | Medium | 2644 | 2735 | 0.012695 | 3.8025 | 0.0426%
POINT MORETTI 110135874 | POINT MORETTI 1101 | CENTRAL COAST | 0.27376 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.4196 | 0.030718 | Low | Low | Medium | 2751 | 2735 | 0.012695 | 3.7898 | 0.04246%
PEORIA 1704 | PEORIA 1704 | YOSEMITE | 0.12912 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.3748 | 0.030148 | Low | Low | Medium | 2769 | 2735 | 0.012695 | 3.7771 | 0.04231%
MARIPOSA 210210250 | MARIPOSA 2102 | YOSEMITE | 0.04003 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.119 | 0.026901 | Low | Low | Low | 2841 | 2735 | 0.012695 | 3.7644 | 0.04217%
COAST RD 0401CB | COAST RD 0401 | CENTRAL COAST | 0.04709 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.0553 | 0.026093 | Low | Low | Low | 2862 | 2735 | 0.012695 | 3.7517 | 0.04203%
NARROWS 2104CB | NARROWS 2104 | SIERRA | 0.002841 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.6515 | 0.020967 | Low | Low | Low | 2982 | 2735 | 0.012695 | 3.739 | 0.04189%
HOOPA 1101 | HOOPA 1101 | HUMBOLDT | 0.098699 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.5065 | 0.019125 | Low | Low | Low | 3026 | 2735 | 0.012695 | 3.7263 | 0.04175%
POTTER VALLEY P H 1104CB | POTTER VALLEY P H 1104 | HUMBOLDT | 0.077279 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.3279 | 0.016858 | Low | Low | Low | 3068 | 2735 | 0.012695 | 3.7136 | 0.0416%
POTTER VALLEY P H 11054634 | POTTER VALLEY P H 1105 | HUMBOLDT | 0.13813 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.3268 | 0.016844 | Low | Low | Low | 3069 | 2735 | 0.012695 | 3.7009 | 0.04146%
CORNING 110193362 | CORNING 1101 | NORTH VALLEY | 0.36788 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.0353 | 0.013144 | Low | Low | Low | 3124 | 2735 | 0.012695 | 3.6882 | 0.04132%
JOLON 110268034 | JOLON 1102 | CENTRAL COAST | 0.019914 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.71712 | 0.0091041 | Low | Low | Low | 3152 | 2735 | 0.012695 | 3.6755 | 0.04118%
PEORIA 1701 | PEORIA 1701 | YOSEMITE | 0.00281 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.6973 | 0.0088524 | Low | Low | Low | 3156 | 2735 | 0.012695 | 3.6628 | 0.04103%
HIGGINS 1108CB | HIGGINS 1108 | SIERRA | 0.020411 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.189 | 0.040485 | Low | Low | High | 2526 | 2766 | 0.012695 | 3.6501 | 0.04089%
CMC 1102CB | CMC 1102 | LOS PADRES | 0.46264 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.714 | 0.034455 | Low | Low | Medium | 2664 | 2766 | 0.012695 | 3.6374 | 0.04075%
HIGHLANDS 1101CB | HIGHLANDS 1101 | HUMBOLDT | 0.026418 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.6761 | 0.033974 | Low | Low | Medium | 2682 | 2766 | 0.012695 | 3.6247 | 0.04061%
CASTRO VALLEY 1101MR204 | CASTRO VALLEY 1101 | MISSION | 2.1197 | 29.3697 | 13.12% | 0 | 1 | 73.48% | 0% | 0 | 0.012645 | 1 | 4.251 | 0.053753 | Low | Low | High | 2275 | 2769 | 0.012645 | 3.612 | 0.04047%
EDENVALE 2107CB | EDENVALE 2107 | SAN JOSE | 0.73661 | 33.423 | 98.26% | 0 | 0 | 2.254% | 0% | 0 | 0.01259 | 1 | 2.8521 | 0.035908 | Low | Low | Medium | 2630 | 2770 | 0.01259 | 3.5994 | 0.04032%
LAS PULGAS 0401CB | LAS PULGAS 0401 | PENINSULA | 0.063561 | 10 | 100% | 0 | 1 | 1.053% | 0% | 0 | 0.012548 | 1 | 4.5955 | 0.057664 | Low | Low | High | 2212 | 2771 | 0.012548 | 3.5868 | 0.04018%
POSO MOUNTAIN 210448268 | POSO MOUNTAIN 2104 | KERN | 4.774 | 10 | 10.21% | 0 | 0 | 90.31% | 0% | 0 | 0.012535 | 1 | 2.7681 | 0.034699 | Low | Low | Medium | 2658 | 2772 | 0.012535 | 3.5743 | 0.04004%
SANTA YNEZ 1102320270 | SANTA YNEZ 1102 | LOS PADRES | 0.55315 | 10 | 90.55% | 0 | 2 | 19.74% | 0% | 0 | 0.012507 | 1 | 2.5016 | 0.031288 | Low | Low | Medium | 2743 | 2773 | 0.012507 | 3.5617 | 0.0399%
OREGON TRAIL 110346860 | OREGON TRAIL 1103 | NORTH VALLEY | 0.53541 | 10 | 100% | 0 | 0 | 16.12% | 0% | 0 | 0.012504 | 1 | 2.7222 | 0.034039 | Low | Low | Medium | 2681 | 2774 | 0.012504 | 3.5492 | 0.03976%
JESSUP 110338864 | JESSUP 1103 | NORTH VALLEY | 0.59204 | 10 | 100% | 1 | 3 | 7.85% | 0% | 0 | 0.012422 | 1 | 2.5473 | 0.031642 | Low | Low | Medium | 2732 | 2775 | 0.012422 | 3.5367 | 0.03962%
FRANKLIN 1101P138 | FRANKLIN 1101 | EAST BAY | 1.4993 | 10 | 0% | 0 | 0 | 97.65% | 0% | 0 | 0.012403 | 1 | 3.2 | 0.03969 | Low | Low | High | 2544 | 2776 | 0.012403 | 3.5243 | 0.03948%
HALF MOON BAY 11039112 | HALF MOON BAY 1103 | PENINSULA | 3.4704 | 36.5949 | 39.16% | 3 | 0 | 43.21% | 0% | 0 | 0.012394 | 1 | 3.3557 | 0.041589 | Low | Low | High | 2506 | 2777 | 0.012394 | 3.5119 | 0.03934%
PEABODY 2106CB | PEABODY 2106 | SACRAMENTO | 0.58049 | 10 | 53.14% | 0 | 0 | 53.74% | 0% | 0 | 0.012385 | 1 | 2.9801 | 0.036907 | Low | Low | Medium | 2615 | 2778 | 0.012385 | 3.4995 | 0.0392%
STONE CORRAL 11107784F | STONE CORRAL 1110 | FRESNO | 0.37155 | 63.2273 | 64.55% | 0 | 0 | 7.804% | 0% | 0 | 0.012359 | 1 | 2.6713 | 0.033015 | Low | Low | Medium | 2700 | 2779 | 0.012359 | 3.4871 | 0.03907%
COTATI 1102464 | COTATI 1102 | SONOMA | 1.2747 | 26.0788 | 66.97% | 0 | 1 | 15.73% | 0% | 0 | 0.012358 | 1 | 2.9928 | 0.036986 | Low | Low | Medium | 2612 | 2780 | 0.012358 | 3.4748 | 0.03893%
ELK 11014628 | ELK 1101 | HUMBOLDT | 2.8486 | 10 | 0% | 0 | 7 | 69.22% | 0% | 0 | 0.012349 | 1 | 2.1397 | 0.026424 | Low | Low | Low | 2854 | 2781 | 0.012349 | 3.4624 | 0.03879%
COVELO 1101536 | COVELO 1101 | HUMBOLDT | 0.011418 | 10 | 100% | 1 | 0 | 0.05103% | 0% | 0 | 0.012329 | 1 | 1.2835 | 0.015825 | Low | Low | Low | 3089 | 2782 | 0.012329 | 3.45 | 0.03865%
MORRO BAY 1101V66 | MORRO BAY 1101 | LOS PADRES | 3.6398 | 32.9293 | 34.81% | 0 | 0 | 22.6% | 18.48% | 0 | 0.01232 | 1 | 2.4197 | 0.029811 | Low | Low | Medium | 2779 | 2783 | 0.01232 | 3.4377 | 0.03851%
FITCH MOUNTAIN 11115060 | FITCH MOUNTAIN 1111 | SONOMA | 2.1624 | 43.6089 | 39.41% | 0 | 3 | 35.19% | 0% | 0 | 0.012308 | 1 | 2.9515 | 0.036326 | Low | Low | Medium | 2622 | 2784 | 0.012308 | 3.4254 | 0.03837%
BANGOR 110155206 | BANGOR 1101 | NORTH VALLEY | 2.9326 | 34.2156 | 61.32% | 1 | 0 | 28.49% | 0% | 0 | 0.012304 | 1 | 2.8829 | 0.03547 | Low | Low | Medium | 2640 | 2785 | 0.012304 | 3.4131 | 0.03824%
KERN OIL 11063301 | KERN OIL 1106 | KERN | 0.36257 | 10 | 100% | 0 | 0 | 1.116% | 0% | 0 | 0.012298 | 1 | 2.7994 | 0.034427 | Low | Low | Medium | 2667 | 2786 | 0.012298 | 3.4008 | 0.0381%
PANORAMA 1101CB | PANORAMA 1101 | NORTH VALLEY | 1.9355 | 10 | 100% | 0 | 2 | 10.24% | 0% | 0 | 0.012297 | 1 | 1.9576 | 0.024072 | Low | Low | Low | 2909 | 2787 | 0.012297 | 3.3885 | 0.03796%
SAN RAFAEL 1104CB | SAN RAFAEL 1104 | NORTH BAY | 2.4428 | 10 | 2.078% | 0 | 0 | 23.27% | 19.55% | 0 | 0.012295 | 1 | 4.9116 | 0.060389 | Low | Low | High | 2176 | 2788 | 0.012295 | 3.3762 | 0.03782%
RISING RIVER 11011532 | RISING RIVER 1101 | NORTH VALLEY | 3.0653 | 21.21 | 32.28% | 0 | 0 | 62.2% | 0% | 0 | 0.012255 | 1 | 1.2187 | 0.014936 | Low | Low | Low | 3104 | 2789 | 0.012255 | 3.3639 | 0.03769%
SAN LUIS OBISPO 1105CB | SAN LUIS OBISPO 1105 | LOS PADRES | 1.9887 | 39.9951 | 43.06% | 3 | 3 | 16.92% | 0% | 0 | 0.012254 | 1 | 3.1619 | 0.038746 | Low | Low | High | 2567 | 2790 | 0.012254 | 3.3516 | 0.03755%
MORGAN HILL 2105XR494 | MORGAN HILL 2105 | SAN JOSE | 0.23352 | 25.7168 | 100% | 0 | 0 | 3.179% | 0% | 0 | 0.012233 | 1 | 3.2406 | 0.039642 | Low | Low | High | 2546 | 2791 | 0.012233 | 3.3394 | 0.03741%
SNEATH LANE 11071277 | SNEATH LANE 1107 | PENINSULA | 0.25243 | 10 | 100% | 0 | 1 | 11.7% | 0% | 0 | 0.012219 | 1 | 3.504 | 0.042815 | Low | Low | High | 2480 | 2792 | 0.012219 | 3.3272 | 0.03727%
BURNEY 1101CB | BURNEY 1101 | NORTH VALLEY | 0.91927 | 10 | 59.07% | 1 | 0 | 46.14% | 0% | 0 | 0.012215 | 1 | 2.7975 | 0.034171 | Low | Low | Medium | 2677 | 2793 | 0.012215 | 3.3149 | 0.03714%
WYANDOTTE 11102590 | WYANDOTTE 1110 | NORTH VALLEY | 0.10676 | 10 | 95.21% | 0 | 0 | 17.59% | 0% | 0 | 0.012201 | 1 | 3.6162 | 0.044121 | Low | Low | High | 2458 | 2794 | 0.012201 | 3.3027 | 0.037%
CABRILLO 1103Y10 | CABRILLO 1103 | LOS PADRES | 4.0955 | 68.6545 | 11.89% | 0 | 1 | 43.98% | 0% | 0 | 0.012191 | 1 | 3.9107 | 0.047675 | Low | Low | High | 2387 | 2795 | 0.012191 | 3.2905 | 0.03686%
CALPELLA 1102CB | CALPELLA 1102 | HUMBOLDT | 1.6769 | 10 | 88.62% | 0 | 2 | 18.53% | 0% | 0 | 0.012165 | 1 | 1.6553 | 0.020137 | Low | Low | Low | 3006 | 2796 | 0.012165 | 3.2783 | 0.03673%
HARTLEY 110194178 | HARTLEY 1101 | HUMBOLDT | 1.6171 | 10 | 47.04% | 0 | 1 | 41.48% | 0% | 0 | 0.012159 | 1 | 2.8315 | 0.034428 | Low | Low | Medium | 2666 | 2797 | 0.012159 | 3.2662 | 0.03659%
RACETRACK 170310850 | RACETRACK 1703 | YOSEMITE | 0.060314 | 10 | 0% | 0 | 0 | 95.5% | 0% | 0 | 0.012143 | 1 | 3.3993 | 0.041276 | Low | Low | High | 2513 | 2798 | 0.012143 | 3.254 | 0.03645%
NORTH BRANCH 110113496 | NORTH BRANCH 1101 | STOCKTON | 2.2189 | 10 | 62.08% | 0 | 0 | 44.24% | 0% | 0 | 0.012126 | 1 | 3.1825 | 0.03859 | Low | Low | High | 2569 | 2799 | 0.012126 | 3.2419 | 0.03632%
RIO DELL 110270960 | RIO DELL 1102 | HUMBOLDT | 3.7354 | 51.8564 | 33.96% | 2 | 2 | 31.94% | 0% | 0 | 0.012119 | 1 | 0.29794 | 0.0036108 | Low | Low | Low | 3176 | 2800 | 0.012119 | 3.2297 | 0.03618%
REDBUD 110244119 | REDBUD 1102 | HUMBOLDT | 0.66752 | 10 | 86.82% | 0 | 0 | 23.81% | 0% | 0 | 0.012119 | 1 | 3.3402 | 0.040479 | Low | Low | High | 2527 | 2801 | 0.012119 | 3.2176 | 0.03605%
WILLITS 1104CB | WILLITS 1104 | HUMBOLDT | 2.2442 | 16.2086 | 22.49% | 1 | 7 | 29.86% | 0% | 0 | 0.012113 | 1 | 2.4118 | 0.029214 | Low | Low | Medium | 2793 | 2802 | 0.012113 | 3.2055 | 0.03591%
CABRILLO 1104Y22 | CABRILLO 1104 | LOS PADRES | 7.1091 | 12.8346 | 36.03% | 1 | 10 | 27.87% | 0% | 0 | 0.012091 | 1 | 3.3316 | 0.040283 | Low | Low | High | 2531 | 2803 | 0.012091 | 3.1934 | 0.03578%
JESSUP 1102CB | JESSUP 1102 | NORTH VALLEY | 0.20781 | 10 | 69.42% | 4 | 1 | 3.869% | 0% | 0 | 0.01209 | 1 | 2.7419 | 0.033151 | Low | Low | Medium | 2696 | 2804 | 0.01209 | 3.1813 | 0.03564%
COVELO 1101562360 | COVELO 1101 | HUMBOLDT | 2.2904 | 16.1283 | 100% | 0 | 1 | 6.052% | 0% | 0 | 0.012043 | 1 | 1.4309 | 0.017233 | Low | Low | Low | 3061 | 2805 | 0.012043 | 3.1692 | 0.0355%
COTATI 1104426 | COTATI 1104 | SONOMA | 2.1239 | 10 | 43.82% | 0 | 2 | 54.27% | 0% | 0 | 0.012029 | 1 | 3.2883 | 0.039554 | Low | Low | High | 2547 | 2806 | 0.012029 | 3.1572 | 0.03537%
HUMBOLDT BAY 11024724 | HUMBOLDT BAY 1102 | HUMBOLDT | 7.0458 | 41.454 | 0.8967% | 10 | 0 | 45.74% | 0% | 0 | 0.012021 | 1 | 3.6836 | 0.044279 | Low | Low | High | 2453 | 2807 | 0.012021 | 3.1451 | 0.03523%
OAKLAND K 1101CR172 | OAKLAND K 1101 | EAST BAY | 0.63886 | 10 | 27.9% | 0 | 1 | 30.68% | 23.7% | 0 | 0.011998 | 1 | 3.8735 | 0.046474 | Low | Low | High | 2406 | 2808 | 0.011998 | 3.1331 | 0.0351%
ZACA 1102Y48 | ZACA 1102 | LOS PADRES | 4.0585 | 10 | 41.4% | 0 | 6 | 34.23% | 0% | 0 | 0.011989 | 1 | 2.7812 | 0.033343 | Low | Low | Medium | 2692 | 2809 | 0.011989 | 3.1211 | 0.03497%
WISE 110163199 | WISE 1101 | SIERRA | 0.5708 | 42.4087 | 13.05% | 0 | 0 | 61.18% | 0% | 0 | 0.01197 | 1 | 3.0242 | 0.036199 | Low | Low | Medium | 2626 | 2810 | 0.01197 | 3.1091 | 0.03483%
GREENBRAE 110388832 | GREENBRAE 1103 | NORTH BAY | 1.2167 | 10 | 6.453% | 0 | 0 | 88.72% | 0% | 0 | 0.011967 | 1 | 3.9315 | 0.047049 | Low | Low | High | 2400 | 2811 | 0.011967 | 3.0972 | 0.0347%
GEYSERVILLE 1101CB | GEYSERVILLE 1101 | SONOMA | 0.2847 | 40.3314 | 82.04% | 0 | 1 | 3.457% | 0% | 0 | 0.011941 | 1 | 1.4595 | 0.017428 | Low | Low | Low | 3055 | 2812 | 0.011941 | 3.0852 | 0.03456%
DEL MONTE 21049096 | DEL MONTE 2104 | CENTRAL COAST | 2.1074 | 10 | 10.71% | 2 | 5 | 31.81% | 0% | 0 | 0.011931 | 1 | 3.6328 | 0.043344 | Low | Low | High | 2470 | 2813 | 0.011931 | 3.0732 | 0.03443%
CASTRO VALLEY 1108MR341 | CASTRO VALLEY 1108 | MISSION | 2.4534 | 10 | 13.13% | 0 | 1 | 77.41% | 2.031% | 0 | 0.011918 | 1 | 3.5792 | 0.042656 | Low | Low | High | 2486 | 2814 | 0.011918 | 3.0613 | 0.0343%
BUTTE 11052410 | BUTTE 1105 | NORTH VALLEY | 1.8432 | 10 | 92.92% | 0 | 0 | 16.76% | 0% | 0 | 0.011878 | 1 | 2.9154 | 0.034628 | Low | Low | Medium | 2660 | 2815 | 0.011878 | 3.0494 | 0.03416%
PALMER 1101M88 | PALMER 1101 | LOS PADRES | 2.2617 | 68.2305 | 27.53% | 0 | 1 | 14.75% | 0% | 0 | 0.011798 | 1 | 1.1586 | 0.013669 | Low | Low | Low | 3117 | 2816 | 0.011798 | 3.0375 | 0.03403%
TEJON 11032280 | TEJON 1103 | KERN | 2.7582 | 10 | 100% | 0 | 0 | 9.965% | 0% | 0 | 0.011765 | 1 | 2.0211 | 0.023777 | Low | Low | Low | 2914 | 2817 | 0.011765 | 3.0257 | 0.0339%
ELK 1101CB | ELK 1101 | HUMBOLDT | 0.88673 | 10 | 0% | 1 | 0 | 90.98% | 0% | 0 | 0.011764 | 1 | 0.82427 | 0.0096969 | Low | Low | Low | 3148 | 2818 | 0.011764 | 3.014 | 0.03376%
SAN ARDO 11017632 | SAN ARDO 1101 | CENTRAL COAST | 0.79963 | 10 | 100% | 0 | 0 | 9.729% | 0% | 0 | 0.011737 | 1 | 0.481 | 0.0056455 | Low | Low | Low | 3167 | 2819 | 0.011737 | 3.0022 | 0.03363%
SOLEDAD 21027008 | SOLEDAD 2102 | CENTRAL COAST | 1.2631 | 69.0048 | 38.01% | 0 | 0 | 6.974% | 0% | 0 | 0.011715 | 1 | 2.322 | 0.027202 | Low | Low | Medium | 2834 | 2820 | 0.011715 | 2.9905 | 0.0335%
GONZALES 11033096 | GONZALES 1103 | CENTRAL COAST | 1.0413 | 57.173 | 49.23% | 0 | 0 | 5.766% | 0% | 0 | 0.011709 | 1 | 2.2241 | 0.026042 | Low | Low | Low | 2863 | 2821 | 0.011709 | 2.9787 | 0.03337%
PUEBLO 2103694 | PUEBLO 2103 | NORTH BAY | 0.4502 | 10 | 100% | 0 | 0 | 9.445% | 0% | 0 | 0.011704 | 1 | 3.3141 | 0.038789 | Low | Low | High | 2566 | 2822 | 0.011704 | 2.967 | 0.03324%
KONOCTI 11022293 | KONOCTI 1102 | HUMBOLDT | 0.16556 | 10 | 100% | 0 | 0 | 9.444% | 0% | 0 | 0.011704 | 1 | 3.1767 | 0.03718 | Low | Low | High | 2608 | 2823 | 0.011704 | 2.9553 | 0.03311%
HARTLEY 1101738 | HARTLEY 1101 | HUMBOLDT | 3.053 | 10 | 42.13% | 1 | 2 | 37.87% | 0% | 0 | 0.011659 | 1 | 2.581 | 0.030092 | Low | Low | Medium | 2772 | 2824 | 0.011659 | 2.9436 | 0.03298%
CALAVERAS CEMENT 110113424 | CALAVERAS CEMENT 1101 | STOCKTON | 1.1628 | 27.7873 | 54.51% | 0 | 1 | 32.26% | 0% | 0 | 0.011657 | 1 | 2.5395 | 0.029604 | Low | Low | Medium | 2783 | 2825 | 0.011657 | 2.932 | 0.03285%
ANDERSON 1103CB | ANDERSON 1103 | NORTH VALLEY | 3.2551 | 15.9196 | 80.29% | 1 | 2 | 15.59% | 0% | 0 | 0.011642 | 1 | 2.5308 | 0.029465 | Low | Low | Medium | 2786 | 2826 | 0.011642 | 2.9203 | 0.03272%
GEYSERVILLE 1101480 | GEYSERVILLE 1101 | SONOMA | 1.4699 | 10 | 99.61% | 0 | 0 | 9.197% | 0% | 0 | 0.011639 | 1 | 1.237 | 0.014397 | Low | Low | Low | 3111 | 2827 | 0.011639 | 2.9087 | 0.03259%
WILLOW PASS 1101CB | WILLOW PASS 1101 | DIABLO | 0.46926 | 10 | 100% | 0 | 1 | 6.681% | 0% | 0 | 0.011627 | 1 | 3.2051 | 0.037265 | Low | Low | High | 2604 | 2828 | 0.011627 | 2.897 | 0.03245%
CAYUCOS 11014701 | CAYUCOS 1101 | LOS PADRES | 2.0826 | 72.227 | 28.46% | 1 | 0 | 23.77% | 0% | 0 | 0.011613 | 1 | 2.3562 | 0.027363 | Low | Low | Medium | 2827 | 2829 | 0.011613 | 2.8854 | 0.03232%
HOPLAND 1101CB | HOPLAND 1101 | HUMBOLDT | 0.39955 | 10 | 100% | 0 | 1 | 6.5% | 0% | 0 | 0.011606 | 1 | 1.3337 | 0.015479 | Low | Low | Low | 3097 | 2830 | 0.011606 | 2.8738 | 0.03219%
MORRO BAY 110280174 | MORRO BAY 1102 | LOS PADRES | 3.4488 | 10 | 0% | 1 | 0 | 76.14% | 0% | 0 | 0.011588 | 1 | 3.8574 | 0.044702 | Low | Low | High | 2443 | 2831 | 0.011588 | 2.8622 | 0.03206%
GIRVAN 1102CB | GIRVAN 1102 | NORTH VALLEY | 4.7326 | 13.9144 | 68.55% | 4 | 1 | 22.51% | 1.048% | 1 | 0.01158 | 1 | 2.7229 | 0.031532 | Low | Low | Medium | 2733 | 2832 | 0.01158 | 2.8506 | 0.03193%
RED BLUFF 1105161818 | RED BLUFF 1105 | NORTH VALLEY | 0.38337 | 10 | 100% | 0 | 0 | 8.045% | 0% | 0 | 0.011543 | 1 | 1.3232 | 0.015274 | Low | Low | Low | 3099 | 2833 | 0.011543 | 2.839 | 0.03181%
OAKHURST 110311900 | OAKHURST 1103 | YOSEMITE | 0.064919 | 10 | 100% | 0 | 0 | 7.722% | 0% | 0 | 0.011506 | 1 | 3.147 | 0.03621 | Low | Low | High | 2625 | 2834 | 0.011506 | 2.8275 | 0.03168%
WYANDOTTE 110313018 | WYANDOTTE 1103 | NORTH VALLEY | 0.12548 | 10 | 100% | 0 | 0 | 7.599% | 0% | 0 | 0.011492 | 1 | 3.697 | 0.042487 | Low | Low | High | 2487 | 2835 | 0.011492 | 2.816 | 0.03155%
SOLEDAD 2101CB | SOLEDAD 2101 | CENTRAL COAST | 1.1091 | 10 | 100% | 0 | 0 | 7.451% | 0% | 0 | 0.011475 | 1 | 2.5437 | 0.02919 | Low | Low | Medium | 2794 | 2836 | 0.011475 | 2.8045 | 0.03142%
OCEANO 1105V44 | OCEANO 1105 | LOS PADRES | 0.92167 | 10 | 6.253% | 0 | 2 | 80.43% | 0% | 0 | 0.011472 | 1 | 2.8318 | 0.032488 | Low | Low | Medium | 2711 | 2837 | 0.011472 | 2.793 | 0.03129%
BRENTWOOD 2105502672 | BRENTWOOD 2105 | DIABLO | 1.383 | 10 | 100% | 0 | 0 | 7.371% | 0% | 0 | 0.011466 | 1 | 2.4116 | 0.027652 | Low | Low | Medium | 2820 | 2838 | 0.011466 | 2.7815 | 0.03116%
CARLOTTA 11214045 | CARLOTTA 1121 | HUMBOLDT | 0.14338 | 10 | 100% | 0 | 0 | 7.252% | 0% | 0 | 0.011453 | 1 | 2.6575 | 0.030436 | Low | Low | Medium | 2763 | 2839 | 0.011453 | 2.7701 | 0.03103%
PETALUMA C 1109270 | PETALUMA C 1109 | SONOMA | 1.61 | 25.9839 | 62.25% | 0 | 3 | 21.02% | 0% | 0 | 0.011438 | 1 | 3.35 | 0.038318 | Low | Low | High | 2577 | 2840 | 0.011438 | 2.7586 | 0.0309%
BIG RIVER 11012989 | BIG RIVER 1101 | HUMBOLDT | 0.072968 | 10 | 100% | 0 | 0 | 6.918% | 0% | 0 | 0.011415 | 1 | 2.5683 | 0.029316 | Low | Low | Medium | 2791 | 2841 | 0.011415 | 2.7472 | 0.03078%
BELMONT 11038958 | BELMONT 1103 | PENINSULA | 0.46477 | 10 | 49.35% | 0 | 4 | 26.9% | 0% | 0 | 0.011413 | 1 | 3.8671 | 0.044135 | Low | Low | High | 2456 | 2842 | 0.011413 | 2.7357 | 0.03065%
SYCAMORE CREEK 1109CB | SYCAMORE CREEK 1109 | NORTH VALLEY | 0.58228 | 10 | 100% | 0 | 0 | 6.6% | 0% | 0 | 0.011379 | 1 | 3.2447 | 0.036922 | Low | Low | High | 2613 | 2843 | 0.011379 | 2.7243 | 0.03052%
HOLLISTER 21024780 | HOLLISTER 2102 | CENTRAL COAST | 2.8684 | 10 | 66.05% | 0 | 1 | 19.03% | 0% | 0 | 0.011367 | 1 | 2.5162 | 0.028602 | Low | Low | Medium | 2807 | 2844 | 0.011367 | 2.713 | 0.03039%
ROB ROY 210512584 | ROB ROY 2105 | CENTRAL COAST | 3.0913 | 10 | 22.02% | 2 | 1 | 25.72% | 0% | 0 | 0.011337 | 1 | 2.7064 | 0.030682 | Low | Low | Medium | 2752 | 2845 | 0.011337 | 2.7016 | 0.03027%
CASTRO VALLEY 1101MR359 | CASTRO VALLEY 1101 | MISSION | 0.81851 | 10 | 96.11% | 0 | 0 | 9.323% | 0% | 0 | 0.011325 | 1 | 4.4348 | 0.050223 | Low | Low | High | 2347 | 2846 | 0.011325 | 2.6903 | 0.03014%
DUNBAR 110113481 | DUNBAR 1101 | SONOMA | 0.13904 | 10 | 89.93% | 1 | 0 | 12.88% | 0% | 0 | 0.011301 | 1 | 2.8533 | 0.032246 | Low | Low | Medium | 2720 | 2847 | 0.011301 | 2.6789 | 0.03001%
CASTRO VALLEY 1106MR205 | CASTRO VALLEY 1106 | MISSION | 0.6704 | 10 | 69.55% | 0 | 0 | 12.34% | 11.35% | 0 | 0.01128 | 1 | 4.0306 | 0.045466 | Low | Low | High | 2432 | 2848 | 0.01128 | 2.6676 | 0.02989%
LAS GALLINAS A 11051218 | LAS GALLINAS A 1105 | NORTH BAY | 0.13008 | 10 | 100% | 0 | 0 | 5.571% | 0% | 0 | 0.011264 | 1 | 3.0158 | 0.033969 | Low | Low | Medium | 2683 | 2849 | 0.011264 | 2.6563 | 0.02976%
SAN CARLOS 110479774 | SAN CARLOS 1104 | PENINSULA | 0.48017 | 10 | 65.63% | 1 | 1 | 30.37% | 0% | 0 | 0.011253 | 1 | 4.0855 | 0.045976 | Low | Low | High | 2420 | 2850 | 0.011253 | 2.6451 | 0.02963%
SAUSALITO 11011270 | SAUSALITO 1101 | NORTH BAY | 0.49678 | 64.5423 | 0% | 0 | 0 | 50.41% | 0% | 0 | 0.011233 | 1 | 3.3242 | 0.037341 | Low | Low | High | 2600 | 2851 | 0.011233 | 2.6338 | 0.02951%
WYANDOTTE 11091520 | WYANDOTTE 1109 | NORTH VALLEY | 4.1645 | 10 | 80.53% | 0 | 0 | 21.24% | 0% | 0 | 0.011222 | 1 | 3.4039 | 0.038199 | Low | Low | High | 2580 | 2852 | 0.011222 | 2.6226 | 0.02938%
WYANDOTTE 11101952 | WYANDOTTE 1110 | NORTH VALLEY | 0.44853 | 10 | 100% | 0 | 0 | 5.144% | 0% | 0 | 0.011216 | 1 | 2.5511 | 0.028613 | Low | Low | Medium | 2806 | 2853 | 0.011216 | 2.6114 | 0.02925%
MADISON 21011606 | MADISON 2101 | SACRAMENTO | 0.66018 | 28.3427 | 86.09% | 0 | 0 | 3.933% | 0% | 0 | 0.0112 | 1 | 1.8042 | 0.020206 | Low | Low | Low | 3004 | 2854 | 0.0112 | 2.6002 | 0.02913%
WILLOW PASS 2107P500R | WILLOW PASS 2107 | DIABLO | 0.15832 | 10 | 100% | 0 | 0 | 4.986% | 0% | 0 | 0.011198 | 1 | 3.1106 | 0.034834 | Low | Low | High | 2655 | 2855 | 0.011198 | 2.589 | 0.029%
EL CERRITO G 1113CB | EL CERRITO G 1113 | EAST BAY | 0.20892 | 10 | 100% | 0 | 0 | 4.98% | 0% | 0 | 0.011198 | 1 | 4.968 | 0.055631 | Low | Low | High | 2251 | 2856 | 0.011198 | 2.5778 | 0.02888%
TASSAJARA 2103CB | TASSAJARA 2103 | DIABLO | 1.7119 | 10 | 14.73% | 0 | 4 | 9.614% | 35.07% | 0 | 0.011177 | 1 | 4.2565 | 0.047577 | Low | Low | High | 2390 | 2857 | 0.011177 | 2.5666 | 0.02875%
LAS POSITAS 2108MR190 | LAS POSITAS 2108 | MISSION | 1.1924 | 39.2847 | 52.56% | 0 | 0 | 10.54% | 0% | 0 | 0.011177 | 1 | 2.9514 | 0.032988 | Low | Low | Medium | 2701 | 2858 | 0.011177 | 2.5554 | 0.02863%
OLEMA 110137074 | OLEMA 1101 | NORTH BAY | 0.013643 | 10 | 100% | 0 | 0 | 4.337% | 0% | 0 | 0.011127 | 1 | 2.8085 | 0.03125 | Low | Low | Medium | 2744 | 2859 | 0.011127 | 2.5442 | 0.0285%
CLAY 1102CB | CLAY 1102 | STOCKTON | 1.1664 | 10 | 0% | 0 | 0 | 60.02% | 0% | 0 | 0.011126 | 1 | 3.2104 | 0.035721 | Low | Low | High | 2633 | 2860 | 0.011126 | 2.5331 | 0.02838%
MORRO BAY 1102CB | MORRO BAY 1102 | LOS PADRES | 3.3958 | 10 | 1.002% | 0 | 0 | 71.82% | 0% | 0 | 0.011049 | 1 | 3.3405 | 0.036911 | Low | Low | High | 2614 | 2861 | 0.011049 | 2.522 | 0.02825%
CLAY 1103CB | CLAY 1103 | STOCKTON | 5.7506 | 36.571 | 11.82% | 0 | 1 | 42.68% | 0% | 0 | 0.011049 | 1 | 3.1111 | 0.034376 | Low | Low | High | 2670 | 2862 | 0.011049 | 2.5109 | 0.02813%
COTTONWOOD 1103CB | COTTONWOOD 1103 | NORTH VALLEY | 0.091321 | 14.0615 | 100% | 0 | 0 | 0.8116% | 0% | 0 | 0.011044 | 1 | 2.0553 | 0.022699 | Low | Low | Low | 2949 | 2863 | 0.011044 | 2.4999 | 0.02801%
PUEBLO 2102CB | PUEBLO 2102 | NORTH BAY | 0.216 | 10 | 100% | 0 | 1 | 1.423% | 0% | 0 | 0.011037 | 1 | 2.8708 | 0.031684 | Low | Low | Medium | 2731 | 2864 | 0.011037 | 2.4888 | 0.02788%
OROSI 11027948F | OROSI 1102 | FRESNO | 0.26307 | 10 | 100% | 0 | 0 | 3.077% | 0% | 0 | 0.010989 | 1 | 2.0809 | 0.022866 | Low | Low | Low | 2942 | 2865 | 0.010989 | 2.4778 | 0.02776%
FORT BRAGG A 1102 | FORT BRAGG A 1102 | HUMBOLDT | 0.10961 | 10 | 0% | 0 | 0 | 85.38% | 0% | 0 | 0.010984 | 1 | 2.0184 | 0.02217 | Low | Low | Low | 2960 | 2866 | 0.010984 | 2.4668 | 0.02764%
SAN BERNARD 1101CB | SAN BERNARD 1101 | KERN | 0.91753 | 10 | 100% | 0 | 0 | 2.928% | 0% | 0 | 0.010972 | 1 | 3.031 | 0.033257 | Low | Low | Medium | 2694 | 2867 | 0.010972 | 2.4558 | 0.02751%
CLOVERDALE 1102670 | CLOVERDALE 1102 | SONOMA | 0.27521 | 10 | 95.35% | 0 | 0 | 6.733% | 0% | 0 | 0.01097 | 1 | 2.3989 | 0.026316 | Low | Low | Medium | 2855 | 2868 | 0.01097 | 2.4448 | 0.02739%
SARATOGA 110413314 | SARATOGA 1104 | DE ANZA | 1.7714 | 10 | 52.47% | 2 | 5 | 15.54% | 0% | 0 | 0.010963 | 1 | 4.2395 | 0.046476 | Low | Low | High | 2405 | 2869 | 0.010963 | 2.4339 | 0.02727%
EEL RIVER 1102530 | EEL RIVER 1102 | HUMBOLDT | 5.0874 | 49.3959 | 37.23% | 9 | 0 | 15.69% | 0% | 0 | 0.010956 | 1 | 2.1273 | 0.023307 | Low | Low | Low | 2931 | 2870 | 0.010956 | 2.4229 | 0.02714%
ROSSMOOR 1101L501R | ROSSMOOR 1101 | DIABLO | 0.055455 | 10 | 100% | 0 | 0 | 2.751% | 0% | 0 | 0.010953 | 1 | 3.5964 | 0.039392 | Low | Low | High | 2550 | 2871 | 0.010953 | 2.4119 | 0.02702%
WESTLEY 11039010 | WESTLEY 1103 | YOSEMITE | 0.92376 | 10 | 100% | 0 | 0 | 2.686% | 0% | 0 | 0.010946 | 1 | 1.3317 | 0.014577 | Low | Low | Low | 3108 | 2872 | 0.010946 | 2.401 | 0.0269%
RACETRACK 170310870 | RACETRACK 1703 | YOSEMITE | 1.0803 | 10 | 45.22% | 0 | 3 | 41.49% | 0% | 0 | 0.010943 | 1 | 3.3367 | 0.036514 | Low | Low | High | 2621 | 2873 | 0.010943 | 2.39 | 0.02678%
SAN LEANDRO U 1114MR544 | SAN LEANDRO U 1114 | MISSION | 2.1618 | 10 | 45.25% | 0 | 0 | 34.37% | 0% | 0 | 0.010938 | 1 | 3.5146 | 0.038442 | Low | Low | High | 2574 | 2874 | 0.010938 | 2.3791 | 0.02665%
HOLLYWOOD 0401CB | HOLLYWOOD 0401 | EAST BAY | 2.9599 | 10 | 0% | 0 | 1 | 55.84% | 0% | 0 | 0.010899 | 1 | 4.4177 | 0.048147 | Low | Low | High | 2376 | 2875 | 0.010899 | 2.3682 | 0.02653%
SUMMIT 110148636 | SUMMIT 1101 | SIERRA | 0.057422 | 10 | 100% | 0 | 0 | 2.116% | 0% | 0 | 0.010884 | 1 | 1.1135 | 0.01212 | Low | Low | Low | 3136 | 2876 | 0.010884 | 2.3573 | 0.02641%
LOYOLA 1102LL12 | LOYOLA 1102 | DE ANZA | 0.10967 | 10 | 100% | 0 | 0 | 1.811% | 0% | 0 | 0.010852 | 1 | 2.7206 | 0.029523 | Low | Low | Medium | 2784 | 2877 | 0.010852 | 2.3464 | 0.02629%
WALDO 0402CB | WALDO 0402 | EAST BAY | 3.0716 | 10 | 16.14% | 2 | 4 | 59.8% | 0% | 0 | 0.010847 | 1 | 4.7456 | 0.051476 | Low | Low | High | 2321 | 2878 | 0.010847 | 2.3355 | 0.02616%
DIVIDE 110348160 | DIVIDE 1103 | LOS PADRES | 2.2423 | 10 | 32.11% | 0 | 0 | 17.66% | 0% | 0 | 0.010844 | 1 | 2.8904 | 0.031344 | Low | Low | Medium | 2741 | 2879 | 0.010844 | 2.3247 | 0.02604%
HOLLISTER 210441808 | HOLLISTER 2104 | CENTRAL COAST | 0.1888 | 10 | 100% | 0 | 0 | 1.735% | 0% | 0 | 0.010843 | 1 | 2.6518 | 0.028755 | Low | Low | Medium | 2804 | 2880 | 0.010843 | 2.3138 | 0.02592%
HOPLAND 1101558 | HOPLAND 1101 | HUMBOLDT | 0.37929 | 10 | 97.04% | 0 | 0 | 4.114% | 0% | 0 | 0.010837 | 1 | 1.1824 | 0.012815 | Low | Low | Low | 3128 | 2881 | 0.010837 | 2.303 | 0.0258%
RIO DEL MAR 0401CB | RIO DEL MAR 0401 | CENTRAL COAST | 1.702 | 10 | 16.67% | 5 | 1 | 48.18% | 0% | 0 | 0.010828 | 1 | 3.3814 | 0.036613 | Low | Low | High | 2619 | 2882 | 0.010828 | 2.2922 | 0.02568%
VIEJO 220292792 | VIEJO 2202 | CENTRAL COAST | 0.01896 | 10 | 100% | 0 | 0 | 1.272% | 0% | 0 | 0.010794 | 1 | 4.1247 | 0.044521 | Low | Low | High | 2447 | 2883 | 0.010794 | 2.2813 | 0.02556%
MONTEREY 04022644 | MONTEREY 0402 | CENTRAL COAST | 0.7655 | 10 | 0% | 1 | 1 | 53.52% | 0% | 0 | 0.010791 | 1 | 3.0937 | 0.033385 | Low | Low | High | 2690 | 2884 | 0.010791 | 2.2705 | 0.02544%
SAN RAFAEL 1106910 | SAN RAFAEL 1106 | NORTH BAY | 1.5306 | 10 | 41.18% | 0 | 1 | 20.8% | 0% | 0 | 0.010777 | 1 | 3.8096 | 0.041054 | Low | Low | High | 2517 | 2885 | 0.010777 | 2.2597 | 0.02532%
MADISON 21011943 | MADISON 2101 | SACRAMENTO | 0.028904 | 10 | 100% | 0 | 0 | 0.9967% | 0% | 0 | 0.010764 | 1 | 2.1991 | 0.023671 | Low | Low | Low | 2917 | 2886 | 0.010764 | 2.249 | 0.02519%
LINCOLN 11042072 | LINCOLN 1104 | SIERRA | 0.13391 | 10 | 100% | 0 | 0 | 0.7885% | 0% | 0 | 0.010742 | 1 | 3.0303 | 0.032552 | Low | Low | Medium | 2709 | 2887 | 0.010742 | 2.2382 | 0.02507%
SAN LEANDRO U 1107MR560 | SAN LEANDRO U 1107 | MISSION | 0.061986 | 10 | 100% | 0 | 0 | 0.7828% | 0% | 0 | 0.010742 | 1 | 3.7725 | 0.040522 | Low | Low | High | 2525 | 2888 | 0.010742 | 2.2275 | 0.02495%
STONE CORRAL 11107320 | STONE CORRAL 1110 | FRESNO | 1.9474 | 22.4898 | 48.09% | 0 | 0 | 8.248% | 0% | 0 | 0.010731 | 1 | 2.3816 | 0.025558 | Low | Low | Medium | 2871 | 2889 | 0.010731 | 2.2167 | 0.02483%
PANORAMA 1102CB | PANORAMA 1102 | NORTH VALLEY | 0.071747 | 10 | 100% | 0 | 0 | 0.6421% | 0% | 0 | 0.010727 | 1 | 2.3856 | 0.025589 | Low | Low | Medium | 2870 | 2890 | 0.010727 | 2.206 | 0.02471%
HATTON 11022070 | HATTON 1102 | CENTRAL COAST | 0.49418 | 10 | 29.42% | 0 | 3 | 25.81% | 0% | 0 | 0.010726 | 1 | 3.2805 | 0.035187 | Low | Low | High | 2646 | 2891 | 0.010726 | 2.1953 | 0.02459%
EL CERRITO G 1112BR196 | EL CERRITO G 1112 | EAST BAY | 0.02286 | 10 | 100% | 0 | 0 | 0.6321% | 0% | 0 | 0.010725 | 1 | 4.3473 | 0.046627 | Low | Low | High | 2403 | 2892 | 0.010725 | 2.1845 | 0.02447%
EAST MARYSVILLE 11081706 | EAST MARYSVILLE 1108 | SIERRA | 0.35809 | 10 | 100% | 0 | 0 | 0.5923% | 0% | 0 | 0.010721 | 1 | 2.2096 | 0.02369 | Low | Low | Low | 2916 | 2893 | 0.010721 | 2.1738 | 0.02435%
BUELLTON 1101753644 | BUELLTON 1101 | LOS PADRES | 0.0028488 | 10 | 100% | 0 | 0 | 0.4009% | 0% | 0 | 0.010701 | 1 | 2.7101 | 0.029001 | Low | Low | Medium | 2797 | 2894 | 0.010701 | 2.1631 | 0.02423%
PRUNEDALE 11103716 | PRUNEDALE 1110 | CENTRAL COAST | 0.046537 | 10 | 100% | 0 | 0 | 0.3534% | 0% | 0 | 0.010696 | 1 | 2.4997 | 0.026736 | Low | Low | Medium | 2843 | 2895 | 0.010696 | 2.1524 | 0.02411%
DOLAN ROAD 11013012 | DOLAN ROAD 1101 | CENTRAL COAST | 2.5496 | 10 | 65.12% | 1 | 1 | 12.08% | 0% | 0 | 0.010669 | 1 | 3.8845 | 0.041444 | Low | Low | High | 2507 | 2896 | 0.010669 | 2.1417 | 0.02399%
BIG MEADOWS 21012016 | BIG MEADOWS 2101 | NORTH VALLEY | 0.0028416 | 10 | 100% | 0 | 0 | 0.06646% | 0% | 0 | 0.010666 | 1 | 4.0333 | 0.043017 | Low | Low | High | 2476 | 2897 | 0.010666 | 2.131 | 0.02387%
SUNOL 1101CB | SUNOL 1101 | MISSION | 3.3865 | 29.3526 | 12.99% | 0 | 0 | 58.39% | 0% | 0 | 0.010654 | 1 | 2.0615 | 0.021963 | Low | Low | Low | 2964 | 2898 | 0.010654 | 2.1204 | 0.02375%
DOLAN ROAD 110122158 | DOLAN ROAD 1101 | CENTRAL COAST | 1.2712 | 10 | 84.22% | 0 | 1 | 10.85% | 0% | 0 | 0.010653 | 1 | 3.6785 | 0.039186 | Low | Low | High | 2555 | 2899 | 0.010653 | 2.1097 | 0.02363%
FAIRVIEW 2207P150 | FAIRVIEW 2207 | DIABLO | 1.7182 | 19.1624 | 0% | 0 | 0 | 75.67% | 0% | 0 | 0.010614 | 1 | 3.2893 | 0.034913 | Low | Low | High | 2653 | 2900 | 0.010614 | 2.099 | 0.02352%
SANTA YNEZ 1102CB | SANTA YNEZ 1102 | LOS PADRES | 1.3864 | 10 | 42.97% | 0 | 2 | 15.51% | 0% | 0 | 0.010594 | 1 | 2.8741 | 0.030449 | Low | Low | Medium | 2759 | 2901 | 0.010594 | 2.0884 | 0.0234%
SAN LEANDRO U 11149838 | SAN LEANDRO U 1114 | MISSION | 1.9933 | 10 | 1.408% | 0 | 0 | 80.56% | 0% | 0 | 0.010593 | 1 | 3.6901 | 0.039087 | Low | Low | High | 2557 | 2902 | 0.010593 | 2.0778 | 0.02328%
CAMBRIA 1102W50 | CAMBRIA 1102 | LOS PADRES | 2.1309 | 10 | 10.45% | 0 | 0 | 58.83% | 0% | 0 | 0.010493 | 1 | 3.0352 | 0.031848 | Low | Low | Medium | 2730 | 2903 | 0.010493 | 2.0672 | 0.02316%
GRASS VALLEY 1103CB | GRASS VALLEY 1103 | SIERRA | 0.095866 | 10 | 0% | 0 | 0 | 80.7% | 0% | 0 | 0.010486 | 1 | 3.0497 | 0.03198 | Low | Low | Medium | 2726 | 2904 | 0.010486 | 2.0568 | 0.02304%
COTATI 1105893 | COTATI 1105 | SONOMA | 0.50896 | 59.1092 | 51.41% | 0 | 0 | 4.828% | 0% | 0 | 0.010484 | 1 | 2.2464 | 0.023552 | Low | Low | Medium | 2923 | 2905 | 0.010484 | 2.0463 | 0.02292%
LAS GALLINAS A 1105904 | LAS GALLINAS A 1105 | NORTH BAY | 2.5108 | 10 | 36.59% | 0 | 1 | 34.95% | 0% | 0 | 0.010466 | 1 | 3.9244 | 0.041073 | Low | Low | High | 2515 | 2906 | 0.010466 | 2.0358 | 0.02281%
COTTONWOOD 1101CB | COTTONWOOD 1101 | NORTH VALLEY | 5.2937 | 10 | 60.95% | 2 | 2 | 23.27% | 0% | 0 | 0.010444 | 1 | 2.0305 | 0.021206 | Low | Low | Low | 2979 | 2907 | 0.010444 | 2.0253 | 0.02269%
PURISIMA 1101Y42 | PURISIMA 1101 | LOS PADRES | 0.33998 | 72.2951 | 27.05% | 0 | 0 | 2.02% | 0% | 0 | 0.010429 | 1 | 2.6418 | 0.02755 | Low | Low | Medium | 2824 | 2908 | 0.010429 | 2.0149 | 0.02257%
TEMPLETON 2108A40 | TEMPLETON 2108 | LOS PADRES | 1.2118 | 10 | 85.64% | 0 | 0 | 9.425% | 0% | 0 | 0.010408 | 1 | 3.2792 | 0.03413 | Low | Low | High | 2679 | 2909 | 0.010408 | 2.0044 | 0.02246%
RESERVATION ROAD 11023032 | RESERVATION ROAD 1102 | CENTRAL COAST | 1.7351 | 10 | 40.39% | 0 | 1 | 17.91% | 0% | 0 | 0.010406 | 1 | 2.6242 | 0.027307 | Low | Low | Medium | 2831 | 2910 | 0.010406 | 1.994 | 0.02234%
CLEAR LAKE 11024708 | CLEAR LAKE 1102 | HUMBOLDT | 0.26472 | 10 | 85.61% | 0 | 0 | 9.354% | 0% | 0 | 0.010398 | 1 | 3.0898 | 0.032127 | Low | Low | High | 2723 | 2911 | 0.010398 | 1.9836 | 0.02222%
CAMBRIA 1101CB | CAMBRIA 1101 | LOS PADRES | 7.5504 | 30.2261 | 1.521% | 0 | 1 | 62.43% | 0% | 0 | 0.010371 | 1 | 1.7969 | 0.018636 | Low | Low | Low | 3033 | 2912 | 0.010371 | 1.9732 | 0.02211%
PACIFICA 110266732 | PACIFICA 1102 | PENINSULA | 1.1315 | 10 | 0% | 1 | 0 | 38.02% | 24.53% | 0 | 0.010334 | 1 | 3.8564 | 0.039854 | Low | Low | High | 2542 | 2913 | 0.010334 | 1.9629 | 0.02199%
CARLOTTA 1121CB | CARLOTTA 1121 | HUMBOLDT | 3.8375 | 25.0692 | 63.58% | 0 | 0 | 16.59% | 0% | 0 | 0.010334 | 1 | 2.4931 | 0.025765 | Low | Low | Medium | 2865 | 2914 | 0.010334 | 1.9525 | 0.02187%
ATASCADERO 1101A22 | ATASCADERO 1101 | LOS PADRES | 0.48233 | 10 | 88.74% | 0 | 1 | 3.681% | 0% | 0 | 0.010296 | 1 | 2.761 | 0.028426 | Low | Low | Medium | 2810 | 2915 | 0.010296 | 1.9422 | 0.02176%
MORGAN HILL 2105XR602 | MORGAN HILL 2105 | SAN JOSE | 0.59187 | 10 | 11.22% | 0 | 0 | 69.56% | 0% | 0 | 0.010291 | 1 | 3.3208 | 0.034174 | Low | Low | High | 2676 | 2916 | 0.010291 | 1.9319 | 0.02164%
LLAGAS 2105XR234 | LLAGAS 2105 | SAN JOSE | 0.40589 | 10 | 70.52% | 0 | 1 | 18.63% | 0% | 0 | 0.01029 | 1 | 3.2175 | 0.033108 | Low | Low | High | 2697 | 2917 | 0.01029 | 1.9216 | 0.02153%
WILLITS 110337504 | WILLITS 1103 | HUMBOLDT | 0.81372 | 28.0694 | 47.51% | 0 | 2 | 22.82% | 0% | 0 | 0.010255 | 1 | 2.412 | 0.024736 | Low | Low | Medium | 2891 | 2918 | 0.010255 | 1.9113 | 0.02141%
LAKEVILLE 1102530 | LAKEVILLE 1102 | SONOMA | 0.62549 | 57.7371 | 40.72% | 0 | 0 | 12.01% | 0% | 0 | 0.010222 | 1 | 3.1695 | 0.032397 | Low | Low | High | 2714 | 2919 | 0.010222 | 1.9011 | 0.0213%
FORT ORD 210637286 | FORT ORD 2106 | CENTRAL COAST | 1.5847 | 10 | 0% | 0 | 4 | 43% | 0% | 0 | 0.010213 | 1 | 2.936 | 0.029984 | Low | Low | Medium | 2775 | 2920 | 0.010213 | 1.8908 | 0.02118%
SAN LUIS OBISPO 1104645976 | SAN LUIS OBISPO 1104 | LOS PADRES | 2.1274 | 42.6681 | 27.62% | 0 | 0 | 32.32% | 0% | 0 | 0.010145 | 1 | 2.231 | 0.022633 | Low | Low | Medium | 2951 | 2921 | 0.010145 | 1.8806 | 0.02107%
HARRIS 11082062 | HARRIS 1108 | HUMBOLDT | 2.3961 | 14.4145 | 20.24% | 1 | 5 | 45.88% | 0% | 0 | 0.010144 | 1 | 4.1719 | 0.042318 | Low | Low | High | 2489 | 2922 | 0.010144 | 1.8705 | 0.02095%
SONOMA 11054456 | SONOMA 1105 | SONOMA | 1.6486 | 23.1811 | 52.93% | 0 | 1 | 22.31% | 0% | 0 | 0.010106 | 1 | 3.401 | 0.034372 | Low | Low | High | 2672 | 2923 | 0.010106 | 1.8603 | 0.02084%
BRENTWOOD 210596324 | BRENTWOOD 2105 | DIABLO | 0.37122 | 10 | 0% | 0 | 0 | 76.98% | 0% | 0 | 0.010106 | 1 | 2.6232 | 0.02651 | Low | Low | Medium | 2850 | 2924 | 0.010106 | 1.8502 | 0.02073%
LINCOLN 110195756 | LINCOLN 1101 | SIERRA | 3.5302 | 10.7023 | 65.54% | 2 | 0 | 19.54% | 0% | 0 | 0.010072 | 1 | 2.5936 | 0.026122 | Low | Low | Medium | 2860 | 2925 | 0.010072 | 1.8401 | 0.02061%
NARROWS 21022718 | NARROWS 2102 | SIERRA | 0.45209 | 10 | 82.65% | 0 | 1 | 6.234% | 0% | 0 | 0.010047 | 1 | 3.7245 | 0.037421 | Low | Low | High | 2596 | 2926 | 0.010047 | 1.8301 | 0.0205%
CURTIS 170190120 | CURTIS 1701 | YOSEMITE | 2.5983 | 10 | 28.78% | 0 | 1 | 50.57% | 0% | 0 | 0.010044 | 1 | 3.5453 | 0.035611 | Low | Low | High | 2636 | 2927 | 0.010044 | 1.82 | 0.02039%
MESA 1103M92 | MESA 1103 | LOS PADRES | 1.0274 | 49.2008 | 44.21% | 0 | 0 | 12.96% | 0% | 0 | 0.010021 | 1 | 2.7565 | 0.027622 | Low | Low | Medium | 2822 | 2928 | 0.010021 | 1.81 | 0.02028%
TIDEWATER 210665866 | TIDEWATER 2106 | DIABLO | 4.2405 | 36.2821 | 12.3% | 0 | 0 | 47.54% | 0% | 0 | 0.0099699 | 1 | 3.5683 | 0.035576 | Low | Low | High | 2638 | 2929 | 0.0099699 | 1.7999 | 0.02016%
UKIAH 111472990 | UKIAH 1114 | HUMBOLDT | 0.7336 | 10 | 33.42% | 1 | 5 | 22.74% | 0% | 0 | 0.0099473 | 1 | 3.0013 | 0.029855 | Low | Low | Medium | 2778 | 2930 | 0.0099473 | 1.79 | 0.02005%
FITCH MOUNTAIN 1113154 | FITCH MOUNTAIN 1113 | SONOMA | 2.1793 | 18.0666 | 70.63% | 0 | 0 | 11.51% | 0% | 0 | 0.0099274 | 1 | 2.5363 | 0.025179 | Low | Low | Medium | 2877 | 2931 | 0.0099274 | 1.78 | 0.01994%
HARTLEY 1102CB | HARTLEY 1102 | HUMBOLDT | 2.7707 | 10 | 40.84% | 0 | 2 | 23.94% | 0% | 0 | 0.0099181 | 1 | 2.3095 | 0.022906 | Low | Low | Medium | 2941 | 2932 | 0.0099181 | 1.7701 | 0.01983%
EDES 1112CB | EDES 1112 | EAST BAY | 0.77646 | 10 | 11.31% | 0 | 0 | 52.35% | 0% | 0 | 0.0099087 | 1 | 3.3253 | 0.032949 | Low | Low | High | 2702 | 2933 | 0.0099087 | 1.7602 | 0.01972%
SONOMA 1104914376 | SONOMA 1104 | SONOMA | 0.42319 | 32.6662 | 64.75% | 0 | 0 | 6.07% | 0% | 0 | 0.0098958 | 1 | 3.98 | 0.039385 | Low | Low | High | 2551 | 2934 | 0.0098958 | 1.7503 | 0.01961%
MENLO 11029110 | MENLO 1102 | PENINSULA | 0.16148 | 10 | 87.04% | 1 | 0 | 1.751% | 0% | 0 | 0.0098849 | 1 | 3.7774 | 0.037339 | Low | Low | High | 2601 | 2935 | 0.0098849 | 1.7404 | 0.0195%
RACETRACK 1703332820 | RACETRACK 1703 | YOSEMITE | 1.3085 | 10 | 3.686% | 0 | 0 | 71.54% | 0% | 0 | 0.0098677 | 1 | 3.4356 | 0.033901 | Low | Low | High | 2685 | 2936 | 0.0098677 | 1.7305 | 0.01939%
EEL RIVER 110249130 | EEL RIVER 1102 | HUMBOLDT | 1.458 | 43.0989 | 47.28% | 0 | 1 | 10.5% | 0% | 0 | 0.0098241 | 1 | 2.4567 | 0.024135 | Low | Low | Medium | 2905 | 2937 | 0.0098241 | 1.7206 | 0.01928%
SAN ARDO 110193072 | SAN ARDO 1101 | CENTRAL COAST | 0.72134 | 10 | 63.38% | 0 | 0 | 8.566% | 0% | 0 | 0.0098197 | 1 | 0.54117 | 0.0053141 | Low | Low | Low | 3169 | 2938 | 0.0098197 | 1.7108 | 0.01917%
HARTLEY 1101CB | HARTLEY 1101 | HUMBOLDT | 1.2777 | 10 | 19.8% | 0 | 1 | 42.25% | 0% | 0 | 0.0098099 | 1 | 2.5013 | 0.024537 | Low | Low | Medium | 2894 | 2939 | 0.0098099 | 1.701 | 0.01906%
BUELLTON 11016621 | BUELLTON 1101 | LOS PADRES | 1.6446 | 36.7928 | 44.49% | 0 | 1 | 16.9% | 0% | 0 | 0.0098043 | 1 | 2.0776 | 0.020369 | Low | Low | Low | 2996 | 2940 | 0.0098043 | 1.6912 | 0.01895%
SANTA YNEZ 1104CB | SANTA YNEZ 1104 | LOS PADRES | 0.81728 | 10 | 74.93% | 2 | 0 | 9.437% | 0% | 0 | 0.00979 | 1 | 3.444 | 0.033717 | Low | Low | High | 2687 | 2941 | 0.00979 | 1.6814 | 0.01884%
PETALUMA C 1108630 | PETALUMA C 1108 | SONOMA | 1.2522 | 54.3048 | 11.61% | 0 | 2 | 29.56% | 0% | 0 | 0.0097687 | 1 | 3 | 0.029306 | Low | Low | Medium | 2792 | 2942 | 0.0097687 | 1.6716 | 0.01873%
MIRABEL 1102206 | MIRABEL 1102 | SONOMA | 1.6804 | 10 | 37.83% | 0 | 1 | 13.09% | 0% | 0 | 0.0097141 | 1 | 3.0324 | 0.029457 | Low | Low | Medium | 2787 | 2943 | 0.0097141 | 1.6618 | 0.01862%
OAKLAND X 1101CR224 | OAKLAND X 1101 | EAST BAY | 0.53647 | 10 | 23.35% | 2 | 2 | 46.33% | 0% | 0 | 0.0096559 | 1 | 4.5636 | 0.044066 | Low | Low | High | 2459 | 2944 | 0.0096559 | 1.6521 | 0.01851%
GRASS VALLEY 110358498 | GRASS VALLEY 1103 | SIERRA | 0.54343 | 10 | 37.4% | 0 | 2 | 23.91% | 0% | 0 | 0.0096407 | 1 | 2.8446 | 0.027424 | Low | Low | Medium | 2826 | 2945 | 0.0096407 | 1.6424 | 0.0184%
ATASCADERO 1103A46 | ATASCADERO 1103 | LOS PADRES | 0.63104 | 65.2454 | 33.62% | 0 | 0 | 6.794% | 0% | 0 | 0.0096376 | 1 | 2.251 | 0.021694 | Low | Low | Medium | 2970 | 2946 | 0.0096376 | 1.6328 | 0.01829%
STELLING 110913228 | STELLING 1109 | DE ANZA | 0.52786 | 10 | 79.39% | 0 | 0 | 6.214% | 0% | 0 | 0.0095798 | 1 | 3.5877 | 0.034369 | Low | Low | High | 2673 | 2947 | 0.0095798 | 1.6232 | 0.01818%
FORT ORD 210736596 | FORT ORD 2107 | CENTRAL COAST | 2.9621 | 10 | 1.434% | 0 | 3 | 23.77% | 0% | 0 | 0.0095449 | 1 | 3.1211 | 0.029791 | Low | Low | High | 2781 | 2948 | 0.0095449 | 1.6136 | 0.01808%
REDBUD 1102432 | REDBUD 1102 | HUMBOLDT | 1.3051 | 10 | 69.46% | 0 | 1 | 11.62% | 0% | 0 | 0.0095157 | 1 | 3.1897 | 0.030352 | Low | Low | High | 2765 | 2949 | 0.0095157 | 1.604 | 0.01797%
OAKLAND K 1101CB | OAKLAND K 1101 | EAST BAY | 0.35314 | 10 | 0% | 1 | 1 | 14.81% | 24.18% | 0 | 0.0095124 | 1 | 4.2078 | 0.040027 | Low | Low | High | 2539 | 2950 | 0.0095124 | 1.5945 | 0.01786%
STAFFORD 110242542 | STAFFORD 1102 | NORTH BAY | 0.92749 | 10 | 53.57% | 0 | 0 | 26.56% | 0% | 0 | 0.0094932 | 1 | 2.9041 | 0.027569 | Low | Low | Medium | 2823 | 2951 | 0.0094932 | 1.585 | 0.01776%
EL CERRITO G 1110CB | EL CERRITO G 1110 | EAST BAY | 1.4466 | 10 | 13.89% | 0 | 3 | 52.88% | 0% | 0 | 0.0094866 | 1 | 4.6174 | 0.043803 | Low | Low | High | 2467 | 2952 | 0.0094866 | 1.5755 | 0.01765%
BERESFORD 04039154 | BERESFORD 0403 | PENINSULA | 3.1988 | 10 | 17.34% | 4 | 1 | 48.83% | 0% | 0 | 0.0094751 | 1 | 3.2128 | 0.030442 | Low | Low | High | 2760 | 2953 | 0.0094751 | 1.566 | 0.01754%
LOS COCHES 1101CB | LOS COCHES 1101 | CENTRAL COAST | 2.6219 | 75.2391 | 12.86% | 0 | 1 | 13.12% | 0% | 0 | 0.009461 | 1 | 2.1351 | 0.020201 | Low | Low | Low | 3005 | 2954 | 0.009461 | 1.5566 | 0.01744%
SAN LUIS OBISPO 1107CB | SAN LUIS OBISPO 1107 | LOS PADRES | 0.84728 | 10 | 25.92% | 0 | 0 | 48.86% | 0% | 0 | 0.0094493 | 1 | 3.0675 | 0.028986 | Low | Low | Medium | 2798 | 2955 | 0.0094493 | 1.5471 | 0.01733%
SONOMA 1107126 | SONOMA 1107 | SONOMA | 2.2583 | 59.5559 | 29.29% | 0 | 1 | 10.13% | 0% | 0 | 0.009446 | 1 | 2.8041 | 0.026487 | Low | Low | Medium | 2852 | 2956 | 0.009446 | 1.5376 | 0.01723%
FLINT 110140666 | FLINT 1101 | SIERRA | 0.79305 | 10 | 48.92% | 0 | 1 | 27.77% | 0% | 0 | 0.009443 | 1 | 3.3257 | 0.031404 | Low | Low | High | 2737 | 2957 | 0.009443 | 1.5282 | 0.01712%
JARVIS 1108MR368 | JARVIS 1108 | MISSION | 0.80128 | 10 | 39.98% | 0 | 0 | 23.87% | 0% | 0 | 0.0094416 | 1 | 3.9056 | 0.036875 | Low | Low | High | 2617 | 2958 | 0.0094416 | 1.5188 | 0.01701%
MC ARTHUR 11011488 | MC ARTHUR 1101 | NORTH VALLEY | 2.4985 | 10 | 70.57% | 0 | 2 | 7.462% | 0% | 0 | 0.0094078 | 1 | 0.63499 | 0.0059739 | Low | Low | Low | 3165 | 2959 | 0.0094078 | 1.5093 | 0.01691%
HARTLEY 110186876 | HARTLEY 1101 | HUMBOLDT | 2.3866 | 10 | 49.85% | 0 | 0 | 28.66% | 0% | 0 | 0.0094023 | 1 | 2.9982 | 0.02819 | Low | Low | Medium | 2814 | 2960 | 0.0094023 | 1.4999 | 0.0168%
POINT MORETTI 11015074 | POINT MORETTI 1101 | CENTRAL COAST | 1.726 | 19.9026 | 1.553% | 2 | 1 | 56.7% | 0% | 0 | 0.009381 | 1 | 3.1003 | 0.029084 | Low | Low | High | 2796 | 2961 | 0.009381 | 1.4905 | 0.0167%
ROSSMOOR 110676468 | ROSSMOOR 1106 | DIABLO | 1.5034 | 10 | 14.83% | 1 | 2 | 51.08% | 0% | 0 | 0.0093177 | 1 | 3.7505 | 0.034946 | Low | Low | High | 2652 | 2962 | 0.0093177 | 1.4811 | 0.01659%
ROSSMOOR 110192164 | ROSSMOOR 1101 | DIABLO | 0.25455 | 10 | 51.39% | 0 | 0 | 26.2% | 0% | 0 | 0.0092923 | 1 | 3.7629 | 0.034966 | Low | Low | High | 2651 | 2963 | 0.0092923 | 1.4718 | 0.01649%
ATASCADERO 1101CB | ATASCADERO 1101 | LOS PADRES | 0.44126 | 10 | 57.34% | 0 | 0 | 21.26% | 0% | 0 | 0.0092885 | 1 | 3.1059 | 0.028849 | Low | Low | High | 2802 | 2964 | 0.0092885 | 1.4625 | 0.01638%
TEMPLETON 2113A32 | TEMPLETON 2113 | LOS PADRES | 0.77097 | 10 | 66.93% | 0 | 0 | 13.18% | 0% | 0 | 0.0092713 | 1 | 2.8821 | 0.026721 | Low | Low | Medium | 2844 | 2965 | 0.0092713 | 1.4532 | 0.01628%
SOBRANTE 110142914 | SOBRANTE 1101 | DIABLO | 0.83179 | 10 | 55.86% | 0 | 1 | 20.13% | 0% | 0 | 0.0092648 | 1 | 3.3242 | 0.030798 | Low | Low | High | 2748 | 2966 | 0.0092648 | 1.4439 | 0.01618%
SWIFT 2109XR300 | SWIFT 2109 | SAN JOSE | 0.30955 | 10 | 37.52% | 0 | 0 | 37.32% | 0% | 0 | 0.0092647 | 1 | 4.5685 | 0.042326 | Low | Low | High | 2488 | 2967 | 0.0092647 | 1.4347 | 0.01607%
OAKLAND J 1102CR254 | OAKLAND J 1102 | EAST BAY | 1.0198 | 10 | 0% | 1 | 0 | 66.21% | 0% | 0 | 0.0092017 | 1 | 3.4742 | 0.031969 | Low | Low | High | 2727 | 2968 | 0.0092017 | 1.4254 | 0.01597%
FRANKLIN 1104P136 | FRANKLIN 1104 | EAST BAY | 3.8457 | 10 | 0% | 0 | 1 | 65.24% | 0% | 0 | 0.009184 | 1 | 3.4131 | 0.031346 | Low | Low | High | 2740 | 2969 | 0.009184 | 1.4162 | 0.01587%
DEL MONTE 210332886 | DEL MONTE 2103 | CENTRAL COAST | 1.2598 | 10 | 0% | 5 | 1 | 31.74% | 0% | 0 | 0.0091616 | 1 | 3.2009 | 0.029325 | Low | Low | High | 2790 | 2970 | 0.0091616 | 1.407 | 0.01576%
OLEMA 1101320 | OLEMA 1101 | NORTH BAY | 0.033859 | 54.8898 | 25.18% | 0 | 1 | 0.2531% | 0% | 0 | 0.0091583 | 1 | 2.7217 | 0.024926 | Low | Low | Medium | 2884 | 2971 | 0.0091583 | 1.3979 | 0.01566%
OAKLAND J 1106CR330 | OAKLAND J 1106 | EAST BAY | 0.49535 | 10 | 40.09% | 0 | 0 | 20.57% | 0% | 0 | 0.0091449 | 1 | 3.1852 | 0.029128 | Low | Low | High | 2795 | 2972 | 0.0091449 | 1.3887 | 0.01556%
SNEATH LANE 1106CB | SNEATH LANE 1106 | PENINSULA | 1.101 | 10 | 47.15% | 3 | 3 | 17.83% | 0% | 0 | 0.0091441 | 1 | 3.7667 | 0.034443 | Low | Low | High | 2665 | 2973 | 0.0091441 | 1.3796 | 0.01546%
FROGTOWN 1702CB | FROGTOWN 1702 | STOCKTON | 2.2987 | 10 | 21.1% | 0 | 2 | 44.33% | 0% | 0 | 0.0090529 | 1 | 1.9418 | 0.017579 | Low | Low | Low | 3052 | 2974 | 0.0090529 | 1.3704 | 0.01535%
OAKLAND J 1106CR164 | OAKLAND J 1106 | EAST BAY | 1.4865 | 10 | 46.08% | 2 | 1 | 22.66% | 0% | 0 | 0.0090035 | 1 | 3.2151 | 0.028947 | Low | Low | High | 2799 | 2975 | 0.0090035 | 1.3614 | 0.01525%
VALLEY VIEW 1105CB | VALLEY VIEW 1105 | EAST BAY | 0.87089 | 10 | 56.45% | 0 | 0 | 18.73% | 0% | 0 | 0.0089925 | 1 | 4.7951 | 0.04312 | Low | Low | High | 2475 | 2976 | 0.0089925 | 1.3524 | 0.01515%
ELK 11011300 | ELK 1101 | HUMBOLDT | 3.0348 | 10 | 21.85% | 10 | 1 | 31.85% | 0% | 0 | 0.0089861 | 1 | 0.83981 | 0.0075467 | Low | Low | Low | 3161 | 2977 | 0.0089861 | 1.3434 | 0.01505%
VALLEY VIEW 1106P128 | VALLEY VIEW 1106 | EAST BAY | 0.72514 | 10 | 44.15% | 0 | 0 | 28.68% | 0% | 0 | 0.0089763 | 1 | 3.3463 | 0.030037 | Low | Low | High | 2774 | 2978 | 0.0089763 | 1.3344 | 0.01495%
HICKS 1116CB | HICKS 1116 | SAN JOSE | 1.3112 | 10 | 43.95% | 1 | 3 | 7.743% | 0% | 0 | 0.0089608 | 1 | 3.9753 | 0.035622 | Low | Low | High | 2635 | 2979 | 0.0089608 | 1.3254 | 0.01485%
GABILAN 11013034 | GABILAN 1101 | CENTRAL COAST | 0.41092 | 10 | 76.33% | 0 | 0 | 1.978% | 0% | 0 | 0.0089581 | 1 | 2.2622 | 0.020265 | Low | Low | Medium | 3000 | 2980 | 0.0089581 | 1.3165 | 0.01475%
HOLLISTER 210491424 | HOLLISTER 2104 | CENTRAL COAST | 0.19482 | 10 | 75.59% | 0 | 0 | 2.224% | 0% | 0 | 0.0089256 | 1 | 2.6389 | 0.023554 | Low | Low | Medium | 2922 | 2981 | 0.0089256 | 1.3075 | 0.01465%
WYANDOTTE 110942650 | WYANDOTTE 1109 | NORTH VALLEY | 0.71686 | 10 | 44.77% | 0 | 0 | 27.21% | 0% | 0 | 0.0088907 | 1 | 4.2335 | 0.037638 | Low | Low | High | 2591 | 2982 | 0.0088907 | 1.2986 | 0.01455%
FLORENCE 0401CB | FLORENCE 0401 | EAST BAY | 1.7144 | 10 | 2.295% | 5 | 1 | 39.92% | 0% | 0 | 0.00887 | 1 | 4.5207 | 0.040099 | Low | Low | High | 2537 | 2983 | 0.00887 | 1.2897 | 0.01445%
VALLEY VIEW 1105P126 | VALLEY VIEW 1105 | EAST BAY | 0.94179 | 10 | 5.099% | 0 | 0 | 45.94% | 0% | 0 | 0.008838 | 1 | 3.9116 | 0.034571 | Low | Low | High | 2661 | 2984 | 0.008838 | 1.2808 | 0.01435%
VINEYARD 2107CB | VINEYARD 2107 | MISSION | 1.6942 | 13.0214 | 48.11% | 0 | 2 | 16.67% | 0% | 0 | 0.0087566 | 1 | 3.1976 | 0.028 | Low | Low | High | 2816 | 2985 | 0.0087566 | 1.272 | 0.01425%
SAN CARLOS 11048846 | SAN CARLOS 1104 | PENINSULA | 1.1188 | 10 | 42.43% | 0 | 1 | 25.48% | 0% | 0 | 0.0087545 | 1 | 4.0972 | 0.035869 | Low | Low | High | 2631 | 2986 | 0.0087545 | 1.2632 | 0.01415%
NOVATO 11041282 | NOVATO 1104 | NORTH BAY | 1.3064 | 10 | 9.821% | 0 | 6 | 28.52% | 0% | 0 | 0.008753 | 1 | 3.0035 | 0.026289 | Low | Low | Medium | 2856 | 2987 | 0.008753 | 1.2545 | 0.01405%
ELK 1101900 | ELK 1101 | HUMBOLDT | 6.0335 | 22.7757 | 2.097% | 2 | 3 | 29.53% | 0% | 0 | 0.0087294 | 1 | 1.5553 | 0.013577 | Low | Low | Low | 3119 | 2988 | 0.0087294 | 1.2457 | 0.01396%
WYANDOTTE 110213914 | WYANDOTTE 1102 | NORTH VALLEY | 0.60739 | 10 | 33.65% | 0 | 0 | 34.43% | 0% | 0 | 0.0087222 | 1 | 2.7969 | 0.024396 | Low | Low | Medium | 2899 | 2989 | 0.0087222 | 1.237 | 0.01386%
OAKLAND J 1102CR252 | OAKLAND J 1102 | EAST BAY | 1.1914 | 10 | 48.94% | 0 | 1 | 19.56% | 0% | 0 | 0.0087055 | 1 | 3.4603 | 0.030124 | Low | Low | High | 2770 | 2990 | 0.0087055 | 1.2283 | 0.01376%
BELMONT 1103415994 | BELMONT 1103 | PENINSULA | 1.0684 | 10 | 38.18% | 0 | 2 | 26.01% | 0% | 0 | 0.0086782 | 1 | 3.9933 | 0.034655 | Low | Low | High | 2659 | 2991 | 0.0086782 | 1.2196 | 0.01366%
KERN OIL 110646960 | KERN OIL 1106 | KERN | 1.1498 | 10 | 1.744% | 0 | 0 | 59.65% | 0% | 0 | 0.0086311 | 1 | 2.7916 | 0.024095 | Low | Low | Medium | 2908 | 2992 | 0.0086311 | 1.2109 | 0.01357%
OAKLAND X 1105CB | OAKLAND X 1105 | EAST BAY | 3.475 | 10 | 21.39% | 0 | 3 | 23.79% | 0% | 0 | 0.0086247 | 1 | 3.5708 | 0.030797 | Low | Low | High | 2749 | 2993 | 0.0086247 | 1.2022 | 0.01347%
HALF MOON BAY 11036014 | HALF MOON BAY 1103 | PENINSULA | 5.273 | 14.6725 | 1.871% | 0 | 0 | 42.92% | 0% | 0 | 0.0086216 | 1 | 2.0756 | 0.017895 | Low | Low | Low | 3048 | 2994 | 0.0086216 | 1.1936 | 0.01337%
GREEN VALLEY 210112130 | GREEN VALLEY 2101 | CENTRAL COAST | 1.2937 | 17.054 | 59.16% | 0 | 0 | 7.411% | 0% | 0 | 0.0086186 | 1 | 3.2862 | 0.028323 | Low | Low | High | 2813 | 2995 | 0.0086186 | 1.185 | 0.01328%
BAYWOOD 1101CB | BAYWOOD 1101 | LOS PADRES | 1.4233 | 43.3041 | 38.16% | 0 | 0 | 4.9% | 0% | 0 | 0.008459 | 1 | 2.6765 | 0.022641 | Low | Low | Medium | 2950 | 2996 | 0.008459 | 1.1764 | 0.01318%
FAIRVIEW 2207CB | FAIRVIEW 2207 | DIABLO | 0.060291 | 10 | 69.19% | 0 | 0 | 1.178% | 0% | 0 | 0.0083828 | 1 | 2.9891 | 0.025057 | Low | Low | Medium | 2879 | 2997 | 0.0083828 | 1.1679 | 0.01308%
FLINT 1101CB | FLINT 1101 | SIERRA | 0.81732 | 10 | 11.07% | 0 | 2 | 31.46% | 0% | 0 | 0.008378 | 1 | 3.2795 | 0.027475 | Low | Low | High | 2825 | 2998 | 0.008378 | 1.1595 | 0.01299%
COTATI 1105616 | COTATI 1105 | SONOMA | 0.88156 | 51.5142 | 16.32% | 0 | 0 | 2.877% | 0% | 0 | 0.0083693 | 1 | 2.6305 | 0.022015 | Low | Low | Medium | 2963 | 2999 | 0.0083693 | 1.1512 | 0.0129%
ROB ROY 210410930 | ROB ROY 2104 | CENTRAL COAST | 1.4484 | 10 | 54.81% | 0 | 0 | 12.82% | 0% | 0 | 0.0083664 | 1 | 3.3859 | 0.028328 | Low | Low | High | 2812 | 3000 | 0.0083664 | 1.1428 | 0.0128%
FAIRVIEW 2207M501R | FAIRVIEW 2207 | DIABLO | 1.376 | 10 | 11.91% | 1 | 2 | 29.22% | 0% | 0 | 0.0083598 | 1 | 3.1246 | 0.026121 | Low | Low | High | 2861 | 3001 | 0.0083598 | 1.1344 | 0.01271%
BERKELEY F 0402CB | BERKELEY F 0402 | EAST BAY | 0.47631 | 10 | 26.87% | 0 | 0 | 22.4% | 0% | 0 | 0.0083588 | 1 | 4.1661 | 0.034823 | Low | Low | High | 2656 | 3002 | 0.0083588 | 1.1261 | 0.01262%
UKIAH 1114CB | UKIAH 1114 | HUMBOLDT | 1.2249 | 10 | 45.97% | 1 | 2 | 14.08% | 0% | 0 | 0.0083238 | 1 | 2.9939 | 0.024921 | Low | Low | Medium | 2886 | 3003 | 0.0083238 | 1.1177 | 0.01252%
WOOD 0401CB | WOOD 0401 | EAST BAY | 0.4018 | 10 | 54.38% | 0 | 0 | 12.06% | 0% | 0 | 0.0082741 | 1 | 4.5612 | 0.037739 | Low | Low | High | 2589 | 3004 | 0.0082741 | 1.1094 | 0.01243%
FAIRMOUNT 0401CB | FAIRMOUNT 0401 | EAST BAY | 1.4849 | 10 | 0% | 0 | 2 | 25.81% | 0% | 0 | 0.0082593 | 1 | 4.7218 | 0.038999 | Low | Low | High | 2562 | 3005 | 0.0082593 | 1.1011 | 0.01234%
TEMPLETON 2113A30 | TEMPLETON 2113 | LOS PADRES | 0.53596 | 10 | 10.42% | 0 | 0 | 34.36% | 0% | 0 | 0.0082271 | 1 | 2.9117 | 0.023955 | Low | Low | Medium | 2911 | 3006 | 0.0082271 | 1.0928 | 0.01224%
KONOCTI 110264464 | KONOCTI 1102 | HUMBOLDT | 0.53615 | 10 | 9.05% | 1 | 0 | 19.93% | 0% | 0 | 0.0081536 | 1 | 2.9706 | 0.024221 | Low | Low | Medium | 2903 | 3007 | 0.0081536 | 1.0846 | 0.01215%
RIO DEL MAR 0402CB | RIO DEL MAR 0402 | CENTRAL COAST | 1.6949 | 10 | 6.344% | 2 | 0 | 47.04% | 0% | 0 | 0.0081166 | 1 | 3.7099 | 0.030112 | Low | Low | High | 2771 | 3008 | 0.0081166 | 1.0765 | 0.01206%
TASSAJARA 2109CB | TASSAJARA 2109 | DIABLO | 0.80761 | 10 | 0% | 0 | 4 | 46.43% | 0% | 0 | 0.0081085 | 1 | 4.0127 | 0.032537 | Low | Low | High | 2710 | 3009 | 0.0081085 | 1.0683 | 0.01197%
EEL RIVER 11033820 | EEL RIVER 1103 | HUMBOLDT | 2.3658 | 10 | 0% | 0 | 1 | 11.93% | 0% | 0 | 0.0080448 | 1 | 2.2417 | 0.018034 | Low | Low | Medium | 3044 | 3010 | 0.0080448 | 1.0602 | 0.01188%
VIEJO 220146068 | VIEJO 2201 | CENTRAL COAST | 0.073762 | 10 | 0% | 0 | 0 | 53.15% | 0% | 0 | 0.0079762 | 1 | 3.8343 | 0.030583 | Low | Low | High | 2756 | 3011 | 0.0079762 | 1.0522 | 0.01179%
COAST RD 04015134 | COAST RD 0401 | CENTRAL COAST | 1.6146 | 10 | 0% | 0 | 0 | 53.13% | 0% | 0 | 0.007975 | 1 | 2.3974 | 0.019119 | Low | Low | Medium | 3027 | 3012 | 0.007975 | 1.0442 | 0.0117%
IGNACIO 11041290 | IGNACIO 1104 | NORTH BAY | 1.6542 | 10 | 24.98% | 1 | 1 | 15.64% | 0% | 0 | 0.0079604 | 1 | 2.8977 | 0.023067 | Low | Low | Medium | 2937 | 3013 | 0.0079604 | 1.0362 | 0.01161%
BERKELEY F 1105CB | BERKELEY F 1105 | EAST BAY | 1.3653 | 10 | 33.54% | 1 | 1 | 21.32% | 0% | 0 | 0.0079134 | 1 | 4.0804 | 0.03229 | Low | Low | High | 2718 | 3014 | 0.0079134 | 1.0283 | 0.01152%
FORT BRAGG A 1102CB | FORT BRAGG A 1102 | HUMBOLDT | 1.663 | 13.8095 | 19.07% | 2 | 1 | 29% | 0% | 0 | 0.0078888 | 1 | 3.2475 | 0.025619 | Low | Low | High | 2868 | 3015 | 0.0078888 | 1.0204 | 0.01143%
RESERVATION ROAD 110222136 | RESERVATION ROAD 1102 | CENTRAL COAST | 1.1023 | 40.7641 | 13.41% | 0 | 0 | 19.9% | 0% | 0 | 0.0078815 | 1 | 1.7282 | 0.013621 | Low | Low | Low | 3118 | 3016 | 0.0078815 | 1.0125 | 0.01134%
ALHAMBRA 110595016 | ALHAMBRA 1105 | DIABLO | 0.37201 | 51.8878 | 0% | 0 | 0 | 9.208% | 0% | 0 | 0.0078178 | 1 | 2.9552 | 0.023103 | Low | Low | Medium | 2935 | 3017 | 0.0078178 | 1.0046 | 0.01125%
MORRO BAY 1101W20 | MORRO BAY 1101 | LOS PADRES | 1.8981 | 10 | 0% | 0 | 1 | 48.29% | 0% | 0 | 0.0077601 | 1 | 3.1154 | 0.024176 | Low | Low | High | 2904 | 3018 | 0.0077601 | 0.99678 | 0.01117%
PETALUMA C 1109CB | PETALUMA C 1109 | SONOMA | 0.77473 | 10 | 39.24% | 0 | 1 | 15.77% | 0% | 0 | 0.007744 | 1 | 3.3257 | 0.025754 | Low | Low | High | 2866 | 3019 | 0.007744 | 0.98902 | 0.01108%
LOS GATOS 1101CB | LOS GATOS 1101 | DE ANZA | 0.83125 | 10 | 32.44% | 0 | 1 | 21.19% | 0% | 0 | 0.0077301 | 1 | 3.3892 | 0.026199 | Low | Low | High | 2858 | 3020 | 0.0077301 | 0.98128 | 0.01099%
OAKLAND J 1118CR198 | OAKLAND J 1118 | EAST BAY | 0.38627 | 10 | 34.69% | 0 | 0 | 7.348% | 0% | 0 | 0.0076722 | 1 | 3.2489 | 0.024926 | Low | Low | High | 2885 | 3021 | 0.0076722 | 0.97355 | 0.01091%
ALTO 1123CB | ALTO 1123 | NORTH BAY | 2.3955 | 10 | 3.352% | 0 | 0 | 39.61% | 4.121% | 0 | 0.0076595 | 1 | 3.3336 | 0.025533 | Low | Low | High | 2872 | 3022 | 0.0076595 | 0.96587 | 0.01082%
LAS GALLINAS A 11041220 | LAS GALLINAS A 1104 | NORTH BAY | 1.0215 | 10 | 17.87% | 0 | 0 | 20.99% | 0% | 0 | 0.0076561 | 1 | 3.869 | 0.029621 | Low | Low | High | 2782 | 3023 | 0.0076561 | 0.95821 | 0.01073%
SAN RAFAEL 110969860 | SAN RAFAEL 1109 | NORTH BAY | 0.67004 | 10 | 27.57% | 0 | 0 | 26.27% | 0% | 0 | 0.0076522 | 1 | 4.1175 | 0.031508 | Low | Low | High | 2735 | 3024 | 0.0076522 | 0.95056 | 0.01065%
AUBURN 1102CB | AUBURN 1102 | SIERRA | 0.41789 | 10 | 46.75% | 0 | 2 | 6.005% | 0% | 0 | 0.0076302 | 1 | 3.055 | 0.02331 | Low | Low | Medium | 2930 | 3025 | 0.0076302 | 0.94291 | 0.01056%
BOLINAS 11011064 | BOLINAS 1101 | NORTH BAY | 0.79432 | 10 | 14.47% | 2 | 1 | 17.88% | 0% | 0 | 0.0075676 | 1 | 3.2571 | 0.024648 | Low | Low | High | 2893 | 3026 | 0.0075676 | 0.93528 | 0.01048%
MC KEE 1103XR028 | MC KEE 1103 | SAN JOSE | 2.8083 | 15.9921 | 15.4% | 0 | 2 | 26.81% | 0% | 0 | 0.007561 | 1 | 4.2746 | 0.032321 | Low | Low | High | 2716 | 3027 | 0.007561 | 0.92771 | 0.01039%
VIEJO 22029089 | VIEJO 2202 | CENTRAL COAST | 0.44699 | 10 | 0% | 1 | 3 | 26.75% | 0% | 0 | 0.0075545 | 1 | 3.7807 | 0.028562 | Low | Low | High | 2808 | 3028 | 0.0075545 | 0.92015 | 0.01031%
DEL MAR 2109CB | DEL MAR 2109 | SIERRA | 1.7939 | 12.1972 | 19.79% | 0 | 1 | 27.43% | 0% | 0 | 0.0075272 | 1 | 3.1113 | 0.023419 | Low | Low | High | 2925 | 3029 | 0.0075272 | 0.91259 | 0.01022%
SNEATH LANE 110748338 | SNEATH LANE 1107 | PENINSULA | 0.48719 | 10 | 2.1% | 0 | 0 | 45.41% | 0% | 0 | 0.0075134 | 1 | 3.4081 | 0.025607 | Low | Low | High | 2869 | 3030 | 0.0075134 | 0.90507 | 0.01014%
HOLLISTER 2104855412 | HOLLISTER 2104 | CENTRAL COAST | 0.30314 | 60 | 0% | 1 | 0 | 11.12% | 0% | 0 | 0.007471 | 1 | 2.599 | 0.019417 | Low | Low | Medium | 3020 | 3031 | 0.007471 | 0.89755 | 0.01006%
VIEJO 22049540 | VIEJO 2204 | CENTRAL COAST | 0.84933 | 10 | 0% | 3 | 2 | 38.01% | 0% | 0 | 0.0074407 | 1 | 3.0127 | 0.022417 | Low | Low | Medium | 2956 | 3032 | 0.0074407 | 0.89008 | 0.009971%
ALHAMBRA 1105CB | ALHAMBRA 1105 | DIABLO | 0.38371 | 10 | 15.25% | 0 | 0 | 20.22% | 0% | 0 | 0.0074366 | 1 | 3.2796 | 0.02439 | Low | Low | High | 2900 | 3033 | 0.0074366 | 0.88264 | 0.009888%
SNEATH LANE 1107CB | SNEATH LANE 1107 | PENINSULA | 0.3748 | 10 | 41.65% | 0 | 1 | 9.682% | 0% | 0 | 0.0074343 | 1 | 3.594 | 0.026719 | Low | Low | High | 2845 | 3034 | 0.0074343 | 0.8752 | 0.009805%
SAN RAFAEL 1106837 | SAN RAFAEL 1106 | NORTH BAY | 0.43527 | 10 | 0% | 0 | 2 | 28.12% | 0% | 0 | 0.0074019 | 1 | 3.69 | 0.027313 | Low | Low | High | 2830 | 3035 | 0.0074019 | 0.86777 | 0.009721%
CLEAR LAKE 1102CB | CLEAR LAKE 1102 | HUMBOLDT | 0.13095 | 10 | 54.49% | 0 | 0 | 0.5805% | 0% | 0 | 0.0073882 | 1 | 2.7821 | 0.020555 | Low | Low | Medium | 2991 | 3036 | 0.0073882 | 0.86037 | 0.009639%
BIG RIVER 110155402 | BIG RIVER 1101 | HUMBOLDT | 2.6094 | 10 | 0.156% | 5 | 5 | 28.18% | 0% | 0 | 0.0073839 | 1 | 2.3739 | 0.017528 | Low | Low | Medium | 3053 | 3037 | 0.0073839 | 0.85298 | 0.009556%
IONE 1101CB | IONE 1101 | STOCKTON | 1.9633 | 49.7739 | 2.974% | 1 | 0 | 13.95% | 0% | 0 | 0.007346 | 1 | 3.2391 | 0.023794 | Low | Low | High | 2913 | 3038 | 0.007346 | 0.8456 | 0.009473%
SNEATH LANE 11015311 | SNEATH LANE 1101 | PENINSULA | 0.49818 | 10 | 0% | 0 | 0 | 44.61% | 0% | 0 | 0.0073269 | 1 | 4.3756 | 0.032059 | Low | Low | High | 2724 | 3039 | 0.0073269 | 0.83825 | 0.009391%
IGNACIO 1104316 | IGNACIO 1104 | NORTH BAY | 0.5655 | 10 | 40.98% | 0 | 2 | 6.524% | 0% | 0 | 0.0073158 | 1 | 3.4198 | 0.025018 | Low | Low | High | 2882 | 3040 | 0.0073158 | 0.83092 | 0.009309%
ALHAMBRA 110213333 | ALHAMBRA 1102 | DIABLO | 0.074793 | 10 | 23.29% | 0 | 0 | 25.18% | 0% | 0 | 0.007309 | 1 | 3.2612 | 0.023836 | Low | Low | High | 2912 | 3041 | 0.007309 | 0.82361 | 0.009227%
OCEANO 1105V16 | OCEANO 1105 | LOS PADRES | 1.6064 | 10 | 0% | 0 | 0 | 44.18% | 0% | 0 | 0.0072956 | 1 | 3.1854 | 0.023239 | Low | Low | High | 2934 | 3042 | 0.0072956 | 0.8163 | 0.009145%
SAN LUIS OBISPO 1104CB | SAN LUIS OBISPO 1104 | LOS PADRES | 0.36018 | 63.441 | 2.835% | 0 | 0 | 5.218% | 0% | 0 | 0.007285 | 1 | 2.718 | 0.019801 | Low | Low | Medium | 3012 | 3043 | 0.007285 | 0.809 | 0.009063%
PACIFIC GROVE 04222614 | PACIFIC GROVE 0422 | CENTRAL COAST | 0.61996 | 10 | 0% | 1 | 0 | 28.91% | 0% | 0 | 0.007251 | 1 | 4.276 | 0.031005 | Low | Low | High | 2746 | 3044 | 0.007251 | 0.80172 | 0.008982%
CASTRO VALLEY 1104MR201 | CASTRO VALLEY 1104 | MISSION | 1.8766 | 10 | 10.28% | 0 | 1 | 19.54% | 0% | 0 | 0.007241 | 1 | 3.4354 | 0.024876 | Low | Low | High | 2888 | 3045 | 0.007241 | 0.79447 | 0.0089%
FRANKLIN 1104CB | FRANKLIN 1104 | EAST BAY | 0.64777 | 10 | 0% | 0 | 2 | 12.31% | 0% | 0 | 0.0072216 | 1 | 3.7113 | 0.026802 | Low | Low | High | 2842 | 3046 | 0.0072216 | 0.78723 | 0.008819%
MC ARTHUR 110137344 | MC ARTHUR 1101 | NORTH VALLEY | 0.26567 | 10 | 48.66% | 0 | 0 | 2.972% | 0% | 0 | 0.0072135 | 1 | 1.4849 | 0.010712 | Low | Low | Low | 3143 | 3047 | 0.0072135 | 0.78 | 0.008738%
HICKS 1116LB16 | HICKS 1116 | SAN JOSE | 1.4512 | 10 | 12.53% | 1 | 1 | 15.83% | 0% | 0 | 0.0072028 | 1 | 3.6384 | 0.026207 | Low | Low | High | 2857 | 3048 | 0.0072028 | 0.77279 | 0.008657%
CAROLANDS 04049026 | CAROLANDS 0404 | PENINSULA | 0.27754 | 10 | 28.62% | 0 | 0 | 5.507% | 0% | 0 | 0.0071679 | 1 | 3.7571 | 0.026931 | Low | Low | High | 2839 | 3049 | 0.0071679 | 0.76559 | 0.008577%
WALDO 0401CB | WALDO 0401 | EAST BAY | 1.6612 | 10 | 12.79% | 0 | 1 | 29.42% | 0% | 0 | 0.0071421 | 1 | 4.5981 | 0.03284 | Low | Low | High | 2704 | 3050 | 0.0071421 | 0.75842 | 0.008496%
VIEJO 220285904 | VIEJO 2202 | CENTRAL COAST | 0.44182 | 10 | 5.103% | 1 | 0 | 22.34% | 0% | 0 | 0.007082 | 1 | 4.1688 | 0.029523 | Low | Low | High | 2785 | 3051 | 0.007082 | 0.75128 | 0.008416%
TAR FLAT 0402CB | TAR FLAT 0402 | YOSEMITE | 0.52249 | 10 | 7.104% | 0 | 0 | 35.32% | 0% | 0 | 0.0070807 | 1 | 3.3002 | 0.023368 | Low | Low | High | 2927 | 3052 | 0.0070807 | 0.7442 | 0.008337%
LUCERNE 11034624 | LUCERNE 1103 | HUMBOLDT | 0.73972 | 10 | 26.07% | 0 | 0 | 19.5% | 0% | 0 | 0.0070666 | 1 | 2.4759 | 0.017496 | Low | Low | Medium | 3054 | 3053 | 0.0070666 | 0.73712 | 0.008258%
PURISIMA 110149394 | PURISIMA 1101 | LOS PADRES | 0.38618 | 10 | 25.81% | 1 | 0 | 4.395% | 0% | 0 | 0.0070193 | 1 | 4.6217 | 0.032441 | Low | Low | High | 2713 | 3054 | 0.0070193 | 0.73005 | 0.008179%
PUEBLO 11053022 | PUEBLO 1105 | NORTH BAY | 0.42768 | 10 | 42.51% | 0 | 0 | 4.687% | 0% | 0 | 0.0069771 | 1 | 2.7525 | 0.019205 | Low | Low | Medium | 3021 | 3055 | 0.0069771 | 0.72303 | 0.0081%
SAN CARLOS 110436864 | SAN CARLOS 1104 | PENINSULA | 0.3154 | 10 | 0% | 0 | 1 | 37.17% | 0% | 0 | 0.0069476 | 1 | 4.4226 | 0.030727 | Low | Low | High | 2750 | 3056 | 0.0069476 | 0.71605 | 0.008022%
LAKEWOOD 210769586 | LAKEWOOD 2107 | DIABLO | 0.5706 | 16.4781 | 12.07% | 0 | 2 | 6.994% | 0% | 0 | 0.0069201 | 1 | 3.4182 | 0.023654 | Low | Low | High | 2918 | 3057 | 0.0069201 | 0.7091 | 0.007944%
MORGAN HILL 2105XR578 | MORGAN HILL 2105 | SAN JOSE | 0.218 | 10 | 8.67% | 0 | 0 | 31.62% | 0% | 0 | 0.0069127 | 1 | 3.4108 | 0.023578 | Low | Low | High | 2920 | 3058 | 0.0069127 | 0.70218 | 0.007866%
FORT BRAGG A 11021226 | FORT BRAGG A 1102 | HUMBOLDT | 1.1335 | 10 | 21.46% | 0 | 3 | 14.45% | 0% | 0 | 0.0068882 | 1 | 2.0906 | 0.0144 | Low | Low | Low | 3110 | 3059 | 0.0068882 | 0.69527 | 0.007789%
POINT ARENA 1101476 | POINT ARENA 1101 | HUMBOLDT | 2.7213 | 21.4527 | 0% | 6 | 2 | 18.23% | 0% | 0 | 0.0068718 | 1 | 2.4696 | 0.01697 | Low | Low | Medium | 3063 | 3060 | 0.0068718 | 0.68838 | 0.007712%
OCEANO 110376678 | OCEANO 1103 | LOS PADRES | 0.055262 | 10 | 22.91% | 0 | 2 | 14.84% | 0% | 0 | 0.0068538 | 1 | 3.5692 | 0.024463 | Low | Low | High | 2897 | 3061 | 0.0068538 | 0.68151 | 0.007635%
LAS GALLINAS A 1104304 | LAS GALLINAS A 1104 | NORTH BAY | 0.14237 | 10 | 35.52% | 0 | 1 | 5.697% | 0% | 0 | 0.0067954 | 1 | 4.2336 | 0.028769 | Low | Low | High | 2803 | 3062 | 0.0067954 | 0.67466 | 0.007558%
BERESFORD 0403CB | BERESFORD 0403 | PENINSULA | 0.94707 | 10 | 19.89% | 1 | 1 | 17.08% | 0% | 0 | 0.0067843 | 1 | 3.1734 | 0.02153 | Low | Low | High | 2974 | 3063 | 0.0067843 | 0.66786 | 0.007482%
ESTUDILLO 0401CB | ESTUDILLO 0401 | MISSION | 0.69789 | 10 | 26.72% | 0 | 0 | 14.78% | 0% | 0 | 0.0067781 | 1 | 3.4546 | 0.023416 | Low | Low | High | 2926 | 3064 | 0.0067781 | 0.66108 | 0.007406%
SAN RAFAEL 11042235 | SAN RAFAEL 1104 | NORTH BAY | 0.29854 | 10 | 0% | 0 | 1 | 34.56% | 0% | 0 | 0.0067695 | 1 | 4.8094 | 0.032557 | Low | Low | High | 2708 | 3065 | 0.0067695 | 0.6543 | 0.00733%
BRUNSWICK 111094368 | BRUNSWICK 1110 | SIERRA | 0.16855 | 10 | 0% | 0 | 0 | 35.28% | 0% | 0 | 0.0066771 | 1 | 3.0325 | 0.020249 | Low | Low | Medium | 3002 | 3066 | 0.0066771 | 0.64753 | 0.007254%
WYANDOTTE 1107CB | WYANDOTTE 1107 | NORTH VALLEY | 1.0691 | 10 | 31.7% | 0 | 1 | 7.068% | 0% | 0 | 0.0066762 | 1 | 3.9827 | 0.026589 | Low | Low | High | 2846 | 3067 | 0.0066762 | 0.64085 | 0.007179%
OAKLAND J 1105CR132 | OAKLAND J 1105 | EAST BAY | 0.28914 | 10 | 34.84% | 0 | 0 | 6.37% | 0% | 0 | 0.0066625 | 1 | 3.2608 | 0.021725 | Low | Low | High | 2969 | 3068 | 0.0066625 | 0.63418 | 0.007105%
BROWNS VALLEY 110136622 | BROWNS VALLEY 1101 | SIERRA | 2.3766 | 10 | 8.927% | 0 | 1 | 25.35% | 0% | 0 | 0.0066455 | 1 | 1.9026 | 0.012644 | Low | Low | Low | 3129 | 3069 | 0.0066455 | 0.62751 | 0.00703%
MORRO BAY 1101CB | MORRO BAY 1101 | LOS PADRES | 0.64776 | 10 | 6.384% | 0 | 0 | 29.39% | 0% | 0 | 0.0066355 | 1 | 3.4209 | 0.0227 | Low | Low | High | 2948 | 3070 | 0.0066355 | 0.62087 | 0.006956%
VIEJO 22049110 | VIEJO 2204 | CENTRAL COAST | 0.89252 | 10 | 16.91% | 0 | 0 | 20.66% | 0% | 0 | 0.0066316 | 1 | 4.2831 | 0.028404 | Low | Low | High | 2811 | 3071 | 0.0066316 | 0.61423 | 0.006881%
MORAGA 110381146 | MORAGA 1103 | DIABLO | 0.81099 | 10 | 24.05% | 0 | 0 | 14.46% | 0% | 0 | 0.00661 | 1 | 4.5238 | 0.029902 | Low | Low | High | 2777 | 3072 | 0.00661 | 0.6076 | 0.006807%
PACIFICA 1104CB | PACIFICA 1104 | PENINSULA | 0.50255 | 42.4378 | 0% | 0 | 0 | 11.92% | 0% | 0 | 0.006597 | 1 | 3.4551 | 0.022793 | Low | Low | High | 2945 | 3073 | 0.006597 | 0.60099 | 0.006733%
PLACER 110451732 | PLACER 1104 | SIERRA | 1.3434 | 10 | 21.69% | 0 | 0 | 16.14% | 0% | 0 | 0.0065925 | 1 | 3.0863 | 0.020346 | Low | Low | High | 2998 | 3074 | 0.0065925 | 0.5944 | 0.006659%
OCEANO 1106CB | OCEANO 1106 | LOS PADRES | 0.86306 | 10 | 5.571% | 1 | 4 | 19.68% | 0% | 0 | 0.0065904 | 1 | 3.3208 | 0.021885 | Low | Low | High | 2966 | 3075 | 0.0065904 | 0.5878 | 0.006585%
PENRYN 11051378 | PENRYN 1105 | SIERRA | 0.3076 | 10 | 15.69% | 2 | 1 | 16.27% | 0% | 0 | 0.0065875 | 1 | 3.4493 | 0.022722 | Low | Low | High | 2947 | 3076 | 0.0065875 | 0.58121 | 0.006511%
SOLEDAD 111435306 | SOLEDAD 1114 | CENTRAL COAST | 0.90872 | 10 | 9.031% | 0 | 0 | 12.56% | 0% | 0 | 0.0065483 | 1 | 2.7745 | 0.018169 | Low | Low | Medium | 3040 | 3077 | 0.0065483 | 0.57463 | 0.006437%
SAN MIGUEL 1106N34 | SAN MIGUEL 1106 | LOS PADRES | 0.29269 | 10 | 21.51% | 0 | 0 | 2.142% | 0% | 0 | 0.0065395 | 1 | 0.080486 | 0.00052634 | Low | Low | Low | 3181 | 3078 | 0.0065395 | 0.56808 | 0.006364%
CASTRO VALLEY 1106MR233 | CASTRO VALLEY 1106 | MISSION | 0.14387 | 10 | 11.99% | 0 | 0 | 22.61% | 0% | 0 | 0.0064943 | 1 | 3.9938 | 0.025937 | Low | Low | High | 2864 | 3079 | 0.0064943 | 0.56154 | 0.006291%
SAN CARLOS 1103 | SAN CARLOS 1103 | PENINSULA | 0.013694 | 10 | 0% | 0 | 0 | 32.32% | 0% | 0 | 0.0064833 | 1 | 4.5959 | 0.029797 | Low | Low | High | 2780 | 3080 | 0.0064833 | 0.55504 | 0.006218%
OCEANO 1105V48 | OCEANO 1105 | LOS PADRES | 0.76105 | 10 | 0% | 0 | 1 | 30.2% | 0% | 0 | 0.0064819 | 1 | 3.124 | 0.020249 | Low | Low | High | 3001 | 3081 | 0.0064819 | 0.54856 | 0.006145%
OROVILLE 11042588 | OROVILLE 1104 | NORTH VALLEY | 0.2392 | 13.5731 | 31.06% | 1 | 0 | 2.673% | 0% | 0 | 0.0064634 | 1 | 2.6797 | 0.01732 | Low | Low | Medium | 3057 | 3082 | 0.0064634 | 0.54208 | 0.006073%
VIEJO 22032634 | VIEJO 2203 | CENTRAL COAST | 0.37273 | 10 | 10.45% | 0 | 0 | 22.39% | 0% | 0 | 0.0063984 | 1 | 3.0948 | 0.019802 | Low | Low | High | 3011 | 3083 | 0.0063984 | 0.53561 | 0.006%
CAYETANO 2109MR186 | CAYETANO 2109 | MISSION | 0.10978 | 10 | 0% | 0 | 0 | 4.27% | 0% | 0 | 0.0063941 | 1 | 2.8337 | 0.018119 | Low | Low | Medium | 3041 | 3084 | 0.0063941 | 0.52922 | 0.005929%
CLARK ROAD 11022094 | CLARK ROAD 1102 | NORTH VALLEY | 0.57902 | 10 | 17.05% | 0 | 0 | 16.85% | 0% | 0 | 0.0063918 | 1 | 2.1553 | 0.013776 | Low | Low | Low | 3116 | 3085 | 0.0063918 | 0.52282 | 0.005857%
CASTRO VALLEY 1104MR236 | CASTRO VALLEY 1104 | MISSION | 1.7251 | 10 | 10.02% | 0 | 1 | 20.44% | 0% | 0 | 0.0063847 | 1 | 3.5607 | 0.022734 | Low | Low | High | 2946 | 3086 | 0.0063847 | 0.51643 | 0.005785%
OCEANO 1106V28 | OCEANO 1106 | LOS PADRES | 1.0201 | 10 | 22.73% | 0 | 0 | 11.28% | 0% | 0 | 0.006335 | 1 | 3.973 | 0.025169 | Low | Low | High | 2878 | 3087 | 0.006335 | 0.51005 | 0.005714%
TEMPLETON 2108A64 | TEMPLETON 2108 | LOS PADRES | 1.3676 | 10 | 21.6% | 0 | 0 | 11.56% | 0% | 0 | 0.0062941 | 1 | 2.6112 | 0.016435 | Low | Low | Medium | 3073 | 3088 | 0.0062941 | 0.50371 | 0.005643%
HALF MOON BAY 110265568 | HALF MOON BAY 1102 | PENINSULA | 0.079124 | 10 | 0% | 0 | 0 | 2.534% | 0% | 0 | 0.0062845 | 1 | 3.8984 | 0.0245 | Low | Low | High | 2895 | 3089 | 0.0062845 | 0.49742 | 0.005572%
SAN RAFAEL 110648752 | SAN RAFAEL 1106 | NORTH BAY | 0.61983 | 10 | 0% | 0 | 1 | 26.76% | 0% | 0 | 0.0062637 | 1 | 3.4892 | 0.021855 | Low | Low | High | 2968 | 3090 | 0.0062637 | 0.49113 | 0.005502%
MARTELL 1103CB | MARTELL 1103 | STOCKTON | 0.8745 | 10 | 17.84% | 0 | 0 | 13.95% | 0% | 0 | 0.0062499 | 1 | 1.9128 | 0.011955 | Low | Low | Low | 3138 | 3091 | 0.0062499 | 0.48487 | 0.005432%
CORNING 110187304 | CORNING 1101 | NORTH VALLEY | 1.5372 | 10 | 14.41% | 0 | 3 | 10.47% | 0% | 0 | 0.0062491 | 1 | 0.88021 | 0.0055005 | Low | Low | Low | 3168 | 3092 | 0.0062491 | 0.47862 | 0.005362%
PACIFICA 1103CB | PACIFICA 1103 | PENINSULA | 0.044512 | 50.42 | 0% | 0 | 0 | 0.9046% | 0% | 0 | 0.0062412 | 1 | 3.4634 | 0.021616 | Low | Low | High | 2971 | 3093 | 0.0062412 | 0.47237 | 0.005292%
SARATOGA 1105CB | SARATOGA 1105 | DE ANZA | 0.26967 | 10 | 28.45% | 0 | 0 | 4.984% | 0% | 0 | 0.0062358 | 1 | 3.6613 | 0.022831 | Low | Low | High | 2944 | 3094 | 0.0062358 | 0.46613 | 0.005222%
STONE CORRAL 11087100 | STONE CORRAL 1108 | FRESNO | 2.9159 | 10 | 14.41% | 0 | 0 | 15.91% | 0% | 0 | 0.0061962 | 1 | 1.7025 | 0.010549 | Low | Low | Low | 3144 | 3095 | 0.0061962 | 0.45989 | 0.005152%
CLARK ROAD 1102CB | CLARK ROAD 1102 | NORTH VALLEY | 0.16153 | 10 | 1.759% | 0 | 1 | 10.59% | 0% | 0 | 0.006177 | 1 | 1.3847 | 0.0085535 | Low | Low | Low | 3157 | 3096 | 0.006177 | 0.4537 | 0.005083%
PAUL SWEET 210510290 | PAUL SWEET 2105 | CENTRAL COAST | 0.48079 | 10 | 22.97% | 0 | 0 | 8.329% | 0% | 0 | 0.0061637 | 1 | 4.1772 | 0.025747 | Low | Low | High | 2867 | 3097 | 0.0061637 | 0.44752 | 0.005013%
CLARKSVILLE 2106CB | CLARKSVILLE 2106 | SIERRA | 0.13957 | 10 | 0% | 0 | 0 | 27.21% | 0% | 0 | 0.0061619 | 1 | 3.5511 | 0.021882 | Low | Low | High | 2967 | 3098 | 0.0061619 | 0.44136 | 0.004944%
PLACER 1101CB | PLACER 1101 | SIERRA | 0.77573 | 10 | 3.906% | 0 | 0 | 10.24% | 0% | 0 | 0.0061355 | 1 | 3.3142 | 0.020334 | Low | Low | High | 2999 | 3099 | 0.0061355 | 0.43519 | 0.004875%
TIDEWATER 210695842 | TIDEWATER 2106 | DIABLO | 0.21866 | 10 | 7.343% | 0 | 0 | 20.55% | 0% | 0 | 0.0061241 | 1 | 3.7665 | 0.023066 | Low | Low | High | 2938 | 3100 | 0.0061241 | 0.42906 | 0.004807%
MARTELL 110198374 | MARTELL 1101 | STOCKTON | 0.48931 | 10 | 16.23% | 0 | 0 | 12.89% | 0% | 0 | 0.0061034 | 1 | 3.2848 | 0.020049 | Low | Low | High | 3008 | 3101 | 0.0061034 | 0.42293 | 0.004738%
SNEATH LANE 1101CB | SNEATH LANE 1101 | PENINSULA | 0.21236 | 10 | 2.867% | 0 | 1 | 21.58% | 0% | 0 | 0.0060901 | 1 | 3.7657 | 0.022933 | Low | Low | High | 2940 | 3102 | 0.0060901 | 0.41683 | 0.00467%
SAUSALITO 11021224 | SAUSALITO 1102 | NORTH BAY | 0.046722 | 10 | 29.73% | 0 | 0 | 1.494% | 0% | 0 | 0.0060863 | 1 | 3.4619 | 0.02107 | Low | Low | High | 2981 | 3103 | 0.0060863 | 0.41074 | 0.004601%
LAS GALLINAS A 1105CB | LAS GALLINAS A 1105 | NORTH BAY | 0.31033 | 10 | 12.89% | 0 | 0 | 14.92% | 0% | 0 | 0.0060597 | 1 | 3.5062 | 0.021246 | Low | Low | High | 2977 | 3104 | 0.0060597 | 0.40465 | 0.004533%
PIT NO 1 11019702 | PIT NO 1 1101 | NORTH VALLEY | 0.44484 | 10 | 24.55% | 0 | 0 | 4.849% | 0% | 0 | 0.0060315 | 1 | 2.0734 | 0.012506 | Low | Low | Low | 3130 | 3105 | 0.0060315 | 0.39859 | 0.004465%
BANCROFT 0402CB | BANCROFT 0402 | EAST BAY | 1.0716 | 10 | 1.687% | 0 | 0 | 23.45% | 0% | 0 | 0.0060178 | 1 | 3.4396 | 0.020699 | Low | Low | High | 2988 | 3106 | 0.0060178 | 0.39256 | 0.004398%
FAIRVIEW 2207P142 | FAIRVIEW 2207 | DIABLO | 0.64407 | 10 | 4.931% | 0 | 0 | 20.76% | 0% | 0 | 0.0060169 | 1 | 3.6784 | 0.022132 | Low | Low | High | 2961 | 3107 | 0.0060169 | 0.38654 | 0.00433%
PAUL SWEET 210212850 | PAUL SWEET 2102 | CENTRAL COAST | 0.99852 | 10 | 0% | 0 | 0 | 24.38% | 0% | 0 | 0.0059903 | 1 | 4.0239 | 0.024104 | Low | Low | High | 2907 | 3108 | 0.0059903 | 0.38053 | 0.004263%
WILLOW PASS 210821196 | WILLOW PASS 2108 | DIABLO | 0.047227 | 10 | 0% | 0 | 0 | 23.89% | 0% | 0 | 0.005961 | 1 | 3.2102 | 0.019136 | Low | Low | High | 3025 | 3109 | 0.005961 | 0.37454 | 0.004196%
OAKLAND J 1105CR130 | OAKLAND J 1105 | EAST BAY | 0.95094 | 10 | 5.238% | 0 | 0 | 19.42% | 0% | 0 | 0.0059522 | 1 | 3.464 | 0.020619 | Low | Low | High | 2989 | 3110 | 0.0059522 | 0.36858 | 0.004129%
MORRO BAY 1101V70 | MORRO BAY 1101 | LOS PADRES | 0.13653 | 10 | 0% | 0 | 0 | 22.43% | 0% | 0 | 0.0058754 | 1 | 3.6321 | 0.02134 | Low | Low | High | 2976 | 3111 | 0.0058754 | 0.36262 | 0.004062%
ARLINGTON 0401CB | ARLINGTON 0401 | EAST BAY | 0.76473 | 10 | 0% | 0 | 1 | 19.15% | 0% | 0 | 0.005806 | 1 | 4.3631 | 0.025332 | Low | Low | High | 2876 | 3112 | 0.005806 | 0.35675 | 0.003997%
CARMEL 0402CB | CARMEL 0402 | CENTRAL COAST | 0.30828 | 10 | 0% | 0 | 0 | 21.19% | 0% | 0 | 0.0058032 | 1 | 3.3503 | 0.019442 | Low | Low | High | 3019 | 3113 | 0.0058032 | 0.35094 | 0.003932%
HALF MOON BAY 1102CB | HALF MOON BAY 1102 | PENINSULA | 0.43987 | 10 | 9.941% | 0 | 1 | 10.85% | 0% | 0 | 0.0057997 | 1 | 4.0421 | 0.023443 | Low | Low | High | 2924 | 3114 | 0.0057997 | 0.34514 | 0.003867%
IGNACIO 1104 | IGNACIO 1104 | NORTH BAY | 0.012266 | 10 | 0% | 0 | 0 | 20.53% | 0% | 0 | 0.005765 | 1 | 2.9425 | 0.016964 | Low | Low | Medium | 3064 | 3115 | 0.005765 | 0.33934 | 0.003802%
FORT BRAGG A 1103588 | FORT BRAGG A 1103 | HUMBOLDT | 0.37656 | 10 | 0% | 0 | 0 | 20.3% | 0% | 0 | 0.0057518 | 1 | 3.299 | 0.018975 | Low | Low | High | 3030 | 3116 | 0.0057518 | 0.33357 | 0.003737%
TASSAJARA 211238868 | TASSAJARA 2112 | DIABLO | 0.17353 | 10 | 11.26% | 2 | 2 | 4.039% | 0% | 0 | 0.0057426 | 1 | 3.9277 | 0.022555 | Low | Low | High | 2954 | 3117 | 0.0057426 | 0.32782 | 0.003673%
OLEMA 110149756 | OLEMA 1101 | NORTH BAY | 0.14983 | 10 | 0% | 0 | 2 | 2.553% | 0% | 0 | 0.0057386 | 1 | 1.9687 | 0.011298 | Low | Low | Low | 3141 | 3118 | 0.0057386 | 0.32208 | 0.003608%
LAKEWOOD 1102CB | LAKEWOOD 1102 | DIABLO | 0.47236 | 10 | 18.19% | 0 | 0 | 4.922% | 0% | 0 | 0.0057291 | 1 | 3.3099 | 0.018962 | Low | Low | High | 3031 | 3119 | 0.0057291 | 0.31634 | 0.003544%
OAKLAND K 1103CB | OAKLAND K 1103 | EAST BAY | 0.65834 | 10 | 0% | 1 | 2 | 13.28% | 0% | 0 | 0.0056661 | 1 | 4.3233 | 0.024496 | Low | Low | High | 2896 | 3120 | 0.0056661 | 0.31061 | 0.00348%
FLINT 110138570 | FLINT 1101 | SIERRA | 0.12622 | 10 | 17.37% | 0 | 0 | 3.673% | 0% | 0 | 0.0056203 | 1 | 3.1886 | 0.017921 | Low | Low | High | 3047 | 3121 | 0.0056203 | 0.30495 | 0.003416%
SAN RAFAEL 1105CB | SAN RAFAEL 1105 | NORTH BAY | 0.49095 | 10 | 6.778% | 3 | 1 | 5.07% | 0% | 0 | 0.0055495 | 1 | 3.5772 | 0.019852 | Low | Low | High | 3010 | 3122 | 0.0055495 | 0.29933 | 0.003353%
SNEATH LANE 1102CB | SNEATH LANE 1102 | PENINSULA | 0.28247 | 10 | 3.955% | 0 | 1 | 11.21% | 0% | 0 | 0.0055412 | 1 | 3.5434 | 0.019634 | Low | Low | High | 3016 | 3123 | 0.0055412 | 0.29378 | 0.003291%
FREMONT 1104MR707 | FREMONT 1104 | MISSION | 1.4479 | 10 | 0% | 0 | 0 | 16.1% | 0% | 0 | 0.0055159 | 1 | 1.8893 | 0.010421 | Low | Low | Low | 3145 | 3124 | 0.0055159 | 0.28824 | 0.003229%
OAKLAND J 1105153228 | OAKLAND J 1105 | EAST BAY | 0.47385 | 10 | 4.597% | 0 | 0 | 11.41% | 0% | 0 | 0.0054665 | 1 | 3.2905 | 0.017988 | Low | Low | High | 3045 | 3125 | 0.0054665 | 0.28272 | 0.003167%
OCEANO 1105V42 | OCEANO 1105 | LOS PADRES | 0.34173 | 10 | 0% | 0 | 0 | 14.57% | 0% | 0 | 0.0054323 | 1 | 2.6024 | 0.014137 | Low | Low | Medium | 3114 | 3126 | 0.0054323 | 0.27725 | 0.003106%
CORRAL 110175204 | CORRAL 1101 | STOCKTON | 1.1128 | 10 | 10.09% | 0 | 0 | 5.993% | 0% | 0 | 0.0054182 | 1 | 2.7419 | 0.014856 | Low | Low | Medium | 3105 | 3127 | 0.0054182 | 0.27182 | 0.003045%
VIEJO 22029488 | VIEJO 2202 | CENTRAL COAST | 0.18548 | 10 | 0% | 0 | 0 | 14.19% | 0% | 0 | 0.0054123 | 1 | 3.9833 | 0.021559 | Low | Low | High | 2973 | 3128 | 0.0054123 | 0.2664 | 0.002984%
POSO MOUNTAIN 21011703 | POSO MOUNTAIN 2101 | KERN | 0.0074631 | 10 | 0% | 0 | 0 | 0.304% | 0% | 0 | 0.0053821 | 1 | 2.7786 | 0.014955 | Low | Low | Medium | 3103 | 3129 | 0.0053821 | 0.26099 | 0.002924%
CARMEL 0405CB | CARMEL 0405 | CENTRAL COAST | 0.33684 | 10 | 0% | 0 | 1 | 10.77% | 0% | 0 | 0.0053408 | 1 | 3.4633 | 0.018497 | Low | Low | High | 3034 | 3130 | 0.0053408 | 0.25561 | 0.002864%
EL CERRITO G 1111CB | EL CERRITO G 1111 | EAST BAY | 0.94606 | 10 | 6.246% | 0 | 0 | 7.497% | 0% | 0 | 0.0053291 | 1 | 5.2654 | 0.028059 | Low | Low | High | 2815 | 3131 | 0.0053291 | 0.25027 | 0.002804%
GIRVAN 1101CB | GIRVAN 1101 | NORTH VALLEY | 0.35544 | 10 | 1.64% | 0 | 0 | 10.78% | 0% | 0 | 0.0053021 | 1 | 2.487 | 0.013186 | Low | Low | Medium | 3123 | 3132 | 0.0053021 | 0.24494 | 0.002744%
ROSSMOOR 110479146 | ROSSMOOR 1104 | DIABLO | 0.24893 | 10 | 0% | 0 | 0 | 11.42% | 0% | 0 | 0.0052646 | 1 | 3.5101 | 0.018479 | Low | Low | High | 3035 | 3133 | 0.0052646 | 0.23964 | 0.002685%
MONTEREY 04012642 | MONTEREY 0401 | CENTRAL COAST | 0.26645 | 10 | 0% | 0 | 0 | 10.11% | 0% | 0 | 0.0051963 | 1 | 3.0669 | 0.015936 | Low | Low | Medium | 3085 | 3134 | 0.0051963 | 0.23437 | 0.002626%
BOSTON 0401CR242 | BOSTON 0401 | EAST BAY | 0.44969 | 10 | 0% | 0 | 0 | 9.847% | 0% | 0 | 0.0051828 | 1 | 3.8356 | 0.019879 | Low | Low | High | 3009 | 3135 | 0.0051828 | 0.22918 | 0.002567%
DEL MONTE 210386496 | DEL MONTE 2103 | CENTRAL COAST | 0.39145 | 10 | 0% | 3 | 0 | 5.331% | 0% | 0 | 0.0051542 | 1 | 3.545 | 0.018272 | Low | Low | High | 3038 | 3136 | 0.0051542 | 0.22399 | 0.002509%
ARCATA 112233060 | ARCATA 1122 | HUMBOLDT | 0.34235 | 10 | 0% | 0 | 1 | 7.017% | 0% | 0 | 0.0051448 | 1 | 3.0094 | 0.015483 | Low | Low | Medium | 3096 | 3137 | 0.0051448 | 0.21884 | 0.002452%
SNEATH LANE 110168070 | SNEATH LANE 1101 | PENINSULA | 0.099639 | 10 | 0% | 0 | 2 | 4.651% | 0% | 0 | 0.0051309 | 1 | 3.9783 | 0.020412 | Low | Low | High | 2995 | 3138 | 0.0051309 | 0.21369 | 0.002394%
VIEJO 22022014 | VIEJO 2202 | CENTRAL COAST | 0.34884 | 10 | 0% | 0 | 0 | 8.641% | 0% | 0 | 0.0051208 | 1 | 3.9267 | 0.020108 | Low | Low | High | 3007 | 3139 | 0.0051208 | 0.20856 | 0.002336%
CLARKSVILLE 2103CB | CLARKSVILLE 2103 | SIERRA | 0.11367 | 10 | 0% | 0 | 0 | 7.91% | 0% | 0 | 0.0050836 | 1 | 3.5358 | 0.017975 | Low | Low | High | 3046 | 3140 | 0.0050836 | 0.20344 | 0.002279%
VACAVILLE 110847860 | VACAVILLE 1108 | SACRAMENTO | 0.28908 | 10 | 0% | 0 | 0 | 7.334% | 0% | 0 | 0.0050545 | 1 | 3.0859 | 0.015598 | Low | Low | High | 3093 | 3141 | 0.0050545 | 0.19836 | 0.002222%
SAN RAFAEL 11061230 | SAN RAFAEL 1106 | NORTH BAY | 0.27095 | 10 | 0% | 0 | 1 | 5.214% | 0% | 0 | 0.0050532 | 1 | 3.7783 | 0.019092 | Low | Low | High | 3028 | 3142 | 0.0050532 | 0.1933 | 0.002166%
DEL MAR 210938684 | DEL MAR 2109 | SIERRA | 0.062211 | 10 | 0% | 0 | 0 | 6.669% | 0% | 0 | 0.0050211 | 1 | 3.2725 | 0.016432 | Low | Low | High | 3074 | 3143 | 0.0050211 | 0.18825 | 0.002109%
SARATOGA 1103LC40 | SARATOGA 1103 | DE ANZA | 0.12637 | 10 | 0% | 0 | 0 | 6.576% | 0% | 0 | 0.0050164 | 1 | 3.9395 | 0.019762 | Low | Low | High | 3013 | 3144 | 0.0050164 | 0.18323 | 0.002053%
EL CERRITO G 1108CB | EL CERRITO G 1108 | EAST BAY | 0.47538 | 10 | 0% | 0 | 0 | 6.483% | 0% | 0 | 0.0050118 | 1 | 4.7287 | 0.023699 | Low | Low | High | 2915 | 3145 | 0.0050118 | 0.17821 | 0.001996%
FORT BRAGG A 110436526 | FORT BRAGG A 1104 | HUMBOLDT | 0.39885 | 10 | 0% | 0 | 0 | 6.124% | 0% | 0 | 0.0049939 | 1 | 3.6762 | 0.018359 | Low | Low | High | 3037 | 3146 | 0.0049939 | 0.1732 | 0.00194%
SHINGLE SPRINGS 210851474 | SHINGLE SPRINGS 2108 | SIERRA | 0.24496 | 10 | 0% | 0 | 0 | 5.255% | 0% | 0 | 0.0049508 | 1 | 3.2752 | 0.016215 | Low | Low | High | 3076 | 3147 | 0.0049508 | 0.16821 | 0.001884%
FORT BRAGG A 1101CB | FORT BRAGG A 1101 | HUMBOLDT | 0.22122 | 10 | 0% | 0 | 1 | 2.86% | 0% | 0 | 0.0049359 | 1 | 3.4946 | 0.017249 | Low | Low | High | 3060 | 3148 | 0.0049359 | 0.16326 | 0.001829%
RIO DELL 11028768 | RIO DELL 1102 | HUMBOLDT | 0.28084 | 10 | 0% | 0 | 0 | 4.757% | 0% | 0 | 0.0049263 | 1 | 1.9394 | 0.0095539 | Low | Low | Low | 3150 | 3149 | 0.0049263 | 0.15832 | 0.001774%
SNEATH LANE 110275844 | SNEATH LANE 1102 | PENINSULA | 0.025403 | 10 | 0% | 0 | 0 | 4.723% | 0% | 0 | 0.0049246 | 1 | 3.2777 | 0.016141 | Low | Low | High | 3079 | 3150 | 0.0049246 | 0.15339 | 0.001718%
GREENBRAE 1104751 | GREENBRAE 1104 | NORTH BAY | 0.079918 | 10 | 0% | 0 | 1 | 2.532% | 0% | 0 | 0.0049198 | 1 | 3.5848 | 0.017636 | Low | Low | High | 3050 | 3151 | 0.0049198 | 0.14847 | 0.001663%
BRUNSWICK 111095576 | BRUNSWICK 1110 | SIERRA | 0.15603 | 10 | 0% | 0 | 0 | 4.385% | 0% | 0 | 0.004908 | 1 | 3.0967 | 0.015199 | Low | Low | High | 3100 | 3152 | 0.004908 | 0.14355 | 0.001608%
MILPITAS 1109XR044 | MILPITAS 1109 | SAN JOSE | 0.07893 | 10 | 0% | 0 | 0 | 4.212% | 0% | 0 | 0.0048996 | 1 | 3.2735 | 0.016039 | Low | Low | High | 3084 | 3153 | 0.0048996 | 0.13864 | 0.001553%
SAN LEANDRO U 1109CR344 | SAN LEANDRO U 1109 | MISSION | 0.097411 | 10 | 0% | 0 | 0 | 3.929% | 0% | 0 | 0.0048858 | 1 | 3.393 | 0.016577 | Low | Low | High | 3070 | 3154 | 0.0048858 | 0.13374 | 0.001498%
SARATOGA 1107CB | SARATOGA 1107 | DE ANZA | 0.16938 | 10 | 0% | 0 | 1 | 1.739% | 0% | 0 | 0.0048811 | 1 | 3.8453 | 0.018769 | Low | Low | High | 3032 | 3155 | 0.0048811 | 0.12886 | 0.001444%
SAN RAFAEL 11092213 | SAN RAFAEL 1109 | NORTH BAY | 0.014561 | 10 | 0% | 0 | 0 | 3.395% | 0% | 0 | 0.0048598 | 1 | 4.438 | 0.021568 | Low | Low | High | 2972 | 3156 | 0.0048598 | 0.12398 | 0.001389%
FORT BRAGG A 1104CB | FORT BRAGG A 1104 | HUMBOLDT | 0.049503 | 10 | 0% | 1 | 0 | 1.775% | 0% | 0 | 0.0048453 | 1 | 3.575 | 0.017322 | Low | Low | High | 3056 | 3157 | 0.0048453 | 0.11912 | 0.001334%
BRUNSWICK 110765574 | BRUNSWICK 1107 | SIERRA | 0.053599 | 10 | 0% | 0 | 0 | 3.058% | 0% | 0 | 0.0048435 | 1 | 2.9407 | 0.014243 | Low | Low | Medium | 3113 | 3158 | 0.0048435 | 0.11427 | 0.00128%
ALHAMBRA 1102CB | ALHAMBRA 1102 | DIABLO | 0.16935 | 10 | 0% | 0 | 0 | 2.96% | 0% | 0 | 0.0048388 | 1 | 3.2866 | 0.015903 | Low | Low | High | 3086 | 3159 | 0.0048388 | 0.10943 | 0.001226%
VALLEY VIEW 1105P124 | VALLEY VIEW 1105 | EAST BAY | 0.092976 | 10 | 0% | 0 | 0 | 2.939% | 0% | 0 | 0.0048377 | 1 | 3.7353 | 0.01807 | Low | Low | High | 3042 | 3160 | 0.0048377 | 0.10459 | 0.001172%
WOODSIDE 11028862 | WOODSIDE 1102 | PENINSULA | 0.10582 | 10 | 0% | 0 | 0 | 2.762% | 0% | 0 | 0.0048292 | 1 | 4.4266 | 0.021377 | Low | Low | High | 2975 | 3161 | 0.0048292 | 0.09975 | 0.001117%
FRANKLIN 1101P132 | FRANKLIN 1101 | EAST BAY | 0.033203 | 10 | 0% | 0 | 0 | 2.185% | 0% | 0 | 0.0048015 | 1 | 3.2929 | 0.015811 | Low | Low | High | 3090 | 3162 | 0.0048015 | 0.094921 | 0.001063%
HORSESHOE 1104CB | HORSESHOE 1104 | SIERRA | 0.063337 | 10 | 0% | 0 | 0 | 2.137% | 0% | 0 | 0.0047992 | 1 | 4.0681 | 0.019524 | Low | Low | High | 3017 | 3163 | 0.0047992 | 0.09012 | 0.00101%
HARRIS 11084674 | HARRIS 1108 | HUMBOLDT | 0.15936 | 10 | 0% | 0 | 0 | 1.98% | 0% | 0 | 0.0047917 | 1 | 5.073 | 0.024308 | Low | Low | High | 2901 | 3164 | 0.0047917 | 0.08532 | 0.0009558%
CASTRO VALLEY 1101MR518 | CASTRO VALLEY 1101 | MISSION | 0.037775 | 10 | 0% | 0 | 0 | 1.912% | 0% | 0 | 0.0047885 | 1 | 4.111 | 0.019686 | Low | Low | High | 3015 | 3165 | 0.0047885 | 0.080529 | 0.0009021%
HALF MOON BAY 11019014 | HALF MOON BAY 1101 | PENINSULA | 0.031423 | 10 | 0% | 0 | 0 | 1.737% | 0% | 0 | 0.0047801 | 1 | 4.0077 | 0.019157 | Low | Low | High | 3022 | 3166 | 0.0047801 | 0.07574 | 0.0008485%
VIEJO 22039094 | VIEJO 2203 | CENTRAL COAST | 0.038317 | 10 | 0% | 0 | 0 | 1.572% | 0% | 0 | 0.0047723 | 1 | 3.3195 | 0.015842 | Low | Low | High | 3087 | 3167 | 0.0047723 | 0.07096 | 0.000795%
EL CERRITO G 1108BR346 | EL CERRITO G 1108 | EAST BAY | 0.1038 | 10 | 0% | 0 | 0 | 1.483% | 0% | 0 | 0.004768 | 1 | 4.878 | 0.023259 | Low | Low | High | 2933 | 3168 | 0.004768 | 0.066188 | 0.0007415%
SUMMIT 110168706 | SUMMIT 1101 | SIERRA | 0.058904 | 10 | 0% | 0 | 0 | 1.149% | 0% | 0 | 0.0047522 | 1 | 1.0375 | 0.0049304 | Low | Low | Low | 3173 | 3169 | 0.0047522 | 0.06142 | 0.0006881%
RINCON 1102640 | RINCON 1102 | SONOMA | 0.04813 | 10 | 0% | 0 | 0 | 1.143% | 0% | 0 | 0.0047519 | 1 | 3.3054 | 0.015707 | Low | Low | High | 3091 | 3170 | 0.0047519 | 0.056667 | 0.0006348%
CAROLANDS 040484797 | CAROLANDS 0404 | PENINSULA | 0.013784 | 10 | 0% | 0 | 0 | 1.034% | 0% | 0 | 0.0047467 | 1 | 3.2801 | 0.01557 | Low | Low | High | 3094 | 3171 | 0.0047467 | 0.051916 | 0.0005816%
WYANDOTTE 1103CB | WYANDOTTE 1103 | NORTH VALLEY | 0.060864 | 10 | 0% | 0 | 0 | 0.8345% | 0% | 0 | 0.0047373 | 1 | 3.8992 | 0.018471 | Low | Low | High | 3036 | 3172 | 0.0047373 | 0.047169 | 0.0005284%
LAURELES 1112CB | LAURELES 1112 | CENTRAL COAST | 0.015644 | 10 | 0% | 0 | 0 | 0.6574% | 0% | 0 | 0.0047289 | 1 | 2.5304 | 0.011966 | Low | Low | Medium | 3137 | 3173 | 0.0047289 | 0.042432 | 0.0004754%
ALTO 112088190 | ALTO 1120 | NORTH BAY | 0.01959 | 10 | 0% | 0 | 0 | 0.6244% | 0% | 0 | 0.0047274 | 1 | 3.0907 | 0.014611 | Low | Low | High | 3107 | 3174 | 0.0047274 | 0.037703 | 0.0004224%
OCEANO 1104Q04 | OCEANO 1104 | LOS PADRES | 0.015582 | 10 | 0% | 0 | 0 | 0.5987% | 0% | 0 | 0.0047262 | 1 | 4.4629 | 0.021092 | Low | Low | High | 2980 | 3175 | 0.0047262 | 0.032975 | 0.0003694%
VASONA 1102CB | VASONA 1102 | DE ANZA | 0.06716 | 10 | 0% | 0 | 0 | 0.4408% | 0% | 0 | 0.0047187 | 1 | 4.7083 | 0.022217 | Low | Low | High | 2959 | 3176 | 0.0047187 | 0.028249 | 0.0003165%
OAKLAND J 1116CR420 | OAKLAND J 1116 | EAST BAY | 0.031861 | 10 | 0% | 0 | 0 | 0.2787% | 0% | 0 | 0.0047111 | 1 | 3.508 | 0.016527 | Low | Low | High | 3071 | 3177 | 0.0047111 | 0.02353 | 0.0002636%
ALTO 1121CB | ALTO 1121 | NORTH BAY | 0.013093 | 10 | 0% | 0 | 0 | 0.2456% | 0% | 0 | 0.0047095 | 1 | 3.1177 | 0.014683 | Low | Low | High | 3106 | 3178 | 0.0047095 | 0.018819 | 0.0002108%
BRUNSWICK 1110CB | BRUNSWICK 1110 | SIERRA | 0.0037878 | 10 | 0% | 0 | 0 | 0.2212% | 0% | 0 | 0.0047084 | 1 | 2.9563 | 0.01392 | Low | Low | Medium | 3115 | 3179 | 0.0047084 | 0.01411 | 0.0001581%
CAYUCOS 1101W14 | CAYUCOS 1101 | LOS PADRES | 0.012808 | 10 | 0% | 0 | 0 | 0.1056% | 0% | 0 | 0.004703 | 1 | 2.7337 | 0.012857 | Low | Low | Medium | 3127 | 3180 | 0.004703 | 0.0094015 | 0.0001053%
REEDLEY 11127240 | REEDLEY 1112 | FRESNO | 0.0028032 | 10 | 0% | 0 | 0 | 0.01029% | 0% | 0 | 0.0046985 | 1 | 3.2223 | 0.01514 | Low | Low | High | 3101 | 3181 | 0.0046985 | 0.0046985 | 5.264e-05%
OCEANO 1105V20 | OCEANO 1105 | LOS PADRES | 0.031809 | 10 | 0% | 0 | 0 | 0.5465% | 0% | 0 | 0.0047237 | 0 | 0 | 0 | Low | Low | Low | 3182 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
ECHO SUMMIT 1101CB | ECHO SUMMIT 1101 | (blank) | 0.03514 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 0 | 0 | 0 | Medium | Medium | Low | 3182 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
MC ARTHUR 110137388 | MC ARTHUR 1101 | NORTH VALLEY | 8.6734 | 54.6058 | 74.62% | 0 | 2 | 69.39% | 0% | 0 | 0.024182 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
CHOLAME 2102X10 | CHOLAME 2102 | LOS PADRES | 19.7574 | 72.3337 | 100% | 0 | 0 | 44.78% | 0% | 0 | 0.028694 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
DUNLAP 110239190 | DUNLAP 1102 | FRESNO | 1.8032 | 10 | 99.73% | 0 | 0 | 100% | 0% | 0 | 0.02845 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
LAYTONVILLE 11011760 | LAYTONVILLE 1101 | HUMBOLDT | 8.2141 | 83.102 | 88.6% | 5 | 4 | 64.9% | 0% | 0 | 0.039524 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
OILFIELDS 11037006 | OILFIELDS 1103 | CENTRAL COAST | 2.4385 | 10 | 100% | 0 | 0 | 16.07% | 0% | 0 | 0.016263 | 0 | 0 | -0.00036352 | Low | Low | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
CARLOTTA 112144150 | CARLOTTA 1121 | HUMBOLDT | 3.5728 | 56.6428 | 100% | 0 | 1 | 100% | 0% | 0 | 0.039603 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
DUNLAP 11027050 | DUNLAP 1102 | FRESNO | 9.1044 | 57.339 | 92.11% | 4 | 10 | 100% | 0% | 0 | 0.15825 | 0 | 0 | -0.00036352 | High | High | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
PIT NO 5 11013308 | PIT NO 5 1101 | NORTH VALLEY | 0.044135 | 85 | 100% | 0 | 0 | 100% | 0% | 0 | 0.046733 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
EL DORADO PH 210113532 | EL DORADO PH 2101 | SIERRA | 5.3271 | 64.1847 | 100% | 5 | 1 | 100% | 0% | 0 | 0.082958 | 0 | 0 | -0.00036352 | High | High | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
BRIDGEVILLE 1102 | BRIDGEVILLE 1102 | HUMBOLDT | 0.0078479 | 90 | 100% | 0 | 0 | 100% | 0% | 0 | 0.048281 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
BRIDGEVILLE 110237486 | BRIDGEVILLE 1102 | HUMBOLDT | 10.3672 | 71.0468 | 99.35% | 4 | 7 | 92.24% | 0% | 0 | 0.054132 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
DUNLAP 11037170 | DUNLAP 1103 | FRESNO | 5.3633 | 51.4528 | 91.12% | 7 | 8 | 100% | 0% | 0 | 0.057836 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
DUNLAP 1102778286 | DUNLAP 1102 | FRESNO | 2.6016 | 93.4441 | 63.93% | 0 | 0 | 100% | 0% | 0 | 0.042218 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
DUNLAP 1102CB | DUNLAP 1102 | FRESNO | 6.506 | 11.6092 | 99.83% | 1 | 2 | 100% | 0% | 0 | 0.034553 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
BOGARD 1101CB | BOGARD 1101 | NORTH VALLEY | 0.51623 | 20.4818 | 100% | 1 | 0 | 100% | 0% | 0 | 0.03523 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
DUNLAP 11037080 | DUNLAP 1103 | FRESNO | 7.9166 | 53.1398 | 56.92% | 4 | 5 | 100% | 0% | 0 | 0.052315 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
DUNLAP 11027290 | DUNLAP 1102 | FRESNO | 0.73169 | 39.1465 | 99.26% | 0 | 9 | 100% | 0% | 0 | 0.04685 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
DUNLAP 1103CB | DUNLAP 1103 | FRESNO | 5.3266 | 46.6515 | 99.77% | 2 | 1 | 100% | 0% | 0 | 0.043161 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
BALCH NO 1 1101R372 | BALCH NO 1 1101 | FRESNO | 6.0973 | 42.1008 | 100% | 0 | 0 | 100% | 0% | 0 | 0.035267 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
EL DORADO PH 210136764 | EL DORADO PH 2101 | SIERRA | 3.1646 | 79.8685 | 100% | 3 | 0 | 72.39% | 0% | 0 | 0.12435 | 0 | 0 | -0.00036352 | High | High | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
BRIDGEVILLE 1102CB | BRIDGEVILLE 1102 | HUMBOLDT | 0.72529 | 72.3371 | 88.58% | 0 | 0 | 5.257% | 0% | 0 | 0.020259 | 0 | 0 | -0.00036352 | Low | Low | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%
DUNLAP 11037991F | DUNLAP 1103 | FRESNO | 2.6521 | 79.9208 | 100% | 1 | 4 | 100% | 0% | 0 | 0.056283 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | 3.1521e-11 | 3.531e-13%

## conductor_pz_summary_hftd_23_re
PZ_idx | circuit_protection_zone_id | feeder_id | feeder_name | primary_length_m_hftd_23 | Length in Miles | pixel_count | Total Risk | mean_mavf_core_risk | mean_mavf_core_risk_rank | Cumulative Miles | Decreasing Risk |  | Dot 1 | Dot 2 | Dot 3 | Dot 4 | Dot 5 | PSPS Count
10544 | OREGON TRAIL 1103CUS391 | 103521103 | OREGON TRAIL 1103 | 36.3577 | 0.022596 | 1 | 3.1639 | 3.1639 | 1 | 0.022596 | 24761.6364 | 1 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11024 | CALPINE 1144276-G | 48011144 | CALPINE 1144 | 23.7478 | 0.014759 | 1 | 1.8786 | 1.8786 | 2 | 0.037356 | 24759.7577 | 0.99992 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9665 | MARIPOSA 210190130 | 254452101 | MARIPOSA 2101 | 151.1499 | 0.09394 | 1 | 1.6924 | 1.6924 | 3 | 0.1313 | 24758.0654 | 0.99986 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9783 | SHEPHERD 2111688294 | 252062111 | SHEPHERD 2111 | 24.3604 | 0.01514 | 1 | 1.4425 | 1.4425 | 4 | 0.14644 | 24756.6229 | 0.9998 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10354 | MIDDLETOWN 1103CB | 43141103 | MIDDLETOWN 1103 | 85.2366 | 0.052975 | 4 | 5.2026 | 1.3006 | 5 | 0.19941 | 24751.4203 | 0.99959 | 24751.4203 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10600 | UPPER LAKE 1101CB | 42871101 | UPPER LAKE 1101 | 1791.2622 | 1.1133 | 3 | 3.7676 | 1.2559 | 6 | 1.3127 | 24747.6528 | 0.99944 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8894 | KESWICK 11011586 | 103451101 | KESWICK 1101 | 11983.5348 | 7.4478 | 39 | 48.8434 | 1.2524 | 7 | 8.7605 | 24698.8094 | 0.99746 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6776 | MIDDLETOWN 1102302610 | 43141102 | MIDDLETOWN 1102 | 7571.5921 | 4.7058 | 53 | 48.565 | 0.91632 | 8 | 13.4663 | 24650.2444 | 0.9955 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2373 | KONOCTI 1102965078 | 43311102 | KONOCTI 1102 | 10089.0761 | 6.2704 | 59 | 51.7008 | 0.87629 | 9 | 19.7367 | 24598.5436 | 0.99341 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5527 | MARIPOSA 2102241564 | 254452102 | MARIPOSA 2102 | 1146.9072 | 0.71281 | 14 | 10.8148 | 0.77248 | 10 | 20.4495 | 24587.7288 | 0.99298 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7968 | BUCKS CREEK 1101CB | 102211101 | BUCKS CREEK 1101 | 7724.4676 | 4.8008 | 13 | 9.5539 | 0.73491 | 11 | 25.2503 | 24578.1749 | 0.99259 | 24578.1749 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10918 | DEL MAR 2109378446 | 152582109 | DEL MAR 2109 | 157.9488 | 0.098166 | 3 | 2.1945 | 0.73151 | 12 | 25.3484 | 24575.9804 | 0.9925 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6966 | MIDDLETOWN 1102CB | 43141102 | MIDDLETOWN 1102 | 752.0336 | 0.46739 | 12 | 8.6977 | 0.72481 | 13 | 25.8158 | 24567.2827 | 0.99215 | 24567.2827 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3511 | MIDDLETOWN 1103830 | 43141103 | MIDDLETOWN 1103 | 44622.1036 | 27.7328 | 212 | 151.8291 | 0.71618 | 14 | 53.5487 | 24415.4536 | 0.98602 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9537 | POSO MOUNTAIN 2104CB | 253642104 | POSO MOUNTAIN 2104 | 8613.688 | 5.3534 | 38 | 26.7607 | 0.70423 | 15 | 58.9021 | 24388.6929 | 0.98494 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10827 | INDIAN FLAT 11044440 | 252691104 | INDIAN FLAT 1104 | 376.2849 | 0.23386 | 4 | 2.7463 | 0.68656 | 16 | 59.136 | 24385.9466 | 0.98483 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10242 | ELK CREEK 1101CB | 102781101 | ELK CREEK 1101 | 135.534 | 0.084235 | 1 | 0.67079 | 0.67079 | 17 | 59.2202 | 24385.2758 | 0.9848 | 24385.2758 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5791 | TIDEWATER 210614072 | 14652106 | TIDEWATER 2106 | 5897.3117 | 3.6652 | 30 | 19.5994 | 0.65331 | 18 | 62.8854 | 24365.6765 | 0.98401 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10735 | HARTLEY 1101980662 | 43211101 | HARTLEY 1101 | 366.2635 | 0.22763 | 3 | 1.9256 | 0.64187 | 19 | 63.113 | 24363.7509 | 0.98393 | 24363.7509 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10532 | VACA DIXON 1101126774 | 63591101 | VACA DIXON 1101 | 1267.3386 | 0.78766 | 11 | 6.8232 | 0.62029 | 20 | 63.9007 | 24356.9277 | 0.98366 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10277 | KIRKER 2104442850 | 14452104 | KIRKER 2104 | 9258.545 | 5.7542 | 30 | 18.4361 | 0.61454 | 21 | 69.6549 | 24338.4916 | 0.98291 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8742 | COARSEGOLD 2104CB | 254432104 | COARSEGOLD 2104 | 3906.143 | 2.4277 | 27 | 16.0848 | 0.59573 | 22 | 72.0826 | 24322.4068 | 0.98226 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8905 | MIDDLETOWN 1101118494 | 43141101 | MIDDLETOWN 1101 | 1714.9565 | 1.0659 | 12 | 6.971 | 0.58092 | 23 | 73.1484 | 24315.4357 | 0.98198 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10515 | STAFFORD 1102784704 | 43201102 | STAFFORD 1102 | 43.8835 | 0.027274 | 1 | 0.564 | 0.564 | 24 | 73.1757 | 24314.8717 | 0.98196 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10181 | PEABODY 2108113684 | 63642108 | PEABODY 2108 | 590.6521 | 0.36709 | 4 | 2.211 | 0.55276 | 25 | 73.5428 | 24312.6607 | 0.98187 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7688 | PEABODY 2106250154 | 63642106 | PEABODY 2106 | 458.5489 | 0.28499 | 4 | 2.2097 | 0.55243 | 26 | 73.8278 | 24310.451 | 0.98178 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7743 | HIGHLANDS 1102628 | 43361102 | HIGHLANDS 1102 | 22883.905 | 14.2224 | 51 | 27.9838 | 0.5487 | 27 | 88.0502 | 24282.4672 | 0.98065 | 24282.4672 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6480 | TASSAJARA 21123202 | 14662112 | TASSAJARA 2112 | 630.3021 | 0.39174 | 9 | 4.8358 | 0.53731 | 28 | 88.442 | 24277.6315 | 0.98045 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10043 | WYANDOTTE 110932586 | 102911109 | WYANDOTTE 1109 | 2158.8587 | 1.3417 | 15 | 7.9481 | 0.52987 | 29 | 89.7837 | 24269.6834 | 0.98013 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10052 | POSO MOUNTAIN 2103CB | 253642103 | POSO MOUNTAIN 2103 | 3746.9222 | 2.3287 | 10 | 5.1619 | 0.51619 | 30 | 92.1124 | 24264.5215 | 0.97992 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10924 | CALPINE 1146200-G | 48011146 | CALPINE 1146 | 13.7161 | 0.0085246 | 1 | 0.50979 | 0.50979 | 31 | 92.121 | 24264.0117 | 0.9799 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11090 | CALPINE 1146394G | 48011146 | CALPINE 1146 | 18.1683 | 0.011292 | 1 | 0.50979 | 0.50979 | 32 | 92.1323 | 24263.5019 | 0.97988 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4828 | CRESTA 1101546650 | 102251101 | CRESTA 1101 | 1443.177 | 0.89694 | 6 | 3.0174 | 0.50291 | 33 | 93.0292 | 24260.4844 | 0.97976 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9923 | CLOVERDALE 110247214 | 42821102 | CLOVERDALE 1102 | 43.972 | 0.027329 | 1 | 0.48427 | 0.48427 | 34 | 93.0565 | 24260.0002 | 0.97974 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8034 | MARIPOSA 2102CB | 254452102 | MARIPOSA 2102 | 8453.5074 | 5.2539 | 31 | 14.6212 | 0.47165 | 35 | 98.3104 | 24245.379 | 0.97915 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7873 | MARIPOSA 210197142 | 254452101 | MARIPOSA 2101 | 7406.0615 | 4.6029 | 40 | 18.8487 | 0.47122 | 36 | 102.9133 | 24226.5303 | 0.97839 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4526 | VACA DIXON 110540092 | 63591105 | VACA DIXON 1105 | 37272.9556 | 23.1653 | 464 | 217.022 | 0.46772 | 37 | 126.0786 | 24009.5083 | 0.96963 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2215 | MIDDLETOWN 1101481876 | 43141101 | MIDDLETOWN 1101 | 1373.1162 | 0.8534 | 14 | 6.5476 | 0.46769 | 38 | 126.932 | 24002.9607 | 0.96936 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9655 | VOLTA 110149742 | 102541101 | VOLTA 1101 | 5593.8568 | 3.4766 | 28 | 13.0013 | 0.46433 | 39 | 130.4086 | 23989.9594 | 0.96884 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10699 | SUNOL 110148180 | 14241101 | SUNOL 1101 | 21.1502 | 0.013145 | 2 | 0.92206 | 0.46103 | 40 | 130.4218 | 23989.0374 | 0.9688 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7414 | PUTAH CREEK 110246012 | 63681102 | PUTAH CREEK 1102 | 1025.1447 | 0.63713 | 38 | 17.3115 | 0.45557 | 41 | 131.0589 | 23971.7259 | 0.9681 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4076 | VACAVILLE 11046542 | 63601104 | VACAVILLE 1104 | 23588.1989 | 14.6602 | 140 | 62.4985 | 0.44642 | 42 | 145.719 | 23909.2273 | 0.96558 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7056 | POTTER VALLEY P H 110564118 | 42281105 | POTTER VALLEY P H 1105 | 2646.9433 | 1.6451 | 101 | 44.7046 | 0.44262 | 43 | 147.3641 | 23864.5228 | 0.96377 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10934 | POINT MORETTI 1101CB | 82931101 | POINT MORETTI 1101 | 20.574 | 0.012787 | 1 | 0.44218 | 0.44218 | 44 | 147.3769 | 23864.0806 | 0.96375 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5032 | MOUNTAIN QUARRIES 21016953 | 152282101 | MOUNTAIN QUARRIES 2101 | 9187.973 | 5.7104 | 58 | 25.2473 | 0.4353 | 45 | 153.0873 | 23838.8333 | 0.96273 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9729 | BRENTWOOD 210596324 | 14592105 | BRENTWOOD 2105 | 775.7684 | 0.48214 | 6 | 2.5902 | 0.4317 | 46 | 153.5694 | 23836.2431 | 0.96263 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6662 | NORTH DUBLIN 2101CB | 14052101 | NORTH DUBLIN 2101 | 2836.5864 | 1.7629 | 23 | 9.8576 | 0.42859 | 47 | 155.3324 | 23826.3855 | 0.96223 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1690 | DESCHUTES 11049718 | 103351104 | DESCHUTES 1104 | 29935.2858 | 18.6049 | 357 | 151.8163 | 0.42526 | 48 | 173.9373 | 23674.5692 | 0.9561 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
193 | OREGON TRAIL 110335002 | 103521103 | OREGON TRAIL 1103 | 91942.988 | 57.1429 | 641 | 270.4028 | 0.42185 | 49 | 231.0802 | 23404.1664 | 0.94518 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7274 | MARIPOSA 2102440236 | 254452102 | MARIPOSA 2102 | 6874.8043 | 4.2727 | 38 | 15.979 | 0.4205 | 50 | 235.3529 | 23388.1874 | 0.94453 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10024 | CLEAR LAKE 1101881362 | 42141101 | CLEAR LAKE 1101 | 480.0321 | 0.29834 | 10 | 4.1959 | 0.41959 | 51 | 235.6513 | 23383.9915 | 0.94436 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7141 | WILDWOOD 11011454 | 103611101 | WILDWOOD 1101 | 12602.1173 | 7.8323 | 31 | 12.9837 | 0.41883 | 52 | 243.4835 | 23371.0078 | 0.94384 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7033 | VACA DIXON 1105965390 | 63591105 | VACA DIXON 1105 | 1209.1092 | 0.75147 | 21 | 8.6971 | 0.41415 | 53 | 244.235 | 23362.3107 | 0.94349 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9936 | OLETA 1101754718 | 163541101 | OLETA 1101 | 4640.5633 | 2.8841 | 29 | 11.8066 | 0.40712 | 54 | 247.1191 | 23350.5042 | 0.94301 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10113 | CALISTOGA 1101CB | 42711101 | CALISTOGA 1101 | 221.6704 | 0.13777 | 9 | 3.6505 | 0.40561 | 55 | 247.2569 | 23346.8537 | 0.94286 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9252 | STANISLAUS 1701CB | 162821701 | STANISLAUS 1701 | 11032.7196 | 6.8569 | 54 | 21.7909 | 0.40353 | 56 | 254.1138 | 23325.0628 | 0.94198 | 23325.0628 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9014 | MARIPOSA 2101CB | 254452101 | MARIPOSA 2101 | 4029.4321 | 2.5043 | 34 | 13.5444 | 0.39837 | 57 | 256.6181 | 23311.5183 | 0.94144 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4909 | HARTLEY 1101698 | 43211101 | HARTLEY 1101 | 11071.0466 | 6.8807 | 97 | 38.5312 | 0.39723 | 58 | 263.4988 | 23272.9871 | 0.93988 | 23272.9871 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9239 | BANGOR 1101979830 | 103191101 | BANGOR 1101 | 680.7511 | 0.42309 | 7 | 2.7804 | 0.3972 | 59 | 263.9219 | 23270.2067 | 0.93977 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4242 | POTTER VALLEY P H 110495878 | 42281104 | POTTER VALLEY P H 1104 | 9856.7705 | 6.126 | 191 | 75.7306 | 0.3965 | 60 | 270.0479 | 23194.4761 | 0.93671 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2058 | COARSEGOLD 21045310 | 254432104 | COARSEGOLD 2104 | 45195.5088 | 28.0892 | 299 | 117.8076 | 0.39401 | 61 | 298.1371 | 23076.6685 | 0.93195 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8298 | STAFFORD 1102361952 | 43201102 | STAFFORD 1102 | 2196.587 | 1.3652 | 9 | 3.536 | 0.39288 | 62 | 299.5023 | 23073.1326 | 0.93181 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1488 | AUBERRY 1101CB | 254151101 | AUBERRY 1101 | 29229.2172 | 18.1661 | 204 | 79.9801 | 0.39206 | 63 | 317.6684 | 22993.1524 | 0.92858 | 22993.1524 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3596 | VACAVILLE 11088762 | 63601108 | VACAVILLE 1108 | 22259.6162 | 13.8344 | 147 | 57.5327 | 0.39138 | 64 | 331.5028 | 22935.6197 | 0.92626 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6014 | OREGON TRAIL 11041634 | 103521104 | OREGON TRAIL 1104 | 29110.7694 | 18.0925 | 192 | 75.0607 | 0.39094 | 65 | 349.5953 | 22860.5591 | 0.92322 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6392 | COARSEGOLD 210410335 | 254432104 | COARSEGOLD 2104 | 9369.0411 | 5.8229 | 69 | 26.9663 | 0.39082 | 66 | 355.4182 | 22833.5927 | 0.92214 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7352 | JAMESON 1102865502 | 63801102 | JAMESON 1102 | 644.9532 | 0.40084 | 27 | 10.5185 | 0.38957 | 67 | 355.819 | 22823.0743 | 0.92171 | 22823.0743 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3943 | MOUNTAIN QUARRIES 2101CB | 152282101 | MOUNTAIN QUARRIES 2101 | 40215.5467 | 24.9941 | 262 | 101.3032 | 0.38665 | 68 | 380.8131 | 22721.7711 | 0.91762 | 22721.7711 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2633 | PASO ROBLES 1103N54 | 182611103 | PASO ROBLES 1103 | 32201.1783 | 20.0132 | 221 | 85.2354 | 0.38568 | 69 | 400.8263 | 22636.5357 | 0.91418 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6808 | PHILO 110137222 | 42601101 | PHILO 1101 | 40893.1758 | 25.4153 | 152 | 58.3523 | 0.3839 | 70 | 426.2416 | 22578.1834 | 0.91182 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8006 | RISING RIVER 11011532 | 103551101 | RISING RIVER 1101 | 6133.1893 | 3.8118 | 27 | 10.2807 | 0.38077 | 71 | 430.0534 | 22567.9027 | 0.91141 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10120 | DEL MAR 210975802 | 152582109 | DEL MAR 2109 | 576.1553 | 0.35808 | 6 | 2.2741 | 0.37901 | 72 | 430.4114 | 22565.6287 | 0.91131 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8754 | NOTRE DAME 11042408 | 102041104 | NOTRE DAME 1104 | 18541.2413 | 11.5235 | 76 | 28.7393 | 0.37815 | 73 | 441.9349 | 22536.8893 | 0.91015 | 22536.8893 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5603 | HIGHLANDS 1102623120 | 43361102 | HIGHLANDS 1102 | 10535.1094 | 6.5476 | 67 | 25.2855 | 0.3774 | 74 | 448.4825 | 22511.6038 | 0.90913 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2079 | POTTER VALLEY P H 11051904 | 42281105 | POTTER VALLEY P H 1105 | 51242.8521 | 31.8476 | 332 | 125.1141 | 0.37685 | 75 | 480.3302 | 22386.4897 | 0.90408 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8836 | VOLTA 1101CB | 102541101 | VOLTA 1101 | 14817.1823 | 9.2089 | 80 | 30.036 | 0.37545 | 76 | 489.5391 | 22356.4537 | 0.90287 | 22356.4537 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10966 | HICKS 2101984788 | 83432101 | HICKS 2101 | 5.0644 | 0.0031475 | 1 | 0.37348 | 0.37348 | 77 | 489.5422 | 22356.0802 | 0.90285 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6191 | COARSEGOLD 2104570682 | 254432104 | COARSEGOLD 2104 | 3264.3372 | 2.0288 | 26 | 9.6995 | 0.37306 | 78 | 491.571 | 22346.3807 | 0.90246 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8841 | NORTH DUBLIN 210311101 | 14052103 | NORTH DUBLIN 2103 | 5931.2678 | 3.6863 | 37 | 13.6135 | 0.36793 | 79 | 495.2573 | 22332.7673 | 0.90191 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7776 | NORTH DUBLIN 21039473 | 14052103 | NORTH DUBLIN 2103 | 3890.479 | 2.4179 | 27 | 9.8678 | 0.36547 | 80 | 497.6753 | 22322.8995 | 0.90151 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9266 | WILLOW PASS 2107445650 | 13912107 | WILLOW PASS 2107 | 1066.4109 | 0.66278 | 5 | 1.8239 | 0.36477 | 81 | 498.3381 | 22321.0756 | 0.90144 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2272 | MIDDLETOWN 1102414 | 43141102 | MIDDLETOWN 1102 | 9544.4247 | 5.9319 | 114 | 41.5353 | 0.36434 | 82 | 504.27 | 22279.5404 | 0.89976 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3625 | CAYETANO 2109884904 | 14422109 | CAYETANO 2109 | 18723.6816 | 11.6368 | 77 | 27.9711 | 0.36326 | 83 | 515.9068 | 22251.5693 | 0.89863 | 22251.5693 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10903 | PEABODY 2106592742 | 63642106 | PEABODY 2106 | 546.7453 | 0.3398 | 5 | 1.8113 | 0.36227 | 84 | 516.2466 | 22249.7579 | 0.89856 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5260 | VOLTA 11011568 | 102541101 | VOLTA 1101 | 37176.4968 | 23.1053 | 136 | 49.2203 | 0.36191 | 85 | 539.352 | 22200.5377 | 0.89657 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4693 | MIDDLETOWN 1101CB | 43141101 | MIDDLETOWN 1101 | 7612.1604 | 4.731 | 146 | 52.8144 | 0.36174 | 86 | 544.083 | 22147.7233 | 0.89444 | 22147.7233 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10547 | PASO ROBLES 1103N02 | 182611103 | PASO ROBLES 1103 | 70.934 | 0.044086 | 1 | 0.36094 | 0.36094 | 87 | 544.127 | 22147.3624 | 0.89442 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2088 | COARSEGOLD 21035020 | 254432103 | COARSEGOLD 2103 | 26064.8634 | 16.1994 | 159 | 57.2543 | 0.36009 | 88 | 560.3265 | 22090.108 | 0.89211 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7913 | JESSUP 11023105 | 103441102 | JESSUP 1102 | 9659.0441 | 6.0031 | 65 | 23.3856 | 0.35978 | 89 | 566.3296 | 22066.7225 | 0.89117 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10257 | CAYETANO 2111389190 | 14422111 | CAYETANO 2111 | 3542.8058 | 2.2019 | 18 | 6.4703 | 0.35946 | 90 | 568.5315 | 22060.2522 | 0.8909 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10351 | VACAVILLE 1109799940 | 63601109 | VACAVILLE 1109 | 954.7701 | 0.59339 | 9 | 3.2259 | 0.35844 | 91 | 569.1249 | 22057.0263 | 0.89077 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
745 | PUTAH CREEK 110267858 | 63681102 | PUTAH CREEK 1102 | 18377.3415 | 11.4216 | 107 | 38.201 | 0.35702 | 92 | 580.5464 | 22018.8252 | 0.88923 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10611 | PEABODY 2113945670 | 63642113 | PEABODY 2113 | 334.4297 | 0.20785 | 3 | 1.0661 | 0.35536 | 93 | 580.7543 | 22017.7592 | 0.88919 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
835 | ZACA 1102Y54 | 182681102 | ZACA 1102 | 54847.9366 | 34.0882 | 296 | 104.1359 | 0.35181 | 94 | 614.8425 | 21913.6233 | 0.88498 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9806 | OLETA 1101CB | 163541101 | OLETA 1101 | 136.2242 | 0.084664 | 2 | 0.70277 | 0.35138 | 95 | 614.9272 | 21912.9205 | 0.88495 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7864 | SISQUOC 1103867486 | 182811103 | SISQUOC 1103 | 3405.4305 | 2.1165 | 20 | 7.0121 | 0.35061 | 96 | 617.0437 | 21905.9084 | 0.88467 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10173 | CALPINE 1146400 | 48011146 | CALPINE 1146 | 5057.3021 | 3.1431 | 8 | 2.7917 | 0.34896 | 97 | 620.1868 | 21903.1167 | 0.88456 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
615 | KERCKHOFF 1101CB | 252561101 | KERCKHOFF 1101 | 27398.7529 | 17.0284 | 154 | 53.5915 | 0.348 | 98 | 637.2152 | 21849.5252 | 0.88239 | 21849.5252 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1695 | DESCHUTES 110449024 | 103351104 | DESCHUTES 1104 | 26707.9675 | 16.5991 | 209 | 72.7038 | 0.34786 | 99 | 653.8143 | 21776.8214 | 0.87946 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3728 | DESCHUTES 11041370 | 103351104 | DESCHUTES 1104 | 21861.3958 | 13.5869 | 272 | 94.0068 | 0.34561 | 100 | 667.4013 | 21682.8146 | 0.87566 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10316 | CORNING 110135974 | 103331101 | CORNING 1101 | 398.8739 | 0.2479 | 11 | 3.7844 | 0.34404 | 101 | 667.6492 | 21679.0302 | 0.87551 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10256 | VACAVILLE 1104874798 | 63601104 | VACAVILLE 1104 | 662.24 | 0.41158 | 3 | 1.0087 | 0.33623 | 102 | 668.0608 | 21678.0215 | 0.87547 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6277 | WILLITS 1103964 | 42661103 | WILLITS 1103 | 4999.6692 | 3.1073 | 41 | 13.717 | 0.33456 | 103 | 671.1681 | 21664.3045 | 0.87491 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6777 | BELL 11085703 | 152701108 | BELL 1108 | 8525.0586 | 5.2984 | 96 | 31.9947 | 0.33328 | 104 | 676.4664 | 21632.3099 | 0.87362 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10040 | PANORAMA 11021632 | 103461102 | PANORAMA 1102 | 13751.6318 | 8.5467 | 19 | 6.3164 | 0.33244 | 105 | 685.0131 | 21625.9934 | 0.87337 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9960 | WILLITS 1103CB | 42661103 | WILLITS 1103 | 4804 | 2.9857 | 44 | 14.4105 | 0.32751 | 106 | 687.9988 | 21611.583 | 0.87278 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6501 | SAN MIGUEL 1104895760 | 182661104 | SAN MIGUEL 1104 | 14756.3663 | 9.1711 | 96 | 31.3373 | 0.32643 | 107 | 697.17 | 21580.2456 | 0.87152 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4461 | SANTA YNEZ 1104Y04 | 182721104 | SANTA YNEZ 1104 | 25194.6309 | 15.6586 | 238 | 77.261 | 0.32463 | 108 | 712.8286 | 21502.9846 | 0.8684 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10609 | PEABODY 2106CB | 63642106 | PEABODY 2106 | 525.8096 | 0.32679 | 9 | 2.9197 | 0.32442 | 109 | 713.1553 | 21500.0649 | 0.86828 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3147 | HOPLAND 1101768 | 42251101 | HOPLAND 1101 | 27234.0747 | 16.9261 | 115 | 37.2953 | 0.32431 | 110 | 730.0814 | 21462.7695 | 0.86678 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6991 | COVELO 1101478952 | 43061101 | COVELO 1101 | 1143.6662 | 0.71079 | 39 | 12.6234 | 0.32368 | 111 | 730.7922 | 21450.1461 | 0.86627 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9010 | STAFFORD 11021202 | 43201102 | STAFFORD 1102 | 12713.8882 | 7.9017 | 41 | 13.2544 | 0.32328 | 112 | 738.694 | 21436.8917 | 0.86573 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5081 | RED BLUFF 11041566 | 103541104 | RED BLUFF 1104 | 19451.0946 | 12.0889 | 94 | 30.3149 | 0.3225 | 113 | 750.7829 | 21406.5768 | 0.86451 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9508 | ANDERSON 1101426745 | 103261101 | ANDERSON 1101 | 328.8561 | 0.20439 | 3 | 0.96673 | 0.32224 | 114 | 750.9873 | 21405.6101 | 0.86447 | 21405.6101 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10637 | SYCAMORE CREEK 1111153260 | 102971111 | SYCAMORE CREEK 1111 | 424.4592 | 0.2638 | 2 | 0.64373 | 0.32186 | 115 | 751.2511 | 21404.9664 | 0.86444 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3800 | DESCHUTES 11049726 | 103351104 | DESCHUTES 1104 | 25257.4681 | 15.6976 | 197 | 63.2977 | 0.32131 | 116 | 766.9487 | 21341.6686 | 0.86188 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4142 | GIRVAN 1101323094 | 103401101 | GIRVAN 1101 | 58176.4815 | 36.1569 | 208 | 66.6373 | 0.32037 | 117 | 803.1056 | 21275.0313 | 0.85919 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4869 | BELL 11082202 | 152701108 | BELL 1108 | 52339.4363 | 32.5292 | 363 | 116.2183 | 0.32016 | 118 | 835.6348 | 21158.813 | 0.8545 | 21158.813 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9492 | OLETA 1101296804 | 163541101 | OLETA 1101 | 5287.5044 | 3.2862 | 12 | 3.8345 | 0.31954 | 119 | 838.921 | 21154.9785 | 0.85434 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10541 | CLARKSVILLE 2105CB | 153612105 | CLARKSVILLE 2105 | 1293.943 | 0.80419 | 9 | 2.8642 | 0.31824 | 120 | 839.7252 | 21152.1143 | 0.85423 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5372 | TEMPLETON 2113A20 | 183052113 | TEMPLETON 2113 | 11999.0835 | 7.4575 | 92 | 29.2466 | 0.3179 | 121 | 847.1827 | 21122.8677 | 0.85305 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8293 | VACAVILLE 110838316 | 63601108 | VACAVILLE 1108 | 25616.7426 | 15.9209 | 232 | 73.4796 | 0.31672 | 122 | 863.1036 | 21049.3881 | 0.85008 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
907 | COTTONWOOD 1102544790 | 102931102 | COTTONWOOD 1102 | 26342.4042 | 16.3719 | 185 | 57.8548 | 0.31273 | 123 | 879.4755 | 20991.5333 | 0.84774 | 20991.5333 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6176 | COARSEGOLD 21045525 | 254432104 | COARSEGOLD 2104 | 21152.7165 | 13.1465 | 175 | 54.5497 | 0.31171 | 124 | 892.622 | 20936.9836 | 0.84554 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3989 | MIDDLETOWN 1102878 | 43141102 | MIDDLETOWN 1102 | 5430.6654 | 3.3752 | 49 | 15.2435 | 0.31109 | 125 | 895.9972 | 20921.7401 | 0.84493 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2201 | RACETRACK 1704CB | 163761704 | RACETRACK 1704 | 36834.5436 | 22.8928 | 193 | 60.0095 | 0.31093 | 126 | 918.89 | 20861.7305 | 0.8425 | 20861.7305 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4707 | HIGHLANDS 1103828 | 43361103 | HIGHLANDS 1103 | 13828.9706 | 8.5948 | 112 | 34.8164 | 0.31086 | 127 | 927.4847 | 20826.9141 | 0.8411 | 20826.9141 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8759 | KERCKHOFF 1101R308 | 252561101 | KERCKHOFF 1101 | 6217.3701 | 3.8641 | 22 | 6.7983 | 0.30901 | 128 | 931.3489 | 20820.1158 | 0.84082 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7918 | FORESTHILL 1102CB | 152181102 | FORESTHILL 1102 | 2646.4634 | 1.6448 | 13 | 4.0135 | 0.30873 | 129 | 932.9936 | 20816.1023 | 0.84066 | 20816.1023 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9076 | SYCAMORE CREEK 1111976428 | 102971111 | SYCAMORE CREEK 1111 | 14081.5812 | 8.7518 | 82 | 25.2165 | 0.30752 | 130 | 941.7454 | 20790.8858 | 0.83964 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6711 | PUTAH CREEK 110396792 | 63681103 | PUTAH CREEK 1103 | 6394.0351 | 3.9739 | 30 | 9.2067 | 0.30689 | 131 | 945.7193 | 20781.6791 | 0.83927 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9779 | COARSEGOLD 21046210 | 254432104 | COARSEGOLD 2104 | 17177.2503 | 10.6757 | 49 | 14.9278 | 0.30465 | 132 | 956.3951 | 20766.7513 | 0.83867 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7407 | TEMPLETON 2113A12 | 183052113 | TEMPLETON 2113 | 64854.5144 | 40.3073 | 180 | 54.7453 | 0.30414 | 133 | 996.7024 | 20712.006 | 0.83646 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6929 | CLARKSVILLE 2104CB | 153612104 | CLARKSVILLE 2104 | 14163.76 | 8.8028 | 107 | 32.5187 | 0.30391 | 134 | 1005.5052 | 20679.4873 | 0.83514 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8076 | NORTH DUBLIN 2103CB | 14052103 | NORTH DUBLIN 2103 | 22339.3117 | 13.884 | 147 | 44.6134 | 0.30349 | 135 | 1019.3892 | 20634.8739 | 0.83334 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9798 | BALCH NO 1 1101CB | 252501101 | BALCH NO 1 1101 | 16978.5039 | 10.5522 | 33 | 9.9805 | 0.30244 | 136 | 1029.9414 | 20624.8934 | 0.83294 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8821 | SANTA YNEZ 1104CB | 182721104 | SANTA YNEZ 1104 | 56.5182 | 0.035126 | 105 | 31.6947 | 0.30185 | 137 | 1029.9765 | 20593.1987 | 0.83166 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
12 | PASO ROBLES 1103N50 | 182611103 | PASO ROBLES 1103 | 3586.1974 | 2.2288 | 24 | 7.2094 | 0.30039 | 138 | 1032.2054 | 20585.9893 | 0.83137 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
461 | KONOCTI 1102354890 | 43311102 | KONOCTI 1102 | 15016.4864 | 9.3328 | 131 | 38.9233 | 0.29712 | 139 | 1041.5382 | 20547.0661 | 0.82979 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4081 | OREGON TRAIL 11021382 | 103521102 | OREGON TRAIL 1102 | 8797.2782 | 5.4675 | 67 | 19.7671 | 0.29503 | 140 | 1047.0057 | 20527.299 | 0.829 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
207 | AUBERRY 1102CB | 254151102 | AUBERRY 1102 | 55860.8325 | 34.7177 | 368 | 107.3565 | 0.29173 | 141 | 1081.7235 | 20419.9425 | 0.82466 | 20419.9425 | #N/A | #N/A | #N/A | #N/A | #VALUE!
929 | CORRAL 1101CB | 162991101 | CORRAL 1101 | 42311.3503 | 26.2967 | 280 | 81.3506 | 0.29054 | 142 | 1108.0201 | 20338.5918 | 0.82138 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3287 | ANDERSON 11031600 | 103261103 | ANDERSON 1103 | 7231.4682 | 4.4944 | 106 | 30.6232 | 0.2889 | 143 | 1112.5145 | 20307.9686 | 0.82014 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1107 | COARSEGOLD 210410030 | 254432104 | COARSEGOLD 2104 | 54599.1868 | 33.9336 | 227 | 65.0478 | 0.28655 | 144 | 1146.4481 | 20242.9208 | 0.81751 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9519 | ARBUCKLE 1104669720 | 62081104 | ARBUCKLE 1104 | 3612.2461 | 2.245 | 22 | 6.3042 | 0.28655 | 145 | 1148.6932 | 20236.6166 | 0.81726 | 20236.6166 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3809 | WISE 11022230 | 152271102 | WISE 1102 | 38210.8819 | 23.7482 | 278 | 79.0585 | 0.28438 | 146 | 1172.4414 | 20157.5581 | 0.81406 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2464 | SHEPHERD 2111327814 | 252062111 | SHEPHERD 2111 | 18621.0587 | 11.5731 | 119 | 33.8288 | 0.28428 | 147 | 1184.0144 | 20123.7293 | 0.8127 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3815 | PANORAMA 1102280170 | 103461102 | PANORAMA 1102 | 20943.3132 | 13.0164 | 102 | 28.9943 | 0.28426 | 148 | 1197.0308 | 20094.735 | 0.81153 | 20094.735 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10166 | TEMPLETON 21132949 | 183052113 | TEMPLETON 2113 | 766.5719 | 0.47643 | 6 | 1.7049 | 0.28416 | 149 | 1197.5072 | 20093.03 | 0.81146 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6611 | DESCHUTES 1101CB | 103351101 | DESCHUTES 1101 | 8017.5323 | 4.9829 | 118 | 33.5157 | 0.28403 | 150 | 1202.4902 | 20059.5143 | 0.8101 | 20059.5143 | #N/A | #N/A | #N/A | #N/A | #VALUE!
195 | COARSEGOLD 21045300 | 254432104 | COARSEGOLD 2104 | 89782.9365 | 55.8005 | 507 | 143.8456 | 0.28372 | 151 | 1258.2906 | 19915.6687 | 0.8043 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5871 | FLINT 1101750 | 152531101 | FLINT 1101 | 7342.9025 | 4.5636 | 93 | 26.3354 | 0.28318 | 152 | 1262.8543 | 19889.3333 | 0.80323 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
952 | SANTA YNEZ 1104Y66 | 182721104 | SANTA YNEZ 1104 | 27268.3855 | 16.9474 | 138 | 39.0253 | 0.28279 | 153 | 1279.8017 | 19850.3081 | 0.80166 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1401 | SAN JOAQUIN #2 110310320 | 252521103 | SAN JOAQUIN #2 1103 | 18962.0898 | 11.785 | 133 | 37.4782 | 0.28179 | 154 | 1291.5867 | 19812.8299 | 0.80014 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10123 | FULTON 110258990 | 42561102 | FULTON 1102 | 427.9744 | 0.26599 | 6 | 1.6815 | 0.28025 | 155 | 1291.8527 | 19811.1484 | 0.80007 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3591 | SANTA YNEZ 1101277014 | 182721101 | SANTA YNEZ 1101 | 8850.8283 | 5.5008 | 149 | 41.7232 | 0.28002 | 156 | 1297.3535 | 19769.4252 | 0.79839 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2737 | VOLTA 110153118 | 102541101 | VOLTA 1101 | 15490.2629 | 9.6273 | 47 | 13.1375 | 0.27952 | 157 | 1306.9808 | 19756.2877 | 0.79786 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9393 | PUTAH CREEK 1103654021 | 63681103 | PUTAH CREEK 1103 | 329.1954 | 0.2046 | 12 | 3.3454 | 0.27878 | 158 | 1307.1854 | 19752.9423 | 0.79772 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5717 | SHINGLE SPRINGS 210935598 | 153652109 | SHINGLE SPRINGS 2109 | 17452.8092 | 10.847 | 122 | 33.9836 | 0.27855 | 159 | 1318.0323 | 19718.9587 | 0.79635 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1630 | OREGON TRAIL 11041574 | 103521104 | OREGON TRAIL 1104 | 27209.5234 | 16.9108 | 221 | 61.5533 | 0.27852 | 160 | 1334.9432 | 19657.4053 | 0.79387 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2168 | HOPLAND 11014626 | 42251101 | HOPLAND 1101 | 43527.4256 | 27.0525 | 238 | 66.2609 | 0.27841 | 161 | 1361.9956 | 19591.1444 | 0.79119 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10275 | SAN MIGUEL 1105873457 | 182661105 | SAN MIGUEL 1105 | 2440.6531 | 1.5169 | 18 | 4.9901 | 0.27723 | 162 | 1363.5125 | 19586.1543 | 0.79099 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5141 | AUBERRY 1101R2578 | 254151101 | AUBERRY 1101 | 74560.0099 | 46.3393 | 506 | 140.2335 | 0.27714 | 163 | 1409.8519 | 19445.9209 | 0.78532 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
710 | COARSEGOLD 2103CB | 254432103 | COARSEGOLD 2103 | 61825.449 | 38.4248 | 420 | 116.2539 | 0.27679 | 164 | 1448.2766 | 19329.667 | 0.78063 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9397 | BEAR VALLEY 21059570 | 252192105 | BEAR VALLEY 2105 | 12951.7997 | 8.0496 | 59 | 16.3249 | 0.27669 | 165 | 1456.3262 | 19313.3421 | 0.77997 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4772 | COARSEGOLD 2102CB | 254432102 | COARSEGOLD 2102 | 22596.9807 | 14.0441 | 79 | 21.851 | 0.2766 | 166 | 1470.3703 | 19291.4911 | 0.77909 | 19291.4911 | #N/A | #N/A | #N/A | #N/A | #VALUE!
11028 | NARROWS PH 1151CB | 153131151 | NARROWS PH 1151 | 286.9891 | 0.17836 | 2 | 0.55227 | 0.27613 | 167 | 1470.5487 | 19290.9388 | 0.77907 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5439 | KONOCTI 110264664 | 43311102 | KONOCTI 1102 | 44670.3665 | 27.7628 | 263 | 72.501 | 0.27567 | 168 | 1498.3115 | 19218.4378 | 0.77614 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
307 | MOUNTAIN QUARRIES 21011350 | 152282101 | MOUNTAIN QUARRIES 2101 | 34999.9271 | 21.7526 | 212 | 58.3793 | 0.27537 | 169 | 1520.0641 | 19160.0586 | 0.77378 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8396 | NORTH DUBLIN 2101MR765 | 14052101 | NORTH DUBLIN 2101 | 3330.9197 | 2.0702 | 15 | 4.104 | 0.2736 | 170 | 1522.1343 | 19155.9545 | 0.77361 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6379 | PUTAH CREEK 11028352 | 63681102 | PUTAH CREEK 1102 | 10298.4219 | 6.4005 | 133 | 36.3202 | 0.27308 | 171 | 1528.5348 | 19119.6343 | 0.77215 | 19119.6343 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7979 | KONOCTI 1102716 | 43311102 | KONOCTI 1102 | 24685.2253 | 15.342 | 109 | 29.7514 | 0.27295 | 172 | 1543.8768 | 19089.8829 | 0.77095 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1249 | PENRYN 11032198 | 152561103 | PENRYN 1103 | 32552.0609 | 20.2312 | 248 | 67.6807 | 0.27291 | 173 | 1564.108 | 19022.2022 | 0.76821 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10021 | OLETA 1101400470 | 163541101 | OLETA 1101 | 334.0108 | 0.20759 | 3 | 0.81862 | 0.27287 | 174 | 1564.3156 | 19021.3836 | 0.76818 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3674 | AUBERRY 1102R309 | 254151102 | AUBERRY 1102 | 13825.8859 | 8.5928 | 92 | 25.1032 | 0.27286 | 175 | 1572.9084 | 18996.2804 | 0.76717 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1420 | MIDDLETOWN 1102998 | 43141102 | MIDDLETOWN 1102 | 23900.855 | 14.8545 | 205 | 55.6044 | 0.27124 | 176 | 1587.7629 | 18940.676 | 0.76492 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6398 | CAYETANO 2109MR572 | 14422109 | CAYETANO 2109 | 13342.8208 | 8.2926 | 80 | 21.6967 | 0.27121 | 177 | 1596.0555 | 18918.9793 | 0.76404 | 18918.9793 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6361 | APPLE HILL 21026552 | 153662102 | APPLE HILL 2102 | 20088.9562 | 12.4854 | 139 | 37.6964 | 0.2712 | 178 | 1608.5409 | 18881.2829 | 0.76252 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5677 | BANGOR 110180670 | 103191101 | BANGOR 1101 | 23201.6685 | 14.4199 | 158 | 42.753 | 0.27059 | 179 | 1622.9608 | 18838.5299 | 0.7608 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7666 | JAMESON 1103118944 | 63801103 | JAMESON 1103 | 3772.9974 | 2.3449 | 41 | 11.0862 | 0.27039 | 180 | 1625.3058 | 18827.4438 | 0.76035 | 18827.4438 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5313 | HIGHLANDS 1103482 | 43361103 | HIGHLANDS 1103 | 39433.4736 | 24.5081 | 188 | 50.7128 | 0.26975 | 181 | 1649.8138 | 18776.7309 | 0.7583 | 18776.7309 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5299 | HIGGINS 1109CB | 152691109 | HIGGINS 1109 | 36440.0989 | 22.6477 | 254 | 68.0313 | 0.26784 | 182 | 1672.4615 | 18708.6996 | 0.75555 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7848 | OAKHURST 1101636114 | 254421101 | OAKHURST 1101 | 32974.1643 | 20.4936 | 153 | 40.8546 | 0.26702 | 183 | 1692.9551 | 18667.8449 | 0.7539 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10324 | SANTA YNEZ 1104564710 | 182721104 | SANTA YNEZ 1104 | 273.7323 | 0.17013 | 7 | 1.8637 | 0.26624 | 184 | 1693.1252 | 18665.9812 | 0.75383 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10018 | LINCOLN 1104275986 | 153701104 | LINCOLN 1104 | 934.5883 | 0.58085 | 5 | 1.3263 | 0.26526 | 185 | 1693.7061 | 18664.6549 | 0.75377 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5709 | HIGGINS 110950072 | 152691109 | HIGGINS 1109 | 68212.3656 | 42.3943 | 424 | 112.4633 | 0.26524 | 186 | 1736.1003 | 18552.1917 | 0.74923 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3710 | MARIPOSA 210110070 | 254452101 | MARIPOSA 2101 | 42054.457 | 26.137 | 249 | 65.835 | 0.2644 | 187 | 1762.2373 | 18486.3566 | 0.74657 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3891 | MARIPOSA 210210880 | 254452102 | MARIPOSA 2102 | 63861.6467 | 39.6903 | 362 | 95.458 | 0.2637 | 188 | 1801.9276 | 18390.8986 | 0.74272 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1822 | BELL 110750172 | 152701107 | BELL 1107 | 28142.3136 | 17.4906 | 210 | 55.3341 | 0.2635 | 189 | 1819.4182 | 18335.5645 | 0.74048 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7084 | VACAVILLE 111113652 | 63601111 | VACAVILLE 1111 | 6914.8485 | 4.2976 | 58 | 15.2768 | 0.26339 | 190 | 1823.7158 | 18320.2877 | 0.73987 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3429 | CLOVERDALE 1101399855 | 42821101 | CLOVERDALE 1101 | 4409.9199 | 2.7408 | 19 | 5.0028 | 0.26331 | 191 | 1826.4566 | 18315.2848 | 0.73966 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9762 | HARTLEY 11014710 | 43211101 | HARTLEY 1101 | 2414.0517 | 1.5003 | 18 | 4.7355 | 0.26308 | 192 | 1827.9569 | 18310.5493 | 0.73947 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2103 | DOBBINS 11011808 | 153741101 | DOBBINS 1101 | 25003.3757 | 15.5397 | 171 | 44.9426 | 0.26282 | 193 | 1843.4966 | 18265.6067 | 0.73766 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3817 | DESCHUTES 11011380 | 103351101 | DESCHUTES 1101 | 28672.6173 | 17.8201 | 204 | 53.462 | 0.26207 | 194 | 1861.3167 | 18212.1447 | 0.7355 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1392 | SAND CREEK 110345190 | 254601103 | SAND CREEK 1103 | 60483.5997 | 37.5908 | 416 | 108.5552 | 0.26095 | 195 | 1898.9075 | 18103.5895 | 0.73111 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4741 | BRENTWOOD 2105B504R | 14592105 | BRENTWOOD 2105 | 14074.6887 | 8.7475 | 97 | 25.289 | 0.26071 | 196 | 1907.655 | 18078.3005 | 0.73009 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7636 | VACA DIXON 110118292 | 63591101 | VACA DIXON 1101 | 73.0344 | 0.045391 | 73 | 18.9907 | 0.26015 | 197 | 1907.7004 | 18059.3098 | 0.72933 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4859 | OREGON TRAIL 1102CB | 103521102 | OREGON TRAIL 1102 | 15053.0301 | 9.3555 | 98 | 25.4708 | 0.25991 | 198 | 1917.0559 | 18033.839 | 0.7283 | 18033.839 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1063 | MARIPOSA 210110990 | 254452101 | MARIPOSA 2101 | 64432.5092 | 40.0451 | 390 | 101.2865 | 0.25971 | 199 | 1957.101 | 17932.5525 | 0.72421 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9382 | CORNING 110185162 | 103331101 | CORNING 1101 | 9267.4821 | 5.7598 | 28 | 7.2492 | 0.2589 | 200 | 1962.8608 | 17925.3033 | 0.72391 | 17925.3033 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1035 | CORRAL 110136652 | 162991101 | CORRAL 1101 | 58152.9177 | 36.1423 | 357 | 92.4048 | 0.25884 | 201 | 1999.003 | 17832.8985 | 0.72018 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4603 | UPPER LAKE 1101660 | 42871101 | UPPER LAKE 1101 | 9914.559 | 6.1619 | 91 | 23.5531 | 0.25883 | 202 | 2005.165 | 17809.3454 | 0.71923 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
521 | WILLITS 1103696 | 42661103 | WILLITS 1103 | 10464.5667 | 6.5038 | 87 | 22.4395 | 0.25793 | 203 | 2011.6688 | 17786.9059 | 0.71833 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
134 | SAN JOAQUIN #2 1103CB | 252521103 | SAN JOAQUIN #2 1103 | 109280.4349 | 67.9182 | 589 | 150.7655 | 0.25597 | 204 | 2079.587 | 17636.1404 | 0.71224 | 17636.1404 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3686 | UKIAH 1111534 | 42771111 | UKIAH 1111 | 30432.3399 | 18.9138 | 142 | 36.3189 | 0.25577 | 205 | 2098.5008 | 17599.8215 | 0.71077 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8712 | ELK CREEK 110193504 | 102781101 | ELK CREEK 1101 | 3461.2366 | 2.1512 | 15 | 3.8139 | 0.25426 | 206 | 2100.652 | 17596.0075 | 0.71062 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10786 | PEABODY 2113873304 | 63642113 | PEABODY 2113 | 1312.9508 | 0.816 | 5 | 1.2709 | 0.25419 | 207 | 2101.468 | 17594.7366 | 0.71056 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9423 | CLAY 110359714 | 163341103 | CLAY 1103 | 7503.916 | 4.6637 | 34 | 8.6328 | 0.25391 | 208 | 2106.1317 | 17586.1038 | 0.71022 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9267 | POTTER VALLEY P H 1105990354 | 42281105 | POTTER VALLEY P H 1105 | 170.3854 | 0.1059 | 2 | 0.50682 | 0.25341 | 209 | 2106.2376 | 17585.597 | 0.7102 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4480 | LUCERNE 1106526 | 43351106 | LUCERNE 1106 | 16256.6321 | 10.1036 | 100 | 25.318 | 0.25318 | 210 | 2116.3412 | 17560.279 | 0.70917 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3034 | HOPLAND 1101558 | 42251101 | HOPLAND 1101 | 4818.3603 | 2.9946 | 72 | 18.1915 | 0.25266 | 211 | 2119.3358 | 17542.0874 | 0.70844 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4451 | HIGHLANDS 1103568 | 43361103 | HIGHLANDS 1103 | 12940.6184 | 8.0426 | 118 | 29.7625 | 0.25222 | 212 | 2127.3784 | 17512.3249 | 0.70724 | 17512.3249 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5062 | AUBERRY 1102R902 | 254151102 | AUBERRY 1102 | 24261.144 | 15.0784 | 156 | 39.2136 | 0.25137 | 213 | 2142.4568 | 17473.1113 | 0.70565 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5371 | SUNOL 1101MR169 | 14241101 | SUNOL 1101 | 4976.4795 | 3.0929 | 96 | 24.0426 | 0.25044 | 214 | 2145.5497 | 17449.0687 | 0.70468 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8139 | LAS GALLINAS A 110599904 | 42991105 | LAS GALLINAS A 1105 | 8949.4853 | 5.5621 | 54 | 13.5032 | 0.25006 | 215 | 2151.1119 | 17435.5655 | 0.70414 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4462 | WILLITS 110337504 | 42661103 | WILLITS 1103 | 1890.9339 | 1.1752 | 41 | 10.2392 | 0.24974 | 216 | 2152.2871 | 17425.3263 | 0.70372 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4593 | POSO MOUNTAIN 2101CB | 253642101 | POSO MOUNTAIN 2101 | 6924.1001 | 4.3034 | 22 | 5.4697 | 0.24862 | 217 | 2156.5905 | 17419.8566 | 0.7035 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6909 | WYANDOTTE 1109702710 | 102911109 | WYANDOTTE 1109 | 4286.5556 | 2.6641 | 49 | 12.174 | 0.24845 | 218 | 2159.2546 | 17407.6826 | 0.70301 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9944 | WYANDOTTE 110366146 | 102911103 | WYANDOTTE 1103 | 252.3083 | 0.15681 | 4 | 0.99171 | 0.24793 | 219 | 2159.4114 | 17406.6909 | 0.70297 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10031 | SOLEDAD 2102346006 | 182052102 | SOLEDAD 2102 | 3650.4625 | 2.2688 | 5 | 1.2382 | 0.24765 | 220 | 2161.6802 | 17405.4527 | 0.70292 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
905 | CORNING 110290036 | 103331102 | CORNING 1102 | 21561.1762 | 13.4004 | 87 | 21.5103 | 0.24724 | 221 | 2175.0805 | 17383.9424 | 0.70205 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5847 | OAKHURST 11035732 | 254421103 | OAKHURST 1103 | 5445.3198 | 3.3843 | 37 | 9.1461 | 0.24719 | 222 | 2178.4648 | 17374.7963 | 0.70168 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5505 | MARIPOSA 210237282 | 254452102 | MARIPOSA 2102 | 86430.7687 | 53.7171 | 498 | 122.1205 | 0.24522 | 223 | 2232.1819 | 17252.6758 | 0.69675 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4841 | OAKHURST 110363334 | 254421103 | OAKHURST 1103 | 27819.9713 | 17.2902 | 154 | 37.6467 | 0.24446 | 224 | 2249.4721 | 17215.0291 | 0.69523 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8342 | BANGOR 110131502 | 103191101 | BANGOR 1101 | 19104.3686 | 11.8734 | 102 | 24.9173 | 0.24429 | 225 | 2261.3455 | 17190.1118 | 0.69422 | 17190.1118 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9205 | POINT MORETTI 110135874 | 82931101 | POINT MORETTI 1101 | 329.4831 | 0.20478 | 4 | 0.97191 | 0.24298 | 226 | 2261.5503 | 17189.1399 | 0.69418 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2854 | SHINGLE SPRINGS 21099372 | 153652109 | SHINGLE SPRINGS 2109 | 28750.7098 | 17.8687 | 190 | 46.1342 | 0.24281 | 227 | 2279.419 | 17143.0056 | 0.69232 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10573 | GEYSERVILLE 1102756 | 42891102 | GEYSERVILLE 1102 | 948.4078 | 0.58944 | 7 | 1.6966 | 0.24238 | 228 | 2280.0084 | 17141.309 | 0.69225 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6313 | SAN MIGUEL 1104N60 | 182661104 | SAN MIGUEL 1104 | 13316.658 | 8.2764 | 66 | 15.9958 | 0.24236 | 229 | 2288.2848 | 17125.3131 | 0.69161 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2085 | LINCOLN 1104685276 | 153701104 | LINCOLN 1104 | 10432.3869 | 6.4838 | 216 | 52.2897 | 0.24208 | 230 | 2294.7686 | 17073.0234 | 0.68949 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7825 | HORSESHOE 1101416226 | 152571101 | HORSESHOE 1101 | 186.6616 | 0.11601 | 5 | 1.2091 | 0.24182 | 231 | 2294.8846 | 17071.8143 | 0.68945 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9295 | BROWNS VALLEY 110117011 | 152921101 | BROWNS VALLEY 1101 | 3005.3172 | 1.8678 | 22 | 5.3136 | 0.24153 | 232 | 2296.7524 | 17066.5007 | 0.68923 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1428 | ZACA 1102Y02 | 182681102 | ZACA 1102 | 16812.4916 | 10.449 | 158 | 38.1442 | 0.24142 | 233 | 2307.2014 | 17028.3565 | 0.68769 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6825 | OLETA 1102186326 | 163541102 | OLETA 1102 | 19088.8539 | 11.8638 | 123 | 29.6596 | 0.24114 | 234 | 2319.0652 | 16998.6969 | 0.68649 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7670 | STANISLAUS 1702CB | 162821702 | STANISLAUS 1702 | 13066.3244 | 8.1208 | 67 | 16.1444 | 0.24096 | 235 | 2327.186 | 16982.5525 | 0.68584 | 16982.5525 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9773 | MADISON 2101117644 | 63172101 | MADISON 2101 | 1080.3525 | 0.67144 | 12 | 2.8784 | 0.23987 | 236 | 2327.8574 | 16979.6741 | 0.68573 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10170 | PUTAH CREEK 1105617260 | 63681105 | PUTAH CREEK 1105 | 1876.8402 | 1.1665 | 15 | 3.5941 | 0.2396 | 237 | 2329.0239 | 16976.08 | 0.68558 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10828 | BUELLTON 110163389 | 183041101 | BUELLTON 1101 | 0 | 0 | 2 | 0.47871 | 0.23935 | 238 | 2329.0239 | 16975.6013 | 0.68556 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8291 | CLEAR LAKE 1102904 | 42141102 | CLEAR LAKE 1102 | 5445.6493 | 3.3845 | 30 | 7.1587 | 0.23862 | 239 | 2332.4084 | 16968.4425 | 0.68527 | 16968.4425 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6235 | SHINGLE SPRINGS 210519522 | 153652105 | SHINGLE SPRINGS 2105 | 15565.1755 | 9.6738 | 113 | 26.9251 | 0.23827 | 240 | 2342.0822 | 16941.5175 | 0.68418 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9843 | SUNOL 1101MR387 | 14241101 | SUNOL 1101 | 8065.9096 | 5.013 | 24 | 5.7062 | 0.23776 | 241 | 2347.0952 | 16935.8113 | 0.68395 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
109 | WISE 11022054 | 152271102 | WISE 1102 | 20940.0353 | 13.0143 | 147 | 34.8898 | 0.23735 | 242 | 2360.1095 | 16900.9214 | 0.68254 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9387 | ANTELOPE 1101318686 | 252021101 | ANTELOPE 1101 | 2345.6024 | 1.4578 | 7 | 1.6578 | 0.23683 | 243 | 2361.5673 | 16899.2636 | 0.68248 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2465 | JESSUP 11021314 | 103441102 | JESSUP 1102 | 9677.7607 | 6.0148 | 161 | 38.0983 | 0.23664 | 244 | 2367.5821 | 16861.1654 | 0.68094 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4610 | KERCKHOFF 1101R353 | 252561101 | KERCKHOFF 1101 | 22190.5443 | 13.7915 | 53 | 12.4952 | 0.23576 | 245 | 2381.3736 | 16848.6702 | 0.68043 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7566 | CORRAL 110112608 | 162991101 | CORRAL 1101 | 27131.1027 | 16.8621 | 187 | 44.029 | 0.23545 | 246 | 2398.2357 | 16804.6412 | 0.67866 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5704 | SHEPHERD 2111707358 | 252062111 | SHEPHERD 2111 | 30537.9753 | 18.9795 | 219 | 51.4409 | 0.23489 | 247 | 2417.2152 | 16753.2003 | 0.67658 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10861 | PEORIA 170492888 | 163781704 | PEORIA 1704 | 400.6025 | 0.24898 | 4 | 0.93885 | 0.23471 | 248 | 2417.4642 | 16752.2615 | 0.67654 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5055 | FROGTOWN 17028482 | 163451702 | FROGTOWN 1702 | 23390.9929 | 14.5376 | 117 | 27.4214 | 0.23437 | 249 | 2432.0018 | 16724.84 | 0.67543 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10192 | MADISON 2101725408 | 63172101 | MADISON 2101 | 1530.1897 | 0.95102 | 9 | 2.1085 | 0.23427 | 250 | 2432.9528 | 16722.7316 | 0.67535 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
852 | PASO ROBLES 1104R56 | 182611104 | PASO ROBLES 1104 | 18526.1855 | 11.5141 | 117 | 27.401 | 0.2342 | 251 | 2444.4669 | 16695.3306 | 0.67424 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9420 | FRENCH GULCH 11011892 | 103381101 | FRENCH GULCH 1101 | 5154.3447 | 3.2034 | 12 | 2.8006 | 0.23339 | 252 | 2447.6703 | 16692.53 | 0.67413 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2713 | ELK CREEK 110137334 | 102781101 | ELK CREEK 1101 | 15392.9848 | 9.5668 | 70 | 16.3175 | 0.23311 | 253 | 2457.2371 | 16676.2125 | 0.67347 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8722 | POSO MOUNTAIN 21033988 | 253642103 | POSO MOUNTAIN 2103 | 27217.7374 | 16.9159 | 68 | 15.8463 | 0.23303 | 254 | 2474.1531 | 16660.3662 | 0.67283 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6130 | OREGON TRAIL 1104CB | 103521104 | OREGON TRAIL 1104 | 17030.244 | 10.5844 | 164 | 38.0188 | 0.23182 | 255 | 2484.7374 | 16622.3474 | 0.67129 | 16622.3474 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6781 | PALMER 1101M84 | 183031101 | PALMER 1101 | 37718.995 | 23.4425 | 145 | 33.5958 | 0.23169 | 256 | 2508.1799 | 16588.7517 | 0.66994 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7251 | PASO ROBLES 1103N58 | 182611103 | PASO ROBLES 1103 | 7319.6094 | 4.5492 | 91 | 21.0205 | 0.23099 | 257 | 2512.7291 | 16567.7312 | 0.66909 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9345 | CHOLAME 21025597 | 182562102 | CHOLAME 2102 | 8229.9238 | 5.1149 | 22 | 5.062 | 0.23009 | 258 | 2517.844 | 16562.6692 | 0.66888 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6582 | UPPER LAKE 1101412 | 42871101 | UPPER LAKE 1101 | 16599.9817 | 10.317 | 152 | 34.9724 | 0.23008 | 259 | 2528.161 | 16527.6968 | 0.66747 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7180 | PASO ROBLES 11032731 | 182611103 | PASO ROBLES 1103 | 2630.6286 | 1.6349 | 13 | 2.9847 | 0.2296 | 260 | 2529.7959 | 16524.712 | 0.66735 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6731 | DEL MAR 2109CB | 152582109 | DEL MAR 2109 | 2376.9126 | 1.4773 | 72 | 16.5281 | 0.22956 | 261 | 2531.2732 | 16508.1839 | 0.66668 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4193 | ANDERSON 1103226050 | 103261103 | ANDERSON 1103 | 7845.4549 | 4.876 | 160 | 36.6601 | 0.22913 | 262 | 2536.1492 | 16471.5238 | 0.6652 | 16471.5238 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2449 | COARSEGOLD 210410400 | 254432104 | COARSEGOLD 2104 | 68567.3531 | 42.6149 | 539 | 123.0305 | 0.22826 | 263 | 2578.7641 | 16348.4933 | 0.66023 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6456 | HIGGINS 110950078 | 152691109 | HIGGINS 1109 | 77925.0015 | 48.4307 | 427 | 97.3194 | 0.22791 | 264 | 2627.1948 | 16251.1739 | 0.6563 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6171 | WYANDOTTE 110737472 | 102911107 | WYANDOTTE 1107 | 14935.9015 | 9.2827 | 157 | 35.7007 | 0.22739 | 265 | 2636.4775 | 16215.4732 | 0.65486 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1604 | COARSEGOLD 210310820 | 254432103 | COARSEGOLD 2103 | 46392.4448 | 28.8331 | 327 | 74.1966 | 0.2269 | 266 | 2665.3106 | 16141.2766 | 0.65187 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3581 | JESSUP 110296554 | 103441102 | JESSUP 1102 | 12987.3897 | 8.0717 | 172 | 38.9486 | 0.22645 | 267 | 2673.3823 | 16102.328 | 0.65029 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10176 | CLARK ROAD 1102CB | 103091102 | CLARK ROAD 1102 | 1435.1005 | 0.89192 | 20 | 4.5263 | 0.22632 | 268 | 2674.2742 | 16097.8016 | 0.65011 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1714 | BUELLTON 1102Y50 | 183041102 | BUELLTON 1102 | 17101.0403 | 10.6284 | 147 | 33.2573 | 0.22624 | 269 | 2684.9026 | 16064.5443 | 0.64877 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2661 | CLAY 11031230 | 163341103 | CLAY 1103 | 27069.5791 | 16.8239 | 136 | 30.7471 | 0.22608 | 270 | 2701.7264 | 16033.7972 | 0.64753 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
511 | COTTONWOOD 11029026 | 102931102 | COTTONWOOD 1102 | 20154.6992 | 12.5262 | 282 | 63.7295 | 0.22599 | 271 | 2714.2527 | 15970.0677 | 0.64495 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5682 | CLOVERDALE 1102672 | 42821102 | CLOVERDALE 1102 | 35088.8854 | 21.8079 | 140 | 31.5995 | 0.22571 | 272 | 2736.0605 | 15938.4682 | 0.64368 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
920 | RED BLUFF 11041630 | 103541104 | RED BLUFF 1104 | 4020.9242 | 2.499 | 152 | 34.2944 | 0.22562 | 273 | 2738.5596 | 15904.1738 | 0.64229 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6155 | AUBERRY 1101R2839 | 254151101 | AUBERRY 1101 | 20608.9537 | 12.8085 | 121 | 27.2266 | 0.22501 | 274 | 2751.3681 | 15876.9472 | 0.64119 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
252 | CLARK ROAD 11022582 | 103091102 | CLARK ROAD 1102 | 32011.0943 | 19.895 | 186 | 41.7559 | 0.22449 | 275 | 2771.2631 | 15835.1913 | 0.63951 | 15835.1913 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5168 | CORNING 11021622 | 103331102 | CORNING 1102 | 54701.9644 | 33.9975 | 126 | 28.2406 | 0.22413 | 276 | 2805.2606 | 15806.9507 | 0.63836 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2620 | AUBERRY 1101R2579 | 254151101 | AUBERRY 1101 | 56162.7607 | 34.9054 | 286 | 64.0469 | 0.22394 | 277 | 2840.166 | 15742.9037 | 0.63578 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7109 | AUBERRY 1102R1013 | 254151102 | AUBERRY 1102 | 20054.4308 | 12.4639 | 132 | 29.5483 | 0.22385 | 278 | 2852.6299 | 15713.3555 | 0.63458 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1039 | SILVERADO 2104726 | 43432104 | SILVERADO 2104 | 48875.2274 | 30.3762 | 263 | 58.7725 | 0.22347 | 279 | 2883.0061 | 15654.583 | 0.63221 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8364 | PEORIA 1705CB | 163781705 | PEORIA 1705 | 11342.4728 | 7.0494 | 33 | 7.3571 | 0.22294 | 280 | 2890.0555 | 15647.226 | 0.63191 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
42 | CEDAR CREEK 11011664 | 103321101 | CEDAR CREEK 1101 | 47581.2918 | 29.572 | 244 | 54.1896 | 0.22209 | 281 | 2919.6274 | 15593.0364 | 0.62973 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8613 | ZACA 1101Y72 | 182681101 | ZACA 1101 | 10265.6354 | 6.3801 | 36 | 7.967 | 0.2213 | 282 | 2926.0076 | 15585.0694 | 0.6294 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5656 | PANORAMA 1102508502 | 103461102 | PANORAMA 1102 | 18917.893 | 11.7575 | 115 | 25.3491 | 0.22043 | 283 | 2937.7651 | 15559.7203 | 0.62838 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2018 | SMARTVILLE 1101CB | 153791101 | SMARTVILLE 1101 | 26026.0287 | 16.1753 | 152 | 33.3354 | 0.21931 | 284 | 2953.9404 | 15526.3848 | 0.62703 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8459 | CAYETANO 21099504 | 14422109 | CAYETANO 2109 | 23283.8699 | 14.471 | 97 | 21.2645 | 0.21922 | 285 | 2968.4114 | 15505.1203 | 0.62618 | 15505.1203 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3475 | SO. CAL. EDISON #3 1101CB | 258861101 | SO. CAL. EDISON #3 1101 | 13738.3645 | 8.5384 | 32 | 6.998 | 0.21869 | 286 | 2976.9499 | 15498.1224 | 0.62589 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5637 | NARROWS 2101CB | 153132101 | NARROWS 2101 | 25047.8448 | 15.5673 | 65 | 14.185 | 0.21823 | 287 | 2992.5172 | 15483.9374 | 0.62532 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8049 | BROWNS VALLEY 110136622 | 152921101 | BROWNS VALLEY 1101 | 8277.82 | 5.1447 | 42 | 9.1438 | 0.21771 | 288 | 2997.6619 | 15474.7936 | 0.62495 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5251 | WYANDOTTE 110313018 | 102911103 | WYANDOTTE 1103 | 1090.3862 | 0.67768 | 20 | 4.3325 | 0.21662 | 289 | 2998.3396 | 15470.4611 | 0.62478 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7438 | OREGON TRAIL 1103CB | 103521103 | OREGON TRAIL 1103 | 4354.341 | 2.7062 | 38 | 8.2246 | 0.21644 | 290 | 3001.0458 | 15462.2365 | 0.62444 | 15462.2365 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9233 | PASO ROBLES 1103N52 | 182611103 | PASO ROBLES 1103 | 10571.3698 | 6.5701 | 32 | 6.9258 | 0.21643 | 291 | 3007.616 | 15455.3107 | 0.62416 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5544 | TYLER 11051536 | 103571105 | TYLER 1105 | 28603.8149 | 17.7774 | 79 | 17.0703 | 0.21608 | 292 | 3025.3933 | 15438.2404 | 0.62347 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8708 | PUTAH CREEK 1105665952 | 63681105 | PUTAH CREEK 1105 | 243.3824 | 0.15126 | 13 | 2.8069 | 0.21591 | 293 | 3025.5446 | 15435.4336 | 0.62336 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9580 | SUMMIT 110147786 | 152591101 | SUMMIT 1101 | 2915.7036 | 1.8121 | 13 | 2.7967 | 0.21513 | 294 | 3027.3567 | 15432.6368 | 0.62325 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10253 | CLOVERDALE 1102736078 | 42821102 | CLOVERDALE 1102 | 373.6781 | 0.23224 | 3 | 0.64381 | 0.2146 | 295 | 3027.589 | 15431.993 | 0.62322 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10589 | DEL MAR 2109306972 | 152582109 | DEL MAR 2109 | 83.4407 | 0.051859 | 2 | 0.4291 | 0.21455 | 296 | 3027.6408 | 15431.5639 | 0.6232 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9314 | CALPINE 1146CB | 48011146 | CALPINE 1146 | 4947.493 | 3.0749 | 21 | 4.4937 | 0.21399 | 297 | 3030.7157 | 15427.0702 | 0.62302 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5389 | BEAR VALLEY 210511210 | 252192105 | BEAR VALLEY 2105 | 27492.7886 | 17.0869 | 139 | 29.7273 | 0.21387 | 298 | 3047.8026 | 15397.3429 | 0.62182 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9003 | HARTLEY 1102385838 | 43211102 | HARTLEY 1102 | 2006.1588 | 1.2468 | 11 | 2.3484 | 0.21349 | 299 | 3049.0494 | 15394.9945 | 0.62173 | 15394.9945 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4243 | CLAYTON 22122944 | 12022212 | CLAYTON 2212 | 24262.4198 | 15.0792 | 148 | 31.5694 | 0.21331 | 300 | 3064.1286 | 15363.4251 | 0.62045 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3022 | DESCHUTES 11041582 | 103351104 | DESCHUTES 1104 | 10265.1395 | 6.3798 | 173 | 36.8955 | 0.21327 | 301 | 3070.5085 | 15326.5296 | 0.61896 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5186 | DUNLAP 11027360 | 254061102 | DUNLAP 1102 | 14342.2552 | 8.9138 | 83 | 17.6557 | 0.21272 | 302 | 3079.4222 | 15308.8739 | 0.61825 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7188 | UPPER LAKE 1101472084 | 42871101 | UPPER LAKE 1101 | 7454.711 | 4.6331 | 66 | 14.0108 | 0.21229 | 303 | 3084.0554 | 15294.863 | 0.61768 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1958 | CURTIS 170411290 | 163351704 | CURTIS 1704 | 12662.0411 | 7.8695 | 75 | 15.9178 | 0.21224 | 304 | 3091.9249 | 15278.9452 | 0.61704 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10301 | SCE VEGAS 1701CB | 188881701 | SCE VEGAS 1701 | 168.4127 | 0.10467 | 1 | 0.2122 | 0.2122 | 305 | 3092.0295 | 15278.733 | 0.61703 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4384 | AUBERRY 110237466 | 254151102 | AUBERRY 1102 | 50460.2287 | 31.3612 | 345 | 72.8874 | 0.21127 | 306 | 3123.3908 | 15205.8456 | 0.61409 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2676 | BUELLTON 1102CB | 183041102 | BUELLTON 1102 | 11401.8921 | 7.0863 | 148 | 31.2055 | 0.21085 | 307 | 3130.4771 | 15174.6401 | 0.61283 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5276 | SANTA YNEZ 110477098 | 182721104 | SANTA YNEZ 1104 | 19250.5668 | 11.9643 | 112 | 23.5673 | 0.21042 | 308 | 3142.4414 | 15151.0728 | 0.61188 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7565 | SILVERADO 2104806 | 43432104 | SILVERADO 2104 | 33831.6044 | 21.0265 | 229 | 48.1076 | 0.21008 | 309 | 3163.4679 | 15102.9653 | 0.60993 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1159 | LONE TREE 210521210 | 13232105 | LONE TREE 2105 | 20686.2377 | 12.8566 | 111 | 23.1943 | 0.20896 | 310 | 3176.3245 | 15079.7709 | 0.609 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1515 | WYANDOTTE 110979932 | 102911109 | WYANDOTTE 1109 | 35504.8505 | 22.0664 | 345 | 71.8562 | 0.20828 | 311 | 3198.3909 | 15007.9148 | 0.6061 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4727 | REDBUD 1101454 | 43191101 | REDBUD 1101 | 8909.2195 | 5.5371 | 54 | 11.1984 | 0.20738 | 312 | 3203.928 | 14996.7164 | 0.60564 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2411 | MARIPOSA 210190180 | 254452101 | MARIPOSA 2101 | 7976.0066 | 4.9571 | 49 | 10.1373 | 0.20688 | 313 | 3208.8851 | 14986.5791 | 0.60523 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6630 | MIDDLETOWN 1101644756 | 43141101 | MIDDLETOWN 1101 | 27875.8932 | 17.325 | 163 | 33.6372 | 0.20636 | 314 | 3226.2101 | 14952.9419 | 0.60388 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8301 | ELK CREEK 11012002 | 102781101 | ELK CREEK 1101 | 35045.7729 | 21.7811 | 109 | 22.3155 | 0.20473 | 315 | 3247.9912 | 14930.6264 | 0.60297 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1537 | BELL 11072400 | 152701107 | BELL 1107 | 41414.8349 | 25.7395 | 320 | 65.3543 | 0.20423 | 316 | 3273.7307 | 14865.2721 | 0.60033 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2016 | PETALUMA C 1108296 | 42631108 | PETALUMA C 1108 | 23764.0701 | 14.7695 | 123 | 25.0928 | 0.20401 | 317 | 3288.5001 | 14840.1792 | 0.59932 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1327 | DESCHUTES 1104CB | 103351104 | DESCHUTES 1104 | 21735.4144 | 13.5086 | 273 | 55.4629 | 0.20316 | 318 | 3302.0088 | 14784.7163 | 0.59708 | 14784.7163 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10175 | JESSUP 1102936897 | 103441102 | JESSUP 1102 | 665.5519 | 0.41364 | 12 | 2.432 | 0.20267 | 319 | 3302.4224 | 14782.2843 | 0.59698 | 14782.2843 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2512 | CLAY 110334338 | 163341103 | CLAY 1103 | 15726.6133 | 9.7742 | 66 | 13.3455 | 0.2022 | 320 | 3312.1966 | 14768.9388 | 0.59644 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3530 | AUBERRY 1102R2850 | 254151102 | AUBERRY 1102 | 42428.4265 | 26.3694 | 222 | 44.7693 | 0.20166 | 321 | 3338.566 | 14724.1695 | 0.59464 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4238 | NORTH BRANCH 1101CB | 163231101 | NORTH BRANCH 1101 | 25410.3119 | 15.7926 | 114 | 22.9503 | 0.20132 | 322 | 3354.3586 | 14701.2192 | 0.59371 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11083 | NARROWS 2104CB | 153132104 | NARROWS 2104 | 4.572 | 0.0028415 | 1 | 0.20132 | 0.20132 | 323 | 3354.3615 | 14701.0179 | 0.5937 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
389 | VASCO 1102MR176 | 13751102 | VASCO 1102 | 62474.1803 | 38.828 | 256 | 51.5086 | 0.20121 | 324 | 3393.1894 | 14649.5093 | 0.59162 | 14649.5093 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7455 | SAN MIGUEL 1104514987 | 182661104 | SAN MIGUEL 1104 | 13379.7927 | 8.3156 | 63 | 12.6303 | 0.20048 | 325 | 3401.505 | 14636.879 | 0.59111 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7507 | NORTH BRANCH 110111158 | 163231101 | NORTH BRANCH 1101 | 20499.8935 | 12.7408 | 229 | 45.8175 | 0.20008 | 326 | 3414.2458 | 14591.0614 | 0.58926 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3193 | AUBERRY 1101R314 | 254151101 | AUBERRY 1101 | 68245.5324 | 42.4149 | 390 | 78.017 | 0.20004 | 327 | 3456.6606 | 14513.0444 | 0.58611 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1293 | MIDDLETOWN 11014646 | 43141101 | MIDDLETOWN 1101 | 29868.2951 | 18.5633 | 165 | 32.9712 | 0.19983 | 328 | 3475.2239 | 14480.0732 | 0.58478 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9642 | LUCERNE 11034200 | 43351103 | LUCERNE 1103 | 6495.7462 | 4.0371 | 37 | 7.3729 | 0.19927 | 329 | 3479.261 | 14472.7003 | 0.58448 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7729 | AUBERRY 110149122 | 254151101 | AUBERRY 1101 | 6376.3554 | 3.9629 | 40 | 7.9627 | 0.19907 | 330 | 3483.224 | 14464.7376 | 0.58416 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
464 | WOODACRE 110196844 | 43021101 | WOODACRE 1101 | 9556.2941 | 5.9393 | 63 | 12.5249 | 0.19881 | 331 | 3489.1633 | 14452.2127 | 0.58365 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4726 | SHINGLE SPRINGS 210985766 | 153652109 | SHINGLE SPRINGS 2109 | 29746.7523 | 18.4877 | 166 | 32.9759 | 0.19865 | 332 | 3507.651 | 14419.2368 | 0.58232 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9424 | VINEYARD 2110391250 | 14502110 | VINEYARD 2110 | 1481.3226 | 0.92065 | 3 | 0.59524 | 0.19841 | 333 | 3508.5716 | 14418.6416 | 0.5823 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
308 | CALPINE 1144CB | 48011144 | CALPINE 1144 | 42270.0145 | 26.271 | 131 | 25.9607 | 0.19817 | 334 | 3534.8426 | 14392.6809 | 0.58125 | 14392.6809 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7335 | UPPER LAKE 11011276 | 42871101 | UPPER LAKE 1101 | 20806.9121 | 12.9316 | 116 | 22.9608 | 0.19794 | 335 | 3547.7742 | 14369.7201 | 0.58032 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3179 | CHOLAME 2102796386 | 182562102 | CHOLAME 2102 | 57391.9753 | 35.6693 | 159 | 31.4686 | 0.19792 | 336 | 3583.4435 | 14338.2515 | 0.57905 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9031 | SAND CREEK 1103CB | 254601103 | SAND CREEK 1103 | 20983.2028 | 13.0411 | 77 | 15.2216 | 0.19768 | 337 | 3596.4847 | 14323.0299 | 0.57844 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6545 | TULUCAY 1101628 | 42301101 | TULUCAY 1101 | 6713.6414 | 4.1726 | 98 | 19.2923 | 0.19686 | 338 | 3600.6572 | 14303.7376 | 0.57766 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4963 | BEAR VALLEY 210190550 | 252192101 | BEAR VALLEY 2101 | 12911.2772 | 8.0244 | 47 | 9.2235 | 0.19624 | 339 | 3608.6816 | 14294.5141 | 0.57728 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8575 | ELK CREEK 11012106 | 102781101 | ELK CREEK 1101 | 21303.4581 | 13.2402 | 67 | 13.1388 | 0.1961 | 340 | 3621.9218 | 14281.3753 | 0.57675 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3500 | DUNLAP 11037040 | 254061103 | DUNLAP 1103 | 39870.081 | 24.7794 | 230 | 45.0921 | 0.19605 | 341 | 3646.7012 | 14236.2832 | 0.57493 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2568 | LAYTONVILLE 1102500 | 42681102 | LAYTONVILLE 1102 | 34375.7452 | 21.3647 | 214 | 41.8921 | 0.19576 | 342 | 3668.0659 | 14194.3911 | 0.57324 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2190 | DIAMOND SPRINGS 110519910 | 152261105 | DIAMOND SPRINGS 1105 | 33304.7006 | 20.699 | 226 | 44.2238 | 0.19568 | 343 | 3688.7649 | 14150.1673 | 0.57146 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9927 | FITCH MOUNTAIN 1111555644 | 42751111 | FITCH MOUNTAIN 1111 | 268.6791 | 0.16699 | 19 | 3.7125 | 0.19539 | 344 | 3688.9319 | 14146.4548 | 0.57131 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
41 | REDBUD 1101708166 | 43191101 | REDBUD 1101 | 18511.1854 | 11.5048 | 162 | 31.6535 | 0.19539 | 345 | 3700.4367 | 14114.8013 | 0.57003 | 14114.8013 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8428 | CALPELLA 11013419 | 43411101 | CALPELLA 1101 | 12848.2917 | 7.9853 | 38 | 7.4218 | 0.19531 | 346 | 3708.4219 | 14107.3795 | 0.56973 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4645 | OLETA 110241396 | 163541102 | OLETA 1102 | 10868.1559 | 6.7546 | 75 | 14.6272 | 0.19503 | 347 | 3715.1765 | 14092.7523 | 0.56914 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1354 | CORRAL 1102CB | 162991102 | CORRAL 1102 | 27168.7986 | 16.8855 | 236 | 46.0213 | 0.19501 | 348 | 3732.0621 | 14046.731 | 0.56728 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6647 | TIVY VALLEY 1107584840 | 252941107 | TIVY VALLEY 1107 | 72531.1064 | 45.0784 | 449 | 87.311 | 0.19446 | 349 | 3777.1404 | 13959.42 | 0.56375 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4112 | JESSUP 110141356 | 103441101 | JESSUP 1101 | 52238.1569 | 32.4662 | 318 | 61.8351 | 0.19445 | 350 | 3809.6067 | 13897.5849 | 0.56125 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1219 | APPLE HILL 21021532 | 153662102 | APPLE HILL 2102 | 62691.3369 | 38.9629 | 465 | 90.2637 | 0.19412 | 351 | 3848.5696 | 13807.3212 | 0.55761 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4008 | OLETA 11011208 | 163541101 | OLETA 1101 | 53098.4432 | 33.0009 | 334 | 64.811 | 0.19404 | 352 | 3881.5705 | 13742.5102 | 0.55499 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9763 | WISHON 1101CB | 251511101 | WISHON 1101 | 12293.5283 | 7.6405 | 36 | 6.9834 | 0.19398 | 353 | 3889.211 | 13735.5268 | 0.55471 | 13735.5268 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4721 | COPPERMINE 1104613086 | 252411104 | COPPERMINE 1104 | 8243.1424 | 5.1231 | 63 | 12.2166 | 0.19391 | 354 | 3894.3341 | 13723.3102 | 0.55422 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8166 | BANGOR 1101CB | 103191101 | BANGOR 1101 | 30178.5623 | 18.7561 | 171 | 33.1366 | 0.19378 | 355 | 3913.0902 | 13690.1736 | 0.55288 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10364 | MADISON 2101745850 | 63172101 | MADISON 2101 | 771.4701 | 0.47947 | 7 | 1.3558 | 0.19369 | 356 | 3913.5697 | 13688.8178 | 0.55282 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10620 | OLETA 1102793776 | 163541102 | OLETA 1102 | 1956.9595 | 1.2163 | 6 | 1.1597 | 0.19328 | 357 | 3914.7859 | 13687.6581 | 0.55278 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1881 | PENRYN 1103604 | 152561103 | PENRYN 1103 | 42516.8793 | 26.4244 | 240 | 46.357 | 0.19315 | 358 | 3941.2103 | 13641.301 | 0.5509 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10174 | LAS GALLINAS A 1105532 | 42991105 | LAS GALLINAS A 1105 | 7099.179 | 4.4122 | 34 | 6.5497 | 0.19264 | 359 | 3945.6225 | 13634.7514 | 0.55064 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9563 | ELK CREEK 11012032 | 102781101 | ELK CREEK 1101 | 14097.676 | 8.7618 | 52 | 10.0031 | 0.19237 | 360 | 3954.3843 | 13624.7483 | 0.55024 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7617 | WYANDOTTE 110213044 | 102911102 | WYANDOTTE 1102 | 7674.8454 | 4.7699 | 51 | 9.8065 | 0.19229 | 361 | 3959.1542 | 13614.9417 | 0.54984 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3855 | SAND CREEK 11037140 | 254601103 | SAND CREEK 1103 | 42300.5526 | 26.29 | 296 | 56.8394 | 0.19202 | 362 | 3985.4442 | 13558.1024 | 0.54754 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5056 | BANGOR 110182350 | 103191101 | BANGOR 1101 | 31579.2765 | 19.6266 | 230 | 44.1515 | 0.19196 | 363 | 4005.0708 | 13513.9509 | 0.54576 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
523 | DUNLAP 11037220 | 254061103 | DUNLAP 1103 | 39952.2483 | 24.8305 | 188 | 36.0414 | 0.19171 | 364 | 4029.9013 | 13477.9095 | 0.54431 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8426 | FORT ROSS 1121CB | 42851121 | FORT ROSS 1121 | 25.9334 | 0.016118 | 1 | 0.19152 | 0.19152 | 365 | 4029.9174 | 13477.7179 | 0.5443 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8629 | FOOTHILL 1101645910 | 182951101 | FOOTHILL 1101 | 774.6277 | 0.48143 | 14 | 2.6788 | 0.19134 | 366 | 4030.3989 | 13475.0391 | 0.54419 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7469 | PALMER 110198478 | 183031101 | PALMER 1101 | 9678.6987 | 6.0154 | 34 | 6.5022 | 0.19124 | 367 | 4036.4142 | 13468.5369 | 0.54393 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5366 | WYANDOTTE 11095607 | 102911109 | WYANDOTTE 1109 | 7265.9446 | 4.5158 | 71 | 13.5714 | 0.19115 | 368 | 4040.93 | 13454.9654 | 0.54338 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9473 | HARTLEY 1102524 | 43211102 | HARTLEY 1102 | 399.4552 | 0.24826 | 31 | 5.8946 | 0.19015 | 369 | 4041.1783 | 13449.0708 | 0.54314 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6494 | WISE 1102697216 | 152271102 | WISE 1102 | 21374.2842 | 13.2842 | 145 | 27.5378 | 0.18992 | 370 | 4054.4625 | 13421.533 | 0.54203 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4257 | REDBUD 1102CB | 43191102 | REDBUD 1102 | 28146.4256 | 17.4931 | 170 | 32.2538 | 0.18973 | 371 | 4071.9556 | 13389.2792 | 0.54073 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9558 | BRENTWOOD 21056512 | 14592105 | BRENTWOOD 2105 | 1047.7996 | 0.65121 | 5 | 0.94545 | 0.18909 | 372 | 4072.6068 | 13388.3338 | 0.54069 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10458 | DEL MAR 2109805882 | 152582109 | DEL MAR 2109 | 477.3024 | 0.29665 | 6 | 1.1343 | 0.18904 | 373 | 4072.9035 | 13387.1995 | 0.54064 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2068 | OLETA 11021228 | 163541102 | OLETA 1102 | 17449.9174 | 10.8452 | 368 | 69.4681 | 0.18877 | 374 | 4083.7487 | 13317.7315 | 0.53784 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2280 | DESCHUTES 11011580 | 103351101 | DESCHUTES 1101 | 76365.8976 | 47.4617 | 383 | 71.9249 | 0.18779 | 375 | 4131.2104 | 13245.8065 | 0.53493 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6271 | COTTONWOOD 110131500 | 102931101 | COTTONWOOD 1101 | 7501.4293 | 4.6622 | 111 | 20.823 | 0.18759 | 376 | 4135.8726 | 13224.9836 | 0.53409 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
449 | CLAYTON 221296224 | 12022212 | CLAYTON 2212 | 31213.3049 | 19.3992 | 174 | 32.6329 | 0.18755 | 377 | 4155.2718 | 13192.3507 | 0.53277 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9225 | BUCKS CREEK 1102CB | 102211102 | BUCKS CREEK 1102 | 47599.3495 | 29.5832 | 121 | 22.6633 | 0.1873 | 378 | 4184.8549 | 13169.6874 | 0.53186 | 13169.6874 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4556 | MARIPOSA 210237288 | 254452102 | MARIPOSA 2102 | 137232.3506 | 85.2905 | 678 | 126.9051 | 0.18718 | 379 | 4270.1454 | 13042.7824 | 0.52673 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9851 | PANORAMA 1101885215 | 103461101 | PANORAMA 1101 | 3225.5678 | 2.0047 | 23 | 4.3021 | 0.18705 | 380 | 4272.1501 | 13038.4803 | 0.52656 | 13038.4803 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1129 | PETALUMA C 1109128 | 42631109 | PETALUMA C 1109 | 56205.3694 | 34.9319 | 269 | 50.2671 | 0.18687 | 381 | 4307.082 | 12988.2132 | 0.52453 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5974 | DOBBINS 110169722 | 153741101 | DOBBINS 1101 | 10673.4289 | 6.6336 | 68 | 12.6993 | 0.18675 | 382 | 4313.7155 | 12975.5139 | 0.52402 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6088 | TYLER 110585132 | 103571105 | TYLER 1105 | 50093.0189 | 31.133 | 217 | 40.4342 | 0.18633 | 383 | 4344.8486 | 12935.0798 | 0.52238 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6487 | STILLWATER 110248952 | 103561102 | STILLWATER 1102 | 17050.5619 | 10.597 | 123 | 22.8305 | 0.18561 | 384 | 4355.4456 | 12912.2492 | 0.52146 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7029 | PENRYN 1106212772 | 152561106 | PENRYN 1106 | 1609.198 | 1.0001 | 11 | 2.041 | 0.18554 | 385 | 4356.4457 | 12910.2083 | 0.52138 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7958 | GEYSERVILLE 110179788 | 42891101 | GEYSERVILLE 1101 | 63661.5746 | 39.5659 | 157 | 29.1256 | 0.18551 | 386 | 4396.0116 | 12881.0826 | 0.5202 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2772 | WYANDOTTE 110913052 | 102911109 | WYANDOTTE 1109 | 31480.1828 | 19.5651 | 213 | 39.4358 | 0.18514 | 387 | 4415.5767 | 12841.6469 | 0.51861 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9699 | LOGAN CREEK 2102795010 | 103142102 | LOGAN CREEK 2102 | 5964.9276 | 3.7072 | 12 | 2.2206 | 0.18505 | 388 | 4419.2839 | 12839.4263 | 0.51852 | 12839.4263 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2290 | JESSUP 11021550 | 103441102 | JESSUP 1102 | 31009.474 | 19.2725 | 237 | 43.5983 | 0.18396 | 389 | 4438.5564 | 12795.828 | 0.51676 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
881 | RED BLUFF 11011556 | 103541101 | RED BLUFF 1101 | 61930.0824 | 38.4898 | 411 | 75.4478 | 0.18357 | 390 | 4477.0462 | 12720.3803 | 0.51371 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11061 | SAN LUIS OBISPO 1103365572 | 182631103 | SAN LUIS OBISPO 1103 | 611.8589 | 0.38027 | 2 | 0.36597 | 0.18299 | 391 | 4477.4265 | 12720.0143 | 0.5137 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6935 | CEDAR CREEK 1101CB | 103321101 | CEDAR CREEK 1101 | 24813.8274 | 15.4219 | 127 | 23.1832 | 0.18254 | 392 | 4492.8484 | 12696.8311 | 0.51276 | 12696.8311 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3564 | JAMESON 1105466348 | 63801105 | JAMESON 1105 | 26039.2723 | 16.1835 | 294 | 53.5743 | 0.18223 | 393 | 4509.0319 | 12643.2568 | 0.5106 | 12643.2568 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2550 | COTTONWOOD 110335470 | 102931103 | COTTONWOOD 1103 | 33111.1919 | 20.5787 | 174 | 31.6926 | 0.18214 | 394 | 4529.6106 | 12611.5642 | 0.50932 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2265 | BELL 1108CB | 152701108 | BELL 1108 | 0 | 0 | 83 | 15.1167 | 0.18213 | 395 | 4529.6106 | 12596.4475 | 0.50871 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6694 | POTTER VALLEY P H 110537476 | 42281105 | POTTER VALLEY P H 1105 | 4231.6102 | 2.63 | 82 | 14.8479 | 0.18107 | 396 | 4532.2406 | 12581.5996 | 0.50811 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2442 | CORRAL 110112612 | 162991101 | CORRAL 1101 | 31091.451 | 19.3235 | 195 | 35.2855 | 0.18095 | 397 | 4551.564 | 12546.3141 | 0.50668 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2325 | COTTONWOOD 11011510 | 102931101 | COTTONWOOD 1101 | 613.4018 | 0.38123 | 35 | 6.3309 | 0.18088 | 398 | 4551.9453 | 12539.9832 | 0.50643 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6987 | TEMPLETON 2113641367 | 183052113 | TEMPLETON 2113 | 63879.2901 | 39.7012 | 278 | 50.2607 | 0.18079 | 399 | 4591.6465 | 12489.7225 | 0.5044 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1077 | CLAYTON 2212Y504R | 12022212 | CLAYTON 2212 | 18838.2347 | 11.708 | 112 | 20.1836 | 0.18021 | 400 | 4603.3546 | 12469.5389 | 0.50358 | 12469.5389 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6538 | DUNLAP 11027060 | 254061102 | DUNLAP 1102 | 28760.1957 | 17.8746 | 162 | 29.1914 | 0.18019 | 401 | 4621.2291 | 12440.3474 | 0.5024 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8223 | POSO MOUNTAIN 210448268 | 253642104 | POSO MOUNTAIN 2104 | 8152.5339 | 5.0668 | 30 | 5.3932 | 0.17977 | 402 | 4626.296 | 12434.9542 | 0.50219 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7847 | OILFIELDS 11032757 | 182391103 | OILFIELDS 1103 | 4222.897 | 2.6245 | 16 | 2.8656 | 0.1791 | 403 | 4628.9205 | 12432.0886 | 0.50207 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1905 | TIVY VALLEY 1107R1817 | 252941107 | TIVY VALLEY 1107 | 31029.2187 | 19.2848 | 145 | 25.9373 | 0.17888 | 404 | 4648.2053 | 12406.1513 | 0.50102 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3840 | SAND CREEK 11037070 | 254601103 | SAND CREEK 1103 | 28250.671 | 17.5579 | 103 | 18.4097 | 0.17873 | 405 | 4665.7632 | 12387.7417 | 0.50028 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1011 | CALISTOGA 1101890 | 42711101 | CALISTOGA 1101 | 39211.6931 | 24.3702 | 203 | 36.2505 | 0.17857 | 406 | 4690.1334 | 12351.4912 | 0.49882 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1851 | KONOCTI 1102CB | 43311102 | KONOCTI 1102 | 6326.3363 | 3.9318 | 97 | 17.2565 | 0.1779 | 407 | 4694.0653 | 12334.2347 | 0.49812 | 12334.2347 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7708 | COLUMBIA HILL 110190730 | 152471101 | COLUMBIA HILL 1101 | 13402.9331 | 8.33 | 77 | 13.6383 | 0.17712 | 408 | 4702.3952 | 12320.5964 | 0.49757 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10514 | SCE TEHACHAPI 1101CB | 258131101 | SCE TEHACHAPI 1101 | 1862.134 | 1.1573 | 2 | 0.3533 | 0.17665 | 409 | 4703.5526 | 12320.2431 | 0.49755 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5375 | TASSAJARA 2109CB | 14662109 | TASSAJARA 2109 | 3111.1631 | 1.9336 | 12 | 2.1128 | 0.17607 | 410 | 4705.4862 | 12318.1303 | 0.49747 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8181 | APPLE HILL 210289934 | 153662102 | APPLE HILL 2102 | 8917.9013 | 5.5425 | 56 | 9.8455 | 0.17581 | 411 | 4711.0287 | 12308.2848 | 0.49707 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3827 | HIGGINS 1109594 | 152691109 | HIGGINS 1109 | 23079.0447 | 14.3437 | 155 | 27.2219 | 0.17563 | 412 | 4725.3724 | 12281.0628 | 0.49597 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
329 | CORNING 110253184 | 103331102 | CORNING 1102 | 51204.6527 | 31.8239 | 123 | 21.5791 | 0.17544 | 413 | 4757.1963 | 12259.4838 | 0.4951 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6969 | PETALUMA C 1108208 | 42631108 | PETALUMA C 1108 | 20077.9466 | 12.4785 | 95 | 16.663 | 0.1754 | 414 | 4769.6748 | 12242.8208 | 0.49443 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8229 | GARBERVILLE 11012026 | 192221101 | GARBERVILLE 1101 | 10220.4249 | 6.352 | 26 | 4.5532 | 0.17512 | 415 | 4776.0269 | 12238.2677 | 0.49424 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8173 | ZACA 1101CB | 182681101 | ZACA 1101 | 12032.4791 | 7.4782 | 60 | 10.4995 | 0.17499 | 416 | 4783.5051 | 12227.7682 | 0.49382 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5131 | PHILO 11013700 | 42601101 | PHILO 1101 | 29156.0449 | 18.1206 | 116 | 20.2673 | 0.17472 | 417 | 4801.6257 | 12207.5009 | 0.493 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
908 | PUTAH CREEK 1102710384 | 63681102 | PUTAH CREEK 1102 | 8584.2298 | 5.3351 | 84 | 14.6739 | 0.17469 | 418 | 4806.9608 | 12192.827 | 0.49241 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9983 | JAMESON 1105913400 | 63801105 | JAMESON 1105 | 172.3529 | 0.10712 | 14 | 2.444 | 0.17457 | 419 | 4807.0679 | 12190.383 | 0.49231 | 12190.383 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6899 | FORT SEWARD 11211690 | 192321121 | FORT SEWARD 1121 | 17377.7027 | 10.8003 | 77 | 13.4358 | 0.17449 | 420 | 4817.8683 | 12176.9472 | 0.49177 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2810 | OAKHURST 110110090 | 254421101 | OAKHURST 1101 | 70938.5406 | 44.0886 | 435 | 75.8506 | 0.17437 | 421 | 4861.9569 | 12101.0967 | 0.4887 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8488 | BROWNS VALLEY 1101CB | 152921101 | BROWNS VALLEY 1101 | 3639.3631 | 2.2619 | 17 | 2.9631 | 0.1743 | 422 | 4864.2187 | 12098.1336 | 0.48858 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1886 | REDBUD 1101323962 | 43191101 | REDBUD 1101 | 33116.5425 | 20.5821 | 282 | 49.0357 | 0.17389 | 423 | 4884.8008 | 12049.0979 | 0.4866 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7655 | SHINGLE SPRINGS 210851476 | 153652108 | SHINGLE SPRINGS 2108 | 7926.327 | 4.9262 | 74 | 12.8462 | 0.1736 | 424 | 4889.727 | 12036.2517 | 0.48608 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6143 | OILFIELDS 1103N64 | 182391103 | OILFIELDS 1103 | 17721.3198 | 11.0139 | 101 | 17.4874 | 0.17314 | 425 | 4900.7409 | 12018.7643 | 0.48538 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3312 | OLETA 11011217 | 163541101 | OLETA 1101 | 22843.3853 | 14.1973 | 116 | 20.0623 | 0.17295 | 426 | 4914.9382 | 11998.7021 | 0.48457 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10420 | SANTA YNEZ 1101673618 | 182721101 | SANTA YNEZ 1101 | 171.3788 | 0.10651 | 4 | 0.69175 | 0.17294 | 427 | 4915.0447 | 11998.0103 | 0.48454 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
50 | MARIPOSA 210135244 | 254452101 | MARIPOSA 2101 | 28098.7686 | 17.4635 | 146 | 25.237 | 0.17286 | 428 | 4932.5082 | 11972.7733 | 0.48352 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6824 | MARIPOSA 21021960 | 254452102 | MARIPOSA 2102 | 39696.7204 | 24.6717 | 223 | 38.4488 | 0.17242 | 429 | 4957.1798 | 11934.3245 | 0.48197 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7293 | WISE 11022234 | 152271102 | WISE 1102 | 24349.9914 | 15.1336 | 179 | 30.784 | 0.17198 | 430 | 4972.3135 | 11903.5405 | 0.48073 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6103 | CALPELLA 1102421412 | 43411102 | CALPELLA 1102 | 1616.3093 | 1.0045 | 38 | 6.5083 | 0.17127 | 431 | 4973.318 | 11897.0323 | 0.48046 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8262 | DESCHUTES 11019722 | 103351101 | DESCHUTES 1101 | 5139.2872 | 3.1941 | 55 | 9.3959 | 0.17084 | 432 | 4976.5121 | 11887.6363 | 0.48008 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3350 | OAKHURST 110310570 | 254421103 | OAKHURST 1103 | 15440.8056 | 9.5965 | 92 | 15.6885 | 0.17053 | 433 | 4986.1086 | 11871.9478 | 0.47945 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7252 | OILFIELDS 1103N42 | 182391103 | OILFIELDS 1103 | 5997.3144 | 3.7274 | 30 | 5.105 | 0.17017 | 434 | 4989.836 | 11866.8428 | 0.47924 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2738 | SAN BENITO 2101221165 | 182742101 | SAN BENITO 2101 | 7056.9288 | 4.3859 | 39 | 6.6364 | 0.17016 | 435 | 4994.2219 | 11860.2064 | 0.47898 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10162 | MADISON 210113372 | 63172101 | MADISON 2101 | 6152.1597 | 3.8236 | 5 | 0.85069 | 0.17014 | 436 | 4998.0455 | 11859.3557 | 0.47894 | 11859.3557 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4788 | COTTONWOOD 11039072 | 102931103 | COTTONWOOD 1103 | 46343.9208 | 28.8029 | 279 | 47.3736 | 0.1698 | 437 | 5026.8484 | 11811.9821 | 0.47703 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10660 | CLAYTON 2212334476 | 12022212 | CLAYTON 2212 | 89.9428 | 0.0559 | 2 | 0.33922 | 0.16961 | 438 | 5026.9043 | 11811.6428 | 0.47701 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5708 | HARTLEY 1101658 | 43211101 | HARTLEY 1101 | 4561.1197 | 2.8348 | 136 | 23.042 | 0.16943 | 439 | 5029.7391 | 11788.6009 | 0.47608 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
52 | HIGHLANDS 1103520 | 43361103 | HIGHLANDS 1103 | 75123.246 | 46.6894 | 437 | 73.9165 | 0.16915 | 440 | 5076.4285 | 11714.6843 | 0.4731 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5485 | ZACA 1102CB | 182681102 | ZACA 1102 | 25226.3338 | 15.6783 | 190 | 32.1248 | 0.16908 | 441 | 5092.1067 | 11682.5595 | 0.4718 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2709 | CHOLAME 2102X10 | 182562102 | CHOLAME 2102 | 34475.596 | 21.4267 | 156 | 26.3532 | 0.16893 | 442 | 5113.5335 | 11656.2063 | 0.47074 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2509 | HIGGINS 111051794 | 152691110 | HIGGINS 1110 | 6303.8446 | 3.9179 | 32 | 5.4026 | 0.16883 | 443 | 5117.4513 | 11650.8036 | 0.47052 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3144 | MORGAN HILL 2105XR564 | 83242105 | MORGAN HILL 2105 | 9126.8572 | 5.6724 | 81 | 13.6018 | 0.16792 | 444 | 5123.1237 | 11637.2018 | 0.46997 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8832 | PEORIA 17046090 | 163781704 | PEORIA 1704 | 879.5421 | 0.54664 | 10 | 1.6726 | 0.16726 | 445 | 5123.6703 | 11635.5292 | 0.4699 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6712 | CORNING 110182846 | 103331101 | CORNING 1101 | 7626.8316 | 4.7401 | 61 | 10.1421 | 0.16626 | 446 | 5128.4104 | 11625.3871 | 0.46949 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3069 | NARROWS 21052228 | 153132105 | NARROWS 2105 | 33727.1471 | 20.9616 | 199 | 33.0243 | 0.16595 | 447 | 5149.372 | 11592.3628 | 0.46816 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10116 | SANTA YNEZ 1104117616 | 182721104 | SANTA YNEZ 1104 | 298.3487 | 0.18542 | 5 | 0.82819 | 0.16564 | 448 | 5149.5574 | 11591.5346 | 0.46812 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10070 | SILVERADO 2102772792 | 43432102 | SILVERADO 2102 | 3782.0495 | 2.3506 | 19 | 3.1366 | 0.16509 | 449 | 5151.908 | 11588.398 | 0.468 | 11588.398 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6113 | MIDDLETOWN 1101439572 | 43141101 | MIDDLETOWN 1101 | 1977.3978 | 1.229 | 18 | 2.9663 | 0.16479 | 450 | 5153.1369 | 11585.4317 | 0.46788 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1940 | NORTH BRANCH 1101TS1115 | 163231101 | NORTH BRANCH 1101 | 28340.5083 | 17.6137 | 147 | 24.1996 | 0.16462 | 451 | 5170.7507 | 11561.2321 | 0.4669 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7043 | ANDERSON 1101514412 | 103261101 | ANDERSON 1101 | 1659.5168 | 1.0314 | 5 | 0.82024 | 0.16405 | 452 | 5171.7821 | 11560.4118 | 0.46687 | 11560.4118 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7318 | PUEBLO 2102226562 | 43292102 | PUEBLO 2102 | 1371.9928 | 0.8527 | 7 | 1.1482 | 0.16403 | 453 | 5172.6348 | 11559.2636 | 0.46682 | 11559.2636 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9693 | WILDWOOD 110198896 | 103611101 | WILDWOOD 1101 | 8090.5275 | 5.0283 | 25 | 4.1004 | 0.16402 | 454 | 5177.6631 | 11555.1632 | 0.46666 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8907 | SHINGLE SPRINGS 1103CB | 153651103 | SHINGLE SPRINGS 1103 | 10648.1095 | 6.6178 | 143 | 23.42 | 0.16378 | 455 | 5184.2809 | 11531.7432 | 0.46571 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3737 | KESWICK 110148480 | 103451101 | KESWICK 1101 | 16927.9852 | 10.5208 | 125 | 20.4433 | 0.16355 | 456 | 5194.8017 | 11511.2999 | 0.46488 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9178 | CORNING 1102915324 | 103331102 | CORNING 1102 | 3584.8296 | 2.228 | 27 | 4.406 | 0.16319 | 457 | 5197.0297 | 11506.8939 | 0.46471 | 11506.8939 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9985 | BOLINAS 1101530 | 42261101 | BOLINAS 1101 | 17644.1656 | 10.9659 | 23 | 3.7427 | 0.16273 | 458 | 5207.9956 | 11503.1512 | 0.46456 | 11503.1512 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10086 | NAPA 1102561208 | 42021102 | NAPA 1102 | 1347.5454 | 0.8375 | 15 | 2.439 | 0.1626 | 459 | 5208.8331 | 11500.7122 | 0.46446 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7995 | HOPLAND 110194006 | 42251101 | HOPLAND 1101 | 22341.6897 | 13.8855 | 112 | 18.2107 | 0.1626 | 460 | 5222.7186 | 11482.5015 | 0.46372 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5192 | HIGHLANDS 1103CB | 43361103 | HIGHLANDS 1103 | 17048.207 | 10.5955 | 144 | 23.3827 | 0.16238 | 461 | 5233.3141 | 11459.1188 | 0.46278 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10927 | SCE REFUGIO 1701CB | 188071701 | SCE REFUGIO 1701 | 3.6129 | 0.0022454 | 1 | 0.16185 | 0.16185 | 462 | 5233.3164 | 11458.957 | 0.46277 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1961 | NARROWS 210534069 | 153132105 | NARROWS 2105 | 25331.8473 | 15.7438 | 156 | 25.1758 | 0.16138 | 463 | 5249.0602 | 11433.7812 | 0.46175 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11018 | CLAY 110398680 | 163341103 | CLAY 1103 | 46.5973 | 0.02896 | 1 | 0.16135 | 0.16135 | 464 | 5249.0892 | 11433.6198 | 0.46175 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5283 | ANDERSON 11011752 | 103261101 | ANDERSON 1101 | 13551.3973 | 8.4222 | 96 | 15.4521 | 0.16096 | 465 | 5257.5114 | 11418.1677 | 0.46112 | 11418.1677 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4672 | LOW GAP 110137498 | 192411101 | LOW GAP 1101 | 26197.7415 | 16.282 | 129 | 20.7336 | 0.16073 | 466 | 5273.7934 | 11397.4341 | 0.46029 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1841 | NARROWS 21057203 | 153132105 | NARROWS 2105 | 29904.6733 | 18.5859 | 197 | 31.6051 | 0.16043 | 467 | 5292.3793 | 11365.8291 | 0.45901 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
652 | MIDDLETOWN 110148212 | 43141101 | MIDDLETOWN 1101 | 17215.2669 | 10.6994 | 110 | 17.6327 | 0.1603 | 468 | 5303.0787 | 11348.1963 | 0.4583 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1128 | SAN MIGUEL 1106605393 | 182661106 | SAN MIGUEL 1106 | 33375.8865 | 20.7432 | 119 | 19.0373 | 0.15998 | 469 | 5323.8219 | 11329.1591 | 0.45753 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3473 | COTTONWOOD 11011610 | 102931101 | COTTONWOOD 1101 | 61821.9357 | 38.4226 | 295 | 47.1875 | 0.15996 | 470 | 5362.2445 | 11281.9716 | 0.45562 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1571 | SAN MIGUEL 1106428314 | 182661106 | SAN MIGUEL 1106 | 23673.0872 | 14.7129 | 73 | 11.675 | 0.15993 | 471 | 5376.9574 | 11270.2966 | 0.45515 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6359 | FROGTOWN 1702592404 | 163451702 | FROGTOWN 1702 | 2642.3361 | 1.6422 | 20 | 3.1926 | 0.15963 | 472 | 5378.5996 | 11267.104 | 0.45502 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7337 | WYANDOTTE 110738438 | 102911107 | WYANDOTTE 1107 | 27128.309 | 16.8604 | 181 | 28.8637 | 0.15947 | 473 | 5395.46 | 11238.2402 | 0.45386 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
932 | MIDDLETOWN 1101548 | 43141101 | MIDDLETOWN 1101 | 44099.7789 | 27.4082 | 298 | 47.4878 | 0.15935 | 474 | 5422.8682 | 11190.7525 | 0.45194 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9379 | SUNOL 11018721 | 14241101 | SUNOL 1101 | 4400.8399 | 2.7351 | 29 | 4.6198 | 0.1593 | 475 | 5425.6033 | 11186.1327 | 0.45175 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1763 | RED BLUFF 110451238 | 103541104 | RED BLUFF 1104 | 63137.7388 | 39.2404 | 335 | 53.3509 | 0.15926 | 476 | 5464.8437 | 11132.7818 | 0.4496 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1814 | CLOVERDALE 110184088 | 42821101 | CLOVERDALE 1101 | 25963.7603 | 16.1366 | 127 | 20.1391 | 0.15858 | 477 | 5480.9803 | 11112.6427 | 0.44878 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4306 | RAWSON 1103428534 | 103531103 | RAWSON 1103 | 7301.7326 | 4.5381 | 18 | 2.8474 | 0.15819 | 478 | 5485.5183 | 11109.7952 | 0.44867 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8922 | CLOVERDALE 1101964556 | 42821101 | CLOVERDALE 1101 | 8116.5647 | 5.0445 | 31 | 4.8988 | 0.15803 | 479 | 5490.5628 | 11104.8964 | 0.44847 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7447 | BELL 1109CB | 152701109 | BELL 1109 | 484.8416 | 0.30133 | 53 | 8.3708 | 0.15794 | 480 | 5490.8641 | 11096.5256 | 0.44813 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5391 | FITCH MOUNTAIN 111324918 | 42751113 | FITCH MOUNTAIN 1113 | 8843.8557 | 5.4965 | 49 | 7.7177 | 0.1575 | 481 | 5496.3606 | 11088.8079 | 0.44782 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6800 | GEYSERVILLE 1101705777 | 42891101 | GEYSERVILLE 1101 | 9890.0744 | 6.1467 | 46 | 7.2434 | 0.15746 | 482 | 5502.5073 | 11081.5646 | 0.44753 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
29 | CALPELLA 1101542 | 43411101 | CALPELLA 1101 | 53958.2006 | 33.5352 | 311 | 48.9707 | 0.15746 | 483 | 5536.0426 | 11032.5939 | 0.44555 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9538 | PIT NO 1 1101CB | 103721101 | PIT NO 1 1101 | 10535.3716 | 6.5478 | 40 | 6.2822 | 0.15705 | 484 | 5542.5904 | 11026.3117 | 0.4453 | 11026.3117 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7813 | CLOVERDALE 1102383183 | 42821102 | CLOVERDALE 1102 | 23566.6207 | 14.6467 | 53 | 8.3141 | 0.15687 | 485 | 5557.2371 | 11017.9977 | 0.44496 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8188 | LAKEVILLE 1102152632 | 43371102 | LAKEVILLE 1102 | 3099.3949 | 1.9263 | 13 | 2.0385 | 0.15681 | 486 | 5559.1634 | 11015.9592 | 0.44488 | 11015.9592 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5065 | WOODACRE 11011456 | 43021101 | WOODACRE 1101 | 6155.4627 | 3.8256 | 46 | 7.1739 | 0.15596 | 487 | 5562.989 | 11008.7852 | 0.44459 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5726 | POINT MORETTI 11015104 | 82931101 | POINT MORETTI 1101 | 2898.3737 | 1.8014 | 11 | 1.7137 | 0.15579 | 488 | 5564.7904 | 11007.0715 | 0.44452 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3142 | MOLINO 110279306 | 42571102 | MOLINO 1102 | 6087.9659 | 3.7837 | 73 | 11.352 | 0.15551 | 489 | 5568.5741 | 10995.7194 | 0.44406 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10072 | BALCH NO 1 1101R372 | 252501101 | BALCH NO 1 1101 | 6703.9319 | 4.1665 | 14 | 2.1754 | 0.15539 | 490 | 5572.7406 | 10993.544 | 0.44397 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1776 | TIVY VALLEY 1107869946 | 252941107 | TIVY VALLEY 1107 | 47850.9 | 29.7395 | 197 | 30.6024 | 0.15534 | 491 | 5602.4801 | 10962.9417 | 0.44274 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9099 | BELL 1110946229 | 152701110 | BELL 1110 | 352.3912 | 0.21901 | 27 | 4.1819 | 0.15489 | 492 | 5602.6991 | 10958.7597 | 0.44257 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11045 | CLARK ROAD 1101CB | 103091101 | CLARK ROAD 1101 | 28.7495 | 0.017868 | 2 | 0.30929 | 0.15464 | 493 | 5602.717 | 10958.4504 | 0.44256 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1243 | SHINGLE SPRINGS 110419502 | 153651104 | SHINGLE SPRINGS 1104 | 72356.9682 | 44.9701 | 672 | 103.8019 | 0.15447 | 494 | 5647.6872 | 10854.6485 | 0.43837 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3579 | WILLITS 1102CB | 42661102 | WILLITS 1102 | 8550.61 | 5.3142 | 114 | 17.5695 | 0.15412 | 495 | 5653.0014 | 10837.0791 | 0.43766 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6413 | UKIAH 1114408 | 42771114 | UKIAH 1114 | 60046.2209 | 37.319 | 280 | 43.1236 | 0.15401 | 496 | 5690.3204 | 10793.9554 | 0.43591 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4125 | SAND CREEK 11037420 | 254601103 | SAND CREEK 1103 | 37320.8645 | 23.1951 | 263 | 40.4954 | 0.15397 | 497 | 5713.5154 | 10753.4601 | 0.43428 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6897 | SALMON CREEK 110188998 | 43161101 | SALMON CREEK 1101 | 12794.9324 | 7.9521 | 116 | 17.8079 | 0.15352 | 498 | 5721.4675 | 10735.6522 | 0.43356 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4452 | SILVERADO 2102942170 | 43432102 | SILVERADO 2102 | 5038.647 | 3.1315 | 99 | 15.1945 | 0.15348 | 499 | 5724.5991 | 10720.4577 | 0.43295 | 10720.4577 | #N/A | #N/A | #N/A | #N/A | #VALUE!
59 | VACAVILLE 1111CB | 63601111 | VACAVILLE 1111 | 11777.3852 | 7.3197 | 154 | 23.6178 | 0.15336 | 500 | 5731.9188 | 10696.8399 | 0.43199 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5605 | SANTA YNEZ 1101Y52 | 182721101 | SANTA YNEZ 1101 | 31529.2091 | 19.5955 | 141 | 21.6184 | 0.15332 | 501 | 5751.5143 | 10675.2215 | 0.43112 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4437 | STILLWATER 1102CB | 103561102 | STILLWATER 1102 | 40301.3395 | 25.0474 | 275 | 42.1242 | 0.15318 | 502 | 5776.5617 | 10633.0973 | 0.42942 | 10633.0973 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3264 | BEAR VALLEY 21059480 | 252192105 | BEAR VALLEY 2105 | 19971.3977 | 12.4123 | 80 | 12.251 | 0.15314 | 503 | 5788.974 | 10620.8463 | 0.42892 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1519 | FROGTOWN 17021573 | 163451702 | FROGTOWN 1702 | 29066.997 | 18.0653 | 156 | 23.8402 | 0.15282 | 504 | 5807.0393 | 10597.0062 | 0.42796 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1732 | NARROWS 21022220 | 153132102 | NARROWS 2102 | 44226.4373 | 27.4869 | 266 | 40.5244 | 0.15235 | 505 | 5834.5262 | 10556.4817 | 0.42632 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2529 | FULTON 1102287172 | 42561102 | FULTON 1102 | 32888.5181 | 20.4403 | 258 | 39.2578 | 0.15216 | 506 | 5854.9666 | 10517.2239 | 0.42474 | 10517.2239 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9038 | OTTER 11022012 | 182941102 | OTTER 1102 | 14813.8509 | 9.2069 | 64 | 9.7211 | 0.15189 | 507 | 5864.1734 | 10507.5028 | 0.42435 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6205 | OILFIELDS 1103N48 | 182391103 | OILFIELDS 1103 | 76703.6711 | 47.6716 | 292 | 44.3489 | 0.15188 | 508 | 5911.8451 | 10463.1538 | 0.42256 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6912 | BANGOR 1101301886 | 103191101 | BANGOR 1101 | 4239.6365 | 2.635 | 90 | 13.6484 | 0.15165 | 509 | 5914.48 | 10449.5055 | 0.422 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10865 | PASO ROBLES 1103N04 | 182611103 | PASO ROBLES 1103 | 859.5841 | 0.53424 | 4 | 0.60641 | 0.1516 | 510 | 5915.0143 | 10448.899 | 0.42198 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10126 | WINDSOR 1103701650 | 43501103 | WINDSOR 1103 | 1191.0562 | 0.74025 | 12 | 1.8191 | 0.15159 | 511 | 5915.7545 | 10447.0799 | 0.42191 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2118 | LUCERNE 11031280 | 43351103 | LUCERNE 1103 | 12933.8174 | 8.0384 | 238 | 35.9845 | 0.1512 | 512 | 5923.7929 | 10411.0954 | 0.42045 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7467 | CORRAL 110214026 | 162991102 | CORRAL 1102 | 16308.5206 | 10.1358 | 101 | 15.2344 | 0.15084 | 513 | 5933.9287 | 10395.861 | 0.41984 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2447 | SAN LUIS OBISPO 110342344 | 182631103 | SAN LUIS OBISPO 1103 | 15185.6709 | 9.438 | 123 | 18.5441 | 0.15077 | 514 | 5943.3667 | 10377.3169 | 0.41909 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9162 | PUTAH CREEK 1105748272 | 63681105 | PUTAH CREEK 1105 | 1206.1255 | 0.74961 | 26 | 3.9074 | 0.15028 | 515 | 5944.1163 | 10373.4095 | 0.41893 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6146 | PETALUMA C 1108618 | 42631108 | PETALUMA C 1108 | 13890.2601 | 8.6329 | 119 | 17.8498 | 0.15 | 516 | 5952.7492 | 10355.5597 | 0.41821 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7759 | BUELLTON 1101Y26 | 183041101 | BUELLTON 1101 | 24411.1885 | 15.1717 | 133 | 19.8785 | 0.14946 | 517 | 5967.9208 | 10335.6812 | 0.41741 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8614 | WILLOW CREEK 110237374 | 192171102 | WILLOW CREEK 1102 | 3616.7474 | 2.2478 | 9 | 1.3444 | 0.14938 | 518 | 5970.1686 | 10334.3367 | 0.41735 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1351 | FULTON 11024522 | 42561102 | FULTON 1102 | 14178.9489 | 8.8123 | 128 | 19.0963 | 0.14919 | 519 | 5978.9809 | 10315.2405 | 0.41658 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5116 | APPLE HILL 210251792 | 153662102 | APPLE HILL 2102 | 15055.1772 | 9.3569 | 99 | 14.7646 | 0.14914 | 520 | 5988.3378 | 10300.4759 | 0.41599 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2803 | ZACA 1102Y48 | 182681102 | ZACA 1102 | 7064.3192 | 4.3905 | 157 | 23.4041 | 0.14907 | 521 | 5992.7283 | 10277.0719 | 0.41504 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
453 | GARBERVILLE 11011604 | 192221101 | GARBERVILLE 1101 | 6733.9297 | 4.1852 | 166 | 24.7419 | 0.14905 | 522 | 5996.9134 | 10252.33 | 0.41404 | 10252.33 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10386 | CALISTOGA 1101537148 | 42711101 | CALISTOGA 1101 | 923.0762 | 0.5737 | 14 | 2.0863 | 0.14902 | 523 | 5997.4871 | 10250.2436 | 0.41396 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1087 | GRASS VALLEY 11032180 | 152031103 | GRASS VALLEY 1103 | 71112.0664 | 44.1964 | 444 | 66.0238 | 0.1487 | 524 | 6041.6836 | 10184.2198 | 0.41129 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6232 | POSO MOUNTAIN 21012181 | 253642101 | POSO MOUNTAIN 2101 | 27116.6383 | 16.8531 | 120 | 17.8426 | 0.14869 | 525 | 6058.5367 | 10166.3773 | 0.41057 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1083 | CLARK ROAD 11022044 | 103091102 | CLARK ROAD 1102 | 13688.923 | 8.5077 | 67 | 9.9595 | 0.14865 | 526 | 6067.0444 | 10156.4177 | 0.41017 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1119 | MERCED FALLS 110287352 | 252811102 | MERCED FALLS 1102 | 42830.7404 | 26.6195 | 215 | 31.9523 | 0.14862 | 527 | 6093.6639 | 10124.4654 | 0.40888 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3359 | WISE 1102307494 | 152271102 | WISE 1102 | 49958.7477 | 31.0496 | 279 | 41.4062 | 0.14841 | 528 | 6124.7134 | 10083.0592 | 0.4072 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8461 | PUTAH CREEK 110264044 | 63681102 | PUTAH CREEK 1102 | 9649.0485 | 5.9969 | 46 | 6.8236 | 0.14834 | 529 | 6130.7103 | 10076.2356 | 0.40693 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7436 | MENLO 110212249 | 24131102 | MENLO 1102 | 3869.5175 | 2.4049 | 25 | 3.7065 | 0.14826 | 530 | 6133.1153 | 10072.5291 | 0.40678 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
170 | NORTH BRANCH 110111206 | 163231101 | NORTH BRANCH 1101 | 28782.1678 | 17.8882 | 146 | 21.5893 | 0.14787 | 531 | 6151.0035 | 10050.9398 | 0.40591 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2440 | VOLTA 110180454 | 102541101 | VOLTA 1101 | 51220.5161 | 31.8338 | 254 | 37.5574 | 0.14786 | 532 | 6182.8373 | 10013.3824 | 0.40439 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6322 | SALMON CREEK 1101196 | 43161101 | SALMON CREEK 1101 | 9030.0657 | 5.6122 | 36 | 5.3118 | 0.14755 | 533 | 6188.4495 | 10008.0706 | 0.40418 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6558 | MOLINO 110266006 | 42571102 | MOLINO 1102 | 14550.7056 | 9.0433 | 98 | 14.4519 | 0.14747 | 534 | 6197.4928 | 9993.6188 | 0.40359 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6860 | GARBERVILLE 1101CB | 192221101 | GARBERVILLE 1101 | 11300.0596 | 7.023 | 87 | 12.8257 | 0.14742 | 535 | 6204.5158 | 9980.793 | 0.40307 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2892 | WYANDOTTE 11071026 | 102911107 | WYANDOTTE 1107 | 36171.5421 | 22.4808 | 273 | 40.2177 | 0.14732 | 536 | 6226.9966 | 9940.5753 | 0.40145 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1817 | COARSEGOLD 210410110 | 254432104 | COARSEGOLD 2104 | 79840.1784 | 49.621 | 518 | 76.1986 | 0.1471 | 537 | 6276.6176 | 9864.3767 | 0.39837 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5315 | GIRVAN 11011636 | 103401101 | GIRVAN 1101 | 29071.18 | 18.0679 | 200 | 29.387 | 0.14693 | 538 | 6294.6854 | 9834.9897 | 0.39719 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7739 | OILFIELDS 1103N40 | 182391103 | OILFIELDS 1103 | 4628.046 | 2.8763 | 23 | 3.3766 | 0.14681 | 539 | 6297.5618 | 9831.6131 | 0.39705 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1598 | COTTONWOOD 11031348 | 102931103 | COTTONWOOD 1103 | 46964.6472 | 29.1887 | 357 | 52.3583 | 0.14666 | 540 | 6326.7505 | 9779.2548 | 0.39494 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2008 | OAKHURST 11015490 | 254421101 | OAKHURST 1101 | 40241.3391 | 25.0102 | 276 | 40.4521 | 0.14657 | 541 | 6351.7607 | 9738.8027 | 0.3933 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6294 | OLETA 1101239062 | 163541101 | OLETA 1101 | 19618.6008 | 12.193 | 113 | 16.5367 | 0.14634 | 542 | 6363.9537 | 9722.266 | 0.39263 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6920 | LAYTONVILLE 110268436 | 42681102 | LAYTONVILLE 1102 | 14664.9715 | 9.1143 | 45 | 6.582 | 0.14627 | 543 | 6373.068 | 9715.684 | 0.39237 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1698 | GARBERVILLE 11022010 | 192221102 | GARBERVILLE 1102 | 10727.9171 | 6.6674 | 39 | 5.6882 | 0.14585 | 544 | 6379.7355 | 9709.9958 | 0.39214 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2911 | SHINGLE SPRINGS 210819762 | 153652108 | SHINGLE SPRINGS 2108 | 7078.7756 | 4.3995 | 72 | 10.4755 | 0.14549 | 545 | 6384.135 | 9699.5204 | 0.39172 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2598 | ELK CREEK 11012008 | 102781101 | ELK CREEK 1101 | 9225.9589 | 5.734 | 154 | 22.3567 | 0.14517 | 546 | 6389.8689 | 9677.1637 | 0.39081 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2127 | OILFIELDS 1103N44 | 182391103 | OILFIELDS 1103 | 29207.7388 | 18.1527 | 109 | 15.8008 | 0.14496 | 547 | 6408.0217 | 9661.3629 | 0.39017 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
381 | MOUNTAIN QUARRIES 21011102 | 152282101 | MOUNTAIN QUARRIES 2101 | 69889.6015 | 43.4367 | 431 | 62.4048 | 0.14479 | 548 | 6451.4583 | 9598.9582 | 0.38765 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3913 | CORNING 110164090 | 103331101 | CORNING 1101 | 21993.72 | 13.6692 | 170 | 24.5486 | 0.1444 | 549 | 6465.1275 | 9574.4096 | 0.38666 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2481 | BROWNS VALLEY 11011268 | 152921101 | BROWNS VALLEY 1101 | 17538.5447 | 10.9003 | 106 | 15.3013 | 0.14435 | 550 | 6476.0278 | 9559.1083 | 0.38605 | 9559.1083 | #N/A | #N/A | #N/A | #N/A | #VALUE!
948 | MARIPOSA 21029590 | 254452102 | MARIPOSA 2102 | 58387.0707 | 36.2878 | 387 | 55.7277 | 0.144 | 551 | 6512.3156 | 9503.3806 | 0.38379 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4109 | TEMPLETON 2113A60 | 183052113 | TEMPLETON 2113 | 11709.0954 | 7.2773 | 88 | 12.6644 | 0.14391 | 552 | 6519.5929 | 9490.7162 | 0.38328 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9361 | CLOVERDALE 1102429006 | 42821102 | CLOVERDALE 1102 | 3213.4446 | 1.9972 | 23 | 3.3029 | 0.1436 | 553 | 6521.59 | 9487.4133 | 0.38315 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
429 | COTTONWOOD 11021578 | 102931102 | COTTONWOOD 1102 | 48498.4276 | 30.142 | 269 | 38.6147 | 0.14355 | 554 | 6551.732 | 9448.7986 | 0.38159 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3755 | INDIAN FLAT 1104CB | 252691104 | INDIAN FLAT 1104 | 20557.4413 | 12.7765 | 85 | 12.1951 | 0.14347 | 555 | 6564.5085 | 9436.6035 | 0.3811 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5039 | OREGON TRAIL 11031448 | 103521103 | OREGON TRAIL 1103 | 49484.9793 | 30.7551 | 232 | 33.2848 | 0.14347 | 556 | 6595.2636 | 9403.3187 | 0.37975 | 9403.3187 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5385 | MONTICELLO 110137384 | 43051101 | MONTICELLO 1101 | 15082.1187 | 9.3736 | 71 | 10.17 | 0.14324 | 557 | 6604.6372 | 9393.1487 | 0.37934 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9323 | POSO MOUNTAIN 21013990 | 253642101 | POSO MOUNTAIN 2101 | 6963.5326 | 4.3279 | 25 | 3.5744 | 0.14297 | 558 | 6608.9651 | 9389.5744 | 0.3792 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8609 | PETALUMA C 1108636 | 42631108 | PETALUMA C 1108 | 15178.9816 | 9.4338 | 108 | 15.4213 | 0.14279 | 559 | 6618.3989 | 9374.1531 | 0.37858 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9301 | VOLTA 110165764 | 102541101 | VOLTA 1101 | 16669.4005 | 10.3601 | 34 | 4.8382 | 0.1423 | 560 | 6628.759 | 9369.3149 | 0.37838 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10478 | STONE CORRAL 1110189488 | 252921110 | STONE CORRAL 1110 | 1327.2585 | 0.8249 | 8 | 1.1369 | 0.14211 | 561 | 6629.5839 | 9368.178 | 0.37833 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1096 | CABRILLO 1103Y12 | 183101103 | CABRILLO 1103 | 42701.7878 | 26.5393 | 274 | 38.9225 | 0.14205 | 562 | 6656.1232 | 9329.2556 | 0.37676 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9878 | CEDAR CREEK 1101451856 | 103321101 | CEDAR CREEK 1101 | 105.147 | 0.065349 | 2 | 0.28345 | 0.14172 | 563 | 6656.1886 | 9328.9721 | 0.37675 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9745 | TASSAJARA 21126392 | 14662112 | TASSAJARA 2112 | 8838.9848 | 5.4935 | 37 | 5.2399 | 0.14162 | 564 | 6661.682 | 9323.7322 | 0.37654 | 9323.7322 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4697 | CALISTOGA 1101242919 | 42711101 | CALISTOGA 1101 | 2111.493 | 1.3123 | 15 | 2.1226 | 0.14151 | 565 | 6662.9943 | 9321.6095 | 0.37645 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5376 | FORT SEWARD 1121CB | 192321121 | FORT SEWARD 1121 | 14807.5224 | 9.2029 | 54 | 7.6353 | 0.14139 | 566 | 6672.1973 | 9313.9743 | 0.37615 | 9313.9743 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4876 | SISQUOC 1102M54 | 182811102 | SISQUOC 1102 | 31884.2274 | 19.8162 | 166 | 23.4289 | 0.14114 | 567 | 6692.0135 | 9290.5454 | 0.3752 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4881 | LINCOLN 11042070 | 153701104 | LINCOLN 1104 | 28951.6433 | 17.9936 | 303 | 42.7554 | 0.14111 | 568 | 6710.007 | 9247.7901 | 0.37347 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8866 | SAN RAMON 2101CB | 14232101 | SAN RAMON 2101 | 1277.3495 | 0.79388 | 11 | 1.5519 | 0.14108 | 569 | 6710.8009 | 9246.2382 | 0.37341 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10487 | HIGGINS 1107746082 | 152691107 | HIGGINS 1107 | 1306.1318 | 0.81177 | 6 | 0.84097 | 0.14016 | 570 | 6711.6127 | 9245.3972 | 0.37338 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3139 | WILLITS 11044650 | 42661104 | WILLITS 1104 | 6190.488 | 3.8474 | 80 | 11.2058 | 0.14007 | 571 | 6715.4601 | 9234.1914 | 0.37292 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
474 | COTTONWOOD 11031616 | 102931103 | COTTONWOOD 1103 | 75536.2374 | 46.9461 | 454 | 63.1735 | 0.13915 | 572 | 6762.4062 | 9171.0179 | 0.37037 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4424 | POSO MOUNTAIN 21014456 | 253642101 | POSO MOUNTAIN 2101 | 37862.2156 | 23.5315 | 102 | 14.1582 | 0.13881 | 573 | 6785.9377 | 9156.8597 | 0.3698 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7546 | LAYTONVILLE 11022502 | 42681102 | LAYTONVILLE 1102 | 28650.0789 | 17.8061 | 80 | 11.0874 | 0.13859 | 574 | 6803.7438 | 9145.7723 | 0.36935 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7849 | BEAR VALLEY 21014160 | 252192101 | BEAR VALLEY 2101 | 36723.9834 | 22.8241 | 192 | 26.57 | 0.13839 | 575 | 6826.5679 | 9119.2023 | 0.36828 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10064 | WILLOW PASS 1101152874 | 13911101 | WILLOW PASS 1101 | 982.3028 | 0.61051 | 10 | 1.3803 | 0.13803 | 576 | 6827.1784 | 9117.822 | 0.36822 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2621 | LINCOLN 1101186060 | 153701101 | LINCOLN 1101 | 17542.5963 | 10.9028 | 161 | 22.1085 | 0.13732 | 577 | 6838.0812 | 9095.7135 | 0.36733 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5254 | SHINGLE SPRINGS 21092679 | 153652109 | SHINGLE SPRINGS 2109 | 11435.2637 | 7.1071 | 70 | 9.6123 | 0.13732 | 578 | 6845.1883 | 9086.1012 | 0.36694 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3959 | SILVERADO 210234959 | 43432102 | SILVERADO 2102 | 41473.2756 | 25.7758 | 205 | 27.9958 | 0.13657 | 579 | 6870.9641 | 9058.1054 | 0.36581 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4389 | VOLTA 11011516 | 102541101 | VOLTA 1101 | 40856.6045 | 25.3925 | 123 | 16.7471 | 0.13616 | 580 | 6896.3566 | 9041.3583 | 0.36514 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9812 | CURTIS 170411300 | 163351704 | CURTIS 1704 | 5912.6947 | 3.6748 | 41 | 5.5803 | 0.1361 | 581 | 6900.0314 | 9035.778 | 0.36491 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4676 | NARROWS 210551582 | 153132105 | NARROWS 2105 | 15330.2671 | 9.5278 | 105 | 14.2523 | 0.13574 | 582 | 6909.5592 | 9021.5257 | 0.36433 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
430 | TEJON 1102732836 | 252931102 | TEJON 1102 | 18788.6293 | 11.6772 | 154 | 20.8364 | 0.1353 | 583 | 6921.2364 | 9000.6893 | 0.36349 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4932 | MONTICELLO 1101720 | 43051101 | MONTICELLO 1101 | 10923.6575 | 6.7891 | 70 | 9.4707 | 0.1353 | 584 | 6928.0255 | 8991.2186 | 0.36311 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6310 | RIO DELL 11024230 | 192251102 | RIO DELL 1102 | 36847.6248 | 22.9009 | 59 | 7.9721 | 0.13512 | 585 | 6950.9265 | 8983.2465 | 0.36279 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
517 | CLARKSVILLE 210413352 | 153612104 | CLARKSVILLE 2104 | 55896.819 | 34.7401 | 409 | 55.1568 | 0.13486 | 586 | 6985.6666 | 8928.0897 | 0.36056 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7402 | MARIPOSA 2102594143 | 254452102 | MARIPOSA 2102 | 814.5641 | 0.50625 | 60 | 8.0769 | 0.13461 | 587 | 6986.1728 | 8920.0128 | 0.36024 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
19 | CLEAR LAKE 1101406 | 42141101 | CLEAR LAKE 1101 | 19984.6537 | 12.4205 | 312 | 41.9011 | 0.1343 | 588 | 6998.5934 | 8878.1117 | 0.35854 | 8878.1117 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4720 | DUNLAP 11027849F | 254061102 | DUNLAP 1102 | 13949.6344 | 8.6698 | 61 | 8.1711 | 0.13395 | 589 | 7007.2631 | 8869.9406 | 0.35821 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6125 | JESSUP 1103348657 | 103441103 | JESSUP 1103 | 3253.8359 | 2.0223 | 29 | 3.8825 | 0.13388 | 590 | 7009.2854 | 8866.0581 | 0.35806 | 8866.0581 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9100 | BANGOR 1101870548 | 103191101 | BANGOR 1101 | 8185.9487 | 5.0876 | 56 | 7.4625 | 0.13326 | 591 | 7014.373 | 8858.5956 | 0.35775 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7774 | RED BLUFF 110176020 | 103541101 | RED BLUFF 1101 | 15031.7581 | 9.3423 | 137 | 18.2456 | 0.13318 | 592 | 7023.7153 | 8840.35 | 0.35702 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5975 | HARTLEY 11011306 | 43211101 | HARTLEY 1101 | 15260.277 | 9.4843 | 117 | 15.5648 | 0.13303 | 593 | 7033.1996 | 8824.7852 | 0.35639 | 8824.7852 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3100 | GARBERVILLE 11022540 | 192221102 | GARBERVILLE 1102 | 26122.3431 | 16.2351 | 135 | 17.9496 | 0.13296 | 594 | 7049.4348 | 8806.8356 | 0.35566 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9542 | OLETA 1102CB | 163541102 | OLETA 1102 | 596.6183 | 0.3708 | 11 | 1.4601 | 0.13274 | 595 | 7049.8056 | 8805.3755 | 0.35561 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6900 | SALT SPRINGS 210110416 | 163692101 | SALT SPRINGS 2101 | 1110.1976 | 0.68999 | 7 | 0.92748 | 0.1325 | 596 | 7050.4956 | 8804.448 | 0.35557 | 8804.448 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1019 | HOPLAND 1101770 | 42251101 | HOPLAND 1101 | 13838.1959 | 8.6005 | 110 | 14.5382 | 0.13217 | 597 | 7059.096 | 8789.9098 | 0.35498 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9774 | WILDWOOD 1101384582 | 103611101 | WILDWOOD 1101 | 7304.3535 | 4.5397 | 8 | 1.0547 | 0.13184 | 598 | 7063.6357 | 8788.8551 | 0.35494 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6290 | WYANDOTTE 110796390 | 102911107 | WYANDOTTE 1107 | 13753.525 | 8.5479 | 124 | 16.2749 | 0.13125 | 599 | 7072.1836 | 8772.5802 | 0.35428 | 8772.5802 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8217 | VINEYARD 2110CB | 14502110 | VINEYARD 2110 | 8994.5064 | 5.5901 | 86 | 11.2491 | 0.1308 | 600 | 7077.7737 | 8761.3311 | 0.35383 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7155 | PEORIA 1701CB | 163781701 | PEORIA 1701 | 14117.7933 | 8.7743 | 70 | 9.1442 | 0.13063 | 601 | 7086.548 | 8752.1869 | 0.35346 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1707 | HIGGINS 11039753 | 152691103 | HIGGINS 1103 | 3306.1166 | 2.0548 | 23 | 3.0036 | 0.13059 | 602 | 7088.6028 | 8749.1833 | 0.35334 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10679 | COVELO 1101627416 | 43061101 | COVELO 1101 | 971.5124 | 0.6038 | 14 | 1.8234 | 0.13024 | 603 | 7089.2066 | 8747.3599 | 0.35326 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2248 | CORRAL 110313474 | 162991103 | CORRAL 1103 | 4726.1259 | 2.9373 | 99 | 12.8713 | 0.13001 | 604 | 7092.1439 | 8734.4886 | 0.35274 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6056 | MARIPOSA 2101309438 | 254452101 | MARIPOSA 2101 | 5938.6322 | 3.6909 | 93 | 12.0584 | 0.12966 | 605 | 7095.8347 | 8722.4301 | 0.35226 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5806 | COLUMBIA HILL 11012212 | 152471101 | COLUMBIA HILL 1101 | 14695.9754 | 9.1336 | 76 | 9.8207 | 0.12922 | 606 | 7104.9684 | 8712.6094 | 0.35186 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5628 | PUEBLO 11041304 | 43291104 | PUEBLO 1104 | 30935.6957 | 19.2267 | 175 | 22.578 | 0.12902 | 607 | 7124.195 | 8690.0314 | 0.35095 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5578 | VASCO 1102886522 | 13751102 | VASCO 1102 | 10908.527 | 6.7797 | 154 | 19.8644 | 0.12899 | 608 | 7130.9747 | 8670.167 | 0.35015 | 8670.167 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2390 | WYANDOTTE 11091520 | 102911109 | WYANDOTTE 1109 | 6700.2969 | 4.1643 | 230 | 29.6011 | 0.1287 | 609 | 7135.139 | 8640.5659 | 0.34895 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2104 | LINCOLN 11045391 | 153701104 | LINCOLN 1104 | 1530.1829 | 0.95101 | 7 | 0.90075 | 0.12868 | 610 | 7136.09 | 8639.6651 | 0.34891 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
826 | TASSAJARA 210419042 | 14662104 | TASSAJARA 2104 | 10069.7209 | 6.2584 | 89 | 11.4466 | 0.12861 | 611 | 7142.3484 | 8628.2185 | 0.34845 | 8628.2185 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7172 | FITCH MOUNTAIN 1113356 | 42751113 | FITCH MOUNTAIN 1113 | 17245.1485 | 10.7179 | 136 | 17.4723 | 0.12847 | 612 | 7153.0663 | 8610.7463 | 0.34775 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
761 | BANGOR 11017446 | 103191101 | BANGOR 1101 | 69991.8942 | 43.5002 | 427 | 54.7764 | 0.12828 | 613 | 7196.5665 | 8555.9699 | 0.34553 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9800 | CALISTOGA 110135588 | 42711101 | CALISTOGA 1101 | 4954.8551 | 3.0795 | 18 | 2.3016 | 0.12786 | 614 | 7199.646 | 8553.6683 | 0.34544 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9664 | PASO ROBLES 110359763 | 182611103 | PASO ROBLES 1103 | 4532.1933 | 2.8168 | 30 | 3.8149 | 0.12716 | 615 | 7202.4628 | 8549.8533 | 0.34529 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5583 | RED BLUFF 11031702 | 103541103 | RED BLUFF 1103 | 26958.2044 | 16.7546 | 177 | 22.5069 | 0.12716 | 616 | 7219.2174 | 8527.3465 | 0.34438 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4955 | WILLITS 1104188268 | 42661104 | WILLITS 1104 | 6867.4982 | 4.2682 | 66 | 8.3425 | 0.1264 | 617 | 7223.4856 | 8519.004 | 0.34404 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9342 | SAND CREEK 11037823F | 254601103 | SAND CREEK 1103 | 7527.4054 | 4.6783 | 49 | 6.1917 | 0.12636 | 618 | 7228.1639 | 8512.8123 | 0.34379 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7895 | PEORIA 1704877670 | 163781704 | PEORIA 1704 | 10595.2996 | 6.585 | 28 | 3.5352 | 0.12626 | 619 | 7234.7489 | 8509.2772 | 0.34365 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1593 | MENLO 1102W80 | 24131102 | MENLO 1102 | 30491.2345 | 18.9504 | 129 | 16.2519 | 0.12598 | 620 | 7253.6993 | 8493.0253 | 0.34299 | 8493.0253 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9134 | SAN LUIS OBISPO 1104350030 | 182631104 | SAN LUIS OBISPO 1104 | 9325.238 | 5.7957 | 107 | 13.4795 | 0.12598 | 621 | 7259.495 | 8479.5457 | 0.34245 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10634 | EDENVALE 2107288980 | 82952107 | EDENVALE 2107 | 532.3299 | 0.33085 | 6 | 0.75188 | 0.12531 | 622 | 7259.8259 | 8478.7939 | 0.34242 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8835 | SOLEDAD 2102955138 | 182052102 | SOLEDAD 2102 | 4227.5124 | 2.6274 | 16 | 2.0024 | 0.12515 | 623 | 7262.4533 | 8476.7915 | 0.34234 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6170 | GIRVAN 11011330 | 103401101 | GIRVAN 1101 | 49990.913 | 31.0696 | 264 | 33.0087 | 0.12503 | 624 | 7293.5228 | 8443.7828 | 0.341 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9760 | RINCON 11035152 | 43321103 | RINCON 1103 | 2685.0442 | 1.6688 | 17 | 2.1064 | 0.1239 | 625 | 7295.1916 | 8441.6764 | 0.34092 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6631 | HIGHLANDS 11031282 | 43361103 | HIGHLANDS 1103 | 22934.9277 | 14.2542 | 164 | 20.2971 | 0.12376 | 626 | 7309.4457 | 8421.3793 | 0.3401 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7124 | SANTA YNEZ 1102CB | 182721102 | SANTA YNEZ 1102 | 2348.085 | 1.4593 | 124 | 15.3456 | 0.12375 | 627 | 7310.9051 | 8406.0337 | 0.33948 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
547 | STILLWATER 11021644 | 103561102 | STILLWATER 1102 | 36747.479 | 22.8387 | 244 | 30.1941 | 0.12375 | 628 | 7333.7438 | 8375.8396 | 0.33826 | 8375.8396 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6046 | WOODWARD 210878448 | 255292108 | WOODWARD 2108 | 31387.7639 | 19.5076 | 188 | 23.2453 | 0.12365 | 629 | 7353.2514 | 8352.5943 | 0.33732 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7443 | GARBERVILLE 11011770 | 192221101 | GARBERVILLE 1101 | 13849.8333 | 8.6077 | 66 | 8.1457 | 0.12342 | 630 | 7361.8591 | 8344.4486 | 0.33699 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2056 | BUELLTON 1101Y06 | 183041101 | BUELLTON 1101 | 48855.5405 | 30.3639 | 304 | 37.4433 | 0.12317 | 631 | 7392.2231 | 8307.0054 | 0.33548 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1863 | DIAMOND SPRINGS 110610587 | 152261106 | DIAMOND SPRINGS 1106 | 35336.5514 | 21.9618 | 212 | 26.0703 | 0.12297 | 632 | 7414.1849 | 8280.9351 | 0.33443 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5060 | CLOVERDALE 1102156 | 42821102 | CLOVERDALE 1102 | 9919.8336 | 6.1652 | 110 | 13.4944 | 0.12268 | 633 | 7420.3501 | 8267.4407 | 0.33388 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8874 | BRIDGEVILLE 110169866 | 192461101 | BRIDGEVILLE 1101 | 10571.2356 | 6.5701 | 46 | 5.6379 | 0.12256 | 634 | 7426.9202 | 8261.8028 | 0.33365 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7200 | DIAMOND SPRINGS 1104705100 | 152261104 | DIAMOND SPRINGS 1104 | 11885.1942 | 7.3867 | 78 | 9.5341 | 0.12223 | 635 | 7434.3068 | 8252.2687 | 0.33327 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5273 | SAND CREEK 11037110 | 254601103 | SAND CREEK 1103 | 29983.2616 | 18.6347 | 132 | 16.0996 | 0.12197 | 636 | 7452.9416 | 8236.1691 | 0.33262 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3234 | FULTON 1107604 | 42561107 | FULTON 1107 | 28058.6741 | 17.4386 | 169 | 20.5661 | 0.12169 | 637 | 7470.3801 | 8215.603 | 0.33179 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8992 | TIDEWATER 2106781445 | 14652106 | TIDEWATER 2106 | 405.5365 | 0.25204 | 6 | 0.72871 | 0.12145 | 638 | 7470.6322 | 8214.8743 | 0.33176 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9503 | SAN LUIS OBISPO 1103153199 | 182631103 | SAN LUIS OBISPO 1103 | 4750.5459 | 2.9525 | 53 | 6.4339 | 0.1214 | 639 | 7473.5847 | 8208.4404 | 0.3315 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8489 | LAYTONVILLE 1102572 | 42681102 | LAYTONVILLE 1102 | 34429.3225 | 21.398 | 155 | 18.7503 | 0.12097 | 640 | 7494.9826 | 8189.6901 | 0.33074 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1408 | ATASCADERO 1103A16 | 182541103 | ATASCADERO 1103 | 31835.9088 | 19.7861 | 122 | 14.7476 | 0.12088 | 641 | 7514.7688 | 8174.9425 | 0.33015 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
68 | TEJON 11022455 | 252931102 | TEJON 1102 | 10165.5764 | 6.3179 | 84 | 10.1082 | 0.12034 | 642 | 7521.0867 | 8164.8343 | 0.32974 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6764 | MAXWELL 11053008 | 62881105 | MAXWELL 1105 | 13636.9493 | 8.4754 | 55 | 6.6112 | 0.1202 | 643 | 7529.5621 | 8158.2231 | 0.32947 | 8158.2231 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3997 | APPLE HILL 2102CB | 153662102 | APPLE HILL 2102 | 66423.2503 | 41.2823 | 448 | 53.7868 | 0.12006 | 644 | 7570.8445 | 8104.4363 | 0.3273 | 8104.4363 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4706 | WYANDOTTE 11031504 | 102911103 | WYANDOTTE 1103 | 17735.4007 | 11.0226 | 186 | 22.3307 | 0.12006 | 645 | 7581.8671 | 8082.1056 | 0.3264 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8185 | CLARKSVILLE 2109CB | 153612109 | CLARKSVILLE 2109 | 1593.4993 | 0.99037 | 15 | 1.7983 | 0.11989 | 646 | 7582.8575 | 8080.3073 | 0.32632 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5862 | HOLLISTER 2102855412 | 182492102 | HOLLISTER 2102 | 45702.3865 | 28.4042 | 108 | 12.9123 | 0.11956 | 647 | 7611.2617 | 8067.395 | 0.3258 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2833 | MARTELL 11033152 | 163011103 | MARTELL 1103 | 26923.3255 | 16.733 | 134 | 16.0208 | 0.11956 | 648 | 7627.9946 | 8051.3742 | 0.32516 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3141 | DIAMOND SPRINGS 11057722 | 152261105 | DIAMOND SPRINGS 1105 | 96782.5255 | 60.1507 | 572 | 68.2291 | 0.11928 | 649 | 7688.1454 | 7983.1451 | 0.3224 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
501 | DOBBINS 11011264 | 153741101 | DOBBINS 1101 | 56286.9636 | 34.9826 | 307 | 36.585 | 0.11917 | 650 | 7723.1279 | 7946.5601 | 0.32092 | 7946.5601 | #N/A | #N/A | #N/A | #N/A | #VALUE!
855 | HIGGINS 1103CB | 152691103 | HIGGINS 1103 | 45174.6839 | 28.0762 | 315 | 37.536 | 0.11916 | 651 | 7751.2042 | 7909.0241 | 0.31941 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
491 | TIVY VALLEY 1107822606 | 252941107 | TIVY VALLEY 1107 | 21701.9466 | 13.4878 | 144 | 17.1275 | 0.11894 | 652 | 7764.692 | 7891.8966 | 0.31871 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8121 | CAYETANO 2109MR186 | 14422109 | CAYETANO 2109 | 818.8837 | 0.50894 | 27 | 3.2061 | 0.11874 | 653 | 7765.201 | 7888.6905 | 0.31859 | 7888.6905 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2634 | APPLE HILL 21028372 | 153662102 | APPLE HILL 2102 | 94481.7777 | 58.7208 | 629 | 74.5861 | 0.11858 | 654 | 7823.9218 | 7814.1044 | 0.31557 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1440 | MARIPOSA 21019400 | 254452101 | MARIPOSA 2101 | 101537.78 | 63.1061 | 667 | 79.0304 | 0.11849 | 655 | 7887.0279 | 7735.074 | 0.31238 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8059 | OILFIELDS 1103N62 | 182391103 | OILFIELDS 1103 | 8948.1922 | 5.5613 | 39 | 4.6183 | 0.11842 | 656 | 7892.5893 | 7730.4558 | 0.31219 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1860 | SHINGLE SPRINGS 2105CB | 153652105 | SHINGLE SPRINGS 2105 | 30610.8387 | 19.0248 | 245 | 28.9401 | 0.11812 | 657 | 7911.614 | 7701.5157 | 0.31103 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1237 | NARROWS 2102CB | 153132102 | NARROWS 2102 | 36287.6403 | 22.5529 | 243 | 28.6917 | 0.11807 | 658 | 7934.1669 | 7672.824 | 0.30987 | 7672.824 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9931 | CORTINA 1101528460 | 63121101 | CORTINA 1101 | 3043.5918 | 1.8916 | 12 | 1.415 | 0.11792 | 659 | 7936.0585 | 7671.409 | 0.30981 | 7671.409 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6877 | COARSEGOLD 21036110 | 254432103 | COARSEGOLD 2103 | 17714.3763 | 11.0096 | 179 | 21.0097 | 0.11737 | 660 | 7947.0681 | 7650.3993 | 0.30896 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3126 | HORSESHOE 110150140 | 152571101 | HORSESHOE 1101 | 6357.3386 | 3.9511 | 82 | 9.6215 | 0.11734 | 661 | 7951.0192 | 7640.7778 | 0.30857 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9916 | SAN LUIS OBISPO 1104777686 | 182631104 | SAN LUIS OBISPO 1104 | 2707.2733 | 1.6826 | 17 | 1.9944 | 0.11731 | 662 | 7952.7018 | 7638.7835 | 0.30849 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8080 | SILVERADO 210258626 | 43432102 | SILVERADO 2102 | 24491.7338 | 15.2217 | 125 | 14.6249 | 0.117 | 663 | 7967.9235 | 7624.1586 | 0.3079 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4277 | SAN JOAQUIN #2 1103157026 | 252521103 | SAN JOAQUIN #2 1103 | 5200.077 | 3.2319 | 44 | 5.1403 | 0.11682 | 664 | 7971.1554 | 7619.0183 | 0.30769 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6827 | PEORIA 170411232 | 163781704 | PEORIA 1704 | 20505.608 | 12.7443 | 222 | 25.8772 | 0.11656 | 665 | 7983.8997 | 7593.1411 | 0.30665 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
772 | DIAMOND SPRINGS 11052102 | 152261105 | DIAMOND SPRINGS 1105 | 60307.8799 | 37.4816 | 417 | 48.4576 | 0.11621 | 666 | 8021.3813 | 7544.6834 | 0.30469 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1946 | WILLITS 1104CB | 42661104 | WILLITS 1104 | 6260.0525 | 3.8906 | 90 | 10.4477 | 0.11609 | 667 | 8025.2719 | 7534.2357 | 0.30427 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2370 | GEYSERVILLE 1102484 | 42891102 | GEYSERVILLE 1102 | 53688.8082 | 33.3678 | 379 | 43.9888 | 0.11607 | 668 | 8058.6397 | 7490.2469 | 0.30249 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7186 | HIGGINS 1104CB | 152691104 | HIGGINS 1104 | 18050.1072 | 11.2182 | 124 | 14.3743 | 0.11592 | 669 | 8069.8579 | 7475.8727 | 0.30191 | 7475.8727 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9814 | PENRYN 1105119949 | 152561105 | PENRYN 1105 | 2221.8702 | 1.3809 | 25 | 2.8822 | 0.11529 | 670 | 8071.2388 | 7472.9905 | 0.3018 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7423 | CLAY 1103CB | 163341103 | CLAY 1103 | 9680.057 | 6.0162 | 110 | 12.6729 | 0.11521 | 671 | 8077.255 | 7460.3176 | 0.30129 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7292 | TIDEWATER 2106745811 | 14652106 | TIDEWATER 2106 | 641.2916 | 0.39857 | 8 | 0.92047 | 0.11506 | 672 | 8077.6536 | 7459.3971 | 0.30125 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8864 | WOODACRE 110191900 | 43021101 | WOODACRE 1101 | 14519.294 | 9.0238 | 91 | 10.4566 | 0.11491 | 673 | 8086.6774 | 7448.9405 | 0.30083 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9782 | SAND CREEK 110397354 | 254601103 | SAND CREEK 1103 | 14168.242 | 8.8056 | 59 | 6.7778 | 0.11488 | 674 | 8095.483 | 7442.1627 | 0.30055 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7321 | CLARKSVILLE 210619642 | 153612106 | CLARKSVILLE 2106 | 1246.4399 | 0.77467 | 17 | 1.9511 | 0.11477 | 675 | 8096.2577 | 7440.2116 | 0.30047 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1291 | MERCED FALLS 11029470 | 252811102 | MERCED FALLS 1102 | 36749.5976 | 22.84 | 277 | 31.7833 | 0.11474 | 676 | 8119.0977 | 7408.4283 | 0.29919 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10278 | PUEBLO 2102943820 | 43292102 | PUEBLO 2102 | 3039.5845 | 1.8891 | 13 | 1.4903 | 0.11464 | 677 | 8120.9868 | 7406.938 | 0.29913 | 7406.938 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2358 | WHITMORE 11011594 | 103601101 | WHITMORE 1101 | 39042.2093 | 24.2649 | 160 | 18.3178 | 0.11449 | 678 | 8145.2517 | 7388.6202 | 0.29839 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
892 | MARIPOSA 210110240 | 254452101 | MARIPOSA 2101 | 34689.059 | 21.5594 | 189 | 21.6045 | 0.11431 | 679 | 8166.8111 | 7367.0158 | 0.29752 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4813 | CLOVERDALE 1102674 | 42821102 | CLOVERDALE 1102 | 27296.9382 | 16.9652 | 122 | 13.9092 | 0.11401 | 680 | 8183.7763 | 7353.1066 | 0.29696 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4778 | SHINGLE SPRINGS 210961892 | 153652109 | SHINGLE SPRINGS 2109 | 48456.6488 | 30.116 | 318 | 36.1635 | 0.11372 | 681 | 8213.8923 | 7316.9431 | 0.2955 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9093 | BANGOR 110155206 | 103191101 | BANGOR 1101 | 0 | 0 | 28 | 3.1783 | 0.11351 | 682 | 8213.8923 | 7313.7647 | 0.29537 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
395 | CALISTOGA 1101734 | 42711101 | CALISTOGA 1101 | 22050.8989 | 13.7047 | 162 | 18.3842 | 0.11348 | 683 | 8227.597 | 7295.3805 | 0.29462 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7143 | COTATI 1103CB | 42271103 | COTATI 1103 | 19422.567 | 12.0712 | 106 | 12.0218 | 0.11341 | 684 | 8239.6682 | 7283.3587 | 0.29414 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2744 | WHITMORE 110145262 | 103601101 | WHITMORE 1101 | 46333.9347 | 28.7967 | 221 | 25.0485 | 0.11334 | 685 | 8268.4649 | 7258.3102 | 0.29313 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4167 | COTTONWOOD 11031344 | 102931103 | COTTONWOOD 1103 | 16285.3354 | 10.1214 | 152 | 17.2178 | 0.11327 | 686 | 8278.5863 | 7241.0924 | 0.29243 | 7241.0924 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9035 | CLEAR LAKE 1101699062 | 42141101 | CLEAR LAKE 1101 | 1359.6473 | 0.84503 | 20 | 2.2645 | 0.11322 | 687 | 8279.4314 | 7238.8279 | 0.29234 | 7238.8279 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2015 | SHINGLE SPRINGS 210912392 | 153652109 | SHINGLE SPRINGS 2109 | 23572.5391 | 14.6504 | 178 | 20.1293 | 0.11309 | 688 | 8294.0818 | 7218.6986 | 0.29153 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2546 | PLACERVILLE 1110421358 | 153081110 | PLACERVILLE 1110 | 23870.6711 | 14.8357 | 169 | 19.0733 | 0.11286 | 689 | 8308.9175 | 7199.6253 | 0.29076 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6240 | SILVERADO 2104722 | 43432104 | SILVERADO 2104 | 12705.3582 | 7.8964 | 99 | 11.1613 | 0.11274 | 690 | 8316.8139 | 7188.464 | 0.29031 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6314 | TEJON 11023751 | 252931102 | TEJON 1102 | 15802.8651 | 9.8215 | 65 | 7.325 | 0.11269 | 691 | 8326.6355 | 7181.139 | 0.29001 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8377 | CAYETANO 2111CB | 14422111 | CAYETANO 2111 | 5449.7896 | 3.3871 | 81 | 9.1187 | 0.11258 | 692 | 8330.0225 | 7172.0203 | 0.28964 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
84 | LINCOLN 110451756 | 153701104 | LINCOLN 1104 | 17440.8058 | 10.8395 | 264 | 29.7041 | 0.11252 | 693 | 8340.8621 | 7142.3162 | 0.28844 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4410 | MC ARTHUR 1101501106 | 103491101 | MC ARTHUR 1101 | 16083.896 | 9.9962 | 86 | 9.6734 | 0.11248 | 694 | 8350.8583 | 7132.6427 | 0.28805 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1376 | CLARKSVILLE 210419772 | 153612104 | CLARKSVILLE 2104 | 28840.3765 | 17.9244 | 185 | 20.7806 | 0.11233 | 695 | 8368.7827 | 7111.8621 | 0.28721 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
138 | CLARKSVILLE 2103593454 | 153612103 | CLARKSVILLE 2103 | 51502.8241 | 32.0092 | 324 | 36.3549 | 0.11221 | 696 | 8400.7919 | 7075.5073 | 0.28574 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6028 | RISING RIVER 11011530 | 103551101 | RISING RIVER 1101 | 18168.0106 | 11.2915 | 167 | 18.7349 | 0.11218 | 697 | 8412.0834 | 7056.7724 | 0.28499 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6687 | CLARK ROAD 110281296 | 103091102 | CLARK ROAD 1102 | 17571.0511 | 10.9205 | 124 | 13.9107 | 0.11218 | 698 | 8423.0039 | 7042.8618 | 0.28443 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2672 | APPLE HILL 210277546 | 153662102 | APPLE HILL 2102 | 69346.9327 | 43.0994 | 403 | 45.1922 | 0.11214 | 699 | 8466.1033 | 6997.6696 | 0.2826 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4377 | MARIPOSA 2101752630 | 254452101 | MARIPOSA 2101 | 30558.9663 | 18.9925 | 154 | 17.2553 | 0.11205 | 700 | 8485.0958 | 6980.4143 | 0.2819 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5474 | COTATI 1105213984 | 42271105 | COTATI 1105 | 11162.845 | 6.9378 | 47 | 5.263 | 0.11198 | 701 | 8492.0335 | 6975.1513 | 0.28169 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6448 | MERCED FALLS 110238748 | 252811102 | MERCED FALLS 1102 | 24704.6186 | 15.354 | 178 | 19.9215 | 0.11192 | 702 | 8507.3876 | 6955.2298 | 0.28089 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1645 | COTATI 110599720 | 42271105 | COTATI 1105 | 14780.8133 | 9.1863 | 134 | 14.9768 | 0.11177 | 703 | 8516.5739 | 6940.2531 | 0.28028 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
439 | HIGGINS 1110CB | 152691110 | HIGGINS 1110 | 14019.0952 | 8.7129 | 134 | 14.9707 | 0.11172 | 704 | 8525.2868 | 6925.2824 | 0.27968 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6646 | UPPER LAKE 110175370 | 42871101 | UPPER LAKE 1101 | 17823.7139 | 11.0775 | 133 | 14.8441 | 0.11161 | 705 | 8536.3643 | 6910.4383 | 0.27908 | 6910.4383 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3320 | LAYTONVILLE 110237586 | 42681102 | LAYTONVILLE 1102 | 22457.0278 | 13.9571 | 72 | 8.0187 | 0.11137 | 706 | 8550.3215 | 6902.4196 | 0.27875 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8527 | HIGGINS 11097831 | 152691109 | HIGGINS 1109 | 14300.9674 | 8.8881 | 86 | 9.5719 | 0.1113 | 707 | 8559.2096 | 6892.8477 | 0.27837 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8404 | TEMPLETON 2110317796 | 183052110 | TEMPLETON 2110 | 8148.5566 | 5.0644 | 65 | 7.2063 | 0.11087 | 708 | 8564.2739 | 6885.6414 | 0.27808 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9399 | CALAVERAS CEMENT 1101585 | 162211101 | CALAVERAS CEMENT 1101 | 22730.6203 | 14.1272 | 95 | 10.5283 | 0.11082 | 709 | 8578.4011 | 6875.1132 | 0.27765 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9168 | CAL WATER 1102690954 | 255451102 | CAL WATER 1102 | 6410.0397 | 3.9839 | 12 | 1.3268 | 0.11057 | 710 | 8582.385 | 6873.7863 | 0.2776 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1850 | OAKHURST 1103CB | 254421103 | OAKHURST 1103 | 51789.1777 | 32.1872 | 417 | 46.0525 | 0.11044 | 711 | 8614.5722 | 6827.7338 | 0.27574 | 6827.7338 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4124 | CALPELLA 1102CB | 43411102 | CALPELLA 1102 | 263.08 | 0.16351 | 61 | 6.7341 | 0.1104 | 712 | 8614.7357 | 6820.9997 | 0.27547 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10720 | OCEANO 1103839302 | 182601103 | OCEANO 1103 | 1806.4039 | 1.1227 | 8 | 0.88007 | 0.11001 | 713 | 8615.8584 | 6820.1196 | 0.27543 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2355 | OLETA 11021204 | 163541102 | OLETA 1102 | 41374.6655 | 25.7145 | 233 | 25.6033 | 0.10989 | 714 | 8641.5729 | 6794.5163 | 0.2744 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
635 | BRUNSWICK 11062790 | 152481106 | BRUNSWICK 1106 | 16028.2028 | 9.9616 | 115 | 12.5971 | 0.10954 | 715 | 8651.5345 | 6781.9193 | 0.27389 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6919 | COTTONWOOD 110168190 | 102931101 | COTTONWOOD 1101 | 38588.9503 | 23.9832 | 238 | 26.0311 | 0.10937 | 716 | 8675.5177 | 6755.8881 | 0.27284 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10335 | PETALUMA C 1109664732 | 42631109 | PETALUMA C 1109 | 1437.8147 | 0.89361 | 6 | 0.65051 | 0.10842 | 717 | 8676.4113 | 6755.2376 | 0.27281 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4157 | CALPELLA 1101600 | 43411101 | CALPELLA 1101 | 30870.3 | 19.186 | 164 | 17.7408 | 0.10818 | 718 | 8695.5973 | 6737.4968 | 0.27209 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3546 | LUCERNE 1103CB | 43351103 | LUCERNE 1103 | 3619.1597 | 2.2493 | 59 | 6.3658 | 0.10789 | 719 | 8697.8466 | 6731.131 | 0.27184 | 6731.131 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6463 | SONOMA 1105229588 | 42721105 | SONOMA 1105 | 15531.0208 | 9.6526 | 149 | 16.0708 | 0.10786 | 720 | 8707.4992 | 6715.0603 | 0.27119 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2133 | FROGTOWN 17011623 | 163451701 | FROGTOWN 1701 | 24554.2111 | 15.2605 | 152 | 16.3546 | 0.1076 | 721 | 8722.7597 | 6698.7057 | 0.27053 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10925 | GOLDTREE 1105551904 | 182581105 | GOLDTREE 1105 | 35.7178 | 0.022199 | 1 | 0.10733 | 0.10733 | 722 | 8722.7819 | 6698.5984 | 0.27052 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9605 | NOTRE DAME 1104937710 | 102041104 | NOTRE DAME 1104 | 1372.1379 | 0.85279 | 8 | 0.85862 | 0.10733 | 723 | 8723.6347 | 6697.7397 | 0.27049 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3953 | JAMESON 11059472 | 63801105 | JAMESON 1105 | 4934.5741 | 3.0669 | 90 | 9.6577 | 0.10731 | 724 | 8726.7016 | 6688.0821 | 0.2701 | 6688.0821 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6952 | OLETA 110151740 | 163541101 | OLETA 1101 | 25031.397 | 15.5571 | 129 | 13.8028 | 0.107 | 725 | 8742.2587 | 6674.2793 | 0.26954 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4360 | CORRAL 110236666 | 162991102 | CORRAL 1102 | 27295.7526 | 16.9644 | 207 | 22.1131 | 0.10683 | 726 | 8759.2231 | 6652.1662 | 0.26865 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10467 | BIG BEND 11011704 | 103751101 | BIG BEND 1101 | 4825.0456 | 2.9988 | 9 | 0.95854 | 0.1065 | 727 | 8762.2219 | 6651.2077 | 0.26861 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2963 | KONOCTI 110275382 | 43311102 | KONOCTI 1102 | 37336.0999 | 23.2045 | 198 | 21.0588 | 0.10636 | 728 | 8785.4264 | 6630.1489 | 0.26776 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7719 | GEYSERVILLE 1102220154 | 42891102 | GEYSERVILLE 1102 | 427.7941 | 0.26588 | 30 | 3.1738 | 0.10579 | 729 | 8785.6923 | 6626.9751 | 0.26763 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4276 | NARROWS 2105CB | 153132105 | NARROWS 2105 | 58073.6402 | 36.093 | 382 | 40.3677 | 0.10567 | 730 | 8821.7853 | 6586.6073 | 0.266 | 6586.6073 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4123 | MARIPOSA 21014410 | 254452101 | MARIPOSA 2101 | 36702.381 | 22.8107 | 232 | 24.471 | 0.10548 | 731 | 8844.596 | 6562.1363 | 0.26501 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5996 | MONTICELLO 1101630 | 43051101 | MONTICELLO 1101 | 30113.0466 | 18.7154 | 93 | 9.7794 | 0.10515 | 732 | 8863.3114 | 6552.3569 | 0.26462 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7010 | WILLITS 1103966 | 42661103 | WILLITS 1103 | 1555.849 | 0.96697 | 34 | 3.5716 | 0.10505 | 733 | 8864.2783 | 6548.7854 | 0.26447 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6094 | PARADISE 110443008 | 102831104 | PARADISE 1104 | 20697.7732 | 12.8637 | 145 | 15.2269 | 0.10501 | 734 | 8877.1421 | 6533.5584 | 0.26386 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6540 | MORGAN HILL 2105XR070 | 83242105 | MORGAN HILL 2105 | 10519.5514 | 6.5379 | 90 | 9.4261 | 0.10473 | 735 | 8883.68 | 6524.1324 | 0.26348 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1104 | BRUNSWICK 11042112 | 152481104 | BRUNSWICK 1104 | 31201.9016 | 19.3921 | 222 | 23.2211 | 0.1046 | 736 | 8903.0721 | 6500.9113 | 0.26254 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3331 | NARROWS 21052216 | 153132105 | NARROWS 2105 | 91192.0768 | 56.6762 | 663 | 69.2068 | 0.10438 | 737 | 8959.7484 | 6431.7045 | 0.25974 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10962 | POINT ARENA 1101CB | 43381101 | POINT ARENA 1101 | 64.9169 | 0.040346 | 2 | 0.20825 | 0.10413 | 738 | 8959.7887 | 6431.4963 | 0.25974 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7695 | JAMESON 110265516 | 63801102 | JAMESON 1102 | 12394.5836 | 7.7033 | 137 | 14.2484 | 0.104 | 739 | 8967.492 | 6417.2479 | 0.25916 | 6417.2479 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4131 | CURTIS 170565908 | 163351705 | CURTIS 1705 | 22380.0869 | 13.9093 | 205 | 21.3052 | 0.10393 | 740 | 8981.4013 | 6395.9427 | 0.2583 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
386 | CORRAL 110112606 | 162991101 | CORRAL 1101 | 36144.366 | 22.4639 | 216 | 22.4476 | 0.10392 | 741 | 9003.8652 | 6373.4951 | 0.25739 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1298 | DESCHUTES 11011652 | 103351101 | DESCHUTES 1101 | 33895.2642 | 21.066 | 170 | 17.5982 | 0.10352 | 742 | 9024.9312 | 6355.8969 | 0.25668 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10344 | CLARKSVILLE 210319572 | 153612103 | CLARKSVILLE 2103 | 595.3794 | 0.37003 | 12 | 1.2418 | 0.10348 | 743 | 9025.3013 | 6354.6551 | 0.25663 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2338 | CLAY 110113442 | 163341101 | CLAY 1101 | 40749.3903 | 25.3259 | 272 | 28.1191 | 0.10338 | 744 | 9050.6272 | 6326.536 | 0.2555 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1080 | PLACER 1103284874 | 152461103 | PLACER 1103 | 3450.771 | 2.1447 | 56 | 5.7804 | 0.10322 | 745 | 9052.7719 | 6320.7556 | 0.25526 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2572 | VACA DIXON 11059792 | 63591105 | VACA DIXON 1105 | 1255.3676 | 0.78022 | 329 | 33.9591 | 0.10322 | 746 | 9053.5521 | 6286.7965 | 0.25389 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10829 | MILPITAS 110962157 | 82831109 | MILPITAS 1109 | 72.1015 | 0.044811 | 3 | 0.30771 | 0.10257 | 747 | 9053.5969 | 6286.4888 | 0.25388 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9526 | DOBBINS 110191464 | 153741101 | DOBBINS 1101 | 11314.1038 | 7.0318 | 81 | 8.2855 | 0.10229 | 748 | 9060.6286 | 6278.2032 | 0.25355 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4686 | ELK CREEK 11012212 | 102781101 | ELK CREEK 1101 | 25107.5196 | 15.6044 | 136 | 13.9025 | 0.10222 | 749 | 9076.2331 | 6264.3007 | 0.25298 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2703 | COTATI 110536536 | 42271105 | COTATI 1105 | 27701.0415 | 17.2163 | 206 | 21.0515 | 0.10219 | 750 | 9093.4494 | 6243.2492 | 0.25213 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
261 | CLARK ROAD 11022584 | 103091102 | CLARK ROAD 1102 | 14615.3184 | 9.0835 | 83 | 8.4581 | 0.1019 | 751 | 9102.5329 | 6234.7911 | 0.25179 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6202 | COARSEGOLD 210490356 | 254432104 | COARSEGOLD 2104 | 7749.0513 | 4.8161 | 148 | 15.079 | 0.10189 | 752 | 9107.3489 | 6219.7121 | 0.25118 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10164 | CALPELLA 1101345230 | 43411101 | CALPELLA 1101 | 1908.1944 | 1.186 | 22 | 2.2398 | 0.10181 | 753 | 9108.5349 | 6217.4723 | 0.25109 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10372 | CLOVERDALE 11024646 | 42821102 | CLOVERDALE 1102 | 242.399 | 0.15065 | 8 | 0.81301 | 0.10163 | 754 | 9108.6855 | 6216.6593 | 0.25106 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10615 | STAFFORD 1102CB | 43201102 | STAFFORD 1102 | 957.3027 | 0.59497 | 10 | 1.0116 | 0.10116 | 755 | 9109.2805 | 6215.6478 | 0.25102 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10097 | GARBERVILLE 110256048 | 192221102 | GARBERVILLE 1102 | 8009.5026 | 4.9779 | 27 | 2.7275 | 0.10102 | 756 | 9114.2584 | 6212.9202 | 0.25091 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2214 | MONTICELLO 11014360 | 43051101 | MONTICELLO 1101 | 12170.4858 | 7.564 | 76 | 7.6765 | 0.10101 | 757 | 9121.8224 | 6205.2438 | 0.2506 | 6205.2438 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2869 | NARROWS 21011202 | 153132101 | NARROWS 2101 | 73649.8789 | 45.7737 | 459 | 46.3007 | 0.10087 | 758 | 9167.5961 | 6158.9431 | 0.24873 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2918 | JESSUP 110338864 | 103441103 | JESSUP 1103 | 2907.107 | 1.8068 | 94 | 9.4715 | 0.10076 | 759 | 9169.4029 | 6149.4716 | 0.24835 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8434 | FORT ROSS 1121204 | 42851121 | FORT ROSS 1121 | 31553.8482 | 19.6108 | 107 | 10.7713 | 0.10067 | 760 | 9189.0138 | 6138.7003 | 0.24791 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9462 | BEAR VALLEY 210110019 | 252192101 | BEAR VALLEY 2101 | 3187.4941 | 1.981 | 11 | 1.1057 | 0.10052 | 761 | 9190.9948 | 6137.5945 | 0.24787 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3132 | MORGAN HILL 210542348 | 83242105 | MORGAN HILL 2105 | 2160.8096 | 1.343 | 53 | 5.3194 | 0.10037 | 762 | 9192.3378 | 6132.2751 | 0.24765 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10415 | SAN LUIS OBISPO 1103934355 | 182631103 | SAN LUIS OBISPO 1103 | 915.6706 | 0.56909 | 12 | 1.2035 | 0.10029 | 763 | 9192.9068 | 6131.0716 | 0.2476 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
800 | NARROWS 210248484 | 153132102 | NARROWS 2102 | 67054.8672 | 41.6749 | 450 | 44.991 | 0.09998 | 764 | 9234.5817 | 6086.0806 | 0.24579 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3794 | HIGGINS 11077559 | 152691107 | HIGGINS 1107 | 7193.5229 | 4.4708 | 52 | 5.1899 | 0.099807 | 765 | 9239.0525 | 6080.8907 | 0.24558 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4136 | MONTICELLO 1101718 | 43051101 | MONTICELLO 1101 | 43463.4041 | 27.0127 | 247 | 24.6369 | 0.099744 | 766 | 9266.0652 | 6056.2538 | 0.24458 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2696 | OLETA 110163500 | 163541101 | OLETA 1101 | 327.1501 | 0.20333 | 46 | 4.584 | 0.099652 | 767 | 9266.2685 | 6051.6698 | 0.2444 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3595 | CEDAR CREEK 11011608 | 103321101 | CEDAR CREEK 1101 | 53827.5719 | 33.4541 | 252 | 25.1102 | 0.099644 | 768 | 9299.7226 | 6026.5596 | 0.24338 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
80 | WHEATLAND 1105248490 | 152811105 | WHEATLAND 1105 | 17726.6224 | 11.0172 | 228 | 22.7114 | 0.099611 | 769 | 9310.7397 | 6003.8482 | 0.24247 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
24 | FITCH MOUNTAIN 1113443164 | 42751113 | FITCH MOUNTAIN 1113 | 4499.5872 | 2.7965 | 111 | 11.0246 | 0.099321 | 770 | 9313.5363 | 5992.8236 | 0.24202 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6194 | CLARK ROAD 110292622 | 103091102 | CLARK ROAD 1102 | 50311.0535 | 31.2685 | 257 | 25.314 | 0.098498 | 771 | 9344.8048 | 5967.5096 | 0.241 | 5967.5096 | #N/A | #N/A | #N/A | #N/A | #VALUE!
643 | PENRYN 1105154362 | 152561105 | PENRYN 1105 | 3480.2712 | 2.163 | 90 | 8.8574 | 0.098415 | 772 | 9346.9678 | 5958.6522 | 0.24064 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10663 | SAN RAMON 2102CB | 14232102 | SAN RAMON 2102 | 2836.6716 | 1.763 | 16 | 1.5736 | 0.098349 | 773 | 9348.7308 | 5957.0787 | 0.24058 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7571 | BROWNS VALLEY 110193870 | 152921101 | BROWNS VALLEY 1101 | 29826.9597 | 18.5376 | 342 | 33.6143 | 0.098287 | 774 | 9367.2684 | 5923.4643 | 0.23922 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9322 | MONTICELLO 1101CB | 43051101 | MONTICELLO 1101 | 859.9008 | 0.53443 | 5 | 0.49137 | 0.098274 | 775 | 9367.8028 | 5922.973 | 0.2392 | 5922.973 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5943 | TEMPLETON 2113A10 | 183052113 | TEMPLETON 2113 | 49945.6996 | 31.0415 | 264 | 25.8725 | 0.098002 | 776 | 9398.8442 | 5897.1005 | 0.23815 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5478 | PENRYN 11072706 | 152561107 | PENRYN 1107 | 9304.8867 | 5.783 | 190 | 18.5915 | 0.09785 | 777 | 9404.6273 | 5878.509 | 0.2374 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3757 | WILLITS 1104934 | 42661104 | WILLITS 1104 | 49660.3767 | 30.8641 | 279 | 27.2301 | 0.097599 | 778 | 9435.4914 | 5851.2789 | 0.2363 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7329 | CORRAL 110213498 | 162991102 | CORRAL 1102 | 1585.9579 | 0.98568 | 13 | 1.2619 | 0.097071 | 779 | 9436.4771 | 5850.017 | 0.23625 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6184 | PEORIA 170190090 | 163781701 | PEORIA 1701 | 48332.111 | 30.0386 | 168 | 16.2826 | 0.09692 | 780 | 9466.5157 | 5833.7343 | 0.2356 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1027 | OILFIELDS 110383158 | 182391103 | OILFIELDS 1103 | 28429.994 | 17.6694 | 132 | 12.7894 | 0.09689 | 781 | 9484.185 | 5820.9449 | 0.23508 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3208 | WILLITS 11032500 | 42661103 | WILLITS 1103 | 48136.3959 | 29.917 | 143 | 13.8385 | 0.096773 | 782 | 9514.102 | 5807.1065 | 0.23452 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9576 | LLAGAS 2104603392 | 83182104 | LLAGAS 2104 | 4685.9835 | 2.9124 | 17 | 1.6426 | 0.096621 | 783 | 9517.0144 | 5805.4639 | 0.23445 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
211 | APPLE HILL 110313312 | 153661103 | APPLE HILL 1103 | 21155.7388 | 13.1484 | 190 | 18.3453 | 0.096554 | 784 | 9530.1627 | 5787.1186 | 0.23371 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1106 | BANGOR 11011958 | 103191101 | BANGOR 1101 | 54465.3426 | 33.8504 | 353 | 33.9382 | 0.096142 | 785 | 9564.0132 | 5753.1804 | 0.23234 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5073 | LAYTONVILLE 1102CB | 42681102 | LAYTONVILLE 1102 | 19267.3702 | 11.9747 | 95 | 9.0993 | 0.095782 | 786 | 9575.9879 | 5744.0811 | 0.23198 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7859 | MOUNTAIN QUARRIES 210135466 | 152282101 | MOUNTAIN QUARRIES 2101 | 11836.6618 | 7.3565 | 82 | 7.8361 | 0.095562 | 787 | 9583.3444 | 5736.245 | 0.23166 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
871 | PEORIA 17019811 | 163781701 | PEORIA 1701 | 5776.4657 | 3.5901 | 92 | 8.7707 | 0.095333 | 788 | 9586.9345 | 5727.4744 | 0.2313 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
669 | CABRILLO 1103CB | 183101103 | CABRILLO 1103 | 875.6492 | 0.54422 | 45 | 4.2824 | 0.095165 | 789 | 9587.4788 | 5723.1919 | 0.23113 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3438 | CALISTOGA 1102CB | 42711102 | CALISTOGA 1102 | 517.8814 | 0.32187 | 37 | 3.5207 | 0.095153 | 790 | 9587.8006 | 5719.6713 | 0.23099 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8923 | SUNOL 1101CB | 14241101 | SUNOL 1101 | 5281.0095 | 3.2822 | 53 | 5.0422 | 0.095135 | 791 | 9591.0828 | 5714.6291 | 0.23079 | 5714.6291 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5883 | SILVERADO 2104632 | 43432104 | SILVERADO 2104 | 29492.7895 | 18.3299 | 193 | 18.327 | 0.094959 | 792 | 9609.4127 | 5696.3021 | 0.23005 | 5696.3021 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5762 | CHALLENGE 11021064 | 103201102 | CHALLENGE 1102 | 31650.7422 | 19.6711 | 179 | 16.9879 | 0.094905 | 793 | 9629.0837 | 5679.3141 | 0.22936 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
847 | CURTIS 17026008 | 163351702 | CURTIS 1702 | 37504.3181 | 23.3091 | 236 | 22.3721 | 0.094797 | 794 | 9652.3928 | 5656.942 | 0.22846 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7905 | CAYETANO 2109CB | 14422109 | CAYETANO 2109 | 2269.8172 | 1.4107 | 51 | 4.8334 | 0.094773 | 795 | 9653.8035 | 5652.1086 | 0.22826 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6145 | OAKHURST 110210100 | 254421102 | OAKHURST 1102 | 16723.3035 | 10.3936 | 142 | 13.4521 | 0.094733 | 796 | 9664.1971 | 5638.6565 | 0.22772 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6083 | MILPITAS 1109XR524 | 82831109 | MILPITAS 1109 | 17523.6666 | 10.891 | 59 | 5.5714 | 0.09443 | 797 | 9675.0882 | 5633.0852 | 0.22749 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
370 | UKIAH 1114CB | 42771114 | UKIAH 1114 | 1067.201 | 0.66327 | 93 | 8.7742 | 0.094346 | 798 | 9675.7514 | 5624.311 | 0.22714 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7085 | MESA 1103854149 | 182821103 | MESA 1103 | 1563.4443 | 0.97169 | 12 | 1.132 | 0.094333 | 799 | 9676.7231 | 5623.179 | 0.22709 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8026 | PEORIA 1704CB | 163781704 | PEORIA 1704 | 13470.2412 | 8.3718 | 64 | 6.0262 | 0.094159 | 800 | 9685.0949 | 5617.1528 | 0.22685 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4910 | PUEBLO 2103373667 | 43292103 | PUEBLO 2103 | 5269.4021 | 3.275 | 45 | 4.2363 | 0.09414 | 801 | 9688.3699 | 5612.9165 | 0.22668 | 5612.9165 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3504 | MOLINO 1102396 | 42571102 | MOLINO 1102 | 25908.1895 | 16.102 | 182 | 17.099 | 0.093951 | 802 | 9704.4719 | 5595.8175 | 0.22599 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8266 | LAS POSITAS 2108MR182 | 14402108 | LAS POSITAS 2108 | 10768.7759 | 6.6928 | 56 | 5.2596 | 0.093921 | 803 | 9711.1648 | 5590.5579 | 0.22577 | 5590.5579 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6506 | CALAVERAS CEMENT 11014786 | 162211101 | CALAVERAS CEMENT 1101 | 28973.985 | 18.0074 | 173 | 16.224 | 0.09378 | 804 | 9729.1722 | 5574.3339 | 0.22512 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1161 | WYANDOTTE 110777578 | 102911107 | WYANDOTTE 1107 | 34427.9014 | 21.3971 | 389 | 36.2858 | 0.09328 | 805 | 9750.5693 | 5538.0481 | 0.22365 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5393 | GARBERVILLE 11024744 | 192221102 | GARBERVILLE 1102 | 27938.0536 | 17.3636 | 161 | 15.0101 | 0.093231 | 806 | 9767.9329 | 5523.038 | 0.22305 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5755 | PENRYN 11072704 | 152561107 | PENRYN 1107 | 2300.3426 | 1.4297 | 76 | 7.0698 | 0.093023 | 807 | 9769.3626 | 5515.9682 | 0.22276 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8038 | WILLITS 1103826 | 42661103 | WILLITS 1103 | 12455.7726 | 7.7413 | 89 | 8.2683 | 0.092902 | 808 | 9777.1039 | 5507.6999 | 0.22243 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5718 | PETALUMA C 1108233646 | 42631108 | PETALUMA C 1108 | 15102.5612 | 9.3863 | 127 | 11.7669 | 0.092653 | 809 | 9786.4902 | 5495.933 | 0.22195 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7314 | CLARKSVILLE 210575884 | 153612105 | CLARKSVILLE 2105 | 17165.4943 | 10.6684 | 94 | 8.7025 | 0.09258 | 810 | 9797.1586 | 5487.2305 | 0.2216 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
837 | DIAMOND SPRINGS 11071402 | 152261107 | DIAMOND SPRINGS 1107 | 71104.0432 | 44.1915 | 541 | 49.924 | 0.092281 | 811 | 9841.3501 | 5437.3065 | 0.21959 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1640 | JESSUP 1101CB | 103441101 | JESSUP 1101 | 2462.2686 | 1.5303 | 66 | 6.0835 | 0.092174 | 812 | 9842.8804 | 5431.223 | 0.21934 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2558 | PENRYN 1103660 | 152561103 | PENRYN 1103 | 16353.7146 | 10.1639 | 233 | 21.4747 | 0.092166 | 813 | 9853.0443 | 5409.7483 | 0.21847 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9244 | KERN OIL 110646960 | 252721106 | KERN OIL 1106 | 1465.0556 | 0.91054 | 14 | 1.29 | 0.092145 | 814 | 9853.9548 | 5408.4583 | 0.21842 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4181 | MONTICELLO 1101666 | 43051101 | MONTICELLO 1101 | 19462.335 | 12.0959 | 90 | 8.2843 | 0.092048 | 815 | 9866.0507 | 5400.174 | 0.21809 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8910 | BRIDGEVILLE 110255612 | 192461102 | BRIDGEVILLE 1102 | 35781.5314 | 22.2384 | 93 | 8.4532 | 0.090894 | 816 | 9888.2891 | 5391.7208 | 0.21774 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3415 | PARADISE 1104409622 | 102831104 | PARADISE 1104 | 20534.7896 | 12.7625 | 156 | 14.1696 | 0.090831 | 817 | 9901.0516 | 5377.5512 | 0.21717 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4056 | CALAVERAS CEMENT 110113424 | 162211101 | CALAVERAS CEMENT 1101 | 2404.2277 | 1.4942 | 43 | 3.9007 | 0.090714 | 818 | 9902.5458 | 5373.6504 | 0.21702 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
345 | COTTONWOOD 1101384360 | 102931101 | COTTONWOOD 1101 | 7892.4211 | 4.9052 | 70 | 6.3298 | 0.090426 | 819 | 9907.451 | 5367.3206 | 0.21676 | 5367.3206 | #N/A | #N/A | #N/A | #N/A | #VALUE!
287 | WHITMORE 11011598 | 103601101 | WHITMORE 1101 | 53928.0023 | 33.5165 | 251 | 22.6955 | 0.09042 | 820 | 9940.9674 | 5344.6251 | 0.21584 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8279 | LOW GAP 110186816 | 192411101 | LOW GAP 1101 | 7103.5026 | 4.4149 | 51 | 4.6062 | 0.090319 | 821 | 9945.3823 | 5340.0189 | 0.21566 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7426 | SANTA MARIA 1108M18 | 182671108 | SANTA MARIA 1108 | 24562.1098 | 15.2655 | 81 | 7.2922 | 0.090027 | 822 | 9960.6477 | 5332.7267 | 0.21536 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7586 | KONOCTI 1102948 | 43311102 | KONOCTI 1102 | 10159.6075 | 6.3142 | 73 | 6.5542 | 0.089784 | 823 | 9966.962 | 5326.1725 | 0.2151 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8787 | GIRVAN 1102212096 | 103401102 | GIRVAN 1102 | 4124.0159 | 2.5631 | 42 | 3.7688 | 0.089733 | 824 | 9969.5251 | 5322.4037 | 0.21495 | 5322.4037 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10586 | LOS MOLINOS 1101297862 | 103481101 | LOS MOLINOS 1101 | 503.2242 | 0.31276 | 4 | 0.35827 | 0.089567 | 825 | 9969.8378 | 5322.0455 | 0.21493 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6573 | SISQUOC 1103858898 | 182811103 | SISQUOC 1103 | 31551.7735 | 19.6096 | 152 | 13.6052 | 0.089508 | 826 | 9989.4474 | 5308.4403 | 0.21438 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10830 | PETALUMA C 1109373772 | 42631109 | PETALUMA C 1109 | 28.6691 | 0.017818 | 2 | 0.17883 | 0.089417 | 827 | 9989.4652 | 5308.2615 | 0.21437 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
817 | CLOVERDALE 1102570 | 42821102 | CLOVERDALE 1102 | 28557.0384 | 17.7483 | 199 | 17.7691 | 0.089292 | 828 | 10007.2135 | 5290.4923 | 0.21366 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5781 | SAN JOAQUIN #3 11035100 | 252531103 | SAN JOAQUIN #3 1103 | 34326.3844 | 21.334 | 204 | 18.2004 | 0.089218 | 829 | 10028.5475 | 5272.2919 | 0.21292 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6729 | SAN LUIS OBISPO 110788962 | 182631107 | SAN LUIS OBISPO 1107 | 3996.9259 | 2.4841 | 45 | 4.0128 | 0.089174 | 830 | 10031.0316 | 5268.2791 | 0.21276 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5238 | DIAMOND SPRINGS 110656026 | 152261106 | DIAMOND SPRINGS 1106 | 24339.1905 | 15.1269 | 158 | 14.0716 | 0.089061 | 831 | 10046.1585 | 5254.2074 | 0.21219 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4137 | UKIAH 1114528 | 42771114 | UKIAH 1114 | 6048.4547 | 3.7591 | 110 | 9.7966 | 0.08906 | 832 | 10049.9177 | 5244.4108 | 0.2118 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2145 | CALISTOGA 1101736 | 42711101 | CALISTOGA 1101 | 55772.0682 | 34.6626 | 350 | 31.0945 | 0.088841 | 833 | 10084.5802 | 5213.3163 | 0.21054 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8817 | WYANDOTTE 1105CB | 102911105 | WYANDOTTE 1105 | 18499.2196 | 11.4973 | 14 | 1.2395 | 0.088539 | 834 | 10096.0776 | 5212.0768 | 0.21049 | 5212.0768 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3899 | PEORIA 170510580 | 163781705 | PEORIA 1705 | 12416.9837 | 7.7172 | 129 | 11.415 | 0.088489 | 835 | 10103.7948 | 5200.6617 | 0.21003 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5666 | WOODSIDE 110147872 | 24251101 | WOODSIDE 1101 | 6709.5897 | 4.17 | 52 | 4.5979 | 0.088422 | 836 | 10107.9648 | 5196.0638 | 0.20984 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7241 | ATASCADERO 1103A14 | 182541103 | ATASCADERO 1103 | 40416.4237 | 25.119 | 152 | 13.4395 | 0.088418 | 837 | 10133.0838 | 5182.6243 | 0.2093 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
878 | FROGTOWN 170275252 | 163451702 | FROGTOWN 1702 | 93174.0996 | 57.9081 | 401 | 35.3494 | 0.088153 | 838 | 10190.9919 | 5147.2749 | 0.20787 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4836 | GRASS VALLEY 11031700 | 152031103 | GRASS VALLEY 1103 | 34930.2373 | 21.7093 | 255 | 22.4191 | 0.087918 | 839 | 10212.7011 | 5124.8558 | 0.20697 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7987 | BELL 1108339792 | 152701108 | BELL 1108 | 4221.2236 | 2.6235 | 43 | 3.7723 | 0.087729 | 840 | 10215.3246 | 5121.0835 | 0.20682 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8725 | LLAGAS 2101984552 | 83182101 | LLAGAS 2101 | 7304.6852 | 4.5399 | 53 | 4.6381 | 0.087511 | 841 | 10219.8645 | 5116.4454 | 0.20663 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4715 | GIRVAN 110280726 | 103401102 | GIRVAN 1102 | 12661.4918 | 7.8692 | 217 | 18.9591 | 0.087369 | 842 | 10227.7337 | 5097.4863 | 0.20586 | 5097.4863 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5678 | SAN LUIS OBISPO 1102348318 | 182631102 | SAN LUIS OBISPO 1102 | 597.0392 | 0.37106 | 6 | 0.52408 | 0.087346 | 843 | 10228.1048 | 5096.9622 | 0.20584 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8497 | BEAR VALLEY 210576694 | 252192105 | BEAR VALLEY 2105 | 7317.351 | 4.5478 | 37 | 3.2299 | 0.087295 | 844 | 10232.6525 | 5093.7323 | 0.20571 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4933 | RACETRACK 17039190 | 163761703 | RACETRACK 1703 | 14438.9195 | 8.9738 | 104 | 9.06 | 0.087115 | 845 | 10241.6264 | 5084.6723 | 0.20534 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10437 | RIO DELL 110275970 | 192251102 | RIO DELL 1102 | 11378.8384 | 7.072 | 33 | 2.869 | 0.08694 | 846 | 10248.6984 | 5081.8033 | 0.20523 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3279 | OAKHURST 1101CB | 254421101 | OAKHURST 1101 | 3724.6766 | 2.3149 | 47 | 4.0694 | 0.086583 | 847 | 10251.0133 | 5077.7339 | 0.20506 | 5077.7339 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6810 | KESWICK 11011590 | 103451101 | KESWICK 1101 | 10388.8945 | 6.4567 | 63 | 5.4516 | 0.086534 | 848 | 10257.47 | 5072.2823 | 0.20484 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2304 | SAN JOAQUIN #3 1103CB | 252531103 | SAN JOAQUIN #3 1103 | 45670.4217 | 28.3844 | 294 | 25.3881 | 0.086354 | 849 | 10285.8544 | 5046.8942 | 0.20382 | 5046.8942 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7373 | TIVY VALLEY 11077380 | 252941107 | TIVY VALLEY 1107 | 20845.5533 | 12.9556 | 240 | 20.6923 | 0.086218 | 850 | 10298.81 | 5026.2019 | 0.20298 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1492 | STILLWATER 110148950 | 103561101 | STILLWATER 1101 | 20081.7793 | 12.4809 | 145 | 12.467 | 0.085979 | 851 | 10311.2909 | 5013.735 | 0.20248 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3172 | RED BLUFF 1105161818 | 103541105 | RED BLUFF 1105 | 212.3638 | 0.13198 | 59 | 5.0669 | 0.08588 | 852 | 10311.4229 | 5008.668 | 0.20228 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5834 | SANTA YNEZ 1102320270 | 182721102 | SANTA YNEZ 1102 | 13648.6049 | 8.4827 | 137 | 11.7464 | 0.08574 | 853 | 10319.9055 | 4996.9216 | 0.2018 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
742 | MORGAN HILL 2105XR176 | 83242105 | MORGAN HILL 2105 | 36252.5852 | 22.5311 | 309 | 26.478 | 0.085689 | 854 | 10342.4366 | 4970.4437 | 0.20073 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8450 | MARTELL 1102CB | 163011102 | MARTELL 1102 | 9142.0744 | 5.6818 | 69 | 5.9113 | 0.08567 | 855 | 10348.1185 | 4964.5324 | 0.20049 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3883 | COTATI 1102167726 | 42271102 | COTATI 1102 | 6114.3744 | 3.8001 | 50 | 4.272 | 0.08544 | 856 | 10351.9186 | 4960.2605 | 0.20032 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10186 | CLAYTON 22159765 | 12022215 | CLAYTON 2215 | 425.4979 | 0.26445 | 16 | 1.3663 | 0.085394 | 857 | 10352.183 | 4958.8941 | 0.20027 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5425 | CORNING 110187304 | 103331101 | CORNING 1101 | 4634.8119 | 2.8806 | 100 | 8.5339 | 0.085339 | 858 | 10355.0636 | 4950.3602 | 0.19992 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4113 | PHILO 1101CB | 42601101 | PHILO 1101 | 51306.3985 | 31.8871 | 469 | 39.9976 | 0.085283 | 859 | 10386.9507 | 4910.3627 | 0.19831 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10106 | GEYSERVILLE 1102537096 | 42891102 | GEYSERVILLE 1102 | 775.9765 | 0.48227 | 6 | 0.51137 | 0.085228 | 860 | 10387.433 | 4909.8513 | 0.19828 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9409 | CLAY 1102CB | 163341102 | CLAY 1102 | 1492.4904 | 0.92759 | 19 | 1.6191 | 0.085217 | 861 | 10388.3606 | 4908.2322 | 0.19822 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6247 | ELK CREEK 11012004 | 102781101 | ELK CREEK 1101 | 40225.06 | 25 | 174 | 14.8204 | 0.085175 | 862 | 10413.3606 | 4893.4117 | 0.19762 | 4893.4117 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2719 | SAN LUIS OBISPO 1104V10 | 182631104 | SAN LUIS OBISPO 1104 | 3504.8307 | 2.1783 | 54 | 4.5956 | 0.085103 | 863 | 10415.5389 | 4888.8162 | 0.19744 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
541 | TEMPLETON 2113R82 | 183052113 | TEMPLETON 2113 | 61789.4025 | 38.4024 | 563 | 47.806 | 0.084913 | 864 | 10453.9413 | 4841.0101 | 0.1955 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7060 | BIG BEND 1102CB | 103751102 | BIG BEND 1102 | 27411.8293 | 17.0366 | 139 | 11.7994 | 0.084888 | 865 | 10470.9778 | 4829.2107 | 0.19503 | 4829.2107 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7634 | IONE 1101L3141 | 163881101 | IONE 1101 | 22255.8256 | 13.8321 | 97 | 8.2002 | 0.084539 | 866 | 10484.8099 | 4821.0105 | 0.1947 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1449 | FORT SEWARD 1122CB | 192321122 | FORT SEWARD 1122 | 28413.1031 | 17.6589 | 111 | 9.3748 | 0.084457 | 867 | 10502.4688 | 4811.6357 | 0.19432 | 4811.6357 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3137 | MOLINO 1102104 | 42571102 | MOLINO 1102 | 34991.65 | 21.7475 | 235 | 19.818 | 0.084332 | 868 | 10524.2162 | 4791.8177 | 0.19352 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4967 | NARROWS 21052748 | 153132105 | NARROWS 2105 | 20831.4864 | 12.9469 | 245 | 20.6156 | 0.084145 | 869 | 10537.1631 | 4771.2021 | 0.19269 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9631 | EDENVALE 2107739448 | 82952107 | EDENVALE 2107 | 2860.1443 | 1.7776 | 12 | 1.0093 | 0.084104 | 870 | 10538.9407 | 4770.1929 | 0.19264 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5449 | PENRYN 110351658 | 152561103 | PENRYN 1103 | 13140.1209 | 8.1666 | 108 | 9.0722 | 0.084002 | 871 | 10547.1073 | 4761.1207 | 0.19228 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9940 | MILPITAS 110598568 | 82831105 | MILPITAS 1105 | 168.1421 | 0.1045 | 7 | 0.58797 | 0.083995 | 872 | 10547.2118 | 4760.5327 | 0.19225 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4281 | PUEBLO 1105637242 | 43291105 | PUEBLO 1105 | 27085.716 | 16.8339 | 193 | 16.1913 | 0.083893 | 873 | 10564.0457 | 4744.3414 | 0.1916 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9696 | LAS GALLINAS A 1104507389 | 42991104 | LAS GALLINAS A 1104 | 212.3341 | 0.13197 | 4 | 0.33537 | 0.083842 | 874 | 10564.1776 | 4744.0061 | 0.19159 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3446 | ELK CREEK 11012228 | 102781101 | ELK CREEK 1101 | 5410.2105 | 3.3625 | 80 | 6.6364 | 0.082955 | 875 | 10567.5401 | 4737.3697 | 0.19132 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2644 | WILLITS 110391948 | 42661103 | WILLITS 1103 | 11942.5868 | 7.4224 | 69 | 5.7219 | 0.082927 | 876 | 10574.9625 | 4731.6477 | 0.19109 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2263 | SWIFT 2110XR366 | 83392110 | SWIFT 2110 | 13567.8022 | 8.4324 | 129 | 10.6874 | 0.082848 | 877 | 10583.3949 | 4720.9604 | 0.19066 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9623 | SANTA YNEZ 1104685160 | 182721104 | SANTA YNEZ 1104 | 943.7591 | 0.58655 | 17 | 1.407 | 0.082766 | 878 | 10583.9815 | 4719.5534 | 0.1906 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7942 | FULTON 11024994 | 42561102 | FULTON 1102 | 2185.8295 | 1.3585 | 45 | 3.7244 | 0.082765 | 879 | 10585.34 | 4715.8289 | 0.19045 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4041 | FROGTOWN 1702737236 | 163451702 | FROGTOWN 1702 | 14101.6239 | 8.7642 | 88 | 7.2534 | 0.082425 | 880 | 10594.1042 | 4708.5755 | 0.19016 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4759 | COTATI 110379140 | 42271103 | COTATI 1103 | 15742.3512 | 9.7839 | 154 | 12.6845 | 0.082367 | 881 | 10603.8881 | 4695.891 | 0.18964 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1164 | BEAR VALLEY 2105454432 | 252192105 | BEAR VALLEY 2105 | 23226.2401 | 14.4352 | 112 | 9.221 | 0.08233 | 882 | 10618.3233 | 4686.67 | 0.18927 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4634 | SHINGLE SPRINGS 211051790 | 153652110 | SHINGLE SPRINGS 2110 | 12725.5168 | 7.909 | 106 | 8.7163 | 0.082229 | 883 | 10626.2323 | 4677.9538 | 0.18892 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4491 | CALPELLA 1102144510 | 43411102 | CALPELLA 1102 | 5010.1846 | 3.1138 | 41 | 3.3694 | 0.08218 | 884 | 10629.3461 | 4674.5844 | 0.18878 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3945 | DOBBINS 11015202 | 153741101 | DOBBINS 1101 | 26267.8985 | 16.3256 | 162 | 13.3091 | 0.082155 | 885 | 10645.6717 | 4661.2753 | 0.18825 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5174 | CALAVERAS CEMENT 110111236 | 162211101 | CALAVERAS CEMENT 1101 | 31777.9091 | 19.7501 | 143 | 11.7029 | 0.081838 | 886 | 10665.4218 | 4649.5724 | 0.18777 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4695 | SILVERADO 21043485 | 43432104 | SILVERADO 2104 | 2803.9876 | 1.7427 | 23 | 1.8802 | 0.081749 | 887 | 10667.1645 | 4647.6922 | 0.1877 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5312 | PETALUMA C 1108632 | 42631108 | PETALUMA C 1108 | 23697.8024 | 14.7283 | 81 | 6.6063 | 0.081559 | 888 | 10681.8928 | 4641.0858 | 0.18743 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8333 | BEAR VALLEY 21054609 | 252192105 | BEAR VALLEY 2105 | 7321.9227 | 4.5506 | 41 | 3.3366 | 0.081381 | 889 | 10686.4434 | 4637.7492 | 0.1873 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7354 | JOLON 11027004 | 182981102 | JOLON 1102 | 12745.3246 | 7.9213 | 128 | 10.3759 | 0.081062 | 890 | 10694.3647 | 4627.3733 | 0.18688 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4785 | MORGAN HILL 2111XR398 | 83242111 | MORGAN HILL 2111 | 60665.5292 | 37.7039 | 341 | 27.5412 | 0.080766 | 891 | 10732.0686 | 4599.8321 | 0.18576 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9589 | CLAY 11031821 | 163341103 | CLAY 1103 | 5767.6056 | 3.5846 | 33 | 2.6559 | 0.080483 | 892 | 10735.6531 | 4597.1762 | 0.18566 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1075 | LINCOLN 110195756 | 153701101 | LINCOLN 1101 | 11950.3804 | 7.4272 | 200 | 16.0759 | 0.080379 | 893 | 10743.0804 | 4581.1003 | 0.18501 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3754 | PALMER 1101M82 | 183031101 | PALMER 1101 | 17447.2632 | 10.8435 | 149 | 11.9687 | 0.080327 | 894 | 10753.9239 | 4569.1316 | 0.18452 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5126 | CRESCENT MILLS 21012056 | 103132101 | CRESCENT MILLS 2101 | 8069.9513 | 5.0155 | 70 | 5.6215 | 0.080308 | 895 | 10758.9394 | 4563.51 | 0.1843 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7701 | SILVERADO 2102808 | 43432102 | SILVERADO 2102 | 4081.7731 | 2.5368 | 39 | 3.1317 | 0.0803 | 896 | 10761.4762 | 4560.3783 | 0.18417 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1034 | HOOPA 11013290 | 192401101 | HOOPA 1101 | 21820.8937 | 13.5618 | 135 | 10.8379 | 0.080281 | 897 | 10775.038 | 4549.5404 | 0.18373 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7166 | GANSNER 1101372132 | 103021101 | GANSNER 1101 | 673.2222 | 0.41841 | 13 | 1.0433 | 0.08025 | 898 | 10775.4564 | 4548.4971 | 0.18369 | 4548.4971 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9769 | UKIAH 1111807988 | 42771111 | UKIAH 1111 | 6706.2477 | 4.168 | 15 | 1.2003 | 0.080023 | 899 | 10779.6244 | 4547.2968 | 0.18364 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6682 | OILFIELDS 1103643162 | 182391103 | OILFIELDS 1103 | 5532.3244 | 3.4384 | 41 | 3.2776 | 0.079941 | 900 | 10783.0628 | 4544.0192 | 0.18351 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10896 | CMC 1102CB | 183111102 | CMC 1102 | 581.8342 | 0.36161 | 5 | 0.39953 | 0.079905 | 901 | 10783.4244 | 4543.6197 | 0.18349 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2989 | KONOCTI 11024300 | 43311102 | KONOCTI 1102 | 43384.1036 | 26.9634 | 268 | 21.3893 | 0.079811 | 902 | 10810.3878 | 4522.2304 | 0.18263 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10408 | POSO MOUNTAIN 21011703 | 253642101 | POSO MOUNTAIN 2101 | 1455.5285 | 0.90462 | 7 | 0.55668 | 0.079525 | 903 | 10811.2924 | 4521.6737 | 0.18261 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6364 | PLACERVILLE 2106935216 | 153082106 | PLACERVILLE 2106 | 33848.7529 | 21.0371 | 204 | 16.2127 | 0.079474 | 904 | 10832.3295 | 4505.461 | 0.18195 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4098 | WYANDOTTE 11071510 | 102911107 | WYANDOTTE 1107 | 41028.1557 | 25.4992 | 243 | 19.297 | 0.079411 | 905 | 10857.8287 | 4486.164 | 0.18117 | 4486.164 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7076 | CLARKSVILLE 210419632 | 153612104 | CLARKSVILLE 2104 | 8997.9268 | 5.5922 | 110 | 8.7285 | 0.07935 | 906 | 10863.4209 | 4477.4355 | 0.18082 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1230 | TEMPLETON 2113A08 | 183052113 | TEMPLETON 2113 | 16842.5186 | 10.4677 | 257 | 20.3891 | 0.079335 | 907 | 10873.8886 | 4457.0464 | 0.18 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5155 | FOOTHILL 1101CB | 182951101 | FOOTHILL 1101 | 21554.4713 | 13.3962 | 149 | 11.8181 | 0.079316 | 908 | 10887.2848 | 4445.2283 | 0.17952 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2049 | FRUITLAND 1141CB | 192311141 | FRUITLAND 1141 | 5135.5453 | 3.1918 | 17 | 1.3481 | 0.079299 | 909 | 10890.4766 | 4443.8802 | 0.17947 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4771 | OCEANO 1104Q12 | 182601104 | OCEANO 1104 | 18203.0478 | 11.3133 | 142 | 11.2544 | 0.079257 | 910 | 10901.7898 | 4432.6258 | 0.17901 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10844 | SPRING GAP 1702188426 | 162831702 | SPRING GAP 1702 | 4.572 | 0.0028415 | 1 | 0.078773 | 0.078773 | 911 | 10901.7927 | 4432.547 | 0.17901 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1175 | HIGGINS 11044281 | 152691104 | HIGGINS 1104 | 21439.832 | 13.3249 | 138 | 10.8532 | 0.078646 | 912 | 10915.1176 | 4421.6938 | 0.17857 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9778 | HIGGINS 11097863 | 152691109 | HIGGINS 1109 | 6797.0988 | 4.2244 | 42 | 3.3019 | 0.078616 | 913 | 10919.342 | 4418.3919 | 0.17844 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6230 | MONTICELLO 110193384 | 43051101 | MONTICELLO 1101 | 25967.2197 | 16.1387 | 101 | 7.9369 | 0.078583 | 914 | 10935.4808 | 4410.455 | 0.17812 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9152 | MIDDLETOWN 11011314 | 43141101 | MIDDLETOWN 1101 | 1489.219 | 0.92556 | 13 | 1.0171 | 0.078235 | 915 | 10936.4063 | 4409.438 | 0.17808 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10292 | BIG MEADOWS 21012248 | 102812101 | BIG MEADOWS 2101 | 14727.9744 | 9.1535 | 28 | 2.18 | 0.077859 | 916 | 10945.5598 | 4407.2579 | 0.17799 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3275 | OCEANO 1104Q10 | 182601104 | OCEANO 1104 | 38031.0006 | 23.6364 | 289 | 22.4946 | 0.077836 | 917 | 10969.1963 | 4384.7634 | 0.17708 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5179 | HARTLEY 1102CB | 43211102 | HARTLEY 1102 | 5515.7018 | 3.428 | 135 | 10.5 | 0.077778 | 918 | 10972.6243 | 4374.2633 | 0.17665 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8256 | MORGAN HILL 2105XR268 | 83242105 | MORGAN HILL 2105 | 12802.5937 | 7.9569 | 61 | 4.7333 | 0.077596 | 919 | 10980.5811 | 4369.53 | 0.17646 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1037 | MIDDLETOWN 11021312 | 43141102 | MIDDLETOWN 1102 | 15822.8795 | 9.834 | 120 | 9.3092 | 0.077577 | 920 | 10990.4151 | 4360.2207 | 0.17609 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3607 | OCEANO 1104V38 | 182601104 | OCEANO 1104 | 19405.5321 | 12.0606 | 212 | 16.4392 | 0.077544 | 921 | 11002.4757 | 4343.7815 | 0.17542 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9877 | CLOVERDALE 1102307342 | 42821102 | CLOVERDALE 1102 | 354.0238 | 0.22003 | 6 | 0.46449 | 0.077416 | 922 | 11002.6958 | 4343.317 | 0.17541 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3974 | FITCH MOUNTAIN 111324550 | 42751113 | FITCH MOUNTAIN 1113 | 17797.4846 | 11.0612 | 203 | 15.6996 | 0.077338 | 923 | 11013.757 | 4327.6174 | 0.17477 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
962 | MIDDLETOWN 1102514 | 43141102 | MIDDLETOWN 1102 | 5391.2208 | 3.3507 | 71 | 5.4884 | 0.077302 | 924 | 11017.1076 | 4322.129 | 0.17455 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10365 | CURTIS 170349746 | 163351703 | CURTIS 1703 | 601.9007 | 0.37408 | 3 | 0.23152 | 0.077172 | 925 | 11017.4817 | 4321.8974 | 0.17454 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3098 | PETALUMA C 1108630 | 42631108 | PETALUMA C 1108 | 2654.0652 | 1.6495 | 55 | 4.2442 | 0.077168 | 926 | 11019.1312 | 4317.6532 | 0.17437 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6234 | SAN JUSTO 1101201311 | 183181101 | SAN JUSTO 1101 | 12645.7551 | 7.8594 | 108 | 8.3218 | 0.077053 | 927 | 11026.9906 | 4309.3315 | 0.17403 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6221 | GARBERVILLE 110135706 | 192221101 | GARBERVILLE 1101 | 16269.027 | 10.1113 | 97 | 7.4591 | 0.076898 | 928 | 11037.1019 | 4301.8723 | 0.17373 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2802 | PENRYN 11072410 | 152561107 | PENRYN 1107 | 5248.3008 | 3.2618 | 96 | 7.3678 | 0.076748 | 929 | 11040.3637 | 4294.5045 | 0.17343 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8295 | COTATI 110387402 | 42271103 | COTATI 1103 | 18273.7697 | 11.3572 | 42 | 3.2189 | 0.07664 | 930 | 11051.721 | 4291.2856 | 0.1733 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10268 | TEJON 11023760 | 252931102 | TEJON 1102 | 10415.8967 | 6.4735 | 6 | 0.45904 | 0.076506 | 931 | 11058.1945 | 4290.8266 | 0.17329 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10279 | VOLTA 1102CB | 102541102 | VOLTA 1102 | 5307.8327 | 3.2988 | 25 | 1.9063 | 0.076253 | 932 | 11061.4933 | 4288.9202 | 0.17321 | 4288.9202 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9092 | FORT ROSS 11214614 | 42851121 | FORT ROSS 1121 | 20206.8972 | 12.5587 | 95 | 7.1985 | 0.075773 | 933 | 11074.052 | 4281.7218 | 0.17292 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3923 | AUBERRY 110137536 | 254151101 | AUBERRY 1101 | 8687.6907 | 5.3994 | 60 | 4.5309 | 0.075515 | 934 | 11079.4514 | 4277.1909 | 0.17273 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5756 | CABRILLO 11031437 | 183101103 | CABRILLO 1103 | 4577.3445 | 2.8448 | 39 | 2.9379 | 0.075332 | 935 | 11082.2963 | 4274.2529 | 0.17262 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6109 | FITCH MOUNTAIN 1113583202 | 42751113 | FITCH MOUNTAIN 1113 | 7874.8461 | 4.8942 | 106 | 7.9607 | 0.075101 | 936 | 11087.1905 | 4266.2923 | 0.17229 | 4266.2923 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4163 | WILLITS 1103538 | 42661103 | WILLITS 1103 | 10176.8073 | 6.3249 | 48 | 3.597 | 0.074937 | 937 | 11093.5154 | 4262.6953 | 0.17215 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9780 | SONOMA 1107854266 | 42721107 | SONOMA 1107 | 321.4105 | 0.19976 | 6 | 0.44896 | 0.074827 | 938 | 11093.7152 | 4262.2463 | 0.17213 | 4262.2463 | #N/A | #N/A | #N/A | #N/A | #VALUE!
260 | BRUNSWICK 11067099 | 152481106 | BRUNSWICK 1106 | 12439.4387 | 7.7312 | 83 | 6.2079 | 0.074794 | 939 | 11101.4464 | 4256.0384 | 0.17188 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3084 | GEYSERVILLE 1102274 | 42891102 | GEYSERVILLE 1102 | 10398.2127 | 6.4625 | 173 | 12.9382 | 0.074787 | 940 | 11107.9089 | 4243.1002 | 0.17136 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6342 | MADISON 21011606 | 63172101 | MADISON 2101 | 254.3531 | 0.15808 | 280 | 20.863 | 0.074511 | 941 | 11108.067 | 4222.2372 | 0.17052 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10492 | DRUM 1101CB | 152321101 | DRUM 1101 | 3483.5782 | 2.1651 | 16 | 1.1913 | 0.074456 | 942 | 11110.232 | 4221.0459 | 0.17047 | 4221.0459 | #N/A | #N/A | #N/A | #N/A | #VALUE!
874 | RISING RIVER 1101CB | 103551101 | RISING RIVER 1101 | 15956.2359 | 9.9169 | 121 | 8.9669 | 0.074106 | 943 | 11120.1489 | 4212.0791 | 0.17011 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8386 | PEORIA 1705999 | 163781705 | PEORIA 1705 | 3715.0604 | 2.3089 | 22 | 1.6297 | 0.074075 | 944 | 11122.4578 | 4210.4494 | 0.17004 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7502 | FITCH MOUNTAIN 11136751 | 42751113 | FITCH MOUNTAIN 1113 | 36483.9202 | 22.6749 | 139 | 10.2759 | 0.073927 | 945 | 11145.1327 | 4200.1735 | 0.16962 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5338 | SAN JOAQUIN #3 1102CB | 252531102 | SAN JOAQUIN #3 1102 | 15601.4012 | 9.6963 | 97 | 7.1632 | 0.073848 | 946 | 11154.8291 | 4193.0103 | 0.16933 | 4193.0103 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7052 | CALISTOGA 1101134232 | 42711101 | CALISTOGA 1101 | 2618.9112 | 1.6277 | 89 | 6.5593 | 0.0737 | 947 | 11156.4567 | 4186.451 | 0.16907 | 4186.451 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10249 | SILVERADO 2102CB | 43432102 | SILVERADO 2102 | 952.8122 | 0.59218 | 22 | 1.621 | 0.073682 | 948 | 11157.0489 | 4184.8299 | 0.169 | 4184.8299 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6791 | CABRILLO 1104Y24 | 183101104 | CABRILLO 1104 | 30845.6135 | 19.1707 | 91 | 6.6947 | 0.073569 | 949 | 11176.2196 | 4178.1352 | 0.16873 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3606 | HORSESHOE 1101CB | 152571101 | HORSESHOE 1101 | 567.3027 | 0.35258 | 55 | 4.0458 | 0.073561 | 950 | 11176.5721 | 4174.0894 | 0.16857 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2673 | PUEBLO 2102792 | 43292102 | PUEBLO 2102 | 31119.1615 | 19.3407 | 180 | 13.2101 | 0.073389 | 951 | 11195.9128 | 4160.8793 | 0.16804 | 4160.8793 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4637 | SAN LUIS OBISPO 1104V40 | 182631104 | SAN LUIS OBISPO 1104 | 23652.2282 | 14.7 | 194 | 14.2374 | 0.073389 | 952 | 11210.6128 | 4146.6419 | 0.16746 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2241 | CURTIS 170247488 | 163351702 | CURTIS 1702 | 30588.7641 | 19.011 | 207 | 15.1897 | 0.07338 | 953 | 11229.6238 | 4131.4522 | 0.16685 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9651 | PURISIMA 1101Y44 | 182971101 | PURISIMA 1101 | 16745.9311 | 10.4077 | 45 | 3.2983 | 0.073295 | 954 | 11240.0315 | 4128.1539 | 0.16672 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1008 | TEMPLETON 2113A70 | 183052113 | TEMPLETON 2113 | 39764.0285 | 24.7135 | 659 | 48.2106 | 0.073157 | 955 | 11264.745 | 4079.9434 | 0.16477 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3782 | AUBERRY 1101R322 | 254151101 | AUBERRY 1101 | 12336.4699 | 7.6672 | 44 | 3.2149 | 0.073065 | 956 | 11272.4122 | 4076.7285 | 0.16464 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
700 | MERCED FALLS 11029460 | 252811102 | MERCED FALLS 1102 | 17926.192 | 11.1412 | 91 | 6.6443 | 0.073014 | 957 | 11283.5534 | 4070.0842 | 0.16437 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1286 | CURTIS 170384944 | 163351703 | CURTIS 1703 | 93674.3078 | 58.219 | 439 | 31.9262 | 0.072725 | 958 | 11341.7723 | 4038.158 | 0.16308 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8476 | ALTO 1124810594 | 42031124 | ALTO 1124 | 899.4073 | 0.55899 | 6 | 0.4361 | 0.072684 | 959 | 11342.3313 | 4037.7219 | 0.16306 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1350 | PENRYN 1107CB | 152561107 | PENRYN 1107 | 8735.2446 | 5.429 | 200 | 14.5295 | 0.072647 | 960 | 11347.7603 | 4023.1925 | 0.16248 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10196 | SANTA YNEZ 1101980192 | 182721101 | SANTA YNEZ 1101 | 6178.6453 | 3.8401 | 19 | 1.3793 | 0.072592 | 961 | 11351.6004 | 4021.8132 | 0.16242 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4126 | VACAVILLE 1104CB | 63601104 | VACAVILLE 1104 | 696.6837 | 0.43299 | 36 | 2.5999 | 0.07222 | 962 | 11352.0333 | 4019.2133 | 0.16232 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6142 | JOLON 1103CB | 182981103 | JOLON 1103 | 21174.1488 | 13.1598 | 91 | 6.5613 | 0.072102 | 963 | 11365.1932 | 4012.652 | 0.16205 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4505 | LOW GAP 11014086 | 192411101 | LOW GAP 1101 | 18494.2051 | 11.4942 | 66 | 4.7585 | 0.072098 | 964 | 11376.6874 | 4007.8935 | 0.16186 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5220 | COTATI 1103132 | 42271103 | COTATI 1103 | 40702.0776 | 25.2965 | 184 | 13.2468 | 0.071994 | 965 | 11401.9839 | 3994.6467 | 0.16132 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2886 | VOLTA 11011596 | 102541101 | VOLTA 1101 | 35104.5465 | 21.8176 | 132 | 9.4937 | 0.071922 | 966 | 11423.8015 | 3985.1529 | 0.16094 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7748 | PEORIA 170413490 | 163781704 | PEORIA 1704 | 6875.4256 | 4.2731 | 49 | 3.522 | 0.071878 | 967 | 11428.0746 | 3981.6309 | 0.1608 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1885 | OREGON TRAIL 110249144 | 103521102 | OREGON TRAIL 1102 | 29574.1503 | 18.3805 | 169 | 12.0855 | 0.071512 | 968 | 11446.4551 | 3969.5454 | 0.16031 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3676 | COTTONWOOD 1101CB | 102931101 | COTTONWOOD 1101 | 184.0196 | 0.11437 | 188 | 13.442 | 0.0715 | 969 | 11446.5694 | 3956.1035 | 0.15977 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7714 | FROGTOWN 17027134 | 163451702 | FROGTOWN 1702 | 32518.1243 | 20.2101 | 172 | 12.2631 | 0.071297 | 970 | 11466.7796 | 3943.8404 | 0.15927 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4319 | MESA 11016111 | 182821101 | MESA 1101 | 39023.9015 | 24.2535 | 202 | 14.3729 | 0.071153 | 971 | 11491.0331 | 3929.4675 | 0.15869 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5571 | CLEAR LAKE 1101740076 | 42141101 | CLEAR LAKE 1101 | 632.3767 | 0.39302 | 106 | 7.5335 | 0.071071 | 972 | 11491.4261 | 3921.934 | 0.15839 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9268 | OLETA 1102799924 | 163541102 | OLETA 1102 | 621.6151 | 0.38634 | 4 | 0.28327 | 0.070818 | 973 | 11491.8125 | 3921.6507 | 0.15838 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1141 | BELL 1109724884 | 152701109 | BELL 1109 | 22589.092 | 14.0392 | 167 | 11.822 | 0.070791 | 974 | 11505.8517 | 3909.8287 | 0.1579 | 3909.8287 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9406 | EDENVALE 2107469810 | 82952107 | EDENVALE 2107 | 3464.1714 | 2.153 | 14 | 0.98941 | 0.070672 | 975 | 11508.0047 | 3908.8393 | 0.15786 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2788 | WYANDOTTE 1110980944 | 102911110 | WYANDOTTE 1110 | 16783.2453 | 10.4309 | 198 | 13.9721 | 0.070566 | 976 | 11518.4355 | 3894.8671 | 0.15729 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3339 | JESSUP 110276068 | 103441102 | JESSUP 1102 | 27642.9269 | 17.1802 | 232 | 16.3207 | 0.070348 | 977 | 11535.6157 | 3878.5465 | 0.15664 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6626 | CLAY 1101CB | 163341101 | CLAY 1101 | 914.1112 | 0.56812 | 33 | 2.3145 | 0.070136 | 978 | 11536.1838 | 3876.232 | 0.15654 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9158 | COVELO 1101306476 | 43061101 | COVELO 1101 | 3106.377 | 1.9306 | 49 | 3.4228 | 0.069853 | 979 | 11538.1145 | 3872.8092 | 0.1564 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5752 | MONTICELLO 110165454 | 43051101 | MONTICELLO 1101 | 2176.3172 | 1.3526 | 23 | 1.6007 | 0.069594 | 980 | 11539.4671 | 3871.2085 | 0.15634 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2727 | OREGON TRAIL 11031500 | 103521103 | OREGON TRAIL 1103 | 41880.4686 | 26.0289 | 261 | 18.1383 | 0.069495 | 981 | 11565.4959 | 3853.0702 | 0.15561 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10741 | HALF MOON BAY 11038920 | 24101103 | HALF MOON BAY 1103 | 158.1242 | 0.098275 | 2 | 0.13895 | 0.069477 | 982 | 11565.5942 | 3852.9313 | 0.1556 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2684 | BEAR VALLEY 210110000 | 252192101 | BEAR VALLEY 2101 | 47097.1904 | 29.2711 | 230 | 15.9156 | 0.069198 | 983 | 11594.8653 | 3837.0157 | 0.15496 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1190 | OCEANO 1104V36 | 182601104 | OCEANO 1104 | 18028.895 | 11.205 | 150 | 10.3677 | 0.069118 | 984 | 11606.0703 | 3826.648 | 0.15454 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9260 | DIAMOND SPRINGS 110777086 | 152261107 | DIAMOND SPRINGS 1107 | 4371.5846 | 2.717 | 47 | 3.2429 | 0.068998 | 985 | 11608.7873 | 3823.4051 | 0.15441 | 3823.4051 | #N/A | #N/A | #N/A | #N/A | #VALUE!
87 | CORNING 110185152 | 103331101 | CORNING 1101 | 37332.1384 | 23.2021 | 279 | 19.2463 | 0.068983 | 986 | 11631.9894 | 3804.1589 | 0.15363 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2893 | UKIAH 1114544 | 42771114 | UKIAH 1114 | 786.2676 | 0.48867 | 98 | 6.7406 | 0.068781 | 987 | 11632.478 | 3797.4183 | 0.15336 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
69 | BROWNS VALLEY 110197188 | 152921101 | BROWNS VALLEY 1101 | 10919.7899 | 6.7867 | 71 | 4.8715 | 0.068613 | 988 | 11639.2647 | 3792.5468 | 0.15316 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1342 | AUBERRY 1101R2838 | 254151101 | AUBERRY 1101 | 32896.73 | 20.4455 | 210 | 14.3942 | 0.068544 | 989 | 11659.7102 | 3778.1526 | 0.15258 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9647 | GARCIA 0401CB | 43040401 | GARCIA 0401 | 46.711 | 0.029031 | 1 | 0.068469 | 0.068469 | 990 | 11659.7392 | 3778.0841 | 0.15258 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2407 | FROGTOWN 1702835115 | 163451702 | FROGTOWN 1702 | 29192.1081 | 18.143 | 191 | 13.0639 | 0.068398 | 991 | 11677.8822 | 3765.0202 | 0.15205 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3939 | ZACA 1101Y70 | 182681101 | ZACA 1101 | 10839.1211 | 6.7366 | 61 | 4.1658 | 0.068291 | 992 | 11684.6188 | 3760.8544 | 0.15188 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3966 | SAN BENITO 2101295566 | 182742101 | SAN BENITO 2101 | 751.534 | 0.46708 | 18 | 1.2287 | 0.068263 | 993 | 11685.0859 | 3759.6257 | 0.15183 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1800 | BANGOR 11011804 | 103191101 | BANGOR 1101 | 69024.1301 | 42.8988 | 394 | 26.8697 | 0.068197 | 994 | 11727.9846 | 3732.756 | 0.15075 | 3732.756 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1078 | BIG MEADOWS 21012260 | 102812101 | BIG MEADOWS 2101 | 25414.2279 | 15.795 | 185 | 12.5404 | 0.067786 | 995 | 11743.7797 | 3720.2156 | 0.15024 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8083 | ANDERSON 1101583708 | 103261101 | ANDERSON 1101 | 1011.3641 | 0.62857 | 11 | 0.74538 | 0.067762 | 996 | 11744.4082 | 3719.4702 | 0.15021 | 3719.4702 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6638 | SAN RAMON 2117CB | 14232117 | SAN RAMON 2117 | 1098.894 | 0.68297 | 23 | 1.5576 | 0.067722 | 997 | 11745.0912 | 3717.9126 | 0.15015 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7538 | CABRILLO 1103Y46 | 183101103 | CABRILLO 1103 | 50653.8838 | 31.4816 | 277 | 18.7037 | 0.067522 | 998 | 11776.5728 | 3699.2089 | 0.14939 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4175 | MARTELL 1101CB | 163011101 | MARTELL 1101 | 9459.2642 | 5.879 | 171 | 11.5263 | 0.067405 | 999 | 11782.4518 | 3687.6826 | 0.14893 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9619 | PETALUMA C 1108456397 | 42631108 | PETALUMA C 1108 | 2239.0721 | 1.3916 | 19 | 1.2792 | 0.067328 | 1000 | 11783.8434 | 3686.4034 | 0.14888 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3701 | FRENCH GULCH 1101CB | 103381101 | FRENCH GULCH 1101 | 3697.5337 | 2.298 | 32 | 2.1534 | 0.067293 | 1001 | 11786.1414 | 3684.25 | 0.14879 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4093 | RED BLUFF 1105146070 | 103541105 | RED BLUFF 1105 | 20479.5896 | 12.7281 | 167 | 11.191 | 0.067012 | 1002 | 11798.8695 | 3673.059 | 0.14834 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1562 | LAYTONVILLE 110264908 | 42681102 | LAYTONVILLE 1102 | 6238.0239 | 3.877 | 84 | 5.6276 | 0.066995 | 1003 | 11802.7465 | 3667.4314 | 0.14811 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7452 | SAN RAMON 210853732 | 14232108 | SAN RAMON 2108 | 12542.8 | 7.7954 | 77 | 5.1484 | 0.066862 | 1004 | 11810.5419 | 3662.283 | 0.1479 | 3662.283 | #N/A | #N/A | #N/A | #N/A | #VALUE!
509 | CALISTOGA 110143924 | 42711101 | CALISTOGA 1101 | 12523.7999 | 7.7836 | 107 | 7.1532 | 0.066852 | 1005 | 11818.3255 | 3655.1298 | 0.14761 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2808 | PASO ROBLES 1104P02 | 182611104 | PASO ROBLES 1104 | 515.0322 | 0.32009 | 93 | 6.2143 | 0.06682 | 1006 | 11818.6456 | 3648.9155 | 0.14736 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6977 | CLOVERDALE 1102172096 | 42821102 | CLOVERDALE 1102 | 425.5098 | 0.26446 | 12 | 0.79884 | 0.06657 | 1007 | 11818.9101 | 3648.1167 | 0.14733 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6400 | PHILO 1102CB | 42601102 | PHILO 1102 | 12387.7147 | 7.699 | 131 | 8.7089 | 0.06648 | 1008 | 11826.6091 | 3639.4078 | 0.14698 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1390 | CURTIS 170539256 | 163351705 | CURTIS 1705 | 42581.0612 | 26.4643 | 287 | 19.0271 | 0.066296 | 1009 | 11853.0734 | 3620.3808 | 0.14621 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9080 | SUMMIT 110249484 | 152591102 | SUMMIT 1102 | 4257.4421 | 2.646 | 27 | 1.7893 | 0.06627 | 1010 | 11855.7194 | 3618.5915 | 0.14614 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
493 | BRUNSWICK 11102664 | 152481110 | BRUNSWICK 1110 | 12910.8902 | 8.0242 | 132 | 8.7364 | 0.066185 | 1011 | 11863.7436 | 3609.8551 | 0.14578 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6828 | SILVERADO 210298998 | 43432102 | SILVERADO 2102 | 118.1019 | 0.073401 | 136 | 8.9779 | 0.066014 | 1012 | 11863.817 | 3600.8772 | 0.14542 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
828 | ATASCADERO 1103A18 | 182541103 | ATASCADERO 1103 | 14189.3642 | 8.8187 | 188 | 12.4068 | 0.065994 | 1013 | 11872.6357 | 3588.4703 | 0.14492 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7881 | CALISTOGA 1102141073 | 42711102 | CALISTOGA 1102 | 1996.4523 | 1.2408 | 27 | 1.7745 | 0.065722 | 1014 | 11873.8765 | 3586.6958 | 0.14485 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5591 | CURTIS 17029220 | 163351702 | CURTIS 1702 | 17704.0281 | 11.0031 | 123 | 8.0763 | 0.065661 | 1015 | 11884.8796 | 3578.6196 | 0.14452 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1187 | PENRYN 11051342 | 152561105 | PENRYN 1105 | 33351.1972 | 20.7279 | 440 | 28.7609 | 0.065366 | 1016 | 11905.6075 | 3549.8587 | 0.14336 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8143 | CLAYTON 2215W531R | 12022215 | CLAYTON 2215 | 10443.673 | 6.4908 | 100 | 6.5356 | 0.065356 | 1017 | 11912.0983 | 3543.3231 | 0.1431 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2291 | SHINGLE SPRINGS 210913322 | 153652109 | SHINGLE SPRINGS 2109 | 66617.6825 | 41.4032 | 490 | 32.0124 | 0.065331 | 1018 | 11953.5015 | 3511.3107 | 0.1418 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2286 | BEAR VALLEY 210521160 | 252192105 | BEAR VALLEY 2105 | 38269.4773 | 23.7846 | 194 | 12.6462 | 0.065187 | 1019 | 11977.2861 | 3498.6645 | 0.14129 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9841 | MESA 1103126697 | 182821103 | MESA 1103 | 1641.863 | 1.0204 | 10 | 0.65062 | 0.065062 | 1020 | 11978.3065 | 3498.0139 | 0.14127 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9670 | FRENCH GULCH 1102CB | 103381102 | FRENCH GULCH 1102 | 2729.0129 | 1.6961 | 12 | 0.77689 | 0.06474 | 1021 | 11980.0026 | 3497.237 | 0.14124 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2589 | FORT ROSS 1121124 | 42851121 | FORT ROSS 1121 | 29762.4384 | 18.4975 | 99 | 6.3951 | 0.064597 | 1022 | 11998.5001 | 3490.8419 | 0.14098 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2518 | OCEANO 1104Q08 | 182601104 | OCEANO 1104 | 19981.628 | 12.4187 | 148 | 9.5547 | 0.064559 | 1023 | 12010.9188 | 3481.2872 | 0.14059 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10030 | MC ARTHUR 1102542920 | 103491102 | MC ARTHUR 1102 | 2034.8319 | 1.2647 | 10 | 0.64427 | 0.064427 | 1024 | 12012.1834 | 3480.6429 | 0.14057 | 3480.6429 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4185 | PASO ROBLES 1104R12 | 182611104 | PASO ROBLES 1104 | 52796.2686 | 32.8131 | 278 | 17.8868 | 0.064341 | 1025 | 12044.9965 | 3462.7561 | 0.13984 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7956 | JESSUP 11011993 | 103441101 | JESSUP 1101 | 4470.3512 | 2.7783 | 39 | 2.5043 | 0.064212 | 1026 | 12047.7749 | 3460.2518 | 0.13974 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10640 | CALISTOGA 110266730 | 42711102 | CALISTOGA 1102 | 1703.3079 | 1.0586 | 6 | 0.38421 | 0.064035 | 1027 | 12048.8335 | 3459.8676 | 0.13973 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9262 | LAKEVILLE 110287432 | 43371102 | LAKEVILLE 1102 | 15708.5355 | 9.7629 | 81 | 5.176 | 0.063901 | 1028 | 12058.5964 | 3454.6916 | 0.13952 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6678 | MIDDLETOWN 11011325 | 43141101 | MIDDLETOWN 1101 | 13829.5499 | 8.5951 | 80 | 5.0891 | 0.063613 | 1029 | 12067.1915 | 3449.6025 | 0.13931 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5737 | UKIAH 11151216 | 42771115 | UKIAH 1115 | 21628.5531 | 13.4422 | 182 | 11.561 | 0.063522 | 1030 | 12080.6337 | 3438.0415 | 0.13885 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1518 | DIAMOND SPRINGS 110518935 | 152261105 | DIAMOND SPRINGS 1105 | 10773.8274 | 6.696 | 76 | 4.805 | 0.063224 | 1031 | 12087.3297 | 3433.2365 | 0.13865 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8962 | TEMPLETON 2110N30 | 183052110 | TEMPLETON 2110 | 32768.3238 | 20.3656 | 120 | 7.5782 | 0.063152 | 1032 | 12107.6954 | 3425.6583 | 0.13835 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5800 | CLARK ROAD 11022070 | 103091102 | CLARK ROAD 1102 | 14786.6222 | 9.1899 | 72 | 4.5436 | 0.063106 | 1033 | 12116.8853 | 3421.1147 | 0.13816 | 3421.1147 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1728 | TEMPLETON 2112116402 | 183052112 | TEMPLETON 2112 | 3810.8828 | 2.3685 | 64 | 4.0307 | 0.062979 | 1034 | 12119.2538 | 3417.084 | 0.138 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
727 | APPLE HILL 2102186912 | 153662102 | APPLE HILL 2102 | 94273.5723 | 58.5914 | 606 | 38.1293 | 0.06292 | 1035 | 12177.8452 | 3378.9548 | 0.13646 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7181 | BEAR VALLEY 21054170 | 252192105 | BEAR VALLEY 2105 | 15319.6405 | 9.5212 | 45 | 2.8251 | 0.062779 | 1036 | 12187.3664 | 3376.1297 | 0.13635 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8856 | GARBERVILLE 11028189 | 192221102 | GARBERVILLE 1102 | 1685.4401 | 1.0475 | 11 | 0.68809 | 0.062553 | 1037 | 12188.4139 | 3375.4416 | 0.13632 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1917 | PANORAMA 1101CB | 103461101 | PANORAMA 1101 | 1828.844 | 1.1366 | 175 | 10.9155 | 0.062374 | 1038 | 12189.5506 | 3364.5261 | 0.13588 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9789 | TASSAJARA 2106203380 | 14662106 | TASSAJARA 2106 | 809.5956 | 0.50317 | 26 | 1.6207 | 0.062335 | 1039 | 12190.0537 | 3362.9054 | 0.13581 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8449 | VACAVILLE 111112342 | 63601111 | VACAVILLE 1111 | 352.0949 | 0.21883 | 16 | 0.99668 | 0.062293 | 1040 | 12190.2726 | 3361.9087 | 0.13577 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3572 | OLETA 110113478 | 163541101 | OLETA 1101 | 19846.6513 | 12.3348 | 169 | 10.5049 | 0.062159 | 1041 | 12202.6073 | 3351.4038 | 0.13535 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1028 | LOW GAP 11012094 | 192411101 | LOW GAP 1101 | 25248.6295 | 15.6921 | 139 | 8.6323 | 0.062103 | 1042 | 12218.2995 | 3342.7715 | 0.135 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3105 | NOTRE DAME 11042028 | 102041104 | NOTRE DAME 1104 | 17437.7183 | 10.8376 | 86 | 5.3333 | 0.062015 | 1043 | 12229.1371 | 3337.4382 | 0.13478 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2667 | FROGTOWN 170212282 | 163451702 | FROGTOWN 1702 | 58482.1143 | 36.3469 | 261 | 16.1631 | 0.061928 | 1044 | 12265.4839 | 3321.2751 | 0.13413 | 3321.2751 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7606 | NOTRE DAME 11042537 | 102041104 | NOTRE DAME 1104 | 8030.1143 | 4.9907 | 37 | 2.2852 | 0.061762 | 1045 | 12270.4747 | 3318.9899 | 0.13404 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2093 | ATASCADERO 1103A46 | 182541103 | ATASCADERO 1103 | 633.1098 | 0.39348 | 94 | 5.8045 | 0.06175 | 1046 | 12270.8682 | 3313.1854 | 0.1338 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7485 | SHINGLE SPRINGS 210551738 | 153652105 | SHINGLE SPRINGS 2105 | 26.6806 | 0.016582 | 19 | 1.1697 | 0.061564 | 1047 | 12270.8847 | 3312.0157 | 0.13376 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
284 | PERRY 1101V78 | 183071101 | PERRY 1101 | 47471.3302 | 29.5036 | 164 | 10.0783 | 0.061453 | 1048 | 12300.3884 | 3301.9374 | 0.13335 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10468 | CALPINE 1144962 | 48011144 | CALPINE 1144 | 63.3636 | 0.039381 | 1 | 0.061428 | 0.061428 | 1049 | 12300.4278 | 3301.876 | 0.13335 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8597 | ORO FINO 1102127563 | 103031102 | ORO FINO 1102 | 11105.9314 | 6.9024 | 63 | 3.8642 | 0.061336 | 1050 | 12307.3301 | 3298.0118 | 0.13319 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6425 | MADISON 2101351038 | 63172101 | MADISON 2101 | 2661.6552 | 1.6542 | 130 | 7.971 | 0.061316 | 1051 | 12308.9844 | 3290.0408 | 0.13287 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5524 | JESSUP 11011496 | 103441101 | JESSUP 1101 | 23526.9728 | 14.6221 | 201 | 12.3032 | 0.06121 | 1052 | 12323.6065 | 3277.7376 | 0.13237 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10127 | SPAULDING 1101CB | 152251101 | SPAULDING 1101 | 56.7484 | 0.035269 | 1 | 0.061207 | 0.061207 | 1053 | 12323.6417 | 3277.6764 | 0.13237 | 3277.6764 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4318 | HIGGINS 11102408 | 152691110 | HIGGINS 1110 | 18614.5661 | 11.569 | 124 | 7.5471 | 0.060864 | 1054 | 12335.2108 | 3270.1292 | 0.13206 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7906 | PIT NO 7 1101CB | 103501101 | PIT NO 7 1101 | 4357.8457 | 2.7084 | 3 | 0.18246 | 0.060819 | 1055 | 12337.9192 | 3269.9468 | 0.13206 | 3269.9468 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7035 | SYCAMORE CREEK 1111CB | 102971111 | SYCAMORE CREEK 1111 | 777.7423 | 0.48337 | 85 | 5.1608 | 0.060715 | 1056 | 12338.4026 | 3264.786 | 0.13185 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4688 | UPPER LAKE 1101452 | 42871101 | UPPER LAKE 1101 | 8129.076 | 5.0523 | 207 | 12.5666 | 0.060708 | 1057 | 12343.4548 | 3252.2194 | 0.13134 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7853 | CLOVERDALE 1102670 | 42821102 | CLOVERDALE 1102 | 587.1475 | 0.36491 | 43 | 2.6041 | 0.06056 | 1058 | 12343.8197 | 3249.6153 | 0.13124 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9980 | BRIDGEVILLE 1101CB | 192461101 | BRIDGEVILLE 1101 | 13703.2012 | 8.5166 | 51 | 3.0852 | 0.060495 | 1059 | 12352.3363 | 3246.53 | 0.13111 | 3246.53 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3075 | REDBUD 11022013 | 43191102 | REDBUD 1102 | 238.9679 | 0.14852 | 51 | 3.0845 | 0.06048 | 1060 | 12352.4848 | 3243.4455 | 0.13099 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
377 | FROGTOWN 1702L5407 | 163451702 | FROGTOWN 1702 | 29410.8857 | 18.279 | 153 | 9.2508 | 0.060463 | 1061 | 12370.7638 | 3234.1948 | 0.13061 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
599 | CURTIS 170356972 | 163351703 | CURTIS 1703 | 13791.0471 | 8.5712 | 57 | 3.4306 | 0.060186 | 1062 | 12379.335 | 3230.7642 | 0.13047 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9546 | COTATI 1102CB | 42271102 | COTATI 1102 | 2904.3184 | 1.805 | 19 | 1.137 | 0.05984 | 1063 | 12381.1401 | 3229.6272 | 0.13043 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9754 | CALPELLA 1102708161 | 43411102 | CALPELLA 1102 | 1615.0007 | 1.0037 | 12 | 0.71527 | 0.059606 | 1064 | 12382.1438 | 3228.9119 | 0.1304 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7941 | FRUITLAND 11426064 | 192311142 | FRUITLAND 1142 | 10776.9352 | 6.6979 | 66 | 3.928 | 0.059515 | 1065 | 12388.8417 | 3224.9839 | 0.13024 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1172 | CORRAL 110336680 | 162991103 | CORRAL 1103 | 15055.3944 | 9.357 | 265 | 15.7601 | 0.059472 | 1066 | 12398.1987 | 3209.2239 | 0.1296 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7127 | SONOMA 1107844168 | 42721107 | SONOMA 1107 | 7309.0201 | 4.5426 | 100 | 5.9437 | 0.059437 | 1067 | 12402.7413 | 3203.2802 | 0.12936 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2372 | GRASS VALLEY 11032110 | 152031103 | GRASS VALLEY 1103 | 31798.2221 | 19.7627 | 224 | 13.3106 | 0.059423 | 1068 | 12422.504 | 3189.9695 | 0.12883 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2173 | PUEBLO 1105696 | 43291105 | PUEBLO 1105 | 6037.9333 | 3.7526 | 79 | 4.663 | 0.059025 | 1069 | 12426.2566 | 3185.3066 | 0.12864 | 3185.3066 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2604 | JESSUP 11031540 | 103441103 | JESSUP 1103 | 256.3874 | 0.15935 | 157 | 9.2418 | 0.058865 | 1070 | 12426.4159 | 3176.0648 | 0.12827 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8024 | PENRYN 11072708 | 152561107 | PENRYN 1107 | 15094.9992 | 9.3816 | 124 | 7.2881 | 0.058775 | 1071 | 12435.7975 | 3168.7766 | 0.12797 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
660 | GABILAN 1101460414 | 182331101 | GABILAN 1101 | 8655.1604 | 5.3792 | 38 | 2.2313 | 0.058719 | 1072 | 12441.1768 | 3166.5453 | 0.12788 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2838 | MENDOCINO 110148750 | 42951101 | MENDOCINO 1101 | 28839.2375 | 17.9237 | 165 | 9.6724 | 0.058621 | 1073 | 12459.1005 | 3156.8729 | 0.12749 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5642 | ALHAMBRA 110582622 | 14101105 | ALHAMBRA 1105 | 41703.3816 | 25.9188 | 254 | 14.8609 | 0.058508 | 1074 | 12485.0193 | 3142.012 | 0.12689 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5965 | JOLON 1102CB | 182981102 | JOLON 1102 | 37939.8486 | 23.5798 | 181 | 10.5701 | 0.058399 | 1075 | 12508.5991 | 3131.4419 | 0.12646 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5646 | SANTA YNEZ 1104512912 | 182721104 | SANTA YNEZ 1104 | 1435.1217 | 0.89193 | 23 | 1.3428 | 0.058383 | 1076 | 12509.491 | 3130.099 | 0.12641 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1584 | COLUMBIA HILL 1101CB | 152471101 | COLUMBIA HILL 1101 | 63324.3345 | 39.3563 | 375 | 21.8875 | 0.058367 | 1077 | 12548.8473 | 3108.2116 | 0.12553 | 3108.2116 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8255 | CRESCENT MILLS 21012562 | 103132101 | CRESCENT MILLS 2101 | 31122.7322 | 19.3429 | 222 | 12.8572 | 0.057915 | 1078 | 12568.1902 | 3095.3543 | 0.12501 | 3095.3543 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2533 | MOLINO 1101338 | 42571101 | MOLINO 1101 | 12496.8829 | 7.7669 | 176 | 10.1921 | 0.05791 | 1079 | 12575.9571 | 3085.1622 | 0.12459 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9899 | LLAGAS 21014523 | 83182101 | LLAGAS 2101 | 1471.0588 | 0.91427 | 28 | 1.6186 | 0.057806 | 1080 | 12576.8714 | 3083.5436 | 0.12453 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10017 | PASO ROBLES 1107289947 | 182611107 | PASO ROBLES 1107 | 447.6357 | 0.27821 | 21 | 1.2108 | 0.057658 | 1081 | 12577.1496 | 3082.3328 | 0.12448 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
451 | CALISTOGA 11011087 | 42711101 | CALISTOGA 1101 | 3157.1282 | 1.9622 | 22 | 1.2681 | 0.05764 | 1082 | 12579.1117 | 3081.0648 | 0.12443 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
90 | TYLER 1105816852 | 103571105 | TYLER 1105 | 20545.6876 | 12.7692 | 423 | 24.3431 | 0.057549 | 1083 | 12591.881 | 3056.7217 | 0.12345 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
67 | WOODACRE 1102CB | 43021102 | WOODACRE 1102 | 20085.8093 | 12.4834 | 141 | 8.1136 | 0.057543 | 1084 | 12604.3644 | 3048.6081 | 0.12312 | 3048.6081 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3103 | JOLON 11027070 | 182981102 | JOLON 1102 | 10307.0829 | 6.4059 | 132 | 7.5892 | 0.057494 | 1085 | 12610.7703 | 3041.0189 | 0.12281 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6894 | DESCHUTES 11011654 | 103351101 | DESCHUTES 1101 | 28221.2564 | 17.5396 | 168 | 9.6576 | 0.057486 | 1086 | 12628.3099 | 3031.3613 | 0.12242 | 3031.3613 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1819 | ALTO 11243745 | 42031124 | ALTO 1124 | 7247.2343 | 4.5042 | 52 | 2.9856 | 0.057415 | 1087 | 12632.8141 | 3028.3757 | 0.1223 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1989 | ELECTRA 1101CB | 162161101 | ELECTRA 1101 | 50985.8349 | 31.6879 | 293 | 16.8213 | 0.05741 | 1088 | 12664.502 | 3011.5544 | 0.12162 | 3011.5544 | #N/A | #N/A | #N/A | #N/A | #VALUE!
994 | BUTTE 1105751990 | 103081105 | BUTTE 1105 | 39436.6029 | 24.51 | 243 | 13.9439 | 0.057382 | 1089 | 12689.012 | 2997.6106 | 0.12106 | 2997.6106 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7429 | MOUNTAIN QUARRIES 210151584 | 152282101 | MOUNTAIN QUARRIES 2101 | 35041.5534 | 21.7785 | 224 | 12.8393 | 0.057318 | 1090 | 12710.7905 | 2984.7712 | 0.12054 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7628 | WISE 11011404 | 152271101 | WISE 1101 | 2402.8891 | 1.4934 | 47 | 2.6884 | 0.057199 | 1091 | 12712.2839 | 2982.0829 | 0.12043 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7386 | SAN RAMON 2108CB | 14232108 | SAN RAMON 2108 | 14012.7161 | 8.709 | 102 | 5.8326 | 0.057183 | 1092 | 12720.9928 | 2976.2502 | 0.1202 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9327 | CALISTOGA 110189150 | 42711101 | CALISTOGA 1101 | 15332.2939 | 9.5291 | 88 | 5.029 | 0.057148 | 1093 | 12730.5219 | 2971.2212 | 0.11999 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4436 | SAN RAMON 2119CB | 14232119 | SAN RAMON 2119 | 1187.935 | 0.73831 | 21 | 1.199 | 0.057097 | 1094 | 12731.2602 | 2970.0222 | 0.11994 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4471 | ELECTRA 11024756 | 162161102 | ELECTRA 1102 | 15139.4165 | 9.4092 | 95 | 5.4181 | 0.057032 | 1095 | 12740.6694 | 2964.6041 | 0.11973 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10516 | GARBERVILLE 11022124 | 192221102 | GARBERVILLE 1102 | 5026.2322 | 3.1238 | 6 | 0.34203 | 0.057006 | 1096 | 12743.7932 | 2964.2621 | 0.11971 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10428 | ANNAPOLIS 1101CB | 42861101 | ANNAPOLIS 1101 | 1058.7166 | 0.658 | 7 | 0.39904 | 0.057005 | 1097 | 12744.4512 | 2963.863 | 0.1197 | 2963.863 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5436 | TEMPLETON 2110901690 | 183052110 | TEMPLETON 2110 | 60028.2631 | 37.3078 | 306 | 17.4196 | 0.056927 | 1098 | 12781.759 | 2946.4434 | 0.11899 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1208 | HOPLAND 1101CB | 42251101 | HOPLAND 1101 | 23579.7024 | 14.6549 | 190 | 10.8047 | 0.056867 | 1099 | 12796.4139 | 2935.6387 | 0.11856 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
582 | SWIFT 2110853720 | 83392110 | SWIFT 2110 | 50276.8108 | 31.2472 | 140 | 7.9275 | 0.056625 | 1100 | 12827.6612 | 2927.7112 | 0.11824 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6471 | SALMON CREEK 110137368 | 43161101 | SALMON CREEK 1101 | 9786.5772 | 6.0824 | 48 | 2.7166 | 0.056596 | 1101 | 12833.7436 | 2924.9946 | 0.11813 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7036 | WOODACRE 1101CB | 43021101 | WOODACRE 1101 | 4454.6417 | 2.7686 | 35 | 1.9778 | 0.056508 | 1102 | 12836.5121 | 2923.0168 | 0.11805 | 2923.0168 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9354 | FRUITLAND 114137410 | 192311141 | FRUITLAND 1141 | 8413.1179 | 5.2288 | 42 | 2.3718 | 0.056472 | 1103 | 12841.7409 | 2920.645 | 0.11795 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8408 | GOLDTREE 1105CB | 182581105 | GOLDTREE 1105 | 11908.479 | 7.4012 | 76 | 4.29 | 0.056447 | 1104 | 12849.1421 | 2916.355 | 0.11778 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1036 | FRUITLAND 1142CB | 192311142 | FRUITLAND 1142 | 16900.9683 | 10.504 | 116 | 6.5332 | 0.056321 | 1105 | 12859.6461 | 2909.8218 | 0.11751 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5437 | FITCH MOUNTAIN 1113775992 | 42751113 | FITCH MOUNTAIN 1113 | 3381.5311 | 2.1016 | 34 | 1.9125 | 0.056251 | 1106 | 12861.7477 | 2907.9093 | 0.11744 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8868 | SALMON CREEK 1101461703 | 43161101 | SALMON CREEK 1101 | 1414.65 | 0.87921 | 8 | 0.44912 | 0.05614 | 1107 | 12862.627 | 2907.4602 | 0.11742 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1882 | SHINGLE SPRINGS 211051800 | 153652110 | SHINGLE SPRINGS 2110 | 14796.5287 | 9.1961 | 128 | 7.1719 | 0.05603 | 1108 | 12871.8231 | 2900.2883 | 0.11713 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3611 | SANTA MARIA 1108M80 | 182671108 | SANTA MARIA 1108 | 93735.5013 | 58.257 | 397 | 22.1966 | 0.055911 | 1109 | 12930.0801 | 2878.0917 | 0.11623 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6376 | MONTE RIO 11131991 | 42811113 | MONTE RIO 1113 | 11465.3295 | 7.1257 | 51 | 2.8451 | 0.055786 | 1110 | 12937.2058 | 2875.2466 | 0.11612 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1111 | PEORIA 17056697 | 163781705 | PEORIA 1705 | 6657.3541 | 4.1376 | 46 | 2.5653 | 0.055767 | 1111 | 12941.3434 | 2872.6813 | 0.11601 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3012 | RACETRACK 170311270 | 163761703 | RACETRACK 1703 | 20312.1456 | 12.6241 | 123 | 6.8493 | 0.055685 | 1112 | 12953.9675 | 2865.832 | 0.11574 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
722 | MONTE RIO 11125040 | 42811112 | MONTE RIO 1112 | 6507.5662 | 4.0445 | 46 | 2.5589 | 0.055628 | 1113 | 12958.0119 | 2863.2731 | 0.11563 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9716 | WINDSOR 1103171410 | 43501103 | WINDSOR 1103 | 2217.9639 | 1.3785 | 40 | 2.2241 | 0.055603 | 1114 | 12959.3904 | 2861.049 | 0.11554 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
15 | MENDOCINO 1101450 | 42951101 | MENDOCINO 1101 | 9311.1997 | 5.7869 | 208 | 11.531 | 0.055438 | 1115 | 12965.1774 | 2849.518 | 0.11508 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6036 | PLACER 1103CB | 152461103 | PLACER 1103 | 11213.2305 | 6.9691 | 99 | 5.4797 | 0.05535 | 1116 | 12972.1464 | 2844.0383 | 0.11486 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6178 | GEYSERVILLE 110135492 | 42891101 | GEYSERVILLE 1101 | 16074.976 | 9.9907 | 219 | 12.0973 | 0.055239 | 1117 | 12982.1371 | 2831.941 | 0.11437 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6625 | WYANDOTTE 1107829470 | 102911107 | WYANDOTTE 1107 | 16595.0205 | 10.3139 | 93 | 5.136 | 0.055226 | 1118 | 12992.451 | 2826.805 | 0.11416 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7721 | CURTIS 17058110 | 163351705 | CURTIS 1705 | 13110.3306 | 8.1481 | 99 | 5.4634 | 0.055185 | 1119 | 13000.5991 | 2821.3417 | 0.11394 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8806 | CLAYTON 2212859443 | 12022212 | CLAYTON 2212 | 475.2837 | 0.29539 | 5 | 0.27584 | 0.055167 | 1120 | 13000.8945 | 2821.0658 | 0.11393 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8792 | DUNLAP 1103CB | 254061103 | DUNLAP 1103 | 9029.352 | 5.6118 | 38 | 2.0943 | 0.055113 | 1121 | 13006.5063 | 2818.9715 | 0.11384 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4534 | MERCED FALLS 110285002 | 252811102 | MERCED FALLS 1102 | 57093.5104 | 35.4838 | 394 | 21.6802 | 0.055026 | 1122 | 13041.9901 | 2797.2913 | 0.11297 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2247 | FROGTOWN 170113412 | 163451701 | FROGTOWN 1701 | 62439.7255 | 38.8065 | 333 | 18.321 | 0.055018 | 1123 | 13080.7966 | 2778.9703 | 0.11223 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3205 | COTATI 110361736 | 42271103 | COTATI 1103 | 19558.6498 | 12.1558 | 129 | 7.0932 | 0.054986 | 1124 | 13092.9524 | 2771.8771 | 0.11194 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9516 | WILDWOOD 11011576 | 103611101 | WILDWOOD 1101 | 12974.577 | 8.0638 | 51 | 2.801 | 0.054922 | 1125 | 13101.0162 | 2769.0761 | 0.11183 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4729 | FITCH MOUNTAIN 1113352 | 42751113 | FITCH MOUNTAIN 1113 | 9086.2434 | 5.6471 | 123 | 6.7498 | 0.054876 | 1126 | 13106.6633 | 2762.3263 | 0.11156 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6906 | IONE 1101CB | 163881101 | IONE 1101 | 2970.8687 | 1.8464 | 85 | 4.663 | 0.054859 | 1127 | 13108.5097 | 2757.6633 | 0.11137 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1910 | FROGTOWN 17016807 | 163451701 | FROGTOWN 1701 | 7894.5527 | 4.9065 | 49 | 2.6713 | 0.054517 | 1128 | 13113.4162 | 2754.992 | 0.11126 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1099 | HIGHLANDS 110275140 | 43361102 | HIGHLANDS 1102 | 13968.9875 | 8.6818 | 238 | 12.967 | 0.054483 | 1129 | 13122.098 | 2742.025 | 0.11074 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9073 | CORRAL 1103831781 | 162991103 | CORRAL 1103 | 1186.1396 | 0.73719 | 19 | 1.0324 | 0.054336 | 1130 | 13122.8352 | 2740.9926 | 0.1107 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1018 | APPLE HILL 21029722 | 153662102 | APPLE HILL 2102 | 62437.5165 | 38.8052 | 359 | 19.4965 | 0.054308 | 1131 | 13161.6404 | 2721.4961 | 0.10991 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
882 | MORGAN HILL 2105XR152 | 83242105 | MORGAN HILL 2105 | 14045.9028 | 8.7296 | 156 | 8.4685 | 0.054285 | 1132 | 13170.3699 | 2713.0276 | 0.10957 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7464 | CLARKSVILLE 2106CB | 153612106 | CLARKSVILLE 2106 | 224.6189 | 0.1396 | 9 | 0.48794 | 0.054215 | 1133 | 13170.5095 | 2712.5396 | 0.10955 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8313 | RED BLUFF 1104135854 | 103541104 | RED BLUFF 1104 | 2325.1244 | 1.4451 | 34 | 1.8351 | 0.053974 | 1134 | 13171.9546 | 2710.7045 | 0.10947 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8191 | KESWICK 11011588 | 103451101 | KESWICK 1101 | 13991.4401 | 8.6957 | 33 | 1.7809 | 0.053968 | 1135 | 13180.6504 | 2708.9236 | 0.1094 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5209 | OLETA 11022642 | 163541102 | OLETA 1102 | 7497.8568 | 4.6599 | 27 | 1.4537 | 0.053841 | 1136 | 13185.3103 | 2707.4699 | 0.10934 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2961 | SYCAMORE CREEK 11112014 | 102971111 | SYCAMORE CREEK 1111 | 35984.1335 | 22.3643 | 181 | 9.731 | 0.053762 | 1137 | 13207.6746 | 2697.7389 | 0.10895 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5221 | EL DORADO PH 210163464 | 152762101 | EL DORADO PH 2101 | 21920.8692 | 13.6239 | 70 | 3.7492 | 0.05356 | 1138 | 13221.2985 | 2693.9897 | 0.1088 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1685 | WILLOW CREEK 110347966 | 192171103 | WILLOW CREEK 1103 | 27271.3222 | 16.9492 | 167 | 8.9254 | 0.053445 | 1139 | 13238.2477 | 2685.0643 | 0.10844 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1361 | RED BLUFF 11051564 | 103541105 | RED BLUFF 1105 | 1891.6003 | 1.1756 | 133 | 7.1038 | 0.053412 | 1140 | 13239.4234 | 2677.9605 | 0.10815 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
566 | MORGAN HILL 2110814616 | 83242110 | MORGAN HILL 2110 | 157.4015 | 0.097826 | 28 | 1.4955 | 0.053409 | 1141 | 13239.5212 | 2676.4651 | 0.10809 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9804 | FROGTOWN 1702694042 | 163451702 | FROGTOWN 1702 | 972.0471 | 0.60413 | 8 | 0.42716 | 0.053395 | 1142 | 13240.1253 | 2676.0379 | 0.10807 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
548 | SHINGLE SPRINGS 21107742 | 153652110 | SHINGLE SPRINGS 2110 | 73535.6671 | 45.7027 | 475 | 25.3612 | 0.053392 | 1143 | 13285.828 | 2650.6767 | 0.10705 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4014 | CURTIS 1704CB | 163351704 | CURTIS 1704 | 22355.1304 | 13.8938 | 170 | 9.058 | 0.053282 | 1144 | 13299.7218 | 2641.6187 | 0.10668 | 2641.6187 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5744 | WOODSIDE 11018974 | 24251101 | WOODSIDE 1101 | 21278.6691 | 13.2248 | 149 | 7.8956 | 0.05299 | 1145 | 13312.9466 | 2633.7232 | 0.10636 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4200 | MOLINO 1101322 | 42571101 | MOLINO 1101 | 22860.7646 | 14.2081 | 167 | 8.847 | 0.052976 | 1146 | 13327.1547 | 2624.8762 | 0.10601 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7680 | PALMER 1101M88 | 183031101 | PALMER 1101 | 4969.351 | 3.0885 | 85 | 4.4993 | 0.052933 | 1147 | 13330.2431 | 2620.3768 | 0.10582 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2401 | WOODSIDE 11018884 | 24251101 | WOODSIDE 1101 | 12033.5669 | 7.4789 | 74 | 3.9061 | 0.052785 | 1148 | 13337.7221 | 2616.4708 | 0.10567 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5333 | GARBERVILLE 11022500 | 192221102 | GARBERVILLE 1102 | 25777.1884 | 16.0206 | 106 | 5.5813 | 0.052654 | 1149 | 13353.7427 | 2610.8895 | 0.10544 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3787 | BEAR VALLEY 21014500 | 252192101 | BEAR VALLEY 2101 | 38902.9544 | 24.1783 | 516 | 27.1089 | 0.052537 | 1150 | 13377.921 | 2583.7806 | 0.10435 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8553 | RED BLUFF 11041302 | 103541104 | RED BLUFF 1104 | 22389.9711 | 13.9155 | 113 | 5.9272 | 0.052453 | 1151 | 13391.8365 | 2577.8535 | 0.10411 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10783 | BEAR VALLEY 2105CB | 252192105 | BEAR VALLEY 2105 | 6175.4075 | 3.838 | 9 | 0.4711 | 0.052345 | 1152 | 13395.6745 | 2577.3824 | 0.10409 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10429 | BUTTE 1105244246 | 103081105 | BUTTE 1105 | 1936.2709 | 1.2034 | 11 | 0.57496 | 0.052269 | 1153 | 13396.8779 | 2576.8074 | 0.10406 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1753 | BRUNSWICK 110651484 | 152481106 | BRUNSWICK 1106 | 24741.7275 | 15.3771 | 195 | 10.1812 | 0.052211 | 1154 | 13412.255 | 2566.6262 | 0.10365 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7841 | STONE CORRAL 1110975698 | 252921110 | STONE CORRAL 1110 | 1441.7984 | 0.89608 | 44 | 2.2966 | 0.052194 | 1155 | 13413.1511 | 2564.3296 | 0.10356 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10305 | MIDDLETOWN 1101612 | 43141101 | MIDDLETOWN 1101 | 6362.7002 | 3.9544 | 25 | 1.3033 | 0.05213 | 1156 | 13417.1055 | 2563.0264 | 0.10351 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9510 | PUEBLO 2103776244 | 43292103 | PUEBLO 2103 | 274.5802 | 0.17065 | 5 | 0.26059 | 0.052117 | 1157 | 13417.2762 | 2562.7658 | 0.1035 | 2562.7658 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2874 | FORT ROSS 11214947 | 42851121 | FORT ROSS 1121 | 16652.8009 | 10.3498 | 56 | 2.913 | 0.052018 | 1158 | 13427.626 | 2559.8528 | 0.10338 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5370 | FROGTOWN 17027108 | 163451702 | FROGTOWN 1702 | 15478.9307 | 9.6202 | 99 | 5.1341 | 0.05186 | 1159 | 13437.2462 | 2554.7187 | 0.10317 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7742 | WEST POINT 110272036 | 163201102 | WEST POINT 1102 | 20864.4611 | 12.9673 | 105 | 5.441 | 0.051819 | 1160 | 13450.2135 | 2549.2777 | 0.10295 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8013 | WILLITS 110337506 | 42661103 | WILLITS 1103 | 18602.139 | 11.5613 | 77 | 3.9812 | 0.051705 | 1161 | 13461.7748 | 2545.2964 | 0.10279 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8123 | OTTER 1102CB | 182941102 | OTTER 1102 | 10891.762 | 6.7693 | 40 | 2.0626 | 0.051564 | 1162 | 13468.5441 | 2543.2338 | 0.10271 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7649 | HARTLEY 1101CB | 43211101 | HARTLEY 1101 | 2361.7078 | 1.4678 | 33 | 1.6967 | 0.051416 | 1163 | 13470.0119 | 2541.5371 | 0.10264 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4094 | HOPLAND 1101960 | 42251101 | HOPLAND 1101 | 6237.2835 | 3.8765 | 33 | 1.6966 | 0.051413 | 1164 | 13473.8884 | 2539.8405 | 0.10257 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7517 | PENRYN 110790970 | 152561107 | PENRYN 1107 | 2317.6472 | 1.4404 | 45 | 2.3055 | 0.051234 | 1165 | 13475.3289 | 2537.535 | 0.10248 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
371 | CURTIS 1701CB | 163351701 | CURTIS 1701 | 12973.5363 | 8.0631 | 159 | 8.1275 | 0.051116 | 1166 | 13483.392 | 2529.4074 | 0.10215 | 2529.4074 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8728 | CORRAL 1103569005 | 162991103 | CORRAL 1103 | 1152.5978 | 0.71634 | 38 | 1.939 | 0.051027 | 1167 | 13484.1083 | 2527.4684 | 0.10207 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3664 | PLACERVILLE 2106CB | 153082106 | PLACERVILLE 2106 | 10545.3693 | 6.554 | 31 | 1.5771 | 0.050873 | 1168 | 13490.6623 | 2525.8914 | 0.10201 | 2525.8914 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10993 | MESA 1103737698 | 182821103 | MESA 1103 | 324.8619 | 0.2019 | 3 | 0.15225 | 0.050749 | 1169 | 13490.8642 | 2525.7391 | 0.102 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7973 | PENRYN 110550548 | 152561105 | PENRYN 1105 | 154.2272 | 0.095853 | 58 | 2.9403 | 0.050695 | 1170 | 13490.96 | 2522.7988 | 0.10188 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9859 | CUYAMA 1103684566 | 253141103 | CUYAMA 1103 | 4856.693 | 3.0185 | 4 | 0.20251 | 0.050626 | 1171 | 13493.9785 | 2522.5963 | 0.10188 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7777 | GANSNER 11012424 | 103021101 | GANSNER 1101 | 30186.9031 | 18.7613 | 141 | 7.1288 | 0.050559 | 1172 | 13512.7398 | 2515.4675 | 0.10159 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10622 | TEJON 1103286542 | 252931103 | TEJON 1103 | 3501.8559 | 2.1764 | 25 | 1.2632 | 0.050527 | 1173 | 13514.9162 | 2514.2043 | 0.10154 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2224 | COTATI 1103148 | 42271103 | COTATI 1103 | 24850.3478 | 15.4446 | 107 | 5.39 | 0.050374 | 1174 | 13530.3608 | 2508.8143 | 0.10132 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2728 | MESA 1103M72 | 182821103 | MESA 1103 | 13551.8371 | 8.4225 | 180 | 9.0403 | 0.050224 | 1175 | 13538.7833 | 2499.774 | 0.10095 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4743 | WYANDOTTE 11031508 | 102911103 | WYANDOTTE 1103 | 43792.5733 | 27.2173 | 249 | 12.4656 | 0.050062 | 1176 | 13566.0006 | 2487.3085 | 0.10045 | 2487.3085 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1729 | LUCERNE 1106664 | 43351106 | LUCERNE 1106 | 15503.1919 | 9.6353 | 140 | 7.006 | 0.050043 | 1177 | 13575.6359 | 2480.3024 | 0.10017 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1094 | HIGGINS 110332120 | 152691103 | HIGGINS 1103 | 65394.3269 | 40.6428 | 485 | 24.23 | 0.049959 | 1178 | 13616.2787 | 2456.0724 | 0.099189 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1827 | BELL 11082226 | 152701108 | BELL 1108 | 38762.6482 | 24.0911 | 329 | 16.3638 | 0.049738 | 1179 | 13640.3699 | 2439.7086 | 0.098528 | 2439.7086 | #N/A | #N/A | #N/A | #N/A | #VALUE!
971 | KANAKA 110183288 | 103221101 | KANAKA 1101 | 27936.7507 | 17.3628 | 140 | 6.9631 | 0.049736 | 1180 | 13657.7327 | 2432.7455 | 0.098247 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6396 | MC ARTHUR 11011490 | 103491101 | MC ARTHUR 1101 | 16986.9503 | 10.5575 | 122 | 6.0634 | 0.0497 | 1181 | 13668.2901 | 2426.6822 | 0.098002 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1501 | PIERCY 2110XR258 | 83912110 | PIERCY 2110 | 35307.703 | 21.9439 | 117 | 5.814 | 0.049692 | 1182 | 13690.234 | 2420.8682 | 0.097767 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4371 | BELLEVUE 2103552 | 43182103 | BELLEVUE 2103 | 15233.6156 | 9.4678 | 172 | 8.5251 | 0.049565 | 1183 | 13699.7017 | 2412.343 | 0.097423 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
774 | MORGAN HILL 2110654924 | 83242110 | MORGAN HILL 2110 | 4423.0701 | 2.749 | 61 | 3.0099 | 0.049343 | 1184 | 13702.4507 | 2409.3331 | 0.097301 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4796 | SISQUOC 1102M52 | 182811102 | SISQUOC 1102 | 54530.2399 | 33.8908 | 131 | 6.4386 | 0.04915 | 1185 | 13736.3415 | 2402.8945 | 0.097041 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
899 | RACETRACK 170455798 | 163761704 | RACETRACK 1704 | 37886.6196 | 23.5467 | 246 | 12.0752 | 0.049086 | 1186 | 13759.8882 | 2390.8193 | 0.096553 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8632 | STELLING 11102243 | 83481110 | STELLING 1110 | 3051.2175 | 1.8963 | 16 | 0.78482 | 0.049051 | 1187 | 13761.7845 | 2390.0345 | 0.096522 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4409 | HIGGINS 11071070 | 152691107 | HIGGINS 1107 | 12735.6646 | 7.9153 | 100 | 4.8737 | 0.048737 | 1188 | 13769.6998 | 2385.1608 | 0.096325 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2076 | SAN JUSTO 110136902 | 183181101 | SAN JUSTO 1101 | 19990.5557 | 12.4242 | 147 | 7.1641 | 0.048735 | 1189 | 13782.124 | 2377.9967 | 0.096036 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6423 | TASSAJARA 2113MR276 | 14662113 | TASSAJARA 2113 | 6199.9698 | 3.8533 | 42 | 2.0447 | 0.048684 | 1190 | 13785.9773 | 2375.952 | 0.095953 | 2375.952 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7009 | PENRYN 110551676 | 152561105 | PENRYN 1105 | 12910.4516 | 8.0239 | 145 | 7.0475 | 0.048603 | 1191 | 13794.0012 | 2368.9045 | 0.095668 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9522 | STONE CORRAL 1110894956 | 252921110 | STONE CORRAL 1110 | 1243.2231 | 0.77267 | 16 | 0.77554 | 0.048471 | 1192 | 13794.7739 | 2368.129 | 0.095637 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4908 | DIVIDE 1103567884 | 182571103 | DIVIDE 1103 | 4025.5628 | 2.5019 | 27 | 1.3004 | 0.048164 | 1193 | 13797.2758 | 2366.8286 | 0.095584 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
537 | FORT SEWARD 11211602 | 192321121 | FORT SEWARD 1121 | 29307.7542 | 18.2149 | 109 | 5.244 | 0.048111 | 1194 | 13815.4906 | 2361.5845 | 0.095373 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
522 | MONTE RIO 1111292 | 42811111 | MONTE RIO 1111 | 25055.0465 | 15.5718 | 165 | 7.9294 | 0.048057 | 1195 | 13831.0625 | 2353.6552 | 0.095052 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6679 | LAYTONVILLE 11011760 | 42681101 | LAYTONVILLE 1101 | 15610.272 | 9.7018 | 73 | 3.5072 | 0.048043 | 1196 | 13840.7643 | 2350.148 | 0.094911 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7262 | LOW GAP 11014160 | 192411101 | LOW GAP 1101 | 34990.3559 | 21.7466 | 194 | 9.3109 | 0.047994 | 1197 | 13862.5109 | 2340.8371 | 0.094535 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2115 | GARBERVILLE 1102CB | 192221102 | GARBERVILLE 1102 | 19300.4618 | 11.9953 | 191 | 9.1665 | 0.047992 | 1198 | 13874.5063 | 2331.6707 | 0.094165 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
859 | SALT SPRINGS 21011216 | 163692101 | SALT SPRINGS 2101 | 8821.9491 | 5.4829 | 32 | 1.5347 | 0.04796 | 1199 | 13879.9891 | 2330.136 | 0.094103 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4717 | CAMBRIA 1101V76 | 182771101 | CAMBRIA 1101 | 30510.6388 | 18.9625 | 59 | 2.8276 | 0.047925 | 1200 | 13898.9516 | 2327.3084 | 0.093988 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3890 | KANAKA 110165606 | 103221101 | KANAKA 1101 | 20505.679 | 12.7444 | 145 | 6.9481 | 0.047918 | 1201 | 13911.696 | 2320.3603 | 0.093708 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11044 | SAN LUIS OBISPO 1104753254 | 182631104 | SAN LUIS OBISPO 1104 | 561.1486 | 0.34876 | 2 | 0.095314 | 0.047657 | 1202 | 13912.0447 | 2320.2649 | 0.093704 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
868 | PEORIA 170459596 | 163781704 | PEORIA 1704 | 33598.813 | 20.8818 | 294 | 13.9806 | 0.047553 | 1203 | 13932.9265 | 2306.2844 | 0.093139 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5643 | CLEAR LAKE 1102991285 | 42141102 | CLEAR LAKE 1102 | 525.9001 | 0.32685 | 24 | 1.1393 | 0.047469 | 1204 | 13933.2534 | 2305.1451 | 0.093093 | 2305.1451 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2996 | BURNEY 11012402 | 103311101 | BURNEY 1101 | 2411.6802 | 1.4989 | 18 | 0.85235 | 0.047353 | 1205 | 13934.7523 | 2304.2928 | 0.093059 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
982 | WEST POINT 11024788 | 163201102 | WEST POINT 1102 | 111874.9537 | 69.5307 | 673 | 31.8454 | 0.047319 | 1206 | 14004.283 | 2272.4474 | 0.091773 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6337 | MIWUK 170219772 | 163661702 | MIWUK 1702 | 6198.5938 | 3.8525 | 41 | 1.9386 | 0.047283 | 1207 | 14008.1354 | 2270.5088 | 0.091695 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1317 | MOLINO 1102178 | 42571102 | MOLINO 1102 | 19626.441 | 12.1979 | 182 | 8.5954 | 0.047227 | 1208 | 14020.3334 | 2261.9135 | 0.091347 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2756 | AUBERRY 1101R2845 | 254151101 | AUBERRY 1101 | 28680.0593 | 17.8248 | 172 | 8.1154 | 0.047182 | 1209 | 14038.1581 | 2253.7981 | 0.09102 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1878 | JESSUP 110168362 | 103441101 | JESSUP 1101 | 8312.3827 | 5.1662 | 96 | 4.5193 | 0.047076 | 1210 | 14043.3243 | 2249.2788 | 0.090837 | 2249.2788 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1899 | SAN BENITO 2104785888 | 182742104 | SAN BENITO 2104 | 7730.7085 | 4.8047 | 49 | 2.304 | 0.047021 | 1211 | 14048.129 | 2246.9748 | 0.090744 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1312 | MOUNTAIN QUARRIES 210192474 | 152282101 | MOUNTAIN QUARRIES 2101 | 24305.4181 | 15.1059 | 173 | 8.12 | 0.046937 | 1212 | 14063.2349 | 2238.8547 | 0.090416 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9280 | FREMONT 1104MR339 | 14351104 | FREMONT 1104 | 1921.2331 | 1.1941 | 73 | 3.4227 | 0.046887 | 1213 | 14064.4289 | 2235.432 | 0.090278 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10367 | PEORIA 170488630 | 163781704 | PEORIA 1704 | 1252.5971 | 0.77849 | 6 | 0.28105 | 0.046842 | 1214 | 14065.2074 | 2235.151 | 0.090267 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3920 | LLAGAS 2107XR178 | 83182107 | LLAGAS 2107 | 9493.9491 | 5.9005 | 138 | 6.4625 | 0.04683 | 1215 | 14071.108 | 2228.6884 | 0.090006 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9293 | DUNLAP 110239190 | 254061102 | DUNLAP 1102 | 2877.2566 | 1.7882 | 17 | 0.79463 | 0.046743 | 1216 | 14072.8962 | 2227.8938 | 0.089974 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9995 | GEYSERVILLE 1102180193 | 42891102 | GEYSERVILLE 1102 | 3477.0858 | 2.161 | 23 | 1.0737 | 0.046684 | 1217 | 14075.0572 | 2226.82 | 0.08993 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2795 | BELL 1108467470 | 152701108 | BELL 1108 | 2987.9 | 1.857 | 40 | 1.857 | 0.046424 | 1218 | 14076.9142 | 2224.9631 | 0.089855 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6866 | EDENVALE 1102XR064 | 82951102 | EDENVALE 1102 | 1175.6095 | 0.73065 | 35 | 1.6236 | 0.046387 | 1219 | 14077.6449 | 2223.3395 | 0.08979 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2884 | MC ARTHUR 110137388 | 103491101 | MC ARTHUR 1101 | 13050.4067 | 8.1109 | 56 | 2.5868 | 0.046193 | 1220 | 14085.7557 | 2220.7527 | 0.089685 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8090 | PENRYN 1105817491 | 152561105 | PENRYN 1105 | 2279.4584 | 1.4167 | 24 | 1.1084 | 0.046183 | 1221 | 14087.1724 | 2219.6443 | 0.08964 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
196 | MILPITAS 1109XR082 | 82831109 | MILPITAS 1109 | 31674.5025 | 19.6858 | 186 | 8.5807 | 0.046133 | 1222 | 14106.8583 | 2211.0636 | 0.089294 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9874 | JARVIS 1108767280 | 13501108 | JARVIS 1108 | 816.4039 | 0.5074 | 11 | 0.50728 | 0.046117 | 1223 | 14107.3657 | 2210.5563 | 0.089273 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3653 | PUEBLO 2103678 | 43292103 | PUEBLO 2103 | 56857.8795 | 35.3374 | 325 | 14.9751 | 0.046077 | 1224 | 14142.7031 | 2195.5812 | 0.088669 | 2195.5812 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4529 | MC ARTHUR 110138998 | 103491101 | MC ARTHUR 1101 | 189.4976 | 0.11777 | 61 | 2.8099 | 0.046064 | 1225 | 14142.8208 | 2192.7713 | 0.088555 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9562 | MOLINO 1101600112 | 42571101 | MOLINO 1101 | 1283.9759 | 0.798 | 18 | 0.82393 | 0.045774 | 1226 | 14143.6188 | 2191.9473 | 0.088522 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8471 | MONTICELLO 1101654 | 43051101 | MONTICELLO 1101 | 13220.1574 | 8.2164 | 71 | 3.2338 | 0.045547 | 1227 | 14151.8352 | 2188.7135 | 0.088391 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9084 | SWIFT 2110XR254 | 83392110 | SWIFT 2110 | 40510.5344 | 25.1775 | 134 | 6.1028 | 0.045544 | 1228 | 14177.0127 | 2182.6107 | 0.088145 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5247 | MOLINO 1102658 | 42571102 | MOLINO 1102 | 17510.52 | 10.8829 | 107 | 4.8515 | 0.045341 | 1229 | 14187.8955 | 2177.7592 | 0.087949 | 2177.7592 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1624 | CLAY 11037124 | 163341103 | CLAY 1103 | 17797.9944 | 11.0615 | 286 | 12.9498 | 0.045279 | 1230 | 14198.9571 | 2164.8094 | 0.087426 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6683 | UKIAH 11143606 | 42771114 | UKIAH 1114 | 17219.5096 | 10.702 | 129 | 5.828 | 0.045178 | 1231 | 14209.6591 | 2158.9814 | 0.087191 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6114 | GANSNER 110137550 | 103021101 | GANSNER 1101 | 590.535 | 0.36702 | 33 | 1.4864 | 0.045042 | 1232 | 14210.0261 | 2157.495 | 0.087131 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10276 | LAKEVILLE 1102367100 | 43371102 | LAKEVILLE 1102 | 900.8036 | 0.55985 | 6 | 0.26958 | 0.04493 | 1233 | 14210.5859 | 2157.2254 | 0.08712 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3592 | CURTIS 17039330 | 163351703 | CURTIS 1703 | 66516.2766 | 41.3401 | 345 | 15.4037 | 0.044648 | 1234 | 14251.9261 | 2141.8217 | 0.086498 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1338 | SILVERADO 210437632 | 43432104 | SILVERADO 2104 | 42770.2942 | 26.5819 | 304 | 13.5588 | 0.044601 | 1235 | 14278.508 | 2128.2629 | 0.08595 | 2128.2629 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9592 | BELL 1107912460 | 152701107 | BELL 1107 | 226.2188 | 0.1406 | 6 | 0.26697 | 0.044495 | 1236 | 14278.6486 | 2127.996 | 0.085939 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9543 | GARBERVILLE 110237054 | 192221102 | GARBERVILLE 1102 | 14394.233 | 8.9461 | 76 | 3.3774 | 0.044439 | 1237 | 14287.5946 | 2124.6186 | 0.085803 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
528 | PLACERVILLE 210692012 | 153082106 | PLACERVILLE 2106 | 29794.6367 | 18.5175 | 219 | 9.7026 | 0.044304 | 1238 | 14306.1121 | 2114.916 | 0.085411 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2289 | PASO ROBLES 1103351084 | 182611103 | PASO ROBLES 1103 | 3813.7275 | 2.3702 | 91 | 4.0272 | 0.044255 | 1239 | 14308.4824 | 2110.8888 | 0.085248 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4151 | SHINGLE SPRINGS 2109CB | 153652109 | SHINGLE SPRINGS 2109 | 44000.0643 | 27.3462 | 341 | 15.0331 | 0.044085 | 1240 | 14335.8286 | 2095.8557 | 0.084641 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8694 | MC ARTHUR 11011544 | 103491101 | MC ARTHUR 1101 | 27291.0085 | 16.9615 | 135 | 5.9476 | 0.044056 | 1241 | 14352.7901 | 2089.9081 | 0.084401 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5303 | STONE CORRAL 11087100 | 252921108 | STONE CORRAL 1108 | 3757.8694 | 2.3355 | 130 | 5.7148 | 0.04396 | 1242 | 14355.1256 | 2084.1933 | 0.08417 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5138 | SUMMIT 11022302 | 152591102 | SUMMIT 1102 | 2152.9343 | 1.3381 | 19 | 0.8342 | 0.043905 | 1243 | 14356.4637 | 2083.3591 | 0.084137 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3403 | PENRYN 11051378 | 152561105 | PENRYN 1105 | 1447.5189 | 0.89964 | 25 | 1.096 | 0.043839 | 1244 | 14357.3633 | 2082.2631 | 0.084092 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5562 | GARBERVILLE 110139524 | 192221101 | GARBERVILLE 1101 | 8232.0089 | 5.1162 | 138 | 6.0334 | 0.04372 | 1245 | 14362.4795 | 2076.2298 | 0.083849 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3303 | BIG BEND 1101180398 | 103751101 | BIG BEND 1101 | 8946.0191 | 5.56 | 48 | 2.0957 | 0.04366 | 1246 | 14368.0395 | 2074.1341 | 0.083764 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5481 | VACAVILLE 110847860 | 63601108 | VACAVILLE 1108 | 466.0192 | 0.28963 | 54 | 2.353 | 0.043573 | 1247 | 14368.3291 | 2071.7811 | 0.083669 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8994 | SAN LUIS OBISPO 1104982992 | 182631104 | SAN LUIS OBISPO 1104 | 14390.2086 | 8.9436 | 52 | 2.2633 | 0.043526 | 1248 | 14377.2727 | 2069.5178 | 0.083578 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6482 | UKIAH 1113691436 | 42771113 | UKIAH 1113 | 1680.7069 | 1.0446 | 28 | 1.2166 | 0.043449 | 1249 | 14378.3173 | 2068.3012 | 0.083528 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7283 | COVELO 1101112804 | 43061101 | COVELO 1101 | 16512.5111 | 10.2626 | 67 | 2.9107 | 0.043443 | 1250 | 14388.5799 | 2065.3906 | 0.083411 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2688 | STILLWATER 11021466 | 103561102 | STILLWATER 1102 | 33039.7041 | 20.5343 | 211 | 9.1248 | 0.043245 | 1251 | 14409.1142 | 2056.2658 | 0.083042 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6122 | EEL RIVER 11024814 | 192381102 | EEL RIVER 1102 | 43433.15 | 26.9939 | 117 | 5.0562 | 0.043216 | 1252 | 14436.1081 | 2051.2096 | 0.082838 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8658 | MENLO 11037902 | 24131103 | MENLO 1103 | 18823.9554 | 11.6992 | 143 | 6.1722 | 0.043162 | 1253 | 14447.8072 | 2045.0373 | 0.082589 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5986 | SILVERADO 210478268 | 43432104 | SILVERADO 2104 | 15647.3206 | 9.7249 | 114 | 4.9171 | 0.043133 | 1254 | 14457.5321 | 2040.1202 | 0.08239 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3705 | ALTO 11221212 | 42031122 | ALTO 1122 | 2977.1941 | 1.8503 | 25 | 1.0764 | 0.043056 | 1255 | 14459.3824 | 2039.0438 | 0.082347 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
565 | CALPELLA 1101CB | 43411101 | CALPELLA 1101 | 18947.9362 | 11.7762 | 226 | 9.722 | 0.043018 | 1256 | 14471.1587 | 2029.3218 | 0.081954 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1815 | OTTER 110298036 | 182941102 | OTTER 1102 | 14803.9566 | 9.2007 | 64 | 2.7435 | 0.042868 | 1257 | 14480.3594 | 2026.5782 | 0.081843 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5821 | HIGHLANDS 11034630 | 43361103 | HIGHLANDS 1103 | 1729.1767 | 1.0747 | 42 | 1.7982 | 0.042814 | 1258 | 14481.4341 | 2024.78 | 0.081771 | 2024.78 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1927 | HIGGINS 1110166282 | 152691110 | HIGGINS 1110 | 38601.364 | 23.9909 | 256 | 10.8796 | 0.042498 | 1259 | 14505.425 | 2013.9005 | 0.081331 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6705 | GIRVAN 11021028 | 103401102 | GIRVAN 1102 | 28404.1063 | 17.6533 | 208 | 8.8364 | 0.042483 | 1260 | 14523.0782 | 2005.0641 | 0.080975 | 2005.0641 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3470 | OILFIELDS 1103370932 | 182391103 | OILFIELDS 1103 | 619.9296 | 0.38529 | 6 | 0.25478 | 0.042464 | 1261 | 14523.4635 | 2004.8093 | 0.080964 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9825 | GIRVAN 1101CB | 103401101 | GIRVAN 1101 | 2471.5392 | 1.5361 | 31 | 1.3146 | 0.042406 | 1262 | 14524.9996 | 2003.4947 | 0.080911 | 2003.4947 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4531 | CRESCENT MILLS 21013113 | 103132101 | CRESCENT MILLS 2101 | 1919.7007 | 1.1931 | 9 | 0.3815 | 0.042389 | 1263 | 14526.1927 | 2003.1132 | 0.080896 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4502 | WILLITS 1103968 | 42661103 | WILLITS 1103 | 42969.09 | 26.7055 | 283 | 11.9944 | 0.042383 | 1264 | 14552.8982 | 1991.1188 | 0.080411 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
293 | MENDOCINO 110131322 | 42951101 | MENDOCINO 1101 | 9420.014 | 5.8546 | 310 | 13.1348 | 0.04237 | 1265 | 14558.7527 | 1977.984 | 0.079881 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
332 | MESA 1101CB | 182821101 | MESA 1101 | 22299.6831 | 13.8593 | 230 | 9.7444 | 0.042367 | 1266 | 14572.6121 | 1968.2396 | 0.079487 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6761 | HORSESHOE 11011682 | 152571101 | HORSESHOE 1101 | 326.6132 | 0.20299 | 112 | 4.7402 | 0.042324 | 1267 | 14572.8151 | 1963.4994 | 0.079296 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4789 | APPLE HILL 110412842 | 153661104 | APPLE HILL 1104 | 25454.1408 | 15.8199 | 209 | 8.8429 | 0.042311 | 1268 | 14588.6349 | 1954.6565 | 0.078939 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5435 | SUNOL 1101MR299 | 14241101 | SUNOL 1101 | 7955.2462 | 4.9442 | 58 | 2.452 | 0.042276 | 1269 | 14593.5791 | 1952.2045 | 0.07884 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5875 | MESA 11016113 | 182821101 | MESA 1101 | 2800.3205 | 1.7404 | 100 | 4.2268 | 0.042268 | 1270 | 14595.3195 | 1947.9777 | 0.078669 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6536 | PINE GROVE 11026080 | 163751102 | PINE GROVE 1102 | 55307.7629 | 34.374 | 322 | 13.6042 | 0.042249 | 1271 | 14629.6935 | 1934.3734 | 0.07812 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10453 | RIO DELL 11027124 | 192251102 | RIO DELL 1102 | 1081.3743 | 0.67208 | 5 | 0.21114 | 0.042229 | 1272 | 14630.3656 | 1934.1623 | 0.078111 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9767 | SAN BERNARD 1101641042 | 253191101 | SAN BERNARD 1101 | 2300.7684 | 1.4299 | 22 | 0.92827 | 0.042194 | 1273 | 14631.7956 | 1933.234 | 0.078074 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7173 | OTTER 110237132 | 182941102 | OTTER 1102 | 9343.2123 | 5.8068 | 50 | 2.1086 | 0.042173 | 1274 | 14637.6024 | 1931.1254 | 0.077989 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7839 | FROGTOWN 1702204480 | 163451702 | FROGTOWN 1702 | 807.68 | 0.50198 | 28 | 1.1785 | 0.04209 | 1275 | 14638.1044 | 1929.9469 | 0.077941 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1556 | HOPLAND 110180620 | 42251101 | HOPLAND 1101 | 1997.9252 | 1.2417 | 51 | 2.1446 | 0.04205 | 1276 | 14639.3461 | 1927.8023 | 0.077854 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
796 | MESA 1101M86 | 182821101 | MESA 1101 | 20500.8716 | 12.7414 | 217 | 9.0801 | 0.041844 | 1277 | 14652.0875 | 1918.7222 | 0.077488 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4020 | CABRILLO 1103Y10 | 183101103 | CABRILLO 1103 | 7788.8369 | 4.8408 | 122 | 5.0971 | 0.041779 | 1278 | 14656.9283 | 1913.6251 | 0.077282 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4294 | FITCH MOUNTAIN 11134566 | 42751113 | FITCH MOUNTAIN 1113 | 20128.0864 | 12.5097 | 180 | 7.5169 | 0.041761 | 1279 | 14669.438 | 1906.1082 | 0.076978 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3368 | PEORIA 17051834 | 163781705 | PEORIA 1705 | 37922.7084 | 23.5691 | 217 | 9.0231 | 0.041581 | 1280 | 14693.0071 | 1897.0852 | 0.076614 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4811 | CALAVERAS CEMENT 1101502 | 162211101 | CALAVERAS CEMENT 1101 | 60591.0346 | 37.6576 | 331 | 13.7543 | 0.041554 | 1281 | 14730.6646 | 1883.3309 | 0.076058 | 1883.3309 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8493 | COTATI 1102282 | 42271102 | COTATI 1102 | 4475.09 | 2.7813 | 62 | 2.5746 | 0.041526 | 1282 | 14733.4459 | 1880.7562 | 0.075954 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3229 | WISE 1102CB | 152271102 | WISE 1102 | 22633.2401 | 14.0667 | 177 | 7.3353 | 0.041442 | 1283 | 14747.5126 | 1873.4209 | 0.075658 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2423 | APPLE HILL 110413512 | 153661104 | APPLE HILL 1104 | 45791.8869 | 28.4598 | 345 | 14.2801 | 0.041392 | 1284 | 14775.9724 | 1859.1408 | 0.075082 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3013 | BIG MEADOWS 21012586 | 102812101 | BIG MEADOWS 2101 | 10070.6101 | 6.2589 | 91 | 3.7526 | 0.041237 | 1285 | 14782.2313 | 1855.3882 | 0.07493 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6401 | COPPERMINE 1104556430 | 252411104 | COPPERMINE 1104 | 7792.8441 | 4.8433 | 122 | 5.0096 | 0.041063 | 1286 | 14787.0746 | 1850.3785 | 0.074728 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9989 | ORO FINO 11022236 | 103031102 | ORO FINO 1102 | 4120.4561 | 2.5609 | 11 | 0.45093 | 0.040994 | 1287 | 14789.6355 | 1849.9276 | 0.074709 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3633 | BIG BEND 11021972 | 103751102 | BIG BEND 1102 | 34265.9827 | 21.2964 | 177 | 7.25 | 0.040961 | 1288 | 14810.932 | 1842.6776 | 0.074417 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7419 | MARTELL 110299214 | 163011102 | MARTELL 1102 | 2953.539 | 1.8356 | 21 | 0.85759 | 0.040838 | 1289 | 14812.7676 | 1841.82 | 0.074382 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5589 | BUELLTON 1101Y36 | 183041101 | BUELLTON 1101 | 60717.9561 | 37.7365 | 283 | 11.5464 | 0.0408 | 1290 | 14850.5041 | 1830.2737 | 0.073916 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2824 | GEYSERVILLE 1101166 | 42891101 | GEYSERVILLE 1101 | 9969.1209 | 6.1958 | 110 | 4.4835 | 0.040759 | 1291 | 14856.6999 | 1825.7901 | 0.073735 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
612 | DIAMOND SPRINGS 11062100 | 152261106 | DIAMOND SPRINGS 1106 | 62879.0761 | 39.0796 | 403 | 16.4004 | 0.040696 | 1292 | 14895.7795 | 1809.3897 | 0.073072 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4758 | LAYTONVILLE 1101402 | 42681101 | LAYTONVILLE 1101 | 37584.6138 | 23.359 | 151 | 6.145 | 0.040695 | 1293 | 14919.1385 | 1803.2447 | 0.072824 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7625 | ATASCADERO 1103440856 | 182541103 | ATASCADERO 1103 | 56011.6123 | 34.8114 | 349 | 14.1857 | 0.040647 | 1294 | 14953.9499 | 1789.059 | 0.072251 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3291 | FRUITLAND 11426054 | 192311142 | FRUITLAND 1142 | 11579.672 | 7.1968 | 58 | 2.3572 | 0.040642 | 1295 | 14961.1467 | 1786.7018 | 0.072156 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2753 | CALPELLA 11011204 | 43411101 | CALPELLA 1101 | 15255.8356 | 9.4816 | 124 | 5.0263 | 0.040535 | 1296 | 14970.6283 | 1781.6755 | 0.071953 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6226 | FULTON 1107214 | 42561107 | FULTON 1107 | 18868.3768 | 11.7268 | 142 | 5.7514 | 0.040503 | 1297 | 14982.3551 | 1775.924 | 0.071721 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6297 | PEORIA 170176030 | 163781701 | PEORIA 1701 | 8222.4339 | 5.1103 | 55 | 2.2201 | 0.040366 | 1298 | 14987.4654 | 1773.7039 | 0.071631 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4946 | WYANDOTTE 11031976 | 102911103 | WYANDOTTE 1103 | 38264.4277 | 23.7815 | 217 | 8.7412 | 0.040282 | 1299 | 15011.2469 | 1764.9627 | 0.071278 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3803 | CALAVERAS CEMENT 1101CB | 162211101 | CALAVERAS CEMENT 1101 | 16846.5197 | 10.4702 | 203 | 8.1671 | 0.040232 | 1300 | 15021.717 | 1756.7956 | 0.070948 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
601 | FORESTHILL 11022106 | 152181102 | FORESTHILL 1102 | 44861.5543 | 27.8816 | 264 | 10.6117 | 0.040196 | 1301 | 15049.5987 | 1746.1839 | 0.07052 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3937 | AUBERRY 1101176050 | 254151101 | AUBERRY 1101 | 33994.9384 | 21.128 | 168 | 6.7464 | 0.040157 | 1302 | 15070.7267 | 1739.4374 | 0.070247 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3563 | SHINGLE SPRINGS 21092053 | 153652109 | SHINGLE SPRINGS 2109 | 9238.0472 | 5.7415 | 74 | 2.9697 | 0.040131 | 1303 | 15076.4681 | 1736.4677 | 0.070127 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
639 | LAYTONVILLE 1101CB | 42681101 | LAYTONVILLE 1101 | 9580.003 | 5.954 | 90 | 3.6104 | 0.040116 | 1304 | 15082.4222 | 1732.8573 | 0.069982 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8583 | UKIAH 1111168892 | 42771111 | UKIAH 1111 | 264.3207 | 0.16428 | 8 | 0.32079 | 0.040099 | 1305 | 15082.5864 | 1732.5365 | 0.069969 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6071 | SHINGLE SPRINGS 210981390 | 153652109 | SHINGLE SPRINGS 2109 | 29957.8137 | 18.6189 | 208 | 8.3022 | 0.039915 | 1306 | 15101.2053 | 1724.2343 | 0.069633 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5271 | WILLITS 1104504 | 42661104 | WILLITS 1104 | 36253.1832 | 22.5315 | 205 | 8.1484 | 0.039748 | 1307 | 15123.7368 | 1716.0859 | 0.069304 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8156 | PIKE CITY 1102CB | 152201102 | PIKE CITY 1102 | 15315.8587 | 9.5189 | 44 | 1.7406 | 0.03956 | 1308 | 15133.2557 | 1714.3452 | 0.069234 | 1714.3452 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1834 | CASTRO VALLEY 1110MR748 | 14091110 | CASTRO VALLEY 1110 | 10026.1125 | 6.2313 | 86 | 3.3984 | 0.039516 | 1309 | 15139.487 | 1710.9468 | 0.069097 | 1710.9468 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4232 | GABILAN 1101989608 | 182331101 | GABILAN 1101 | 1209.612 | 0.75178 | 6 | 0.23708 | 0.039513 | 1310 | 15140.2388 | 1710.7098 | 0.069087 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2029 | OCEANO 1102V56 | 182601102 | OCEANO 1102 | 15022.8264 | 9.3367 | 115 | 4.5359 | 0.039442 | 1311 | 15149.5755 | 1706.1739 | 0.068904 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6282 | MOLINO 1101891 | 42571101 | MOLINO 1101 | 5070.4899 | 3.1513 | 41 | 1.615 | 0.03939 | 1312 | 15152.7268 | 1704.5589 | 0.068839 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7224 | MIRABEL 1101116 | 42091101 | MIRABEL 1101 | 16625.8808 | 10.3331 | 112 | 4.4087 | 0.039363 | 1313 | 15163.0599 | 1700.1502 | 0.068661 | 1700.1502 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3752 | MONTE RIO 1113539938 | 42811113 | MONTE RIO 1113 | 4460.237 | 2.7721 | 26 | 1.0232 | 0.039354 | 1314 | 15165.8319 | 1699.127 | 0.068619 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8901 | BRIDGEVILLE 110237486 | 192461102 | BRIDGEVILLE 1102 | 11162.2658 | 6.9374 | 85 | 3.3351 | 0.039237 | 1315 | 15172.7693 | 1695.7919 | 0.068485 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3640 | FROGTOWN 1702CB | 163451702 | FROGTOWN 1702 | 2351.3614 | 1.4614 | 47 | 1.844 | 0.039234 | 1316 | 15174.2307 | 1693.9479 | 0.06841 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4627 | SAN LUIS OBISPO 1107V02 | 182631107 | SAN LUIS OBISPO 1107 | 29266.1566 | 18.189 | 202 | 7.9151 | 0.039184 | 1317 | 15192.4197 | 1686.0327 | 0.068091 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2477 | CEDAR CREEK 11011656 | 103321101 | CEDAR CREEK 1101 | 51859.3271 | 32.2308 | 208 | 8.1485 | 0.039176 | 1318 | 15224.6505 | 1677.8842 | 0.067761 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6350 | NAPA 11121302 | 42021112 | NAPA 1112 | 32333.7369 | 20.0955 | 317 | 12.3798 | 0.039053 | 1319 | 15244.7461 | 1665.5044 | 0.067261 | 1665.5044 | #N/A | #N/A | #N/A | #N/A | #VALUE!
798 | HIGGINS 1107CB | 152691107 | HIGGINS 1107 | 9216.7854 | 5.7283 | 243 | 9.4114 | 0.03873 | 1320 | 15250.4743 | 1656.093 | 0.066881 | 1656.093 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10498 | CLAYTON 2212158138 | 12022212 | CLAYTON 2212 | 829.4376 | 0.5155 | 10 | 0.38704 | 0.038704 | 1321 | 15250.9898 | 1655.706 | 0.066866 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9150 | SPANISH CREEK 4401CB | 103104401 | SPANISH CREEK 4401 | 12447.7538 | 7.7363 | 22 | 0.85144 | 0.038702 | 1322 | 15258.7262 | 1654.8545 | 0.066831 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
561 | ALTO 11221260 | 42031122 | ALTO 1122 | 4807.0969 | 2.9876 | 36 | 1.3919 | 0.038665 | 1323 | 15261.7138 | 1653.4626 | 0.066775 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2054 | PUEBLO 1104580658 | 43291104 | PUEBLO 1104 | 15111.3604 | 9.3918 | 107 | 4.1214 | 0.038518 | 1324 | 15271.1056 | 1649.3412 | 0.066609 | 1649.3412 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3362 | REDBUD 110191960 | 43191101 | REDBUD 1101 | 10487.6883 | 6.5181 | 90 | 3.4639 | 0.038488 | 1325 | 15277.6237 | 1645.8773 | 0.066469 | 1645.8773 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3879 | WILLITS 11032506 | 42661103 | WILLITS 1103 | 20286.2385 | 12.608 | 89 | 3.4198 | 0.038425 | 1326 | 15290.2317 | 1642.4575 | 0.066331 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2472 | SANTA ROSA A 1104220 | 42151104 | SANTA ROSA A 1104 | 15438.0154 | 9.5948 | 105 | 4.0198 | 0.038284 | 1327 | 15299.8265 | 1638.4376 | 0.066168 | 1638.4376 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2655 | TEMPLETON 2110R90 | 183052110 | TEMPLETON 2110 | 48580.6781 | 30.1931 | 259 | 9.9144 | 0.038279 | 1328 | 15330.0196 | 1628.5233 | 0.065768 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4442 | OCEANO 1104Q06 | 182601104 | OCEANO 1104 | 20064.3385 | 12.4701 | 154 | 5.8691 | 0.038111 | 1329 | 15342.4896 | 1622.6542 | 0.065531 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3161 | MARTELL 110368192 | 163011103 | MARTELL 1103 | 4402.6894 | 2.7363 | 72 | 2.734 | 0.037972 | 1330 | 15345.2259 | 1619.9202 | 0.065421 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7038 | MIRABEL 1102334 | 42091102 | MIRABEL 1102 | 9584.4637 | 5.9568 | 84 | 3.1833 | 0.037896 | 1331 | 15351.1827 | 1616.7369 | 0.065292 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6568 | GEYSERVILLE 110137454 | 42891101 | GEYSERVILLE 1101 | 10482.9729 | 6.5152 | 114 | 4.3002 | 0.037721 | 1332 | 15357.6979 | 1612.4367 | 0.065118 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9085 | SAN LUIS OBISPO 1107V62 | 182631107 | SAN LUIS OBISPO 1107 | 11108.5021 | 6.904 | 50 | 1.8704 | 0.037409 | 1333 | 15364.6019 | 1610.5663 | 0.065043 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3181 | SONOMA 110478372 | 42721104 | SONOMA 1104 | 26751.8084 | 16.6264 | 198 | 7.3862 | 0.037304 | 1334 | 15381.2283 | 1603.1801 | 0.064745 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
296 | TASSAJARA 2112D514R | 14662112 | TASSAJARA 2112 | 5032.0091 | 3.1274 | 73 | 2.7213 | 0.037278 | 1335 | 15384.3557 | 1600.4588 | 0.064635 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5732 | SWIFT 2107XR526 | 83392107 | SWIFT 2107 | 3365.6589 | 2.0918 | 64 | 2.3758 | 0.037122 | 1336 | 15386.4474 | 1598.083 | 0.064539 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4671 | PURISIMA 1101Y42 | 182971101 | PURISIMA 1101 | 5628.4599 | 3.4981 | 127 | 4.714 | 0.037118 | 1337 | 15389.9456 | 1593.369 | 0.064348 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7642 | PENRYN 1105168616 | 152561105 | PENRYN 1105 | 5078.9905 | 3.1566 | 102 | 3.7791 | 0.03705 | 1338 | 15393.1022 | 1589.5899 | 0.064196 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2287 | OCEANO 1104104102 | 182601104 | OCEANO 1104 | 5329.5584 | 3.3123 | 32 | 1.1853 | 0.03704 | 1339 | 15396.4145 | 1588.4046 | 0.064148 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9499 | OILFIELDS 1103N46 | 182391103 | OILFIELDS 1103 | 9360.6261 | 5.8177 | 29 | 1.0726 | 0.036988 | 1340 | 15402.2322 | 1587.332 | 0.064104 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5619 | NARROWS 21052426 | 153132105 | NARROWS 2105 | 13782.7728 | 8.566 | 226 | 8.3335 | 0.036874 | 1341 | 15410.7982 | 1578.9985 | 0.063768 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3889 | RINCON 1103474 | 43321103 | RINCON 1103 | 29501.1448 | 18.3351 | 174 | 6.4055 | 0.036813 | 1342 | 15429.1333 | 1572.593 | 0.063509 | 1572.593 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6070 | CRESCENT MILLS 21012230 | 103132101 | CRESCENT MILLS 2101 | 10972.6709 | 6.8196 | 112 | 4.0978 | 0.036587 | 1343 | 15435.9529 | 1568.4952 | 0.063344 | 1568.4952 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7395 | HALF MOON BAY 11018902 | 24101101 | HALF MOON BAY 1101 | 22787.1296 | 14.1623 | 145 | 5.2919 | 0.036496 | 1344 | 15450.1152 | 1563.2033 | 0.06313 | 1563.2033 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8155 | PIT NO 5 11011606 | 101321101 | PIT NO 5 1101 | 8892.9459 | 5.527 | 40 | 1.4593 | 0.036482 | 1345 | 15455.6422 | 1561.744 | 0.063071 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6340 | ELECTRA 11011238 | 162161101 | ELECTRA 1101 | 5824.674 | 3.6201 | 81 | 2.9509 | 0.036431 | 1346 | 15459.2622 | 1558.7932 | 0.062952 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
988 | FROGTOWN 1701CB | 163451701 | FROGTOWN 1701 | 16189.7881 | 10.062 | 76 | 2.7614 | 0.036334 | 1347 | 15469.3242 | 1556.0317 | 0.06284 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6703 | POTTER VALLEY P H 110576498 | 42281105 | POTTER VALLEY P H 1105 | 23942.9529 | 14.8806 | 119 | 4.3234 | 0.036331 | 1348 | 15484.2049 | 1551.7084 | 0.062666 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10138 | LLAGAS 2107870396 | 83182107 | LLAGAS 2107 | 1326.4884 | 0.82442 | 40 | 1.4531 | 0.036327 | 1349 | 15485.0293 | 1550.2553 | 0.062607 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7528 | LAYTONVILLE 110189606 | 42681101 | LAYTONVILLE 1101 | 18716.1946 | 11.6322 | 100 | 3.6226 | 0.036226 | 1350 | 15496.6615 | 1546.6327 | 0.062461 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1489 | CURTIS 1702CB | 163351702 | CURTIS 1702 | 35506.5152 | 22.0674 | 293 | 10.5993 | 0.036175 | 1351 | 15518.7289 | 1536.0334 | 0.062033 | 1536.0334 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3159 | SALMON CREEK 1101194 | 43161101 | SALMON CREEK 1101 | 10907.7439 | 6.7792 | 62 | 2.2407 | 0.03614 | 1352 | 15525.5081 | 1533.7927 | 0.061942 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5649 | MORGAN HILL 2111XR186 | 83242111 | MORGAN HILL 2111 | 4651.2538 | 2.8908 | 191 | 6.8827 | 0.036035 | 1353 | 15528.3989 | 1526.91 | 0.061664 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
972 | BRUNSWICK 11062392 | 152481106 | BRUNSWICK 1106 | 9811.7074 | 6.098 | 111 | 3.996 | 0.036 | 1354 | 15534.4969 | 1522.914 | 0.061503 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4961 | TEMPLETON 2110R94 | 183052110 | TEMPLETON 2110 | 22380.6586 | 13.9097 | 179 | 6.4343 | 0.035946 | 1355 | 15548.4066 | 1516.4797 | 0.061243 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2592 | CAYUCOS 11014701 | 182551101 | CAYUCOS 1101 | 3388.7478 | 2.1061 | 65 | 2.3356 | 0.035932 | 1356 | 15550.5127 | 1514.1441 | 0.061149 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
160 | MOUNTAIN QUARRIES 21011346 | 152282101 | MOUNTAIN QUARRIES 2101 | 49591.6622 | 30.8214 | 410 | 14.6948 | 0.035841 | 1357 | 15581.3341 | 1499.4493 | 0.060555 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3187 | SAN MIGUEL 1104R58 | 182661104 | SAN MIGUEL 1104 | 870.4973 | 0.54102 | 130 | 4.6554 | 0.035811 | 1358 | 15581.8751 | 1494.7939 | 0.060367 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8179 | LOS OSITOS 21037062 | 182082103 | LOS OSITOS 2103 | 19664.1429 | 12.2213 | 53 | 1.8977 | 0.035805 | 1359 | 15594.0965 | 1492.8962 | 0.060291 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7911 | OAKLAND K 110217430 | 12101102 | OAKLAND K 1102 | 2364.8217 | 1.4697 | 15 | 0.5365 | 0.035767 | 1360 | 15595.5662 | 1492.3597 | 0.060269 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
88 | SILVERADO 2105658898 | 43432105 | SILVERADO 2105 | 27632.4579 | 17.1737 | 151 | 5.4002 | 0.035763 | 1361 | 15612.7399 | 1486.9595 | 0.060051 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2757 | BURNEY 11011358 | 103311101 | BURNEY 1101 | 13566.1241 | 8.4314 | 51 | 1.8143 | 0.035574 | 1362 | 15621.1713 | 1485.1452 | 0.059978 | 1485.1452 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2335 | PLACERVILLE 21067522 | 153082106 | PLACERVILLE 2106 | 108391.3301 | 67.3656 | 745 | 26.4689 | 0.035529 | 1363 | 15688.537 | 1458.6763 | 0.058909 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10054 | GARBERVILLE 110197300 | 192221101 | GARBERVILLE 1101 | 5161.3802 | 3.2078 | 32 | 1.1341 | 0.035439 | 1364 | 15691.7448 | 1457.5422 | 0.058863 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2680 | SAN RAMON 2107MR284 | 14232107 | SAN RAMON 2107 | 23633.8875 | 14.6886 | 134 | 4.7399 | 0.035373 | 1365 | 15706.4333 | 1452.8023 | 0.058671 | 1452.8023 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6323 | FORT ROSS 112170288 | 42851121 | FORT ROSS 1121 | 18879.7984 | 11.7339 | 94 | 3.3247 | 0.035369 | 1366 | 15718.1672 | 1449.4776 | 0.058537 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4070 | CLAYTON 2213CB | 12022213 | CLAYTON 2213 | 6230.9216 | 3.8725 | 51 | 1.8029 | 0.03535 | 1367 | 15722.0398 | 1447.6747 | 0.058464 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5947 | GARCIA 0401666 | 43040401 | GARCIA 0401 | 3872.5577 | 2.4068 | 12 | 0.42373 | 0.035311 | 1368 | 15724.4466 | 1447.251 | 0.058447 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8699 | UKIAH 1113548420 | 42771113 | UKIAH 1113 | 8369.7684 | 5.2018 | 54 | 1.9041 | 0.035261 | 1369 | 15729.6484 | 1445.3469 | 0.05837 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7081 | NOVATO 110455398 | 42211104 | NOVATO 1104 | 5879.4418 | 3.6541 | 82 | 2.8881 | 0.035221 | 1370 | 15733.3025 | 1442.4588 | 0.058254 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2938 | PETALUMA C 110948000 | 42631109 | PETALUMA C 1109 | 15284.0145 | 9.4991 | 115 | 4.0442 | 0.035167 | 1371 | 15742.8016 | 1438.4145 | 0.05809 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9847 | PENRYN 1105CB | 152561105 | PENRYN 1105 | 978.5043 | 0.60814 | 7 | 0.24593 | 0.035133 | 1372 | 15743.4097 | 1438.1686 | 0.058081 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1921 | WYANDOTTE 110641650 | 102911106 | WYANDOTTE 1106 | 1862.3816 | 1.1575 | 152 | 5.3392 | 0.035126 | 1373 | 15744.5672 | 1432.8294 | 0.057865 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7481 | OTTER 11012052 | 182941101 | OTTER 1101 | 7781.6967 | 4.8364 | 53 | 1.854 | 0.034981 | 1374 | 15749.4036 | 1430.9754 | 0.05779 | 1430.9754 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3295 | REDBUD 1102510 | 43191102 | REDBUD 1102 | 6767.6989 | 4.2062 | 101 | 3.5299 | 0.03495 | 1375 | 15753.6097 | 1427.4454 | 0.057647 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4887 | WOODSIDE 11018972 | 24251101 | WOODSIDE 1101 | 10000.1577 | 6.2151 | 60 | 2.096 | 0.034933 | 1376 | 15759.8249 | 1425.3494 | 0.057563 | 1425.3494 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9433 | JAMESON 11028842 | 63801102 | JAMESON 1102 | 241.1115 | 0.14985 | 42 | 1.4608 | 0.03478 | 1377 | 15759.9747 | 1423.8887 | 0.057504 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5225 | SHADY GLEN 110248894 | 152431102 | SHADY GLEN 1102 | 14293.1803 | 8.8833 | 119 | 4.1244 | 0.034658 | 1378 | 15768.858 | 1419.7643 | 0.057337 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4594 | WEIMAR 11012058 | 152491101 | WEIMAR 1101 | 34315.2065 | 21.327 | 256 | 8.853 | 0.034582 | 1379 | 15790.185 | 1410.9113 | 0.05698 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10315 | CLAYTON 2212523764 | 12022212 | CLAYTON 2212 | 177.5745 | 0.11036 | 5 | 0.17239 | 0.034478 | 1380 | 15790.2954 | 1410.7389 | 0.056973 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4872 | SUNOL 1101MR196 | 14241101 | SUNOL 1101 | 6333.1478 | 3.9361 | 96 | 3.304 | 0.034417 | 1381 | 15794.2315 | 1407.4349 | 0.056839 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1388 | MIWUK 170193062 | 163661701 | MIWUK 1701 | 13326.2559 | 8.2823 | 84 | 2.8813 | 0.034301 | 1382 | 15802.5138 | 1404.5537 | 0.056723 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10333 | SAN ARDO 1101650772 | 182191101 | SAN ARDO 1101 | 1261.3702 | 0.78395 | 10 | 0.3426 | 0.03426 | 1383 | 15803.2977 | 1404.2111 | 0.056709 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
132 | APPLE HILL 1103CB | 153661103 | APPLE HILL 1103 | 31128.549 | 19.3465 | 268 | 9.1777 | 0.034245 | 1384 | 15822.6442 | 1395.0334 | 0.056338 | 1395.0334 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7451 | LOW GAP 1101CB | 192411101 | LOW GAP 1101 | 3490.2509 | 2.1692 | 23 | 0.78267 | 0.034029 | 1385 | 15824.8135 | 1394.2507 | 0.056307 | 1394.2507 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10038 | JESSUP 110194468 | 103441101 | JESSUP 1101 | 2757.0604 | 1.7135 | 21 | 0.71385 | 0.033993 | 1386 | 15826.527 | 1393.5368 | 0.056278 | 1393.5368 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3608 | PIT NO 1 11011552 | 103721101 | PIT NO 1 1101 | 23841.5992 | 14.8177 | 221 | 7.4946 | 0.033912 | 1387 | 15841.3446 | 1386.0422 | 0.055975 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5359 | SAN LUIS OBISPO 1104CB | 182631104 | SAN LUIS OBISPO 1104 | 124.2488 | 0.077221 | 65 | 2.2011 | 0.033863 | 1388 | 15841.4218 | 1383.8412 | 0.055886 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9613 | REEDLEY 1112477952 | 252341112 | REEDLEY 1112 | 282.8465 | 0.17579 | 14 | 0.47381 | 0.033843 | 1389 | 15841.5976 | 1383.3674 | 0.055867 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6901 | JESSUP 11019752 | 103441101 | JESSUP 1101 | 6137.4536 | 3.8145 | 41 | 1.3873 | 0.033837 | 1390 | 15845.4121 | 1381.98 | 0.055811 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8898 | RACETRACK 17036014 | 163761703 | RACETRACK 1703 | 11167.2532 | 6.9405 | 73 | 2.4695 | 0.033829 | 1391 | 15852.3526 | 1379.5105 | 0.055712 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7674 | LLAGAS 21011451 | 83182101 | LLAGAS 2101 | 9963.2757 | 6.1922 | 61 | 2.0624 | 0.03381 | 1392 | 15858.5448 | 1377.4481 | 0.055628 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5880 | POINT MORETTI 11015076 | 82931101 | POINT MORETTI 1101 | 12059.1468 | 7.4948 | 67 | 2.2618 | 0.033758 | 1393 | 15866.0396 | 1375.1863 | 0.055537 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8948 | CLARKSVILLE 2109102734 | 153612109 | CLARKSVILLE 2109 | 954.1374 | 0.593 | 7 | 0.23628 | 0.033754 | 1394 | 15866.6326 | 1374.9501 | 0.055527 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10958 | CURTIS 170511790 | 163351705 | CURTIS 1705 | 22.8988 | 0.014232 | 1 | 0.033732 | 0.033732 | 1395 | 15866.6468 | 1374.9163 | 0.055526 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10247 | MILPITAS 1108342498 | 82831108 | MILPITAS 1108 | 49.0072 | 0.030458 | 9 | 0.3035 | 0.033722 | 1396 | 15866.6773 | 1374.6128 | 0.055514 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5434 | MADISON 1105495270 | 63171105 | MADISON 1105 | 863.3194 | 0.53656 | 50 | 1.6844 | 0.033688 | 1397 | 15867.2139 | 1372.9284 | 0.055446 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5420 | PETALUMA C 1108600 | 42631108 | PETALUMA C 1108 | 5966.5276 | 3.7082 | 107 | 3.586 | 0.033514 | 1398 | 15870.9221 | 1369.3425 | 0.055301 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5203 | HALSEY 11012414 | 152241101 | HALSEY 1101 | 23793.415 | 14.7877 | 168 | 5.6261 | 0.033489 | 1399 | 15885.7098 | 1363.7163 | 0.055074 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
322 | PIKE CITY 11011730 | 152201101 | PIKE CITY 1101 | 13645.4759 | 8.4807 | 73 | 2.441 | 0.033438 | 1400 | 15894.1905 | 1361.2753 | 0.054975 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5994 | RED BLUFF 11011334 | 103541101 | RED BLUFF 1101 | 2886.1165 | 1.7937 | 155 | 5.1706 | 0.033359 | 1401 | 15895.9842 | 1356.1047 | 0.054766 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3212 | HALF MOON BAY 1103H82 | 24101103 | HALF MOON BAY 1103 | 52489.3402 | 32.6223 | 262 | 8.7095 | 0.033242 | 1402 | 15928.6066 | 1347.3952 | 0.054415 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1462 | GIRVAN 11029012 | 103401102 | GIRVAN 1102 | 25166.2142 | 15.6409 | 176 | 5.8466 | 0.033219 | 1403 | 15944.2475 | 1341.5486 | 0.054179 | 1341.5486 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10706 | GONZALES 1104807000 | 182131104 | GONZALES 1104 | 1354.2941 | 0.8417 | 7 | 0.23242 | 0.033203 | 1404 | 15945.0892 | 1341.3162 | 0.054169 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5652 | CORRAL 110214028 | 162991102 | CORRAL 1102 | 6133.5417 | 3.812 | 103 | 3.4066 | 0.033074 | 1405 | 15948.9012 | 1337.9096 | 0.054032 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7408 | KANAKA 11011044 | 103221101 | KANAKA 1101 | 9889.843 | 6.1466 | 17 | 0.56161 | 0.033036 | 1406 | 15955.0478 | 1337.348 | 0.054009 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2114 | WYANDOTTE 11091040 | 102911109 | WYANDOTTE 1109 | 1682.9824 | 1.046 | 62 | 2.0459 | 0.032999 | 1407 | 15956.0938 | 1335.3021 | 0.053926 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9307 | LINCOLN 11012310 | 153701101 | LINCOLN 1101 | 1304.6994 | 0.81088 | 34 | 1.119 | 0.032911 | 1408 | 15956.9046 | 1334.1831 | 0.053881 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4870 | BEAR VALLEY 2101CB | 252192101 | BEAR VALLEY 2101 | 30214.013 | 18.7781 | 154 | 5.065 | 0.03289 | 1409 | 15975.6828 | 1329.118 | 0.053677 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3833 | APPLE HILL 110412832 | 153661104 | APPLE HILL 1104 | 23234.3604 | 14.4402 | 166 | 5.4427 | 0.032787 | 1410 | 15990.123 | 1323.6754 | 0.053457 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10090 | TIVY VALLEY 1107599142 | 252941107 | TIVY VALLEY 1107 | 573.3105 | 0.35631 | 19 | 0.62205 | 0.03274 | 1411 | 15990.4793 | 1323.0533 | 0.053432 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2297 | STANISLAUS 17011812 | 162821701 | STANISLAUS 1701 | 30912.6745 | 19.2124 | 234 | 7.6418 | 0.032657 | 1412 | 16009.6917 | 1315.4116 | 0.053123 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8485 | HOLLISTER 2102113634 | 182492102 | HOLLISTER 2102 | 2941.0752 | 1.8279 | 76 | 2.4817 | 0.032654 | 1413 | 16011.5196 | 1312.9299 | 0.053023 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7193 | ELECTRA 1102CB | 162161102 | ELECTRA 1102 | 4270.3268 | 2.654 | 7 | 0.22761 | 0.032515 | 1414 | 16014.1736 | 1312.7023 | 0.053014 | 1312.7023 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5731 | PLACERVILLE 21062224 | 153082106 | PLACERVILLE 2106 | 16910.6519 | 10.51 | 123 | 3.999 | 0.032512 | 1415 | 16024.6836 | 1308.7033 | 0.052852 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4312 | MENDOCINO 110137462 | 42951101 | MENDOCINO 1101 | 3795.803 | 2.3591 | 63 | 2.0448 | 0.032457 | 1416 | 16027.0427 | 1306.6585 | 0.052769 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8959 | OLETA 1101894006 | 163541101 | OLETA 1101 | 627.9545 | 0.39028 | 8 | 0.25912 | 0.03239 | 1417 | 16027.433 | 1306.3994 | 0.052759 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4513 | SAN LUIS OBISPO 1104V14 | 182631104 | SAN LUIS OBISPO 1104 | 13103.4117 | 8.1438 | 69 | 2.2342 | 0.03238 | 1418 | 16035.5768 | 1304.1652 | 0.052669 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4357 | APPLE HILL 11038412 | 153661103 | APPLE HILL 1103 | 31508.6751 | 19.5828 | 201 | 6.5027 | 0.032352 | 1419 | 16055.1596 | 1297.6625 | 0.052406 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2717 | JOLON 11027002 | 182981102 | JOLON 1102 | 13447.6997 | 8.3578 | 117 | 3.7818 | 0.032323 | 1420 | 16063.5174 | 1293.8807 | 0.052253 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5768 | BIG BASIN 110210254 | 82841102 | BIG BASIN 1102 | 3449.8351 | 2.1441 | 11 | 0.35552 | 0.03232 | 1421 | 16065.6615 | 1293.5252 | 0.052239 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5734 | APPLE HILL 1104CB | 153661104 | APPLE HILL 1104 | 6578.3972 | 4.0885 | 51 | 1.6467 | 0.032289 | 1422 | 16069.75 | 1291.8784 | 0.052173 | 1291.8784 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7601 | JARVIS 1111907698 | 13501111 | JARVIS 1111 | 2466.4182 | 1.5329 | 14 | 0.4515 | 0.03225 | 1423 | 16071.2829 | 1291.4269 | 0.052154 | 1291.4269 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7801 | HALF MOON BAY 11012500 | 24101101 | HALF MOON BAY 1101 | 10490.7768 | 6.5201 | 74 | 2.3859 | 0.032243 | 1424 | 16077.8029 | 1289.041 | 0.052058 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4135 | BRUNSWICK 11041020 | 152481104 | BRUNSWICK 1104 | 46299.321 | 28.7752 | 311 | 10.0103 | 0.032187 | 1425 | 16106.5782 | 1279.0307 | 0.051654 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7772 | FRUITLAND 11422006 | 192311142 | FRUITLAND 1142 | 13398.0902 | 8.327 | 75 | 2.412 | 0.03216 | 1426 | 16114.9051 | 1276.6187 | 0.051556 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10311 | MADISON 2101760730 | 63172101 | MADISON 2101 | 964.21 | 0.59926 | 17 | 0.54562 | 0.032096 | 1427 | 16115.5044 | 1276.0731 | 0.051534 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1525 | CHALLENGE 11025462 | 103201102 | CHALLENGE 1102 | 37447.0905 | 23.2735 | 248 | 7.9564 | 0.032082 | 1428 | 16138.7779 | 1268.1167 | 0.051213 | 1268.1167 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7510 | FRUITLAND 114263170 | 192311142 | FRUITLAND 1142 | 20031.3406 | 12.4496 | 86 | 2.7478 | 0.031951 | 1429 | 16151.2275 | 1265.3689 | 0.051102 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8635 | MOLINO 11026917 | 42571102 | MOLINO 1102 | 11229.1017 | 6.9789 | 58 | 1.8526 | 0.031941 | 1430 | 16158.2064 | 1263.5163 | 0.051027 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5301 | REEDLEY 1104887932 | 252341104 | REEDLEY 1104 | 2732.0868 | 1.698 | 34 | 1.0845 | 0.031896 | 1431 | 16159.9044 | 1262.4319 | 0.050983 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8600 | CALPELLA 1101619542 | 43411101 | CALPELLA 1101 | 2408.2569 | 1.4967 | 21 | 0.66935 | 0.031874 | 1432 | 16161.4011 | 1261.7625 | 0.050956 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
145 | MOUNTAIN QUARRIES 21011130 | 152282101 | MOUNTAIN QUARRIES 2101 | 32234.9294 | 20.0341 | 231 | 7.3538 | 0.031834 | 1433 | 16181.4353 | 1254.4088 | 0.050659 | 1254.4088 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8867 | FORESTHILL 110137238 | 152181101 | FORESTHILL 1101 | 18384.2813 | 11.4259 | 79 | 2.5038 | 0.031693 | 1434 | 16192.8612 | 1251.905 | 0.050558 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10121 | COARSEGOLD 210210610 | 254432102 | COARSEGOLD 2102 | 2196.7777 | 1.3653 | 22 | 0.6951 | 0.031595 | 1435 | 16194.2265 | 1251.2099 | 0.05053 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8481 | PERRY 110185870 | 183071101 | PERRY 1101 | 18409.1169 | 11.4413 | 109 | 3.4337 | 0.031502 | 1436 | 16205.6678 | 1247.7762 | 0.050392 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3885 | BELLEVUE 2103478 | 43182103 | BELLEVUE 2103 | 13396.6859 | 8.3261 | 213 | 6.6661 | 0.031296 | 1437 | 16213.9939 | 1241.1101 | 0.050122 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1942 | UKIAH 1113CB | 42771113 | UKIAH 1113 | 75.4379 | 0.046885 | 69 | 2.1574 | 0.031266 | 1438 | 16214.0408 | 1238.9527 | 0.050035 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10742 | GEYSERVILLE 1101463260 | 42891101 | GEYSERVILLE 1101 | 873.7132 | 0.54302 | 6 | 0.18701 | 0.031168 | 1439 | 16214.5838 | 1238.7657 | 0.050028 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8417 | CURTIS 1703CB | 163351703 | CURTIS 1703 | 14555.9213 | 9.0466 | 119 | 3.7053 | 0.031137 | 1440 | 16223.6304 | 1235.0604 | 0.049878 | 1235.0604 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1279 | ORO FINO 11022556 | 103031102 | ORO FINO 1102 | 10719.4797 | 6.6622 | 41 | 1.2723 | 0.031032 | 1441 | 16230.2926 | 1233.7881 | 0.049827 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1200 | OCEANO 1106CB | 182601106 | OCEANO 1106 | 1811.9234 | 1.1261 | 57 | 1.7687 | 0.03103 | 1442 | 16231.4187 | 1232.0194 | 0.049755 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
766 | SISQUOC 1103M98 | 182811103 | SISQUOC 1103 | 12614.6664 | 7.8401 | 56 | 1.7353 | 0.030988 | 1443 | 16239.2588 | 1230.284 | 0.049685 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8592 | STELLING 11109265 | 83481110 | STELLING 1110 | 8915.672 | 5.5411 | 45 | 1.3941 | 0.03098 | 1444 | 16244.7999 | 1228.8899 | 0.049629 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5933 | MIRABEL 1102524356 | 42091102 | MIRABEL 1102 | 2088.1166 | 1.2978 | 29 | 0.89528 | 0.030872 | 1445 | 16246.0977 | 1227.9947 | 0.049593 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
802 | ALLEGHANY 1101806 | 152101101 | ALLEGHANY 1101 | 18143.3915 | 11.2762 | 65 | 2.0063 | 0.030867 | 1446 | 16257.3739 | 1225.9883 | 0.049512 | 1225.9883 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1506 | GARBERVILLE 11011750 | 192221101 | GARBERVILLE 1101 | 13584.4704 | 8.4428 | 62 | 1.911 | 0.030822 | 1447 | 16265.8167 | 1224.0773 | 0.049434 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4004 | COARSEGOLD 21025380 | 254432102 | COARSEGOLD 2102 | 22971.0374 | 14.2766 | 143 | 4.4053 | 0.030806 | 1448 | 16280.0933 | 1219.672 | 0.049257 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1308 | RINCON 1101578 | 43321101 | RINCON 1101 | 27517.4977 | 17.1022 | 170 | 5.2285 | 0.030756 | 1449 | 16297.1955 | 1214.4436 | 0.049045 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10309 | BOLINAS 1101806 | 42261101 | BOLINAS 1101 | 4898.4533 | 3.0444 | 17 | 0.52134 | 0.030667 | 1450 | 16300.2399 | 1213.9222 | 0.049024 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6983 | BASALT 1106657038 | 42461106 | BASALT 1106 | 4182.6167 | 2.5995 | 72 | 2.2073 | 0.030657 | 1451 | 16302.8394 | 1211.715 | 0.048935 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3194 | DIAMOND SPRINGS 1103467046 | 152261103 | DIAMOND SPRINGS 1103 | 24654.328 | 15.3228 | 266 | 8.1346 | 0.030581 | 1452 | 16318.1622 | 1203.5803 | 0.048607 | 1203.5803 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4703 | WISE 1101CB | 152271101 | WISE 1101 | 7662.7202 | 4.7624 | 112 | 3.4229 | 0.030561 | 1453 | 16322.9246 | 1200.1575 | 0.048468 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6843 | DUNBAR 11033127 | 43071103 | DUNBAR 1103 | 15054.5807 | 9.3565 | 78 | 2.3729 | 0.030422 | 1454 | 16332.2811 | 1197.7845 | 0.048373 | 1197.7845 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3373 | VOLTA 11021646 | 102541102 | VOLTA 1102 | 38535.0265 | 23.9497 | 215 | 6.5396 | 0.030417 | 1455 | 16356.2307 | 1191.2449 | 0.048108 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9167 | WILDWOOD 1101CB | 103611101 | WILDWOOD 1101 | 200.8618 | 0.12484 | 2 | 0.060827 | 0.030413 | 1456 | 16356.3556 | 1191.1841 | 0.048106 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1377 | FROGTOWN 170211212 | 163451702 | FROGTOWN 1702 | 35943.9954 | 22.3393 | 155 | 4.691 | 0.030264 | 1457 | 16378.6949 | 1186.4931 | 0.047917 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2196 | ATASCADERO 1101A02 | 182541101 | ATASCADERO 1101 | 41006.5742 | 25.4858 | 253 | 7.649 | 0.030233 | 1458 | 16404.1807 | 1178.844 | 0.047608 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6596 | STELLING 111060090 | 83481110 | STELLING 1110 | 10545.4488 | 6.554 | 62 | 1.8706 | 0.030171 | 1459 | 16410.7347 | 1176.9735 | 0.047532 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6029 | PANORAMA 1101713592 | 103461101 | PANORAMA 1101 | 16715.2405 | 10.3886 | 152 | 4.5608 | 0.030005 | 1460 | 16421.1233 | 1172.4126 | 0.047348 | 1172.4126 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3261 | CRESCENT MILLS 2101CB | 103132101 | CRESCENT MILLS 2101 | 4545.9264 | 2.8253 | 60 | 1.7959 | 0.029932 | 1461 | 16423.9486 | 1170.6167 | 0.047275 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4399 | PLACERVILLE 210619552 | 153082106 | PLACERVILLE 2106 | 34339.9089 | 21.3424 | 238 | 7.123 | 0.029928 | 1462 | 16445.291 | 1163.4937 | 0.046988 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10240 | LLAGAS 2105534019 | 83182105 | LLAGAS 2105 | 1147.9573 | 0.71346 | 5 | 0.14947 | 0.029893 | 1463 | 16446.0045 | 1163.3442 | 0.046982 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5361 | HOOPA 11013174 | 192401101 | HOOPA 1101 | 29750.1978 | 18.4899 | 162 | 4.8397 | 0.029875 | 1464 | 16464.4943 | 1158.5046 | 0.046786 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5027 | PEORIA 17048040 | 163781704 | PEORIA 1704 | 11785.9847 | 7.325 | 145 | 4.3312 | 0.02987 | 1465 | 16471.8194 | 1154.1733 | 0.046611 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9000 | CASTRO VALLEY 11088971 | 14091108 | CASTRO VALLEY 1108 | 12716.2407 | 7.9032 | 72 | 2.1419 | 0.029749 | 1466 | 16479.7226 | 1152.0314 | 0.046525 | 1152.0314 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3972 | CORRAL 1103936674 | 162991103 | CORRAL 1103 | 1063.5848 | 0.66102 | 56 | 1.6648 | 0.029729 | 1467 | 16480.3836 | 1150.3666 | 0.046458 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5038 | MOLINO 110241392 | 42571102 | MOLINO 1102 | 7062.7077 | 4.3895 | 171 | 5.078 | 0.029696 | 1468 | 16484.7731 | 1145.2886 | 0.046253 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8758 | PUTAH CREEK 11033783 | 63681103 | PUTAH CREEK 1103 | 142.5109 | 0.088571 | 96 | 2.8498 | 0.029685 | 1469 | 16484.8617 | 1142.4388 | 0.046137 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10009 | OREGON TRAIL 110346860 | 103521103 | OREGON TRAIL 1103 | 1149.598 | 0.71448 | 15 | 0.44471 | 0.029648 | 1470 | 16485.5761 | 1141.9941 | 0.046119 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
944 | CURTIS 17036064 | 163351703 | CURTIS 1703 | 30550.9366 | 18.9875 | 199 | 5.8832 | 0.029564 | 1471 | 16504.5637 | 1136.1109 | 0.045882 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5754 | SANTA YNEZ 1102Y18 | 182721102 | SANTA YNEZ 1102 | 7856.8971 | 4.8831 | 60 | 1.7733 | 0.029555 | 1472 | 16509.4468 | 1134.3376 | 0.04581 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1748 | CLAY 110113450 | 163341101 | CLAY 1101 | 1509.284 | 0.93803 | 42 | 1.2403 | 0.029532 | 1473 | 16510.3848 | 1133.0972 | 0.04576 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2073 | WILLOW CREEK 11032936 | 192171103 | WILLOW CREEK 1103 | 53378.6829 | 33.1751 | 249 | 7.3486 | 0.029513 | 1474 | 16543.5599 | 1125.7486 | 0.045463 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3589 | MIRABEL 1101688780 | 42091101 | MIRABEL 1101 | 922.8958 | 0.57358 | 14 | 0.41239 | 0.029456 | 1475 | 16544.1334 | 1125.3362 | 0.045447 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4182 | GARBERVILLE 11021510 | 192221102 | GARBERVILLE 1102 | 21171.8285 | 13.1584 | 107 | 3.1476 | 0.029417 | 1476 | 16557.2918 | 1122.1886 | 0.04532 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3154 | CALISTOGA 1102634 | 42711102 | CALISTOGA 1102 | 18046.5459 | 11.216 | 178 | 5.2284 | 0.029373 | 1477 | 16568.5078 | 1116.9603 | 0.045109 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
133 | GEYSERVILLE 1102522 | 42891102 | GEYSERVILLE 1102 | 12875.7792 | 8.0023 | 109 | 3.2003 | 0.029361 | 1478 | 16576.5102 | 1113.76 | 0.044979 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10360 | OLEMA 110175686 | 42291101 | OLEMA 1101 | 7450.4021 | 4.6305 | 31 | 0.90772 | 0.029281 | 1479 | 16581.1406 | 1112.8523 | 0.044943 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9801 | KANAKA 1101CB | 103221101 | KANAKA 1101 | 7605.9803 | 4.7271 | 37 | 1.0834 | 0.029281 | 1480 | 16585.8678 | 1111.7689 | 0.044899 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4062 | WHITMORE 1101CB | 103601101 | WHITMORE 1101 | 9497.7631 | 5.9029 | 69 | 2.0181 | 0.029248 | 1481 | 16591.7707 | 1109.7508 | 0.044817 | 1109.7508 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1547 | WILLITS 110391810 | 42661103 | WILLITS 1103 | 47379.4324 | 29.4465 | 296 | 8.6442 | 0.029203 | 1482 | 16621.2172 | 1101.1066 | 0.044468 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8861 | GEYSERVILLE 1102331444 | 42891102 | GEYSERVILLE 1102 | 3579.9474 | 2.225 | 44 | 1.2781 | 0.029048 | 1483 | 16623.4421 | 1099.8285 | 0.044417 | 1099.8285 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3080 | PIKE CITY 1101CB | 152201101 | PIKE CITY 1101 | 31622.6384 | 19.6536 | 162 | 4.7034 | 0.029034 | 1484 | 16643.0957 | 1095.125 | 0.044227 | 1095.125 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9245 | FRUITLAND 1142899734 | 192311142 | FRUITLAND 1142 | 5471.5337 | 3.4006 | 36 | 1.0351 | 0.028754 | 1485 | 16646.4963 | 1094.0899 | 0.044185 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2842 | SAN LUIS OBISPO 1101CB | 182631101 | SAN LUIS OBISPO 1101 | 5779.9667 | 3.5923 | 75 | 2.1556 | 0.028742 | 1486 | 16650.0886 | 1091.9342 | 0.044098 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8606 | PUEBLO 1105684564 | 43291105 | PUEBLO 1105 | 443.3906 | 0.27557 | 28 | 0.80024 | 0.02858 | 1487 | 16650.3641 | 1091.134 | 0.044066 | 1091.134 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3749 | VINEYARD 2107978364 | 14502107 | VINEYARD 2107 | 1557.6573 | 0.96809 | 36 | 1.0276 | 0.028543 | 1488 | 16651.3322 | 1090.1064 | 0.044024 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1264 | TEMPLETON 2113CB | 183052113 | TEMPLETON 2113 | 1446.4903 | 0.899 | 288 | 8.2077 | 0.028499 | 1489 | 16652.2312 | 1081.8987 | 0.043693 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6493 | POINT ARENA 11013702 | 43381101 | POINT ARENA 1101 | 7864.1375 | 4.8876 | 35 | 0.99668 | 0.028477 | 1490 | 16657.1188 | 1080.902 | 0.043652 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2973 | TEMPLETON 2111R86 | 183052111 | TEMPLETON 2111 | 17574.2947 | 10.9225 | 160 | 4.5451 | 0.028407 | 1491 | 16668.0413 | 1076.3569 | 0.043469 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2170 | MC KEE 1111711900 | 83531111 | MC KEE 1111 | 14456.1594 | 8.9846 | 116 | 3.2883 | 0.028347 | 1492 | 16677.0259 | 1073.0686 | 0.043336 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7676 | JARVIS 1108289662 | 13501108 | JARVIS 1108 | 533.3553 | 0.33148 | 11 | 0.31049 | 0.028227 | 1493 | 16677.3574 | 1072.7581 | 0.043323 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5235 | BELLEVUE 2103648 | 43182103 | BELLEVUE 2103 | 6117.4965 | 3.802 | 187 | 5.2662 | 0.028161 | 1494 | 16681.1594 | 1067.492 | 0.043111 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10298 | PIT NO 5 11011618 | 101321101 | PIT NO 5 1101 | 9746.1598 | 6.0573 | 15 | 0.42131 | 0.028087 | 1495 | 16687.2167 | 1067.0706 | 0.043094 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5972 | TASSAJARA 2104CB | 14662104 | TASSAJARA 2104 | 159.1645 | 0.098921 | 22 | 0.61638 | 0.028017 | 1496 | 16687.3156 | 1066.4543 | 0.043069 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2469 | ELECTRA 11026014 | 162161102 | ELECTRA 1102 | 8043.0218 | 4.9988 | 50 | 1.3963 | 0.027926 | 1497 | 16692.3144 | 1065.058 | 0.043012 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1225 | SUNOL 1101MR298 | 14241101 | SUNOL 1101 | 8244.1822 | 5.1238 | 39 | 1.0891 | 0.027925 | 1498 | 16697.4382 | 1063.9689 | 0.042968 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
739 | COTATI 1105CB | 42271105 | COTATI 1105 | 4309.0759 | 2.6781 | 35 | 0.97488 | 0.027854 | 1499 | 16700.1163 | 1062.994 | 0.042929 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1612 | CABRILLO 1104Y22 | 183101104 | CABRILLO 1104 | 16721.66 | 10.3926 | 178 | 4.9383 | 0.027743 | 1500 | 16710.5089 | 1058.0558 | 0.04273 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2769 | ANNAPOLIS 110176842 | 42861101 | ANNAPOLIS 1101 | 9156.7064 | 5.6909 | 33 | 0.91488 | 0.027724 | 1501 | 16716.1998 | 1057.1409 | 0.042693 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2631 | TEMPLETON 2111A66 | 183052111 | TEMPLETON 2111 | 54313.8381 | 33.7563 | 429 | 11.8573 | 0.027639 | 1502 | 16749.9561 | 1045.2836 | 0.042214 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2379 | SAN LUIS OBISPO 1103CB | 182631103 | SAN LUIS OBISPO 1103 | 0 | 0 | 68 | 1.8764 | 0.027594 | 1503 | 16749.9561 | 1043.4072 | 0.042138 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4288 | SAN LUIS OBISPO 1103V82 | 182631103 | SAN LUIS OBISPO 1103 | 14130.1147 | 8.7819 | 174 | 4.7975 | 0.027572 | 1504 | 16758.738 | 1038.6096 | 0.041944 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3496 | APPLE HILL 21027502 | 153662102 | APPLE HILL 2102 | 36933.3454 | 22.9542 | 267 | 7.351 | 0.027532 | 1505 | 16781.6922 | 1031.2586 | 0.041647 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3795 | SAN LUIS OBISPO 1101V12 | 182631101 | SAN LUIS OBISPO 1101 | 33868.1694 | 21.0492 | 127 | 3.4815 | 0.027414 | 1506 | 16802.7414 | 1027.7771 | 0.041507 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5816 | PAUL SWEET 210710986 | 83252107 | PAUL SWEET 2107 | 14988.5933 | 9.3155 | 180 | 4.9339 | 0.027411 | 1507 | 16812.0569 | 1022.8431 | 0.041308 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9709 | LAYTONVILLE 1102682 | 42681102 | LAYTONVILLE 1102 | 23844.5349 | 14.8195 | 97 | 2.6464 | 0.027282 | 1508 | 16826.8764 | 1020.1968 | 0.041201 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1461 | LOS OSITOS 21033010 | 182082103 | LOS OSITOS 2103 | 50061.44 | 31.1134 | 229 | 6.2474 | 0.027281 | 1509 | 16857.9898 | 1013.9493 | 0.040948 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6161 | HIGHLANDS 1102556 | 43361102 | HIGHLANDS 1102 | 285.9131 | 0.1777 | 90 | 2.4505 | 0.027227 | 1510 | 16858.1674 | 1011.4989 | 0.040849 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8442 | MARTELL 11016074 | 163011101 | MARTELL 1101 | 5923.6574 | 3.6816 | 34 | 0.92248 | 0.027132 | 1511 | 16861.849 | 1010.5764 | 0.040812 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7912 | HALF MOON BAY 1101818874 | 24101101 | HALF MOON BAY 1101 | 9148.5425 | 5.6859 | 42 | 1.1374 | 0.02708 | 1512 | 16867.5349 | 1009.439 | 0.040766 | 1009.439 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5790 | HIGGINS 1110869408 | 152691110 | HIGGINS 1110 | 710.7103 | 0.44171 | 6 | 0.16225 | 0.027041 | 1513 | 16867.9766 | 1009.2768 | 0.04076 | 1009.2768 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9590 | OILFIELDS 11037006 | 182391103 | OILFIELDS 1103 | 0 | 0 | 42 | 1.1346 | 0.027015 | 1514 | 16867.9766 | 1008.1421 | 0.040714 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9570 | SWIFT 2102889948 | 83392102 | SWIFT 2102 | 706.8877 | 0.43933 | 8 | 0.21509 | 0.026886 | 1515 | 16868.4159 | 1007.927 | 0.040705 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9335 | SAN MIGUEL 1106N34 | 182661106 | SAN MIGUEL 1106 | 6041.6356 | 3.7549 | 62 | 1.6585 | 0.02675 | 1516 | 16872.1708 | 1006.2685 | 0.040638 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8060 | MONTE RIO 1112120 | 42811112 | MONTE RIO 1112 | 10326.1868 | 6.4178 | 67 | 1.788 | 0.026687 | 1517 | 16878.5886 | 1004.4805 | 0.040566 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2780 | HIGHLANDS 1102CB | 43361102 | HIGHLANDS 1102 | 11922.4207 | 7.4098 | 78 | 2.0789 | 0.026652 | 1518 | 16885.9984 | 1002.4017 | 0.040482 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5253 | HOOPA 110182542 | 192401101 | HOOPA 1101 | 19513.0606 | 12.1274 | 150 | 3.9969 | 0.026646 | 1519 | 16898.1259 | 998.4048 | 0.040321 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9493 | BRUNSWICK 1103904574 | 152481103 | BRUNSWICK 1103 | 2518.7659 | 1.5654 | 25 | 0.6657 | 0.026628 | 1520 | 16899.6913 | 997.7391 | 0.040294 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2834 | WILLOW PASS 1101CB | 13911101 | WILLOW PASS 1101 | 1899.3733 | 1.1805 | 75 | 1.9914 | 0.026552 | 1521 | 16900.8718 | 995.7477 | 0.040213 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4322 | WYANDOTTE 11095973 | 102911109 | WYANDOTTE 1109 | 138.2354 | 0.085914 | 35 | 0.92904 | 0.026544 | 1522 | 16900.9577 | 994.8186 | 0.040176 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9896 | PUEBLO 2102773926 | 43292102 | PUEBLO 2102 | 706.7417 | 0.43924 | 25 | 0.66311 | 0.026524 | 1523 | 16901.3969 | 994.1555 | 0.040149 | 994.1555 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7392 | WINDSOR 1103CB | 43501103 | WINDSOR 1103 | 0 | 0 | 64 | 1.6933 | 0.026458 | 1524 | 16901.3969 | 992.4623 | 0.040081 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7312 | PEABODY 2113CB | 63642113 | PEABODY 2113 | 587.3881 | 0.36506 | 40 | 1.057 | 0.026426 | 1525 | 16901.762 | 991.4052 | 0.040038 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5020 | BONNIE NOOK 1101CB | 152301101 | BONNIE NOOK 1101 | 23251.1044 | 14.4507 | 153 | 4.0386 | 0.026396 | 1526 | 16916.2126 | 987.3666 | 0.039875 | 987.3666 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2080 | NEWBURG 11313446 | 192151131 | NEWBURG 1131 | 475.0126 | 0.29522 | 87 | 2.2944 | 0.026372 | 1527 | 16916.5079 | 985.0722 | 0.039782 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5621 | FORT ROSS 112137326 | 42851121 | FORT ROSS 1121 | 8213.253 | 5.1046 | 31 | 0.8171 | 0.026358 | 1528 | 16921.6124 | 984.2551 | 0.039749 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7707 | SUMMIT 110148632 | 152591101 | SUMMIT 1101 | 4391.6286 | 2.7294 | 38 | 1.0003 | 0.026323 | 1529 | 16924.3418 | 983.2548 | 0.039709 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4086 | WEST POINT 110236676 | 163201102 | WEST POINT 1102 | 27305.8877 | 16.9707 | 173 | 4.5232 | 0.026145 | 1530 | 16941.3126 | 978.7317 | 0.039526 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3634 | CHALLENGE 11021902 | 103201102 | CHALLENGE 1102 | 7840.3138 | 4.8728 | 44 | 1.1468 | 0.026064 | 1531 | 16946.1854 | 977.5849 | 0.03948 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5849 | HOPLAND 11011100 | 42251101 | HOPLAND 1101 | 5979.935 | 3.7166 | 68 | 1.772 | 0.026059 | 1532 | 16949.9019 | 975.8128 | 0.039408 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9887 | NOVATO 1104676060 | 42211104 | NOVATO 1104 | 722.7771 | 0.44921 | 9 | 0.23441 | 0.026046 | 1533 | 16950.3511 | 975.5784 | 0.039399 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6186 | CALAVERAS CEMENT 110111188 | 162211101 | CALAVERAS CEMENT 1101 | 48202.5217 | 29.9581 | 294 | 7.641 | 0.02599 | 1534 | 16980.3092 | 967.9374 | 0.03909 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6575 | CLARK ROAD 110247006 | 103091102 | CLARK ROAD 1102 | 7194.664 | 4.4715 | 51 | 1.3227 | 0.025936 | 1535 | 16984.7807 | 966.6146 | 0.039037 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5041 | MARTELL 1103CB | 163011103 | MARTELL 1103 | 2844.8661 | 1.7681 | 76 | 1.9702 | 0.025924 | 1536 | 16986.5488 | 964.6444 | 0.038957 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7535 | PARADISE 11042034 | 102831104 | PARADISE 1104 | 17659.7087 | 10.9756 | 99 | 2.5583 | 0.025842 | 1537 | 16997.5244 | 962.0861 | 0.038854 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3586 | PENRYN 1107346 | 152561107 | PENRYN 1107 | 22629.4944 | 14.0643 | 309 | 7.9433 | 0.025706 | 1538 | 17011.5887 | 954.1428 | 0.038533 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8624 | JESSUP 11012839 | 103441101 | JESSUP 1101 | 2358.3859 | 1.4657 | 20 | 0.5138 | 0.02569 | 1539 | 17013.0544 | 953.629 | 0.038512 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2763 | GOLDTREE 1108CB | 182581108 | GOLDTREE 1108 | 3646.1026 | 2.2661 | 50 | 1.2836 | 0.025673 | 1540 | 17015.3205 | 952.3454 | 0.038461 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9750 | COVELO 1101430286 | 43061101 | COVELO 1101 | 5942.5051 | 3.6933 | 13 | 0.33348 | 0.025652 | 1541 | 17019.0138 | 952.0119 | 0.038447 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8494 | BRENTWOOD 2105502672 | 14592105 | BRENTWOOD 2105 | 2285.3291 | 1.4203 | 127 | 3.2558 | 0.025636 | 1542 | 17020.4341 | 948.7561 | 0.038316 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5780 | GREEN VALLEY 210111054 | 83192101 | GREEN VALLEY 2101 | 39167.0021 | 24.3425 | 272 | 6.9646 | 0.025605 | 1543 | 17044.7766 | 941.7916 | 0.038034 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5526 | LLAGAS 2107XR188 | 83182107 | LLAGAS 2107 | 608.151 | 0.37797 | 43 | 1.1006 | 0.025596 | 1544 | 17045.1546 | 940.6909 | 0.03799 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3427 | COTATI 1105616 | 42271105 | COTATI 1105 | 4247.523 | 2.6399 | 198 | 5.0659 | 0.025585 | 1545 | 17047.7944 | 935.625 | 0.037785 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9956 | CLARKSVILLE 2109781566 | 153612109 | CLARKSVILLE 2109 | 1113.5139 | 0.69205 | 11 | 0.28069 | 0.025518 | 1546 | 17048.4865 | 935.3443 | 0.037774 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1199 | BEAR VALLEY 21059560 | 252192105 | BEAR VALLEY 2105 | 35435.963 | 22.0236 | 226 | 5.7297 | 0.025353 | 1547 | 17070.5101 | 929.6146 | 0.037543 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4849 | ELECTRA 11017104 | 162161101 | ELECTRA 1101 | 19430.6652 | 12.0762 | 148 | 3.7447 | 0.025302 | 1548 | 17082.5863 | 925.87 | 0.037391 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4914 | JESSUP 11019002 | 103441101 | JESSUP 1101 | 1568.4919 | 0.97482 | 74 | 1.8716 | 0.025292 | 1549 | 17083.5611 | 923.9984 | 0.037316 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6329 | SILVERADO 2102636 | 43432102 | SILVERADO 2102 | 8793.2474 | 5.465 | 81 | 2.0483 | 0.025287 | 1550 | 17089.0262 | 921.9501 | 0.037233 | 921.9501 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7235 | BRIDGEVILLE 110137484 | 192461101 | BRIDGEVILLE 1101 | 12688.6958 | 7.8861 | 74 | 1.8698 | 0.025267 | 1551 | 17096.9122 | 920.0803 | 0.037157 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4335 | UKIAH 1114844294 | 42771114 | UKIAH 1114 | 3879.784 | 2.4113 | 55 | 1.3883 | 0.025242 | 1552 | 17099.3235 | 918.692 | 0.037101 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5817 | TIVY VALLEY 110737522 | 252941107 | TIVY VALLEY 1107 | 833.6297 | 0.5181 | 43 | 1.0845 | 0.025221 | 1553 | 17099.8416 | 917.6075 | 0.037058 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
402 | REDBUD 1102922 | 43191102 | REDBUD 1102 | 12589.4258 | 7.8244 | 84 | 2.1157 | 0.025187 | 1554 | 17107.666 | 915.4918 | 0.036972 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4837 | SAN LUIS OBISPO 1104V46 | 182631104 | SAN LUIS OBISPO 1104 | 32077.3964 | 19.9362 | 206 | 5.1879 | 0.025184 | 1555 | 17127.6022 | 910.3039 | 0.036763 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6418 | DUNLAP 1102CB | 254061102 | DUNLAP 1102 | 10840.0956 | 6.7372 | 79 | 1.9873 | 0.025156 | 1556 | 17134.3394 | 908.3166 | 0.036682 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8607 | ANNAPOLIS 1101608 | 42861101 | ANNAPOLIS 1101 | 28658.1175 | 17.8111 | 74 | 1.86 | 0.025135 | 1557 | 17152.1505 | 906.4566 | 0.036607 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8805 | FRUITLAND 114293234 | 192311142 | FRUITLAND 1142 | 18471.7273 | 11.4803 | 96 | 2.4059 | 0.025062 | 1558 | 17163.6308 | 904.0507 | 0.03651 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3300 | FULTON 1102CB | 42561102 | FULTON 1102 | 326.8592 | 0.20314 | 48 | 1.2029 | 0.025061 | 1559 | 17163.8339 | 902.8477 | 0.036462 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4515 | GIRVAN 11019732 | 103401101 | GIRVAN 1101 | 33758.8908 | 20.9813 | 267 | 6.6872 | 0.025046 | 1560 | 17184.8152 | 896.1605 | 0.036191 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
602 | STAFFORD 1102524 | 43201102 | STAFFORD 1102 | 9871.5042 | 6.1352 | 162 | 4.0533 | 0.02502 | 1561 | 17190.9504 | 892.1072 | 0.036028 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6121 | OTTER 110263868 | 182941102 | OTTER 1102 | 25546.2406 | 15.8771 | 171 | 4.2689 | 0.024964 | 1562 | 17206.8275 | 887.8383 | 0.035855 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4102 | SPAULDING 1101578852 | 152251101 | SPAULDING 1101 | 33210.6867 | 20.6406 | 173 | 4.3156 | 0.024946 | 1563 | 17227.4681 | 883.5227 | 0.035681 | 883.5227 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9390 | COAST RD 04015134 | 88820401 | COAST RD 0401 | 1018.6198 | 0.63308 | 23 | 0.57321 | 0.024922 | 1564 | 17228.1011 | 882.9495 | 0.035658 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9959 | BRIDGEVILLE 1102384530 | 192461102 | BRIDGEVILLE 1102 | 6144.6716 | 3.8189 | 12 | 0.29735 | 0.024779 | 1565 | 17231.9201 | 882.6522 | 0.035646 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2322 | KANAKA 11011034 | 103221101 | KANAKA 1101 | 17942.0463 | 11.1511 | 80 | 1.9751 | 0.024689 | 1566 | 17243.0711 | 880.6771 | 0.035566 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5230 | BANGOR 11011806 | 103191101 | BANGOR 1101 | 6482.8365 | 4.0291 | 17 | 0.41764 | 0.024567 | 1567 | 17247.1003 | 880.2594 | 0.035549 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4084 | JOLON 11027040 | 182981102 | JOLON 1102 | 33515.8907 | 20.8303 | 119 | 2.8953 | 0.02433 | 1568 | 17267.9305 | 877.3642 | 0.035432 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7751 | MIWUK 17018050 | 163661701 | MIWUK 1701 | 19488.3045 | 12.1121 | 137 | 3.3307 | 0.024311 | 1569 | 17280.0426 | 874.0335 | 0.035298 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10676 | KERN OIL 1106397902 | 252721106 | KERN OIL 1106 | 717.5326 | 0.44595 | 9 | 0.21872 | 0.024302 | 1570 | 17280.4885 | 873.8148 | 0.035289 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5615 | ELECTRA 110161816 | 162161101 | ELECTRA 1101 | 37826.9874 | 23.5096 | 228 | 5.5405 | 0.0243 | 1571 | 17303.9981 | 868.2743 | 0.035065 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
801 | OCEANO 1102CB | 182601102 | OCEANO 1102 | 25449.7716 | 15.8171 | 183 | 4.4352 | 0.024236 | 1572 | 17319.8153 | 863.8391 | 0.034886 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8403 | MOLINO 1101472660 | 42571101 | MOLINO 1101 | 2333.6937 | 1.4504 | 18 | 0.43606 | 0.024226 | 1573 | 17321.2657 | 863.403 | 0.034869 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4244 | BRUNSWICK 1104CB | 152481104 | BRUNSWICK 1104 | 621.7387 | 0.38641 | 28 | 0.67743 | 0.024194 | 1574 | 17321.6521 | 862.7256 | 0.034841 | 862.7256 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10152 | SPENCE 1102321000 | 182201102 | SPENCE 1102 | 2330.3266 | 1.4483 | 13 | 0.31443 | 0.024187 | 1575 | 17323.1004 | 862.4112 | 0.034829 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3391 | COTATI 1105734248 | 42271105 | COTATI 1105 | 774.6582 | 0.48145 | 9 | 0.2175 | 0.024166 | 1576 | 17323.5819 | 862.1937 | 0.03482 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9545 | WYANDOTTE 110942650 | 102911109 | WYANDOTTE 1109 | 1459.6214 | 0.90716 | 37 | 0.89104 | 0.024082 | 1577 | 17324.489 | 861.3026 | 0.034784 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4392 | CLARK ROAD 110290548 | 103091102 | CLARK ROAD 1102 | 28870.4925 | 17.9431 | 168 | 4.0325 | 0.024003 | 1578 | 17342.4321 | 857.2701 | 0.034621 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9548 | FROGTOWN 1702224708 | 163451702 | FROGTOWN 1702 | 1033.1582 | 0.64211 | 9 | 0.21591 | 0.02399 | 1579 | 17343.0743 | 857.0542 | 0.034612 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2473 | COLUMBIA HILL 110135424 | 152471101 | COLUMBIA HILL 1101 | 22308.0719 | 13.8646 | 147 | 3.4923 | 0.023757 | 1580 | 17356.9388 | 853.5619 | 0.034471 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3207 | SHADY GLEN 110151696 | 152431101 | SHADY GLEN 1101 | 28077.2635 | 17.4501 | 238 | 5.6532 | 0.023753 | 1581 | 17374.3889 | 847.9088 | 0.034243 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7684 | PETALUMA C 1109738866 | 42631109 | PETALUMA C 1109 | 3280.2516 | 2.0387 | 28 | 0.66451 | 0.023732 | 1582 | 17376.4276 | 847.2443 | 0.034216 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10885 | MORGAN HILL 2111940112 | 83242111 | MORGAN HILL 2111 | 455.0253 | 0.2828 | 2 | 0.047401 | 0.023701 | 1583 | 17376.7104 | 847.1969 | 0.034214 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10683 | SAN BERNARD 1101438074 | 253191101 | SAN BERNARD 1101 | 516.2478 | 0.32085 | 6 | 0.14187 | 0.023646 | 1584 | 17377.0313 | 847.055 | 0.034208 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
274 | GEYSERVILLE 1102350 | 42891102 | GEYSERVILLE 1102 | 8365.2365 | 5.199 | 194 | 4.5846 | 0.023632 | 1585 | 17382.2303 | 842.4704 | 0.034023 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6780 | FOOTHILL 1102CB | 182951102 | FOOTHILL 1102 | 12699.351 | 7.8927 | 97 | 2.2918 | 0.023627 | 1586 | 17390.123 | 840.1786 | 0.033931 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5469 | FROGTOWN 1701L3361 | 163451701 | FROGTOWN 1701 | 3015.6838 | 1.8743 | 21 | 0.49595 | 0.023616 | 1587 | 17391.9973 | 839.6827 | 0.033911 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
279 | GEYSERVILLE 1101122 | 42891101 | GEYSERVILLE 1101 | 2112.7276 | 1.3131 | 54 | 1.2745 | 0.023602 | 1588 | 17393.3103 | 838.4082 | 0.033859 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1737 | FORT BRAGG A 110195294 | 42761101 | FORT BRAGG A 1101 | 43494.7194 | 27.0321 | 186 | 4.3615 | 0.023449 | 1589 | 17420.3425 | 834.0467 | 0.033683 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1091 | COLUMBIA HILL 1101764 | 152471101 | COLUMBIA HILL 1101 | 23643.468 | 14.6945 | 146 | 3.4148 | 0.023389 | 1590 | 17435.037 | 830.6318 | 0.033545 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9377 | COVELO 1101516510 | 43061101 | COVELO 1101 | 6073.3479 | 3.7746 | 73 | 1.706 | 0.02337 | 1591 | 17438.8116 | 828.9258 | 0.033476 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2700 | PINE GROVE 11023172 | 163751102 | PINE GROVE 1102 | 60635.9905 | 37.6855 | 448 | 10.4588 | 0.023346 | 1592 | 17476.4971 | 818.4669 | 0.033054 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10187 | LLAGAS 2105154256 | 83182105 | LLAGAS 2105 | 430.6088 | 0.26763 | 2 | 0.046636 | 0.023318 | 1593 | 17476.7647 | 818.4203 | 0.033052 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8561 | FROGTOWN 1702307998 | 163451702 | FROGTOWN 1702 | 895.4026 | 0.5565 | 6 | 0.13989 | 0.023314 | 1594 | 17477.3212 | 818.2804 | 0.033046 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4078 | PENNGROVE 1101170 | 43471101 | PENNGROVE 1101 | 28905.2433 | 17.9647 | 223 | 5.1925 | 0.023285 | 1595 | 17495.286 | 813.0879 | 0.032837 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7270 | LAKEVILLE 1102347280 | 43371102 | LAKEVILLE 1102 | 12761.9341 | 7.9316 | 99 | 2.3024 | 0.023256 | 1596 | 17503.2176 | 810.7855 | 0.032744 | 810.7855 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2895 | ALHAMBRA 11058302 | 14101105 | ALHAMBRA 1105 | 13154.2224 | 8.1754 | 83 | 1.9261 | 0.023206 | 1597 | 17511.393 | 808.8594 | 0.032666 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9502 | WILLOW CREEK 11033090 | 192171103 | WILLOW CREEK 1103 | 17393.6531 | 10.8102 | 58 | 1.3443 | 0.023177 | 1598 | 17522.2032 | 807.5152 | 0.032612 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6394 | ORO FINO 11022040 | 103031102 | ORO FINO 1102 | 14724.8662 | 9.1516 | 21 | 0.48652 | 0.023168 | 1599 | 17531.3548 | 807.0286 | 0.032592 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2990 | HICKS 2101XR548 | 83432101 | HICKS 2101 | 2708.1629 | 1.6831 | 95 | 2.2001 | 0.023159 | 1600 | 17533.0379 | 804.8285 | 0.032503 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
633 | RACETRACK 170310870 | 163761703 | RACETRACK 1703 | 3071.5505 | 1.909 | 28 | 0.64616 | 0.023077 | 1601 | 17534.9469 | 804.1824 | 0.032477 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4692 | PINE GROVE 11023168 | 163751102 | PINE GROVE 1102 | 48228.3961 | 29.9741 | 285 | 6.5678 | 0.023045 | 1602 | 17564.921 | 797.6146 | 0.032212 | 797.6146 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10488 | HALF MOON BAY 1103531594 | 24101103 | HALF MOON BAY 1103 | 3998.7287 | 2.4852 | 25 | 0.57293 | 0.022917 | 1603 | 17567.4062 | 797.0416 | 0.032189 | 797.0416 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1419 | CURTIS 17048140 | 163351704 | CURTIS 1704 | 42456.9039 | 26.3871 | 260 | 5.958 | 0.022915 | 1604 | 17593.7934 | 791.0836 | 0.031948 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5050 | ATASCADERO 1101A22 | 182541101 | ATASCADERO 1101 | 0 | 0 | 167 | 3.8224 | 0.022889 | 1605 | 17593.7934 | 787.2613 | 0.031794 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10722 | TASSAJARA 2103557000 | 14662103 | TASSAJARA 2103 | 335.0317 | 0.20822 | 3 | 0.068564 | 0.022855 | 1606 | 17594.0016 | 787.1927 | 0.031791 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4033 | GANSNER 11012006 | 103021101 | GANSNER 1101 | 27571.1883 | 17.1356 | 151 | 3.4479 | 0.022834 | 1607 | 17611.1372 | 783.7448 | 0.031652 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5518 | BIG BEND 1101641808 | 103751101 | BIG BEND 1101 | 41435.7029 | 25.7525 | 234 | 5.3404 | 0.022822 | 1608 | 17636.8897 | 778.4044 | 0.031436 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8814 | CLAY 11037142 | 163341103 | CLAY 1103 | 6275.5413 | 3.9003 | 100 | 2.2773 | 0.022773 | 1609 | 17640.7899 | 776.1271 | 0.031344 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9514 | HALF MOON BAY 110258448 | 24101102 | HALF MOON BAY 1102 | 7141.1012 | 4.4382 | 22 | 0.50086 | 0.022766 | 1610 | 17645.2282 | 775.6262 | 0.031324 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4404 | EEL RIVER 1102630456 | 192381102 | EEL RIVER 1102 | 8616.6169 | 5.3553 | 37 | 0.84216 | 0.022761 | 1611 | 17650.5834 | 774.784 | 0.03129 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9626 | SAUSALITO 110284278 | 42491102 | SAUSALITO 1102 | 2490.1671 | 1.5476 | 18 | 0.4089 | 0.022717 | 1612 | 17652.1311 | 774.3751 | 0.031273 | 774.3751 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5345 | ELK 11011300 | 42981101 | ELK 1101 | 5711.2619 | 3.5496 | 64 | 1.447 | 0.02261 | 1613 | 17655.6806 | 772.9281 | 0.031215 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3272 | KESWICK 11019712 | 103451101 | KESWICK 1101 | 29909.7326 | 18.589 | 214 | 4.838 | 0.022607 | 1614 | 17674.2697 | 768.0901 | 0.031019 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7529 | EEL RIVER 11021902 | 192381102 | EEL RIVER 1102 | 10562.7391 | 6.5648 | 43 | 0.97115 | 0.022585 | 1615 | 17680.8344 | 767.119 | 0.03098 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9292 | PUEBLO 2102895310 | 43292102 | PUEBLO 2102 | 592.9592 | 0.36853 | 31 | 0.69951 | 0.022565 | 1616 | 17681.203 | 766.4195 | 0.030952 | 766.4195 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3684 | VASCO 1102MR178 | 13751102 | VASCO 1102 | 2579.6297 | 1.6033 | 117 | 2.6398 | 0.022562 | 1617 | 17682.8062 | 763.7797 | 0.030845 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6059 | RINCON 1103198 | 43321103 | RINCON 1103 | 10335.8179 | 6.4238 | 62 | 1.3987 | 0.02256 | 1618 | 17689.23 | 762.381 | 0.030789 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8232 | FOOTHILL 1101251688 | 182951101 | FOOTHILL 1101 | 11233.7101 | 6.9818 | 68 | 1.5291 | 0.022486 | 1619 | 17696.2118 | 760.8519 | 0.030727 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9659 | CAMBRIA 1101858200 | 182771101 | CAMBRIA 1101 | 9200.2096 | 5.718 | 31 | 0.69582 | 0.022446 | 1620 | 17701.9297 | 760.1561 | 0.030699 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5819 | COTTONWOOD 110359128 | 102931103 | COTTONWOOD 1103 | 1201.9482 | 0.74702 | 65 | 1.4558 | 0.022397 | 1621 | 17702.6768 | 758.7002 | 0.03064 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9234 | WILDWOOD 110185112 | 103611101 | WILDWOOD 1101 | 10932.2503 | 6.7944 | 54 | 1.2088 | 0.022386 | 1622 | 17709.4712 | 757.4914 | 0.030591 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2051 | LAYTONVILLE 1101518 | 42681101 | LAYTONVILLE 1101 | 4840.0159 | 3.0081 | 165 | 3.6911 | 0.02237 | 1623 | 17712.4793 | 753.8003 | 0.030442 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4400 | CALISTOGA 1102769230 | 42711102 | CALISTOGA 1102 | 17732.852 | 11.021 | 160 | 3.574 | 0.022338 | 1624 | 17723.5003 | 750.2263 | 0.030298 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1232 | VOLTA 110237350 | 102541102 | VOLTA 1102 | 39069.9006 | 24.2821 | 255 | 5.6788 | 0.02227 | 1625 | 17747.7824 | 744.5475 | 0.030069 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1076 | MC ARTHUR 1101648698 | 103491101 | MC ARTHUR 1101 | 17135.0454 | 10.6495 | 173 | 3.85 | 0.022255 | 1626 | 17758.4319 | 740.6975 | 0.029913 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6771 | HALSEY 1102CB | 152241102 | HALSEY 1102 | 12682.5013 | 7.8822 | 86 | 1.9068 | 0.022172 | 1627 | 17766.3141 | 738.7907 | 0.029836 | 738.7907 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1966 | GARBERVILLE 11011514 | 192221101 | GARBERVILLE 1101 | 23767.6372 | 14.7717 | 123 | 2.7266 | 0.022168 | 1628 | 17781.0858 | 736.0641 | 0.029726 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7554 | SAN LUIS OBISPO 1105512313 | 182631105 | SAN LUIS OBISPO 1105 | 785.9125 | 0.48845 | 10 | 0.22063 | 0.022063 | 1629 | 17781.5743 | 735.8434 | 0.029717 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6120 | PUEBLO 2103895784 | 43292103 | PUEBLO 2103 | 12538.91 | 7.793 | 110 | 2.4251 | 0.022046 | 1630 | 17789.3673 | 733.4184 | 0.029619 | 733.4184 | #N/A | #N/A | #N/A | #N/A | #VALUE!
63 | CORRAL 110175204 | 162991101 | CORRAL 1101 | 1376.4738 | 0.85548 | 130 | 2.8515 | 0.021935 | 1631 | 17790.2227 | 730.5669 | 0.029504 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9574 | MONROE 2103848530 | 43302103 | MONROE 2103 | 715.3706 | 0.44461 | 17 | 0.37143 | 0.021849 | 1632 | 17790.6673 | 730.1954 | 0.029489 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7210 | WEST POINT 110234416 | 163201102 | WEST POINT 1102 | 16821.5127 | 10.4546 | 113 | 2.466 | 0.021823 | 1633 | 17801.122 | 727.7294 | 0.029389 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2105 | WEST POINT 1102CB | 163201102 | WEST POINT 1102 | 28620.471 | 17.7877 | 195 | 4.2374 | 0.02173 | 1634 | 17818.9097 | 723.492 | 0.029218 | 723.492 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6954 | WYANDOTTE 1110144140 | 102911110 | WYANDOTTE 1110 | 417.0111 | 0.25917 | 20 | 0.43439 | 0.021719 | 1635 | 17819.1689 | 723.0576 | 0.029201 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9884 | ELK 1101311906 | 42981101 | ELK 1101 | 1112.4459 | 0.69139 | 12 | 0.2601 | 0.021675 | 1636 | 17819.8603 | 722.7975 | 0.02919 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1046 | GARBERVILLE 11028652 | 192221102 | GARBERVILLE 1102 | 21158.9046 | 13.1503 | 114 | 2.4661 | 0.021633 | 1637 | 17833.0106 | 720.3314 | 0.029091 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3164 | BRUNSWICK 11062416 | 152481106 | BRUNSWICK 1106 | 46563.0328 | 28.9391 | 360 | 7.7569 | 0.021547 | 1638 | 17861.9497 | 712.5745 | 0.028777 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3168 | LUCERNE 1103630 | 43351103 | LUCERNE 1103 | 20012.2615 | 12.4377 | 154 | 3.3154 | 0.021529 | 1639 | 17874.3874 | 709.259 | 0.028643 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9831 | HALF MOON BAY 1101771258 | 24101101 | HALF MOON BAY 1101 | 308.3578 | 0.19165 | 4 | 0.085935 | 0.021484 | 1640 | 17874.5791 | 709.1731 | 0.02864 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8239 | FRUITLAND 11413902 | 192311141 | FRUITLAND 1141 | 8223.6344 | 5.111 | 9 | 0.1925 | 0.021389 | 1641 | 17879.6901 | 708.9806 | 0.028632 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4880 | CURTIS 1705CB | 163351705 | CURTIS 1705 | 21461.232 | 13.3382 | 163 | 3.4854 | 0.021383 | 1642 | 17893.0284 | 705.4952 | 0.028491 | 705.4952 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1762 | VINEYARD 2108609690 | 14502108 | VINEYARD 2108 | 7774.3071 | 4.8318 | 72 | 1.5396 | 0.021383 | 1643 | 17897.8601 | 703.9556 | 0.028429 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7400 | CLARKSVILLE 21096502 | 153612109 | CLARKSVILLE 2109 | 1500.682 | 0.93268 | 52 | 1.1051 | 0.021251 | 1644 | 17898.7928 | 702.8506 | 0.028385 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10207 | MONTE RIO 111159046 | 42811111 | MONTE RIO 1111 | 5641.1576 | 3.506 | 15 | 0.31869 | 0.021246 | 1645 | 17902.2988 | 702.5319 | 0.028372 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4878 | PLACERVILLE 21069712 | 153082106 | PLACERVILLE 2106 | 39765.9579 | 24.7147 | 226 | 4.8004 | 0.021241 | 1646 | 17927.0135 | 697.7315 | 0.028178 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2046 | LINCOLN 11042072 | 153701104 | LINCOLN 1104 | 501.4668 | 0.31166 | 193 | 4.091 | 0.021197 | 1647 | 17927.3252 | 693.6404 | 0.028013 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7243 | SILVERADO 2104708 | 43432104 | SILVERADO 2104 | 6040.8568 | 3.7544 | 61 | 1.292 | 0.02118 | 1648 | 17931.0796 | 692.3484 | 0.027961 | 692.3484 | #N/A | #N/A | #N/A | #N/A | #VALUE!
593 | BRUNSWICK 11021010 | 152481102 | BRUNSWICK 1102 | 71394.2707 | 44.3718 | 479 | 10.1396 | 0.021168 | 1649 | 17975.4514 | 682.2089 | 0.027551 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5896 | CHALLENGE 11015460 | 103201101 | CHALLENGE 1101 | 18980.3372 | 11.7964 | 91 | 1.9215 | 0.021116 | 1650 | 17987.2478 | 680.2873 | 0.027473 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9400 | BELL 110880680 | 152701108 | BELL 1108 | 1030.5857 | 0.64051 | 24 | 0.50627 | 0.021095 | 1651 | 17987.8883 | 679.7811 | 0.027453 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6134 | CALAVERAS CEMENT 110180930 | 162211101 | CALAVERAS CEMENT 1101 | 29528.4888 | 18.3521 | 180 | 3.7835 | 0.021019 | 1652 | 18006.2404 | 675.9976 | 0.0273 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5626 | WYANDOTTE 1103CB | 102911103 | WYANDOTTE 1103 | 394.0047 | 0.24488 | 100 | 2.1017 | 0.021017 | 1653 | 18006.4852 | 673.8959 | 0.027215 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5183 | ALTO 1125902 | 42031125 | ALTO 1125 | 19453.8935 | 12.0907 | 83 | 1.7351 | 0.020905 | 1654 | 18018.5759 | 672.1607 | 0.027145 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7644 | LLAGAS 2101783467 | 83182101 | LLAGAS 2101 | 16448.6096 | 10.2229 | 61 | 1.2679 | 0.020785 | 1655 | 18028.7988 | 670.8929 | 0.027094 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7011 | MOUNTAIN QUARRIES 21011180 | 152282101 | MOUNTAIN QUARRIES 2101 | 20847.2086 | 12.9566 | 141 | 2.9287 | 0.020771 | 1656 | 18041.7554 | 667.9642 | 0.026976 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11063 | APPLE HILL 1104814656 | 153661104 | APPLE HILL 1104 | 28.1252 | 0.01748 | 1 | 0.020643 | 0.020643 | 1657 | 18041.7729 | 667.9435 | 0.026975 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9926 | BUCKS CREEK 1103CB | 102211103 | BUCKS CREEK 1103 | 3707.9332 | 2.3045 | 31 | 0.63931 | 0.020623 | 1658 | 18044.0774 | 667.3042 | 0.026949 | 667.3042 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3649 | FROGTOWN 1702812366 | 163451702 | FROGTOWN 1702 | 4421.1038 | 2.7477 | 28 | 0.57668 | 0.020596 | 1659 | 18046.8251 | 666.7275 | 0.026926 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9417 | DUNBAR 1102694641 | 43071102 | DUNBAR 1102 | 6527.852 | 4.0571 | 49 | 1.0071 | 0.020553 | 1660 | 18050.8822 | 665.7204 | 0.026885 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8194 | STANISLAUS 17017144 | 162821701 | STANISLAUS 1701 | 7491.0055 | 4.6557 | 52 | 1.0649 | 0.020479 | 1661 | 18055.5379 | 664.6556 | 0.026842 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10788 | FITCH MOUNTAIN 1111752596 | 42751111 | FITCH MOUNTAIN 1111 | 395.1334 | 0.24558 | 6 | 0.12279 | 0.020465 | 1662 | 18055.7835 | 664.5328 | 0.026837 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3463 | WOODACRE 1102851 | 43021102 | WOODACRE 1102 | 2029.0984 | 1.2611 | 14 | 0.28582 | 0.020416 | 1663 | 18057.0446 | 664.247 | 0.026826 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
331 | WEST POINT 11024790 | 163201102 | WEST POINT 1102 | 52731.0383 | 32.7726 | 305 | 6.2151 | 0.020377 | 1664 | 18089.8171 | 658.0318 | 0.026575 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8939 | STELLING 111060080 | 83481110 | STELLING 1110 | 15418.9407 | 9.5829 | 64 | 1.3021 | 0.020345 | 1665 | 18099.4001 | 656.7297 | 0.026522 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5387 | PLACERVILLE 210611132 | 153082106 | PLACERVILLE 2106 | 69633.6958 | 43.2776 | 420 | 8.5102 | 0.020262 | 1666 | 18142.6777 | 648.2195 | 0.026178 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3326 | ORO FINO 110265932 | 103031102 | ORO FINO 1102 | 7276.7194 | 4.5225 | 48 | 0.97052 | 0.020219 | 1667 | 18147.2002 | 647.249 | 0.026139 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7230 | PINE GROVE 110283098 | 163751102 | PINE GROVE 1102 | 12739.0077 | 7.9173 | 104 | 2.0942 | 0.020137 | 1668 | 18155.1175 | 645.1548 | 0.026055 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2235 | MOLINO 1102318 | 42571102 | MOLINO 1102 | 31114.0365 | 19.3375 | 228 | 4.5821 | 0.020097 | 1669 | 18174.455 | 640.5727 | 0.02587 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9552 | JOLON 11027068 | 182981102 | JOLON 1102 | 6139.1207 | 3.8155 | 12 | 0.23993 | 0.019995 | 1670 | 18178.2705 | 640.3327 | 0.02586 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7621 | UKIAH 1115CB | 42771115 | UKIAH 1115 | 6936.1203 | 4.3108 | 73 | 1.4531 | 0.019906 | 1671 | 18182.5813 | 638.8796 | 0.025801 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5118 | SAN LUIS OBISPO 1107V60 | 182631107 | SAN LUIS OBISPO 1107 | 25811.5583 | 16.042 | 142 | 2.8258 | 0.0199 | 1672 | 18198.6233 | 636.0538 | 0.025687 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1916 | MOLINO 1104368158 | 42571104 | MOLINO 1104 | 4484.8758 | 2.7874 | 105 | 2.0855 | 0.019862 | 1673 | 18201.4107 | 633.9684 | 0.025603 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8812 | ANTLER 11011376 | 103271101 | ANTLER 1101 | 14477.8455 | 8.998 | 70 | 1.3885 | 0.019836 | 1674 | 18210.4087 | 632.5799 | 0.025547 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3393 | SILVERADO 2102714 | 43432102 | SILVERADO 2102 | 5568.6627 | 3.4609 | 121 | 2.3993 | 0.019829 | 1675 | 18213.8697 | 630.1806 | 0.02545 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8102 | FORESTHILL 110175340 | 152181101 | FORESTHILL 1101 | 7696.0179 | 4.7831 | 62 | 1.2202 | 0.01968 | 1676 | 18218.6528 | 628.9604 | 0.025401 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7713 | DUNBAR 11014817 | 43071101 | DUNBAR 1101 | 5079.2964 | 3.1568 | 42 | 0.82599 | 0.019666 | 1677 | 18221.8096 | 628.1344 | 0.025367 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6368 | EAST QUINCY 1101951424 | 102551101 | EAST QUINCY 1101 | 1124.2371 | 0.69872 | 49 | 0.95554 | 0.019501 | 1678 | 18222.5083 | 627.1789 | 0.025329 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6762 | HOOPA 11013304 | 192401101 | HOOPA 1101 | 27901.6416 | 17.341 | 88 | 1.7148 | 0.019486 | 1679 | 18239.8493 | 625.4641 | 0.025259 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4845 | SAN JOAQUIN #3 110210342 | 252531102 | SAN JOAQUIN #3 1102 | 2930.8819 | 1.8216 | 23 | 0.44766 | 0.019463 | 1680 | 18241.6709 | 625.0165 | 0.025241 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3381 | LUCERNE 110638436 | 43351106 | LUCERNE 1106 | 7253.5318 | 4.5081 | 62 | 1.2043 | 0.019424 | 1681 | 18246.179 | 623.8122 | 0.025193 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8990 | HALF MOON BAY 1103540991 | 24101103 | HALF MOON BAY 1103 | 2544.5262 | 1.5814 | 16 | 0.31068 | 0.019417 | 1682 | 18247.7604 | 623.5015 | 0.02518 | 623.5015 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1522 | RIO DELL 11021504 | 192251102 | RIO DELL 1102 | 17454.8051 | 10.8482 | 64 | 1.2379 | 0.019342 | 1683 | 18258.6086 | 622.2636 | 0.02513 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6286 | DUNBAR 1101416 | 43071101 | DUNBAR 1101 | 4249.986 | 2.6414 | 28 | 0.54085 | 0.019316 | 1684 | 18261.25 | 621.7228 | 0.025108 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2445 | MC ARTHUR 11011546 | 103491101 | MC ARTHUR 1101 | 22193.9329 | 13.7936 | 102 | 1.9643 | 0.019258 | 1685 | 18275.0436 | 619.7585 | 0.025029 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2748 | HALF MOON BAY 11036018 | 24101103 | HALF MOON BAY 1103 | 25219.5525 | 15.6741 | 160 | 3.0757 | 0.019223 | 1686 | 18290.7177 | 616.6828 | 0.024905 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4766 | CLOVERDALE 1101807953 | 42821101 | CLOVERDALE 1101 | 745.8215 | 0.46353 | 11 | 0.21093 | 0.019176 | 1687 | 18291.1812 | 616.4718 | 0.024896 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3508 | CLEAR LAKE 1102223792 | 42141102 | CLEAR LAKE 1102 | 1262.347 | 0.78455 | 10 | 0.19106 | 0.019106 | 1688 | 18291.9658 | 616.2808 | 0.024889 | 616.2808 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3278 | KONOCTI 1108CB | 43311108 | KONOCTI 1108 | 10229.3323 | 6.3576 | 98 | 1.864 | 0.019021 | 1689 | 18298.3233 | 614.4167 | 0.024813 | 614.4167 | #N/A | #N/A | #N/A | #N/A | #VALUE!
218 | MADISON 21017702 | 63172101 | MADISON 2101 | 0 | 0 | 168 | 3.174 | 0.018893 | 1690 | 18298.3233 | 611.2427 | 0.024685 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5100 | RIO DELL 110270960 | 192251102 | RIO DELL 1102 | 9297.8122 | 5.7786 | 103 | 1.9167 | 0.018609 | 1691 | 18304.102 | 609.3261 | 0.024608 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1226 | FORT ROSS 11212987 | 42851121 | FORT ROSS 1121 | 3171.9583 | 1.9714 | 18 | 0.33485 | 0.018603 | 1692 | 18306.0733 | 608.9912 | 0.024594 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4217 | CHALLENGE 1102CB | 103201102 | CHALLENGE 1102 | 24644.898 | 15.3169 | 123 | 2.2755 | 0.0185 | 1693 | 18321.3902 | 606.7157 | 0.024502 | 606.7157 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4592 | PHILO 1102928 | 42601102 | PHILO 1102 | 22468.3871 | 13.9642 | 125 | 2.3111 | 0.018489 | 1694 | 18335.3544 | 604.4046 | 0.024409 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4143 | MENDOCINO 1101CB | 42951101 | MENDOCINO 1101 | 4240.0548 | 2.6352 | 54 | 0.98966 | 0.018327 | 1695 | 18337.9897 | 603.4149 | 0.024369 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5556 | WEST POINT 11021305 | 163201102 | WEST POINT 1102 | 18201.3708 | 11.3122 | 105 | 1.9226 | 0.01831 | 1696 | 18349.3019 | 601.4923 | 0.024291 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7818 | SONOMA 1105575872 | 42721105 | SONOMA 1105 | 1906.857 | 1.1851 | 12 | 0.21935 | 0.018279 | 1697 | 18350.487 | 601.273 | 0.024282 | 601.273 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1713 | HALF MOON BAY 1103H80 | 24101103 | HALF MOON BAY 1103 | 31889.194 | 19.8193 | 164 | 2.9927 | 0.018248 | 1698 | 18370.3063 | 598.2803 | 0.024162 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3304 | DIAMOND SPRINGS 11039432 | 152261103 | DIAMOND SPRINGS 1103 | 28100.4349 | 17.4645 | 251 | 4.5765 | 0.018233 | 1699 | 18387.7708 | 593.7038 | 0.023977 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1922 | ALLEGHANY 1102CB | 152101102 | ALLEGHANY 1102 | 28981.2992 | 18.012 | 104 | 1.8932 | 0.018204 | 1700 | 18405.7828 | 591.8106 | 0.0239 | 591.8106 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4888 | DUNBAR 110179086 | 43071101 | DUNBAR 1101 | 10954.594 | 6.8083 | 82 | 1.4907 | 0.018179 | 1701 | 18412.5911 | 590.3199 | 0.02384 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1290 | FROGTOWN 170232556 | 163451702 | FROGTOWN 1702 | 188.0999 | 0.1169 | 19 | 0.34478 | 0.018147 | 1702 | 18412.708 | 589.9751 | 0.023826 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4459 | CLARK ROAD 11022094 | 103091102 | CLARK ROAD 1102 | 5517.0419 | 3.4289 | 11 | 0.19897 | 0.018088 | 1703 | 18416.1369 | 589.7761 | 0.023818 | 589.7761 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8596 | SAN JOAQUIN #3 1101CB | 252531101 | SAN JOAQUIN #3 1101 | 19055.2866 | 11.8429 | 80 | 1.4463 | 0.018079 | 1704 | 18427.9798 | 588.3298 | 0.02376 | 588.3298 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7985 | MERCED FALLS 1102482838 | 252811102 | MERCED FALLS 1102 | 14284.261 | 8.8777 | 52 | 0.93898 | 0.018057 | 1705 | 18436.8575 | 587.3908 | 0.023722 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5651 | MOUNTAIN QUARRIES 21012422 | 152282101 | MOUNTAIN QUARRIES 2101 | 13951.5772 | 8.671 | 81 | 1.4615 | 0.018043 | 1706 | 18445.5285 | 585.9293 | 0.023663 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9070 | SILVERADO 2102437194 | 43432102 | SILVERADO 2102 | 1702.9792 | 1.0584 | 17 | 0.30645 | 0.018026 | 1707 | 18446.5869 | 585.6229 | 0.02365 | 585.6229 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2577 | HARTLEY 110186876 | 43211101 | HARTLEY 1101 | 3945.9351 | 2.4524 | 110 | 1.9808 | 0.018007 | 1708 | 18449.0393 | 583.6421 | 0.02357 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5850 | GEYSERVILLE 1101711966 | 42891101 | GEYSERVILLE 1101 | 6326.045 | 3.9317 | 122 | 2.1848 | 0.017908 | 1709 | 18452.971 | 581.4573 | 0.023482 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8508 | PIKE CITY 11011720 | 152201101 | PIKE CITY 1101 | 9489.0848 | 5.8975 | 34 | 0.60738 | 0.017864 | 1710 | 18458.8685 | 580.8499 | 0.023458 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4021 | GRASS VALLEY 11012766 | 152031101 | GRASS VALLEY 1101 | 5300.562 | 3.2943 | 31 | 0.55287 | 0.017834 | 1711 | 18462.1628 | 580.297 | 0.023435 | 580.297 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5421 | DUNBAR 1102261774 | 43071102 | DUNBAR 1102 | 21761.0718 | 13.5246 | 142 | 2.5319 | 0.01783 | 1712 | 18475.6874 | 577.7652 | 0.023333 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1746 | TEMPLETON 2111CB | 183052111 | TEMPLETON 2111 | 3627.2584 | 2.2544 | 118 | 2.1007 | 0.017802 | 1713 | 18477.9418 | 575.6645 | 0.023248 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2820 | ALTO 1124432 | 42031124 | ALTO 1124 | 12624.3351 | 7.8461 | 72 | 1.2765 | 0.017729 | 1714 | 18485.7878 | 574.388 | 0.023197 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5452 | PUEBLO 2102850102 | 43292102 | PUEBLO 2102 | 287.4404 | 0.17865 | 23 | 0.40756 | 0.01772 | 1715 | 18485.9665 | 573.9804 | 0.02318 | 573.9804 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3283 | CURTIS 170390320 | 163351703 | CURTIS 1703 | 44849.664 | 27.8742 | 282 | 4.9917 | 0.017701 | 1716 | 18513.8407 | 568.9887 | 0.022979 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3501 | CRESCENT MILLS 21012232 | 103132101 | CRESCENT MILLS 2101 | 25513.6468 | 15.8568 | 128 | 2.2614 | 0.017667 | 1717 | 18529.6976 | 566.7274 | 0.022887 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10143 | GRASS VALLEY 1101750804 | 152031101 | GRASS VALLEY 1101 | 390.0676 | 0.24243 | 5 | 0.088275 | 0.017655 | 1718 | 18529.94 | 566.6391 | 0.022884 | 566.6391 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3289 | MONTICELLO 11011589 | 43051101 | MONTICELLO 1101 | 6873.0951 | 4.2717 | 52 | 0.91781 | 0.01765 | 1719 | 18534.2117 | 565.7213 | 0.022847 | 565.7213 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1138 | ELECTRA 110136816 | 162161101 | ELECTRA 1101 | 8023.9266 | 4.9869 | 60 | 1.0575 | 0.017625 | 1720 | 18539.1986 | 564.6638 | 0.022804 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9331 | WILLOW CREEK 1102CB | 192171102 | WILLOW CREEK 1102 | 11789.4236 | 7.3272 | 71 | 1.25 | 0.017606 | 1721 | 18546.5257 | 563.4138 | 0.022753 | 563.4138 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6284 | ANTLER 11011378 | 103271101 | ANTLER 1101 | 39490.7149 | 24.5436 | 201 | 3.5323 | 0.017574 | 1722 | 18571.0694 | 559.8814 | 0.022611 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8843 | HOLLISTER 2104117328 | 182492104 | HOLLISTER 2104 | 9894.6539 | 6.1496 | 44 | 0.77216 | 0.017549 | 1723 | 18577.2189 | 559.1093 | 0.02258 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
106 | WYANDOTTE 11101954 | 102911110 | WYANDOTTE 1110 | 4223.5591 | 2.625 | 132 | 2.3057 | 0.017468 | 1724 | 18579.8439 | 556.8035 | 0.022487 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7269 | CURTIS 17046060 | 163351704 | CURTIS 1704 | 6540.8971 | 4.0652 | 50 | 0.873 | 0.01746 | 1725 | 18583.9091 | 555.9305 | 0.022451 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4024 | MOLINO 11015042 | 42571101 | MOLINO 1101 | 9737.3633 | 6.0518 | 90 | 1.5687 | 0.01743 | 1726 | 18589.9609 | 554.3619 | 0.022388 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8422 | FROGTOWN 1702739858 | 163451702 | FROGTOWN 1702 | 7850.7225 | 4.8793 | 46 | 0.80161 | 0.017426 | 1727 | 18594.8402 | 553.5602 | 0.022356 | 553.5602 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3353 | KANAKA 11011406 | 103221101 | KANAKA 1101 | 43882.3619 | 27.2731 | 204 | 3.5397 | 0.017352 | 1728 | 18622.1132 | 550.0205 | 0.022213 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10623 | MORGAN HILL 2111477914 | 83242111 | MORGAN HILL 2111 | 307.8291 | 0.19132 | 3 | 0.051987 | 0.017329 | 1729 | 18622.3045 | 549.9685 | 0.022211 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1703 | SAN LUIS OBISPO 1105796050 | 182631105 | SAN LUIS OBISPO 1105 | 383.7484 | 0.2385 | 45 | 0.7781 | 0.017291 | 1730 | 18622.543 | 549.1904 | 0.022179 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2587 | MENLO 11031721 | 24131103 | MENLO 1103 | 10927.2973 | 6.7914 | 52 | 0.89751 | 0.01726 | 1731 | 18629.3344 | 548.2929 | 0.022143 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5617 | MIRABEL 1101298 | 42091101 | MIRABEL 1101 | 20253.8323 | 12.5878 | 123 | 2.1202 | 0.017238 | 1732 | 18641.9222 | 546.1727 | 0.022057 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
183 | CLEAR LAKE 110192870 | 42141101 | CLEAR LAKE 1101 | 185.9475 | 0.11557 | 187 | 3.2176 | 0.017207 | 1733 | 18642.0378 | 542.9551 | 0.021927 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5761 | SAN LUIS OBISPO 1102597518 | 182631102 | SAN LUIS OBISPO 1102 | 65.1647 | 0.0405 | 30 | 0.51524 | 0.017175 | 1734 | 18642.0783 | 542.4398 | 0.021906 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
694 | PIT NO 1 11013312 | 103721101 | PIT NO 1 1101 | 12944.3529 | 8.045 | 82 | 1.4079 | 0.017169 | 1735 | 18650.1233 | 541.0319 | 0.02185 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6571 | MC ARTHUR 11011488 | 103491101 | MC ARTHUR 1101 | 3970.6557 | 2.4678 | 217 | 3.7195 | 0.01714 | 1736 | 18652.5911 | 537.3125 | 0.021699 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7993 | STILLWATER 1101CB | 103561101 | STILLWATER 1101 | 6754.5413 | 4.198 | 47 | 0.80543 | 0.017137 | 1737 | 18656.789 | 536.5071 | 0.021667 | 536.5071 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3453 | LOS GATOS 110760114 | 82021107 | LOS GATOS 1107 | 39130.9882 | 24.3201 | 220 | 3.7337 | 0.016971 | 1738 | 18681.1091 | 532.7734 | 0.021516 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3503 | CLAYTON 2215184604 | 12022215 | CLAYTON 2215 | 3361.2922 | 2.0891 | 106 | 1.7951 | 0.016935 | 1739 | 18683.1982 | 530.9783 | 0.021444 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5231 | BURNEY 1101CB | 103311101 | BURNEY 1101 | 1997.9569 | 1.2417 | 29 | 0.48997 | 0.016895 | 1740 | 18684.4399 | 530.4883 | 0.021424 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5033 | ALTO 11243121 | 42031124 | ALTO 1124 | 4501.3904 | 2.7976 | 36 | 0.60788 | 0.016885 | 1741 | 18687.2375 | 529.8804 | 0.021399 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4749 | FRUITLAND 11418860 | 192311141 | FRUITLAND 1141 | 3211.911 | 1.9962 | 34 | 0.57347 | 0.016867 | 1742 | 18689.2337 | 529.307 | 0.021376 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8284 | FRENCH GULCH 11011464 | 103381101 | FRENCH GULCH 1101 | 1371.4854 | 0.85238 | 10 | 0.1686 | 0.01686 | 1743 | 18690.0861 | 529.1384 | 0.021369 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10232 | TIGER CREEK 0201CB | 161380201 | TIGER CREEK 0201 | 6022.6718 | 3.7431 | 20 | 0.33603 | 0.016801 | 1744 | 18693.8292 | 528.8024 | 0.021356 | 528.8024 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5809 | TEMPLETON 2110N32 | 183052110 | TEMPLETON 2110 | 47470.9597 | 29.5034 | 251 | 4.208 | 0.016765 | 1745 | 18723.3326 | 524.5943 | 0.021186 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7289 | PLACERVILLE 111019582 | 153081110 | PLACERVILLE 1110 | 11698.5344 | 7.2707 | 80 | 1.341 | 0.016762 | 1746 | 18730.6033 | 523.2534 | 0.021132 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9046 | OTTER 11022166 | 182941102 | OTTER 1102 | 6559.0006 | 4.0764 | 41 | 0.68648 | 0.016743 | 1747 | 18734.6798 | 522.5669 | 0.021104 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3955 | GRAYS FLAT 0401CB | 102530401 | GRAYS FLAT 0401 | 17261.1138 | 10.7279 | 77 | 1.2881 | 0.016728 | 1748 | 18745.4076 | 521.2788 | 0.021052 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4383 | FRUITLAND 114195324 | 192311141 | FRUITLAND 1141 | 10430.483 | 6.4826 | 40 | 0.66685 | 0.016671 | 1749 | 18751.8902 | 520.612 | 0.021025 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9718 | GARBERVILLE 1101323694 | 192221101 | GARBERVILLE 1101 | 10298.1869 | 6.4004 | 17 | 0.28324 | 0.016661 | 1750 | 18758.2906 | 520.3287 | 0.021014 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7551 | GARBERVILLE 1101438596 | 192221101 | GARBERVILLE 1101 | 17736.2716 | 11.0232 | 69 | 1.1471 | 0.016624 | 1751 | 18769.3137 | 519.1817 | 0.020967 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9937 | OTTER 11022002 | 182941102 | OTTER 1102 | 4546.6103 | 2.8257 | 27 | 0.44657 | 0.01654 | 1752 | 18772.1395 | 518.7351 | 0.020949 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5432 | ALLEGHANY 1101804 | 152101101 | ALLEGHANY 1101 | 35223.4878 | 21.8915 | 163 | 2.6936 | 0.016525 | 1753 | 18794.031 | 516.0415 | 0.02084 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6356 | NORTH BRANCH 110113496 | 163231101 | NORTH BRANCH 1101 | 3211.8845 | 1.9962 | 58 | 0.95734 | 0.016506 | 1754 | 18796.0272 | 515.0842 | 0.020802 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
249 | RINCON 1103CB | 43321103 | RINCON 1103 | 3931.2505 | 2.4433 | 41 | 0.67489 | 0.016461 | 1755 | 18798.4705 | 514.4093 | 0.020774 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1025 | MARIPOSA 2101439030 | 254452101 | MARIPOSA 2101 | 31570.1115 | 19.621 | 200 | 3.2868 | 0.016434 | 1756 | 18818.0914 | 511.1225 | 0.020642 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8791 | GLENN 11012012 | 102601101 | GLENN 1101 | 3708.2991 | 2.3047 | 73 | 1.1972 | 0.016401 | 1757 | 18820.3962 | 509.9252 | 0.020593 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10780 | CALPINE 1144962 | 48011144 | CALPINE 1144 | 6465.1165 | 4.0181 | 13 | 0.21307 | 0.01639 | 1758 | 18824.4143 | 509.7121 | 0.020585 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
715 | ALTO 1124430 | 42031124 | ALTO 1124 | 11355.5979 | 7.0575 | 92 | 1.5006 | 0.016311 | 1759 | 18831.4718 | 508.2116 | 0.020524 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9633 | MONTE RIO 11131067 | 42811113 | MONTE RIO 1113 | 1306.3843 | 0.81192 | 11 | 0.176 | 0.016 | 1760 | 18832.2837 | 508.0356 | 0.020517 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1412 | PLACERVILLE 1109CB | 153081109 | PLACERVILLE 1109 | 17449.8742 | 10.8452 | 133 | 2.1275 | 0.015996 | 1761 | 18843.1289 | 505.9081 | 0.020431 | 505.9081 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8245 | BEAR VALLEY 210513430 | 252192105 | BEAR VALLEY 2105 | 21106.6036 | 13.1178 | 129 | 2.057 | 0.015945 | 1762 | 18856.2467 | 503.8511 | 0.020348 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8966 | MORAGA 1101772781 | 13801101 | MORAGA 1101 | 2316.7745 | 1.4399 | 12 | 0.1892 | 0.015766 | 1763 | 18857.6866 | 503.6619 | 0.02034 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3619 | PINE GROVE 11013166 | 163751101 | PINE GROVE 1101 | 19778.1528 | 12.2922 | 147 | 2.3172 | 0.015763 | 1764 | 18869.9788 | 501.3447 | 0.020247 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4486 | WEST POINT 1101CB | 163201101 | WEST POINT 1101 | 7713.2869 | 4.7938 | 20 | 0.31472 | 0.015736 | 1765 | 18874.7727 | 501.03 | 0.020234 | 501.03 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3894 | BONNIE NOOK 110186696 | 152301101 | BONNIE NOOK 1101 | 15512.3886 | 9.641 | 86 | 1.3421 | 0.015606 | 1766 | 18884.4137 | 499.6879 | 0.02018 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1913 | OLEMA 1101416 | 42291101 | OLEMA 1101 | 26031.4486 | 16.1787 | 79 | 1.2278 | 0.015542 | 1767 | 18900.5923 | 498.4601 | 0.02013 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2787 | PINE GROVE 11013170 | 163751101 | PINE GROVE 1101 | 64049.8846 | 39.8073 | 445 | 6.9125 | 0.015534 | 1768 | 18940.3996 | 491.5476 | 0.019851 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8370 | SWIFT 2110XR332 | 83392110 | SWIFT 2110 | 29699.1922 | 18.4582 | 83 | 1.2892 | 0.015532 | 1769 | 18958.8578 | 490.2584 | 0.019799 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6569 | CURTIS 17058170 | 163351705 | CURTIS 1705 | 12388.5528 | 7.6995 | 109 | 1.6904 | 0.015509 | 1770 | 18966.5573 | 488.568 | 0.019731 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9835 | SPRING GAP 1702CB | 162831702 | SPRING GAP 1702 | 11971.7401 | 7.4405 | 18 | 0.27759 | 0.015422 | 1771 | 18973.9978 | 488.2904 | 0.01972 | 488.2904 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1693 | BUCKS CREEK 1103338520 | 102211103 | BUCKS CREEK 1103 | 12653.3631 | 7.8641 | 87 | 1.3409 | 0.015412 | 1772 | 18981.8619 | 486.9496 | 0.019665 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4370 | OREGON TRAIL 11021584 | 103521102 | OREGON TRAIL 1102 | 20998.6153 | 13.0507 | 136 | 2.0926 | 0.015387 | 1773 | 18994.9126 | 484.857 | 0.019581 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6223 | MOLINO 1101152 | 42571101 | MOLINO 1101 | 2668.6977 | 1.6586 | 125 | 1.9072 | 0.015258 | 1774 | 18996.5712 | 482.9497 | 0.019504 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
991 | PEORIA 170413494 | 163781704 | PEORIA 1704 | 4454.735 | 2.7686 | 93 | 1.4148 | 0.015212 | 1775 | 18999.3399 | 481.535 | 0.019447 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10392 | VINEYARD 2108383748 | 14502108 | VINEYARD 2108 | 582.318 | 0.36191 | 4 | 0.060827 | 0.015207 | 1776 | 18999.7018 | 481.4741 | 0.019444 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5782 | GARBERVILLE 11026084 | 192221102 | GARBERVILLE 1102 | 24635.3535 | 15.311 | 120 | 1.8189 | 0.015158 | 1777 | 19015.0127 | 479.6552 | 0.019371 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8670 | COTATI 1102462 | 42271102 | COTATI 1102 | 4550.7014 | 2.8283 | 40 | 0.6053 | 0.015132 | 1778 | 19017.841 | 479.0499 | 0.019346 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5839 | SOLEDAD 21027048 | 182052102 | SOLEDAD 2102 | 18663.2877 | 11.5993 | 173 | 2.607 | 0.015069 | 1779 | 19029.4403 | 476.4429 | 0.019241 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5090 | BRIDGEVILLE 1102CB | 192461102 | BRIDGEVILLE 1102 | 4723.1827 | 2.9355 | 52 | 0.78316 | 0.015061 | 1780 | 19032.3758 | 475.6597 | 0.01921 | 475.6597 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10131 | CMC 1101CB | 183111101 | CMC 1101 | 3286.0633 | 2.0423 | 16 | 0.23983 | 0.014989 | 1781 | 19034.4181 | 475.4199 | 0.0192 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4953 | FRENCH GULCH 11021462 | 103381102 | FRENCH GULCH 1102 | 16116.0676 | 10.0162 | 51 | 0.76245 | 0.01495 | 1782 | 19044.4343 | 474.6575 | 0.019169 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8365 | GRASS VALLEY 110358498 | 152031103 | GRASS VALLEY 1103 | 1920.6561 | 1.1937 | 34 | 0.50797 | 0.01494 | 1783 | 19045.628 | 474.1495 | 0.019149 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4523 | TIDEWATER 210665866 | 14652106 | TIDEWATER 2106 | 5501.1432 | 3.419 | 65 | 0.9697 | 0.014918 | 1784 | 19049.047 | 473.1798 | 0.019109 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7430 | FOOTHILL 1101549904 | 182951101 | FOOTHILL 1101 | 250.4434 | 0.15565 | 54 | 0.80473 | 0.014902 | 1785 | 19049.2026 | 472.3751 | 0.019077 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10743 | ANDERSON 1101909424 | 103261101 | ANDERSON 1101 | 642.3156 | 0.3992 | 8 | 0.1191 | 0.014888 | 1786 | 19049.6018 | 472.256 | 0.019072 | 472.256 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6685 | OCEANO 1102749231 | 182601102 | OCEANO 1102 | 8940.1081 | 5.5563 | 141 | 2.0934 | 0.014847 | 1787 | 19055.1582 | 470.1626 | 0.018988 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2541 | BRUNSWICK 110651486 | 152481106 | BRUNSWICK 1106 | 91205.7549 | 56.6847 | 656 | 9.7068 | 0.014797 | 1788 | 19111.8429 | 460.4558 | 0.018596 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7750 | BRUNSWICK 110765574 | 152481107 | BRUNSWICK 1107 | 939.5268 | 0.58392 | 23 | 0.34024 | 0.014793 | 1789 | 19112.4268 | 460.1156 | 0.018582 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5279 | MC ARTHUR 110137344 | 103491101 | MC ARTHUR 1101 | 181.3406 | 0.1127 | 75 | 1.1076 | 0.014768 | 1790 | 19112.5395 | 459.008 | 0.018537 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7132 | ANTLER 11011612 | 103271101 | ANTLER 1101 | 14766.2971 | 9.1773 | 86 | 1.2683 | 0.014748 | 1791 | 19121.7168 | 457.7396 | 0.018486 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3386 | NEWBURG 1132665674 | 192151132 | NEWBURG 1132 | 698.7983 | 0.43431 | 20 | 0.29443 | 0.014722 | 1792 | 19122.1511 | 457.4452 | 0.018474 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7872 | PIT NO 1 110170952 | 103721101 | PIT NO 1 1101 | 2724.6488 | 1.6934 | 29 | 0.42606 | 0.014692 | 1793 | 19123.8445 | 457.0192 | 0.018457 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5114 | DUNBAR 110147964 | 43071101 | DUNBAR 1101 | 10475.6408 | 6.5107 | 68 | 0.99704 | 0.014662 | 1794 | 19130.3552 | 456.0221 | 0.018416 | 456.0221 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7691 | POINT ARENA 110198224 | 43381101 | POINT ARENA 1101 | 3847.8762 | 2.3915 | 23 | 0.33704 | 0.014654 | 1795 | 19132.7467 | 455.6851 | 0.018403 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2530 | BRUNSWICK 111061602 | 152481110 | BRUNSWICK 1110 | 15796.3436 | 9.8175 | 137 | 2.0068 | 0.014648 | 1796 | 19142.5641 | 453.6783 | 0.018322 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7167 | FRENCH GULCH 11012905 | 103381101 | FRENCH GULCH 1101 | 15594.3492 | 9.692 | 83 | 1.2158 | 0.014648 | 1797 | 19152.2561 | 452.4625 | 0.018273 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4457 | HIGGINS 11041006 | 152691104 | HIGGINS 1104 | 17529.4826 | 10.8946 | 266 | 3.8939 | 0.014639 | 1798 | 19163.1507 | 448.5686 | 0.018115 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7710 | CARLOTTA 11214045 | 192291121 | CARLOTTA 1121 | 576.108 | 0.35805 | 18 | 0.26312 | 0.014618 | 1799 | 19163.5088 | 448.3055 | 0.018105 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9405 | SILVERADO 2105861266 | 43432105 | SILVERADO 2105 | 2503.894 | 1.5562 | 31 | 0.45311 | 0.014616 | 1800 | 19165.065 | 447.8524 | 0.018087 | 447.8524 | #N/A | #N/A | #N/A | #N/A | #VALUE!
463 | WEIMAR 11012084 | 152491101 | WEIMAR 1101 | 29723.3403 | 18.4732 | 219 | 3.1928 | 0.014579 | 1801 | 19183.5382 | 444.6596 | 0.017958 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3551 | WILLOW CREEK 11014904 | 192171101 | WILLOW CREEK 1101 | 29337.0631 | 18.2331 | 121 | 1.7608 | 0.014552 | 1802 | 19201.7713 | 442.8987 | 0.017886 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6996 | KONOCTI 1102714370 | 43311102 | KONOCTI 1102 | 3423.0115 | 2.1274 | 28 | 0.40694 | 0.014533 | 1803 | 19203.8987 | 442.4918 | 0.01787 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1102 | MC KEE 1107XR010 | 83531107 | MC KEE 1107 | 4483.0278 | 2.7862 | 160 | 2.3052 | 0.014407 | 1804 | 19206.6849 | 440.1866 | 0.017777 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2551 | SOLEDAD 2102823854 | 182052102 | SOLEDAD 2102 | 3307.4207 | 2.0556 | 33 | 0.47422 | 0.01437 | 1805 | 19208.7405 | 439.7124 | 0.017758 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2101 | SAN BENITO 210488772 | 182742104 | SAN BENITO 2104 | 39135.7756 | 24.323 | 474 | 6.8057 | 0.014358 | 1806 | 19233.0635 | 432.9067 | 0.017483 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7410 | RIO DELL 11028852 | 192251102 | RIO DELL 1102 | 7473.9899 | 4.6451 | 46 | 0.66027 | 0.014354 | 1807 | 19237.7086 | 432.2464 | 0.017456 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5404 | PIT NO 3 21011386 | 103732101 | PIT NO 3 2101 | 11052.9537 | 6.8695 | 47 | 0.67181 | 0.014294 | 1808 | 19244.5781 | 431.5746 | 0.017429 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4186 | MARIPOSA 210110170 | 254452101 | MARIPOSA 2101 | 26253.3221 | 16.3165 | 149 | 2.1297 | 0.014293 | 1809 | 19260.8946 | 429.4449 | 0.017343 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7884 | SONOMA 11045661 | 42721104 | SONOMA 1104 | 4658.2663 | 2.8951 | 66 | 0.94309 | 0.014289 | 1810 | 19263.7898 | 428.5018 | 0.017305 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
967 | DUNBAR 1102903030 | 43071102 | DUNBAR 1102 | 2341.4408 | 1.4552 | 17 | 0.24273 | 0.014278 | 1811 | 19265.245 | 428.2591 | 0.017295 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3516 | NARROWS 21022718 | 153132102 | NARROWS 2102 | 495.6422 | 0.30804 | 114 | 1.6275 | 0.014276 | 1812 | 19265.553 | 426.6316 | 0.01723 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5103 | SAN LUIS OBISPO 1107V18 | 182631107 | SAN LUIS OBISPO 1107 | 4344.0922 | 2.6999 | 41 | 0.5828 | 0.014215 | 1813 | 19268.2529 | 426.0488 | 0.017206 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
177 | KING CITY 11037038 | 182031103 | KING CITY 1103 | 29491.4615 | 18.3291 | 186 | 2.6339 | 0.014161 | 1814 | 19286.5819 | 423.4149 | 0.0171 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4472 | WEST POINT 110277204 | 163201102 | WEST POINT 1102 | 11918.386 | 7.4073 | 68 | 0.95841 | 0.014094 | 1815 | 19293.9893 | 422.4565 | 0.017061 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8017 | PIT NO 3 2101CB | 103732101 | PIT NO 3 2101 | 7292.0294 | 4.532 | 7 | 0.098493 | 0.01407 | 1816 | 19298.5213 | 422.358 | 0.017057 | 422.358 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4764 | ALLEGHANY 1101CB | 152101101 | ALLEGHANY 1101 | 7034.6563 | 4.3721 | 40 | 0.5623 | 0.014057 | 1817 | 19302.8934 | 421.7957 | 0.017034 | 421.7957 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2091 | STELLING 111060094 | 83481110 | STELLING 1110 | 15867.8413 | 9.8619 | 95 | 1.3339 | 0.014041 | 1818 | 19312.7553 | 420.4618 | 0.01698 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2701 | PEORIA 170567898 | 163781705 | PEORIA 1705 | 6917.4777 | 4.2992 | 70 | 0.98259 | 0.014037 | 1819 | 19317.0545 | 419.4792 | 0.016941 | 419.4792 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8037 | CAYUCOS 1102613456 | 182551102 | CAYUCOS 1102 | 21637.0644 | 13.4475 | 145 | 2.0341 | 0.014028 | 1820 | 19330.5021 | 417.4452 | 0.016859 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4958 | WILLOW CREEK 11035012 | 192171103 | WILLOW CREEK 1103 | 17904.0624 | 11.1274 | 131 | 1.8356 | 0.014012 | 1821 | 19341.6295 | 415.6095 | 0.016784 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1586 | MARTELL 110111244 | 163011101 | MARTELL 1101 | 33294.1457 | 20.6924 | 202 | 2.826 | 0.01399 | 1822 | 19362.3219 | 412.7835 | 0.01667 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8222 | DUNBAR 1102528 | 43071102 | DUNBAR 1102 | 5521.142 | 3.4314 | 50 | 0.69934 | 0.013987 | 1823 | 19365.7534 | 412.0842 | 0.016642 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6649 | SAN LUIS OBISPO 1108337126 | 182631108 | SAN LUIS OBISPO 1108 | 1128.521 | 0.70138 | 28 | 0.39101 | 0.013964 | 1824 | 19366.4547 | 411.6932 | 0.016626 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
716 | LAKEVILLE 1102280 | 43371102 | LAKEVILLE 1102 | 1106.406 | 0.68764 | 52 | 0.72376 | 0.013918 | 1825 | 19367.1424 | 410.9694 | 0.016597 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1162 | DUNBAR 1101302 | 43071101 | DUNBAR 1101 | 14104.3324 | 8.7659 | 123 | 1.7022 | 0.013839 | 1826 | 19375.9083 | 409.2672 | 0.016528 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5443 | DUNBAR 1103534 | 43071103 | DUNBAR 1103 | 25519.0889 | 15.8602 | 162 | 2.2178 | 0.01369 | 1827 | 19391.7685 | 407.0495 | 0.016439 | 407.0495 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3834 | STILLWATER 11011320 | 103561101 | STILLWATER 1101 | 31878.2376 | 19.8125 | 179 | 2.4499 | 0.013687 | 1828 | 19411.5809 | 404.5996 | 0.01634 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3066 | SHADY GLEN 1102CB | 152431102 | SHADY GLEN 1102 | 34051.8134 | 21.1633 | 240 | 3.2616 | 0.01359 | 1829 | 19432.7443 | 401.338 | 0.016208 | 401.338 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8639 | GREEN VALLEY 2101135762 | 83192101 | GREEN VALLEY 2101 | 1189.5286 | 0.7393 | 28 | 0.3791 | 0.013539 | 1830 | 19433.4836 | 400.9589 | 0.016193 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1363 | BURNEY 11011322 | 103311101 | BURNEY 1101 | 25851.0688 | 16.0665 | 81 | 1.0943 | 0.01351 | 1831 | 19449.5501 | 399.8645 | 0.016149 | 399.8645 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5427 | PENRYN 1103CB | 152561103 | PENRYN 1103 | 3866.6599 | 2.4031 | 37 | 0.49946 | 0.013499 | 1832 | 19451.9533 | 399.3651 | 0.016128 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8202 | DUNBAR 1102861496 | 43071102 | DUNBAR 1102 | 7188.816 | 4.4679 | 51 | 0.68805 | 0.013491 | 1833 | 19456.4211 | 398.677 | 0.016101 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3776 | ALTO 1125510 | 42031125 | ALTO 1125 | 11861.6385 | 7.3721 | 77 | 1.0369 | 0.013466 | 1834 | 19463.7932 | 397.6402 | 0.016059 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2524 | PHILO 1102920 | 42601102 | PHILO 1102 | 28596.0082 | 17.7725 | 258 | 3.4601 | 0.013411 | 1835 | 19481.5657 | 394.1801 | 0.015919 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8287 | LUCERNE 11034624 | 43351103 | LUCERNE 1103 | 50.6724 | 0.031493 | 42 | 0.55825 | 0.013292 | 1836 | 19481.5972 | 393.6218 | 0.015896 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3582 | SAN RAFAEL 1108516 | 42011108 | SAN RAFAEL 1108 | 17602.5759 | 10.9401 | 135 | 1.7929 | 0.013281 | 1837 | 19492.5373 | 391.8289 | 0.015824 | 391.8289 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6863 | GREEN VALLEY 2101942143 | 83192101 | GREEN VALLEY 2101 | 8138.4591 | 5.0581 | 74 | 0.97798 | 0.013216 | 1838 | 19497.5954 | 390.8509 | 0.015785 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7880 | POINT ARENA 110183354 | 43381101 | POINT ARENA 1101 | 8260.8147 | 5.1341 | 36 | 0.47457 | 0.013182 | 1839 | 19502.7295 | 390.3763 | 0.015765 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2799 | TASSAJARA 211238868 | 14662112 | TASSAJARA 2112 | 3119.1276 | 1.9386 | 61 | 0.80215 | 0.01315 | 1840 | 19504.6681 | 389.5742 | 0.015733 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10912 | TOCALOMA 0241CB | 43150241 | TOCALOMA 0241 | 26.5151 | 0.016479 | 1 | 0.013124 | 0.013124 | 1841 | 19504.6845 | 389.5611 | 0.015732 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6124 | ANDERSON 1101CB | 103261101 | ANDERSON 1101 | 1904.2009 | 1.1835 | 85 | 1.115 | 0.013117 | 1842 | 19505.868 | 388.4461 | 0.015687 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6165 | BRUNSWICK 1105CB | 152481105 | BRUNSWICK 1105 | 1870.8826 | 1.1628 | 21 | 0.27501 | 0.013096 | 1843 | 19507.0308 | 388.1711 | 0.015676 | 388.1711 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9119 | SONOMA 1106296492 | 42721106 | SONOMA 1106 | 1270.5979 | 0.78968 | 29 | 0.37968 | 0.013092 | 1844 | 19507.8205 | 387.7914 | 0.015661 | 387.7914 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3902 | SOLEDAD 2102858388 | 182052102 | SOLEDAD 2102 | 7717.2675 | 4.7963 | 72 | 0.93942 | 0.013047 | 1845 | 19512.6168 | 386.852 | 0.015623 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6187 | JESSUP 11013383 | 103441101 | JESSUP 1101 | 2267.9133 | 1.4095 | 24 | 0.31066 | 0.012944 | 1846 | 19514.0263 | 386.5413 | 0.01561 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4407 | APPLE HILL 210297982 | 153662102 | APPLE HILL 2102 | 15545.7354 | 9.6617 | 104 | 1.3407 | 0.012892 | 1847 | 19523.688 | 385.2006 | 0.015556 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7041 | JAMESON 1105371694 | 63801105 | JAMESON 1105 | 365.7311 | 0.2273 | 40 | 0.51277 | 0.012819 | 1848 | 19523.9153 | 384.6878 | 0.015536 | 384.6878 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3447 | WYANDOTTE 11031974 | 102911103 | WYANDOTTE 1103 | 36068.6353 | 22.4168 | 259 | 3.3188 | 0.012814 | 1849 | 19546.3321 | 381.369 | 0.015402 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7950 | SONOMA 11033052 | 42721103 | SONOMA 1103 | 20257.093 | 12.5899 | 163 | 2.0855 | 0.012795 | 1850 | 19558.922 | 379.2835 | 0.015317 | 379.2835 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5166 | LOS GATOS 1106LB48 | 82021106 | LOS GATOS 1106 | 23668.374 | 14.71 | 142 | 1.8115 | 0.012757 | 1851 | 19573.632 | 377.4719 | 0.015244 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3055 | LAS POSITAS 2108MR190 | 14402108 | LAS POSITAS 2108 | 1336.9264 | 0.83091 | 130 | 1.6567 | 0.012744 | 1852 | 19574.4629 | 375.8152 | 0.015177 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8820 | HICKS 2101CB | 83432101 | HICKS 2101 | 8660.4867 | 5.3825 | 20 | 0.25483 | 0.012742 | 1853 | 19579.8454 | 375.5604 | 0.015167 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
987 | OAKHURST 110310140 | 254421103 | OAKHURST 1103 | 26724.0842 | 16.6091 | 188 | 2.3869 | 0.012696 | 1854 | 19596.4545 | 373.1735 | 0.015071 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1124 | COARSEGOLD 210210040 | 254432102 | COARSEGOLD 2102 | 28379.0201 | 17.6377 | 213 | 2.6967 | 0.01266 | 1855 | 19614.0922 | 370.4768 | 0.014962 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6998 | PUEBLO 1104640 | 43291104 | PUEBLO 1104 | 1636.7685 | 1.0173 | 43 | 0.54429 | 0.012658 | 1856 | 19615.1095 | 369.9326 | 0.01494 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2113 | HALSEY 11025739 | 152241102 | HALSEY 1102 | 10731.8696 | 6.6699 | 74 | 0.93104 | 0.012582 | 1857 | 19621.7794 | 369.0015 | 0.014902 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9463 | ATASCADERO 1103A06 | 182541103 | ATASCADERO 1103 | 441.6127 | 0.27446 | 27 | 0.33927 | 0.012566 | 1858 | 19622.0538 | 368.6622 | 0.014888 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
673 | FLINT 110140666 | 152531101 | FLINT 1101 | 575.1734 | 0.35747 | 18 | 0.22615 | 0.012564 | 1859 | 19622.4113 | 368.4361 | 0.014879 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6086 | SONOMA 1102113082 | 42721102 | SONOMA 1102 | 9857.3648 | 6.1264 | 75 | 0.94012 | 0.012535 | 1860 | 19628.5377 | 367.496 | 0.014841 | 367.496 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4138 | ORO FINO 11022096 | 103031102 | ORO FINO 1102 | 22772.919 | 14.1535 | 129 | 1.6166 | 0.012531 | 1861 | 19642.6912 | 365.8794 | 0.014776 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8669 | HORSESHOE 1101663244 | 152571101 | HORSESHOE 1101 | 464.3934 | 0.28862 | 6 | 0.075153 | 0.012526 | 1862 | 19642.9798 | 365.8043 | 0.014773 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1101 | HOOPA 110137202 | 192401101 | HOOPA 1101 | 40065.4375 | 24.9008 | 190 | 2.3773 | 0.012512 | 1863 | 19667.8806 | 363.427 | 0.014677 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1135 | LOS GATOS 1106LB44 | 82021106 | LOS GATOS 1106 | 31139.8726 | 19.3536 | 213 | 2.6623 | 0.012499 | 1864 | 19687.2342 | 360.7647 | 0.01457 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5450 | FORESTHILL 11011802 | 152181101 | FORESTHILL 1101 | 35771.0229 | 22.2318 | 259 | 3.2365 | 0.012496 | 1865 | 19709.466 | 357.5283 | 0.014439 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5898 | WISE 1102465074 | 152271102 | WISE 1102 | 7662.1855 | 4.7621 | 57 | 0.7122 | 0.012495 | 1866 | 19714.2281 | 356.8161 | 0.01441 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7150 | FRUITLAND 1141200856 | 192311141 | FRUITLAND 1141 | 4144.4334 | 2.5758 | 31 | 0.38602 | 0.012452 | 1867 | 19716.8039 | 356.43 | 0.014394 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6814 | SAN ARDO 11017632 | 182191101 | SAN ARDO 1101 | 3566.1023 | 2.2163 | 35 | 0.43499 | 0.012428 | 1868 | 19719.0202 | 355.995 | 0.014377 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4514 | SOLEDAD 2101526864 | 182052101 | SOLEDAD 2101 | 5008.6837 | 3.1129 | 18 | 0.22335 | 0.012408 | 1869 | 19722.1331 | 355.7717 | 0.014368 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10395 | CLARKSVILLE 2109649874 | 153612109 | CLARKSVILLE 2109 | 608.4651 | 0.37816 | 5 | 0.061618 | 0.012324 | 1870 | 19722.5113 | 355.7101 | 0.014365 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
368 | POINT MORETTI 11015078 | 82931101 | POINT MORETTI 1101 | 23873.1972 | 14.8373 | 154 | 1.8962 | 0.012313 | 1871 | 19737.3486 | 353.8139 | 0.014289 | 353.8139 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4025 | CARLOTTA 1121CB | 192291121 | CARLOTTA 1121 | 4224.1485 | 2.6253 | 255 | 3.1369 | 0.012302 | 1872 | 19739.9739 | 350.677 | 0.014162 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9319 | GONZALES 11013094 | 182131101 | GONZALES 1101 | 6578.8406 | 4.0888 | 63 | 0.77477 | 0.012298 | 1873 | 19744.0627 | 349.9022 | 0.014131 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5655 | CHALLENGE 1101CB | 103201101 | CHALLENGE 1101 | 26652.3351 | 16.5645 | 128 | 1.5636 | 0.012215 | 1874 | 19760.6272 | 348.3386 | 0.014068 | 348.3386 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9730 | MC KEE 1108976553 | 83531108 | MC KEE 1108 | 1744.6035 | 1.0843 | 20 | 0.24394 | 0.012197 | 1875 | 19761.7115 | 348.0947 | 0.014058 | 348.0947 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8214 | BRUNSWICK 1106CB | 152481106 | BRUNSWICK 1106 | 14066.7084 | 8.7425 | 88 | 1.0703 | 0.012162 | 1876 | 19770.454 | 347.0244 | 0.014015 | 347.0244 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3779 | NOTRE DAME 1103317782 | 102041103 | NOTRE DAME 1103 | 874.1929 | 0.54331 | 53 | 0.64349 | 0.012141 | 1877 | 19770.9973 | 346.3809 | 0.013989 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1366 | HALF MOON BAY 11036014 | 24101103 | HALF MOON BAY 1103 | 9962.9663 | 6.192 | 106 | 1.2867 | 0.012138 | 1878 | 19777.1894 | 345.0943 | 0.013937 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7316 | HOLLISTER 2102676164 | 182492102 | HOLLISTER 2102 | 487.5008 | 0.30298 | 26 | 0.3136 | 0.012062 | 1879 | 19777.4923 | 344.7807 | 0.013924 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2140 | BRUNSWICK 1102CB | 152481102 | BRUNSWICK 1102 | 10098.7974 | 6.2764 | 73 | 0.87889 | 0.01204 | 1880 | 19783.7688 | 343.9018 | 0.013888 | 343.9018 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9978 | FROGTOWN 1702411508 | 163451702 | FROGTOWN 1702 | 726.7977 | 0.45171 | 6 | 0.072157 | 0.012026 | 1881 | 19784.2205 | 343.8296 | 0.013886 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5364 | FULTON 1104466 | 42561104 | FULTON 1104 | 622.9644 | 0.38717 | 21 | 0.25243 | 0.01202 | 1882 | 19784.6077 | 343.5772 | 0.013875 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
916 | WYANDOTTE 1105329930 | 102911105 | WYANDOTTE 1105 | 10526.1812 | 6.5421 | 137 | 1.6456 | 0.012012 | 1883 | 19791.1497 | 341.9315 | 0.013809 | 341.9315 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4781 | SONOMA 1105539450 | 42721105 | SONOMA 1105 | 2403.5482 | 1.4938 | 28 | 0.33537 | 0.011978 | 1884 | 19792.6436 | 341.5962 | 0.013795 | 341.5962 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5493 | SHADY GLEN 11012768 | 152431101 | SHADY GLEN 1101 | 12269.0577 | 7.6253 | 88 | 1.0528 | 0.011963 | 1885 | 19800.2688 | 340.5434 | 0.013753 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8268 | LLAGAS 2101587857 | 83182101 | LLAGAS 2101 | 171.8621 | 0.10681 | 28 | 0.33442 | 0.011944 | 1886 | 19800.3756 | 340.209 | 0.013739 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1441 | MIWUK 170111800 | 163661701 | MIWUK 1701 | 15325.4468 | 9.5248 | 116 | 1.3764 | 0.011866 | 1887 | 19809.9005 | 338.8326 | 0.013684 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2749 | ELK 1101900 | 42981101 | ELK 1101 | 14125.5477 | 8.7791 | 185 | 2.1939 | 0.011859 | 1888 | 19818.6795 | 336.6387 | 0.013595 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1288 | CALAVERAS CEMENT 11012646 | 162211101 | CALAVERAS CEMENT 1101 | 28413.9838 | 17.6594 | 149 | 1.7642 | 0.01184 | 1889 | 19836.339 | 334.8745 | 0.013524 | 334.8745 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8429 | FOOTHILL 1101386844 | 182951101 | FOOTHILL 1101 | 615.6019 | 0.3826 | 19 | 0.22478 | 0.01183 | 1890 | 19836.7216 | 334.6497 | 0.013515 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6057 | LLAGAS 2101XR264 | 83182101 | LLAGAS 2101 | 0 | 0 | 258 | 3.0254 | 0.011726 | 1891 | 19836.7216 | 331.6243 | 0.013393 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5358 | UKIAH 1113968652 | 42771113 | UKIAH 1113 | 1606.1834 | 0.99825 | 25 | 0.2921 | 0.011684 | 1892 | 19837.7198 | 331.3322 | 0.013381 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9622 | SAN RAFAEL 110863598 | 42011108 | SAN RAFAEL 1108 | 3076.8023 | 1.9122 | 24 | 0.28035 | 0.011681 | 1893 | 19839.632 | 331.0519 | 0.01337 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6523 | ALTO 1124870444 | 42031124 | ALTO 1124 | 4746.504 | 2.95 | 35 | 0.40831 | 0.011666 | 1894 | 19842.582 | 330.6436 | 0.013353 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4747 | SANTA ROSA A 1104716 | 42151104 | SANTA ROSA A 1104 | 14319.9438 | 8.8999 | 109 | 1.2698 | 0.01165 | 1895 | 19851.4819 | 329.3738 | 0.013302 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9188 | HALF MOON BAY 1102350336 | 24101102 | HALF MOON BAY 1102 | 1936.9418 | 1.2038 | 13 | 0.15117 | 0.011629 | 1896 | 19852.6857 | 329.2226 | 0.013296 | 329.2226 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10068 | SAN LUIS OBISPO 1108809986 | 182631108 | SAN LUIS OBISPO 1108 | 1661.0044 | 1.0323 | 18 | 0.20927 | 0.011626 | 1897 | 19853.7181 | 329.0133 | 0.013287 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3493 | MARTELL 110198374 | 163011101 | MARTELL 1101 | 1330.8093 | 0.8271 | 46 | 0.53436 | 0.011616 | 1898 | 19854.5452 | 328.479 | 0.013266 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3767 | HOLLISTER 210491424 | 182492104 | HOLLISTER 2104 | 303.1658 | 0.18842 | 95 | 1.0973 | 0.01155 | 1899 | 19854.7336 | 327.3817 | 0.013221 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7603 | CLOVERDALE 1102262 | 42821102 | CLOVERDALE 1102 | 2067.1657 | 1.2848 | 61 | 0.70445 | 0.011548 | 1900 | 19856.0183 | 326.6772 | 0.013193 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
712 | SILVERADO 2105247660 | 43432105 | SILVERADO 2105 | 3858.4886 | 2.3981 | 35 | 0.40392 | 0.011541 | 1901 | 19858.4164 | 326.2733 | 0.013177 | 326.2733 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4631 | BRUNSWICK 11052210 | 152481105 | BRUNSWICK 1105 | 36938.5346 | 22.9574 | 280 | 3.2229 | 0.01151 | 1902 | 19881.3738 | 323.0504 | 0.013046 | 323.0504 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1236 | OAKHURST 11035480 | 254421103 | OAKHURST 1103 | 27352.0687 | 16.9994 | 180 | 2.0709 | 0.011505 | 1903 | 19898.3733 | 320.9796 | 0.012963 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2425 | PIT NO 3 21011360 | 103732101 | PIT NO 3 2101 | 36106.6297 | 22.4404 | 92 | 1.0584 | 0.011504 | 1904 | 19920.8137 | 319.9212 | 0.01292 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9598 | MILPITAS 1109XR044 | 82831109 | MILPITAS 1109 | 677.8018 | 0.42126 | 18 | 0.20585 | 0.011436 | 1905 | 19921.2349 | 319.7153 | 0.012912 | 319.7153 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3999 | CALAVERAS CEMENT 11011419 | 162211101 | CALAVERAS CEMENT 1101 | 24160.9517 | 15.0161 | 130 | 1.4856 | 0.011428 | 1906 | 19936.2511 | 318.2297 | 0.012852 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3421 | HIGGINS 1104324510 | 152691104 | HIGGINS 1104 | 20073.6016 | 12.4758 | 154 | 1.7562 | 0.011404 | 1907 | 19948.7269 | 316.4735 | 0.012781 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6037 | COARSEGOLD 210210050 | 254432102 | COARSEGOLD 2102 | 11290.6239 | 7.0172 | 81 | 0.92095 | 0.01137 | 1908 | 19955.7441 | 315.5525 | 0.012744 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
942 | WEST POINT 110293116 | 163201102 | WEST POINT 1102 | 68103.7314 | 42.3267 | 453 | 5.1406 | 0.011348 | 1909 | 19998.0708 | 310.4119 | 0.012536 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1810 | CABRILLO 1104CB | 183101104 | CABRILLO 1104 | 6641.9361 | 4.128 | 121 | 1.3695 | 0.011318 | 1910 | 20002.1988 | 309.0424 | 0.012481 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1626 | MOLINO 110251788 | 42571102 | MOLINO 1102 | 8188.5748 | 5.0892 | 153 | 1.7234 | 0.011264 | 1911 | 20007.288 | 307.319 | 0.012411 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6259 | RISING RIVER 11019032 | 103551101 | RISING RIVER 1101 | 36827.5633 | 22.8885 | 175 | 1.9611 | 0.011207 | 1912 | 20030.1765 | 305.3578 | 0.012332 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1825 | FORT BRAGG A 11014622 | 42761101 | FORT BRAGG A 1101 | 21650.6648 | 13.456 | 109 | 1.2138 | 0.011136 | 1913 | 20043.6325 | 304.144 | 0.012283 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5920 | CASTRO VALLEY 1110MR243 | 14091110 | CASTRO VALLEY 1110 | 8929.805 | 5.5499 | 72 | 0.79807 | 0.011084 | 1914 | 20049.1824 | 303.346 | 0.012251 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3864 | PLACER 1103429574 | 152461103 | PLACER 1103 | 8004.0474 | 4.9745 | 114 | 1.2634 | 0.011083 | 1915 | 20054.1569 | 302.0826 | 0.0122 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4013 | LAURELES 1111CB | 182371111 | LAURELES 1111 | 11515.5312 | 7.1569 | 82 | 0.90815 | 0.011075 | 1916 | 20061.3139 | 301.1744 | 0.012163 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9810 | MENLO 11028896 | 24131102 | MENLO 1102 | 1537.9857 | 0.95586 | 14 | 0.15491 | 0.011065 | 1917 | 20062.2698 | 301.0195 | 0.012157 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8395 | CARLOTTA 112142896 | 192291121 | CARLOTTA 1121 | 3686.5968 | 2.2912 | 71 | 0.78303 | 0.011029 | 1918 | 20064.561 | 300.2365 | 0.012125 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5390 | SOLEDAD 2102304826 | 182052102 | SOLEDAD 2102 | 8398.3076 | 5.2196 | 61 | 0.6707 | 0.010995 | 1919 | 20069.7806 | 299.5658 | 0.012098 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4943 | PINE GROVE 1102CB | 163751102 | PINE GROVE 1102 | 17461.9206 | 10.8527 | 136 | 1.4895 | 0.010952 | 1920 | 20080.6332 | 298.0762 | 0.012038 | 298.0762 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2277 | ORO FINO 11022560 | 103031102 | ORO FINO 1102 | 26913.6157 | 16.7269 | 179 | 1.9534 | 0.010913 | 1921 | 20097.3601 | 296.1228 | 0.011959 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8219 | CAMPHORA 1101613562 | 182071101 | CAMPHORA 1101 | 5945.3079 | 3.695 | 29 | 0.31622 | 0.010904 | 1922 | 20101.0552 | 295.8066 | 0.011946 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8001 | MOLINO 1102189602 | 42571102 | MOLINO 1102 | 1011.2208 | 0.62848 | 9 | 0.098117 | 0.010902 | 1923 | 20101.6837 | 295.7085 | 0.011942 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8797 | CAMP EVERS 210533542 | 83622105 | CAMP EVERS 2105 | 4316.4835 | 2.6827 | 39 | 0.42515 | 0.010901 | 1924 | 20104.3664 | 295.2833 | 0.011925 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6026 | ROSSMOOR 110837848 | 14161108 | ROSSMOOR 1108 | 9580.5994 | 5.9544 | 60 | 0.65406 | 0.010901 | 1925 | 20110.3208 | 294.6293 | 0.011899 | 294.6293 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9862 | MONTE RIO 11113891 | 42811111 | MONTE RIO 1111 | 5583.0951 | 3.4699 | 23 | 0.2504 | 0.010887 | 1926 | 20113.7907 | 294.3789 | 0.011889 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9761 | HALF MOON BAY 1103341542 | 24101103 | HALF MOON BAY 1103 | 9768.7602 | 6.0713 | 47 | 0.5116 | 0.010885 | 1927 | 20119.862 | 293.8673 | 0.011868 | 293.8673 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6971 | WILLOW CREEK 11037514 | 192171103 | WILLOW CREEK 1103 | 14595.7178 | 9.0713 | 118 | 1.2841 | 0.010882 | 1928 | 20128.9333 | 292.5832 | 0.011816 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8324 | MONTE RIO 1112999 | 42811112 | MONTE RIO 1112 | 1412.3755 | 0.8778 | 7 | 0.075506 | 0.010787 | 1929 | 20129.8111 | 292.5077 | 0.011813 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3097 | ATASCADERO 1103492068 | 182541103 | ATASCADERO 1103 | 11954.6281 | 7.4298 | 75 | 0.80789 | 0.010772 | 1930 | 20137.2409 | 291.6998 | 0.01178 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1425 | CLAY 110184572 | 163341101 | CLAY 1101 | 844.7995 | 0.52505 | 27 | 0.29075 | 0.010769 | 1931 | 20137.766 | 291.409 | 0.011769 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8269 | COTATI 1105893 | 42271105 | COTATI 1105 | 312.2303 | 0.19405 | 91 | 0.9759 | 0.010724 | 1932 | 20137.96 | 290.4331 | 0.011729 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1839 | VOLTA 11021650 | 102541102 | VOLTA 1102 | 34931.9743 | 21.7104 | 154 | 1.6479 | 0.010701 | 1933 | 20159.6704 | 288.7852 | 0.011663 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5835 | APPLE HILL 110497086 | 153661104 | APPLE HILL 1104 | 41345.0987 | 25.6961 | 301 | 3.2174 | 0.010689 | 1934 | 20185.3665 | 285.5678 | 0.011533 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7014 | ALTO 1122591122 | 42031122 | ALTO 1122 | 748.6821 | 0.46531 | 7 | 0.074542 | 0.010649 | 1935 | 20185.8319 | 285.4933 | 0.01153 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1545 | MARTELL 110191216 | 163011101 | MARTELL 1101 | 65291.6361 | 40.579 | 380 | 4.0231 | 0.010587 | 1936 | 20226.4109 | 281.4701 | 0.011367 | 281.4701 | #N/A | #N/A | #N/A | #N/A | #VALUE!
812 | DUNBAR 1102246 | 43071102 | DUNBAR 1102 | 21497.7557 | 13.3609 | 148 | 1.563 | 0.010561 | 1937 | 20239.7718 | 279.9071 | 0.011304 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6481 | DEL MONTE 21043088 | 182222104 | DEL MONTE 2104 | 24808.0862 | 15.4183 | 175 | 1.8381 | 0.010503 | 1938 | 20255.1901 | 278.069 | 0.01123 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
336 | CAMBRIA 1102CB | 182771102 | CAMBRIA 1102 | 25753.259 | 16.0058 | 153 | 1.6015 | 0.010468 | 1939 | 20271.1959 | 276.4675 | 0.011165 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3334 | VOLTA 110297816 | 102541102 | VOLTA 1102 | 8457.2763 | 5.2562 | 50 | 0.52009 | 0.010402 | 1940 | 20276.4521 | 275.9474 | 0.011144 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1241 | CALAVERAS CEMENT 110147968 | 162211101 | CALAVERAS CEMENT 1101 | 65100.4862 | 40.4602 | 306 | 3.1777 | 0.010385 | 1941 | 20316.9123 | 272.7697 | 0.011016 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8572 | LOS GATOS 110760024 | 82021107 | LOS GATOS 1107 | 6398.0407 | 3.9764 | 27 | 0.28029 | 0.010381 | 1942 | 20320.8887 | 272.4894 | 0.011004 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8425 | PINE GROVE 110194936 | 163751101 | PINE GROVE 1101 | 14750.2856 | 9.1674 | 82 | 0.84992 | 0.010365 | 1943 | 20330.0561 | 271.6395 | 0.01097 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10220 | ALLEGHANY 1101808 | 152101101 | ALLEGHANY 1101 | 9941.3745 | 6.1786 | 23 | 0.23829 | 0.010361 | 1944 | 20336.2347 | 271.4012 | 0.010961 | 271.4012 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7876 | PUEBLO 2103706399 | 43292103 | PUEBLO 2103 | 537.9717 | 0.33435 | 16 | 0.1654 | 0.010338 | 1945 | 20336.5691 | 271.2358 | 0.010954 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1021 | EL DORADO PH 210119752 | 152762101 | EL DORADO PH 2101 | 58764.7318 | 36.5225 | 436 | 4.4909 | 0.0103 | 1946 | 20373.0916 | 266.7448 | 0.010773 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5417 | SILVERADO 2105131568 | 43432105 | SILVERADO 2105 | 6658.8017 | 4.1385 | 57 | 0.58604 | 0.010281 | 1947 | 20377.2301 | 266.1588 | 0.010749 | 266.1588 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3018 | LUCERNE 110638632 | 43351106 | LUCERNE 1106 | 7535.3678 | 4.6833 | 58 | 0.59423 | 0.010245 | 1948 | 20381.9133 | 265.5646 | 0.010725 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9909 | OLEMA 1101337220 | 42291101 | OLEMA 1101 | 7959.8917 | 4.9471 | 28 | 0.28665 | 0.010237 | 1949 | 20386.8604 | 265.2779 | 0.010713 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7162 | BIG BEND 1101CB | 103751101 | BIG BEND 1101 | 37377.2089 | 23.2301 | 171 | 1.7454 | 0.010207 | 1950 | 20410.0905 | 263.5325 | 0.010643 | 263.5325 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9067 | PEORIA 170570198 | 163781705 | PEORIA 1705 | 3628.2739 | 2.255 | 36 | 0.36709 | 0.010197 | 1951 | 20412.3455 | 263.1654 | 0.010628 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6816 | REDBUD 1101400 | 43191101 | REDBUD 1101 | 1410.4889 | 0.87662 | 14 | 0.14273 | 0.010195 | 1952 | 20413.2221 | 263.0227 | 0.010622 | 263.0227 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5252 | POINT ARENA 110137426 | 43381101 | POINT ARENA 1101 | 1270.4089 | 0.78956 | 65 | 0.66101 | 0.010169 | 1953 | 20414.0117 | 262.3617 | 0.010595 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7444 | HOLLISTER 21064004 | 182492106 | HOLLISTER 2106 | 14083.7966 | 8.7531 | 180 | 1.8224 | 0.010124 | 1954 | 20422.7648 | 260.5393 | 0.010522 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2021 | WOODACRE 11021280 | 43021102 | WOODACRE 1102 | 13812.836 | 8.5847 | 111 | 1.1221 | 0.010109 | 1955 | 20431.3496 | 259.4173 | 0.010477 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9350 | WEST POINT 1101L3355 | 163201101 | WEST POINT 1101 | 3618.1853 | 2.2487 | 27 | 0.2728 | 0.010104 | 1956 | 20433.5983 | 259.1445 | 0.010466 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4549 | ALHAMBRA 110595016 | 14101105 | ALHAMBRA 1105 | 1223.0109 | 0.76011 | 69 | 0.69458 | 0.010066 | 1957 | 20434.3584 | 258.4499 | 0.010438 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5052 | BIG MEADOWS 21012474 | 102812101 | BIG MEADOWS 2101 | 13410.8685 | 8.3349 | 83 | 0.83287 | 0.010035 | 1958 | 20442.6933 | 257.617 | 0.010404 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
616 | SONOMA 1104414 | 42721104 | SONOMA 1104 | 2113.8048 | 1.3137 | 260 | 2.5977 | 0.009991 | 1959 | 20444.007 | 255.0193 | 0.010299 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8621 | FELTON 0401CB | 83140401 | FELTON 0401 | 4062.5857 | 2.5249 | 34 | 0.33859 | 0.0099584 | 1960 | 20446.5319 | 254.6808 | 0.010285 | 254.6808 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10564 | WISE 110163199 | 152271101 | WISE 1101 | 989.41 | 0.61492 | 8 | 0.079388 | 0.0099235 | 1961 | 20447.1469 | 254.6014 | 0.010282 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6010 | MORGAN HILL 2111XR292 | 83242111 | MORGAN HILL 2111 | 17975.9221 | 11.1721 | 130 | 1.287 | 0.0098996 | 1962 | 20458.319 | 253.3144 | 0.01023 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
222 | DUNBAR 1102CB | 43071102 | DUNBAR 1102 | 12733.914 | 7.9142 | 113 | 1.1166 | 0.0098816 | 1963 | 20466.2331 | 252.1978 | 0.010185 | 252.1978 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8045 | PERRY 1101W26 | 183071101 | PERRY 1101 | 4390.419 | 2.7287 | 18 | 0.17783 | 0.0098794 | 1964 | 20468.9618 | 252.02 | 0.010178 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7530 | BUCKS CREEK 11031131 | 102211103 | BUCKS CREEK 1103 | 4424.1224 | 2.7496 | 33 | 0.3254 | 0.0098607 | 1965 | 20471.7114 | 251.6946 | 0.010165 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7965 | RINCON 1103568 | 43321103 | RINCON 1103 | 20285.8832 | 12.6078 | 129 | 1.2694 | 0.0098399 | 1966 | 20484.3192 | 250.4252 | 0.010113 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7623 | PANOCHE 11034008 | 253671103 | PANOCHE 1103 | 56919.5652 | 35.3757 | 138 | 1.3505 | 0.0097859 | 1967 | 20519.6949 | 249.0748 | 0.010059 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1557 | WILLOW CREEK 11015002 | 192171101 | WILLOW CREEK 1101 | 21939.7249 | 13.6356 | 161 | 1.5733 | 0.0097721 | 1968 | 20533.3305 | 247.5015 | 0.0099954 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2260 | EL DORADO PH 210152456 | 152762101 | EL DORADO PH 2101 | 16414.576 | 10.2017 | 96 | 0.93593 | 0.0097493 | 1969 | 20543.5323 | 246.5655 | 0.0099576 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4474 | SPENCE 1104965598 | 182201104 | SPENCE 1104 | 14815.8266 | 9.2081 | 139 | 1.3544 | 0.0097442 | 1970 | 20552.7404 | 245.2111 | 0.0099029 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9612 | DIAMOND SPRINGS 1107203504 | 152261107 | DIAMOND SPRINGS 1107 | 226.4943 | 0.14077 | 4 | 0.038931 | 0.0097327 | 1971 | 20552.8811 | 245.1721 | 0.0099013 | 245.1721 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7259 | SUMMIT 1101742 | 152591101 | SUMMIT 1101 | 2084.4879 | 1.2955 | 21 | 0.20366 | 0.009698 | 1972 | 20554.1766 | 244.9685 | 0.0098931 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3486 | GRASS VALLEY 11012208 | 152031101 | GRASS VALLEY 1101 | 18971.647 | 11.791 | 159 | 1.5405 | 0.0096885 | 1973 | 20565.9676 | 243.428 | 0.0098309 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6926 | EL DORADO PH 210113532 | 152762101 | EL DORADO PH 2101 | 8576.7798 | 5.3305 | 46 | 0.44507 | 0.0096754 | 1974 | 20571.2981 | 242.9829 | 0.0098129 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4034 | OAKHURST 11035120 | 254421103 | OAKHURST 1103 | 9912.3897 | 6.1606 | 19 | 0.18333 | 0.0096488 | 1975 | 20577.4587 | 242.7996 | 0.0098055 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3547 | RINCON 1101539980 | 43321101 | RINCON 1101 | 474.6546 | 0.295 | 4 | 0.038517 | 0.0096291 | 1976 | 20577.7537 | 242.7611 | 0.0098039 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2441 | SILVERADO 2103617828 | 43432103 | SILVERADO 2103 | 2303.2847 | 1.4315 | 28 | 0.26958 | 0.0096279 | 1977 | 20579.1852 | 242.4915 | 0.009793 | 242.4915 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5129 | NEWBURG 1131380686 | 192151131 | NEWBURG 1131 | 3014.5331 | 1.8735 | 34 | 0.32624 | 0.0095954 | 1978 | 20581.0587 | 242.1653 | 0.0097799 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2275 | BUTTE 11051243 | 103081105 | BUTTE 1105 | 8319.7013 | 5.1707 | 50 | 0.47679 | 0.0095359 | 1979 | 20586.2295 | 241.6885 | 0.0097606 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4445 | PINE GROVE 1102467560 | 163751102 | PINE GROVE 1102 | 3279.179 | 2.038 | 27 | 0.25736 | 0.009532 | 1980 | 20588.2675 | 241.4311 | 0.0097502 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6213 | JESSUP 1103728460 | 103441103 | JESSUP 1103 | 1173.0161 | 0.72903 | 17 | 0.16201 | 0.0095302 | 1981 | 20588.9965 | 241.2691 | 0.0097437 | 241.2691 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3085 | SHINGLE SPRINGS 210819622 | 153652108 | SHINGLE SPRINGS 2108 | 9040.145 | 5.6185 | 165 | 1.5722 | 0.0095283 | 1982 | 20594.615 | 239.6969 | 0.0096802 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9214 | SAN RAFAEL 11081250 | 42011108 | SAN RAFAEL 1108 | 5741.9405 | 3.5686 | 26 | 0.24699 | 0.0094996 | 1983 | 20598.1837 | 239.4499 | 0.0096702 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10597 | MONTE RIO 11135024 | 42811113 | MONTE RIO 1113 | 526.6111 | 0.32729 | 4 | 0.037943 | 0.0094858 | 1984 | 20598.5109 | 239.412 | 0.0096687 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2882 | WILLOW PASS 2108CB | 13912108 | WILLOW PASS 2108 | 318.0802 | 0.19769 | 91 | 0.86121 | 0.0094639 | 1985 | 20598.7086 | 238.5508 | 0.0096339 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5172 | LOS OSITOS 2103220608 | 182082103 | LOS OSITOS 2103 | 1678.7883 | 1.0434 | 10 | 0.09449 | 0.009449 | 1986 | 20599.752 | 238.4563 | 0.0096301 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1655 | BRUNSWICK 110750010 | 152481107 | BRUNSWICK 1107 | 9841.1126 | 6.1163 | 117 | 1.1046 | 0.0094406 | 1987 | 20605.8683 | 237.3518 | 0.0095855 | 237.3518 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3494 | WILLITS 110434008 | 42661104 | WILLITS 1104 | 36886.2403 | 22.9249 | 259 | 2.4408 | 0.0094239 | 1988 | 20628.7932 | 234.911 | 0.0094869 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7626 | RESERVATION ROAD 11023030 | 182731102 | RESERVATION ROAD 1102 | 16131.8418 | 10.026 | 186 | 1.7499 | 0.0094083 | 1989 | 20638.8193 | 233.161 | 0.0094162 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10686 | HARTLEY 110158095 | 43211101 | HARTLEY 1101 | 251.9158 | 0.15657 | 2 | 0.018803 | 0.0094017 | 1990 | 20638.9758 | 233.1422 | 0.0094155 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7656 | PHILO 11022600 | 42601102 | PHILO 1102 | 32204.7216 | 20.0154 | 114 | 1.0603 | 0.0093006 | 1991 | 20658.9912 | 232.0819 | 0.0093726 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7863 | SANTA ROSA A 1104642 | 42151104 | SANTA ROSA A 1104 | 14995.9698 | 9.3201 | 127 | 1.173 | 0.0092364 | 1992 | 20668.3112 | 230.9089 | 0.0093253 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
581 | POINT ARENA 1101474 | 43381101 | POINT ARENA 1101 | 14496.4925 | 9.0096 | 77 | 0.70936 | 0.0092125 | 1993 | 20677.3209 | 230.1996 | 0.0092966 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9791 | LOS OSITOS 2103695270 | 182082103 | LOS OSITOS 2103 | 1116.1992 | 0.69372 | 12 | 0.11039 | 0.009199 | 1994 | 20678.0146 | 230.0892 | 0.0092922 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9383 | CASTRO VALLEY 1110MR525 | 14091110 | CASTRO VALLEY 1110 | 17.8831 | 0.011114 | 2 | 0.018393 | 0.0091967 | 1995 | 20678.0257 | 230.0708 | 0.0092914 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5023 | MC ARTHUR 11021324 | 103491102 | MC ARTHUR 1102 | 1638.5898 | 1.0184 | 169 | 1.5507 | 0.0091756 | 1996 | 20679.0441 | 228.5201 | 0.0092288 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7662 | CASTRO VALLEY 1110610800 | 14091110 | CASTRO VALLEY 1110 | 3862.9953 | 2.4009 | 33 | 0.30062 | 0.0091096 | 1997 | 20681.445 | 228.2195 | 0.0092167 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6717 | NEWBURG 1132910230 | 192151132 | NEWBURG 1132 | 1560.5069 | 0.96986 | 27 | 0.24556 | 0.0090947 | 1998 | 20682.4148 | 227.9739 | 0.0092067 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10 | KONOCTI 1102532 | 43311102 | KONOCTI 1102 | 15658.0016 | 9.7315 | 124 | 1.1234 | 0.0090595 | 1999 | 20692.1463 | 226.8505 | 0.0091614 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5170 | EL DORADO PH 2102542272 | 152762102 | EL DORADO PH 2102 | 12585.3616 | 7.8219 | 80 | 0.72357 | 0.0090446 | 2000 | 20699.9682 | 226.127 | 0.0091321 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8963 | MIRABEL 1101253331 | 42091101 | MIRABEL 1101 | 107.6584 | 0.06691 | 5 | 0.045085 | 0.0090171 | 2001 | 20700.0351 | 226.0819 | 0.0091303 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10053 | ROB ROY 21046577 | 83692104 | ROB ROY 2104 | 5581.4139 | 3.4689 | 33 | 0.29681 | 0.0089943 | 2002 | 20703.504 | 225.7851 | 0.0091183 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8505 | NEWBURG 113190242 | 192151131 | NEWBURG 1131 | 6652.6427 | 4.1346 | 51 | 0.45866 | 0.0089934 | 2003 | 20707.6386 | 225.3264 | 0.0090998 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
283 | SAN RAFAEL 1104802 | 42011104 | SAN RAFAEL 1104 | 13782.7792 | 8.5661 | 162 | 1.451 | 0.0089568 | 2004 | 20716.2047 | 223.8754 | 0.0090412 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9446 | ECHO SUMMIT 1101481660 | 158031101 | ECHO SUMMIT 1101 | 1750.3957 | 1.0879 | 21 | 0.18809 | 0.0089565 | 2005 | 20717.2925 | 223.6873 | 0.0090336 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1636 | LOS COCHES 1101625902 | 182151101 | LOS COCHES 1101 | 4214.4266 | 2.6193 | 26 | 0.23178 | 0.0089147 | 2006 | 20719.9118 | 223.4555 | 0.0090243 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8007 | SAN JUSTO 11014002 | 183181101 | SAN JUSTO 1101 | 29553.7891 | 18.3678 | 140 | 1.246 | 0.0088999 | 2007 | 20738.2796 | 222.2095 | 0.0089739 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4827 | ATASCADERO 1103A88 | 182541103 | ATASCADERO 1103 | 1506.8203 | 0.93649 | 41 | 0.36363 | 0.008869 | 2008 | 20739.2161 | 221.8459 | 0.0089593 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6300 | DRUM 11011602 | 152321101 | DRUM 1101 | 26067.9128 | 16.2013 | 121 | 1.0723 | 0.0088619 | 2009 | 20755.4174 | 220.7736 | 0.008916 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7254 | ALLEGHANY 1101VR816 | 152101101 | ALLEGHANY 1101 | 6675.8935 | 4.1491 | 49 | 0.43385 | 0.0088541 | 2010 | 20759.5665 | 220.3398 | 0.0088984 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2986 | PINE GROVE 110235576 | 163751102 | PINE GROVE 1102 | 12676.983 | 7.8788 | 77 | 0.68102 | 0.0088445 | 2011 | 20767.4453 | 219.6588 | 0.0088709 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8230 | SAN LUIS OBISPO 1102357407 | 182631102 | SAN LUIS OBISPO 1102 | 382.6506 | 0.23782 | 5 | 0.044188 | 0.0088377 | 2012 | 20767.6831 | 219.6146 | 0.0088691 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1189 | PEORIA 170575274 | 163781705 | PEORIA 1705 | 623.7122 | 0.38764 | 43 | 0.37982 | 0.0088331 | 2013 | 20768.0708 | 219.2347 | 0.0088538 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
299 | MONTE RIO 111164758 | 42811111 | MONTE RIO 1111 | 16840.1197 | 10.4662 | 97 | 0.8528 | 0.0087918 | 2014 | 20778.537 | 218.3819 | 0.0088194 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8131 | HARTLEY 1101534548 | 43211101 | HARTLEY 1101 | 643.683 | 0.40005 | 7 | 0.061222 | 0.008746 | 2015 | 20778.937 | 218.3207 | 0.0088169 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3395 | BOLINAS 1101504 | 42261101 | BOLINAS 1101 | 10763.1252 | 6.6893 | 53 | 0.46123 | 0.0087025 | 2016 | 20785.6264 | 217.8595 | 0.0087983 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6220 | LAKEVILLE 1102530 | 43371102 | LAKEVILLE 1102 | 114.9911 | 0.071467 | 55 | 0.47853 | 0.0087005 | 2017 | 20785.6978 | 217.381 | 0.0087789 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8104 | MONTE RIO 111137520 | 42811111 | MONTE RIO 1111 | 3437.9631 | 2.1367 | 20 | 0.17369 | 0.0086846 | 2018 | 20787.8345 | 217.2073 | 0.0087719 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5024 | MONTE RIO 1113180 | 42811113 | MONTE RIO 1113 | 3158.1165 | 1.9628 | 28 | 0.24298 | 0.0086779 | 2019 | 20789.7973 | 216.9643 | 0.0087621 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2418 | CLEAR LAKE 11011302 | 42141101 | CLEAR LAKE 1101 | 12188.0095 | 7.5749 | 189 | 1.6401 | 0.0086777 | 2020 | 20797.3722 | 215.3242 | 0.0086959 | 215.3242 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6344 | WEST POINT 11021303 | 163201102 | WEST POINT 1102 | 25207.4138 | 15.6665 | 146 | 1.2651 | 0.0086648 | 2021 | 20813.0387 | 214.0591 | 0.0086448 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
147 | SHADY GLEN 11022232 | 152431102 | SHADY GLEN 1102 | 16843.7265 | 10.4684 | 88 | 0.76044 | 0.0086414 | 2022 | 20823.5072 | 213.2987 | 0.0086141 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8652 | LOYOLA 1102725939 | 82161102 | LOYOLA 1102 | 150.5355 | 0.093558 | 14 | 0.12055 | 0.0086108 | 2023 | 20823.6007 | 213.1782 | 0.0086092 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10013 | GREEN VALLEY 21016601 | 83192101 | GREEN VALLEY 2101 | 3063.6094 | 1.904 | 19 | 0.16314 | 0.0085862 | 2024 | 20825.5048 | 213.015 | 0.0086026 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3970 | PUEBLO 1105348368 | 43291105 | PUEBLO 1105 | 4473.6471 | 2.7804 | 107 | 0.91803 | 0.0085797 | 2025 | 20828.2852 | 212.097 | 0.0085655 | 212.097 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5419 | MIRABEL 11014859 | 42091101 | MIRABEL 1101 | 3008.5895 | 1.8699 | 22 | 0.18826 | 0.0085572 | 2026 | 20830.155 | 211.9087 | 0.0085579 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3836 | PURISIMA 1101CB | 182971101 | PURISIMA 1101 | 5917.6189 | 3.6778 | 32 | 0.27301 | 0.0085315 | 2027 | 20833.8328 | 211.6357 | 0.0085469 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
589 | EL DORADO PH 21016852 | 152762101 | EL DORADO PH 2101 | 40624.2727 | 25.2481 | 309 | 2.6354 | 0.0085289 | 2028 | 20859.081 | 209.0003 | 0.0084405 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7704 | GOLDTREE 1107CB | 182581107 | GOLDTREE 1107 | 1480.1268 | 0.9199 | 28 | 0.23879 | 0.0085282 | 2029 | 20860.0009 | 208.7615 | 0.0084308 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10273 | POINT ARENA 11014923 | 43381101 | POINT ARENA 1101 | 4611.3164 | 2.866 | 12 | 0.10222 | 0.008518 | 2030 | 20862.8668 | 208.6593 | 0.0084267 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
327 | CURTIS 170463502 | 163351704 | CURTIS 1704 | 16836.9835 | 10.4643 | 107 | 0.90898 | 0.0084952 | 2031 | 20873.3311 | 207.7503 | 0.00839 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7937 | CLARK ROAD 11022068 | 103091102 | CLARK ROAD 1102 | 17517.3264 | 10.8871 | 90 | 0.76407 | 0.0084897 | 2032 | 20884.2182 | 206.9862 | 0.0083592 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4769 | WYANDOTTE 1107CB | 102911107 | WYANDOTTE 1107 | 2030.3761 | 1.2619 | 199 | 1.6868 | 0.0084763 | 2033 | 20885.4801 | 205.2995 | 0.008291 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7564 | COLUMBIA HILL 11018233 | 152471101 | COLUMBIA HILL 1101 | 7978.7453 | 4.9588 | 51 | 0.43182 | 0.008467 | 2034 | 20890.4389 | 204.8676 | 0.0082736 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2536 | HALSEY 1101CB | 152241101 | HALSEY 1101 | 27644.3487 | 17.1811 | 231 | 1.9501 | 0.0084422 | 2035 | 20907.62 | 202.9175 | 0.0081948 | 202.9175 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2174 | DIAMOND SPRINGS 1104CB | 152261104 | DIAMOND SPRINGS 1104 | 9046.8091 | 5.6226 | 127 | 1.0659 | 0.008393 | 2036 | 20913.2426 | 201.8516 | 0.0081518 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4975 | EL DORADO PH 210119612 | 152762101 | EL DORADO PH 2101 | 14689.1647 | 9.1294 | 102 | 0.85418 | 0.0083743 | 2037 | 20922.372 | 200.9974 | 0.0081173 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7088 | SAUSALITO 11021500 | 42491102 | SAUSALITO 1102 | 1869.3575 | 1.1618 | 8 | 0.066779 | 0.0083473 | 2038 | 20923.5338 | 200.9306 | 0.0081146 | 200.9306 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4510 | CAMP EVERS 210511010 | 83622105 | CAMP EVERS 2105 | 3501.2634 | 2.176 | 26 | 0.21641 | 0.0083235 | 2039 | 20925.7098 | 200.7142 | 0.0081059 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7509 | WESTLEY 1103237522 | 162671103 | WESTLEY 1103 | 1485.982 | 0.92354 | 39 | 0.32346 | 0.0082937 | 2040 | 20926.6334 | 200.3908 | 0.0080928 | 200.3908 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2971 | CASTRO VALLEY 1111MR334 | 14091111 | CASTRO VALLEY 1111 | 9116.5949 | 5.666 | 80 | 0.65886 | 0.0082358 | 2041 | 20932.2994 | 199.7319 | 0.0080662 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
143 | RACETRACK 1703CB | 163761703 | RACETRACK 1703 | 25353.1416 | 15.7571 | 216 | 1.7632 | 0.008163 | 2042 | 20948.0565 | 197.9687 | 0.007995 | 197.9687 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1117 | MORGAN HILL 2104152774 | 83242104 | MORGAN HILL 2104 | 10319.2603 | 6.4135 | 84 | 0.68304 | 0.0081314 | 2043 | 20954.4699 | 197.2857 | 0.0079674 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3526 | SILVERADO 2103920793 | 43432103 | SILVERADO 2103 | 10473.7039 | 6.5094 | 51 | 0.40968 | 0.008033 | 2044 | 20960.9794 | 196.876 | 0.0079508 | 196.876 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7263 | FORESTHILL 11011820 | 152181101 | FORESTHILL 1101 | 9227.6622 | 5.735 | 51 | 0.40941 | 0.0080276 | 2045 | 20966.7144 | 196.4666 | 0.0079343 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4807 | PLACER 1103238990 | 152461103 | PLACER 1103 | 65.0773 | 0.040446 | 84 | 0.67354 | 0.0080184 | 2046 | 20966.7548 | 195.793 | 0.0079071 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7786 | UPPER LAKE 11016663 | 42871101 | UPPER LAKE 1101 | 3787.49 | 2.3539 | 17 | 0.13592 | 0.0079953 | 2047 | 20969.1088 | 195.6571 | 0.0079016 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
797 | DUNBAR 1101CB | 43071101 | DUNBAR 1101 | 5020.5865 | 3.1203 | 191 | 1.5267 | 0.007993 | 2048 | 20972.2291 | 194.1304 | 0.00784 | 194.1304 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1103 | HOOPA 1101CB | 192401101 | HOOPA 1101 | 37375.4287 | 23.229 | 440 | 3.4806 | 0.0079104 | 2049 | 20995.4581 | 190.6499 | 0.0076994 | 190.6499 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8668 | BIG BASIN 110211062 | 82841102 | BIG BASIN 1102 | 21428.2343 | 13.3177 | 88 | 0.69511 | 0.007899 | 2050 | 21008.7758 | 189.9548 | 0.0076713 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7844 | ELK 11011260 | 42981101 | ELK 1101 | 25226.838 | 15.6786 | 120 | 0.94759 | 0.0078966 | 2051 | 21024.4544 | 189.0072 | 0.0076331 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2387 | HALSEY 110239104 | 152241102 | HALSEY 1102 | 49366.035 | 30.6812 | 346 | 2.7292 | 0.007888 | 2052 | 21055.1356 | 186.2779 | 0.0075228 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1085 | MORAGA 1101CB | 13801101 | MORAGA 1101 | 13611.4014 | 8.4595 | 92 | 0.72506 | 0.0078811 | 2053 | 21063.5951 | 185.5529 | 0.0074936 | 185.5529 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6726 | MARTELL 110292172 | 163011102 | MARTELL 1102 | 190.7947 | 0.11858 | 45 | 0.35387 | 0.0078638 | 2054 | 21063.7137 | 185.199 | 0.0074793 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1984 | HALF MOON BAY 110369412 | 24101103 | HALF MOON BAY 1103 | 25048.7626 | 15.5679 | 150 | 1.1767 | 0.0078448 | 2055 | 21079.2816 | 184.0223 | 0.0074317 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2299 | VINEYARD 2107CB | 14502107 | VINEYARD 2107 | 3069.8489 | 1.9079 | 111 | 0.8653 | 0.0077955 | 2056 | 21081.1895 | 183.157 | 0.0073968 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9627 | POINT ARENA 11011296 | 43381101 | POINT ARENA 1101 | 5630.7668 | 3.4995 | 37 | 0.28757 | 0.007772 | 2057 | 21084.6891 | 182.8694 | 0.0073852 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2765 | FORESTHILL 1101CB | 152181101 | FORESTHILL 1101 | 14659.7522 | 9.1111 | 110 | 0.85174 | 0.0077431 | 2058 | 21093.8002 | 182.0177 | 0.0073508 | 182.0177 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4087 | BURNEY 11011340 | 103311101 | BURNEY 1101 | 28996.5273 | 18.0215 | 144 | 1.1103 | 0.0077101 | 2059 | 21111.8216 | 180.9074 | 0.007306 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8844 | MIDDLETOWN 1101614 | 43141101 | MIDDLETOWN 1101 | 2222.7419 | 1.3814 | 18 | 0.13857 | 0.0076984 | 2060 | 21113.2031 | 180.7688 | 0.0073004 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3083 | MONTE RIO 1113320 | 42811113 | MONTE RIO 1113 | 4467.496 | 2.7766 | 29 | 0.22308 | 0.0076924 | 2061 | 21115.9796 | 180.5458 | 0.0072914 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7740 | POINT MORETTI 110136514 | 82931101 | POINT MORETTI 1101 | 11050.0531 | 6.8677 | 64 | 0.4904 | 0.0076624 | 2062 | 21122.8473 | 180.0554 | 0.0072715 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
898 | COTATI 11055156 | 42271105 | COTATI 1105 | 7784.4976 | 4.8381 | 114 | 0.86938 | 0.0076261 | 2063 | 21127.6854 | 179.186 | 0.0072364 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3027 | PHILO 11021308 | 42601102 | PHILO 1102 | 51491.5441 | 32.0022 | 245 | 1.8679 | 0.0076242 | 2064 | 21159.6876 | 177.3181 | 0.007161 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10504 | KANAKA 11011036 | 103221101 | KANAKA 1101 | 989.4598 | 0.61495 | 4 | 0.030429 | 0.0076073 | 2065 | 21160.3026 | 177.2876 | 0.0071598 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2446 | FOOTHILL 1102V06 | 182951102 | FOOTHILL 1102 | 3602.7995 | 2.2392 | 66 | 0.50199 | 0.007606 | 2066 | 21162.5417 | 176.7856 | 0.0071395 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4588 | COARSEGOLD 21025722 | 254432102 | COARSEGOLD 2102 | 3182.5999 | 1.978 | 23 | 0.17492 | 0.0076053 | 2067 | 21164.5197 | 176.6107 | 0.0071324 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8714 | OTTER 1101CB | 182941101 | OTTER 1101 | 10367.8883 | 6.4437 | 54 | 0.41015 | 0.0075954 | 2068 | 21170.9634 | 176.2006 | 0.0071159 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9866 | DUNBAR 1101343 | 43071101 | DUNBAR 1101 | 7140.9406 | 4.4381 | 39 | 0.29486 | 0.0075606 | 2069 | 21175.4015 | 175.9057 | 0.007104 | 175.9057 | #N/A | #N/A | #N/A | #N/A | #VALUE!
723 | BIG BASIN 110296986 | 82841102 | BIG BASIN 1102 | 9497.5055 | 5.9027 | 63 | 0.47604 | 0.0075562 | 2070 | 21181.3043 | 175.4297 | 0.0070847 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5272 | NEWBURG 1133CB | 192151133 | NEWBURG 1133 | 5089.2485 | 3.163 | 92 | 0.69311 | 0.0075338 | 2071 | 21184.4672 | 174.7365 | 0.0070567 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6817 | HALF MOON BAY 1103695411 | 24101103 | HALF MOON BAY 1103 | 13352.973 | 8.2989 | 99 | 0.74539 | 0.0075292 | 2072 | 21192.7662 | 173.9911 | 0.0070266 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9735 | EEL RIVER 1103216324 | 192381103 | EEL RIVER 1103 | 3681.9233 | 2.2883 | 23 | 0.17297 | 0.0075204 | 2073 | 21195.0545 | 173.8182 | 0.0070197 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
803 | DIAMOND SPRINGS 1107CB | 152261107 | DIAMOND SPRINGS 1107 | 0 | 0 | 51 | 0.38224 | 0.0074949 | 2074 | 21195.0545 | 173.4359 | 0.0070042 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2229 | EL DORADO PH 210136764 | 152762101 | EL DORADO PH 2101 | 5034.5882 | 3.129 | 46 | 0.34473 | 0.0074941 | 2075 | 21198.1835 | 173.0912 | 0.0069903 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5945 | SANTA ROSA A 1111758024 | 42151111 | SANTA ROSA A 1111 | 7589.8929 | 4.7171 | 72 | 0.53884 | 0.007484 | 2076 | 21202.9007 | 172.5524 | 0.0069685 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
726 | DIAMOND SPRINGS 1106930190 | 152261106 | DIAMOND SPRINGS 1106 | 27579.5424 | 17.1408 | 207 | 1.5476 | 0.0074761 | 2077 | 21220.0415 | 171.0048 | 0.006906 | 171.0048 | #N/A | #N/A | #N/A | #N/A | #VALUE!
353 | CURTIS 170210940 | 163351702 | CURTIS 1702 | 13824.9592 | 8.5923 | 138 | 1.0183 | 0.0073788 | 2078 | 21228.6337 | 169.9865 | 0.0068649 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1231 | RED BLUFF 1103CB | 103541103 | RED BLUFF 1103 | 164.6636 | 0.10234 | 261 | 1.9098 | 0.0073172 | 2079 | 21228.7361 | 168.0767 | 0.0067878 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10001 | PANOCHE 11034036 | 253671103 | PANOCHE 1103 | 16000.3845 | 9.9443 | 57 | 0.41612 | 0.0073003 | 2080 | 21238.6804 | 167.6606 | 0.006771 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9426 | GREEN VALLEY 2101380922 | 83192101 | GREEN VALLEY 2101 | 1588.6005 | 0.98732 | 30 | 0.2187 | 0.0072901 | 2081 | 21239.6677 | 167.4419 | 0.0067622 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1700 | LUCERNE 110676850 | 43351106 | LUCERNE 1106 | 3458.1261 | 2.1492 | 51 | 0.37072 | 0.0072691 | 2082 | 21241.8169 | 167.0712 | 0.0067472 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2002 | HOLLISTER 21054018 | 182492105 | HOLLISTER 2105 | 71470.9964 | 44.4195 | 280 | 2.035 | 0.0072679 | 2083 | 21286.2364 | 165.0362 | 0.006665 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2867 | MONTE RIO 1113346 | 42811113 | MONTE RIO 1113 | 16160.3417 | 10.0437 | 101 | 0.72881 | 0.0072159 | 2084 | 21296.2802 | 164.3074 | 0.0066356 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7311 | LOS OSITOS 2102258878 | 182082102 | LOS OSITOS 2102 | 5357.1763 | 3.3295 | 26 | 0.18757 | 0.0072141 | 2085 | 21299.6097 | 164.1198 | 0.006628 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1213 | WOODACRE 1102137662 | 43021102 | WOODACRE 1102 | 13813.2405 | 8.585 | 104 | 0.74714 | 0.0071841 | 2086 | 21308.1947 | 163.3727 | 0.0065978 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2384 | BONNIE NOOK 1102CB | 152301102 | BONNIE NOOK 1102 | 54723.5805 | 34.0109 | 337 | 2.4164 | 0.0071702 | 2087 | 21342.2056 | 160.9563 | 0.0065002 | 160.9563 | #N/A | #N/A | #N/A | #N/A | #VALUE!
324 | PLACERVILLE 1110953474 | 153081110 | PLACERVILLE 1110 | 17115.5789 | 10.6374 | 133 | 0.94748 | 0.0071239 | 2088 | 21352.843 | 160.0088 | 0.006462 | 160.0088 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9849 | FOOTHILL 1101722270 | 182951101 | FOOTHILL 1101 | 283.5574 | 0.17623 | 5 | 0.035479 | 0.0070957 | 2089 | 21353.0192 | 159.9733 | 0.0064605 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3510 | MONTE RIO 1111140 | 42811111 | MONTE RIO 1111 | 13525.925 | 8.4064 | 96 | 0.67561 | 0.0070376 | 2090 | 21361.4256 | 159.2977 | 0.0064332 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1551 | CARLOTTA 11214914 | 192291121 | CARLOTTA 1121 | 17097.4476 | 10.6261 | 138 | 0.97117 | 0.0070374 | 2091 | 21372.0518 | 158.3266 | 0.006394 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4560 | COARSEGOLD 210210330 | 254432102 | COARSEGOLD 2102 | 15550.3229 | 9.6646 | 90 | 0.62906 | 0.0069896 | 2092 | 21381.7164 | 157.6975 | 0.0063686 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6442 | PIT NO 1 11019702 | 103721101 | PIT NO 1 1101 | 1035.9167 | 0.64383 | 91 | 0.63564 | 0.006985 | 2093 | 21382.3602 | 157.0619 | 0.006343 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8877 | WILLOW CREEK 11013050 | 192171101 | WILLOW CREEK 1101 | 4223.7094 | 2.6251 | 18 | 0.12569 | 0.0069828 | 2094 | 21384.9852 | 156.9362 | 0.0063379 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9559 | SONOMA 1103581588 | 42721103 | SONOMA 1103 | 313.0143 | 0.19454 | 14 | 0.097419 | 0.0069585 | 2095 | 21385.1798 | 156.8388 | 0.0063339 | 156.8388 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2326 | BRUNSWICK 11052140 | 152481105 | BRUNSWICK 1105 | 55629.2693 | 34.5738 | 373 | 2.5928 | 0.0069513 | 2096 | 21419.7536 | 154.2459 | 0.0062292 | 154.2459 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7797 | SAUSALITO 1101331806 | 42491101 | SAUSALITO 1101 | 799.0558 | 0.49662 | 5 | 0.034637 | 0.0069274 | 2097 | 21420.2502 | 154.2113 | 0.0062278 | 154.2113 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1778 | WEIMAR 11026175 | 152491102 | WEIMAR 1102 | 4418.4642 | 2.7461 | 30 | 0.20713 | 0.0069045 | 2098 | 21422.9963 | 154.0042 | 0.0062195 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2962 | CURTIS 1704803 | 163351704 | CURTIS 1704 | 15630.8479 | 9.7146 | 93 | 0.64118 | 0.0068944 | 2099 | 21432.7109 | 153.363 | 0.0061936 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5429 | MIRABEL 1101228 | 42091101 | MIRABEL 1101 | 3403.012 | 2.115 | 123 | 0.84091 | 0.0068367 | 2100 | 21434.8259 | 152.5221 | 0.0061596 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8011 | HORSESHOE 1101603250 | 152571101 | HORSESHOE 1101 | 927.3694 | 0.57636 | 21 | 0.14351 | 0.0068337 | 2101 | 21435.4023 | 152.3786 | 0.0061538 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7095 | PUEBLO 2102618 | 43292102 | PUEBLO 2102 | 742.2572 | 0.46132 | 118 | 0.80516 | 0.0068234 | 2102 | 21435.8636 | 151.5734 | 0.0061213 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8240 | WOODSIDE 11018601 | 24251101 | WOODSIDE 1101 | 961.631 | 0.59766 | 9 | 0.061013 | 0.0067792 | 2103 | 21436.4613 | 151.5124 | 0.0061188 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3848 | REEDLEY 11127240 | 252341112 | REEDLEY 1112 | 1553.9231 | 0.96577 | 234 | 1.5828 | 0.0067642 | 2104 | 21437.427 | 149.9296 | 0.0060549 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4429 | SONOMA 1105138 | 42721105 | SONOMA 1105 | 104.0479 | 0.064666 | 197 | 1.3309 | 0.0067556 | 2105 | 21437.4917 | 148.5987 | 0.0060012 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1588 | CORRAL 110359770 | 162991103 | CORRAL 1103 | 7749.7634 | 4.8165 | 97 | 0.65443 | 0.0067467 | 2106 | 21442.3082 | 147.9443 | 0.0059747 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6984 | GABILAN 1101566352 | 182331101 | GABILAN 1101 | 680.7554 | 0.42309 | 9 | 0.060679 | 0.0067421 | 2107 | 21442.7313 | 147.8836 | 0.0059723 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8546 | SPENCE 1102990464 | 182201102 | SPENCE 1102 | 3365.9887 | 2.092 | 53 | 0.3568 | 0.0067321 | 2108 | 21444.8233 | 147.5268 | 0.0059579 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9813 | BOLINAS 110137034 | 42261101 | BOLINAS 1101 | 7287.0481 | 4.5289 | 16 | 0.10722 | 0.006701 | 2109 | 21449.3522 | 147.4196 | 0.0059535 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8495 | PENRYN 110550550 | 152561105 | PENRYN 1105 | 0 | 0 | 127 | 0.84852 | 0.0066813 | 2110 | 21449.3522 | 146.5711 | 0.0059193 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
533 | HIGHLANDS 110439458 | 43361104 | HIGHLANDS 1104 | 1902.6531 | 1.1825 | 72 | 0.47971 | 0.0066627 | 2111 | 21450.5347 | 146.0913 | 0.0058999 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6908 | MENLO 11038512 | 24131103 | MENLO 1103 | 39804.5313 | 24.7387 | 228 | 1.5133 | 0.0066372 | 2112 | 21475.2734 | 144.5781 | 0.0058388 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1455 | LAS GALLINAS A 1105904 | 42991105 | LAS GALLINAS A 1105 | 2469.2456 | 1.5346 | 78 | 0.51694 | 0.0066274 | 2113 | 21476.808 | 144.0611 | 0.0058179 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2184 | GEYSERVILLE 110289714 | 42891102 | GEYSERVILLE 1102 | 178.2278 | 0.11077 | 71 | 0.47052 | 0.0066271 | 2114 | 21476.9188 | 143.5906 | 0.0057989 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2865 | MOLINO 1102344 | 42571102 | MOLINO 1102 | 2427.2453 | 1.5085 | 77 | 0.50953 | 0.0066172 | 2115 | 21478.4273 | 143.0811 | 0.0057783 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2057 | SHINGLE SPRINGS 210911092 | 153652109 | SHINGLE SPRINGS 2109 | 36100.2834 | 22.4365 | 239 | 1.5798 | 0.0066099 | 2116 | 21500.8638 | 141.5013 | 0.0057145 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10095 | SILVERADO 2104645 | 43432104 | SILVERADO 2104 | 1626.8938 | 1.0111 | 13 | 0.085285 | 0.0065604 | 2117 | 21501.8749 | 141.416 | 0.0057111 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6812 | CLOVERDALE 1101474708 | 42821101 | CLOVERDALE 1101 | 422.046 | 0.2623 | 13 | 0.084962 | 0.0065356 | 2118 | 21502.1372 | 141.3311 | 0.0057077 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
891 | TEMPLETON 2108A64 | 183052108 | TEMPLETON 2108 | 3242.5015 | 2.0152 | 150 | 0.9794 | 0.0065293 | 2119 | 21504.1525 | 140.3517 | 0.0056681 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
851 | HIGGINS 1110861610 | 152691110 | HIGGINS 1110 | 1689.7743 | 1.0502 | 99 | 0.64633 | 0.0065286 | 2120 | 21505.2027 | 139.7053 | 0.005642 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10050 | MIRABEL 110286326 | 42091102 | MIRABEL 1102 | 1133.0955 | 0.70422 | 5 | 0.032614 | 0.0065228 | 2121 | 21505.9069 | 139.6727 | 0.0056407 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1904 | SONOMA 1105404 | 42721105 | SONOMA 1105 | 3785.8959 | 2.3529 | 63 | 0.41053 | 0.0065164 | 2122 | 21508.2598 | 139.2622 | 0.0056241 | 139.2622 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4884 | PLACERVILLE 1112CB | 153081112 | PLACERVILLE 1112 | 13697.3672 | 8.513 | 117 | 0.76223 | 0.0065148 | 2123 | 21516.7728 | 138.5 | 0.0055933 | 138.5 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3571 | OAKHURST 110377384 | 254421103 | OAKHURST 1103 | 7595.6346 | 4.7207 | 61 | 0.39738 | 0.0065145 | 2124 | 21521.4935 | 138.1026 | 0.0055773 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2586 | VOLTA 11021504 | 102541102 | VOLTA 1102 | 13347.4853 | 8.2955 | 95 | 0.61869 | 0.0065125 | 2125 | 21529.789 | 137.4839 | 0.0055523 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5574 | PARADISE 1104920400 | 102831104 | PARADISE 1104 | 7538.764 | 4.6854 | 66 | 0.42879 | 0.0064968 | 2126 | 21534.4744 | 137.0551 | 0.005535 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3679 | SUNOL 1101MR297 | 14241101 | SUNOL 1101 | 9531.5764 | 5.9239 | 66 | 0.42822 | 0.0064881 | 2127 | 21540.3983 | 136.6269 | 0.0055177 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3379 | GEYSERVILLE 1101354 | 42891101 | GEYSERVILLE 1101 | 1010.2026 | 0.62784 | 79 | 0.51214 | 0.0064828 | 2128 | 21541.0262 | 136.1147 | 0.005497 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5354 | FORT ROSS 1121560 | 42851121 | FORT ROSS 1121 | 8145.5491 | 5.0625 | 31 | 0.20026 | 0.0064599 | 2129 | 21546.0887 | 135.9145 | 0.0054889 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1701 | CALAVERAS CEMENT 110136880 | 162211101 | CALAVERAS CEMENT 1101 | 9899.4771 | 6.1526 | 92 | 0.59319 | 0.0064477 | 2130 | 21552.2412 | 135.3213 | 0.005465 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3076 | PLACERVILLE 21061104 | 153082106 | PLACERVILLE 2106 | 79643.684 | 49.4989 | 462 | 2.9785 | 0.0064469 | 2131 | 21601.7401 | 132.3428 | 0.0053447 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6813 | CASTRO VALLEY 111010315 | 14091110 | CASTRO VALLEY 1110 | 8831.8074 | 5.489 | 53 | 0.34084 | 0.006431 | 2132 | 21607.2291 | 132.002 | 0.0053309 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7135 | MOLINO 1102982462 | 42571102 | MOLINO 1102 | 2320.5593 | 1.4422 | 18 | 0.11569 | 0.006427 | 2133 | 21608.6713 | 131.8863 | 0.0053262 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8349 | BRUNSWICK 1110CB | 152481110 | BRUNSWICK 1110 | 5.4992 | 0.0034177 | 26 | 0.16685 | 0.0064174 | 2134 | 21608.6748 | 131.7194 | 0.0053195 | 131.7194 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3244 | PLACERVILLE 111219712 | 153081112 | PLACERVILLE 1112 | 20776.2868 | 12.9125 | 151 | 0.96818 | 0.0064118 | 2135 | 21621.5873 | 130.7513 | 0.0052804 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3409 | PINE GROVE 110213438 | 163751102 | PINE GROVE 1102 | 26618.9181 | 16.5438 | 172 | 1.1008 | 0.0063999 | 2136 | 21638.1311 | 129.6505 | 0.0052359 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9640 | OLEMA 110149756 | 42291101 | OLEMA 1101 | 1727.7805 | 1.0738 | 40 | 0.25449 | 0.0063622 | 2137 | 21639.2049 | 129.396 | 0.0052257 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5813 | PERRY 1101CB | 183071101 | PERRY 1101 | 4085.1757 | 2.539 | 27 | 0.16885 | 0.0062536 | 2138 | 21641.7438 | 129.2271 | 0.0052188 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5598 | FROGTOWN 170236870 | 163451702 | FROGTOWN 1702 | 541.2922 | 0.33642 | 29 | 0.1812 | 0.0062483 | 2139 | 21642.0803 | 129.0459 | 0.0052115 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7823 | FORT BRAGG A 11013113 | 42761101 | FORT BRAGG A 1101 | 16133.333 | 10.0269 | 68 | 0.42396 | 0.0062347 | 2140 | 21652.1072 | 128.622 | 0.0051944 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3839 | PARADISE 11052214 | 102831105 | PARADISE 1105 | 24265.0129 | 15.0808 | 233 | 1.4503 | 0.0062243 | 2141 | 21667.188 | 127.1717 | 0.0051358 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
955 | STANISLAUS 170179826 | 162821701 | STANISLAUS 1701 | 16584.8842 | 10.3076 | 95 | 0.59051 | 0.0062159 | 2142 | 21677.4956 | 126.5812 | 0.005112 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
165 | CHALLENGE 110198174 | 103201101 | CHALLENGE 1101 | 19681.5881 | 12.2322 | 66 | 0.40952 | 0.0062048 | 2143 | 21689.7278 | 126.1717 | 0.0050955 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2120 | BRUNSWICK 110350070 | 152481103 | BRUNSWICK 1103 | 28555.3412 | 17.7473 | 201 | 1.2469 | 0.0062036 | 2144 | 21707.475 | 124.9248 | 0.0050451 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4607 | SARATOGA 1107413816 | 83371107 | SARATOGA 1107 | 17928.3843 | 11.1426 | 104 | 0.64404 | 0.0061927 | 2145 | 21718.6176 | 124.2807 | 0.0050191 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1564 | SAN LUIS OBISPO 1101483444 | 182631101 | SAN LUIS OBISPO 1101 | 3311.0968 | 2.0579 | 67 | 0.4124 | 0.0061552 | 2146 | 21720.6754 | 123.8683 | 0.0050024 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4427 | PLACERVILLE 11118582 | 153081111 | PLACERVILLE 1111 | 15254.7771 | 9.4809 | 163 | 0.99993 | 0.0061345 | 2147 | 21730.1563 | 122.8684 | 0.004962 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9649 | LOS GATOS 1107LA60 | 82021107 | LOS GATOS 1107 | 13957.1729 | 8.6744 | 61 | 0.3737 | 0.0061263 | 2148 | 21738.8308 | 122.4947 | 0.004947 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3992 | VOLTA 11021502 | 102541102 | VOLTA 1102 | 11680.2523 | 7.2593 | 80 | 0.48915 | 0.0061144 | 2149 | 21746.0901 | 122.0056 | 0.0049272 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4576 | VALLEY VIEW 1106CB | 14341106 | VALLEY VIEW 1106 | 6042.2888 | 3.7553 | 50 | 0.30391 | 0.0060781 | 2150 | 21749.8454 | 121.7016 | 0.0049149 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10363 | SAN LEANDRO U 1114653758 | 13111114 | SAN LEANDRO U 1114 | 582.3673 | 0.36194 | 5 | 0.030336 | 0.0060671 | 2151 | 21750.2074 | 121.6713 | 0.0049137 | 121.6713 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7007 | ORO FINO 110238698 | 103031102 | ORO FINO 1102 | 25178.9612 | 15.6488 | 103 | 0.62159 | 0.0060349 | 2152 | 21765.8562 | 121.0497 | 0.0048886 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3531 | HALF MOON BAY 11039112 | 24101103 | HALF MOON BAY 1103 | 1386.5143 | 0.86172 | 68 | 0.40806 | 0.0060009 | 2153 | 21766.7179 | 120.6417 | 0.0048721 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9344 | HALF MOON BAY 1101821698 | 24101101 | HALF MOON BAY 1101 | 1364.9269 | 0.84831 | 9 | 0.054007 | 0.0060008 | 2154 | 21767.5662 | 120.5876 | 0.0048699 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10526 | SANTA ROSA A 1108409621 | 42151108 | SANTA ROSA A 1108 | 219.1314 | 0.13619 | 4 | 0.023977 | 0.0059943 | 2155 | 21767.7024 | 120.5637 | 0.004869 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3796 | CAMP EVERS 210612518 | 83622106 | CAMP EVERS 2106 | 25177.1399 | 15.6477 | 145 | 0.85978 | 0.0059295 | 2156 | 21783.3501 | 119.7039 | 0.0048342 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2601 | BRUNSWICK 11062104 | 152481106 | BRUNSWICK 1106 | 15810.2753 | 9.8261 | 123 | 0.72777 | 0.0059169 | 2157 | 21793.1763 | 118.9761 | 0.0048049 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2204 | OAKHURST 11035470 | 254421103 | OAKHURST 1103 | 14989.8273 | 9.3162 | 104 | 0.61457 | 0.0059093 | 2158 | 21802.4925 | 118.3616 | 0.00478 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2618 | ARVIN 110194892 | 253801101 | ARVIN 1101 | 345.9853 | 0.21503 | 66 | 0.38983 | 0.0059064 | 2159 | 21802.7075 | 117.9717 | 0.0047643 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6041 | CAMP EVERS 210694770 | 83622106 | CAMP EVERS 2106 | 3806.5671 | 2.3658 | 55 | 0.32482 | 0.0059058 | 2160 | 21805.0733 | 117.6469 | 0.0047512 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1981 | COTATI 1105328 | 42271105 | COTATI 1105 | 2414.9476 | 1.5009 | 173 | 1.0175 | 0.0058817 | 2161 | 21806.5742 | 116.6294 | 0.0047101 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
519 | POINT ARENA 110147952 | 43381101 | POINT ARENA 1101 | 16717.6297 | 10.3901 | 88 | 0.51485 | 0.0058506 | 2162 | 21816.9643 | 116.1145 | 0.0046893 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2535 | COTATI 1102825 | 42271102 | COTATI 1102 | 749.4567 | 0.46579 | 26 | 0.15112 | 0.0058122 | 2163 | 21817.4301 | 115.9634 | 0.0046832 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
698 | RESERVATION ROAD 11013026 | 182731101 | RESERVATION ROAD 1101 | 35201.2582 | 21.8777 | 238 | 1.3726 | 0.0057671 | 2164 | 21839.3078 | 114.5908 | 0.0046278 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4296 | MORGAN HILL 2105XR494 | 83242105 | MORGAN HILL 2105 | 737.5052 | 0.45836 | 98 | 0.56354 | 0.0057504 | 2165 | 21839.7662 | 114.0273 | 0.004605 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
875 | FULTON 110777670 | 42561107 | FULTON 1107 | 10874.5833 | 6.7586 | 98 | 0.56305 | 0.0057454 | 2166 | 21846.5248 | 113.4642 | 0.0045823 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2839 | CAMP EVERS 210510294 | 83622105 | CAMP EVERS 2105 | 13501.9938 | 8.3915 | 95 | 0.54194 | 0.0057046 | 2167 | 21854.9163 | 112.9223 | 0.0045604 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4923 | GEYSERVILLE 1101480 | 42891101 | GEYSERVILLE 1101 | 2502.4894 | 1.5553 | 161 | 0.91803 | 0.0057021 | 2168 | 21856.4716 | 112.0043 | 0.0045233 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5117 | WOODSIDE 11018912 | 24251101 | WOODSIDE 1101 | 6268.7877 | 3.8961 | 52 | 0.29627 | 0.0056974 | 2169 | 21860.3677 | 111.708 | 0.0045113 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6008 | GEYSERVILLE 1101482 | 42891101 | GEYSERVILLE 1101 | 595.0555 | 0.36983 | 38 | 0.2155 | 0.0056711 | 2170 | 21860.7375 | 111.4925 | 0.0045026 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3612 | BIG BASIN 110212992 | 82841102 | BIG BASIN 1102 | 22915.4569 | 14.242 | 160 | 0.90521 | 0.0056575 | 2171 | 21874.9796 | 110.5873 | 0.0044661 | 110.5873 | #N/A | #N/A | #N/A | #N/A | #VALUE!
151 | SUMMIT 1102CB | 152591102 | SUMMIT 1102 | 1694.4122 | 1.0531 | 22 | 0.12422 | 0.0056462 | 2172 | 21876.0327 | 110.4631 | 0.0044611 | 110.4631 | #N/A | #N/A | #N/A | #N/A | #VALUE!
585 | LUCERNE 110647198 | 43351106 | LUCERNE 1106 | 4939.462 | 3.0699 | 70 | 0.39345 | 0.0056207 | 2173 | 21879.1026 | 110.0696 | 0.0044452 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7910 | SILVERADO 2105167360 | 43432105 | SILVERADO 2105 | 15413.5909 | 9.5796 | 70 | 0.39281 | 0.0056116 | 2174 | 21888.6822 | 109.6768 | 0.0044293 | 109.6768 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1304 | CURTIS 17028000 | 163351702 | CURTIS 1702 | 23055.4602 | 14.3291 | 174 | 0.97497 | 0.0056032 | 2175 | 21903.0112 | 108.7018 | 0.0043899 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
417 | RALSTON 1101CB | 24141101 | RALSTON 1101 | 606.8044 | 0.37713 | 37 | 0.207 | 0.0055946 | 2176 | 21903.3884 | 108.4948 | 0.0043816 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1975 | RALSTON 11022028 | 24141102 | RALSTON 1102 | 3373.7724 | 2.0968 | 38 | 0.21223 | 0.0055851 | 2177 | 21905.4852 | 108.2826 | 0.004373 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6769 | ATASCADERO 1101A50 | 182541101 | ATASCADERO 1101 | 31118.7087 | 19.3404 | 269 | 1.5011 | 0.0055802 | 2178 | 21924.8256 | 106.7815 | 0.0043124 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2377 | GUALALA 11121294 | 42841112 | GUALALA 1112 | 31953.6798 | 19.8593 | 234 | 1.2961 | 0.0055387 | 2179 | 21944.6849 | 105.4855 | 0.00426 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5858 | FAIRVIEW 2207P150 | 13432207 | FAIRVIEW 2207 | 3652.8381 | 2.2703 | 18 | 0.09937 | 0.0055206 | 2180 | 21946.9552 | 105.3861 | 0.004256 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2861 | PIT NO 5 11011660 | 101321101 | PIT NO 5 1101 | 7855.6793 | 4.8823 | 43 | 0.23729 | 0.0055185 | 2181 | 21951.8375 | 105.1488 | 0.0042464 | 105.1488 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4568 | RINCON 1101CB | 43321101 | RINCON 1101 | 2580.5041 | 1.6038 | 68 | 0.37397 | 0.0054995 | 2182 | 21953.4413 | 104.7748 | 0.0042313 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8511 | SAN ARDO 1101610148 | 182191101 | SAN ARDO 1101 | 3154.5584 | 1.9606 | 58 | 0.31791 | 0.0054812 | 2183 | 21955.4019 | 104.4569 | 0.0042185 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4730 | HARTLEY 110194178 | 43211101 | HARTLEY 1101 | 3457.4484 | 2.1488 | 57 | 0.3113 | 0.0054615 | 2184 | 21957.5507 | 104.1456 | 0.0042059 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1445 | BIG BASIN 1102CB | 82841102 | BIG BASIN 1102 | 9963.4073 | 6.1923 | 59 | 0.31943 | 0.0054141 | 2185 | 21963.743 | 103.8262 | 0.004193 | 103.8262 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6388 | HALF MOON BAY 11036012 | 24101103 | HALF MOON BAY 1103 | 10729.2764 | 6.6683 | 79 | 0.42722 | 0.0054078 | 2186 | 21970.4113 | 103.399 | 0.0041758 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
629 | LAURELES 11112020 | 182371111 | LAURELES 1111 | 55275.2572 | 34.3538 | 281 | 1.5107 | 0.005376 | 2187 | 22004.7651 | 101.8883 | 0.0041148 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3079 | OCEANO 1102V50 | 182601102 | OCEANO 1102 | 11517.5193 | 7.1582 | 107 | 0.57427 | 0.005367 | 2188 | 22011.9233 | 101.3141 | 0.0040916 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
342 | WOODACRE 1101404 | 43021101 | WOODACRE 1101 | 19975.081 | 12.4146 | 152 | 0.81576 | 0.0053668 | 2189 | 22024.3378 | 100.4983 | 0.0040586 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4506 | TIDEWATER 210657926 | 14652106 | TIDEWATER 2106 | 200.7916 | 0.12479 | 97 | 0.51954 | 0.0053561 | 2190 | 22024.4626 | 99.9788 | 0.0040376 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6794 | CAMP EVERS 21055188 | 83622105 | CAMP EVERS 2105 | 3280.6197 | 2.0389 | 19 | 0.10162 | 0.0053482 | 2191 | 22026.5016 | 99.8771 | 0.0040335 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4962 | MONTE RIO 1113652 | 42811113 | MONTE RIO 1113 | 2607.8717 | 1.6208 | 25 | 0.13357 | 0.0053427 | 2192 | 22028.1224 | 99.7436 | 0.0040281 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5950 | COTATI 1102260 | 42271102 | COTATI 1102 | 4317.1662 | 2.6831 | 68 | 0.36316 | 0.0053405 | 2193 | 22030.8055 | 99.3804 | 0.0040135 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2816 | HICKS 2101574315 | 83432101 | HICKS 2101 | 11904.9852 | 7.399 | 78 | 0.4148 | 0.005318 | 2194 | 22038.2045 | 98.9656 | 0.0039967 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4882 | NARROWS 210276952 | 153132102 | NARROWS 2102 | 3648.4496 | 2.2675 | 161 | 0.84337 | 0.0052383 | 2195 | 22040.472 | 98.1222 | 0.0039627 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8374 | SAN JOAQUIN #3 1103501771 | 252531103 | SAN JOAQUIN #3 1103 | 7891.6601 | 4.9047 | 54 | 0.28214 | 0.0052248 | 2196 | 22045.3767 | 97.8401 | 0.0039513 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4446 | OTTER 1101440 | 182941101 | OTTER 1101 | 13392.7701 | 8.3237 | 107 | 0.5515 | 0.0051543 | 2197 | 22053.7004 | 97.2886 | 0.003929 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1813 | PUEBLO 210375612 | 43292103 | PUEBLO 2103 | 0 | 0 | 114 | 0.58294 | 0.0051135 | 2198 | 22053.7004 | 96.7057 | 0.0039055 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3962 | POINT MORETTI 110112122 | 82931101 | POINT MORETTI 1101 | 10570.3766 | 6.5695 | 63 | 0.32133 | 0.0051004 | 2199 | 22060.2699 | 96.3843 | 0.0038925 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6972 | BRUNSWICK 1102940 | 152481102 | BRUNSWICK 1102 | 1911.101 | 1.1878 | 46 | 0.23308 | 0.005067 | 2200 | 22061.4577 | 96.1513 | 0.0038831 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2994 | SHADY GLEN 110132726 | 152431101 | SHADY GLEN 1101 | 19581.5665 | 12.17 | 146 | 0.73876 | 0.00506 | 2201 | 22073.6277 | 95.4125 | 0.0038532 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5931 | EAST QUINCY 11012452 | 102551101 | EAST QUINCY 1101 | 228.5177 | 0.14202 | 87 | 0.43716 | 0.0050248 | 2202 | 22073.7697 | 94.9753 | 0.0038356 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1799 | MORGAN HILL 2105XR578 | 83242105 | MORGAN HILL 2105 | 261.0602 | 0.16225 | 12 | 0.060209 | 0.0050174 | 2203 | 22073.932 | 94.9151 | 0.0038332 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5416 | ANNAPOLIS 1101528344 | 42861101 | ANNAPOLIS 1101 | 43372.0838 | 26.9559 | 171 | 0.85498 | 0.0049999 | 2204 | 22100.8879 | 94.0601 | 0.0037986 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7537 | LOS OSITOS 2102148504 | 182082102 | LOS OSITOS 2102 | 275.7602 | 0.17139 | 14 | 0.069948 | 0.0049963 | 2205 | 22101.0593 | 93.9902 | 0.0037958 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
235 | KONOCTI 11022293 | 43311102 | KONOCTI 1102 | 2820.5709 | 1.753 | 21 | 0.10427 | 0.0049653 | 2206 | 22102.8123 | 93.8859 | 0.0037916 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3072 | ANTLER 1101CB | 103271101 | ANTLER 1101 | 2574.4725 | 1.6 | 18 | 0.088829 | 0.0049349 | 2207 | 22104.4123 | 93.7971 | 0.003788 | 93.7971 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8410 | CAMP EVERS 210611533 | 83622106 | CAMP EVERS 2106 | 4249.6596 | 2.6412 | 28 | 0.13679 | 0.0048855 | 2208 | 22107.0535 | 93.6603 | 0.0037825 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3050 | AUBERRY 1101R324 | 254151101 | AUBERRY 1101 | 17238.3934 | 10.7137 | 119 | 0.5799 | 0.0048731 | 2209 | 22117.7672 | 93.0804 | 0.0037591 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9906 | POINT MORETTI 110183716 | 82931101 | POINT MORETTI 1101 | 4027.3677 | 2.503 | 22 | 0.10689 | 0.0048588 | 2210 | 22120.2703 | 92.9735 | 0.0037547 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5631 | PARADISE 1105878870 | 102831105 | PARADISE 1105 | 4057.446 | 2.5217 | 29 | 0.1404 | 0.0048412 | 2211 | 22122.792 | 92.8331 | 0.0037491 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1901 | MOUNTAIN QUARRIES 21011184 | 152282101 | MOUNTAIN QUARRIES 2101 | 18820.6068 | 11.6971 | 136 | 0.65828 | 0.0048403 | 2212 | 22134.4891 | 92.1748 | 0.0037225 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4871 | BRUNSWICK 11052130 | 152481105 | BRUNSWICK 1105 | 23180.7639 | 14.4069 | 163 | 0.78581 | 0.0048209 | 2213 | 22148.896 | 91.389 | 0.0036908 | 91.389 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10520 | CASTRO VALLEY 1110MR273 | 14091110 | CASTRO VALLEY 1110 | 1164.6083 | 0.72381 | 13 | 0.062294 | 0.0047919 | 2214 | 22149.6198 | 91.3267 | 0.0036882 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9367 | REDBUD 110244119 | 43191102 | REDBUD 1102 | 512.7214 | 0.31866 | 35 | 0.16668 | 0.0047623 | 2215 | 22149.9385 | 91.1601 | 0.0036815 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1147 | STAFFORD 11011082 | 43201101 | STAFFORD 1101 | 2511.2326 | 1.5607 | 36 | 0.17143 | 0.0047619 | 2216 | 22151.4992 | 90.9886 | 0.0036746 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2516 | MIWUK 17028130 | 163661702 | MIWUK 1702 | 15961.1359 | 9.9199 | 123 | 0.5855 | 0.0047602 | 2217 | 22161.4191 | 90.4031 | 0.0036509 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2340 | JESSUP 1102CB | 103441102 | JESSUP 1102 | 159.6823 | 0.099243 | 47 | 0.22372 | 0.0047601 | 2218 | 22161.5184 | 90.1794 | 0.0036419 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10932 | CALPELLA 1102127462 | 43411102 | CALPELLA 1102 | 189.2737 | 0.11763 | 2 | 0.0094316 | 0.0047158 | 2219 | 22161.636 | 90.17 | 0.0036415 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9177 | MORAGA 1105829530 | 13801105 | MORAGA 1105 | 2687.7051 | 1.6704 | 32 | 0.15048 | 0.0047024 | 2220 | 22163.3064 | 90.0195 | 0.0036354 | 90.0195 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1591 | SAN JOAQUIN #3 1101673480 | 252531101 | SAN JOAQUIN #3 1101 | 20487.8392 | 12.7333 | 88 | 0.41346 | 0.0046984 | 2221 | 22176.0397 | 89.606 | 0.0036187 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7450 | WILLOW CREEK 1103CB | 192171103 | WILLOW CREEK 1103 | 6307.2067 | 3.92 | 54 | 0.25202 | 0.0046671 | 2222 | 22179.9596 | 89.354 | 0.0036086 | 89.354 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3048 | LAURELES 1111432 | 182371111 | LAURELES 1111 | 79373.0607 | 49.3307 | 320 | 1.488 | 0.0046501 | 2223 | 22229.2903 | 87.866 | 0.0035485 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9657 | PIT NO 5 1101CB | 101321101 | PIT NO 5 1101 | 1162.2395 | 0.72234 | 10 | 0.046279 | 0.0046279 | 2224 | 22230.0127 | 87.8197 | 0.0035466 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2107 | MIRABEL 110238514 | 42091102 | MIRABEL 1102 | 17257.2473 | 10.7254 | 102 | 0.47021 | 0.0046099 | 2225 | 22240.7381 | 87.3495 | 0.0035276 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4382 | WOODSIDE 11011922 | 24251101 | WOODSIDE 1101 | 7391.7604 | 4.594 | 70 | 0.32116 | 0.004588 | 2226 | 22245.3321 | 87.0283 | 0.0035146 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4539 | LOS GATOS 110760118 | 82021107 | LOS GATOS 1107 | 44902.9478 | 27.9074 | 323 | 1.4785 | 0.0045775 | 2227 | 22273.2395 | 85.5498 | 0.0034549 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8332 | VINEYARD 2108MR172 | 14502108 | VINEYARD 2108 | 856.8002 | 0.5325 | 26 | 0.11876 | 0.0045679 | 2228 | 22273.772 | 85.431 | 0.0034501 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4690 | CORRAL 1103681991 | 162991103 | CORRAL 1103 | 2212.0344 | 1.3748 | 50 | 0.22586 | 0.0045171 | 2229 | 22275.1468 | 85.2052 | 0.003441 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10188 | BOLINAS 11011232 | 42261101 | BOLINAS 1101 | 3637.3088 | 2.2606 | 22 | 0.099054 | 0.0045024 | 2230 | 22277.4074 | 85.1061 | 0.003437 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4590 | REDBUD 11021212 | 43191102 | REDBUD 1102 | 0 | 0 | 62 | 0.2789 | 0.0044984 | 2231 | 22277.4074 | 84.8272 | 0.0034258 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6700 | TIVY VALLEY 1107CB | 252941107 | TIVY VALLEY 1107 | 290.0531 | 0.18027 | 155 | 0.69495 | 0.0044835 | 2232 | 22277.5876 | 84.1323 | 0.0033977 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7824 | CAYUCOS 1102317156 | 182551102 | CAYUCOS 1102 | 3816.311 | 2.3719 | 67 | 0.29506 | 0.0044039 | 2233 | 22279.9595 | 83.8372 | 0.0033858 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9117 | WEST POINT 11021535 | 163201102 | WEST POINT 1102 | 4933.5895 | 3.0662 | 30 | 0.13136 | 0.0043786 | 2234 | 22283.0257 | 83.7058 | 0.0033805 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1000 | MORGAN HILL 2111CB | 83242111 | MORGAN HILL 2111 | 353.0082 | 0.2194 | 38 | 0.16582 | 0.0043636 | 2235 | 22283.2451 | 83.54 | 0.0033738 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9339 | LAKEWOOD 2109432198 FM | 13532109 | LAKEWOOD 2109 | 907.0096 | 0.56371 | 31 | 0.13525 | 0.004363 | 2236 | 22283.8088 | 83.4048 | 0.0033683 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
420 | ARCATA 11225384 | 192021122 | ARCATA 1122 | 25050.2712 | 15.5688 | 202 | 0.88081 | 0.0043604 | 2237 | 22299.3777 | 82.524 | 0.0033327 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
268 | MIRABEL 1102332 | 42091102 | MIRABEL 1102 | 9174.8238 | 5.7022 | 67 | 0.29194 | 0.0043573 | 2238 | 22305.0799 | 82.232 | 0.0033209 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6281 | MONTE RIO 11131989 | 42811113 | MONTE RIO 1113 | 1195.1936 | 0.74282 | 9 | 0.039138 | 0.0043487 | 2239 | 22305.8227 | 82.1929 | 0.0033194 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11081 | OAKHURST 110310723 | 254421103 | OAKHURST 1103 | 6.3415 | 0.0039412 | 1 | 0.0043094 | 0.0043094 | 2240 | 22305.8266 | 82.1886 | 0.0033192 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8151 | SILVERADO 2105309298 | 43432105 | SILVERADO 2105 | 1768.6422 | 1.0992 | 23 | 0.099116 | 0.0043094 | 2241 | 22306.9259 | 82.0895 | 0.0033152 | 82.0895 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4858 | GUALALA 111223444 | 42841112 | GUALALA 1112 | 23380.6907 | 14.5312 | 135 | 0.57599 | 0.0042666 | 2242 | 22321.457 | 81.5135 | 0.0032919 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2658 | CAMP EVERS 210660124 | 83622106 | CAMP EVERS 2106 | 36140.2282 | 22.4613 | 267 | 1.1389 | 0.0042657 | 2243 | 22343.9183 | 80.3745 | 0.0032459 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7144 | BELLEVUE 1102392 | 43181102 | BELLEVUE 1102 | 404.9115 | 0.25165 | 68 | 0.28853 | 0.0042431 | 2244 | 22344.17 | 80.086 | 0.0032343 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5164 | MORAGA 1104N532R | 13801104 | MORAGA 1104 | 5942.762 | 3.6935 | 65 | 0.27482 | 0.004228 | 2245 | 22347.8635 | 79.8112 | 0.0032232 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9096 | BIG BASIN 11022253 | 82841102 | BIG BASIN 1102 | 2335.3363 | 1.4514 | 12 | 0.050377 | 0.0041981 | 2246 | 22349.3149 | 79.7608 | 0.0032211 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4580 | WEST POINT 11021341 | 163201102 | WEST POINT 1102 | 15927.2159 | 9.8988 | 87 | 0.36454 | 0.0041901 | 2247 | 22359.2137 | 79.3962 | 0.0032064 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2630 | MC ARTHUR 110153120 | 103491101 | MC ARTHUR 1101 | 173.1766 | 0.10763 | 92 | 0.38483 | 0.004183 | 2248 | 22359.3213 | 79.0114 | 0.0031909 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9114 | LAS GALLINAS A 1105CB | 42991105 | LAS GALLINAS A 1105 | 710.3038 | 0.44146 | 26 | 0.10768 | 0.0041416 | 2249 | 22359.7628 | 78.9037 | 0.0031865 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2500 | EL DORADO PH 2101CB | 152762101 | EL DORADO PH 2101 | 11999.4505 | 7.4577 | 74 | 0.3064 | 0.0041406 | 2250 | 22367.2205 | 78.5973 | 0.0031742 | 78.5973 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2083 | ALTO 11201214 | 42031120 | ALTO 1120 | 5549.8668 | 3.4493 | 45 | 0.18594 | 0.004132 | 2251 | 22370.6698 | 78.4114 | 0.0031666 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1240 | EL DORADO PH 210126000 | 152762101 | EL DORADO PH 2101 | 55311.5705 | 34.3764 | 339 | 1.3974 | 0.0041222 | 2252 | 22405.0461 | 77.014 | 0.0031102 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2830 | MENLO 11029110 | 24131102 | MENLO 1102 | 1491.4373 | 0.92693 | 138 | 0.55893 | 0.0040502 | 2253 | 22405.9731 | 76.455 | 0.0030876 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8665 | BRUNSWICK 111094368 | 152481110 | BRUNSWICK 1110 | 596.3821 | 0.37065 | 9 | 0.036317 | 0.0040353 | 2254 | 22406.3437 | 76.4187 | 0.0030862 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2181 | MERCED FALLS 110222774 | 252811102 | MERCED FALLS 1102 | 1624.1247 | 1.0094 | 27 | 0.10841 | 0.0040151 | 2255 | 22407.3531 | 76.3103 | 0.0030818 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2725 | BIG BASIN 110212124 | 82841102 | BIG BASIN 1102 | 7217.2962 | 4.4856 | 59 | 0.2367 | 0.0040119 | 2256 | 22411.8387 | 76.0736 | 0.0030722 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1448 | PARADISE 1103CB | 102831103 | PARADISE 1103 | 2217.6155 | 1.3783 | 61 | 0.24245 | 0.0039747 | 2257 | 22413.2169 | 75.8311 | 0.0030624 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3467 | WEIMAR 11012740 | 152491101 | WEIMAR 1101 | 30939.0056 | 19.2287 | 235 | 0.93271 | 0.003969 | 2258 | 22432.4457 | 74.8984 | 0.0030248 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
497 | AUBURN 1101173014 | 152161101 | AUBURN 1101 | 5290.5313 | 3.2881 | 43 | 0.16924 | 0.0039357 | 2259 | 22435.7338 | 74.7292 | 0.0030179 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7194 | WEST POINT 1101L373 | 163201101 | WEST POINT 1101 | 11899.5211 | 7.3956 | 93 | 0.36311 | 0.0039044 | 2260 | 22443.1294 | 74.3661 | 0.0030033 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6474 | STAFFORD 11021048 | 43201102 | STAFFORD 1102 | 8484.8832 | 5.2734 | 72 | 0.28093 | 0.0039018 | 2261 | 22448.4027 | 74.0851 | 0.0029919 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4378 | RESERVATION ROAD 110222136 | 182731102 | RESERVATION ROAD 1102 | 2842.9957 | 1.7669 | 59 | 0.22909 | 0.0038829 | 2262 | 22450.1697 | 73.856 | 0.0029827 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7747 | ANITA 1106552724 | 102841106 | ANITA 1106 | 2363.8176 | 1.4691 | 77 | 0.29791 | 0.0038689 | 2263 | 22451.6388 | 73.5581 | 0.0029706 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6189 | PLACER 1101106534 | 152461101 | PLACER 1101 | 1949.2483 | 1.2115 | 38 | 0.14601 | 0.0038425 | 2264 | 22452.8503 | 73.4121 | 0.0029648 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8134 | MORAGA 110518396 | 13801105 | MORAGA 1105 | 293.2889 | 0.18228 | 16 | 0.061277 | 0.0038298 | 2265 | 22453.0325 | 73.3509 | 0.0029623 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2828 | PANORAMA 11019092 | 103461101 | PANORAMA 1101 | 255.1238 | 0.15856 | 113 | 0.43208 | 0.0038237 | 2266 | 22453.1911 | 72.9188 | 0.0029448 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1451 | MIWUK 1701953336 | 163661701 | MIWUK 1701 | 19079.6136 | 11.8581 | 132 | 0.50381 | 0.0038168 | 2267 | 22465.0492 | 72.415 | 0.0029245 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8189 | CAMP EVERS 210660120 | 83622106 | CAMP EVERS 2106 | 6993.663 | 4.3466 | 42 | 0.16006 | 0.0038109 | 2268 | 22469.3957 | 72.2549 | 0.002918 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3086 | PANOCHE 11034016 | 253671103 | PANOCHE 1103 | 3776.8409 | 2.3473 | 59 | 0.22447 | 0.0038045 | 2269 | 22471.7431 | 72.0304 | 0.002909 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3744 | FORESTHILL 110150486 | 152181101 | FORESTHILL 1101 | 18786.575 | 11.6759 | 163 | 0.61325 | 0.0037623 | 2270 | 22483.419 | 71.4172 | 0.0028842 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1371 | PINE GROVE 11021222 | 163751102 | PINE GROVE 1102 | 27771.0153 | 17.2598 | 218 | 0.81905 | 0.0037571 | 2271 | 22500.6788 | 70.5981 | 0.0028511 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2904 | MONTE RIO 111153477 | 42811111 | MONTE RIO 1111 | 3295.7871 | 2.0483 | 21 | 0.078812 | 0.0037529 | 2272 | 22502.7271 | 70.5193 | 0.0028479 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4467 | RINCON 1102CB | 43321102 | RINCON 1102 | 4772.4685 | 2.9661 | 49 | 0.18233 | 0.0037209 | 2273 | 22505.6933 | 70.337 | 0.0028406 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4949 | BRENTWOOD 210598606 | 14592105 | BRENTWOOD 2105 | 138.4782 | 0.086065 | 88 | 0.32681 | 0.0037138 | 2274 | 22505.7793 | 70.0102 | 0.0028274 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8946 | MIRABEL 110213597 | 42091102 | MIRABEL 1102 | 751.816 | 0.46726 | 6 | 0.022273 | 0.0037122 | 2275 | 22506.2466 | 69.9879 | 0.0028265 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3893 | FAIRVIEW 2207P304 | 13432207 | FAIRVIEW 2207 | 8440.4652 | 5.2458 | 47 | 0.17426 | 0.0037077 | 2276 | 22511.4924 | 69.8137 | 0.0028194 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7178 | BURNEY 11019042 | 103311101 | BURNEY 1101 | 5080.7921 | 3.1577 | 31 | 0.11469 | 0.0036996 | 2277 | 22514.6501 | 69.699 | 0.0028148 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8790 | MONTICELLO 110152910 | 43051101 | MONTICELLO 1101 | 3510.8305 | 2.182 | 41 | 0.1512 | 0.0036877 | 2278 | 22516.8321 | 69.5478 | 0.0028087 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8586 | WEST POINT 1102L3733 | 163201102 | WEST POINT 1102 | 2820.1267 | 1.7527 | 22 | 0.080956 | 0.0036798 | 2279 | 22518.5848 | 69.4668 | 0.0028054 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2143 | VOLTA 11029742 | 102541102 | VOLTA 1102 | 14685.6636 | 9.1272 | 120 | 0.44061 | 0.0036718 | 2280 | 22527.712 | 69.0262 | 0.0027876 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8195 | SAUSALITO 11021268 | 42491102 | SAUSALITO 1102 | 7937.7862 | 4.9334 | 46 | 0.16855 | 0.0036642 | 2281 | 22532.6454 | 68.8577 | 0.0027808 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
200 | PETALUMA C 1109270 | 42631109 | PETALUMA C 1109 | 3397.4138 | 2.1115 | 101 | 0.36934 | 0.0036568 | 2282 | 22534.7569 | 68.4883 | 0.0027659 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9326 | COARSEGOLD 2102383092 | 254432102 | COARSEGOLD 2102 | 613.1926 | 0.3811 | 5 | 0.018173 | 0.0036345 | 2283 | 22535.138 | 68.4701 | 0.0027652 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10306 | SOLEDAD 1114413916 | 182051114 | SOLEDAD 1114 | 2275.8898 | 1.4145 | 24 | 0.086994 | 0.0036248 | 2284 | 22536.5525 | 68.3832 | 0.0027617 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6836 | LLAGAS 2106338878 | 83182106 | LLAGAS 2106 | 3300.0012 | 2.051 | 23 | 0.083266 | 0.0036203 | 2285 | 22538.6034 | 68.2999 | 0.0027583 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
685 | MONTE RIO 1113524 | 42811113 | MONTE RIO 1113 | 10078.6837 | 6.2639 | 76 | 0.2749 | 0.0036171 | 2286 | 22544.8674 | 68.025 | 0.0027472 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3555 | DUNBAR 1103CB | 43071103 | DUNBAR 1103 | 4335.2228 | 2.6944 | 149 | 0.53768 | 0.0036086 | 2287 | 22547.5617 | 67.4873 | 0.0027255 | 67.4873 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6157 | IGNACIO 11041290 | 42481104 | IGNACIO 1104 | 6586.7468 | 4.0937 | 126 | 0.45104 | 0.0035797 | 2288 | 22551.6554 | 67.0363 | 0.0027073 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1177 | ORO FINO 1101CB | 103031101 | ORO FINO 1101 | 35929.6836 | 22.3304 | 271 | 0.96987 | 0.0035789 | 2289 | 22573.9859 | 66.0664 | 0.0026681 | 66.0664 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3178 | PENNGROVE 1101461338 | 43471101 | PENNGROVE 1101 | 2872.7742 | 1.7854 | 24 | 0.085418 | 0.0035591 | 2290 | 22575.7713 | 65.981 | 0.0026646 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3360 | GRASS VALLEY 1101CB | 152031101 | GRASS VALLEY 1101 | 1415.7705 | 0.87991 | 32 | 0.11363 | 0.0035509 | 2291 | 22576.6512 | 65.8673 | 0.0026601 | 65.8673 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10815 | HICKS 2101949522 | 83432101 | HICKS 2101 | 708.2171 | 0.44016 | 2 | 0.0070929 | 0.0035464 | 2292 | 22577.0914 | 65.8603 | 0.0026598 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6548 | WEST POINT 110113444 | 163201101 | WEST POINT 1101 | 27386.8447 | 17.021 | 221 | 0.77919 | 0.0035258 | 2293 | 22594.1124 | 65.0811 | 0.0026283 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2950 | HICKS 2101XR162 | 83432101 | HICKS 2101 | 989.1765 | 0.61478 | 122 | 0.42983 | 0.0035232 | 2294 | 22594.7272 | 64.6512 | 0.0026109 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9560 | VINEYARD 2107246084 | 14502107 | VINEYARD 2107 | 385.2443 | 0.23943 | 7 | 0.024523 | 0.0035033 | 2295 | 22594.9666 | 64.6267 | 0.00261 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3073 | CAMP EVERS 210510728 | 83622105 | CAMP EVERS 2105 | 16852.1183 | 10.4737 | 134 | 0.46719 | 0.0034865 | 2296 | 22605.4403 | 64.1595 | 0.0025911 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7203 | BRUNSWICK 110663124 | 152481106 | BRUNSWICK 1106 | 9481.8427 | 5.893 | 65 | 0.22596 | 0.0034764 | 2297 | 22611.3333 | 63.9336 | 0.002582 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7594 | SHINGLE SPRINGS 2108CB | 153652108 | SHINGLE SPRINGS 2108 | 2376.1029 | 1.4768 | 18 | 0.062504 | 0.0034725 | 2298 | 22612.81 | 63.871 | 0.0025794 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
180 | HIGGINS 11041374 | 152691104 | HIGGINS 1104 | 12470.1527 | 7.7503 | 117 | 0.40592 | 0.0034694 | 2299 | 22620.5603 | 63.4651 | 0.002563 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8764 | TRES PINOS 1111203126 | 183221111 | TRES PINOS 1111 | 107.4611 | 0.066788 | 58 | 0.19963 | 0.0034419 | 2300 | 22620.6271 | 63.2655 | 0.002555 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6133 | SALT SPRINGS 210237300 | 163692102 | SALT SPRINGS 2102 | 11208.5924 | 6.9662 | 41 | 0.14002 | 0.0034152 | 2301 | 22627.5932 | 63.1255 | 0.0025493 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8353 | VOLTA 110254932 | 102541102 | VOLTA 1102 | 7042.6654 | 4.377 | 46 | 0.15706 | 0.0034144 | 2302 | 22631.9703 | 62.9684 | 0.002543 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1504 | HUMBOLDT BAY 1102741980 | 192341102 | HUMBOLDT BAY 1102 | 9241.1429 | 5.7434 | 81 | 0.27592 | 0.0034064 | 2303 | 22637.7137 | 62.6925 | 0.0025318 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
341 | COTATI 1102464 | 42271102 | COTATI 1102 | 3443.5911 | 2.1402 | 103 | 0.35026 | 0.0034005 | 2304 | 22639.8539 | 62.3422 | 0.0025177 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1877 | FORT BRAGG A 110231304 | 42761102 | FORT BRAGG A 1102 | 34880.3162 | 21.6783 | 119 | 0.40289 | 0.0033857 | 2305 | 22661.5322 | 61.9394 | 0.0025014 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9731 | FITCH MOUNTAIN 1111792628 | 42751111 | FITCH MOUNTAIN 1111 | 365.6177 | 0.22723 | 13 | 0.043913 | 0.0033779 | 2306 | 22661.7594 | 61.8954 | 0.0024997 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10338 | FRANKLIN 1104P146 | 13921104 | FRANKLIN 1104 | 5843.5425 | 3.6318 | 36 | 0.12123 | 0.0033674 | 2307 | 22665.3912 | 61.7742 | 0.0024948 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11025 | CALPINE 1144304 | 48011144 | CALPINE 1144 | 74.6067 | 0.046368 | 2 | 0.006711 | 0.0033555 | 2308 | 22665.4376 | 61.7675 | 0.0024945 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7073 | RINCON 1101663641 | 43321101 | RINCON 1101 | 1173.5613 | 0.72937 | 13 | 0.043609 | 0.0033545 | 2309 | 22666.1669 | 61.7239 | 0.0024927 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
37 | CURTIS 17019230 | 163351701 | CURTIS 1701 | 4064.6381 | 2.5262 | 41 | 0.13704 | 0.0033425 | 2310 | 22668.6931 | 61.5868 | 0.0024872 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7129 | GANSNER 1101336664 | 103021101 | GANSNER 1101 | 1158.7417 | 0.72016 | 16 | 0.053319 | 0.0033324 | 2311 | 22669.4133 | 61.5335 | 0.002485 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6003 | CALPELLA 1102477890 | 43411102 | CALPELLA 1102 | 1726.9794 | 1.0733 | 35 | 0.11642 | 0.0033264 | 2312 | 22670.4866 | 61.4171 | 0.0024803 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6936 | LAMONT 11024222 | 253911102 | LAMONT 1102 | 4245.3884 | 2.6385 | 87 | 0.28934 | 0.0033258 | 2313 | 22673.1251 | 61.1278 | 0.0024686 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1031 | VOLTA 110253130 | 102541102 | VOLTA 1102 | 22213.2961 | 13.8057 | 168 | 0.55788 | 0.0033207 | 2314 | 22686.9308 | 60.5699 | 0.0024461 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
729 | RADUM 1105806392 | 13151105 | RADUM 1105 | 5446.9277 | 3.3853 | 79 | 0.26192 | 0.0033155 | 2315 | 22690.3161 | 60.308 | 0.0024355 | 60.308 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6737 | POINT ARENA 1101476 | 43381101 | POINT ARENA 1101 | 4825.127 | 2.9988 | 97 | 0.31915 | 0.0032902 | 2316 | 22693.3149 | 59.9888 | 0.0024227 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9971 | LOS OSITOS 2103258688 | 182082103 | LOS OSITOS 2103 | 1727.2951 | 1.0735 | 17 | 0.0559 | 0.0032882 | 2317 | 22694.3884 | 59.9329 | 0.0024204 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2467 | HARRIS 1109183860 | 192431109 | HARRIS 1109 | 7942.1796 | 4.9361 | 92 | 0.30215 | 0.0032843 | 2318 | 22699.3245 | 59.6308 | 0.0024082 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3741 | PINE GROVE 110152088 | 163751101 | PINE GROVE 1101 | 3986.2342 | 2.4775 | 28 | 0.091793 | 0.0032783 | 2319 | 22701.802 | 59.539 | 0.0024045 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8487 | PIT NO 3 21011482 | 103732101 | PIT NO 3 2101 | 19365.2645 | 12.0356 | 43 | 0.14076 | 0.0032735 | 2320 | 22713.8376 | 59.3982 | 0.0023988 | 59.3982 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9213 | GREEN VALLEY 210197574 | 83192101 | GREEN VALLEY 2101 | 5743.5714 | 3.5697 | 60 | 0.19528 | 0.0032547 | 2321 | 22717.4072 | 59.2029 | 0.0023909 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6945 | CHOLAME 2102X06 | 182562102 | CHOLAME 2102 | 651.9578 | 0.40519 | 40 | 0.13013 | 0.0032533 | 2322 | 22717.8124 | 59.0728 | 0.0023857 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1559 | PAUL SWEET 21065178 | 83252106 | PAUL SWEET 2106 | 11550.9267 | 7.1789 | 84 | 0.27223 | 0.0032408 | 2323 | 22724.9914 | 58.8006 | 0.0023747 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8048 | DEL MONTE 21042762 | 182222104 | DEL MONTE 2104 | 15060.1277 | 9.3599 | 138 | 0.44498 | 0.0032245 | 2324 | 22734.3513 | 58.3556 | 0.0023567 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
394 | WOODSIDE 11049032 | 24251104 | WOODSIDE 1104 | 3452.7748 | 2.1459 | 72 | 0.23216 | 0.0032245 | 2325 | 22736.4972 | 58.1234 | 0.0023473 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3140 | BAYWOOD 1101CB | 182801101 | BAYWOOD 1101 | 7426.5465 | 4.6156 | 214 | 0.6863 | 0.003207 | 2326 | 22741.1128 | 57.4371 | 0.0023196 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
197 | BRUNSWICK 1105733408 | 152481105 | BRUNSWICK 1105 | 5546.1563 | 3.447 | 45 | 0.14429 | 0.0032065 | 2327 | 22744.5598 | 57.2928 | 0.0023138 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1600 | RINCON 1104786782 | 43321104 | RINCON 1104 | 3549.2326 | 2.2059 | 46 | 0.14745 | 0.0032053 | 2328 | 22746.7657 | 57.1454 | 0.0023078 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7931 | PIT NO 5 11011658 | 101321101 | PIT NO 5 1101 | 7306.3402 | 4.5409 | 25 | 0.079597 | 0.0031839 | 2329 | 22751.3066 | 57.0658 | 0.0023046 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4023 | DUNLAP 11037080 | 254061103 | DUNLAP 1103 | 17026.2434 | 10.5819 | 67 | 0.21238 | 0.0031698 | 2330 | 22761.8885 | 56.8534 | 0.002296 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7290 | ARCATA 1121716954 | 192021121 | ARCATA 1121 | 11115.6995 | 6.9085 | 97 | 0.30741 | 0.0031691 | 2331 | 22768.7969 | 56.546 | 0.0022836 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8705 | CARLOTTA 112144150 | 192291121 | CARLOTTA 1121 | 5746.8082 | 3.5717 | 13 | 0.04119 | 0.0031685 | 2332 | 22772.3686 | 56.5048 | 0.0022819 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5063 | WOODSIDE 11043583 | 24251104 | WOODSIDE 1104 | 4565.0094 | 2.8372 | 38 | 0.12014 | 0.0031615 | 2333 | 22775.2057 | 56.3847 | 0.0022771 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8125 | PINE GROVE 1101CB | 163751101 | PINE GROVE 1101 | 6922.9717 | 4.3027 | 57 | 0.17956 | 0.0031502 | 2334 | 22779.5084 | 56.2051 | 0.0022698 | 56.2051 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6730 | CAMP EVERS 210637210 | 83622106 | CAMP EVERS 2106 | 9746.716 | 6.0576 | 65 | 0.20437 | 0.0031442 | 2335 | 22785.566 | 56.0007 | 0.0022616 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
82 | SNEATH LANE 1107CB | 22721107 | SNEATH LANE 1107 | 1615.0564 | 1.0038 | 45 | 0.14045 | 0.003121 | 2336 | 22786.5698 | 55.8603 | 0.0022559 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1487 | STAFFORD 11021258 | 43201102 | STAFFORD 1102 | 501.9247 | 0.31195 | 65 | 0.2027 | 0.0031184 | 2337 | 22786.8817 | 55.6576 | 0.0022477 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
201 | RESERVATION ROAD 1101CB | 182731101 | RESERVATION ROAD 1101 | 8212.888 | 5.1043 | 106 | 0.32923 | 0.0031059 | 2338 | 22791.9861 | 55.3284 | 0.0022344 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9832 | WILLOW CREEK 1101CB | 192171101 | WILLOW CREEK 1101 | 460.8364 | 0.28641 | 6 | 0.018622 | 0.0031037 | 2339 | 22792.2725 | 55.3097 | 0.0022337 | 55.3097 | #N/A | #N/A | #N/A | #N/A | #VALUE!
22 | PARADISE 1104457900 | 102831104 | PARADISE 1104 | 19380.7293 | 12.0452 | 208 | 0.64448 | 0.0030985 | 2340 | 22804.3177 | 54.6653 | 0.0022077 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7703 | SILVERADO 21051306 | 43432105 | SILVERADO 2105 | 393.5916 | 0.24462 | 55 | 0.17016 | 0.0030939 | 2341 | 22804.5623 | 54.4951 | 0.0022008 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8415 | BIG MEADOWS 21012476 | 102812101 | BIG MEADOWS 2101 | 13050.7122 | 8.1111 | 75 | 0.23028 | 0.0030704 | 2342 | 22812.6734 | 54.2648 | 0.0021915 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2480 | REDBUD 1101CB | 43191101 | REDBUD 1101 | 5407.5285 | 3.3608 | 91 | 0.27776 | 0.0030523 | 2343 | 22816.0342 | 53.987 | 0.0021803 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10178 | MAPLE CREEK 1101555034 | 192101101 | MAPLE CREEK 1101 | 2404.9179 | 1.4947 | 8 | 0.024368 | 0.0030461 | 2344 | 22817.5289 | 53.9627 | 0.0021793 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1443 | MENLO 11028952 | 24131102 | MENLO 1102 | 10739.4056 | 6.6746 | 82 | 0.24916 | 0.0030386 | 2345 | 22824.2034 | 53.7135 | 0.0021692 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5316 | PAUL SWEET 210610424 | 83252106 | PAUL SWEET 2106 | 9151.9906 | 5.688 | 87 | 0.26332 | 0.0030267 | 2346 | 22829.8914 | 53.4502 | 0.0021586 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2267 | ELK 11011298 | 42981101 | ELK 1101 | 19969.5788 | 12.4112 | 119 | 0.35978 | 0.0030233 | 2347 | 22842.3026 | 53.0904 | 0.0021441 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6724 | CURTIS 17039210 | 163351703 | CURTIS 1703 | 36192.6146 | 22.4939 | 124 | 0.37459 | 0.0030209 | 2348 | 22864.7965 | 52.7158 | 0.0021289 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3063 | ELECTRA 1101L1697 | 162161101 | ELECTRA 1101 | 9283.5435 | 5.7698 | 70 | 0.21145 | 0.0030208 | 2349 | 22870.5662 | 52.5044 | 0.0021204 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8682 | CLARKSVILLE 210951744 | 153612109 | CLARKSVILLE 2109 | 2099.9047 | 1.3051 | 25 | 0.075372 | 0.0030149 | 2350 | 22871.8713 | 52.429 | 0.0021173 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6410 | SILVERADO 2105616 | 43432105 | SILVERADO 2105 | 798.8754 | 0.4965 | 103 | 0.31016 | 0.0030112 | 2351 | 22872.3678 | 52.1188 | 0.0021048 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2231 | HICKS 2103LB50 | 83432103 | HICKS 2103 | 18130.2581 | 11.268 | 65 | 0.19436 | 0.0029902 | 2352 | 22883.6359 | 51.9245 | 0.002097 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1742 | MIWUK 1701CB | 163661701 | MIWUK 1701 | 26145.2982 | 16.2494 | 187 | 0.55914 | 0.0029901 | 2353 | 22899.8853 | 51.3653 | 0.0020744 | 51.3653 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4916 | SARATOGA 1107167792 | 83371107 | SARATOGA 1107 | 7540.5809 | 4.6865 | 48 | 0.14324 | 0.0029842 | 2354 | 22904.5718 | 51.2221 | 0.0020686 | 51.2221 | #N/A | #N/A | #N/A | #N/A | #VALUE!
55 | CURTIS 170234426 | 163351702 | CURTIS 1702 | 7591.2944 | 4.718 | 81 | 0.24054 | 0.0029697 | 2355 | 22909.2898 | 50.9816 | 0.0020589 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4236 | LOS GATOS 1106LA64 | 82021106 | LOS GATOS 1106 | 20425.5788 | 12.6946 | 152 | 0.4512 | 0.0029684 | 2356 | 22921.9844 | 50.5304 | 0.0020407 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6476 | PAUL SWEET 21068091 | 83252106 | PAUL SWEET 2106 | 9678.478 | 6.0152 | 69 | 0.20457 | 0.0029648 | 2357 | 22927.9996 | 50.3258 | 0.0020324 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7197 | BIG BASIN 110212758 | 82841102 | BIG BASIN 1102 | 9624.9945 | 5.982 | 70 | 0.20629 | 0.002947 | 2358 | 22933.9816 | 50.1195 | 0.0020241 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2069 | BIG BASIN 11025066 | 82841102 | BIG BASIN 1102 | 22120.764 | 13.7481 | 121 | 0.35169 | 0.0029066 | 2359 | 22947.7297 | 49.7678 | 0.0020099 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8715 | OLEMA 1101602 | 42291101 | OLEMA 1101 | 26032.3379 | 16.1792 | 115 | 0.33328 | 0.0028981 | 2360 | 22963.9089 | 49.4345 | 0.0019964 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5548 | ANTLER 11011384 | 103271101 | ANTLER 1101 | 14709.9253 | 9.1423 | 106 | 0.30589 | 0.0028857 | 2361 | 22973.0512 | 49.1286 | 0.0019841 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2497 | ROB ROY 210410714 | 83692104 | ROB ROY 2104 | 22795.5157 | 14.1675 | 212 | 0.61141 | 0.002884 | 2362 | 22987.2187 | 48.5172 | 0.0019594 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2343 | OCEANO 1104CB | 182601104 | OCEANO 1104 | 7352.5883 | 4.5697 | 146 | 0.41777 | 0.0028615 | 2363 | 22991.7883 | 48.0995 | 0.0019425 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7790 | SANTA ROSA A 1111147198 | 42151111 | SANTA ROSA A 1111 | 2173.9439 | 1.3511 | 24 | 0.068464 | 0.0028527 | 2364 | 22993.1395 | 48.031 | 0.0019397 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5803 | BEN LOMOND 04015206 | 83040401 | BEN LOMOND 0401 | 11520.3774 | 7.16 | 78 | 0.22141 | 0.0028387 | 2365 | 23000.2994 | 47.8096 | 0.0019308 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6276 | MONTE RIO 1113202 | 42811113 | MONTE RIO 1113 | 8481.1425 | 5.2711 | 55 | 0.15561 | 0.0028293 | 2366 | 23005.5705 | 47.654 | 0.0019245 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6911 | DEL MONTE 21042624 | 182222104 | DEL MONTE 2104 | 29790.8638 | 18.5151 | 148 | 0.41844 | 0.0028273 | 2367 | 23024.0856 | 47.2355 | 0.0019076 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3771 | CURTIS 170510590 | 163351705 | CURTIS 1705 | 26358.3376 | 16.3818 | 199 | 0.56169 | 0.0028226 | 2368 | 23040.4674 | 46.6738 | 0.0018849 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2714 | MIWUK 1702CB | 163661702 | MIWUK 1702 | 14569.4696 | 9.055 | 110 | 0.30977 | 0.0028161 | 2369 | 23049.5224 | 46.3641 | 0.0018724 | 46.3641 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3825 | SARATOGA 1105LC14 | 83371105 | SARATOGA 1105 | 15879.1839 | 9.869 | 137 | 0.38575 | 0.0028157 | 2370 | 23059.3914 | 45.9783 | 0.0018568 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5150 | HAMILTON BRANCH 11012046 | 102361101 | HAMILTON BRANCH 1101 | 14724.19 | 9.1511 | 57 | 0.1604 | 0.0028141 | 2371 | 23068.5425 | 45.8179 | 0.0018504 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6397 | BRUNSWICK 110584480 | 152481105 | BRUNSWICK 1105 | 7615.7819 | 4.7332 | 50 | 0.14032 | 0.0028064 | 2372 | 23073.2758 | 45.6776 | 0.0018447 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7609 | SAN LUIS OBISPO 1107V58 | 182631107 | SAN LUIS OBISPO 1107 | 1838.4445 | 1.1426 | 25 | 0.069698 | 0.0027879 | 2373 | 23074.4184 | 45.6079 | 0.0018419 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10167 | HAMILTON BRANCH 11012436 | 102361101 | HAMILTON BRANCH 1101 | 8535.8961 | 5.3051 | 19 | 0.052436 | 0.0027598 | 2374 | 23079.7235 | 45.5555 | 0.0018398 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
289 | BIG BASIN 110169550 | 82841101 | BIG BASIN 1101 | 28222.9499 | 17.5407 | 188 | 0.51784 | 0.0027545 | 2375 | 23097.2642 | 45.0376 | 0.0018188 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3662 | SONOMA 1107294 | 42721107 | SONOMA 1107 | 0 | 0 | 66 | 0.18104 | 0.002743 | 2376 | 23097.2642 | 44.8566 | 0.0018115 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6355 | BIG RIVER 11017273 | 43081101 | BIG RIVER 1101 | 10648.4179 | 6.618 | 38 | 0.10415 | 0.0027408 | 2377 | 23103.8822 | 44.7524 | 0.0018073 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7672 | POINT ARENA 11012637 | 43381101 | POINT ARENA 1101 | 6500.6025 | 4.0402 | 28 | 0.076678 | 0.0027385 | 2378 | 23107.9223 | 44.6758 | 0.0018042 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1790 | CAMP EVERS 210510912 | 83622105 | CAMP EVERS 2105 | 7824.9032 | 4.8632 | 54 | 0.14765 | 0.0027343 | 2379 | 23112.7856 | 44.5281 | 0.0017983 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10750 | BOGARD 1101CB | 103301101 | BOGARD 1101 | 830.5012 | 0.51616 | 7 | 0.019049 | 0.0027213 | 2380 | 23113.3017 | 44.5091 | 0.0017975 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6610 | GREEN VALLEY 210112824 | 83192101 | GREEN VALLEY 2101 | 1410.0846 | 0.87637 | 97 | 0.26383 | 0.0027199 | 2381 | 23114.1781 | 44.2452 | 0.0017868 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6375 | HOLLISTER 21054048 | 182492105 | HOLLISTER 2105 | 29209.8997 | 18.1541 | 157 | 0.42694 | 0.0027194 | 2382 | 23132.3322 | 43.8183 | 0.0017696 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
317 | PARADISE 11042206 | 102831104 | PARADISE 1104 | 6659.3031 | 4.1388 | 227 | 0.61291 | 0.0027 | 2383 | 23136.4709 | 43.2054 | 0.0017449 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6305 | WILLOW CREEK 110191926 | 192171101 | WILLOW CREEK 1101 | 10358.7223 | 6.438 | 48 | 0.12929 | 0.0026935 | 2384 | 23142.9089 | 43.0761 | 0.0017396 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5185 | SILVERADO 21023010 | 43432102 | SILVERADO 2102 | 569.5009 | 0.35395 | 106 | 0.28537 | 0.0026922 | 2385 | 23143.2629 | 42.7907 | 0.0017281 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
122 | STANISLAUS 17021888 | 162821702 | STANISLAUS 1702 | 30440.0056 | 18.9186 | 231 | 0.62036 | 0.0026855 | 2386 | 23162.1815 | 42.1704 | 0.0017031 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7468 | ROB ROY 210410298 | 83692104 | ROB ROY 2104 | 17635.9746 | 10.9608 | 138 | 0.37018 | 0.0026825 | 2387 | 23173.1423 | 41.8002 | 0.0016881 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3981 | CAMP EVERS 210510214 | 83622105 | CAMP EVERS 2105 | 22409.5851 | 13.9276 | 149 | 0.39885 | 0.0026769 | 2388 | 23187.0699 | 41.4013 | 0.001672 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4982 | WEST POINT 110136674 | 163201101 | WEST POINT 1101 | 15144.1466 | 9.4121 | 125 | 0.33299 | 0.0026639 | 2389 | 23196.4821 | 41.0683 | 0.0016585 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7345 | WILLOW CREEK 110129362 | 192171101 | WILLOW CREEK 1101 | 12371.5145 | 7.6889 | 74 | 0.19654 | 0.0026559 | 2390 | 23204.171 | 40.8718 | 0.0016506 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8996 | FORT ORD 210637286 | 182402106 | FORT ORD 2106 | 4150.8287 | 2.5798 | 25 | 0.066357 | 0.0026543 | 2391 | 23206.7508 | 40.8054 | 0.0016479 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8063 | COARSEGOLD 210210207 | 254432102 | COARSEGOLD 2102 | 5731.5328 | 3.5622 | 38 | 0.10042 | 0.0026426 | 2392 | 23210.313 | 40.705 | 0.0016439 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4536 | TASSAJARA 2108437582 | 14662108 | TASSAJARA 2108 | 1172.6243 | 0.72879 | 31 | 0.081807 | 0.0026389 | 2393 | 23211.0418 | 40.6232 | 0.0016406 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1013 | CASTRO VALLEY 1108MR337 | 14091108 | CASTRO VALLEY 1108 | 14629.5479 | 9.0923 | 193 | 0.50578 | 0.0026206 | 2394 | 23220.1341 | 40.1174 | 0.0016201 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1167 | BIG BASIN 110195690 | 82841101 | BIG BASIN 1101 | 6226.9882 | 3.8701 | 58 | 0.15175 | 0.0026164 | 2395 | 23224.0042 | 39.9657 | 0.001614 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7588 | IGNACIO 1104450582 | 42481104 | IGNACIO 1104 | 4807.846 | 2.9881 | 50 | 0.13049 | 0.0026097 | 2396 | 23226.9923 | 39.8352 | 0.0016087 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
976 | BRUNSWICK 1103CB | 152481103 | BRUNSWICK 1103 | 2701.0978 | 1.6787 | 82 | 0.21397 | 0.0026094 | 2397 | 23228.671 | 39.6212 | 0.0016001 | 39.6212 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3119 | BIG BASIN 1101CB | 82841101 | BIG BASIN 1101 | 7486.7827 | 4.6531 | 45 | 0.11632 | 0.0025849 | 2398 | 23233.3241 | 39.5049 | 0.0015954 | 39.5049 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8530 | MORRO BAY 1102CB | 183011102 | MORRO BAY 1102 | 7279.8498 | 4.5245 | 36 | 0.092875 | 0.0025799 | 2399 | 23237.8485 | 39.412 | 0.0015917 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1372 | TASSAJARA 2112CB | 14662112 | TASSAJARA 2112 | 279.4297 | 0.17367 | 22 | 0.056746 | 0.0025794 | 2400 | 23238.0222 | 39.3553 | 0.0015894 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1496 | BRUNSWICK 1103173934 | 152481103 | BRUNSWICK 1103 | 17611.7153 | 10.9458 | 125 | 0.32131 | 0.0025705 | 2401 | 23248.968 | 39.034 | 0.0015764 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1818 | MORRO BAY 1101V66 | 183011101 | MORRO BAY 1101 | 5840.07 | 3.6296 | 151 | 0.38811 | 0.0025703 | 2402 | 23252.5976 | 38.6459 | 0.0015607 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3089 | CAMBRIA 1101CB | 182771101 | CAMBRIA 1101 | 415.9182 | 0.25849 | 45 | 0.11523 | 0.0025606 | 2403 | 23252.8561 | 38.5306 | 0.0015561 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3722 | BRUNSWICK 11032784 | 152481103 | BRUNSWICK 1103 | 23592.2379 | 14.6627 | 202 | 0.51568 | 0.0025529 | 2404 | 23267.5187 | 38.0149 | 0.0015352 | 38.0149 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3654 | PENNGROVE 1101247511 | 43471101 | PENNGROVE 1101 | 1938.4111 | 1.2047 | 26 | 0.065929 | 0.0025357 | 2405 | 23268.7235 | 37.949 | 0.0015326 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2397 | MILPITAS 1109XR374 | 82831109 | MILPITAS 1109 | 763.9032 | 0.47477 | 29 | 0.073398 | 0.002531 | 2406 | 23269.1982 | 37.8756 | 0.0015296 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1430 | ANTLER 11011520 | 103271101 | ANTLER 1101 | 14435.9237 | 8.972 | 69 | 0.17381 | 0.002519 | 2407 | 23278.1702 | 37.7018 | 0.0015226 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9020 | EAST QUINCY 1101424048 | 102551101 | EAST QUINCY 1101 | 1068.5882 | 0.66413 | 12 | 0.030204 | 0.002517 | 2408 | 23278.8344 | 37.6716 | 0.0015214 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5728 | HALF MOON BAY 1101CB | 24101101 | HALF MOON BAY 1101 | 2571.5148 | 1.5982 | 80 | 0.20127 | 0.0025158 | 2409 | 23280.4326 | 37.4703 | 0.0015132 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2399 | MONTE RIO 1113477 | 42811113 | MONTE RIO 1113 | 2946.6356 | 1.8313 | 25 | 0.062875 | 0.002515 | 2410 | 23282.2639 | 37.4075 | 0.0015107 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5291 | MIWUK 1702823548 | 163661702 | MIWUK 1702 | 31748.5399 | 19.7318 | 231 | 0.57976 | 0.0025098 | 2411 | 23301.9958 | 36.8277 | 0.0014873 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2843 | PLACERVILLE 111219742 | 153081112 | PLACERVILLE 1112 | 10549.7356 | 6.5567 | 92 | 0.23086 | 0.0025093 | 2412 | 23308.5525 | 36.5968 | 0.001478 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7112 | BELLEVUE 2103646 | 43182103 | BELLEVUE 2103 | 13544.3225 | 8.4179 | 154 | 0.3855 | 0.0025033 | 2413 | 23316.9703 | 36.2113 | 0.0014624 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
637 | DUNBAR 1101160 | 43071101 | DUNBAR 1101 | 4469.2889 | 2.7777 | 77 | 0.19213 | 0.0024952 | 2414 | 23319.748 | 36.0192 | 0.0014546 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
551 | MC KEE 1103XR028 | 83531103 | MC KEE 1103 | 1226.5796 | 0.76232 | 134 | 0.33428 | 0.0024946 | 2415 | 23320.5103 | 35.6849 | 0.0014411 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4532 | RESERVATION ROAD 1102CB | 182731102 | RESERVATION ROAD 1102 | 12591.5795 | 7.8257 | 180 | 0.44438 | 0.0024688 | 2416 | 23328.336 | 35.2405 | 0.0014232 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2736 | ROSSMOOR 110845268 | 14161108 | ROSSMOOR 1108 | 4400.5557 | 2.735 | 112 | 0.27393 | 0.0024458 | 2417 | 23331.071 | 34.9666 | 0.0014121 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4245 | SONOMA 1104914376 | 42721104 | SONOMA 1104 | 862.0577 | 0.53577 | 93 | 0.22569 | 0.0024267 | 2418 | 23331.6068 | 34.7409 | 0.001403 | 34.7409 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9993 | STELLING 1109478699 | 83481109 | STELLING 1109 | 1328.3865 | 0.8256 | 14 | 0.033967 | 0.0024262 | 2419 | 23332.4324 | 34.707 | 0.0014016 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1421 | ORO FINO 11012022 | 103031101 | ORO FINO 1101 | 25888.9554 | 16.0901 | 207 | 0.50113 | 0.0024209 | 2420 | 23348.5225 | 34.2058 | 0.0013814 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4226 | RIO DELL 1102772210 | 192251102 | RIO DELL 1102 | 1329.7793 | 0.82646 | 32 | 0.076733 | 0.0023979 | 2421 | 23349.3489 | 34.1291 | 0.0013783 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3489 | WEIMAR 1101CB | 152491101 | WEIMAR 1101 | 14897.5939 | 9.2589 | 116 | 0.27716 | 0.0023893 | 2422 | 23358.6078 | 33.8519 | 0.0013671 | 33.8519 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9667 | NORTH TOWER 2101CB | 42042101 | NORTH TOWER 2101 | 2179.3543 | 1.3545 | 22 | 0.052462 | 0.0023847 | 2423 | 23359.9623 | 33.7995 | 0.001365 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8228 | GONZALES 1104415382 | 182131104 | GONZALES 1104 | 97.0433 | 0.060313 | 8 | 0.018978 | 0.0023723 | 2424 | 23360.0226 | 33.7805 | 0.0013642 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4259 | DIAMOND SPRINGS 110676088 | 152261106 | DIAMOND SPRINGS 1106 | 17715.9929 | 11.0106 | 124 | 0.29407 | 0.0023715 | 2425 | 23371.0332 | 33.4864 | 0.0013524 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9364 | MIWUK 170236888 | 163661702 | MIWUK 1702 | 977.9121 | 0.60778 | 7 | 0.016592 | 0.0023702 | 2426 | 23371.641 | 33.4698 | 0.0013517 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5480 | PUEBLO 2102647842 | 43292102 | PUEBLO 2102 | 187.7325 | 0.11668 | 6 | 0.014218 | 0.0023697 | 2427 | 23371.7576 | 33.4556 | 0.0013511 | 33.4556 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1607 | MONTE RIO 11133970 | 42811113 | MONTE RIO 1113 | 11750.7224 | 7.3031 | 87 | 0.20565 | 0.0023638 | 2428 | 23379.0608 | 33.25 | 0.0013428 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4343 | BOLINAS 11011236 | 42261101 | BOLINAS 1101 | 5809.1133 | 3.6104 | 34 | 0.080354 | 0.0023633 | 2429 | 23382.6712 | 33.1696 | 0.0013396 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4341 | PLACERVILLE 210623190 | 153082106 | PLACERVILLE 2106 | 5918.813 | 3.6786 | 45 | 0.10591 | 0.0023536 | 2430 | 23386.3497 | 33.0637 | 0.0013353 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6831 | INDIAN FLAT 110410270 | 252691104 | INDIAN FLAT 1104 | 6119.8962 | 3.8035 | 39 | 0.091612 | 0.002349 | 2431 | 23390.1533 | 32.9721 | 0.0013316 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10358 | KONOCTI 11024421 | 43311102 | KONOCTI 1102 | 585.3593 | 0.3638 | 5 | 0.011609 | 0.0023217 | 2432 | 23390.5171 | 32.9605 | 0.0013311 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
822 | PERRY 1101V74 | 183071101 | PERRY 1101 | 6901.1378 | 4.2891 | 61 | 0.14103 | 0.0023119 | 2433 | 23394.8061 | 32.8195 | 0.0013254 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1876 | HATTON 1102CB | 182291102 | HATTON 1102 | 3167.0883 | 1.9684 | 66 | 0.15136 | 0.0022934 | 2434 | 23396.7745 | 32.6681 | 0.0013193 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5363 | BIG BASIN 110110720 | 82841101 | BIG BASIN 1101 | 7578.3102 | 4.71 | 44 | 0.10045 | 0.002283 | 2435 | 23401.4845 | 32.5676 | 0.0013152 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3635 | PERRY 1101V88 | 183071101 | PERRY 1101 | 1732.6065 | 1.0768 | 48 | 0.10934 | 0.002278 | 2436 | 23402.5613 | 32.4583 | 0.0013108 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4348 | SANTA ROSA A 110432180 | 42151104 | SANTA ROSA A 1104 | 3970.2131 | 2.4675 | 36 | 0.081948 | 0.0022763 | 2437 | 23405.0288 | 32.3763 | 0.0013075 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9525 | BIG BASIN 11028403 | 82841102 | BIG BASIN 1102 | 7867.7292 | 4.8898 | 42 | 0.095499 | 0.0022738 | 2438 | 23409.9186 | 32.2808 | 0.0013037 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7227 | SAN RAFAEL 11071415 | 42011107 | SAN RAFAEL 1107 | 1280.0188 | 0.79554 | 14 | 0.031789 | 0.0022706 | 2439 | 23410.7141 | 32.2491 | 0.0013024 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
649 | ORO FINO 11022090 | 103031102 | ORO FINO 1102 | 23726.1931 | 14.7459 | 183 | 0.41496 | 0.0022675 | 2440 | 23425.4601 | 31.8341 | 0.0012856 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2752 | FULTON 1107CB | 42561107 | FULTON 1107 | 875.3178 | 0.54401 | 166 | 0.37591 | 0.0022645 | 2441 | 23426.0041 | 31.4582 | 0.0012704 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8081 | CAMP EVERS 210612840 | 83622106 | CAMP EVERS 2106 | 6323.0478 | 3.9298 | 50 | 0.1129 | 0.002258 | 2442 | 23429.9339 | 31.3453 | 0.0012659 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
365 | PURISIMA 110149394 | 182971101 | PURISIMA 1101 | 1836.8422 | 1.1416 | 111 | 0.24985 | 0.0022509 | 2443 | 23431.0755 | 31.0954 | 0.0012558 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
707 | DEL MONTE 21042760 | 182222104 | DEL MONTE 2104 | 4358.9956 | 2.7091 | 28 | 0.062701 | 0.0022393 | 2444 | 23433.7846 | 31.0327 | 0.0012533 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7540 | LUCERNE 11062327 | 43351106 | LUCERNE 1106 | 1914.889 | 1.1901 | 20 | 0.044762 | 0.0022381 | 2445 | 23434.9747 | 30.988 | 0.0012515 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9432 | GUALALA 1111445166 | 42841111 | GUALALA 1111 | 12164.2635 | 7.5601 | 71 | 0.15871 | 0.0022354 | 2446 | 23442.5349 | 30.8293 | 0.001245 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2414 | PINE GROVE 110245292 | 163751102 | PINE GROVE 1102 | 17350.6047 | 10.7835 | 132 | 0.29501 | 0.002235 | 2447 | 23453.3183 | 30.5342 | 0.0012331 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7039 | IGNACIO 1101CB | 42481101 | IGNACIO 1101 | 2690.5619 | 1.6722 | 19 | 0.042331 | 0.0022279 | 2448 | 23454.9905 | 30.4919 | 0.0012314 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6713 | LAURELES 1112438 | 182371112 | LAURELES 1112 | 8226.4088 | 5.1127 | 48 | 0.10675 | 0.0022241 | 2449 | 23460.1033 | 30.3852 | 0.0012271 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1808 | HARTLEY 1101738 | 43211101 | HARTLEY 1101 | 4208.5049 | 2.6156 | 106 | 0.23488 | 0.0022159 | 2450 | 23462.7189 | 30.1503 | 0.0012176 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9055 | ORO FINO 1102CB | 103031102 | ORO FINO 1102 | 3376.1921 | 2.0983 | 27 | 0.059189 | 0.0021922 | 2451 | 23464.8172 | 30.0911 | 0.0012152 | 30.0911 | #N/A | #N/A | #N/A | #N/A | #VALUE!
500 | ALTO 112278672 | 42031122 | ALTO 1122 | 6078.7898 | 3.778 | 123 | 0.26916 | 0.0021883 | 2452 | 23468.5952 | 29.8219 | 0.0012044 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9919 | MONTE RIO 1113678 | 42811113 | MONTE RIO 1113 | 3004.004 | 1.867 | 17 | 0.037196 | 0.002188 | 2453 | 23470.4622 | 29.7847 | 0.0012029 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8710 | SUMMIT 110186658 | 152591101 | SUMMIT 1101 | 1029.0279 | 0.63954 | 7 | 0.015303 | 0.0021861 | 2454 | 23471.1017 | 29.7694 | 0.0012022 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3183 | PINE GROVE 11011021 | 163751101 | PINE GROVE 1101 | 6702.9103 | 4.1659 | 56 | 0.12161 | 0.0021716 | 2455 | 23475.2676 | 29.6478 | 0.0011973 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3039 | BIG BASIN 110110296 | 82841101 | BIG BASIN 1101 | 23203.5804 | 14.4211 | 181 | 0.3928 | 0.0021702 | 2456 | 23489.6887 | 29.255 | 0.0011815 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10621 | EEL RIVER 1103987714 | 192381103 | EEL RIVER 1103 | 1218.9668 | 0.75759 | 6 | 0.01302 | 0.0021699 | 2457 | 23490.4463 | 29.242 | 0.0011809 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2552 | HALSEY 11022514 | 152241102 | HALSEY 1102 | 17648.4979 | 10.9686 | 212 | 0.45975 | 0.0021687 | 2458 | 23501.4149 | 28.7823 | 0.0011624 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1900 | PLACERVILLE 1111508410 | 153081111 | PLACERVILLE 1111 | 7530.8771 | 4.6805 | 73 | 0.15783 | 0.002162 | 2459 | 23506.0954 | 28.6244 | 0.001156 | 28.6244 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7805 | POINT MORETTI 11015074 | 82931101 | POINT MORETTI 1101 | 2196.7079 | 1.3653 | 34 | 0.073264 | 0.0021548 | 2460 | 23507.4607 | 28.5512 | 0.001153 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9738 | ECHO SUMMIT 1101344250 | 158031101 | ECHO SUMMIT 1101 | 1299.2708 | 0.8075 | 10 | 0.021484 | 0.0021484 | 2461 | 23508.2682 | 28.5297 | 0.0011522 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3248 | HARRIS 1109355914 | 192431109 | HARRIS 1109 | 13002.7807 | 8.0813 | 104 | 0.2233 | 0.0021471 | 2462 | 23516.3495 | 28.3064 | 0.0011432 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5158 | MORRO BAY 1101W20 | 183011101 | MORRO BAY 1101 | 3551.7376 | 2.2074 | 48 | 0.10251 | 0.0021357 | 2463 | 23518.5569 | 28.2039 | 0.001139 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5206 | CAMP EVERS 21065020 | 83622106 | CAMP EVERS 2106 | 24253.1314 | 15.0734 | 185 | 0.3934 | 0.0021265 | 2464 | 23533.6303 | 27.8105 | 0.0011231 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8641 | PETALUMA C 1109857148 | 42631109 | PETALUMA C 1109 | 1503.7135 | 0.93456 | 31 | 0.065491 | 0.0021126 | 2465 | 23534.5649 | 27.745 | 0.0011205 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4750 | PENNGROVE 1101554 | 43471101 | PENNGROVE 1101 | 0 | 0 | 130 | 0.2744 | 0.0021107 | 2466 | 23534.5649 | 27.4706 | 0.0011094 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5805 | PARADISE 110439216 | 102831104 | PARADISE 1104 | 2624.8047 | 1.6313 | 41 | 0.086098 | 0.0021 | 2467 | 23536.1962 | 27.3845 | 0.0011059 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3222 | WEST POINT 11014706 | 163201101 | WEST POINT 1101 | 18429.634 | 11.4541 | 138 | 0.28923 | 0.0020959 | 2468 | 23547.6503 | 27.0953 | 0.0010942 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2065 | EL DORADO PH 21026645 | 152762102 | EL DORADO PH 2102 | 6787.3604 | 4.2184 | 52 | 0.10851 | 0.0020868 | 2469 | 23551.8687 | 26.9867 | 0.0010899 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6903 | VINEYARD 2107MR332 | 14502107 | VINEYARD 2107 | 520.6629 | 0.32359 | 31 | 0.064186 | 0.0020705 | 2470 | 23552.1923 | 26.9226 | 0.0010873 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3802 | MORRO BAY 1102868170 | 183011102 | MORRO BAY 1102 | 14595.2194 | 9.071 | 59 | 0.12083 | 0.0020479 | 2471 | 23561.2632 | 26.8017 | 0.0010824 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3290 | TAR FLAT 04023144 | 163240402 | TAR FLAT 0402 | 7828.9119 | 4.8657 | 58 | 0.11868 | 0.0020462 | 2472 | 23566.1289 | 26.683 | 0.0010776 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9541 | RINCON 1101839669 | 43321101 | RINCON 1101 | 989.219 | 0.6148 | 12 | 0.02446 | 0.0020383 | 2473 | 23566.7437 | 26.6586 | 0.0010766 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
671 | CAMP EVERS 21045096 | 83622104 | CAMP EVERS 2104 | 32680.7032 | 20.3112 | 232 | 0.4728 | 0.0020379 | 2474 | 23587.0549 | 26.1858 | 0.0010575 | 26.1858 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6416 | PLACER 1102CB | 152461102 | PLACER 1102 | 3361.7302 | 2.0893 | 23 | 0.046849 | 0.0020369 | 2475 | 23589.1443 | 26.1389 | 0.0010556 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9674 | GUALALA 1112CB | 42841112 | GUALALA 1112 | 2568.9228 | 1.5966 | 22 | 0.044389 | 0.0020177 | 2476 | 23590.7409 | 26.0946 | 0.0010538 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1510 | MONTE RIO 1113CB | 42811113 | MONTE RIO 1113 | 7286.2366 | 4.5284 | 49 | 0.098667 | 0.0020136 | 2477 | 23595.2693 | 25.9959 | 0.0010498 | 25.9959 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1572 | ECHO SUMMIT 11012500 | 158031101 | ECHO SUMMIT 1101 | 3521.417 | 2.1886 | 26 | 0.05151 | 0.0019811 | 2478 | 23597.4579 | 25.9444 | 0.0010478 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
808 | PEORIA 1701169700 | 163781701 | PEORIA 1701 | 13421.5222 | 8.3415 | 63 | 0.1243 | 0.001973 | 2479 | 23605.7994 | 25.8201 | 0.0010427 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1792 | MORAGA 1102CB | 13801102 | MORAGA 1102 | 8539.83 | 5.3075 | 130 | 0.25639 | 0.0019722 | 2480 | 23611.1069 | 25.5637 | 0.0010324 | 25.5637 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6608 | FORT ROSS 1121134 | 42851121 | FORT ROSS 1121 | 13272.5409 | 8.2489 | 99 | 0.19475 | 0.0019671 | 2481 | 23619.3559 | 25.3689 | 0.0010245 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5795 | HIGGINS 1103995672 | 152691103 | HIGGINS 1103 | 5928.6387 | 3.6847 | 79 | 0.15487 | 0.0019604 | 2482 | 23623.0405 | 25.2141 | 0.0010183 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7320 | FAIRVIEW 220799096 | 13432207 | FAIRVIEW 2207 | 15895.8244 | 9.8793 | 56 | 0.10978 | 0.0019603 | 2483 | 23632.9199 | 25.1043 | 0.0010138 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1460 | PARADISE 1105121988 | 102831105 | PARADISE 1105 | 11219.1712 | 6.9728 | 92 | 0.17929 | 0.0019488 | 2484 | 23639.8926 | 24.925 | 0.0010066 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
223 | ROB ROY 210410960 | 83692104 | ROB ROY 2104 | 30132.5387 | 18.7275 | 320 | 0.62252 | 0.0019454 | 2485 | 23658.6201 | 24.3025 | 0.00098146 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9882 | VOLTA 1102453266 | 102541102 | VOLTA 1102 | 510.1509 | 0.31706 | 5 | 0.0096562 | 0.0019312 | 2486 | 23658.9372 | 24.2928 | 0.00098107 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2825 | COTATI 1104CB | 42271104 | COTATI 1104 | 7279.3949 | 4.5242 | 93 | 0.17769 | 0.0019107 | 2487 | 23663.4613 | 24.1151 | 0.00097389 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9868 | VOLTA 110293418 | 102541102 | VOLTA 1102 | 4145.9232 | 2.5767 | 23 | 0.043787 | 0.0019038 | 2488 | 23666.0381 | 24.0713 | 0.00097212 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7915 | LOS GATOS 1106697500 | 82021106 | LOS GATOS 1106 | 10836.6474 | 6.735 | 74 | 0.14082 | 0.0019029 | 2489 | 23672.7731 | 23.9305 | 0.00096644 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9296 | DUNBAR 1103835658 | 43071103 | DUNBAR 1103 | 50.0391 | 0.0311 | 11 | 0.020885 | 0.0018987 | 2490 | 23672.8042 | 23.9096 | 0.00096559 | 23.9096 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6742 | ALTO 11251158 | 42031125 | ALTO 1125 | 3588.3989 | 2.2302 | 65 | 0.12337 | 0.0018981 | 2491 | 23675.0344 | 23.7863 | 0.00096061 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4000 | RINCON 1101576 | 43321101 | RINCON 1101 | 1582.5592 | 0.98357 | 116 | 0.21618 | 0.0018636 | 2492 | 23676.0179 | 23.5701 | 0.00095188 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4995 | SOLEDAD 21027008 | 182052102 | SOLEDAD 2102 | 8088.7008 | 5.0272 | 122 | 0.22537 | 0.0018473 | 2493 | 23681.0451 | 23.3447 | 0.00094278 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6887 | HATTON 1102648928 | 182291102 | HATTON 1102 | 6359.2353 | 3.9523 | 44 | 0.081123 | 0.0018437 | 2494 | 23684.9974 | 23.2636 | 0.0009395 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9513 | GREEN VALLEY 2101535998 | 83192101 | GREEN VALLEY 2101 | 7140.4635 | 4.4378 | 43 | 0.079178 | 0.0018414 | 2495 | 23689.4352 | 23.1844 | 0.0009363 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2632 | APPLE HILL 110412947 | 153661104 | APPLE HILL 1104 | 5709.2465 | 3.5483 | 49 | 0.0901 | 0.0018388 | 2496 | 23692.9835 | 23.0943 | 0.00093266 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7783 | MIRABEL 110257840 | 42091102 | MIRABEL 1102 | 4238.9331 | 2.6345 | 29 | 0.053161 | 0.0018331 | 2497 | 23695.6181 | 23.0411 | 0.00093052 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
26 | TASSAJARA 2103CB | 14662103 | TASSAJARA 2103 | 787.8623 | 0.48966 | 259 | 0.47354 | 0.0018283 | 2498 | 23696.1077 | 22.5676 | 0.00091139 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8978 | BIG RIVER 1101954 | 43081101 | BIG RIVER 1101 | 12372.699 | 7.6897 | 78 | 0.1423 | 0.0018244 | 2499 | 23703.7974 | 22.4253 | 0.00090565 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
85 | HALSEY 11011704 | 152241101 | HALSEY 1101 | 21231.8185 | 13.1957 | 160 | 0.29168 | 0.001823 | 2500 | 23716.9931 | 22.1336 | 0.00089387 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2388 | CAMP EVERS 21059031 | 83622105 | CAMP EVERS 2105 | 1741.4201 | 1.0823 | 17 | 0.030932 | 0.0018195 | 2501 | 23718.0754 | 22.1027 | 0.00089262 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2038 | MORAGA 1104CB | 13801104 | MORAGA 1104 | 15741.0344 | 9.7831 | 214 | 0.38772 | 0.0018118 | 2502 | 23727.8585 | 21.715 | 0.00087696 | 21.715 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6140 | OCEANO 1106V28 | 182601106 | OCEANO 1106 | 1958.2873 | 1.2171 | 99 | 0.17873 | 0.0018053 | 2503 | 23729.0756 | 21.5362 | 0.00086974 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9346 | LAURELES 11116421 | 182371111 | LAURELES 1111 | 2777.3682 | 1.7261 | 20 | 0.036089 | 0.0018044 | 2504 | 23730.8017 | 21.5002 | 0.00086829 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
680 | CAMP EVERS 210612760 | 83622106 | CAMP EVERS 2106 | 42462.3954 | 26.3906 | 299 | 0.53531 | 0.0017903 | 2505 | 23757.1923 | 20.9648 | 0.00084667 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1725 | BOLINAS 1101CB | 42261101 | BOLINAS 1101 | 3442.3441 | 2.1394 | 26 | 0.04631 | 0.0017811 | 2506 | 23759.3317 | 20.9185 | 0.0008448 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1486 | BEN LOMOND 1101BL 1101 | 83041101 | BEN LOMOND 1101 | 13568.3761 | 8.4328 | 101 | 0.17858 | 0.0017681 | 2507 | 23767.7645 | 20.74 | 0.00083758 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8439 | OAKHURST 110310190 | 254421103 | OAKHURST 1103 | 13591.0884 | 8.4469 | 61 | 0.10725 | 0.0017583 | 2508 | 23776.2114 | 20.6327 | 0.00083325 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10411 | BURNEY 1102272636 | 103311102 | BURNEY 1102 | 431.3681 | 0.2681 | 5 | 0.0087708 | 0.0017542 | 2509 | 23776.4795 | 20.6239 | 0.0008329 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9794 | SONOMA 1106510055 | 42721106 | SONOMA 1106 | 817.6203 | 0.50815 | 11 | 0.019238 | 0.0017489 | 2510 | 23776.9877 | 20.6047 | 0.00083212 | 20.6047 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1870 | TEMPLETON 2110307832 | 183052110 | TEMPLETON 2110 | 2614.1136 | 1.6247 | 133 | 0.23192 | 0.0017438 | 2511 | 23778.6123 | 20.3728 | 0.00082276 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4149 | EL DORADO PH 210219542 | 152762102 | EL DORADO PH 2102 | 15319.5774 | 9.5212 | 111 | 0.19285 | 0.0017374 | 2512 | 23788.1335 | 20.1799 | 0.00081497 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5394 | BRUNSWICK 11052100 | 152481105 | BRUNSWICK 1105 | 6391.6672 | 3.9724 | 47 | 0.081621 | 0.0017366 | 2513 | 23792.106 | 20.0983 | 0.00081167 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7138 | MONTE RIO 11138299 | 42811113 | MONTE RIO 1113 | 1934.2169 | 1.2021 | 13 | 0.02235 | 0.0017192 | 2514 | 23793.3081 | 20.076 | 0.00081077 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2315 | MORAGA 1101108540 | 13801101 | MORAGA 1101 | 7751.409 | 4.8175 | 44 | 0.075547 | 0.001717 | 2515 | 23798.1256 | 20.0004 | 0.00080772 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
110 | RACETRACK 17038120 | 163761703 | RACETRACK 1703 | 14371.6326 | 8.932 | 108 | 0.18434 | 0.0017068 | 2516 | 23807.0576 | 19.8161 | 0.00080027 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1996 | MORAGA 1103E510R | 13801103 | MORAGA 1103 | 807.8365 | 0.50207 | 84 | 0.14305 | 0.0017029 | 2517 | 23807.5597 | 19.673 | 0.0007945 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2784 | FRENCH GULCH 11022902 | 103381102 | FRENCH GULCH 1102 | 11242.8228 | 6.9875 | 8 | 0.013563 | 0.0016954 | 2518 | 23814.5472 | 19.6595 | 0.00079395 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4648 | HALF MOON BAY 1102863822 | 24101102 | HALF MOON BAY 1102 | 168.7519 | 0.10488 | 8 | 0.013546 | 0.0016933 | 2519 | 23814.6521 | 19.6459 | 0.0007934 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4537 | LAKEWOOD 2107396264 | 13532107 | LAKEWOOD 2107 | 7704.2 | 4.7882 | 95 | 0.16081 | 0.0016927 | 2520 | 23819.4403 | 19.4851 | 0.00078691 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6727 | BRUNSWICK 11032200 | 152481103 | BRUNSWICK 1103 | 8965.9106 | 5.5723 | 64 | 0.10808 | 0.0016888 | 2521 | 23825.0126 | 19.377 | 0.00078254 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5446 | PENRYN 11052406 | 152561105 | PENRYN 1105 | 123.5636 | 0.076795 | 50 | 0.084272 | 0.0016854 | 2522 | 23825.0894 | 19.2928 | 0.00077914 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9065 | OTTER 11017611 | 182941101 | OTTER 1101 | 7068.0362 | 4.3928 | 42 | 0.070701 | 0.0016834 | 2523 | 23829.4822 | 19.2221 | 0.00077628 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4321 | BRUNSWICK 110633050 | 152481106 | BRUNSWICK 1106 | 1793.1664 | 1.1145 | 56 | 0.094072 | 0.0016799 | 2524 | 23830.5967 | 19.128 | 0.00077248 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7573 | ROSSMOOR 110639424 | 14161106 | ROSSMOOR 1106 | 1481.6598 | 0.92086 | 36 | 0.060313 | 0.0016754 | 2525 | 23831.5175 | 19.0677 | 0.00077005 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1005 | ROB ROY 21045082 | 83692104 | ROB ROY 2104 | 32012.7007 | 19.896 | 215 | 0.35844 | 0.0016672 | 2526 | 23851.4135 | 18.7092 | 0.00075557 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5885 | LAURELES 11122768 | 182371112 | LAURELES 1112 | 10109.7249 | 6.2832 | 92 | 0.15315 | 0.0016647 | 2527 | 23857.6968 | 18.5561 | 0.00074939 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2281 | VOLTA 110185234 | 102541101 | VOLTA 1101 | 12730.8347 | 7.9123 | 92 | 0.15202 | 0.0016524 | 2528 | 23865.609 | 18.404 | 0.00074325 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3545 | PACIFICA 1104230272 | 22811104 | PACIFICA 1104 | 1377.39 | 0.85605 | 18 | 0.029673 | 0.0016485 | 2529 | 23866.4651 | 18.3744 | 0.00074205 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6564 | NEWBURG 1131557468 | 192151131 | NEWBURG 1131 | 1423.6732 | 0.88482 | 28 | 0.046129 | 0.0016475 | 2530 | 23867.3499 | 18.3282 | 0.00074019 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2123 | IGNACIO 11011300 | 42481101 | IGNACIO 1101 | 5145.088 | 3.1977 | 84 | 0.13814 | 0.0016445 | 2531 | 23870.5476 | 18.1901 | 0.00073461 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7516 | SAN LUIS OBISPO 1107CB | 182631107 | SAN LUIS OBISPO 1107 | 1251.1033 | 0.77757 | 19 | 0.031229 | 0.0016436 | 2532 | 23871.3252 | 18.1589 | 0.00073335 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1994 | SILVERADO 2103218894 | 43432103 | SILVERADO 2103 | 540.1994 | 0.33574 | 14 | 0.022819 | 0.00163 | 2533 | 23871.6609 | 18.1361 | 0.00073243 | 18.1361 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10204 | DUNBAR 110113481 | 43071101 | DUNBAR 1101 | 0 | 0 | 14 | 0.022805 | 0.0016289 | 2534 | 23871.6609 | 18.1133 | 0.0007315 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3837 | AUBERRY 1101D4982 | 254151101 | AUBERRY 1101 | 4312.861 | 2.6805 | 21 | 0.034121 | 0.0016248 | 2535 | 23874.3414 | 18.0791 | 0.00073013 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
586 | WEIMAR 11022038 | 152491102 | WEIMAR 1102 | 21510.9233 | 13.3691 | 155 | 0.2504 | 0.0016155 | 2536 | 23887.7105 | 17.8287 | 0.00072001 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5218 | SYCAMORE CREEK 11112268 | 102971111 | SYCAMORE CREEK 1111 | 35117.3516 | 21.8256 | 217 | 0.34805 | 0.0016039 | 2537 | 23909.5361 | 17.4807 | 0.00070596 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1040 | GANSNER 110152664 | 103021101 | GANSNER 1101 | 284.4033 | 0.17676 | 44 | 0.070524 | 0.0016028 | 2538 | 23909.7128 | 17.4102 | 0.00070311 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3804 | POINT MORETTI 110110726 | 82931101 | POINT MORETTI 1101 | 16936.721 | 10.5262 | 124 | 0.19849 | 0.0016007 | 2539 | 23920.2391 | 17.2117 | 0.00069509 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1389 | STANISLAUS 17011331 | 162821701 | STANISLAUS 1701 | 7064.7733 | 4.3908 | 63 | 0.10065 | 0.0015977 | 2540 | 23924.6299 | 17.111 | 0.00069103 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8302 | VALLEY VIEW 1106P166 | 14341106 | VALLEY VIEW 1106 | 7068.5222 | 4.3931 | 27 | 0.043133 | 0.0015975 | 2541 | 23929.023 | 17.0679 | 0.00068929 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7677 | POINT MORETTI 110136516 | 82931101 | POINT MORETTI 1101 | 6699.7019 | 4.1639 | 53 | 0.08431 | 0.0015908 | 2542 | 23933.1869 | 16.9836 | 0.00068588 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9231 | ROB ROY 21045304 | 83692104 | ROB ROY 2104 | 5763.285 | 3.5819 | 60 | 0.094707 | 0.0015784 | 2543 | 23936.7688 | 16.8889 | 0.00068206 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10838 | LAS GALLINAS A 1106685852 | 42991106 | LAS GALLINAS A 1106 | 104.9331 | 0.065216 | 3 | 0.0046945 | 0.0015648 | 2544 | 23936.834 | 16.8842 | 0.00068187 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1125 | LAS GALLINAS A 1106CB | 42991106 | LAS GALLINAS A 1106 | 153.7468 | 0.095554 | 111 | 0.17365 | 0.0015644 | 2545 | 23936.9295 | 16.7105 | 0.00067486 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6613 | HICKS 111660050 | 83431116 | HICKS 1116 | 13116.246 | 8.1518 | 98 | 0.15235 | 0.0015546 | 2546 | 23945.0813 | 16.5582 | 0.0006687 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10410 | PUEBLO 2102391312 | 43292102 | PUEBLO 2102 | 229.6394 | 0.14272 | 13 | 0.020186 | 0.0015528 | 2547 | 23945.2241 | 16.538 | 0.00066789 | 16.538 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3988 | SAN RAFAEL 1108322 | 42011108 | SAN RAFAEL 1108 | 11550.5948 | 7.1787 | 88 | 0.13618 | 0.0015474 | 2548 | 23952.4028 | 16.4018 | 0.00066239 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3811 | OAKLAND X 1106950688 | 12541106 | OAKLAND X 1106 | 5883.5054 | 3.6566 | 50 | 0.077034 | 0.0015407 | 2549 | 23956.0594 | 16.3248 | 0.00065928 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1254 | CURTIS 17039240 | 163351703 | CURTIS 1703 | 17656.496 | 10.9736 | 151 | 0.23246 | 0.0015394 | 2550 | 23967.033 | 16.0923 | 0.00064989 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9703 | VOLTA 110280982 | 102541102 | VOLTA 1102 | 836.5231 | 0.5199 | 8 | 0.012305 | 0.0015382 | 2551 | 23967.5529 | 16.08 | 0.00064939 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8204 | BEN LOMOND 04015144 | 83040401 | BEN LOMOND 0401 | 6368.9288 | 3.9583 | 36 | 0.055061 | 0.0015295 | 2552 | 23971.5112 | 16.025 | 0.00064717 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4922 | BIG RIVER 11013019 | 43081101 | BIG RIVER 1101 | 426.9368 | 0.26534 | 11 | 0.016682 | 0.0015165 | 2553 | 23971.7766 | 16.0083 | 0.00064649 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4844 | SANTA ROSA A 1104173590 | 42151104 | SANTA ROSA A 1104 | 6901.197 | 4.2891 | 46 | 0.069603 | 0.0015131 | 2554 | 23976.0657 | 15.9387 | 0.00064368 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7483 | FLINT 1101CB | 152531101 | FLINT 1101 | 1037.2766 | 0.64467 | 36 | 0.054259 | 0.0015072 | 2555 | 23976.7104 | 15.8844 | 0.00064149 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6669 | DUNBAR 1101234 | 43071101 | DUNBAR 1101 | 5584.5077 | 3.4708 | 81 | 0.12191 | 0.0015051 | 2556 | 23980.1812 | 15.7625 | 0.00063657 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7886 | OAKHURST 1102CB | 254421102 | OAKHURST 1102 | 4253.8822 | 2.6438 | 61 | 0.091479 | 0.0014997 | 2557 | 23982.825 | 15.671 | 0.00063287 | 15.671 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1710 | ELK 110191336 | 42981101 | ELK 1101 | 12740.7114 | 7.9184 | 78 | 0.11676 | 0.0014969 | 2558 | 23990.7434 | 15.5543 | 0.00062816 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
583 | MONTE RIO 1111969182 | 42811111 | MONTE RIO 1111 | 8578.2654 | 5.3314 | 64 | 0.095599 | 0.0014937 | 2559 | 23996.0748 | 15.4587 | 0.0006243 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3182 | KONOCTI 1108950 | 43311108 | KONOCTI 1108 | 9978.6098 | 6.2017 | 85 | 0.12697 | 0.0014937 | 2560 | 24002.2765 | 15.3317 | 0.00061917 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5332 | CLAYTON 2212CB | 12022212 | CLAYTON 2212 | 1899.4744 | 1.1805 | 140 | 0.20851 | 0.0014894 | 2561 | 24003.4571 | 15.1232 | 0.00061075 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4270 | LAS GALLINAS A 1104304 | 42991104 | LAS GALLINAS A 1104 | 221.043 | 0.13738 | 27 | 0.039953 | 0.0014798 | 2562 | 24003.5945 | 15.0832 | 0.00060914 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
886 | SALT SPRINGS 21024796 | 163692102 | SALT SPRINGS 2102 | 11571.4706 | 7.1917 | 114 | 0.16766 | 0.0014707 | 2563 | 24010.7862 | 14.9156 | 0.00060237 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1846 | BIG RIVER 11013002 | 43081101 | BIG RIVER 1101 | 11656.2739 | 7.2444 | 76 | 0.11126 | 0.001464 | 2564 | 24018.0306 | 14.8043 | 0.00059787 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6005 | MIRABEL 1101201156 | 42091101 | MIRABEL 1101 | 2335.0863 | 1.4513 | 26 | 0.038044 | 0.0014632 | 2565 | 24019.4819 | 14.7663 | 0.00059634 | 14.7663 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9286 | SOLEDAD 2101315500 | 182052101 | SOLEDAD 2101 | 1783.0288 | 1.1082 | 22 | 0.032073 | 0.0014578 | 2566 | 24020.59 | 14.7342 | 0.00059504 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2001 | SAN RAFAEL 110839156 | 42011108 | SAN RAFAEL 1108 | 5580.9258 | 3.4686 | 62 | 0.089693 | 0.0014467 | 2567 | 24024.0586 | 14.6445 | 0.00059142 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2593 | HIGGINS 1104533648 | 152691104 | HIGGINS 1104 | 10867.8258 | 6.7544 | 93 | 0.13321 | 0.0014323 | 2568 | 24030.813 | 14.5113 | 0.00058604 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2853 | EL DORADO PH 2101668674 | 152762101 | EL DORADO PH 2101 | 15298.6549 | 9.5082 | 112 | 0.16003 | 0.0014289 | 2569 | 24040.3212 | 14.3513 | 0.00057958 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
701 | CAMP EVERS 210512590 | 83622105 | CAMP EVERS 2105 | 8233.9726 | 5.1174 | 69 | 0.09844 | 0.0014267 | 2570 | 24045.4386 | 14.2528 | 0.0005756 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9206 | SISQUOC 110245261 | 182811102 | SISQUOC 1102 | 164.9958 | 0.10255 | 10 | 0.01423 | 0.001423 | 2571 | 24045.5411 | 14.2386 | 0.00057503 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6505 | MONTE RIO 11131313 | 42811113 | MONTE RIO 1113 | 1996.4298 | 1.2408 | 19 | 0.026709 | 0.0014057 | 2572 | 24046.7819 | 14.2119 | 0.00057395 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4406 | COTATI 110475972 | 42271104 | COTATI 1104 | 5386.1403 | 3.3475 | 61 | 0.085021 | 0.0013938 | 2573 | 24050.1294 | 14.1269 | 0.00057051 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7967 | MENLO 11038982 | 24131103 | MENLO 1103 | 7434.3823 | 4.6205 | 50 | 0.06964 | 0.0013928 | 2574 | 24054.7499 | 14.0572 | 0.0005677 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9897 | ORO FINO 110239154 | 103031102 | ORO FINO 1102 | 1419.8889 | 0.88247 | 11 | 0.015315 | 0.0013923 | 2575 | 24055.6324 | 14.0419 | 0.00056708 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5536 | GUALALA 1111CB | 42841111 | GUALALA 1111 | 6227.6638 | 3.8705 | 47 | 0.065391 | 0.0013913 | 2576 | 24059.5029 | 13.9765 | 0.00056444 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3869 | PINE GROVE 11021765 | 163751102 | PINE GROVE 1102 | 2336.7952 | 1.4523 | 20 | 0.027774 | 0.0013887 | 2577 | 24060.9553 | 13.9487 | 0.00056332 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2705 | FORT ORD 210736596 | 182402107 | FORT ORD 2107 | 6572.3951 | 4.0848 | 145 | 0.20079 | 0.0013847 | 2578 | 24065.04 | 13.7479 | 0.00055521 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5302 | BIG BASIN 11015000 | 82841101 | BIG BASIN 1101 | 3149.0186 | 1.9571 | 23 | 0.031772 | 0.0013814 | 2579 | 24066.9972 | 13.7162 | 0.00055393 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10692 | ROSSMOOR 1109CB | 14161109 | ROSSMOOR 1109 | 7.571 | 0.0047054 | 6 | 0.0079259 | 0.001321 | 2580 | 24067.0019 | 13.7082 | 0.00055361 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5396 | FORT BRAGG A 11041316 | 42761104 | FORT BRAGG A 1104 | 22101.0688 | 13.7359 | 166 | 0.21786 | 0.0013124 | 2581 | 24080.7378 | 13.4904 | 0.00054481 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6380 | GUALALA 111135562 | 42841111 | GUALALA 1111 | 22914.0776 | 14.2412 | 147 | 0.19119 | 0.0013006 | 2582 | 24094.979 | 13.2992 | 0.00053709 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5878 | OLEMA 11011318 | 42291101 | OLEMA 1101 | 13693.4076 | 8.5105 | 113 | 0.14661 | 0.0012974 | 2583 | 24103.4895 | 13.1526 | 0.00053117 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7013 | SALT SPRINGS 2102L491 | 163692102 | SALT SPRINGS 2102 | 3564.5514 | 2.2154 | 31 | 0.039999 | 0.0012903 | 2584 | 24105.7048 | 13.1126 | 0.00052955 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3314 | LLAGAS 2101XR244 | 83182101 | LLAGAS 2101 | 0 | 0 | 157 | 0.20135 | 0.0012825 | 2585 | 24105.7048 | 12.9112 | 0.00052142 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
595 | GARBERVILLE 1103CB | 192221103 | GARBERVILLE 1103 | 971.3906 | 0.60372 | 31 | 0.039451 | 0.0012726 | 2586 | 24106.3086 | 12.8718 | 0.00051983 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
842 | ELK 11011272 | 42981101 | ELK 1101 | 35548.517 | 22.0935 | 236 | 0.29926 | 0.0012681 | 2587 | 24128.4021 | 12.5725 | 0.00050774 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3308 | SNEATH LANE 1106CB | 22721106 | SNEATH LANE 1106 | 4885.2685 | 3.0362 | 66 | 0.083532 | 0.0012656 | 2588 | 24131.4383 | 12.489 | 0.00050437 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4674 | WEST POINT 110112256 | 163201101 | WEST POINT 1101 | 10425.1159 | 6.4793 | 86 | 0.10855 | 0.0012622 | 2589 | 24137.9176 | 12.3804 | 0.00049998 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
141 | MORRO BAY 1102W34 | 183011102 | MORRO BAY 1102 | 12223.0154 | 7.5967 | 112 | 0.14094 | 0.0012584 | 2590 | 24145.5142 | 12.2395 | 0.00049429 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8023 | HOLLISTER 2105903238 | 182492105 | HOLLISTER 2105 | 6450.8713 | 4.0092 | 30 | 0.037741 | 0.001258 | 2591 | 24149.5235 | 12.2018 | 0.00049277 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
53 | DUNBAR 1102448 | 43071102 | DUNBAR 1102 | 3932.5973 | 2.4441 | 116 | 0.1457 | 0.001256 | 2592 | 24151.9676 | 12.0561 | 0.00048688 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5111 | ALHAMBRA 110581514 | 14101105 | ALHAMBRA 1105 | 4781.286 | 2.9716 | 65 | 0.08141 | 0.0012525 | 2593 | 24154.9392 | 11.9746 | 0.0004836 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
347 | BRUNSWICK 11052204 | 152481105 | BRUNSWICK 1105 | 11625.6324 | 7.2254 | 84 | 0.1044 | 0.0012429 | 2594 | 24162.1646 | 11.8702 | 0.00047938 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2860 | CAMP EVERS 210311046 | 83622103 | CAMP EVERS 2103 | 25866.5621 | 16.0762 | 194 | 0.23912 | 0.0012326 | 2595 | 24178.2407 | 11.6311 | 0.00046972 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5152 | WOODSIDE 11018522 | 24251101 | WOODSIDE 1101 | 3071.2008 | 1.9088 | 123 | 0.14833 | 0.0012059 | 2596 | 24180.1495 | 11.4828 | 0.00046373 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10217 | PAUL SWEET 2102959032 | 83252102 | PAUL SWEET 2102 | 1283.5288 | 0.79772 | 11 | 0.013238 | 0.0012034 | 2597 | 24180.9472 | 11.4696 | 0.0004632 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6918 | DUNBAR 1103872066 | 43071103 | DUNBAR 1103 | 856.8881 | 0.53256 | 13 | 0.015478 | 0.0011906 | 2598 | 24181.4798 | 11.4541 | 0.00046257 | 11.4541 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5057 | WEIMAR 11012764 | 152491101 | WEIMAR 1101 | 9871.3778 | 6.1351 | 68 | 0.080958 | 0.0011906 | 2599 | 24187.6149 | 11.3731 | 0.0004593 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8401 | IGNACIO 11051943 | 42481105 | IGNACIO 1105 | 1959.963 | 1.2181 | 17 | 0.020183 | 0.0011872 | 2600 | 24188.833 | 11.3529 | 0.00045849 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2098 | VOLTA 1102641544 | 102541102 | VOLTA 1102 | 7956.2573 | 4.9448 | 58 | 0.068531 | 0.0011816 | 2601 | 24193.7779 | 11.2844 | 0.00045572 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5971 | SANTA ROSA A 110464565 | 42151104 | SANTA ROSA A 1104 | 1284.2848 | 0.79819 | 13 | 0.015275 | 0.001175 | 2602 | 24194.576 | 11.2691 | 0.0004551 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1887 | NAPA 1112CB | 42021112 | NAPA 1112 | 940.9991 | 0.58483 | 226 | 0.26497 | 0.0011724 | 2603 | 24195.1609 | 11.0042 | 0.0004444 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5833 | DEL MONTE 21049500 | 182222104 | DEL MONTE 2104 | 9168.0738 | 5.698 | 71 | 0.082807 | 0.0011663 | 2604 | 24200.8589 | 10.9214 | 0.00044106 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3301 | RALSTON 1101836528 | 24141101 | RALSTON 1101 | 4679.584 | 2.9084 | 39 | 0.045051 | 0.0011552 | 2605 | 24203.7673 | 10.8763 | 0.00043924 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1278 | LOS GATOS 1107CB | 82021107 | LOS GATOS 1107 | 24616.6476 | 15.2993 | 192 | 0.22088 | 0.0011504 | 2606 | 24219.0666 | 10.6554 | 0.00043032 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1215 | SAN RAMON 2106CB | 14232106 | SAN RAMON 2106 | 755.1177 | 0.46931 | 25 | 0.028724 | 0.001149 | 2607 | 24219.5359 | 10.6267 | 0.00042916 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10840 | CLOVERDALE 1101704542 | 42821101 | CLOVERDALE 1101 | 345.9417 | 0.215 | 3 | 0.0034424 | 0.0011475 | 2608 | 24219.7509 | 10.6233 | 0.00042902 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9582 | LOS OSITOS 2102624200 | 182082102 | LOS OSITOS 2102 | 2491.858 | 1.5487 | 6 | 0.0068593 | 0.0011432 | 2609 | 24221.2996 | 10.6164 | 0.00042874 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6642 | STANISLAUS 1702L5381 | 162821702 | STANISLAUS 1702 | 1955.4877 | 1.2153 | 15 | 0.017144 | 0.0011429 | 2610 | 24222.515 | 10.5993 | 0.00042805 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10129 | VALLEY VIEW 1103218424 | 14341103 | VALLEY VIEW 1103 | 866.5125 | 0.53854 | 4 | 0.0045488 | 0.0011372 | 2611 | 24223.0535 | 10.5947 | 0.00042787 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2575 | BIG RIVER 110155402 | 43081101 | BIG RIVER 1101 | 3994.4825 | 2.4826 | 104 | 0.11683 | 0.0011234 | 2612 | 24225.5361 | 10.4779 | 0.00042315 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2609 | MIRABEL 1102503000 | 42091102 | MIRABEL 1102 | 7373.131 | 4.5824 | 54 | 0.060401 | 0.0011185 | 2613 | 24230.1185 | 10.4175 | 0.00042071 | 10.4175 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8405 | MONTE RIO 1111240 | 42811111 | MONTE RIO 1111 | 4953.3762 | 3.0785 | 42 | 0.046762 | 0.0011134 | 2614 | 24233.1971 | 10.3707 | 0.00041882 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1947 | ROB ROY 210410930 | 83692104 | ROB ROY 2104 | 1585.2477 | 0.98524 | 149 | 0.16578 | 0.0011126 | 2615 | 24234.1823 | 10.2049 | 0.00041213 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6789 | MIRABEL 11021139 | 42091102 | MIRABEL 1102 | 3291.1128 | 2.0454 | 25 | 0.027677 | 0.0011071 | 2616 | 24236.2277 | 10.1773 | 0.00041101 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10452 | PIT NO 3 21011480 | 103732101 | PIT NO 3 2101 | 3463.9371 | 2.1529 | 20 | 0.022077 | 0.0011038 | 2617 | 24238.3806 | 10.1552 | 0.00041012 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3881 | CORRAL 110275622 | 162991102 | CORRAL 1102 | 1956.9061 | 1.2162 | 78 | 0.085711 | 0.0010989 | 2618 | 24239.5968 | 10.0695 | 0.00040666 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
656 | MORAGA 1105CB | 13801105 | MORAGA 1105 | 9244.2642 | 5.7453 | 121 | 0.13044 | 0.001078 | 2619 | 24245.3422 | 9.939 | 0.00040139 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7044 | SALT SPRINGS 210297924 | 163692102 | SALT SPRINGS 2102 | 8287.4089 | 5.1507 | 49 | 0.052198 | 0.0010653 | 2620 | 24250.4928 | 9.8868 | 0.00039928 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1866 | HIGGINS 1104842642 | 152691104 | HIGGINS 1104 | 9353.842 | 5.8135 | 80 | 0.084021 | 0.0010503 | 2621 | 24256.3063 | 9.8028 | 0.00039589 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1316 | SHADY GLEN 1101CB | 152431101 | SHADY GLEN 1101 | 5676.9517 | 3.5282 | 72 | 0.075616 | 0.0010502 | 2622 | 24259.8345 | 9.7272 | 0.00039283 | 9.7272 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8148 | MIWUK 1702S1547 | 163661702 | MIWUK 1702 | 4459.8848 | 2.7718 | 39 | 0.040901 | 0.0010487 | 2623 | 24262.6064 | 9.6863 | 0.00039118 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4763 | SNEATH LANE 11071277 | 22721107 | SNEATH LANE 1107 | 0 | 0 | 30 | 0.030539 | 0.001018 | 2624 | 24262.6064 | 9.6558 | 0.00038995 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10287 | DUNLAP 11027290 | 254061102 | DUNLAP 1102 | 1075.4071 | 0.66837 | 8 | 0.0081011 | 0.0010126 | 2625 | 24263.2747 | 9.6477 | 0.00038962 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9998 | RESEARCH 2102644462 | 14692102 | RESEARCH 2102 | 567.6161 | 0.35278 | 24 | 0.024298 | 0.0010124 | 2626 | 24263.6275 | 9.6234 | 0.00038864 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1937 | SARATOGA 1107LC12 | 83371107 | SARATOGA 1107 | 12044.6481 | 7.4858 | 86 | 0.086838 | 0.0010097 | 2627 | 24271.1133 | 9.5365 | 0.00038513 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3 | HIGGINS 1104498932 | 152691104 | HIGGINS 1104 | 6024.2456 | 3.7441 | 57 | 0.057431 | 0.0010076 | 2628 | 24274.8574 | 9.4791 | 0.00038281 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7928 | HALSEY 11015731 | 152241101 | HALSEY 1101 | 5029.6194 | 3.1259 | 41 | 0.041274 | 0.0010067 | 2629 | 24277.9833 | 9.4378 | 0.00038115 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5582 | TAMARACK 1101CB | 152291101 | TAMARACK 1101 | 28123.7558 | 17.479 | 148 | 0.14896 | 0.0010065 | 2630 | 24295.4623 | 9.2889 | 0.00037513 | 9.2889 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5935 | MORAGA 1103CB | 13801103 | MORAGA 1103 | 2141.3708 | 1.3309 | 82 | 0.082476 | 0.0010058 | 2631 | 24296.7932 | 9.2064 | 0.0003718 | 9.2064 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6299 | PEORIA 170587222 | 163781705 | PEORIA 1705 | 8240.0573 | 5.1212 | 57 | 0.057176 | 0.0010031 | 2632 | 24301.9144 | 9.1492 | 0.00036949 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2943 | PAUL SWEET 2105CB | 83252105 | PAUL SWEET 2105 | 11980.8022 | 7.4461 | 86 | 0.086208 | 0.0010024 | 2633 | 24309.3606 | 9.063 | 0.00036601 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9018 | GREEN VALLEY 2101509068 | 83192101 | GREEN VALLEY 2101 | 1655.4712 | 1.0289 | 22 | 0.022042 | 0.0010019 | 2634 | 24310.3894 | 9.041 | 0.00036512 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8604 | MORGAN HILL 2105975388 | 83242105 | MORGAN HILL 2105 | 775.2264 | 0.48181 | 18 | 0.018029 | 0.0010016 | 2635 | 24310.8713 | 9.0229 | 0.00036439 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5120 | PAUL SWEET 21045394 | 83252104 | PAUL SWEET 2104 | 23340.3938 | 14.5061 | 180 | 0.17859 | 0.00099214 | 2636 | 24325.3774 | 8.8443 | 0.00035718 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6690 | GUALALA 1111887180 | 42841111 | GUALALA 1111 | 8589.4892 | 5.3384 | 61 | 0.060163 | 0.00098628 | 2637 | 24330.7158 | 8.7842 | 0.00035475 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3875 | FORT BRAGG A 11014698 | 42761101 | FORT BRAGG A 1101 | 12883.0062 | 8.0068 | 101 | 0.098734 | 0.00097756 | 2638 | 24338.7226 | 8.6854 | 0.00035076 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8479 | SALT SPRINGS 2102L7283 | 163692102 | SALT SPRINGS 2102 | 1053.4945 | 0.65475 | 12 | 0.011693 | 0.00097446 | 2639 | 24339.3774 | 8.6738 | 0.00035029 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1105 | PLACER 110451732 | 152461104 | PLACER 1104 | 1093.5921 | 0.67967 | 110 | 0.10706 | 0.00097323 | 2640 | 24340.0571 | 8.5667 | 0.00034597 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6916 | BEN LOMOND 110196738 | 83041101 | BEN LOMOND 1101 | 10792.8538 | 6.7078 | 84 | 0.081712 | 0.00097276 | 2641 | 24346.7649 | 8.485 | 0.00034267 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5851 | SAN RAFAEL 1109692576 | 42011109 | SAN RAFAEL 1109 | 3874.9491 | 2.4083 | 51 | 0.049424 | 0.0009691 | 2642 | 24349.1732 | 8.4356 | 0.00034067 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1894 | HALF MOON BAY 11028848 | 24101102 | HALF MOON BAY 1102 | 6200.2521 | 3.8535 | 117 | 0.11277 | 0.00096385 | 2643 | 24353.0266 | 8.3228 | 0.00033612 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3844 | OLEMA 110150396 | 42291101 | OLEMA 1101 | 20827.3892 | 12.9443 | 162 | 0.15566 | 0.00096084 | 2644 | 24365.971 | 8.1671 | 0.00032983 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8685 | SANTA ROSA A 1111114 | 42151111 | SANTA ROSA A 1111 | 17.4908 | 0.010871 | 40 | 0.038422 | 0.00096055 | 2645 | 24365.9818 | 8.1287 | 0.00032828 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3877 | LOS GATOS 110660116 | 82021106 | LOS GATOS 1106 | 19634.1928 | 12.2027 | 151 | 0.14421 | 0.00095505 | 2646 | 24378.1846 | 7.9845 | 0.00032245 | 7.9845 | #N/A | #N/A | #N/A | #N/A | #VALUE!
46 | MONTE RIO 11111703 | 42811111 | MONTE RIO 1111 | 2213.9946 | 1.376 | 16 | 0.015271 | 0.00095446 | 2647 | 24379.5606 | 7.9692 | 0.00032184 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2992 | EMERALD LAKE 0401CB | 24080401 | EMERALD LAKE 0401 | 15035.2163 | 9.3444 | 130 | 0.12314 | 0.00094726 | 2648 | 24388.905 | 7.8461 | 0.00031686 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5798 | DIAMOND SPRINGS 1107217974 | 152261107 | DIAMOND SPRINGS 1107 | 6593.0651 | 4.0976 | 44 | 0.04135 | 0.00093976 | 2649 | 24393.0026 | 7.8047 | 0.00031519 | 7.8047 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5351 | TEMPLETON 2113A32 | 183052113 | TEMPLETON 2113 | 2633.3805 | 1.6367 | 76 | 0.071294 | 0.00093807 | 2650 | 24394.6393 | 7.7334 | 0.00031232 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5142 | STANISLAUS 17021850 | 162821702 | STANISLAUS 1702 | 21661.1812 | 13.4625 | 182 | 0.16988 | 0.00093342 | 2651 | 24408.1018 | 7.5636 | 0.00030545 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7375 | ARCATA 11224218 | 192021122 | ARCATA 1122 | 7690.241 | 4.7795 | 27 | 0.025131 | 0.00093079 | 2652 | 24412.8813 | 7.5384 | 0.00030444 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2956 | BIG BASIN 110276752 | 82841102 | BIG BASIN 1102 | 4380.3192 | 2.7224 | 36 | 0.032874 | 0.00091318 | 2653 | 24415.6037 | 7.5056 | 0.00030311 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3629 | BRUNSWICK 11051030 | 152481105 | BRUNSWICK 1105 | 25567.0003 | 15.89 | 217 | 0.19746 | 0.00090994 | 2654 | 24431.4937 | 7.3081 | 0.00029514 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9250 | MIWUK 17021808 | 163661702 | MIWUK 1702 | 2949.8139 | 1.8333 | 27 | 0.024551 | 0.00090929 | 2655 | 24433.327 | 7.2835 | 0.00029415 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8540 | DEL MONTE 210436720 | 182222104 | DEL MONTE 2104 | 9577.7665 | 5.9526 | 87 | 0.077895 | 0.00089535 | 2656 | 24439.2796 | 7.2056 | 0.000291 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
950 | JARVIS 1108MR366 | 13501108 | JARVIS 1108 | 0 | 0 | 134 | 0.11813 | 0.00088159 | 2657 | 24439.2796 | 7.0875 | 0.00028623 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1888 | ROB ROY 2104CB | 83692104 | ROB ROY 2104 | 23033.3792 | 14.3153 | 170 | 0.14865 | 0.0008744 | 2658 | 24453.595 | 6.9389 | 0.00028023 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
311 | SALT SPRINGS 21023142 | 163692102 | SALT SPRINGS 2102 | 28901.7283 | 17.9625 | 256 | 0.22061 | 0.00086175 | 2659 | 24471.5575 | 6.7183 | 0.00027132 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
978 | BRYANT 0402CB | 13090402 | BRYANT 0402 | 3768.052 | 2.3419 | 111 | 0.095332 | 0.00085884 | 2660 | 24473.8994 | 6.6229 | 0.00026747 | 6.6229 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7054 | STANISLAUS 1702L3151 | 162821702 | STANISLAUS 1702 | 1595.4085 | 0.99155 | 13 | 0.011082 | 0.00085242 | 2661 | 24474.8909 | 6.6118 | 0.00026702 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3980 | BIG BASIN 110112838 | 82841101 | BIG BASIN 1101 | 3807.4911 | 2.3664 | 32 | 0.027215 | 0.00085046 | 2662 | 24477.2573 | 6.5846 | 0.00026592 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8804 | SILVERADO 2103403102 | 43432103 | SILVERADO 2103 | 788.5735 | 0.4901 | 18 | 0.015221 | 0.00084561 | 2663 | 24477.7474 | 6.5694 | 0.00026531 | 6.5694 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6283 | HATTON 11022010 | 182291102 | HATTON 1102 | 6409.6213 | 3.9836 | 43 | 0.036277 | 0.00084365 | 2664 | 24481.731 | 6.5331 | 0.00026384 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
164 | CORONA 11034446 | 43491103 | CORONA 1103 | 0 | 0 | 124 | 0.10422 | 0.00084052 | 2665 | 24481.731 | 6.4289 | 0.00025963 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5512 | MORAGA 1101669542 | 13801101 | MORAGA 1101 | 5668.7589 | 3.5232 | 49 | 0.040836 | 0.0008334 | 2666 | 24485.2542 | 6.3881 | 0.00025798 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5671 | CURTIS 170190120 | 163351701 | CURTIS 1701 | 5041.5999 | 3.1334 | 64 | 0.052727 | 0.00082387 | 2667 | 24488.3875 | 6.3353 | 0.00025585 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5328 | OROSI 11027948F | 252841102 | OROSI 1102 | 1712.0139 | 1.064 | 74 | 0.060809 | 0.00082174 | 2668 | 24489.4516 | 6.2745 | 0.0002534 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3271 | STAFFORD 1101CB | 43201101 | STAFFORD 1101 | 2188.9817 | 1.3605 | 180 | 0.14746 | 0.0008192 | 2669 | 24490.812 | 6.1271 | 0.00024744 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3349 | STANISLAUS 17026028 | 162821702 | STANISLAUS 1702 | 13370.3026 | 8.3097 | 115 | 0.09369 | 0.0008147 | 2670 | 24499.1217 | 6.0334 | 0.00024366 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4063 | REDBUD 1102432 | 43191102 | REDBUD 1102 | 1802.3639 | 1.1202 | 130 | 0.1047 | 0.00080536 | 2671 | 24500.2419 | 5.9287 | 0.00023943 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4207 | SPRING GAP 170210720 | 162831702 | SPRING GAP 1702 | 7675.033 | 4.7701 | 25 | 0.019779 | 0.00079114 | 2672 | 24505.012 | 5.9089 | 0.00023863 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6208 | BIG MEADOWS 2101CB | 102812101 | BIG MEADOWS 2101 | 3388.6184 | 2.106 | 21 | 0.016605 | 0.00079069 | 2673 | 24507.118 | 5.8923 | 0.00023796 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
682 | ROSSMOOR 110676468 | 14161106 | ROSSMOOR 1106 | 1281.0776 | 0.79619 | 35 | 0.027617 | 0.00078905 | 2674 | 24507.9142 | 5.8647 | 0.00023685 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5936 | OAKLAND K 1102CB | 12101102 | OAKLAND K 1102 | 4816.3453 | 2.9934 | 40 | 0.030752 | 0.0007688 | 2675 | 24510.9076 | 5.8339 | 0.0002356 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5479 | ROSSMOOR 1108CB | 14161108 | ROSSMOOR 1108 | 6728.9489 | 4.1821 | 92 | 0.070139 | 0.00076238 | 2676 | 24515.0896 | 5.7638 | 0.00023277 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3739 | WEIMAR 1102CB | 152491102 | WEIMAR 1102 | 19605.5563 | 12.1849 | 151 | 0.11354 | 0.00075189 | 2677 | 24527.2746 | 5.6503 | 0.00022819 | 5.6503 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4477 | MIWUK 170238218 | 163661702 | MIWUK 1702 | 17605.0564 | 10.9416 | 132 | 0.098599 | 0.00074696 | 2678 | 24538.2162 | 5.5517 | 0.0002242 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
262 | ROB ROY 21055090 | 83692105 | ROB ROY 2105 | 34218.6566 | 21.267 | 245 | 0.18191 | 0.00074249 | 2679 | 24559.4832 | 5.3698 | 0.00021686 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
459 | HARTLEY 1102824 | 43211102 | HARTLEY 1102 | 137.5107 | 0.085463 | 103 | 0.074902 | 0.00072721 | 2680 | 24559.5687 | 5.2949 | 0.00021383 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3196 | SPRING GAP 17029280 | 162831702 | SPRING GAP 1702 | 10262.6071 | 6.3783 | 80 | 0.057699 | 0.00072124 | 2681 | 24565.9469 | 5.2372 | 0.0002115 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1359 | CAMP EVERS 210311056 | 83622103 | CAMP EVERS 2103 | 6717.0632 | 4.1747 | 48 | 0.034556 | 0.00071991 | 2682 | 24570.1216 | 5.2026 | 0.00021011 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2485 | EEL RIVER 1102530 | 192381102 | EEL RIVER 1102 | 117.5277 | 0.073044 | 255 | 0.17964 | 0.00070447 | 2683 | 24570.1947 | 5.023 | 0.00020285 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6651 | PINECREST 04011818 | 163160401 | PINECREST 0401 | 4942.4923 | 3.0718 | 26 | 0.018183 | 0.00069935 | 2684 | 24573.2664 | 5.0048 | 0.00020212 | 5.0048 | #N/A | #N/A | #N/A | #N/A | #VALUE!
413 | BRUNSWICK 11062796 | 152481106 | BRUNSWICK 1106 | 31981.5846 | 19.8767 | 253 | 0.17585 | 0.00069507 | 2685 | 24593.1431 | 4.8289 | 0.00019502 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4105 | CAMP EVERS 210410442 | 83622104 | CAMP EVERS 2104 | 9105.2092 | 5.6589 | 133 | 0.092361 | 0.00069444 | 2686 | 24598.802 | 4.7366 | 0.00019129 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2116 | LUCERNE 1106CB | 43351106 | LUCERNE 1106 | 3043.2971 | 1.8914 | 48 | 0.033315 | 0.00069407 | 2687 | 24600.6935 | 4.7032 | 0.00018994 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10094 | HARRIS 1109237791 | 192431109 | HARRIS 1109 | 2280.4467 | 1.4173 | 23 | 0.015935 | 0.00069283 | 2688 | 24602.1108 | 4.6873 | 0.0001893 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9596 | BRUNSWICK 1104285704 | 152481104 | BRUNSWICK 1104 | 1685.8276 | 1.0477 | 17 | 0.011648 | 0.00068515 | 2689 | 24603.1585 | 4.6757 | 0.00018883 | 4.6757 | #N/A | #N/A | #N/A | #N/A | #VALUE!
591 | MIWUK 170110600 | 163661701 | MIWUK 1701 | 21367.0688 | 13.2797 | 161 | 0.10996 | 0.000683 | 2690 | 24616.4382 | 4.5657 | 0.00018439 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7040 | PAUL SWEET 2106428102 | 83252106 | PAUL SWEET 2106 | 19729.9421 | 12.2622 | 158 | 0.10786 | 0.00068264 | 2691 | 24628.7005 | 4.4578 | 0.00018003 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9535 | HOLLISTER 2105480430 | 182492105 | HOLLISTER 2105 | 1450.1348 | 0.90126 | 39 | 0.026574 | 0.00068138 | 2692 | 24629.6017 | 4.4313 | 0.00017896 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
751 | GUALALA 1112662 | 42841112 | GUALALA 1112 | 10019.7655 | 6.2273 | 104 | 0.070638 | 0.00067921 | 2693 | 24635.8291 | 4.3606 | 0.0001761 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9192 | PURISIMA 110154728 | 182971101 | PURISIMA 1101 | 1667.872 | 1.0366 | 37 | 0.024517 | 0.00066262 | 2694 | 24636.8657 | 4.3361 | 0.00017511 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6603 | MIRABEL 11027347 | 42091102 | MIRABEL 1102 | 1315.3758 | 0.81751 | 10 | 0.0065864 | 0.00065864 | 2695 | 24637.6832 | 4.3295 | 0.00017485 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6890 | CHALLENGE 110113026 | 103201101 | CHALLENGE 1101 | 12912.9615 | 8.0255 | 70 | 0.045688 | 0.00065269 | 2696 | 24645.7086 | 4.2838 | 0.000173 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4651 | PACIFICA 1102320094 | 22811102 | PACIFICA 1102 | 440.0576 | 0.2735 | 11 | 0.0071266 | 0.00064788 | 2697 | 24645.9821 | 4.2767 | 0.00017272 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7773 | MONTE RIO 111215401 | 42811112 | MONTE RIO 1112 | 1388.1732 | 0.86276 | 11 | 0.0070561 | 0.00064146 | 2698 | 24646.8449 | 4.2697 | 0.00017243 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8375 | MONTE RIO 1111256 | 42811111 | MONTE RIO 1111 | 2415.6319 | 1.5013 | 17 | 0.010817 | 0.00063627 | 2699 | 24648.3462 | 4.2588 | 0.00017199 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6923 | OLEMA 1101758594 | 42291101 | OLEMA 1101 | 1943.4938 | 1.2079 | 21 | 0.013182 | 0.00062774 | 2700 | 24649.5541 | 4.2457 | 0.00017146 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10215 | IGNACIO 11011779 | 42481101 | IGNACIO 1101 | 540.9099 | 0.33618 | 5 | 0.0031313 | 0.00062625 | 2701 | 24649.8903 | 4.2425 | 0.00017133 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4571 | TEMPLETON 2113A30 | 183052113 | TEMPLETON 2113 | 401.1046 | 0.24929 | 25 | 0.015522 | 0.00062089 | 2702 | 24650.1396 | 4.227 | 0.00017071 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5501 | FORT BRAGG A 11013100 | 42761101 | FORT BRAGG A 1101 | 19636.3272 | 12.2041 | 198 | 0.12179 | 0.00061511 | 2703 | 24662.3436 | 4.1052 | 0.00016579 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7330 | HAMILTON BRANCH 110190334 | 102361101 | HAMILTON BRANCH 1101 | 5394.0455 | 3.3524 | 44 | 0.027059 | 0.00061497 | 2704 | 24665.696 | 4.0782 | 0.0001647 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3053 | HIGGINS 11032194 | 152691103 | HIGGINS 1103 | 2142.6429 | 1.3317 | 36 | 0.021853 | 0.00060703 | 2705 | 24667.0277 | 4.0563 | 0.00016381 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9597 | MORGAN HILL 2105XR602 | 83242105 | MORGAN HILL 2105 | 391.3667 | 0.24324 | 13 | 0.0078688 | 0.00060529 | 2706 | 24667.2709 | 4.0484 | 0.0001635 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5378 | DIAMOND SPRINGS 1105CB | 152261105 | DIAMOND SPRINGS 1105 | 3330.3293 | 2.0698 | 47 | 0.028118 | 0.00059825 | 2707 | 24669.3407 | 4.0203 | 0.00016236 | 4.0203 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1437 | HORSESHOE 110450142 | 152571104 | HORSESHOE 1104 | 3596.2025 | 2.2351 | 55 | 0.032757 | 0.00059558 | 2708 | 24671.5758 | 3.9876 | 0.00016104 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4026 | MIRABEL 1101CB | 42091101 | MIRABEL 1101 | 792.3448 | 0.49245 | 70 | 0.04163 | 0.00059471 | 2709 | 24672.0682 | 3.9459 | 0.00015936 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7798 | LOS GATOS 110712041 | 82021107 | LOS GATOS 1107 | 10143.7851 | 6.3044 | 65 | 0.038543 | 0.00059297 | 2710 | 24678.3727 | 3.9074 | 0.0001578 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1553 | MEADOW LANE 2106C558R | 14302106 | MEADOW LANE 2106 | 1942.5032 | 1.2073 | 180 | 0.10648 | 0.00059158 | 2711 | 24679.5799 | 3.8009 | 0.0001535 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
380 | STANISLAUS 17021804 | 162821702 | STANISLAUS 1702 | 13482.9013 | 8.3797 | 118 | 0.069602 | 0.00058985 | 2712 | 24687.9596 | 3.7313 | 0.00015069 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10645 | DIAMOND SPRINGS 1103635040 | 152261103 | DIAMOND SPRINGS 1103 | 324.181 | 0.20148 | 2 | 0.0011776 | 0.0005888 | 2713 | 24688.1611 | 3.7301 | 0.00015064 | 3.7301 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7077 | CORONA 1103776806 | 43491103 | CORONA 1103 | 412.4097 | 0.25631 | 15 | 0.0087716 | 0.00058477 | 2714 | 24688.4174 | 3.7213 | 0.00015029 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4432 | BRUNSWICK 11053611 | 152481105 | BRUNSWICK 1105 | 2597.3823 | 1.6143 | 23 | 0.013281 | 0.00057745 | 2715 | 24690.0317 | 3.7081 | 0.00014975 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5741 | HICKS 2101XR250 | 83432101 | HICKS 2101 | 0 | 0 | 80 | 0.04581 | 0.00057262 | 2716 | 24690.0317 | 3.6623 | 0.0001479 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8362 | CASTRO VALLEY 1111CB | 14091111 | CASTRO VALLEY 1111 | 357.3361 | 0.22209 | 16 | 0.0091293 | 0.00057058 | 2717 | 24690.2538 | 3.6531 | 0.00014753 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4792 | HALF MOON BAY 1102CB | 24101102 | HALF MOON BAY 1102 | 266.9695 | 0.16592 | 50 | 0.028015 | 0.0005603 | 2718 | 24690.4197 | 3.6251 | 0.0001464 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2151 | MIWUK 170153038 | 163661701 | MIWUK 1701 | 10729.3555 | 6.6683 | 62 | 0.034212 | 0.00055181 | 2719 | 24697.088 | 3.5909 | 0.00014502 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5668 | ALLEGHANY 1101978 | 152101101 | ALLEGHANY 1101 | 22458.2021 | 13.9579 | 130 | 0.071692 | 0.00055148 | 2720 | 24711.0459 | 3.5192 | 0.00014212 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6116 | IGNACIO 1105908 | 42481105 | IGNACIO 1105 | 1126.3756 | 0.70005 | 42 | 0.023126 | 0.00055062 | 2721 | 24711.7459 | 3.4961 | 0.00014119 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2452 | OAKHURST 1103719490 | 254421103 | OAKHURST 1103 | 4856.6254 | 3.0184 | 44 | 0.024132 | 0.00054847 | 2722 | 24714.7643 | 3.4719 | 0.00014021 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1532 | HAMILTON BRANCH 1101CB | 102361101 | HAMILTON BRANCH 1101 | 3755.8808 | 2.3343 | 56 | 0.030608 | 0.00054657 | 2723 | 24717.0986 | 3.4413 | 0.00013898 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8732 | EL CERRITO G 1112418480 | 12501112 | EL CERRITO G 1112 | 1216.9885 | 0.75636 | 13 | 0.0071032 | 0.0005464 | 2724 | 24717.855 | 3.4342 | 0.00013869 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4263 | HALF MOON BAY 11038894 | 24101103 | HALF MOON BAY 1103 | 18102.2842 | 11.2506 | 110 | 0.058844 | 0.00053494 | 2725 | 24729.1056 | 3.3754 | 0.00013632 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4900 | CHESTER 11022564 | 103181102 | CHESTER 1102 | 3598.4394 | 2.2364 | 21 | 0.011191 | 0.00053291 | 2726 | 24731.3421 | 3.3642 | 0.00013586 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1003 | SANTA ROSA A 1111CB | 42151111 | SANTA ROSA A 1111 | 490.8425 | 0.30506 | 88 | 0.046318 | 0.00052634 | 2727 | 24731.6472 | 3.3179 | 0.00013399 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8503 | SAN RAFAEL 11071276 | 42011107 | SAN RAFAEL 1107 | 6012.4282 | 3.7367 | 56 | 0.029412 | 0.00052522 | 2728 | 24735.3839 | 3.2885 | 0.00013281 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6580 | MIWUK 170247143 | 163661702 | MIWUK 1702 | 7882.6346 | 4.8991 | 67 | 0.034985 | 0.00052216 | 2729 | 24740.283 | 3.2535 | 0.00013139 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4101 | LAURELES 1112562376 | 182371112 | LAURELES 1112 | 12746.1039 | 7.9218 | 82 | 0.042763 | 0.00052151 | 2730 | 24748.2047 | 3.2107 | 0.00012967 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5934 | FITCH MOUNTAIN 1113154 | 42751113 | FITCH MOUNTAIN 1113 | 20.5741 | 0.012787 | 108 | 0.056131 | 0.00051973 | 2731 | 24748.2175 | 3.1546 | 0.0001274 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5473 | EL DORADO PH 2102CB | 152762102 | EL DORADO PH 2102 | 8918.2943 | 5.5428 | 46 | 0.023792 | 0.00051722 | 2732 | 24753.7603 | 3.1308 | 0.00012644 | 3.1308 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4174 | CAMP EVERS 210610718 | 83622106 | CAMP EVERS 2106 | 13624.5702 | 8.4677 | 98 | 0.050195 | 0.0005122 | 2733 | 24762.228 | 3.0806 | 0.00012441 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4155 | BRUNSWICK 110532536 | 152481105 | BRUNSWICK 1105 | 17537.3204 | 10.8995 | 144 | 0.072262 | 0.00050182 | 2734 | 24773.1275 | 3.0083 | 0.00012149 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4857 | SEACLIFF 040112946 | 83500401 | SEACLIFF 0401 | 3912.0696 | 2.4314 | 41 | 0.020511 | 0.00050028 | 2735 | 24775.5589 | 2.9878 | 0.00012066 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3888 | PUEBLO 1105716 | 43291105 | PUEBLO 1105 | 161.153 | 0.10016 | 124 | 0.061943 | 0.00049954 | 2736 | 24775.6591 | 2.9259 | 0.00011816 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6409 | MIWUK 1702S2247 | 163661702 | MIWUK 1702 | 2394.0014 | 1.4879 | 21 | 0.010338 | 0.00049228 | 2737 | 24777.1469 | 2.9156 | 0.00011774 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9855 | DUNLAP 1102778286 | 254061102 | DUNLAP 1102 | 4188.0047 | 2.6029 | 5 | 0.0024545 | 0.0004909 | 2738 | 24779.7498 | 2.9131 | 0.00011765 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9129 | ROSSMOOR 1102457174 | 14161102 | ROSSMOOR 1102 | 925.5451 | 0.57523 | 14 | 0.0067687 | 0.00048348 | 2739 | 24780.325 | 2.9063 | 0.00011737 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8205 | ATASCADERO 1102825520 | 182541102 | ATASCADERO 1102 | 1896.9242 | 1.1789 | 21 | 0.0098834 | 0.00047064 | 2740 | 24781.504 | 2.8964 | 0.00011697 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2233 | IGNACIO 11011264 | 42481101 | IGNACIO 1101 | 3078.9362 | 1.9136 | 50 | 0.023178 | 0.00046357 | 2741 | 24783.4175 | 2.8733 | 0.00011604 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4702 | BURNEY 110145984 | 103311101 | BURNEY 1101 | 7772.9197 | 4.8309 | 68 | 0.031442 | 0.00046238 | 2742 | 24788.2484 | 2.8418 | 0.00011477 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
911 | PEORIA 170590374 | 163781705 | PEORIA 1705 | 6578.4615 | 4.0885 | 48 | 0.022042 | 0.0004592 | 2743 | 24792.337 | 2.8198 | 0.00011388 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4097 | SILVERADO 2103CB | 43432103 | SILVERADO 2103 | 0 | 0 | 197 | 0.090077 | 0.00045724 | 2744 | 24792.337 | 2.7297 | 0.00011024 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5992 | MIWUK 17029270 | 163661702 | MIWUK 1702 | 9370.6933 | 5.8239 | 68 | 0.03101 | 0.00045602 | 2745 | 24798.1609 | 2.6987 | 0.00010899 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9472 | LLAGAS 2105XR234 | 83182105 | LLAGAS 2105 | 4.1246 | 0.0025635 | 26 | 0.011846 | 0.00045563 | 2746 | 24798.1635 | 2.6869 | 0.00010851 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6378 | WOODACRE 11011238 | 43021101 | WOODACRE 1101 | 5923.8162 | 3.6817 | 30 | 0.013599 | 0.0004533 | 2747 | 24801.8452 | 2.6733 | 0.00010796 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1227 | MORAGA 110381146 | 13801103 | MORAGA 1103 | 1226.8593 | 0.7625 | 79 | 0.035677 | 0.00045161 | 2748 | 24802.6076 | 2.6376 | 0.00010652 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2519 | CAMPHORA 110122412 | 182071101 | CAMPHORA 1101 | 3680.7169 | 2.2876 | 130 | 0.058447 | 0.0004496 | 2749 | 24804.8952 | 2.5791 | 0.00010416 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2793 | CAMP EVERS 21065302 | 83622106 | CAMP EVERS 2106 | 9546.4932 | 5.9332 | 57 | 0.025567 | 0.00044854 | 2750 | 24810.8284 | 2.5536 | 0.00010313 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5402 | PACIFICA 1101CB | 22811101 | PACIFICA 1101 | 216.2085 | 0.13437 | 38 | 0.017027 | 0.00044808 | 2751 | 24810.9628 | 2.5365 | 0.00010244 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6879 | SEACLIFF 0401CB | 83500401 | SEACLIFF 0401 | 9246.0032 | 5.7464 | 73 | 0.032652 | 0.00044728 | 2752 | 24816.7092 | 2.5039 | 0.00010112 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5244 | DUNBAR 1103440 | 43071103 | DUNBAR 1103 | 3309.7658 | 2.057 | 158 | 0.0698 | 0.00044177 | 2753 | 24818.7662 | 2.4341 | 9.83e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4679 | ROB ROY 210412596 | 83692104 | ROB ROY 2104 | 12925.0786 | 8.033 | 140 | 0.060719 | 0.00043371 | 2754 | 24826.7992 | 2.3734 | 9.5848e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4037 | EL DORADO PH 21019759 | 152762101 | EL DORADO PH 2101 | 4110.5786 | 2.5547 | 32 | 0.013794 | 0.00043106 | 2755 | 24829.354 | 2.3596 | 9.5291e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
909 | TULE POWER HOUSE 1101CB | 258591101 | TULE POWER HOUSE 1101 | 6570.8 | 4.0838 | 11 | 0.0046561 | 0.00042329 | 2756 | 24833.4378 | 2.3549 | 9.5103e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7552 | WEST POINT 1101L2219 | 163201101 | WEST POINT 1101 | 5447.1163 | 3.3854 | 41 | 0.017329 | 0.00042266 | 2757 | 24836.8232 | 2.3376 | 9.4403e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3464 | SERRAMONTE 110412705 | 22861104 | SERRAMONTE 1104 | 0 | 0 | 74 | 0.031276 | 0.00042265 | 2758 | 24836.8232 | 2.3063 | 9.314e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7216 | BIG RIVER 110169032 | 43081101 | BIG RIVER 1101 | 13655.5842 | 8.487 | 101 | 0.042296 | 0.00041877 | 2759 | 24845.3102 | 2.264 | 9.1432e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2590 | WOODSIDE 1104520832 | 24251104 | WOODSIDE 1104 | 9719.2853 | 6.0406 | 90 | 0.036573 | 0.00040636 | 2760 | 24851.3507 | 2.2274 | 8.9955e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8755 | HALF MOON BAY 1101903182 | 24101101 | HALF MOON BAY 1101 | 1052.7078 | 0.65426 | 15 | 0.0060799 | 0.00040533 | 2761 | 24852.005 | 2.2214 | 8.971e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4732 | BIG RIVER 11011286 | 43081101 | BIG RIVER 1101 | 7682.9666 | 4.775 | 92 | 0.036903 | 0.00040112 | 2762 | 24856.78 | 2.1845 | 8.8219e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3369 | ORO FINO 110276008 | 103031102 | ORO FINO 1102 | 25670.8015 | 15.9545 | 170 | 0.068169 | 0.000401 | 2763 | 24872.7345 | 2.1163 | 8.5466e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9255 | LAS GALLINAS A 1106228906 | 42991106 | LAS GALLINAS A 1106 | 988.5949 | 0.61442 | 21 | 0.0083403 | 0.00039716 | 2764 | 24873.3489 | 2.1079 | 8.5129e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2888 | FOOTHILL 110299432 | 182951102 | FOOTHILL 1102 | 2359.0159 | 1.4661 | 115 | 0.045481 | 0.00039549 | 2765 | 24874.8151 | 2.0625 | 8.3293e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7168 | STANISLAUS 17024905 | 162821702 | STANISLAUS 1702 | 3704.1382 | 2.3021 | 35 | 0.01361 | 0.00038885 | 2766 | 24877.1172 | 2.0489 | 8.2743e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4177 | LOS GATOS 110760092 | 82021107 | LOS GATOS 1107 | 15629.1336 | 9.7136 | 108 | 0.041919 | 0.00038814 | 2767 | 24886.8308 | 2.0069 | 8.105e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9726 | SALT SPRINGS 21028442 | 163692102 | SALT SPRINGS 2102 | 19428.9727 | 12.0752 | 50 | 0.019117 | 0.00038233 | 2768 | 24898.9059 | 1.9878 | 8.0278e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1168 | SAN RAFAEL 11081210 | 42011108 | SAN RAFAEL 1108 | 5252.6146 | 3.2645 | 73 | 0.027859 | 0.00038163 | 2769 | 24902.1705 | 1.96 | 7.9153e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9856 | PUEBLO 1105419634 | 43291105 | PUEBLO 1105 | 165.107 | 0.10261 | 14 | 0.0052965 | 0.00037832 | 2770 | 24902.2731 | 1.9547 | 7.8939e-05 | 1.9547 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1493 | SAN RAMON 2107CB | 14232107 | SAN RAMON 2107 | 486.1753 | 0.30216 | 107 | 0.040433 | 0.00037788 | 2771 | 24902.5752 | 1.9142 | 7.7306e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
531 | SAN RAFAEL 1109418 | 42011109 | SAN RAFAEL 1109 | 8262.136 | 5.135 | 130 | 0.049065 | 0.00037742 | 2772 | 24907.7102 | 1.8652 | 7.5325e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10509 | PAUL SWEET 2102337544 | 83252102 | PAUL SWEET 2102 | 579.0642 | 0.35989 | 13 | 0.0048996 | 0.00037689 | 2773 | 24908.0701 | 1.8603 | 7.5127e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
910 | DUNLAP 11027050 | 254061102 | DUNLAP 1102 | 15143.783 | 9.4119 | 67 | 0.024804 | 0.0003702 | 2774 | 24917.482 | 1.8355 | 7.4125e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3656 | HALF MOON BAY 11038089 | 24101103 | HALF MOON BAY 1103 | 4528.4761 | 2.8145 | 29 | 0.010618 | 0.00036614 | 2775 | 24920.2965 | 1.8248 | 7.3696e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6207 | CAMP EVERS 210584166 | 83622105 | CAMP EVERS 2105 | 13231.1785 | 8.2232 | 97 | 0.035334 | 0.00036427 | 2776 | 24928.5197 | 1.7895 | 7.2269e-05 | 1.7895 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6326 | OLEMA 11011252 | 42291101 | OLEMA 1101 | 6608.6355 | 4.1073 | 50 | 0.018071 | 0.00036141 | 2777 | 24932.627 | 1.7714 | 7.154e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
872 | FAIRVIEW 2207M501R | 13432207 | FAIRVIEW 2207 | 4016.4433 | 2.4962 | 60 | 0.021451 | 0.00035751 | 2778 | 24935.1232 | 1.75 | 7.0673e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6151 | EDENVALE 2113CB | 82952113 | EDENVALE 2113 | 24.568 | 0.015269 | 24 | 0.0084091 | 0.00035038 | 2779 | 24935.1385 | 1.7416 | 7.0334e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6316 | BIG RIVER 11011052 | 43081101 | BIG RIVER 1101 | 5356.147 | 3.3289 | 49 | 0.017084 | 0.00034866 | 2780 | 24938.4674 | 1.7245 | 6.9644e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4831 | ROB ROY 2105CB | 83692105 | ROB ROY 2105 | 1181.1241 | 0.73407 | 17 | 0.0058961 | 0.00034683 | 2781 | 24939.2014 | 1.7186 | 6.9406e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5876 | OAKLAND X 1106CR020 | 12541106 | OAKLAND X 1106 | 3932.8974 | 2.4443 | 15 | 0.0051727 | 0.00034485 | 2782 | 24941.6458 | 1.7134 | 6.9197e-05 | 1.7134 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8254 | DOLAN ROAD 1101857972 | 182381101 | DOLAN ROAD 1101 | 1672.4824 | 1.0395 | 18 | 0.0061316 | 0.00034064 | 2783 | 24942.6852 | 1.7073 | 6.8949e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7697 | PARADISE 1103143744 | 102831103 | PARADISE 1103 | 1706.1115 | 1.0604 | 13 | 0.0044176 | 0.00033981 | 2784 | 24943.7456 | 1.7029 | 6.8771e-05 | 1.7029 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4615 | PEORIA 170184318 | 163781701 | PEORIA 1701 | 16486.0902 | 10.2462 | 142 | 0.048002 | 0.00033804 | 2785 | 24953.9917 | 1.6549 | 6.6832e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8175 | WEST POINT 1101L1969 | 163201101 | WEST POINT 1101 | 1768.6139 | 1.0992 | 16 | 0.0051917 | 0.00032448 | 2786 | 24955.0909 | 1.6497 | 6.6623e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2671 | LOS GATOS 1101LB40 | 82021101 | LOS GATOS 1101 | 13714.1212 | 8.5234 | 131 | 0.042384 | 0.00032354 | 2787 | 24963.6143 | 1.6073 | 6.4911e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1669 | SPRING GAP 17029690 | 162831702 | SPRING GAP 1702 | 27916.5832 | 17.3503 | 185 | 0.058094 | 0.00031402 | 2788 | 24980.9646 | 1.5492 | 6.2565e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1740 | GUALALA 1111402866 | 42841111 | GUALALA 1111 | 2560.4032 | 1.5913 | 20 | 0.0062739 | 0.0003137 | 2789 | 24982.5559 | 1.5429 | 6.2311e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6457 | ATASCADERO 1103CB | 182541103 | ATASCADERO 1103 | 304.3324 | 0.18914 | 18 | 0.0056208 | 0.00031227 | 2790 | 24982.745 | 1.5373 | 6.2084e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4913 | SAN LUIS OBISPO 1108CB | 182631108 | SAN LUIS OBISPO 1108 | 10.2676 | 0.0063814 | 69 | 0.02153 | 0.00031202 | 2791 | 24982.7514 | 1.5158 | 6.1215e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3199 | EL CERRITO G 1105BR160 | 12501105 | EL CERRITO G 1105 | 13394.711 | 8.3249 | 132 | 0.04101 | 0.00031068 | 2792 | 24991.0763 | 1.4748 | 5.9559e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7182 | EEL RIVER 1102720639 | 192381102 | EEL RIVER 1102 | 2660.7876 | 1.6537 | 25 | 0.0076549 | 0.0003062 | 2793 | 24992.73 | 1.4671 | 5.925e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6389 | PERRY 1101W10 | 183071101 | PERRY 1101 | 2354.9644 | 1.4636 | 29 | 0.0088744 | 0.00030601 | 2794 | 24994.1936 | 1.4582 | 5.8891e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5102 | DEL MONTE 21049096 | 182222104 | DEL MONTE 2104 | 5304.2381 | 3.2966 | 78 | 0.023869 | 0.00030601 | 2795 | 24997.4902 | 1.4344 | 5.7927e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
483 | EL CERRITO G 1105CB | 12501105 | EL CERRITO G 1105 | 11982.8259 | 7.4474 | 97 | 0.029509 | 0.00030421 | 2796 | 25004.9376 | 1.4049 | 5.6735e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8801 | WOODSIDE 1104420146 | 24251104 | WOODSIDE 1104 | 4389.3602 | 2.728 | 43 | 0.013077 | 0.00030412 | 2797 | 25007.6656 | 1.3918 | 5.6207e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2740 | SUNOL 1101MR650 | 14241101 | SUNOL 1101 | 2086.6412 | 1.2969 | 30 | 0.0088568 | 0.00029523 | 2798 | 25008.9624 | 1.3829 | 5.585e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1558 | RINCON 1103472 | 43321103 | RINCON 1103 | 4930.8208 | 3.0645 | 71 | 0.020918 | 0.00029462 | 2799 | 25012.027 | 1.362 | 5.5005e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1849 | FORT BRAGG A 11044690 | 42761104 | FORT BRAGG A 1104 | 18710.8643 | 11.6289 | 161 | 0.047396 | 0.00029439 | 2800 | 25023.6558 | 1.3146 | 5.3091e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1214 | ROB ROY 21055166 | 83692105 | ROB ROY 2105 | 8840.5786 | 5.4945 | 81 | 0.023482 | 0.00028991 | 2801 | 25029.1503 | 1.2911 | 5.2142e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6981 | HALF MOON BAY 110148868 | 24101101 | HALF MOON BAY 1101 | 0 | 0 | 21 | 0.0059463 | 0.00028316 | 2802 | 25029.1503 | 1.2852 | 5.1902e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5899 | VOLTA 11011640 | 102541101 | VOLTA 1101 | 16804.166 | 10.4439 | 59 | 0.016689 | 0.00028287 | 2803 | 25039.5941 | 1.2685 | 5.1228e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7108 | RESERVATION ROAD 11023032 | 182731102 | RESERVATION ROAD 1102 | 5799.169 | 3.6042 | 84 | 0.023638 | 0.00028141 | 2804 | 25043.1984 | 1.2449 | 5.0274e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5988 | SPRING GAP 1702693441 | 162831702 | SPRING GAP 1702 | 6859.835 | 4.2634 | 59 | 0.016478 | 0.00027928 | 2805 | 25047.4618 | 1.2284 | 4.9608e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5979 | BIG RIVER 11012183 | 43081101 | BIG RIVER 1101 | 4246.8638 | 2.6394 | 33 | 0.009054 | 0.00027436 | 2806 | 25050.1012 | 1.2193 | 4.9243e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
760 | BIG RIVER 1101952 | 43081101 | BIG RIVER 1101 | 16341.5936 | 10.1564 | 130 | 0.03566 | 0.00027431 | 2807 | 25060.2576 | 1.1837 | 4.7802e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1378 | PARADISE 1105CB | 102831105 | PARADISE 1105 | 9822.6918 | 6.1048 | 86 | 0.023131 | 0.00026897 | 2808 | 25066.3624 | 1.1605 | 4.6868e-05 | 1.1605 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4711 | RESEARCH 2102446423 | 14692102 | RESEARCH 2102 | 1135.402 | 0.70566 | 23 | 0.0061027 | 0.00026534 | 2809 | 25067.0681 | 1.1544 | 4.6622e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
534 | STANISLAUS 170237278 | 162821702 | STANISLAUS 1702 | 10929.4406 | 6.7927 | 99 | 0.026055 | 0.00026318 | 2810 | 25073.8608 | 1.1284 | 4.557e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
956 | PAUL SWEET 2106CB | 83252106 | PAUL SWEET 2106 | 8502.7441 | 5.2845 | 115 | 0.029779 | 0.00025895 | 2811 | 25079.1453 | 1.0986 | 4.4367e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
832 | ROSSMOOR 110168920 | 14161101 | ROSSMOOR 1101 | 10341.5361 | 6.4273 | 91 | 0.02345 | 0.0002577 | 2812 | 25085.5726 | 1.0751 | 4.342e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5459 | PARADISE 1106CB | 102831106 | PARADISE 1106 | 7472.667 | 4.6443 | 53 | 0.013022 | 0.0002457 | 2813 | 25090.2169 | 1.0621 | 4.2894e-05 | 1.0621 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8168 | SAUSALITO 1102410 | 42491102 | SAUSALITO 1102 | 2502.9293 | 1.5556 | 28 | 0.0068532 | 0.00024476 | 2814 | 25091.7724 | 1.0553 | 4.2617e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2941 | DIAMOND SPRINGS 1103CB | 152261103 | DIAMOND SPRINGS 1103 | 885.5612 | 0.55038 | 109 | 0.026412 | 0.00024231 | 2815 | 25092.3228 | 1.0289 | 4.1551e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5531 | MAPLE CREEK 1101CB | 192101101 | MAPLE CREEK 1101 | 14267.6715 | 8.8674 | 60 | 0.01427 | 0.00023784 | 2816 | 25101.1902 | 1.0146 | 4.0974e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6907 | BRUNSWICK 111063100 | 152481110 | BRUNSWICK 1110 | 6591.8886 | 4.0969 | 55 | 0.013021 | 0.00023675 | 2817 | 25105.2871 | 1.0016 | 4.0448e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2877 | MONTE RIO 11111701 | 42811111 | MONTE RIO 1111 | 2248.9876 | 1.3978 | 18 | 0.0042401 | 0.00023556 | 2818 | 25106.6849 | 0.99733 | 4.0277e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6347 | PACIFICA 11015001 | 22811101 | PACIFICA 1101 | 0 | 0 | 25 | 0.0058507 | 0.00023403 | 2819 | 25106.6849 | 0.99148 | 4.0041e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1625 | SAN LUIS OBISPO 1105CB | 182631105 | SAN LUIS OBISPO 1105 | 67.4906 | 0.041946 | 43 | 0.0099759 | 0.000232 | 2820 | 25106.7268 | 0.9815 | 3.9638e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5409 | SAN RAFAEL 1108CB | 42011108 | SAN RAFAEL 1108 | 9469.8097 | 5.8855 | 102 | 0.023483 | 0.00023023 | 2821 | 25112.6123 | 0.95802 | 3.869e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8271 | ROSSMOOR 1107857172 | 14161107 | ROSSMOOR 1107 | 152.0386 | 0.094493 | 15 | 0.0034488 | 0.00022992 | 2822 | 25112.7068 | 0.95457 | 3.855e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10147 | WINDSOR 11035060 | 43501103 | WINDSOR 1103 | 291.5638 | 0.18121 | 12 | 0.0027196 | 0.00022663 | 2823 | 25112.888 | 0.95185 | 3.8441e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8566 | CORONA 1103114284 | 43491103 | CORONA 1103 | 451.7326 | 0.28075 | 11 | 0.0024802 | 0.00022547 | 2824 | 25113.1688 | 0.94937 | 3.834e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
849 | STANISLAUS 170237276 | 162821702 | STANISLAUS 1702 | 18746.4684 | 11.651 | 168 | 0.037039 | 0.00022047 | 2825 | 25124.8198 | 0.91233 | 3.6845e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3868 | HATTON 11012026 | 182291101 | HATTON 1101 | 8438.7955 | 5.2447 | 126 | 0.027409 | 0.00021753 | 2826 | 25130.0646 | 0.88492 | 3.5738e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
427 | SAUSALITO 1101688590 | 42491101 | SAUSALITO 1101 | 1691.536 | 1.0513 | 32 | 0.0069459 | 0.00021706 | 2827 | 25131.1158 | 0.87798 | 3.5457e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4476 | CALISTOGA 1102705 | 42711102 | CALISTOGA 1102 | 622.3172 | 0.38677 | 20 | 0.0042596 | 0.00021298 | 2828 | 25131.5026 | 0.87372 | 3.5285e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1205 | MIWUK 17028090 | 163661702 | MIWUK 1702 | 6501.5338 | 4.0407 | 53 | 0.011216 | 0.00021162 | 2829 | 25135.5433 | 0.8625 | 3.4832e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
61 | CAMBRIA 1102W50 | 182771102 | CAMBRIA 1102 | 997.9458 | 0.62023 | 40 | 0.0084371 | 0.00021093 | 2830 | 25136.1636 | 0.85406 | 3.4491e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
189 | BIG RIVER 110179628 | 43081101 | BIG RIVER 1101 | 23813.9358 | 14.8005 | 156 | 0.032839 | 0.00021051 | 2831 | 25150.964 | 0.82123 | 3.3165e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3166 | ALTO 11251226 | 42031125 | ALTO 1125 | 12282.9745 | 7.6339 | 96 | 0.02008 | 0.00020916 | 2832 | 25158.598 | 0.80115 | 3.2354e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6809 | OAKLAND D 1112CR192 | 12041112 | OAKLAND D 1112 | 3963.0316 | 2.463 | 54 | 0.011247 | 0.00020828 | 2833 | 25161.061 | 0.7899 | 3.19e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4374 | OCEANO 1103V22 | 182601103 | OCEANO 1103 | 50.4916 | 0.031381 | 14 | 0.0028528 | 0.00020377 | 2834 | 25161.0924 | 0.78705 | 3.1785e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9957 | DEL MONTE 21043066 | 182222104 | DEL MONTE 2104 | 26.0345 | 0.016181 | 2 | 0.00040718 | 0.00020359 | 2835 | 25161.1086 | 0.78664 | 3.1768e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4818 | ROSSMOOR 11018132 | 14161101 | ROSSMOOR 1101 | 4248.014 | 2.6402 | 47 | 0.0095582 | 0.00020337 | 2836 | 25163.7487 | 0.77708 | 3.1382e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2856 | SAN RAFAEL 11071166 | 42011107 | SAN RAFAEL 1107 | 20163.1012 | 12.5314 | 213 | 0.043227 | 0.00020294 | 2837 | 25176.2802 | 0.73385 | 2.9637e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
445 | MONTE RIO 1112CB | 42811112 | MONTE RIO 1112 | 5679.6302 | 3.5299 | 43 | 0.0086519 | 0.00020121 | 2838 | 25179.8101 | 0.7252 | 2.9287e-05 | 0.7252 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10280 | SAUSALITO 1102964592 | 42491102 | SAUSALITO 1102 | 941.9387 | 0.58542 | 15 | 0.0029736 | 0.00019824 | 2839 | 25180.3955 | 0.72223 | 2.9167e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1145 | OLEMA 11011200 | 42291101 | OLEMA 1101 | 4658.8808 | 2.8955 | 34 | 0.0066525 | 0.00019566 | 2840 | 25183.291 | 0.71558 | 2.8899e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6437 | HAMILTON BRANCH 110153192 | 102361101 | HAMILTON BRANCH 1101 | 889.758 | 0.55299 | 30 | 0.0058109 | 0.0001937 | 2841 | 25183.844 | 0.70976 | 2.8664e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7381 | PACIFICA 1102660408 | 22811102 | PACIFICA 1102 | 570.687 | 0.35468 | 26 | 0.0049624 | 0.00019086 | 2842 | 25184.1987 | 0.7048 | 2.8463e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5360 | ALHAMBRA 1105CB | 14101105 | ALHAMBRA 1105 | 1333.5262 | 0.82879 | 33 | 0.0062254 | 0.00018865 | 2843 | 25185.0275 | 0.69858 | 2.8212e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1909 | MORAGA 1104750618 | 13801104 | MORAGA 1104 | 1538.3917 | 0.95612 | 13 | 0.002388 | 0.0001837 | 2844 | 25185.9836 | 0.69619 | 2.8116e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7663 | SOBRANTE 1103CB | 14671103 | SOBRANTE 1103 | 6745.77 | 4.1925 | 55 | 0.0099135 | 0.00018024 | 2845 | 25190.1761 | 0.68627 | 2.7715e-05 | 0.68627 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4846 | ORINDA 0402402/2 LR | 12350402 | ORINDA 0402 | 10545.4353 | 6.554 | 91 | 0.016305 | 0.00017917 | 2846 | 25196.7301 | 0.66997 | 2.7057e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6268 | CURTIS 1702S2123 | 163351702 | CURTIS 1702 | 2988.9855 | 1.8577 | 25 | 0.0042941 | 0.00017177 | 2847 | 25198.5878 | 0.66568 | 2.6883e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1067 | DIAMOND SPRINGS 1106290705 | 152261106 | DIAMOND SPRINGS 1106 | 5193.0778 | 3.2275 | 38 | 0.0063506 | 0.00016712 | 2848 | 25201.8153 | 0.65933 | 2.6627e-05 | 0.65933 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3874 | PARADISE 1105829194 | 102831105 | PARADISE 1105 | 18124.3826 | 11.2644 | 142 | 0.023319 | 0.00016422 | 2849 | 25213.0797 | 0.63601 | 2.5685e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1686 | CAMP EVERS 210312990 | 83622103 | CAMP EVERS 2103 | 21277.9249 | 13.2243 | 161 | 0.025964 | 0.00016127 | 2850 | 25226.304 | 0.61004 | 2.4637e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6595 | HIGGINS 110432747 | 152691104 | HIGGINS 1104 | 1047.4929 | 0.65102 | 26 | 0.0041824 | 0.00016086 | 2851 | 25226.955 | 0.60586 | 2.4468e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2910 | HALSEY 110176178 | 152241101 | HALSEY 1101 | 32532.3048 | 20.219 | 248 | 0.039517 | 0.00015934 | 2852 | 25247.174 | 0.56634 | 2.2872e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2602 | PRUNEDALE 11103716 | 182961110 | PRUNEDALE 1110 | 690.7324 | 0.42929 | 157 | 0.024316 | 0.00015488 | 2853 | 25247.6033 | 0.54203 | 2.189e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6371 | BAY MEADOWS 210257886 | 24012102 | BAY MEADOWS 2102 | 6549.4745 | 4.0705 | 81 | 0.012232 | 0.00015101 | 2854 | 25251.6738 | 0.52979 | 2.1396e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3718 | TEMPLETON 2108A40 | 183052108 | TEMPLETON 2108 | 6084.3101 | 3.7814 | 174 | 0.026237 | 0.00015079 | 2855 | 25255.4552 | 0.50356 | 2.0336e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8208 | BRUNSWICK 11038918 | 152481103 | BRUNSWICK 1103 | 2431.0442 | 1.5109 | 30 | 0.0044819 | 0.0001494 | 2856 | 25256.9661 | 0.49908 | 2.0155e-05 | 0.49908 | #N/A | #N/A | #N/A | #N/A | #VALUE!
833 | BRUNSWICK 110456468 | 152481104 | BRUNSWICK 1104 | 8910.5893 | 5.538 | 85 | 0.012606 | 0.0001483 | 2857 | 25262.5041 | 0.48647 | 1.9646e-05 | 0.48647 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8651 | MORGAN HILL 2111419718 | 83242111 | MORGAN HILL 2111 | 3649.8042 | 2.2684 | 25 | 0.0036725 | 0.0001469 | 2858 | 25264.7725 | 0.4828 | 1.9498e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4060 | KONOCTI 11081278 | 43311108 | KONOCTI 1108 | 9099.8598 | 5.6556 | 96 | 0.013948 | 0.00014529 | 2859 | 25270.4281 | 0.46885 | 1.8935e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5993 | LAS GALLINAS A 11041220 | 42991104 | LAS GALLINAS A 1104 | 0 | 0 | 57 | 0.0076113 | 0.00013353 | 2860 | 25270.4281 | 0.46124 | 1.8627e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1481 | SOBRANTE 1101CB | 14671101 | SOBRANTE 1101 | 22896.4557 | 14.2302 | 209 | 0.027098 | 0.00012965 | 2861 | 25284.6583 | 0.43414 | 1.7533e-05 | 0.43414 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6330 | CURTIS 170268380 | 163351702 | CURTIS 1702 | 10711.9675 | 6.6575 | 88 | 0.011322 | 0.00012865 | 2862 | 25291.3158 | 0.42282 | 1.7076e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2410 | SAN LEANDRO U 1114MR544 | 13111114 | SAN LEANDRO U 1114 | 27.9821 | 0.017391 | 62 | 0.0076101 | 0.00012274 | 2863 | 25291.3332 | 0.41521 | 1.6768e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5853 | ROB ROY 210410954 | 83692104 | ROB ROY 2104 | 11428.7483 | 7.103 | 90 | 0.011036 | 0.00012262 | 2864 | 25298.4363 | 0.40417 | 1.6323e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4344 | NOVATO 11041282 | 42211104 | NOVATO 1104 | 0 | 0 | 56 | 0.0067363 | 0.00012029 | 2865 | 25298.4363 | 0.39744 | 1.6051e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8432 | SNEATH LANE 110715341 | 22721107 | SNEATH LANE 1107 | 391.2765 | 0.24318 | 18 | 0.0021346 | 0.00011859 | 2866 | 25298.6794 | 0.3953 | 1.5964e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6986 | RESERVATION ROAD 1102303870 | 182731102 | RESERVATION ROAD 1102 | 1028.4638 | 0.63919 | 7 | 0.00082948 | 0.0001185 | 2867 | 25299.3186 | 0.39447 | 1.5931e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4626 | COTATI 1104426 | 42271104 | COTATI 1104 | 3219.5011 | 2.0009 | 52 | 0.0060642 | 0.00011662 | 2868 | 25301.3196 | 0.38841 | 1.5686e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8778 | PAUL SWEET 2107774760 | 83252107 | PAUL SWEET 2107 | 5348.863 | 3.3243 | 37 | 0.0041429 | 0.00011197 | 2869 | 25304.6439 | 0.38427 | 1.5519e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4484 | FROGTOWN 170274648 | 163451702 | FROGTOWN 1702 | 262.1986 | 0.16296 | 63 | 0.0069966 | 0.00011106 | 2870 | 25304.8069 | 0.37727 | 1.5236e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6192 | PEORIA 170169124 | 163781701 | PEORIA 1701 | 4347.2792 | 2.7019 | 33 | 0.0036026 | 0.00010917 | 2871 | 25307.5087 | 0.37367 | 1.5091e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8000 | DIAMOND SPRINGS 1107116815 | 152261107 | DIAMOND SPRINGS 1107 | 2540.2857 | 1.5788 | 33 | 0.0035385 | 0.00010723 | 2872 | 25309.0875 | 0.37013 | 1.4948e-05 | 0.37013 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8610 | HOOPA 110193038 | 192401101 | HOOPA 1101 | 2107.4343 | 1.3098 | 39 | 0.0041517 | 0.00010645 | 2873 | 25310.3973 | 0.36598 | 1.478e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
995 | HALF MOON BAY 11022032 | 24101102 | HALF MOON BAY 1102 | 905.5345 | 0.56279 | 103 | 0.010949 | 0.0001063 | 2874 | 25310.9601 | 0.35503 | 1.4338e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7250 | ORINDA 04013442 | 12350401 | ORINDA 0401 | 5599.863 | 3.4803 | 68 | 0.0072205 | 0.00010618 | 2875 | 25314.4404 | 0.34781 | 1.4046e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
367 | ARCATA 112233060 | 192021122 | ARCATA 1122 | 856.2789 | 0.53218 | 64 | 0.00637 | 9.9531e-05 | 2876 | 25314.9726 | 0.34144 | 1.3789e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2545 | FAIRVIEW 2207P148 | 13432207 | FAIRVIEW 2207 | 1361.9079 | 0.84643 | 54 | 0.0053348 | 9.8792e-05 | 2877 | 25315.819 | 0.3361 | 1.3573e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5688 | STANISLAUS 170275348 | 162821702 | STANISLAUS 1702 | 8532.4043 | 5.3029 | 77 | 0.0073521 | 9.5481e-05 | 2878 | 25321.122 | 0.32875 | 1.3277e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5946 | SALT SPRINGS 21011232 | 163692101 | SALT SPRINGS 2101 | 12420.8061 | 7.7196 | 64 | 0.0058153 | 9.0864e-05 | 2879 | 25328.8415 | 0.32293 | 1.3042e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4735 | ELK 11018779 | 42981101 | ELK 1101 | 6865.4129 | 4.2669 | 41 | 0.0036815 | 8.9792e-05 | 2880 | 25333.1084 | 0.31925 | 1.2893e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
744 | GABILAN 11013034 | 182331101 | GABILAN 1101 | 80.3377 | 0.04993 | 193 | 0.016822 | 8.716e-05 | 2881 | 25333.1583 | 0.30243 | 1.2214e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8975 | SPRING GAP 170286032 | 162831702 | SPRING GAP 1702 | 1615.684 | 1.0042 | 23 | 0.0019637 | 8.538e-05 | 2882 | 25334.1625 | 0.30047 | 1.2134e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6252 | CHESTER 1101922138 | 103181101 | CHESTER 1101 | 2524.6386 | 1.5691 | 24 | 0.00202 | 8.4169e-05 | 2883 | 25335.7316 | 0.29845 | 1.2053e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
320 | GREEN VALLEY 210112106 | 83192101 | GREEN VALLEY 2101 | 556.8348 | 0.34608 | 139 | 0.011248 | 8.0919e-05 | 2884 | 25336.0776 | 0.2872 | 1.1599e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
390 | PETALUMA C 110856774 | 42631108 | PETALUMA C 1108 | 385.0871 | 0.23933 | 39 | 0.0030702 | 7.8722e-05 | 2885 | 25336.317 | 0.28413 | 1.1475e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3580 | SOBRANTE 1102CB | 14671102 | SOBRANTE 1102 | 16799.2868 | 10.4408 | 132 | 0.0098468 | 7.4597e-05 | 2886 | 25346.7578 | 0.27428 | 1.1077e-05 | 0.27428 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5433 | HATTON 110137088 | 182291101 | HATTON 1101 | 11434.4875 | 7.1066 | 135 | 0.0099063 | 7.338e-05 | 2887 | 25353.8644 | 0.26438 | 1.0677e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2226 | FORT BRAGG A 11021226 | 42761102 | FORT BRAGG A 1102 | 2717.7424 | 1.6891 | 102 | 0.0071773 | 7.0366e-05 | 2888 | 25355.5535 | 0.2572 | 1.0387e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7611 | DIAMOND SPRINGS 1106279670 | 152261106 | DIAMOND SPRINGS 1106 | 6244.093 | 3.8807 | 54 | 0.003785 | 7.0093e-05 | 2889 | 25359.4342 | 0.25341 | 1.0234e-05 | 0.25341 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9967 | CRESTA 1101103126 | 102251101 | CRESTA 1101 | 487.0335 | 0.30269 | 5 | 0.00034541 | 6.9083e-05 | 2890 | 25359.7369 | 0.25307 | 1.022e-05 | 0.25307 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6701 | BRUNSWICK 11064639 | 152481106 | BRUNSWICK 1106 | 5228.1955 | 3.2493 | 44 | 0.0029871 | 6.7888e-05 | 2891 | 25362.9862 | 0.25008 | 1.01e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8130 | LAURELES 111110141 | 182371111 | LAURELES 1111 | 4694.7775 | 2.9178 | 21 | 0.0014246 | 6.784e-05 | 2892 | 25365.9041 | 0.24866 | 1.0042e-05 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
17 | SAN RAFAEL 1106910 | 42011106 | SAN RAFAEL 1106 | 2722.6312 | 1.6921 | 89 | 0.005959 | 6.6955e-05 | 2893 | 25367.5962 | 0.2427 | 9.8014e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
428 | SOBRANTE 1102690098 | 14671102 | SOBRANTE 1102 | 11883.9636 | 7.3859 | 108 | 0.0072019 | 6.6684e-05 | 2894 | 25374.9821 | 0.2355 | 9.5105e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6532 | PARADISE 110536656 | 102831105 | PARADISE 1105 | 220.7989 | 0.13723 | 14 | 0.00090588 | 6.4706e-05 | 2895 | 25375.1194 | 0.23459 | 9.4739e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1066 | JARVIS 1101MR210 | 13501101 | JARVIS 1101 | 1314.2646 | 0.81682 | 103 | 0.0064828 | 6.2939e-05 | 2896 | 25375.9362 | 0.22811 | 9.2121e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5877 | OAKLAND K 1102CR014 | 12101102 | OAKLAND K 1102 | 16905.8619 | 10.5071 | 137 | 0.0085442 | 6.2366e-05 | 2897 | 25386.4432 | 0.21956 | 8.8671e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7339 | BIG BASIN 110165444 | 82841101 | BIG BASIN 1101 | 757.2593 | 0.47064 | 9 | 0.00054514 | 6.0572e-05 | 2898 | 25386.9139 | 0.21902 | 8.8451e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1476 | BOLINAS 1101528 | 42261101 | BOLINAS 1101 | 2865.7848 | 1.7811 | 46 | 0.002487 | 5.4065e-05 | 2899 | 25388.695 | 0.21653 | 8.7446e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9601 | CAMP EVERS 2104189010 | 83622104 | CAMP EVERS 2104 | 59.0426 | 0.036695 | 4 | 0.00020939 | 5.2348e-05 | 2900 | 25388.7317 | 0.21632 | 8.7362e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4401 | SILVERADO 2103507513 | 43432103 | SILVERADO 2103 | 4803.4 | 2.9853 | 65 | 0.0032025 | 4.9269e-05 | 2901 | 25391.717 | 0.21312 | 8.6068e-06 | 0.21312 | #N/A | #N/A | #N/A | #N/A | #VALUE!
625 | ROSSMOOR 1101L503R | 14161101 | ROSSMOOR 1101 | 6910.8038 | 4.2951 | 62 | 0.0030213 | 4.8731e-05 | 2902 | 25396.0121 | 0.2101 | 8.4848e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7021 | DOLAN ROAD 1101590402 | 182381101 | DOLAN ROAD 1101 | 3916.034 | 2.4338 | 78 | 0.0037788 | 4.8446e-05 | 2903 | 25398.4459 | 0.20632 | 8.3322e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7515 | PARADISE 1103468200 | 102831103 | PARADISE 1103 | 531.6801 | 0.33044 | 4 | 0.00019244 | 4.8111e-05 | 2904 | 25398.7764 | 0.20613 | 8.3244e-06 | 0.20613 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8899 | NAPA 11025039 | 42021102 | NAPA 1102 | 0 | 0 | 28 | 0.0012694 | 4.5334e-05 | 2905 | 25398.7764 | 0.20486 | 8.2732e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10522 | PARADISE 11042486 | 102831104 | PARADISE 1104 | 146.4228 | 0.091002 | 2 | 8.8537e-05 | 4.4268e-05 | 2906 | 25398.8674 | 0.20477 | 8.2696e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11006 | PARADISE 1105828400 | 102831105 | PARADISE 1105 | 50.1094 | 0.031143 | 2 | 8.8308e-05 | 4.4154e-05 | 2907 | 25398.8985 | 0.20468 | 8.266e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10495 | CEDAR CREEK 11011362 | 103321101 | CEDAR CREEK 1101 | 24.9514 | 0.015507 | 1 | 4.3827e-05 | 4.3827e-05 | 2908 | 25398.914 | 0.20464 | 8.2643e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4622 | EL CERRITO G 1105BR194 | 12501105 | EL CERRITO G 1105 | 6148.6965 | 3.8214 | 74 | 0.0031957 | 4.3185e-05 | 2909 | 25402.7355 | 0.20144 | 8.1352e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7319 | PARADISE 11061212 | 102831106 | PARADISE 1106 | 3232.6075 | 2.0091 | 33 | 0.0014026 | 4.2503e-05 | 2910 | 25404.7445 | 0.20004 | 8.0786e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10489 | CAMP EVERS 210510996 | 83622105 | CAMP EVERS 2105 | 1226.2093 | 0.76209 | 8 | 0.00033892 | 4.2365e-05 | 2911 | 25405.5066 | 0.1997 | 8.0649e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7716 | PARADISE 110599226 | 102831105 | PARADISE 1105 | 1841.8715 | 1.1447 | 42 | 0.0017299 | 4.1187e-05 | 2912 | 25406.6514 | 0.19797 | 7.995e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6446 | FORT BRAGG A 1102956 | 42761102 | FORT BRAGG A 1102 | 18278.7267 | 11.3603 | 145 | 0.0059316 | 4.0908e-05 | 2913 | 25418.0117 | 0.19204 | 7.7555e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2257 | BIG TREES 04025300 | 83050402 | BIG TREES 0402 | 15760.3239 | 9.7951 | 115 | 0.0045672 | 3.9714e-05 | 2914 | 25427.8068 | 0.18747 | 7.571e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9775 | CAMP EVERS 210595050 | 83622105 | CAMP EVERS 2105 | 223.2117 | 0.13873 | 5 | 0.00019766 | 3.9532e-05 | 2915 | 25427.9455 | 0.18727 | 7.563e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2020 | DUNLAP 11037170 | 254061103 | DUNLAP 1103 | 8726.7127 | 5.4237 | 54 | 0.0021326 | 3.9493e-05 | 2916 | 25433.3692 | 0.18514 | 7.4769e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9147 | BEN LOMOND 04015400 | 83040401 | BEN LOMOND 0401 | 731.4241 | 0.45458 | 4 | 0.00015778 | 3.9445e-05 | 2917 | 25433.8238 | 0.18498 | 7.4705e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2924 | ROB ROY 210538430 | 83692105 | ROB ROY 2105 | 6060.3575 | 3.7665 | 90 | 0.0033991 | 3.7768e-05 | 2918 | 25437.5903 | 0.18158 | 7.3333e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2345 | MORGAN HILL 2106CB | 83242106 | MORGAN HILL 2106 | 1003.198 | 0.62349 | 47 | 0.0016536 | 3.5184e-05 | 2919 | 25438.2138 | 0.17993 | 7.2665e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4552 | SHINGLE SPRINGS 2108449638 | 153652108 | SHINGLE SPRINGS 2108 | 41.9833 | 0.026093 | 1 | 3.5151e-05 | 3.5151e-05 | 2920 | 25438.2399 | 0.17989 | 7.2651e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2359 | PACIFICA 1101777484 | 22811101 | PACIFICA 1101 | 1455.0408 | 0.90431 | 50 | 0.0017533 | 3.5066e-05 | 2921 | 25439.1442 | 0.17814 | 7.1942e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6715 | PARADISE 11032534 | 102831103 | PARADISE 1103 | 5105.9059 | 3.1733 | 49 | 0.0016354 | 3.3375e-05 | 2922 | 25442.3175 | 0.17651 | 7.1282e-06 | 0.17651 | #N/A | #N/A | #N/A | #N/A | #VALUE!
416 | PACIFICA 1102CB | 22811102 | PACIFICA 1102 | 560.1275 | 0.34812 | 51 | 0.0016578 | 3.2507e-05 | 2923 | 25442.6657 | 0.17485 | 7.0612e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4774 | PARADISE 11042488 | 102831104 | PARADISE 1104 | 5690.0714 | 3.5364 | 47 | 0.0015162 | 3.2259e-05 | 2924 | 25446.2021 | 0.17333 | 7e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10872 | WILLOW CREEK 1103181562 | 192171103 | WILLOW CREEK 1103 | 4.572 | 0.0028415 | 1 | 3.208e-05 | 3.208e-05 | 2925 | 25446.2049 | 0.1733 | 6.9987e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5198 | PARADISE 1104283794 | 102831104 | PARADISE 1104 | 3810.7404 | 2.3684 | 37 | 0.0011841 | 3.2004e-05 | 2926 | 25448.5733 | 0.17212 | 6.9509e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2421 | FORT BRAGG A 110235592 | 42761102 | FORT BRAGG A 1102 | 21129.6388 | 13.1322 | 149 | 0.0047622 | 3.1961e-05 | 2927 | 25461.7055 | 0.16735 | 6.7586e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6748 | BRUNSWICK 11103907 | 152481110 | BRUNSWICK 1110 | 1437.9091 | 0.89367 | 16 | 0.00050795 | 3.1747e-05 | 2928 | 25462.5991 | 0.16685 | 6.7381e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1323 | PEORIA 17013186 | 163781701 | PEORIA 1701 | 15806.1877 | 9.8236 | 143 | 0.0045118 | 3.1551e-05 | 2929 | 25472.4227 | 0.16233 | 6.5559e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6182 | BERESFORD 0403435168 | 24040403 | BERESFORD 0403 | 2068.4077 | 1.2855 | 26 | 0.00080941 | 3.1131e-05 | 2930 | 25473.7082 | 0.16152 | 6.5232e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8329 | BRUNSWICK 1104244027 | 152481104 | BRUNSWICK 1104 | 492.7502 | 0.30625 | 6 | 0.00018558 | 3.093e-05 | 2931 | 25474.0145 | 0.16134 | 6.5157e-06 | 0.16134 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10464 | CAMP EVERS 210595394 | 83622105 | CAMP EVERS 2105 | 790.3942 | 0.49123 | 8 | 0.00024683 | 3.0854e-05 | 2932 | 25474.5057 | 0.16109 | 6.5057e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4342 | PARADISE 110636042 | 102831106 | PARADISE 1106 | 13184.5103 | 8.1942 | 119 | 0.0036673 | 3.0817e-05 | 2933 | 25482.7 | 0.15742 | 6.3576e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9818 | ANDERSON 1101561686 | 103261101 | ANDERSON 1101 | 147.2029 | 0.091487 | 1 | 2.9674e-05 | 2.9674e-05 | 2934 | 25482.7914 | 0.1574 | 6.3564e-06 | 0.1574 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2309 | BEN LOMOND 040116010 | 83040401 | BEN LOMOND 0401 | 2728.9115 | 1.696 | 25 | 0.00073909 | 2.9564e-05 | 2935 | 25484.4875 | 0.15666 | 6.3266e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2259 | LAKEWOOD 210738404 | 13532107 | LAKEWOOD 2107 | 5730.6143 | 3.5616 | 47 | 0.0013868 | 2.9507e-05 | 2936 | 25488.0491 | 0.15527 | 6.2705e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6756 | FAIRMOUNT 0401395180 | 12650401 | FAIRMOUNT 0401 | 2263.8752 | 1.407 | 20 | 0.00058824 | 2.9412e-05 | 2937 | 25489.4561 | 0.15468 | 6.2468e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9891 | RIO DELL 1102214052 | 192251102 | RIO DELL 1102 | 941.1587 | 0.58493 | 7 | 0.00020531 | 2.933e-05 | 2938 | 25490.041 | 0.15448 | 6.2385e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9611 | DIAMOND SPRINGS 1106176130 | 152261106 | DIAMOND SPRINGS 1106 | 32.0737 | 0.019934 | 1 | 2.9315e-05 | 2.9315e-05 | 2939 | 25490.0609 | 0.15445 | 6.2373e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9648 | CAMP EVERS 2103CB | 83622103 | CAMP EVERS 2103 | 190.3788 | 0.11832 | 6 | 0.00017429 | 2.9049e-05 | 2940 | 25490.1793 | 0.15427 | 6.2303e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7669 | PARADISE 1104CB | 102831104 | PARADISE 1104 | 2211.8341 | 1.3747 | 46 | 0.0013348 | 2.9018e-05 | 2941 | 25491.5539 | 0.15294 | 6.1764e-06 | 0.15294 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8116 | BRUNSWICK 1107969778 | 152481107 | BRUNSWICK 1107 | 1070.9786 | 0.66562 | 9 | 0.00025699 | 2.8554e-05 | 2942 | 25492.2196 | 0.15268 | 6.166e-06 | 0.15268 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1751 | PARADISE 1104954322 | 102831104 | PARADISE 1104 | 6923.0973 | 4.3027 | 63 | 0.0017862 | 2.8353e-05 | 2943 | 25496.5223 | 0.15089 | 6.0939e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6559 | BIG BASIN 11015479 | 82841101 | BIG BASIN 1101 | 289.2777 | 0.17979 | 3 | 8.3319e-05 | 2.7773e-05 | 2944 | 25496.7021 | 0.15081 | 6.0905e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11110 | CAMP EVERS 2105BL 2101 | 83622105 | CAMP EVERS 2105 | 5.191 | 0.0032262 | 1 | 2.7401e-05 | 2.7401e-05 | 2945 | 25496.7053 | 0.15078 | 6.0894e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7068 | BURNS 2101CB | 183582101 | BURNS 2101 | 2742.3098 | 1.7044 | 19 | 0.00051453 | 2.7081e-05 | 2946 | 25498.4097 | 0.15027 | 6.0686e-06 | 0.15027 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10401 | POINT MORETTI 110110722 | 82931101 | POINT MORETTI 1101 | 937.9448 | 0.58294 | 9 | 0.00024019 | 2.6688e-05 | 2947 | 25498.9926 | 0.15003 | 6.0589e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2162 | SOBRANTE 1102L510R | 14671102 | SOBRANTE 1102 | 15538.9501 | 9.6575 | 136 | 0.0035575 | 2.6158e-05 | 2948 | 25508.6501 | 0.14647 | 5.9152e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8264 | MIRABEL 1101781318 | 42091101 | MIRABEL 1101 | 172.1377 | 0.10698 | 3 | 7.6132e-05 | 2.5377e-05 | 2949 | 25508.7571 | 0.14639 | 5.9122e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2959 | PARADISE 110453544 | 102831104 | PARADISE 1104 | 1035.1182 | 0.64333 | 19 | 0.00048097 | 2.5314e-05 | 2950 | 25509.4004 | 0.14591 | 5.8927e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2047 | VALLEY VIEW 1103CB | 14341103 | VALLEY VIEW 1103 | 272.5459 | 0.16939 | 83 | 0.0020921 | 2.5206e-05 | 2951 | 25509.5698 | 0.14382 | 5.8082e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3341 | CAMP EVERS 21055146 | 83622105 | CAMP EVERS 2105 | 9534.7408 | 5.9259 | 63 | 0.0015473 | 2.4561e-05 | 2952 | 25515.4957 | 0.14227 | 5.7458e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4945 | CASTRO VALLEY 1102837904 | 14091102 | CASTRO VALLEY 1102 | 1669.2171 | 1.0374 | 25 | 0.00061089 | 2.4435e-05 | 2953 | 25516.5331 | 0.14166 | 5.7211e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5852 | PARADISE 1104961990 | 102831104 | PARADISE 1104 | 10972.2602 | 6.8193 | 91 | 0.0021547 | 2.3677e-05 | 2954 | 25523.3524 | 0.13951 | 5.6341e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8958 | PARADISE 1103772517 | 102831103 | PARADISE 1103 | 2777.244 | 1.7261 | 24 | 0.00056446 | 2.3519e-05 | 2955 | 25525.0785 | 0.13894 | 5.6113e-06 | 0.13894 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5973 | BEN LOMOND 0401CB | 83040401 | BEN LOMOND 0401 | 12509.5528 | 7.7747 | 106 | 0.0024408 | 2.3026e-05 | 2956 | 25532.8532 | 0.1365 | 5.5127e-06 | 0.1365 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10776 | GRASS VALLEY 1101528232 | 152031101 | GRASS VALLEY 1101 | 149.6502 | 0.093008 | 2 | 4.449e-05 | 2.2245e-05 | 2957 | 25532.9462 | 0.13646 | 5.5109e-06 | 0.13646 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10760 | FLINT 1102CB | 152531102 | FLINT 1102 | 149.4178 | 0.092864 | 2 | 4.436e-05 | 2.218e-05 | 2958 | 25533.0391 | 0.13641 | 5.5091e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3909 | MORRO BAY 1102V84 | 183011102 | MORRO BAY 1102 | 369.7837 | 0.22982 | 126 | 0.0027508 | 2.1832e-05 | 2959 | 25533.2689 | 0.13366 | 5.398e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7549 | PLACERVILLE 1111CB | 153081111 | PLACERVILLE 1111 | 2245.2688 | 1.3954 | 16 | 0.00034924 | 2.1827e-05 | 2960 | 25534.6644 | 0.13331 | 5.3839e-06 | 0.13331 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6107 | POINT MORETTI 110139126 | 82931101 | POINT MORETTI 1101 | 3634.7812 | 2.259 | 31 | 0.00065131 | 2.101e-05 | 2961 | 25536.9234 | 0.13266 | 5.3576e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9485 | CAMP EVERS 2106834583 | 83622106 | CAMP EVERS 2106 | 981.0329 | 0.60972 | 7 | 0.00013984 | 1.9977e-05 | 2962 | 25537.5331 | 0.13252 | 5.352e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6136 | BIG TREES 0402737512 | 83050402 | BIG TREES 0402 | 10917.3933 | 6.7852 | 89 | 0.0017324 | 1.9465e-05 | 2963 | 25544.3183 | 0.13079 | 5.282e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
940 | CAMP EVERS 210511384 | 83622105 | CAMP EVERS 2105 | 8402.4777 | 5.2222 | 59 | 0.0011342 | 1.9223e-05 | 2964 | 25549.5405 | 0.12966 | 5.2362e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8260 | DIAMOND SPRINGS 1106762780 | 152261106 | DIAMOND SPRINGS 1106 | 400.767 | 0.24908 | 11 | 0.00021145 | 1.9222e-05 | 2965 | 25549.7896 | 0.12945 | 5.2277e-06 | 0.12945 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9711 | BRUNSWICK 1103262343 | 152481103 | BRUNSWICK 1103 | 1232.8709 | 0.76623 | 11 | 0.00021112 | 1.9193e-05 | 2966 | 25550.5558 | 0.12923 | 5.2191e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6422 | BIG BASIN 11029741 | 82841102 | BIG BASIN 1102 | 1036.4661 | 0.64417 | 10 | 0.00018794 | 1.8794e-05 | 2967 | 25551.2 | 0.12905 | 5.2115e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
471 | BIG BASIN 11015028 | 82841101 | BIG BASIN 1101 | 8087.7219 | 5.0266 | 59 | 0.0010925 | 1.8516e-05 | 2968 | 25556.2265 | 0.12795 | 5.1674e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5836 | BRUNSWICK 1103851116 | 152481103 | BRUNSWICK 1103 | 316.0008 | 0.1964 | 4 | 7.3835e-05 | 1.8459e-05 | 2969 | 25556.4229 | 0.12788 | 5.1644e-06 | 0.12788 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10320 | DIAMOND SPRINGS 1106926235 | 152261106 | DIAMOND SPRINGS 1106 | 305.3669 | 0.18979 | 4 | 7.3487e-05 | 1.8372e-05 | 2970 | 25556.6127 | 0.12781 | 5.1615e-06 | 0.12781 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10026 | SARATOGA 1103981056 | 83371103 | SARATOGA 1103 | 132.017 | 0.082049 | 2 | 3.6518e-05 | 1.8259e-05 | 2971 | 25556.6948 | 0.12777 | 5.16e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7034 | DIAMOND SPRINGS 110699658 | 152261106 | DIAMOND SPRINGS 1106 | 0 | 0 | 39 | 0.0007109 | 1.8228e-05 | 2972 | 25556.6948 | 0.12706 | 5.1313e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4269 | BRUNSWICK 110378862 | 152481103 | BRUNSWICK 1103 | 123.6088 | 0.076823 | 17 | 0.00030962 | 1.8213e-05 | 2973 | 25556.7716 | 0.12675 | 5.1188e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3650 | ROB ROY 210512584 | 83692105 | ROB ROY 2105 | 5651.1648 | 3.5122 | 297 | 0.0054019 | 1.8188e-05 | 2974 | 25560.2838 | 0.12135 | 4.9006e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2640 | PERRY 1101V72 | 183071101 | PERRY 1101 | 9610.0836 | 5.9727 | 101 | 0.0018297 | 1.8115e-05 | 2975 | 25566.2565 | 0.11952 | 4.8267e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7574 | CAMP EVERS 210611006 | 83622106 | CAMP EVERS 2106 | 3281.0215 | 2.0392 | 24 | 0.00043202 | 1.8001e-05 | 2976 | 25568.2957 | 0.11909 | 4.8093e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10111 | ALLEGHANY 11011101/2 | 152101101 | ALLEGHANY 1101 | 32.8824 | 0.020437 | 1 | 1.7836e-05 | 1.7836e-05 | 2977 | 25568.3161 | 0.11907 | 4.8086e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7350 | SUMMIT 1101CB | 152591101 | SUMMIT 1101 | 221.0797 | 0.1374 | 2 | 3.5488e-05 | 1.7744e-05 | 2978 | 25568.4535 | 0.11903 | 4.8071e-06 | 0.11903 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10523 | CAMP EVERS 2104710556 | 83622104 | CAMP EVERS 2104 | 65.863 | 0.040934 | 2 | 3.5324e-05 | 1.7662e-05 | 2979 | 25568.4944 | 0.119 | 4.8057e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5707 | FLINT 1101958726 | 152531101 | FLINT 1101 | 1605.4653 | 0.9978 | 13 | 0.00022904 | 1.7619e-05 | 2980 | 25569.4922 | 0.11877 | 4.7965e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8628 | POINT MORETTI 11015401 | 82931101 | POINT MORETTI 1101 | 4047.5171 | 2.5155 | 34 | 0.00059516 | 1.7505e-05 | 2981 | 25572.0078 | 0.11817 | 4.7724e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10455 | POTTER VALLEY P H 1104CB | 42281104 | POTTER VALLEY P H 1104 | 158.4451 | 0.098474 | 2 | 3.4822e-05 | 1.7411e-05 | 2982 | 25572.1063 | 0.11814 | 4.771e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1795 | BOLINAS 11011064 | 42261101 | BOLINAS 1101 | 1005.39 | 0.62485 | 51 | 0.00088693 | 1.7391e-05 | 2983 | 25572.7311 | 0.11725 | 4.7352e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11067 | BRUNSWICK 1104761310 | 152481104 | BRUNSWICK 1104 | 43.1053 | 0.02679 | 1 | 1.7283e-05 | 1.7283e-05 | 2984 | 25572.7579 | 0.11723 | 4.7345e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
130 | CAMP EVERS 21055232 | 83622105 | CAMP EVERS 2105 | 7264.9547 | 4.5152 | 50 | 0.00086284 | 1.7257e-05 | 2985 | 25577.2731 | 0.11637 | 4.6997e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9051 | BRUNSWICK 1103956424 | 152481103 | BRUNSWICK 1103 | 1661.8272 | 1.0328 | 21 | 0.00036171 | 1.7224e-05 | 2986 | 25578.3059 | 0.11601 | 4.6851e-06 | 0.11601 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7122 | CAMP EVERS 210510786 | 83622105 | CAMP EVERS 2105 | 7392.1952 | 4.5943 | 58 | 0.0009908 | 1.7083e-05 | 2987 | 25582.9002 | 0.11502 | 4.645e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7997 | CAMP EVERS 210411048 | 83622104 | CAMP EVERS 2104 | 1473.7073 | 0.91592 | 19 | 0.00032099 | 1.6894e-05 | 2988 | 25583.8161 | 0.1147 | 4.6321e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10098 | RALSTON 1101100040 | 24141101 | RALSTON 1101 | 1324.2274 | 0.82301 | 7 | 0.00011745 | 1.6779e-05 | 2989 | 25584.6392 | 0.11458 | 4.6273e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4770 | CAMP EVERS 210574170 | 83622105 | CAMP EVERS 2105 | 5752.9394 | 3.5755 | 43 | 0.00072063 | 1.6759e-05 | 2990 | 25588.2146 | 0.11386 | 4.5982e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10059 | POTTER VALLEY P H 1105CB | 42281105 | POTTER VALLEY P H 1105 | 89.3518 | 0.055533 | 2 | 3.3096e-05 | 1.6548e-05 | 2991 | 25588.2702 | 0.11383 | 4.5969e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1470 | PLACERVILLE 210619732 | 153082106 | PLACERVILLE 2106 | 14898.6258 | 9.2596 | 125 | 0.0020448 | 1.6359e-05 | 2992 | 25597.5297 | 0.11178 | 4.5143e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5865 | CAMP EVERS 210611044 | 83622106 | CAMP EVERS 2106 | 12291.7272 | 7.6394 | 144 | 0.0023496 | 1.6316e-05 | 2993 | 25605.1691 | 0.10943 | 4.4194e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4584 | BRUNSWICK 1107357568 | 152481107 | BRUNSWICK 1107 | 1927.7671 | 1.1981 | 35 | 0.0005675 | 1.6214e-05 | 2994 | 25606.3672 | 0.10886 | 4.3965e-06 | 0.10886 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4170 | SAN RAFAEL 11042651 | 42011104 | SAN RAFAEL 1104 | 1238.5246 | 0.76975 | 10 | 0.00016143 | 1.6143e-05 | 2995 | 25607.1369 | 0.1087 | 4.39e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4250 | SAN RAFAEL 1106837 | 42011106 | SAN RAFAEL 1106 | 1083.651 | 0.67349 | 22 | 0.00035514 | 1.6143e-05 | 2996 | 25607.8104 | 0.10835 | 4.3756e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8770 | MIRABEL 11027401 | 42091102 | MIRABEL 1102 | 1710.0336 | 1.0628 | 12 | 0.00019031 | 1.5859e-05 | 2997 | 25608.8732 | 0.10816 | 4.368e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5879 | BIG BASIN 11019773 | 82841101 | BIG BASIN 1101 | 724.8545 | 0.4505 | 6 | 9.4849e-05 | 1.5808e-05 | 2998 | 25609.3237 | 0.10806 | 4.3641e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4254 | BRUNSWICK 111095576 | 152481110 | BRUNSWICK 1110 | 0 | 0 | 30 | 0.00047296 | 1.5765e-05 | 2999 | 25609.3237 | 0.10759 | 4.345e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5644 | BRUNSWICK 1103234378 | 152481103 | BRUNSWICK 1103 | 1030.7217 | 0.6406 | 13 | 0.00020445 | 1.5727e-05 | 3000 | 25609.9643 | 0.10739 | 4.3368e-06 | 0.10739 | #N/A | #N/A | #N/A | #N/A | #VALUE!
644 | CAMP EVERS 210511004 | 83622105 | CAMP EVERS 2105 | 6981.3249 | 4.3389 | 60 | 0.00093268 | 1.5545e-05 | 3001 | 25614.3032 | 0.10645 | 4.2991e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10461 | GIRVAN 1102296428 | 103401102 | GIRVAN 1102 | 2768.6124 | 1.7207 | 14 | 0.00021689 | 1.5492e-05 | 3002 | 25616.0239 | 0.10624 | 4.2903e-06 | 0.10624 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8135 | WOODSIDE 1101CB | 24251101 | WOODSIDE 1101 | 0 | 0 | 59 | 0.00091153 | 1.545e-05 | 3003 | 25616.0239 | 0.10532 | 4.2535e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
555 | BRUNSWICK 110750008 | 152481107 | BRUNSWICK 1107 | 1828.8508 | 1.1366 | 64 | 0.0009841 | 1.5377e-05 | 3004 | 25617.1606 | 0.10434 | 4.2138e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4851 | DIAMOND SPRINGS 1106910235 | 152261106 | DIAMOND SPRINGS 1106 | 851.0444 | 0.52893 | 16 | 0.00024453 | 1.5283e-05 | 3005 | 25617.6895 | 0.1041 | 4.2039e-06 | 0.1041 | #N/A | #N/A | #N/A | #N/A | #VALUE!
436 | SARATOGA 1107LC26 | 83371107 | SARATOGA 1107 | 9057.4757 | 5.6293 | 74 | 0.0011176 | 1.5103e-05 | 3006 | 25623.3188 | 0.10298 | 4.1588e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3317 | PLACERVILLE 1110CB | 153081110 | PLACERVILLE 1110 | 1390.1141 | 0.86396 | 28 | 0.00042097 | 1.5035e-05 | 3007 | 25624.1827 | 0.10256 | 4.1418e-06 | 0.10256 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4169 | GRASS VALLEY 1102CB | 152031102 | GRASS VALLEY 1102 | 131.7629 | 0.081891 | 81 | 0.0012064 | 1.4894e-05 | 3008 | 25624.2646 | 0.10135 | 4.0931e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1767 | MONTE RIO 111264682 | 42811112 | MONTE RIO 1112 | 2835.1135 | 1.762 | 22 | 0.00032742 | 1.4883e-05 | 3009 | 25626.0267 | 0.10102 | 4.0798e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7374 | MIRABEL 1102841 | 42091102 | MIRABEL 1102 | 1307.0396 | 0.81233 | 12 | 0.00017819 | 1.4849e-05 | 3010 | 25626.839 | 0.10085 | 4.0726e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9494 | SAN RAFAEL 1101546438 | 42011101 | SAN RAFAEL 1101 | 1541.3848 | 0.95798 | 14 | 0.00020577 | 1.4698e-05 | 3011 | 25627.797 | 0.10064 | 4.0643e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7746 | SALT SPRINGS 21014913 | 163692101 | SALT SPRINGS 2101 | 6065.3094 | 3.7696 | 54 | 0.00079082 | 1.4645e-05 | 3012 | 25631.5666 | 0.099849 | 4.0324e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7346 | OAKLAND K 1101CR346 | 12101101 | OAKLAND K 1101 | 330.9469 | 0.20568 | 3 | 4.3821e-05 | 1.4607e-05 | 3013 | 25631.7723 | 0.099805 | 4.0306e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
112 | EL DORADO PH 210219562 | 152762102 | EL DORADO PH 2102 | 11663.8964 | 7.2492 | 98 | 0.0014213 | 1.4503e-05 | 3014 | 25639.0214 | 0.098384 | 3.9732e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3957 | LOS GATOS 1106LA42 | 82021106 | LOS GATOS 1106 | 4459.4554 | 2.7716 | 35 | 0.00050575 | 1.445e-05 | 3015 | 25641.793 | 0.097878 | 3.9528e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10681 | GEYSERVILLE 1101975350 | 42891101 | GEYSERVILLE 1101 | 73.1065 | 0.045436 | 3 | 4.2852e-05 | 1.4284e-05 | 3016 | 25641.8384 | 0.097835 | 3.9511e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10208 | SHINGLE SPRINGS 2110CB | 153652110 | SHINGLE SPRINGS 2110 | 1346.787 | 0.83703 | 15 | 0.00021149 | 1.4099e-05 | 3017 | 25642.6755 | 0.097624 | 3.9425e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10739 | FORT BRAGG A 1104920850 | 42761104 | FORT BRAGG A 1104 | 322.1994 | 0.20025 | 3 | 4.2181e-05 | 1.406e-05 | 3018 | 25642.8757 | 0.097581 | 3.9408e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9733 | AUBURN 11028611 | 152161102 | AUBURN 1102 | 2893.9317 | 1.7986 | 22 | 0.00030508 | 1.3867e-05 | 3019 | 25644.6743 | 0.097276 | 3.9285e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6925 | MIRABEL 11022043 | 42091102 | MIRABEL 1102 | 902.2238 | 0.56074 | 8 | 0.00011074 | 1.3842e-05 | 3020 | 25645.235 | 0.097166 | 3.924e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6206 | SAN RAFAEL 11081247 | 42011108 | SAN RAFAEL 1108 | 443.4693 | 0.27562 | 3 | 4.1142e-05 | 1.3714e-05 | 3021 | 25645.5107 | 0.097124 | 3.9224e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9515 | HARRIS 1109661309 | 192431109 | HARRIS 1109 | 453.7966 | 0.28204 | 16 | 0.00021867 | 1.3667e-05 | 3022 | 25645.7927 | 0.096906 | 3.9135e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10016 | CAMP EVERS 2104600529 | 83622104 | CAMP EVERS 2104 | 422.8048 | 0.26277 | 4 | 5.3422e-05 | 1.3356e-05 | 3023 | 25646.0555 | 0.096852 | 3.9114e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10551 | PUEBLO 1104968601 | 43291104 | PUEBLO 1104 | 12.2398 | 0.0076071 | 1 | 1.3316e-05 | 1.3316e-05 | 3024 | 25646.0631 | 0.096839 | 3.9108e-06 | 0.096839 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8097 | SARATOGA 11075696 | 83371107 | SARATOGA 1107 | 8152.2263 | 5.0666 | 90 | 0.0011939 | 1.3265e-05 | 3025 | 25651.1297 | 0.095645 | 3.8626e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9710 | GEYSERVILLE 1101216442 | 42891101 | GEYSERVILLE 1101 | 327.4361 | 0.2035 | 4 | 5.1625e-05 | 1.2906e-05 | 3026 | 25651.3332 | 0.095593 | 3.8605e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8869 | BRUNSWICK 11047181 | 152481104 | BRUNSWICK 1104 | 1244.1443 | 0.77324 | 11 | 0.00014128 | 1.2843e-05 | 3027 | 25652.1065 | 0.095452 | 3.8548e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8464 | CAMP EVERS 21067603 | 83622106 | CAMP EVERS 2106 | 1527.2306 | 0.94918 | 11 | 0.00014058 | 1.278e-05 | 3028 | 25653.0556 | 0.095312 | 3.8492e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1616 | SARATOGA 1106LC24 | 83371106 | SARATOGA 1106 | 13258.5886 | 8.2403 | 154 | 0.001963 | 1.2747e-05 | 3029 | 25661.2959 | 0.093349 | 3.7699e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10877 | MORAGA 110183424 | 13801101 | MORAGA 1101 | 2600.4486 | 1.6162 | 7 | 8.7822e-05 | 1.2546e-05 | 3030 | 25662.9121 | 0.093261 | 3.7663e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7661 | CAMP EVERS 210616000 | 83622106 | CAMP EVERS 2106 | 3353.5945 | 2.0843 | 51 | 0.0006373 | 1.2496e-05 | 3031 | 25664.9964 | 0.092623 | 3.7406e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11062 | KESWICK 1101CB | 103451101 | KESWICK 1101 | 26.6683 | 0.016574 | 1 | 1.2413e-05 | 1.2413e-05 | 3032 | 25665.0129 | 0.092611 | 3.7401e-06 | 0.092611 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10730 | STAFFORD 1101344092 | 43201101 | STAFFORD 1101 | 115.3192 | 0.071671 | 2 | 2.4736e-05 | 1.2368e-05 | 3033 | 25665.0846 | 0.092586 | 3.7391e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2899 | PLACER 1101208930 | 152461101 | PLACER 1101 | 187.1265 | 0.1163 | 10 | 0.00012302 | 1.2302e-05 | 3034 | 25665.2009 | 0.092463 | 3.7341e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3721 | SHINGLE SPRINGS 210511172 | 153652105 | SHINGLE SPRINGS 2105 | 3218.2333 | 2.0001 | 38 | 0.00045612 | 1.2003e-05 | 3035 | 25667.2011 | 0.092007 | 3.7157e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8829 | MONTE RIO 1111CB | 42811111 | MONTE RIO 1111 | 408.9065 | 0.25414 | 4 | 4.7378e-05 | 1.1845e-05 | 3036 | 25667.4552 | 0.09196 | 3.7138e-06 | 0.09196 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3789 | LOS GATOS 1106LA46 | 82021106 | LOS GATOS 1106 | 2411.7925 | 1.4989 | 20 | 0.00023387 | 1.1694e-05 | 3037 | 25668.9541 | 0.091726 | 3.7044e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8577 | SARATOGA 1115463510 | 83371115 | SARATOGA 1115 | 4697.8741 | 2.9197 | 41 | 0.00047756 | 1.1648e-05 | 3038 | 25671.8739 | 0.091248 | 3.6851e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8231 | HALF MOON BAY 11038898 | 24101103 | HALF MOON BAY 1103 | 1034.8013 | 0.64313 | 9 | 0.00010403 | 1.1558e-05 | 3039 | 25672.517 | 0.091144 | 3.6809e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3716 | CASTRO VALLEY 1102MR359 | 14091102 | CASTRO VALLEY 1102 | 0 | 0 | 90 | 0.0010328 | 1.1476e-05 | 3040 | 25672.517 | 0.090112 | 3.6392e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9742 | MONROE 210392868 | 43302103 | MONROE 2103 | 203.5363 | 0.1265 | 14 | 0.0001602 | 1.1443e-05 | 3041 | 25672.6435 | 0.089951 | 3.6327e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
830 | OAKLAND X 1104391688 | 12541104 | OAKLAND X 1104 | 2071.721 | 1.2876 | 16 | 0.00018295 | 1.1434e-05 | 3042 | 25673.9311 | 0.089768 | 3.6253e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3807 | CAMP EVERS 210355638 | 83622103 | CAMP EVERS 2103 | 2949.5648 | 1.8332 | 42 | 0.00047946 | 1.1416e-05 | 3043 | 25675.7643 | 0.089289 | 3.6059e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2161 | LAKEWOOD 2227W503R | 13532227 | LAKEWOOD 2227 | 121.8736 | 0.075745 | 89 | 0.0010113 | 1.1363e-05 | 3044 | 25675.84 | 0.088278 | 3.5651e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10225 | CLOVERDALE 1101409224 | 42821101 | CLOVERDALE 1101 | 138.7205 | 0.086215 | 4 | 4.524e-05 | 1.131e-05 | 3045 | 25675.9262 | 0.088232 | 3.5633e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9704 | DEL MAR 210938684 | 152582109 | DEL MAR 2109 | 38.3974 | 0.023864 | 1 | 1.1274e-05 | 1.1274e-05 | 3046 | 25675.9501 | 0.088221 | 3.5628e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6951 | MONTE RIO 1111506 | 42811111 | MONTE RIO 1111 | 2021.7882 | 1.2565 | 18 | 0.00020165 | 1.1203e-05 | 3047 | 25677.2066 | 0.088019 | 3.5547e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7579 | WOODSIDE 11012299 | 24251101 | WOODSIDE 1101 | 2927.8179 | 1.8197 | 25 | 0.00027996 | 1.1198e-05 | 3048 | 25679.0263 | 0.08774 | 3.5434e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4426 | SHINGLE SPRINGS 11038752 | 153651103 | SHINGLE SPRINGS 1103 | 2987.795 | 1.8569 | 32 | 0.00034845 | 1.0889e-05 | 3049 | 25680.8832 | 0.087391 | 3.5293e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3276 | CAMP EVERS 210310946 | 83622103 | CAMP EVERS 2103 | 9098.3132 | 5.6546 | 112 | 0.0012153 | 1.0851e-05 | 3050 | 25686.5379 | 0.086176 | 3.4802e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4220 | OAKLAND X 1104CR214 | 12541104 | OAKLAND X 1104 | 4637.1496 | 2.882 | 35 | 0.00037942 | 1.0841e-05 | 3051 | 25689.4199 | 0.085796 | 3.4649e-06 | 0.085796 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3032 | OAKLAND X 1104CR288 | 12541104 | OAKLAND X 1104 | 4382.4988 | 2.7237 | 46 | 0.00049744 | 1.0814e-05 | 3052 | 25692.1436 | 0.085299 | 3.4448e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3352 | OAKLAND X 1104CR022 | 12541104 | OAKLAND X 1104 | 6467.1642 | 4.0194 | 48 | 0.00051505 | 1.073e-05 | 3053 | 25696.163 | 0.084784 | 3.424e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9828 | ALLEGHANY 11021101/2 | 152101102 | ALLEGHANY 1102 | 31.1897 | 0.019385 | 1 | 1.0723e-05 | 1.0723e-05 | 3054 | 25696.1824 | 0.084773 | 3.4236e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9784 | CAMP EVERS 2104496570 | 83622104 | CAMP EVERS 2104 | 389.3118 | 0.24196 | 8 | 8.5734e-05 | 1.0717e-05 | 3055 | 25696.4243 | 0.084687 | 3.4201e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6309 | MONTE RIO 1113250 | 42811113 | MONTE RIO 1113 | 1985.3414 | 1.2339 | 14 | 0.00014927 | 1.0662e-05 | 3056 | 25697.6582 | 0.084538 | 3.4141e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10893 | FROGTOWN 1702390720 | 163451702 | FROGTOWN 1702 | 202.4448 | 0.12582 | 2 | 2.11e-05 | 1.055e-05 | 3057 | 25697.784 | 0.084517 | 3.4132e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4614 | SAN RAFAEL 11081262 | 42011108 | SAN RAFAEL 1108 | 6311.248 | 3.9225 | 57 | 0.00060016 | 1.0529e-05 | 3058 | 25701.7065 | 0.083917 | 3.389e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9095 | LLAGAS 2107250129 | 83182107 | LLAGAS 2107 | 401.6728 | 0.24964 | 5 | 5.23e-05 | 1.046e-05 | 3059 | 25701.9561 | 0.083865 | 3.3869e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8911 | CAMP EVERS 2106CB | 83622106 | CAMP EVERS 2106 | 1101.4532 | 0.68456 | 37 | 0.00038468 | 1.0397e-05 | 3060 | 25702.6407 | 0.08348 | 3.3713e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10545 | PASO ROBLES 1103451760 | 182611103 | PASO ROBLES 1103 | 98.2563 | 0.061067 | 2 | 2.0594e-05 | 1.0297e-05 | 3061 | 25702.7018 | 0.083459 | 3.3705e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1830 | SANTA ROSA A 1104210 | 42151104 | SANTA ROSA A 1104 | 10477.8716 | 6.512 | 107 | 0.0010973 | 1.0255e-05 | 3062 | 25709.2138 | 0.082362 | 3.3262e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10656 | MIWUK 170179118 | 163661701 | MIWUK 1701 | 31.1564 | 0.019364 | 2 | 2.0475e-05 | 1.0238e-05 | 3063 | 25709.2332 | 0.082342 | 3.3254e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7888 | MONTE RIO 1112212 | 42811112 | MONTE RIO 1112 | 3618.1725 | 2.2487 | 27 | 0.00027631 | 1.0234e-05 | 3064 | 25711.4819 | 0.082065 | 3.3142e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5285 | CAMP EVERS 21061625 | 83622106 | CAMP EVERS 2106 | 1400.9701 | 0.87071 | 10 | 0.00010231 | 1.0231e-05 | 3065 | 25712.3526 | 0.081963 | 3.3101e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7246 | HUMBOLDT BAY 1102104220 | 192341102 | HUMBOLDT BAY 1102 | 1476.8749 | 0.91788 | 45 | 0.00045796 | 1.0177e-05 | 3066 | 25713.2705 | 0.081505 | 3.2916e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3485 | SAN RAFAEL 1107CB | 42011107 | SAN RAFAEL 1107 | 7810.3005 | 4.8541 | 107 | 0.0010689 | 9.9897e-06 | 3067 | 25718.1246 | 0.080436 | 3.2484e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1447 | OAKLAND K 1104CR204 | 12101104 | OAKLAND K 1104 | 6639.5298 | 4.1265 | 49 | 0.00048842 | 9.9677e-06 | 3068 | 25722.2511 | 0.079948 | 3.2287e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10822 | GRASS VALLEY 1103CB | 152031103 | GRASS VALLEY 1103 | 191.1806 | 0.11882 | 2 | 1.9912e-05 | 9.9558e-06 | 3069 | 25722.3699 | 0.079928 | 3.2279e-06 | 0.079928 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3457 | OAKLAND K 1101CR178 | 12101101 | OAKLAND K 1101 | 529.8862 | 0.32933 | 7 | 6.9036e-05 | 9.8623e-06 | 3070 | 25722.6992 | 0.079859 | 3.2251e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3129 | SYCAMORE CREEK 1109CB | 102971109 | SYCAMORE CREEK 1109 | 271.1511 | 0.16852 | 108 | 0.0010632 | 9.8448e-06 | 3071 | 25722.8678 | 0.078795 | 3.1822e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2013 | SHINGLE SPRINGS 210851474 | 153652108 | SHINGLE SPRINGS 2108 | 594.1189 | 0.36925 | 68 | 0.00066905 | 9.839e-06 | 3072 | 25723.237 | 0.078126 | 3.1551e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4677 | MIDDLETOWN 1101932140 | 43141101 | MIDDLETOWN 1101 | 861.7057 | 0.53555 | 15 | 0.00014503 | 9.669e-06 | 3073 | 25723.7726 | 0.077981 | 3.1493e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3638 | WOODSIDE 1104CB | 24251104 | WOODSIDE 1104 | 167.7195 | 0.10424 | 114 | 0.0011016 | 9.6632e-06 | 3074 | 25723.8768 | 0.07688 | 3.1048e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8277 | MONTE RIO 1113532 | 42811113 | MONTE RIO 1113 | 844.3261 | 0.52475 | 8 | 7.6993e-05 | 9.6241e-06 | 3075 | 25724.4016 | 0.076803 | 3.1017e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
854 | SHINGLE SPRINGS 1104CB | 153651104 | SHINGLE SPRINGS 1104 | 1129.2677 | 0.70184 | 32 | 0.00030616 | 9.5675e-06 | 3076 | 25725.1034 | 0.076497 | 3.0893e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6660 | HALSEY 11026129 | 152241102 | HALSEY 1102 | 5155.4944 | 3.2042 | 39 | 0.00037178 | 9.5328e-06 | 3077 | 25728.3076 | 0.076125 | 3.0743e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10561 | BIG RIVER 1101CB | 43081101 | BIG RIVER 1101 | 35.3815 | 0.02199 | 1 | 9.4951e-06 | 9.4951e-06 | 3078 | 25728.3295 | 0.076115 | 3.0739e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4323 | GIRVAN 1102CB | 103401102 | GIRVAN 1102 | 1759.2867 | 1.0934 | 102 | 0.0009662 | 9.4726e-06 | 3079 | 25729.423 | 0.075149 | 3.0349e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5228 | MONTE RIO 11135026 | 42811113 | MONTE RIO 1113 | 2967.0616 | 1.844 | 23 | 0.00021778 | 9.4686e-06 | 3080 | 25731.267 | 0.074931 | 3.0261e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7379 | CALPELLA 1102379946 | 43411102 | CALPELLA 1102 | 1211.8313 | 0.75316 | 15 | 0.0001412 | 9.4131e-06 | 3081 | 25732.0202 | 0.07479 | 3.0204e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8927 | ELK 1101CB | 42981101 | ELK 1101 | 39.9198 | 0.02481 | 1 | 9.4072e-06 | 9.4072e-06 | 3082 | 25732.045 | 0.074781 | 3.02e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6426 | ALTO 1125296476 | 42031125 | ALTO 1125 | 1061.0328 | 0.65944 | 11 | 0.00010339 | 9.3993e-06 | 3083 | 25732.7044 | 0.074677 | 3.0158e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7763 | BRUNSWICK 1105297538 | 152481105 | BRUNSWICK 1105 | 1703.5587 | 1.0588 | 15 | 0.0001405 | 9.367e-06 | 3084 | 25733.7632 | 0.074537 | 3.0102e-06 | 0.074537 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6048 | SILVERADO 2105337226 | 43432105 | SILVERADO 2105 | 458.4827 | 0.28495 | 13 | 0.0001217 | 9.3615e-06 | 3085 | 25734.0481 | 0.074415 | 3.0053e-06 | 0.074415 | #N/A | #N/A | #N/A | #N/A | #VALUE!
785 | MIRABEL 1102CB | 42091102 | MIRABEL 1102 | 358.8557 | 0.22303 | 85 | 0.00078931 | 9.286e-06 | 3086 | 25734.2711 | 0.073626 | 2.9734e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10915 | CLARKSVILLE 210551478 | 153612105 | CLARKSVILLE 2105 | 81.0541 | 0.050375 | 3 | 2.7745e-05 | 9.2483e-06 | 3087 | 25734.3215 | 0.073598 | 2.9723e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3642 | AUBURN 1102CB | 152161102 | AUBURN 1102 | 2237.7238 | 1.3908 | 99 | 0.00091369 | 9.2292e-06 | 3088 | 25735.7123 | 0.072684 | 2.9354e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10606 | BERKELEY F 1105BR166 | 12061105 | BERKELEY F 1105 | 61.4345 | 0.038182 | 2 | 1.8446e-05 | 9.2229e-06 | 3089 | 25735.7505 | 0.072666 | 2.9346e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2771 | RIO DELL 1102CB | 192251102 | RIO DELL 1102 | 0 | 0 | 86 | 0.0007924 | 9.2139e-06 | 3090 | 25735.7505 | 0.071874 | 2.9026e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10346 | EEL RIVER 1103241646 | 192381103 | EEL RIVER 1103 | 583.4204 | 0.3626 | 13 | 0.00011881 | 9.1396e-06 | 3091 | 25736.1131 | 0.071755 | 2.8978e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
964 | SAN RAFAEL 110991742 | 42011109 | SAN RAFAEL 1109 | 3844.7445 | 2.3895 | 67 | 0.00060425 | 9.0186e-06 | 3092 | 25738.5026 | 0.07115 | 2.8734e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5348 | EEL RIVER 11033820 | 192381103 | EEL RIVER 1103 | 0 | 0 | 115 | 0.0010334 | 8.9864e-06 | 3093 | 25738.5026 | 0.070117 | 2.8317e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3020 | SARATOGA 1104209146 | 83371104 | SARATOGA 1104 | 4936.2554 | 3.0679 | 85 | 0.00076238 | 8.9692e-06 | 3094 | 25741.5705 | 0.069355 | 2.8009e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10029 | MONTICELLO 11011780 | 43051101 | MONTICELLO 1101 | 115.3297 | 0.071678 | 1 | 8.9608e-06 | 8.9608e-06 | 3095 | 25741.6422 | 0.069346 | 2.8005e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10582 | OAKLAND X 1101328808 | 12541101 | OAKLAND X 1101 | 186.4686 | 0.11589 | 1 | 8.9528e-06 | 8.9528e-06 | 3096 | 25741.7581 | 0.069337 | 2.8002e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8839 | BIG BASIN 11026219 | 82841102 | BIG BASIN 1102 | 1488.6262 | 0.92519 | 11 | 9.662e-05 | 8.7836e-06 | 3097 | 25742.6832 | 0.06924 | 2.7963e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2096 | CALISTOGA 1102184814 | 42711102 | CALISTOGA 1102 | 682.245 | 0.42402 | 20 | 0.00017414 | 8.707e-06 | 3098 | 25743.1073 | 0.069066 | 2.7892e-06 | 0.069066 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10342 | FROGTOWN 1702832694 | 163451702 | FROGTOWN 1702 | 461.5634 | 0.28686 | 5 | 4.3529e-05 | 8.7057e-06 | 3099 | 25743.3941 | 0.069022 | 2.7875e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2914 | EUREKA E 110435934 | 192331104 | EUREKA E 1104 | 78.4109 | 0.048733 | 46 | 0.00039863 | 8.6658e-06 | 3100 | 25743.4429 | 0.068624 | 2.7714e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4896 | IGNACIO 1105490728 | 42481105 | IGNACIO 1105 | 1044.2482 | 0.649 | 11 | 9.5291e-05 | 8.6628e-06 | 3101 | 25744.0919 | 0.068529 | 2.7675e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9315 | LAKEWOOD 2224798018 | 13532224 | LAKEWOOD 2224 | 1448.3137 | 0.90013 | 13 | 0.00011235 | 8.6422e-06 | 3102 | 25744.992 | 0.068416 | 2.763e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9391 | WATERSHED 0402CB | 24240402 | WATERSHED 0402 | 342.98 | 0.21316 | 11 | 9.5055e-05 | 8.6414e-06 | 3103 | 25745.2052 | 0.068321 | 2.7592e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9903 | PACIFICA 1102894156 | 22811102 | PACIFICA 1102 | 625.3701 | 0.38867 | 4 | 3.4445e-05 | 8.6111e-06 | 3104 | 25745.5938 | 0.068287 | 2.7578e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7834 | GREENBRAE 1103718674 | 43091103 | GREENBRAE 1103 | 1301.8094 | 0.80908 | 16 | 0.00013775 | 8.6092e-06 | 3105 | 25746.4029 | 0.068149 | 2.7522e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10810 | PLACERVILLE 1111610322 | 153081111 | PLACERVILLE 1111 | 220.6867 | 0.13716 | 3 | 2.578e-05 | 8.5935e-06 | 3106 | 25746.5401 | 0.068123 | 2.7512e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10497 | FORT ORD 21069658 | 182402106 | FORT ORD 2106 | 156.0125 | 0.096962 | 3 | 2.5485e-05 | 8.4949e-06 | 3107 | 25746.637 | 0.068098 | 2.7501e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5369 | OAKLAND K 1104CR206 | 12101104 | OAKLAND K 1104 | 2877.1568 | 1.7882 | 22 | 0.00018585 | 8.4479e-06 | 3108 | 25748.4252 | 0.067912 | 2.7426e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6668 | PAUL SWEET 21075291 | 83252107 | PAUL SWEET 2107 | 50.439 | 0.031348 | 14 | 0.00011792 | 8.4226e-06 | 3109 | 25748.4565 | 0.067794 | 2.7379e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4822 | CAMP EVERS 21035404 | 83622103 | CAMP EVERS 2103 | 4377.7978 | 2.7208 | 63 | 0.00053014 | 8.4149e-06 | 3110 | 25751.1774 | 0.067264 | 2.7165e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10986 | RINCON 1101205854 | 43321101 | RINCON 1101 | 505.1079 | 0.31393 | 5 | 4.1826e-05 | 8.3652e-06 | 3111 | 25751.4913 | 0.067222 | 2.7148e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1364 | CAMP EVERS 21035402 | 83622103 | CAMP EVERS 2103 | 4595.9767 | 2.8564 | 87 | 0.00072413 | 8.3234e-06 | 3112 | 25754.3477 | 0.066498 | 2.6855e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9661 | SARATOGA 1105431214 | 83371105 | SARATOGA 1105 | 500.3272 | 0.31096 | 9 | 7.4772e-05 | 8.308e-06 | 3113 | 25754.6587 | 0.066423 | 2.6825e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6999 | JESSUP 1102158468 | 103441102 | JESSUP 1102 | 1120.0792 | 0.69613 | 11 | 9.1369e-05 | 8.3063e-06 | 3114 | 25755.3548 | 0.066332 | 2.6788e-06 | 0.066332 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7019 | FORT BRAGG A 1102816 | 42761102 | FORT BRAGG A 1102 | 3941.7419 | 2.4498 | 29 | 0.00023898 | 8.2407e-06 | 3115 | 25757.8046 | 0.066093 | 2.6692e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9287 | SOBRANTE 1103N510R | 14671103 | SOBRANTE 1103 | 401.7471 | 0.24969 | 15 | 0.00012334 | 8.2224e-06 | 3116 | 25758.0543 | 0.065969 | 2.6642e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10537 | FROGTOWN 1702798032 | 163451702 | FROGTOWN 1702 | 244.5065 | 0.15196 | 2 | 1.6394e-05 | 8.1969e-06 | 3117 | 25758.2062 | 0.065953 | 2.6635e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7405 | HARRIS 11082062 | 192431108 | HARRIS 1108 | 2556.2544 | 1.5887 | 83 | 0.00067739 | 8.1613e-06 | 3118 | 25759.795 | 0.065276 | 2.6362e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3886 | SAN RAFAEL 11081457 | 42011108 | SAN RAFAEL 1108 | 1229.3805 | 0.76406 | 9 | 7.3385e-05 | 8.1539e-06 | 3119 | 25760.559 | 0.065202 | 2.6332e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9639 | IGNACIO 1105967039 | 42481105 | IGNACIO 1105 | 292.9124 | 0.18205 | 3 | 2.4417e-05 | 8.139e-06 | 3120 | 25760.7411 | 0.065178 | 2.6322e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10422 | OAKLAND J 1102CR102 | 12091102 | OAKLAND J 1102 | 316.3322 | 0.1966 | 6 | 4.8501e-05 | 8.0835e-06 | 3121 | 25760.9377 | 0.065129 | 2.6302e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10726 | CALISTOGA 1102960240 | 42711102 | CALISTOGA 1102 | 816.2732 | 0.50732 | 5 | 4.0394e-05 | 8.0789e-06 | 3122 | 25761.445 | 0.065089 | 2.6286e-06 | 0.065089 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9181 | MIWUK 1702531976 | 163661702 | MIWUK 1702 | 2102.4835 | 1.3067 | 17 | 0.0001364 | 8.0236e-06 | 3123 | 25762.7517 | 0.064952 | 2.6231e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10385 | ALLEGHANY 11011101/2 | 152101101 | ALLEGHANY 1101 | 36.9839 | 0.022986 | 1 | 8.0126e-06 | 8.0126e-06 | 3124 | 25762.7747 | 0.064944 | 2.6228e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9316 | FORT BRAGG A 1103284356 | 42761103 | FORT BRAGG A 1103 | 218.127 | 0.13557 | 4 | 3.1961e-05 | 7.9902e-06 | 3125 | 25762.9103 | 0.064913 | 2.6215e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10880 | OAKLAND X 1104CR101 | 12541104 | OAKLAND X 1104 | 28.3921 | 0.017646 | 1 | 7.9011e-06 | 7.9011e-06 | 3126 | 25762.9279 | 0.064905 | 2.6212e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4441 | OAKLAND X 1101CR224 | 12541101 | OAKLAND X 1101 | 656.3547 | 0.40793 | 17 | 0.0001342 | 7.8938e-06 | 3127 | 25763.3358 | 0.06477 | 2.6158e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10513 | OILFIELDS 1103441010 | 182391103 | OILFIELDS 1103 | 592.4873 | 0.36823 | 4 | 3.1509e-05 | 7.8772e-06 | 3128 | 25763.7041 | 0.064739 | 2.6145e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1793 | SAN RAFAEL 1109535284 | 42011109 | SAN RAFAEL 1109 | 10.8615 | 0.0067505 | 9 | 7.0747e-05 | 7.8608e-06 | 3129 | 25763.7108 | 0.064668 | 2.6116e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8925 | FRUITLAND 11418746 | 192311141 | FRUITLAND 1141 | 645.6965 | 0.4013 | 8 | 6.2573e-05 | 7.8216e-06 | 3130 | 25764.1121 | 0.064606 | 2.6091e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8734 | LOS GATOS 110160052 | 82021101 | LOS GATOS 1101 | 3169.0097 | 1.9696 | 28 | 0.00021853 | 7.8045e-06 | 3131 | 25766.0817 | 0.064387 | 2.6003e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6798 | SAN CARLOS 110475210 | 24181104 | SAN CARLOS 1104 | 618.926 | 0.38467 | 6 | 4.6387e-05 | 7.7312e-06 | 3132 | 25766.4663 | 0.064341 | 2.5984e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6381 | OAKLAND X 1106CR008 | 12541106 | OAKLAND X 1106 | 7178.6151 | 4.4615 | 65 | 0.00050098 | 7.7074e-06 | 3133 | 25770.9279 | 0.06384 | 2.5782e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10638 | SAN RAFAEL 11092213 | 42011109 | SAN RAFAEL 1109 | 689.8513 | 0.42875 | 6 | 4.6136e-05 | 7.6893e-06 | 3134 | 25771.3566 | 0.063794 | 2.5763e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9009 | ALTO 1124553571 | 42031124 | ALTO 1124 | 174.9029 | 0.1087 | 4 | 3.0647e-05 | 7.6617e-06 | 3135 | 25771.4653 | 0.063763 | 2.5751e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1292 | EEL RIVER 1103CB | 192381103 | EEL RIVER 1103 | 0 | 0 | 374 | 0.0028614 | 7.6507e-06 | 3136 | 25771.4653 | 0.060902 | 2.4595e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2486 | LOYOLA 110260082 | 82161102 | LOYOLA 1102 | 0 | 0 | 57 | 0.00043592 | 7.6477e-06 | 3137 | 25771.4653 | 0.060466 | 2.4419e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9942 | BRUNSWICK 1104327226 | 152481104 | BRUNSWICK 1104 | 79.5833 | 0.049461 | 2 | 1.5292e-05 | 7.6459e-06 | 3138 | 25771.5148 | 0.06045 | 2.4413e-06 | 0.06045 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10778 | PIT NO 5 110190846 | 101321101 | PIT NO 5 1101 | 149.205 | 0.092731 | 2 | 1.5217e-05 | 7.6083e-06 | 3139 | 25771.6075 | 0.060435 | 2.4407e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9691 | STELLING 1109787007 | 83481109 | STELLING 1109 | 307.1886 | 0.19092 | 5 | 3.7958e-05 | 7.5915e-06 | 3140 | 25771.7984 | 0.060397 | 2.4391e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1439 | TAR FLAT 0402CB | 163240402 | TAR FLAT 0402 | 1281.2412 | 0.7963 | 18 | 0.00013659 | 7.5882e-06 | 3141 | 25772.5947 | 0.060261 | 2.4336e-06 | 0.060261 | #N/A | #N/A | #N/A | #N/A | #VALUE!
4239 | TAR FLAT 0401CB | 163240401 | TAR FLAT 0401 | 5623.7964 | 3.4952 | 45 | 0.00034092 | 7.5759e-06 | 3142 | 25776.0899 | 0.05992 | 2.4199e-06 | 0.05992 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6173 | OAKLAND X 1104645092 | 12541104 | OAKLAND X 1104 | 2229.6022 | 1.3857 | 16 | 0.00012085 | 7.5529e-06 | 3143 | 25777.4756 | 0.059799 | 2.415e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9734 | HIGHLANDS 110484640 | 43361104 | HIGHLANDS 1104 | 660.5476 | 0.41053 | 14 | 0.00010543 | 7.5307e-06 | 3144 | 25777.8862 | 0.059693 | 2.4107e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10502 | TRIDAM POWERHOUSE 2101CB | 168152101 | TRIDAM POWERHOUSE 2101 | 80.9954 | 0.050339 | 3 | 2.2433e-05 | 7.4775e-06 | 3145 | 25777.9365 | 0.059671 | 2.4098e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3266 | UKIAH 1113658899 | 42771113 | UKIAH 1113 | 941.3759 | 0.58507 | 8 | 5.9729e-05 | 7.4661e-06 | 3146 | 25778.5216 | 0.059611 | 2.4074e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10496 | FROGTOWN 1702814784 | 163451702 | FROGTOWN 1702 | 280.0552 | 0.17406 | 3 | 2.2342e-05 | 7.4475e-06 | 3147 | 25778.6956 | 0.059589 | 2.4065e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9921 | OAKLAND X 1106CR266 | 12541106 | OAKLAND X 1106 | 1901.6084 | 1.1819 | 8 | 5.9368e-05 | 7.421e-06 | 3148 | 25779.8775 | 0.05953 | 2.4041e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7361 | SARATOGA 11076867 | 83371107 | SARATOGA 1107 | 985.9493 | 0.61277 | 11 | 8.155e-05 | 7.4136e-06 | 3149 | 25780.4903 | 0.059448 | 2.4008e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7276 | SAN CARLOS 11049052 | 24181104 | SAN CARLOS 1104 | 7722.3255 | 4.7995 | 65 | 0.00048153 | 7.4082e-06 | 3150 | 25785.2897 | 0.058966 | 2.3814e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9123 | UKIAH 1114296894 | 42771114 | UKIAH 1114 | 278.1636 | 0.17288 | 6 | 4.4388e-05 | 7.398e-06 | 3151 | 25785.4626 | 0.058922 | 2.3796e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10484 | SANTA ROSA A 1111407286 | 42151111 | SANTA ROSA A 1111 | 98.0196 | 0.06092 | 1 | 7.3466e-06 | 7.3466e-06 | 3152 | 25785.5235 | 0.058915 | 2.3793e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6588 | HARRIS 1108705523 | 192431108 | HARRIS 1108 | 321.9298 | 0.20008 | 11 | 8.0224e-05 | 7.293e-06 | 3153 | 25785.7236 | 0.058834 | 2.376e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3678 | RESEARCH 2102183888 | 14692102 | RESEARCH 2102 | 1898.9745 | 1.1802 | 43 | 0.00031108 | 7.2344e-06 | 3154 | 25786.9038 | 0.058523 | 2.3635e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9265 | ROSSMOOR 1104892332 | 14161104 | ROSSMOOR 1104 | 410.223 | 0.25496 | 4 | 2.8814e-05 | 7.2035e-06 | 3155 | 25787.1588 | 0.058495 | 2.3623e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5151 | EDES 1112CR312 | 13681112 | EDES 1112 | 5934.1286 | 3.6881 | 42 | 0.00030194 | 7.189e-06 | 3156 | 25790.8469 | 0.058193 | 2.3501e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6055 | SILVERADO 2105191725 | 43432105 | SILVERADO 2105 | 558.1402 | 0.34689 | 8 | 5.7337e-05 | 7.1671e-06 | 3157 | 25791.1938 | 0.058135 | 2.3478e-06 | 0.058135 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8973 | DIAMOND SPRINGS 1103394169 | 152261103 | DIAMOND SPRINGS 1103 | 642.0804 | 0.39906 | 7 | 5.0037e-05 | 7.1481e-06 | 3158 | 25791.5928 | 0.058085 | 2.3458e-06 | 0.058085 | #N/A | #N/A | #N/A | #N/A | #VALUE!
9966 | MONROE 2107380760 | 43302107 | MONROE 2107 | 1053.0262 | 0.65446 | 12 | 8.5741e-05 | 7.1451e-06 | 3159 | 25792.2473 | 0.058 | 2.3423e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2463 | OAKLAND K 1103CR188 | 12101103 | OAKLAND K 1103 | 5760.2047 | 3.58 | 47 | 0.00033573 | 7.1432e-06 | 3160 | 25795.8273 | 0.057664 | 2.3288e-06 | 0.057664 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7755 | HICKS 1116983580 | 83431116 | HICKS 1116 | 3958.5011 | 2.4602 | 33 | 0.00023563 | 7.1402e-06 | 3161 | 25798.2875 | 0.057428 | 2.3192e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2292 | OAKLAND K 1104CR326 | 12101104 | OAKLAND K 1104 | 2098.9601 | 1.3045 | 17 | 0.00012068 | 7.0989e-06 | 3162 | 25799.592 | 0.057307 | 2.3144e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10476 | SAN RAFAEL 1106618957 | 42011106 | SAN RAFAEL 1106 | 301.119 | 0.18715 | 4 | 2.8257e-05 | 7.0643e-06 | 3163 | 25799.7791 | 0.057279 | 2.3132e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3538 | CORTINA 1101302192 | 63121101 | CORTINA 1101 | 0 | 0 | 79 | 0.00055773 | 7.0599e-06 | 3164 | 25799.7791 | 0.056721 | 2.2907e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3533 | OAKLAND K 1104432850 | 12101104 | OAKLAND K 1104 | 1988.3274 | 1.2358 | 26 | 0.0001817 | 6.9884e-06 | 3165 | 25801.0149 | 0.05654 | 2.2834e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9797 | DEL MONTE 21032204 | 182222103 | DEL MONTE 2103 | 592.6413 | 0.36833 | 8 | 5.5825e-05 | 6.9782e-06 | 3166 | 25801.3832 | 0.056484 | 2.2811e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10205 | BERKELEY F 1103813976 | 12061103 | BERKELEY F 1103 | 312.2978 | 0.19409 | 4 | 2.7769e-05 | 6.9422e-06 | 3167 | 25801.5773 | 0.056456 | 2.28e-06 | 0.056456 | #N/A | #N/A | #N/A | #N/A | #VALUE!
398 | ROSSMOOR 1104CB | 14161104 | ROSSMOOR 1104 | 0 | 0 | 150 | 0.0010384 | 6.9228e-06 | 3168 | 25801.5773 | 0.055418 | 2.2381e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
465 | MOLINO 1102111666 | 42571102 | MOLINO 1102 | 182.6023 | 0.11349 | 13 | 8.9978e-05 | 6.9214e-06 | 3169 | 25801.6908 | 0.055328 | 2.2344e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9817 | SUMMIT 11016627 | 152591101 | SUMMIT 1101 | 910.3808 | 0.56581 | 8 | 5.5291e-05 | 6.9114e-06 | 3170 | 25802.2566 | 0.055273 | 2.2322e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6657 | SAN RAFAEL 110168970 | 42011101 | SAN RAFAEL 1101 | 75.6257 | 0.047002 | 44 | 0.00030325 | 6.892e-06 | 3171 | 25802.3036 | 0.054969 | 2.2199e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8713 | GANSNER 1101489276 | 103021101 | GANSNER 1101 | 723.7002 | 0.44978 | 9 | 6.1691e-05 | 6.8546e-06 | 3172 | 25802.7534 | 0.054908 | 2.2174e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6405 | ROB ROY 210571630 | 83692105 | ROB ROY 2105 | 2182.1843 | 1.3562 | 26 | 0.00017743 | 6.8241e-06 | 3173 | 25804.1096 | 0.05473 | 2.2103e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1284 | SARATOGA 1106LC22 | 83371106 | SARATOGA 1106 | 12038.7869 | 7.4822 | 114 | 0.00077774 | 6.8223e-06 | 3174 | 25811.5918 | 0.053952 | 2.1789e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4762 | SAN RAFAEL 110668694 | 42011106 | SAN RAFAEL 1106 | 0 | 0 | 32 | 0.00021675 | 6.7736e-06 | 3175 | 25811.5918 | 0.053736 | 2.1701e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9002 | PAUL SWEET 2102168368 | 83252102 | PAUL SWEET 2102 | 590.4471 | 0.36697 | 8 | 5.3993e-05 | 6.7491e-06 | 3176 | 25811.9588 | 0.053682 | 2.1679e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8371 | RINCON 1102782389 | 43321102 | RINCON 1102 | 585.9597 | 0.36418 | 8 | 5.3721e-05 | 6.7151e-06 | 3177 | 25812.3229 | 0.053628 | 2.1658e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7829 | UKIAH 111472990 | 42771114 | UKIAH 1114 | 1175.6663 | 0.73068 | 38 | 0.00025516 | 6.7147e-06 | 3178 | 25813.0536 | 0.053373 | 2.1555e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4895 | SARATOGA 1103LC16 | 83371103 | SARATOGA 1103 | 6889.2884 | 4.2817 | 72 | 0.00048284 | 6.7061e-06 | 3179 | 25817.3353 | 0.05289 | 2.136e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2902 | WAYNE 0401954811 | 13810401 | WAYNE 0401 | 282.8935 | 0.17582 | 9 | 6.0349e-05 | 6.7055e-06 | 3180 | 25817.5111 | 0.05283 | 2.1335e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6002 | SAN RAFAEL 1105818262 | 42011105 | SAN RAFAEL 1105 | 292.9133 | 0.18205 | 11 | 7.3231e-05 | 6.6573e-06 | 3181 | 25817.6932 | 0.052756 | 2.1306e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9719 | PIT NO 5 11011614 | 101321101 | PIT NO 5 1101 | 3000.4112 | 1.8648 | 5 | 3.3257e-05 | 6.6513e-06 | 3182 | 25819.558 | 0.052723 | 2.1292e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5122 | RIDGE 0401CB | 12840401 | RIDGE 0401 | 4270.3121 | 2.654 | 36 | 0.00023916 | 6.6432e-06 | 3183 | 25822.212 | 0.052484 | 2.1196e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1193 | FORT BRAGG A 1102418 | 42761102 | FORT BRAGG A 1102 | 22539.2945 | 14.0083 | 178 | 0.0011785 | 6.6205e-06 | 3184 | 25836.2202 | 0.051305 | 2.072e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8138 | FRANKLIN 1101P138 | 13921101 | FRANKLIN 1101 | 2259.003 | 1.404 | 15 | 9.8527e-05 | 6.5684e-06 | 3185 | 25837.6242 | 0.051207 | 2.068e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11032 | HIGHLANDS 1101CB | 43361101 | HIGHLANDS 1101 | 42.5019 | 0.026415 | 1 | 6.536e-06 | 6.536e-06 | 3186 | 25837.6506 | 0.0512 | 2.0677e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3671 | CAMP EVERS 2104CB | 83622104 | CAMP EVERS 2104 | 629.206 | 0.39105 | 71 | 0.00046338 | 6.5265e-06 | 3187 | 25838.0417 | 0.050737 | 2.049e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8113 | WOODSIDE 110411555 | 24251104 | WOODSIDE 1104 | 1379.9837 | 0.85767 | 11 | 7.165e-05 | 6.5136e-06 | 3188 | 25838.8994 | 0.050665 | 2.0461e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8611 | CAROLANDS 04018888 | 24060401 | CAROLANDS 0401 | 0 | 0 | 25 | 0.0001627 | 6.5082e-06 | 3189 | 25838.8994 | 0.050503 | 2.0396e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10705 | CLOVERDALE 1102801904 | 42821102 | CLOVERDALE 1102 | 22.3881 | 0.013914 | 1 | 6.5066e-06 | 6.5066e-06 | 3190 | 25838.9133 | 0.050496 | 2.0393e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7620 | CASTRO VALLEY 1110MR341 | 14091110 | CASTRO VALLEY 1110 | 417.225 | 0.25931 | 11 | 7.1529e-05 | 6.5027e-06 | 3191 | 25839.1726 | 0.050425 | 2.0364e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6399 | ROB ROY 21049973 | 83692104 | ROB ROY 2104 | 921.5182 | 0.57273 | 7 | 4.5461e-05 | 6.4944e-06 | 3192 | 25839.7453 | 0.050379 | 2.0346e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4710 | VIEJO 220255787 | 182852202 | VIEJO 2202 | 58.9251 | 0.036622 | 1 | 6.491e-06 | 6.491e-06 | 3193 | 25839.7819 | 0.050373 | 2.0343e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3931 | LAS AROMAS 04013342 | 13600401 | LAS AROMAS 0401 | 3691.7497 | 2.2944 | 30 | 0.00019206 | 6.402e-06 | 3194 | 25842.0764 | 0.050181 | 2.0265e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
738 | SAN RAFAEL 1104CB | 42011104 | SAN RAFAEL 1104 | 5560.2483 | 3.4557 | 140 | 0.00089393 | 6.3852e-06 | 3195 | 25845.5321 | 0.049287 | 1.9904e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9201 | HICKS 1116583284 | 83431116 | HICKS 1116 | 236.5766 | 0.14703 | 4 | 2.5347e-05 | 6.3368e-06 | 3196 | 25845.6791 | 0.049261 | 1.9894e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7050 | EAST QUINCY 1101678650 | 102551101 | EAST QUINCY 1101 | 1808.9819 | 1.1243 | 14 | 8.7903e-05 | 6.2788e-06 | 3197 | 25846.8034 | 0.049173 | 1.9859e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9107 | OAKLAND K 1103CR422 | 12101103 | OAKLAND K 1103 | 3238.2816 | 2.0126 | 24 | 0.00015049 | 6.2703e-06 | 3198 | 25848.816 | 0.049023 | 1.9798e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2296 | LAURELES 11112028 | 182371111 | LAURELES 1111 | 14048.0686 | 8.7309 | 107 | 0.00066966 | 6.2585e-06 | 3199 | 25857.5469 | 0.048353 | 1.9528e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4668 | KONOCTI 11084041 | 43311108 | KONOCTI 1108 | 2174.4689 | 1.3514 | 54 | 0.00033741 | 6.2484e-06 | 3200 | 25858.8984 | 0.048016 | 1.9391e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4517 | SILVERADO 2105CB | 43432105 | SILVERADO 2105 | 1011.6246 | 0.62873 | 66 | 0.00041127 | 6.2313e-06 | 3201 | 25859.5271 | 0.047605 | 1.9225e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1407 | SAN RAFAEL 11061230 | 42011106 | SAN RAFAEL 1106 | 1747.5573 | 1.0861 | 57 | 0.00035473 | 6.2233e-06 | 3202 | 25860.6132 | 0.04725 | 1.9082e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7332 | LOS GATOS 1101184035 | 82021101 | LOS GATOS 1101 | 905.936 | 0.56304 | 9 | 5.4649e-05 | 6.0721e-06 | 3203 | 25861.1763 | 0.047195 | 1.906e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10579 | SAN CARLOS 11049048 | 24181104 | SAN CARLOS 1104 | 24.5909 | 0.015283 | 1 | 6.06e-06 | 6.06e-06 | 3204 | 25861.1916 | 0.047189 | 1.9057e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2032 | LUCERNE 11031663 | 43351103 | LUCERNE 1103 | 1947.6462 | 1.2105 | 17 | 0.00010289 | 6.0525e-06 | 3205 | 25862.402 | 0.047086 | 1.9016e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9700 | SAN RAMON 2103MR279 | 14232103 | SAN RAMON 2103 | 4.572 | 0.0028415 | 5 | 3.0261e-05 | 6.0521e-06 | 3206 | 25862.4049 | 0.047056 | 1.9004e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5325 | SAN RAFAEL 1105534 | 42011105 | SAN RAFAEL 1105 | 1569.6662 | 0.97555 | 22 | 0.00013284 | 6.0384e-06 | 3207 | 25863.3804 | 0.046923 | 1.895e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8122 | HATTON 1101CB | 182291101 | HATTON 1101 | 2551.5911 | 1.5858 | 22 | 0.0001325 | 6.0227e-06 | 3208 | 25864.9662 | 0.046791 | 1.8896e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6886 | ALTO 1124526955 | 42031124 | ALTO 1124 | 713.9611 | 0.44373 | 6 | 3.608e-05 | 6.0133e-06 | 3209 | 25865.41 | 0.046755 | 1.8882e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5909 | CAMP EVERS 210392582 | 83622103 | CAMP EVERS 2103 | 245.7655 | 0.15274 | 41 | 0.00024599 | 5.9997e-06 | 3210 | 25865.5627 | 0.046509 | 1.8783e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6632 | SAN RAFAEL 1106588020 | 42011106 | SAN RAFAEL 1106 | 385.2385 | 0.23943 | 19 | 0.00011382 | 5.9904e-06 | 3211 | 25865.8021 | 0.046395 | 1.8737e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
763 | LOS GATOS 1108LB86 | 82021108 | LOS GATOS 1108 | 7270.7679 | 4.5188 | 69 | 0.00041026 | 5.9458e-06 | 3212 | 25870.321 | 0.045985 | 1.8571e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10570 | EL CERRITO G 1105BR164 | 12501105 | EL CERRITO G 1105 | 91.5845 | 0.05692 | 2 | 1.1874e-05 | 5.9372e-06 | 3213 | 25870.3779 | 0.045973 | 1.8566e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9932 | ALTO 1125291744 | 42031125 | ALTO 1125 | 195.7909 | 0.12168 | 3 | 1.7783e-05 | 5.9276e-06 | 3214 | 25870.4996 | 0.045955 | 1.8559e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8178 | DOLAN ROAD 1101156268 | 182381101 | DOLAN ROAD 1101 | 52.7453 | 0.032781 | 31 | 0.00018333 | 5.914e-06 | 3215 | 25870.5323 | 0.045772 | 1.8485e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6600 | VIEJO 2202CB | 182852202 | VIEJO 2202 | 3450.2108 | 2.1443 | 23 | 0.00013588 | 5.9077e-06 | 3216 | 25872.6767 | 0.045636 | 1.843e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4067 | LAS AROMAS 0401LA401R | 13600401 | LAS AROMAS 0401 | 4956.3951 | 3.0804 | 55 | 0.00032487 | 5.9068e-06 | 3217 | 25875.7571 | 0.045311 | 1.8299e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
807 | RESEARCH 210263274 | 14692102 | RESEARCH 2102 | 74.3652 | 0.046218 | 119 | 0.00069789 | 5.8646e-06 | 3218 | 25875.8033 | 0.044613 | 1.8017e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10104 | LAKEWOOD 1102964292 | 13531102 | LAKEWOOD 1102 | 128.1599 | 0.079652 | 2 | 1.1714e-05 | 5.8569e-06 | 3219 | 25875.8829 | 0.044601 | 1.8012e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8987 | ROSSMOOR 110181770 | 14161101 | ROSSMOOR 1101 | 110.4225 | 0.068628 | 21 | 0.00012184 | 5.8019e-06 | 3220 | 25875.9516 | 0.044479 | 1.7963e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9943 | FRANKLIN 1104P136 | 13921104 | FRANKLIN 1104 | 7931.4997 | 4.9295 | 43 | 0.00024939 | 5.7997e-06 | 3221 | 25880.881 | 0.04423 | 1.7862e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9679 | DOBBINS 1101CB | 153741101 | DOBBINS 1101 | 1079.0936 | 0.67066 | 8 | 4.6369e-05 | 5.7961e-06 | 3222 | 25881.5517 | 0.044184 | 1.7844e-06 | 0.044184 | #N/A | #N/A | #N/A | #N/A | #VALUE!
734 | SILVERADO 21051308 | 43432105 | SILVERADO 2105 | 244.9631 | 0.15225 | 60 | 0.00034724 | 5.7874e-06 | 3223 | 25881.7039 | 0.043836 | 1.7703e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5907 | ORINDA 0401401/2 LR | 12350401 | ORINDA 0401 | 158.249 | 0.098352 | 4 | 2.3093e-05 | 5.7731e-06 | 3224 | 25881.8023 | 0.043813 | 1.7694e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
648 | KONOCTI 11084039 | 43311108 | KONOCTI 1108 | 3048.4169 | 1.8946 | 32 | 0.00018435 | 5.7609e-06 | 3225 | 25883.6969 | 0.043629 | 1.762e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5547 | KONOCTI 11084037 | 43311108 | KONOCTI 1108 | 1840.2464 | 1.1437 | 22 | 0.0001266 | 5.7543e-06 | 3226 | 25884.8406 | 0.043502 | 1.7568e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3274 | RACETRACK 170310850 | 163761703 | RACETRACK 1703 | 994.8842 | 0.61832 | 28 | 0.00015971 | 5.704e-06 | 3227 | 25885.4589 | 0.043343 | 1.7504e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5740 | SUMMIT 110148636 | 152591101 | SUMMIT 1101 | 86.4222 | 0.053712 | 38 | 0.00021607 | 5.6861e-06 | 3228 | 25885.5127 | 0.043127 | 1.7417e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8762 | VASONA 1102944560 | 83771102 | VASONA 1102 | 282.6401 | 0.17566 | 9 | 5.0971e-05 | 5.6635e-06 | 3229 | 25885.6883 | 0.043076 | 1.7396e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5538 | BERKELEY F 1103162952 | 12061103 | BERKELEY F 1103 | 2846.7585 | 1.7693 | 25 | 0.00014146 | 5.6583e-06 | 3230 | 25887.4576 | 0.042934 | 1.7339e-06 | 0.042934 | #N/A | #N/A | #N/A | #N/A | #VALUE!
319 | DUNBAR 1103725292 | 43071103 | DUNBAR 1103 | 339.5862 | 0.21105 | 13 | 7.3554e-05 | 5.658e-06 | 3231 | 25887.6686 | 0.042861 | 1.7309e-06 | 0.042861 | #N/A | #N/A | #N/A | #N/A | #VALUE!
5356 | SOBRANTE 110142914 | 14671101 | SOBRANTE 1101 | 665.6425 | 0.4137 | 51 | 0.00028854 | 5.6577e-06 | 3232 | 25888.0823 | 0.042572 | 1.7193e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4656 | OAKLAND K 1104CR208 | 12101104 | OAKLAND K 1104 | 3895.4111 | 2.421 | 29 | 0.00016371 | 5.6453e-06 | 3233 | 25890.5034 | 0.042408 | 1.7127e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1498 | SAN RAFAEL 1101189400 | 42011101 | SAN RAFAEL 1101 | 4446.7436 | 2.7637 | 45 | 0.00025337 | 5.6305e-06 | 3234 | 25893.267 | 0.042155 | 1.7024e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9302 | NEWBURG 1131987158 | 192151131 | NEWBURG 1131 | 397.6831 | 0.24716 | 2 | 1.1243e-05 | 5.6215e-06 | 3235 | 25893.5142 | 0.042144 | 1.702e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1260 | PALO SECO 0401CB | 13180401 | PALO SECO 0401 | 7634.7258 | 4.745 | 55 | 0.00030885 | 5.6154e-06 | 3236 | 25898.2592 | 0.041835 | 1.6895e-06 | 0.041835 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7087 | OAKLAND K 1101CR170 | 12101101 | OAKLAND K 1101 | 2012.9175 | 1.251 | 17 | 9.4663e-05 | 5.5684e-06 | 3237 | 25899.5102 | 0.04174 | 1.6857e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9325 | TASSAJARA 2108189700 | 14662108 | TASSAJARA 2108 | 306.7254 | 0.19063 | 22 | 0.00012213 | 5.5512e-06 | 3238 | 25899.7009 | 0.041618 | 1.6807e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8529 | ROSSMOOR 110479146 | 14161104 | ROSSMOOR 1104 | 85.6157 | 0.05321 | 28 | 0.00015263 | 5.451e-06 | 3239 | 25899.7541 | 0.041465 | 1.6746e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5159 | PAUL SWEET 2109634576 | 83252109 | PAUL SWEET 2109 | 2935.0444 | 1.8241 | 29 | 0.00015794 | 5.4462e-06 | 3240 | 25901.5782 | 0.041308 | 1.6682e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
176 | TASSAJARA 2108D520R | 14662108 | TASSAJARA 2108 | 0 | 0 | 50 | 0.00027228 | 5.4455e-06 | 3241 | 25901.5782 | 0.041035 | 1.6572e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2934 | LAKEWOOD 210769586 | 13532107 | LAKEWOOD 2107 | 688.9218 | 0.42817 | 80 | 0.00043538 | 5.4423e-06 | 3242 | 25902.0064 | 0.0406 | 1.6396e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2160 | HIGHLANDS 1104CB | 43361104 | HIGHLANDS 1104 | 7661.9306 | 4.7619 | 102 | 0.00055429 | 5.4342e-06 | 3243 | 25906.7683 | 0.040046 | 1.6172e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7487 | GANSNER 1101174072 | 103021101 | GANSNER 1101 | 172.7033 | 0.10734 | 3 | 1.6182e-05 | 5.3939e-06 | 3244 | 25906.8756 | 0.040029 | 1.6166e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10550 | SANTA ROSA A 1104834094 | 42151104 | SANTA ROSA A 1104 | 155.4829 | 0.096633 | 3 | 1.6174e-05 | 5.3913e-06 | 3245 | 25906.9723 | 0.040013 | 1.6159e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6137 | CAROLANDS 04049024 | 24060404 | CAROLANDS 0404 | 5646.8015 | 3.5095 | 62 | 0.00033401 | 5.3873e-06 | 3246 | 25910.4818 | 0.039679 | 1.6024e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8307 | SAN RAFAEL 11042235 | 42011104 | SAN RAFAEL 1104 | 296.6637 | 0.18438 | 10 | 5.3477e-05 | 5.3477e-06 | 3247 | 25910.6662 | 0.039626 | 1.6003e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4970 | CASTRO VALLEY 1110264914 | 14091110 | CASTRO VALLEY 1110 | 1396.6171 | 0.868 | 14 | 7.4507e-05 | 5.3219e-06 | 3248 | 25911.5342 | 0.039551 | 1.5973e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6336 | SAN RAFAEL 1101310 | 42011101 | SAN RAFAEL 1101 | 319.7974 | 0.19876 | 48 | 0.00025509 | 5.3143e-06 | 3249 | 25911.7329 | 0.039296 | 1.587e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5625 | LAURELES 11116617 | 182371111 | LAURELES 1111 | 2923.677 | 1.8171 | 13 | 6.8952e-05 | 5.304e-06 | 3250 | 25913.55 | 0.039227 | 1.5842e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4819 | GANSNER 1101590690 | 103021101 | GANSNER 1101 | 102.0304 | 0.063412 | 4 | 2.1169e-05 | 5.2923e-06 | 3251 | 25913.6134 | 0.039206 | 1.5833e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3357 | TASSAJARA 210812712 | 14662108 | TASSAJARA 2108 | 1227.8521 | 0.76312 | 46 | 0.00024294 | 5.2813e-06 | 3252 | 25914.3765 | 0.038963 | 1.5735e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4164 | ELK 11014628 | 42981101 | ELK 1101 | 3975.7324 | 2.4709 | 54 | 0.00028378 | 5.2551e-06 | 3253 | 25916.8475 | 0.038679 | 1.5621e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5329 | ROSSMOOR 1106L522R | 14161106 | ROSSMOOR 1106 | 3031.8636 | 1.8843 | 56 | 0.00029428 | 5.255e-06 | 3254 | 25918.7318 | 0.038385 | 1.5502e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10811 | STAFFORD 1101803535 | 43201101 | STAFFORD 1101 | 262.4984 | 0.16314 | 3 | 1.5658e-05 | 5.2193e-06 | 3255 | 25918.8949 | 0.038369 | 1.5495e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7133 | DEL MONTE 21032000 | 182222103 | DEL MONTE 2103 | 14495.3301 | 9.0089 | 101 | 0.00052618 | 5.2097e-06 | 3256 | 25927.9038 | 0.037843 | 1.5283e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5982 | SAN RAFAEL 1107434 | 42011107 | SAN RAFAEL 1107 | 49.2215 | 0.030591 | 16 | 8.3238e-05 | 5.2024e-06 | 3257 | 25927.9344 | 0.03776 | 1.5249e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7562 | IGNACIO 1105784032 | 42481105 | IGNACIO 1105 | 863.751 | 0.53682 | 11 | 5.7096e-05 | 5.1906e-06 | 3258 | 25928.4712 | 0.037703 | 1.5226e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4422 | ROSSMOOR 1106CB | 14161106 | ROSSMOOR 1106 | 2937.1415 | 1.8254 | 60 | 0.00030957 | 5.1594e-06 | 3259 | 25930.2967 | 0.037393 | 1.5101e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
788 | OAKLAND K 1104CR210 | 12101104 | OAKLAND K 1104 | 4546.547 | 2.8257 | 35 | 0.00018057 | 5.1591e-06 | 3260 | 25933.1224 | 0.037213 | 1.5028e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5398 | HARTLEY 1101471 | 43211101 | HARTLEY 1101 | 0 | 0 | 16 | 8.2468e-05 | 5.1543e-06 | 3261 | 25933.1224 | 0.03713 | 1.4995e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3021 | SAN RAFAEL 1101494 | 42011101 | SAN RAFAEL 1101 | 9034.9185 | 5.6152 | 114 | 0.00058215 | 5.1065e-06 | 3262 | 25938.7376 | 0.036548 | 1.476e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2946 | WOODSIDE 11049116 | 24251104 | WOODSIDE 1104 | 1335.9769 | 0.83032 | 53 | 0.00026765 | 5.0499e-06 | 3263 | 25939.5679 | 0.03628 | 1.4652e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8964 | MARIPOSA 2102527766 | 254452102 | MARIPOSA 2102 | 66.9649 | 0.041619 | 1 | 5.0408e-06 | 5.0408e-06 | 3264 | 25939.6096 | 0.036275 | 1.465e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8147 | LAS GALLINAS A 1105648439 | 42991105 | LAS GALLINAS A 1105 | 10.9115 | 0.0067816 | 3 | 1.5099e-05 | 5.033e-06 | 3265 | 25939.6163 | 0.03626 | 1.4644e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6797 | EMERALD LAKE 04028858 | 24080402 | EMERALD LAKE 0402 | 3073.6226 | 1.9103 | 27 | 0.00013482 | 4.9935e-06 | 3266 | 25941.5266 | 0.036125 | 1.4589e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8050 | BIG RIVER 11015065 | 43081101 | BIG RIVER 1101 | 3543.5774 | 2.2023 | 27 | 0.00013434 | 4.9756e-06 | 3267 | 25943.729 | 0.035991 | 1.4535e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6040 | RACETRACK 17032553 | 163761703 | RACETRACK 1703 | 1548.3173 | 0.96229 | 32 | 0.00015851 | 4.9535e-06 | 3268 | 25944.6912 | 0.035833 | 1.4471e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4959 | VALLEY VIEW 1105305072 | 14341105 | VALLEY VIEW 1105 | 5044.0425 | 3.1349 | 45 | 0.0002229 | 4.9532e-06 | 3269 | 25947.8261 | 0.03561 | 1.4381e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1675 | CASTRO VALLEY 1111227862 | 14091111 | CASTRO VALLEY 1111 | 319.3369 | 0.19847 | 26 | 0.00012875 | 4.952e-06 | 3270 | 25948.0246 | 0.035481 | 1.4329e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9676 | PACIFICA 1103885952 | 22811103 | PACIFICA 1103 | 283.4481 | 0.17616 | 4 | 1.963e-05 | 4.9074e-06 | 3271 | 25948.2008 | 0.035461 | 1.4321e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8421 | EL CERRITO G 1112779030 | 12501112 | EL CERRITO G 1112 | 827.4759 | 0.51428 | 11 | 5.3691e-05 | 4.881e-06 | 3272 | 25948.715 | 0.035408 | 1.4299e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2317 | VACAVILLE 1112CB | 63601112 | VACAVILLE 1112 | 378.608 | 0.23531 | 52 | 0.00025204 | 4.847e-06 | 3273 | 25948.9504 | 0.035156 | 1.4198e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2187 | NEWBURG 1131CB | 192151131 | NEWBURG 1131 | 257.3233 | 0.15993 | 91 | 0.00044057 | 4.8414e-06 | 3274 | 25949.1103 | 0.034715 | 1.402e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8107 | EMERALD LAKE 0402CB | 24080402 | EMERALD LAKE 0402 | 3052.0291 | 1.8968 | 23 | 0.0001105 | 4.8042e-06 | 3275 | 25951.0071 | 0.034605 | 1.3975e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1133 | SAN CARLOS 1103586832 | 24181103 | SAN CARLOS 1103 | 6145.6408 | 3.8195 | 53 | 0.00025437 | 4.7995e-06 | 3276 | 25954.8267 | 0.03435 | 1.3872e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9839 | SAN RAFAEL 11073323 | 42011107 | SAN RAFAEL 1107 | 214.7286 | 0.13345 | 2 | 9.5309e-06 | 4.7655e-06 | 3277 | 25954.9601 | 0.034341 | 1.3868e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3598 | PAUL SWEET 210210290 | 83252102 | PAUL SWEET 2102 | 4.572 | 0.0028415 | 75 | 0.00035541 | 4.7388e-06 | 3278 | 25954.963 | 0.033985 | 1.3725e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4237 | PAUL SWEET 2109687295 | 83252109 | PAUL SWEET 2109 | 1495.545 | 0.92949 | 14 | 6.5958e-05 | 4.7113e-06 | 3279 | 25955.8925 | 0.033919 | 1.3698e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4104 | GREENBRAE 1103CB | 43091103 | GREENBRAE 1103 | 0 | 0 | 61 | 0.00028618 | 4.6915e-06 | 3280 | 25955.8925 | 0.033633 | 1.3583e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9040 | SAN RAFAEL 1101CB | 42011101 | SAN RAFAEL 1101 | 0 | 0 | 17 | 7.9676e-05 | 4.6868e-06 | 3281 | 25955.8925 | 0.033553 | 1.3551e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9787 | ATASCADERO 1103395936 | 182541103 | ATASCADERO 1103 | 685.7662 | 0.42621 | 6 | 2.7994e-05 | 4.6656e-06 | 3282 | 25956.3187 | 0.033525 | 1.3539e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3209 | ROB ROY 210512474 | 83692105 | ROB ROY 2105 | 5487.3001 | 3.4104 | 105 | 0.00048831 | 4.6505e-06 | 3283 | 25959.729 | 0.033037 | 1.3342e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10084 | SAN RAFAEL 1106307651 | 42011106 | SAN RAFAEL 1106 | 169.0436 | 0.10506 | 4 | 1.8507e-05 | 4.6267e-06 | 3284 | 25959.8341 | 0.033019 | 1.3335e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8574 | BIG RIVER 1101262924 | 43081101 | BIG RIVER 1101 | 3032.2865 | 1.8846 | 30 | 0.00013867 | 4.6224e-06 | 3285 | 25961.7187 | 0.03288 | 1.3279e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9375 | BIG MEADOWS 2101439 | 102812101 | BIG MEADOWS 2101 | 1069.2533 | 0.66455 | 12 | 5.5413e-05 | 4.6178e-06 | 3286 | 25962.3832 | 0.032825 | 1.3256e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10457 | ALTO 1124319320 | 42031124 | ALTO 1124 | 210.6172 | 0.1309 | 3 | 1.3844e-05 | 4.6148e-06 | 3287 | 25962.5141 | 0.032811 | 1.3251e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9137 | BERKELEY F 1103620294 | 12061103 | BERKELEY F 1103 | 249.6637 | 0.15517 | 4 | 1.8443e-05 | 4.6109e-06 | 3288 | 25962.6693 | 0.032792 | 1.3243e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10199 | SALT SPRINGS 21023116 | 163692102 | SALT SPRINGS 2102 | 87.1475 | 0.054163 | 2 | 9.1703e-06 | 4.5851e-06 | 3289 | 25962.7235 | 0.032783 | 1.3239e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7887 | EAST QUINCY 1101782320 | 102551101 | EAST QUINCY 1101 | 340.3108 | 0.2115 | 5 | 2.2762e-05 | 4.5524e-06 | 3290 | 25962.935 | 0.03276 | 1.323e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5305 | SAN RAFAEL 1105CB | 42011105 | SAN RAFAEL 1105 | 0 | 0 | 124 | 0.00056425 | 4.5504e-06 | 3291 | 25962.935 | 0.032196 | 1.3002e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8451 | GUALALA 11124431 | 42841112 | GUALALA 1112 | 2267.622 | 1.4093 | 16 | 7.2768e-05 | 4.548e-06 | 3292 | 25964.3443 | 0.032123 | 1.2973e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2628 | EAST QUINCY 1101186938 | 102551101 | EAST QUINCY 1101 | 2672.105 | 1.6607 | 41 | 0.00018638 | 4.5458e-06 | 3293 | 25966.005 | 0.031937 | 1.2898e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8531 | VALLEY VIEW 1106602871 | 14341106 | VALLEY VIEW 1106 | 1324.4478 | 0.82315 | 14 | 6.3511e-05 | 4.5365e-06 | 3294 | 25966.8282 | 0.031873 | 1.2872e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6262 | HIGHLANDS 110448262 | 43361104 | HIGHLANDS 1104 | 9974.998 | 6.1995 | 74 | 0.00033533 | 4.5315e-06 | 3295 | 25973.0277 | 0.031538 | 1.2737e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3513 | FLORENCE 0401CR220 | 12690401 | FLORENCE 0401 | 325.3992 | 0.20224 | 19 | 8.5689e-05 | 4.51e-06 | 3296 | 25973.2299 | 0.031452 | 1.2702e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5570 | SAN CARLOS 11048942 | 24181104 | SAN CARLOS 1104 | 3407.8974 | 2.118 | 35 | 0.00015779 | 4.5084e-06 | 3297 | 25975.3479 | 0.031295 | 1.2638e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5867 | ARLINGTON 0401404226 | 13700401 | ARLINGTON 0401 | 1403.5728 | 0.87233 | 15 | 6.7165e-05 | 4.4777e-06 | 3298 | 25976.2203 | 0.031227 | 1.2611e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1380 | HARRIS 11084674 | 192431108 | HARRIS 1108 | 72.8 | 0.045245 | 85 | 0.00037897 | 4.4584e-06 | 3299 | 25976.2655 | 0.030848 | 1.2458e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7856 | FORT BRAGG A 1102CB | 42761102 | FORT BRAGG A 1102 | 3594.4279 | 2.234 | 73 | 0.00032509 | 4.4533e-06 | 3300 | 25978.4995 | 0.030523 | 1.2327e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7134 | DEL MONTE 2103617344 | 182222103 | DEL MONTE 2103 | 2952.1893 | 1.8348 | 34 | 0.00014986 | 4.4076e-06 | 3301 | 25980.3342 | 0.030373 | 1.2266e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3773 | RINCON 1104CB | 43321104 | RINCON 1104 | 901.4332 | 0.56024 | 34 | 0.00014935 | 4.3928e-06 | 3302 | 25980.8945 | 0.030224 | 1.2206e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7255 | VIEJO 2203CB | 182852203 | VIEJO 2203 | 4727.7308 | 2.9383 | 42 | 0.00018447 | 4.392e-06 | 3303 | 25983.8328 | 0.03004 | 1.2132e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1976 | LAURELES 111268454 | 182371112 | LAURELES 1112 | 13589.2158 | 8.4458 | 142 | 0.00062355 | 4.3912e-06 | 3304 | 25992.2786 | 0.029416 | 1.188e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1047 | DOLAN ROAD 110122158 | 182381101 | DOLAN ROAD 1101 | 184.8198 | 0.11487 | 119 | 0.00052165 | 4.3836e-06 | 3305 | 25992.3934 | 0.028894 | 1.1669e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4984 | PAUL SWEET 210212850 | 83252102 | PAUL SWEET 2102 | 1063.4476 | 0.66094 | 52 | 0.00022741 | 4.3733e-06 | 3306 | 25993.0544 | 0.028667 | 1.1577e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10216 | GUALALA 1111498 | 42841111 | GUALALA 1111 | 4596.7491 | 2.8569 | 18 | 7.8567e-05 | 4.3648e-06 | 3307 | 25995.9113 | 0.028588 | 1.1545e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5466 | WEST POINT 11025357 | 163201102 | WEST POINT 1102 | 5401.7845 | 3.3572 | 37 | 0.0001614 | 4.3621e-06 | 3308 | 25999.2685 | 0.028427 | 1.148e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5373 | VIEJO 22019490 | 182852201 | VIEJO 2201 | 2004.014 | 1.2455 | 21 | 9.1432e-05 | 4.3539e-06 | 3309 | 26000.514 | 0.028336 | 1.1443e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3074 | GANSNER 1101480328 | 103021101 | GANSNER 1101 | 472.375 | 0.29358 | 7 | 3.0278e-05 | 4.3254e-06 | 3310 | 26000.8076 | 0.028305 | 1.1431e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2211 | DEL MONTE 21032654 | 182222103 | DEL MONTE 2103 | 2963.5999 | 1.8419 | 23 | 9.916e-05 | 4.3113e-06 | 3311 | 26002.6495 | 0.028206 | 1.1391e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8914 | CLAYTON 2217CB | 12022217 | CLAYTON 2217 | 373.7851 | 0.23231 | 8 | 3.4288e-05 | 4.2861e-06 | 3312 | 26002.8818 | 0.028172 | 1.1377e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9870 | PUEBLO 2103253312 | 43292103 | PUEBLO 2103 | 682.8006 | 0.42436 | 2 | 8.5718e-06 | 4.2859e-06 | 3313 | 26003.3061 | 0.028163 | 1.1374e-06 | 0.028163 | #N/A | #N/A | #N/A | #N/A | #VALUE!
10448 | DOLAN ROAD 1101173702 | 182381101 | DOLAN ROAD 1101 | 86.6803 | 0.053872 | 3 | 1.2834e-05 | 4.2778e-06 | 3314 | 26003.36 | 0.028151 | 1.1369e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7265 | ALTO 112265474 | 42031122 | ALTO 1122 | 3837.7425 | 2.3852 | 47 | 0.0002004 | 4.2638e-06 | 3315 | 26005.7452 | 0.02795 | 1.1288e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6511 | PACIFICA 1103218962 | 22811103 | PACIFICA 1103 | 86.3363 | 0.053658 | 2 | 8.5182e-06 | 4.2591e-06 | 3316 | 26005.7988 | 0.027942 | 1.1284e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10670 | VACAVILLE 1111772224 | 63601111 | VACAVILLE 1111 | 91.9583 | 0.057152 | 2 | 8.4316e-06 | 4.2158e-06 | 3317 | 26005.856 | 0.027933 | 1.1281e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5386 | CAROLANDS 040484797 | 24060404 | CAROLANDS 0404 | 66.6995 | 0.041454 | 21 | 8.8525e-05 | 4.2155e-06 | 3318 | 26005.8974 | 0.027845 | 1.1245e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1724 | LAURELES 1112CB | 182371112 | LAURELES 1112 | 493.1815 | 0.30651 | 38 | 0.00016012 | 4.2137e-06 | 3319 | 26006.204 | 0.027685 | 1.118e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1512 | ATASCADERO 1102CB | 182541102 | ATASCADERO 1102 | 0 | 0 | 67 | 0.00028187 | 4.207e-06 | 3320 | 26006.204 | 0.027403 | 1.1067e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
557 | GREENBRAE 11021254 | 43091102 | GREENBRAE 1102 | 9639.5738 | 5.991 | 130 | 0.0005443 | 4.1869e-06 | 3321 | 26012.195 | 0.026858 | 1.0847e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9628 | SAN CARLOS 110436864 | 24181104 | SAN CARLOS 1104 | 889.7222 | 0.55297 | 10 | 4.1763e-05 | 4.1763e-06 | 3322 | 26012.748 | 0.026817 | 1.083e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7091 | HATTON 11029642 | 182291102 | HATTON 1102 | 1925.8934 | 1.197 | 18 | 7.5077e-05 | 4.1709e-06 | 3323 | 26013.9449 | 0.026742 | 1.08e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
757 | LAKEWOOD 1102CB | 13531102 | LAKEWOOD 1102 | 23.5925 | 0.014663 | 121 | 0.00050446 | 4.1691e-06 | 3324 | 26013.9596 | 0.026237 | 1.0596e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10987 | ECHO SUMMIT 1101CB | 158031101 | ECHO SUMMIT 1101 | 49.1761 | 0.030563 | 1 | 4.1622e-06 | 4.1622e-06 | 3325 | 26013.9901 | 0.026233 | 1.0594e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9358 | PACIFICA 1102267868 | 22811102 | PACIFICA 1102 | 1363.5441 | 0.84745 | 13 | 5.4041e-05 | 4.157e-06 | 3326 | 26014.8376 | 0.026179 | 1.0572e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5985 | BERESFORD 04039154 | 24040403 | BERESFORD 0403 | 6776.6762 | 4.2117 | 95 | 0.00039442 | 4.1518e-06 | 3327 | 26019.0493 | 0.025784 | 1.0413e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7732 | BIG MEADOWS 21012510 | 102812101 | BIG MEADOWS 2101 | 12778.5068 | 7.9419 | 22 | 9.0933e-05 | 4.1333e-06 | 3328 | 26026.9912 | 0.025694 | 1.0376e-06 | 0.025694 | #N/A | #N/A | #N/A | #N/A | #VALUE!
3692 | LAS GALLINAS A 1107554 | 42991107 | LAS GALLINAS A 1107 | 52.9857 | 0.032931 | 35 | 0.00014456 | 4.1303e-06 | 3329 | 26027.0241 | 0.025549 | 1.0318e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7653 | WOOD 0401265211 | 13380401 | WOOD 0401 | 238.1693 | 0.14802 | 4 | 1.651e-05 | 4.1276e-06 | 3330 | 26027.1722 | 0.025532 | 1.0311e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7212 | VIEJO 2201CB | 182852201 | VIEJO 2201 | 8183.2875 | 5.0859 | 67 | 0.00027516 | 4.1068e-06 | 3331 | 26032.2581 | 0.025257 | 1.02e-06 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4015 | DOLAN ROAD 11013012 | 182381101 | DOLAN ROAD 1101 | 301.9386 | 0.18766 | 160 | 0.00065198 | 4.0749e-06 | 3332 | 26032.4458 | 0.024605 | 9.9369e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6661 | HICKS 2103XR248 | 83432103 | HICKS 2103 | 0 | 0 | 22 | 8.9634e-05 | 4.0743e-06 | 3333 | 26032.4458 | 0.024516 | 9.9007e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9871 | SARATOGA 1103709451 | 83371103 | SARATOGA 1103 | 302.4738 | 0.18799 | 5 | 2.0151e-05 | 4.0301e-06 | 3334 | 26032.6337 | 0.024496 | 9.8925e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3396 | SARATOGA 1107CB | 83371107 | SARATOGA 1107 | 273.8424 | 0.17019 | 135 | 0.00054404 | 4.0299e-06 | 3335 | 26032.8039 | 0.023951 | 9.6728e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
697 | SANTA ROSA A 1107CB | 42151107 | SANTA ROSA A 1107 | 4879.3813 | 3.0326 | 92 | 0.00036531 | 3.9708e-06 | 3336 | 26035.8365 | 0.023586 | 9.5253e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7511 | BERKELEY F 1105189500 | 12061105 | BERKELEY F 1105 | 1225.686 | 0.76177 | 17 | 6.7503e-05 | 3.9708e-06 | 3337 | 26036.5983 | 0.023519 | 9.498e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5683 | OAKLAND K 1104CB | 12101104 | OAKLAND K 1104 | 2366.505 | 1.4708 | 17 | 6.7244e-05 | 3.9555e-06 | 3338 | 26038.0691 | 0.023451 | 9.4709e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4165 | VIEJO 22022606 | 182852202 | VIEJO 2202 | 1279.376 | 0.79514 | 52 | 0.00020362 | 3.9158e-06 | 3339 | 26038.8642 | 0.023248 | 9.3886e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5028 | PUEBLO 21031970 | 43292103 | PUEBLO 2103 | 0 | 0 | 60 | 0.00023459 | 3.9099e-06 | 3340 | 26038.8642 | 0.023013 | 9.2939e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4499 | MORGAN HILL 2109145998 | 83242109 | MORGAN HILL 2109 | 4027.966 | 2.5034 | 28 | 0.00010919 | 3.8997e-06 | 3341 | 26041.3676 | 0.022904 | 9.2498e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1014 | VIEJO 22019114 | 182852201 | VIEJO 2201 | 10977.6209 | 6.8226 | 92 | 0.00035832 | 3.8947e-06 | 3342 | 26048.1902 | 0.022546 | 9.1051e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
230 | CAROLANDS 04049026 | 24060404 | CAROLANDS 0404 | 1184.1509 | 0.73595 | 71 | 0.00027642 | 3.8932e-06 | 3343 | 26048.9262 | 0.022269 | 8.9935e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10928 | FORT ORD 21069656 | 182402106 | FORT ORD 2106 | 188.9883 | 0.11746 | 2 | 7.7429e-06 | 3.8714e-06 | 3344 | 26049.0436 | 0.022262 | 8.9903e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5034 | OAKLAND J 1102CR184 | 12091102 | OAKLAND J 1102 | 5568.9906 | 3.4612 | 43 | 0.00016531 | 3.8445e-06 | 3345 | 26052.5048 | 0.022096 | 8.9236e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4211 | FAIRVIEW 2207P142 | 13432207 | FAIRVIEW 2207 | 1963.5704 | 1.2204 | 41 | 0.00015757 | 3.8432e-06 | 3346 | 26053.7252 | 0.021939 | 8.8599e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10430 | BELL 1107643778 | 152701107 | BELL 1107 | 270.3051 | 0.168 | 4 | 1.5168e-05 | 3.7919e-06 | 3347 | 26053.8932 | 0.021923 | 8.8538e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9697 | DOLAN ROAD 1101882610 | 182381101 | DOLAN ROAD 1101 | 228.3158 | 0.1419 | 8 | 3.0295e-05 | 3.7868e-06 | 3348 | 26054.0351 | 0.021893 | 8.8416e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
238 | LOS GATOS 1102526868 | 82021102 | LOS GATOS 1102 | 1780.5165 | 1.1066 | 20 | 7.5227e-05 | 3.7614e-06 | 3349 | 26055.1417 | 0.021818 | 8.8112e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7260 | SUMMIT 110158642 | 152591101 | SUMMIT 1101 | 2892.0319 | 1.7974 | 13 | 4.8812e-05 | 3.7548e-06 | 3350 | 26056.9391 | 0.021769 | 8.7915e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
535 | ATASCADERO 11012379 | 182541101 | ATASCADERO 1101 | 1171.3689 | 0.72801 | 11 | 4.1301e-05 | 3.7546e-06 | 3351 | 26057.6671 | 0.021728 | 8.7748e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4492 | DEL MONTE 2103468158 | 182222103 | DEL MONTE 2103 | 826.6133 | 0.51374 | 12 | 4.4889e-05 | 3.7407e-06 | 3352 | 26058.1808 | 0.021683 | 8.7567e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8753 | HALF MOON BAY 1102650808 | 24101102 | HALF MOON BAY 1102 | 843.3592 | 0.52415 | 8 | 2.9515e-05 | 3.6894e-06 | 3353 | 26058.705 | 0.021653 | 8.7448e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
43 | WOODSIDE 1104555372 | 24251104 | WOODSIDE 1104 | 6684.5288 | 4.1545 | 54 | 0.0001983 | 3.6721e-06 | 3354 | 26062.8594 | 0.021455 | 8.6647e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10659 | ECHO SUMMIT 110155262 | 158031101 | ECHO SUMMIT 1101 | 266.534 | 0.16565 | 4 | 1.4612e-05 | 3.653e-06 | 3355 | 26063.0251 | 0.021441 | 8.6588e-07 | 0.021441 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7441 | SAN LUIS OBISPO 110596874 | 182631105 | SAN LUIS OBISPO 1105 | 1345.5157 | 0.83624 | 16 | 5.8253e-05 | 3.6408e-06 | 3356 | 26063.8613 | 0.021382 | 8.6352e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9136 | VIEJO 2204CB | 182852204 | VIEJO 2204 | 3727.5543 | 2.3167 | 24 | 8.736e-05 | 3.64e-06 | 3357 | 26066.178 | 0.021295 | 8.6e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4971 | EDES 1112CR282 | 13681112 | EDES 1112 | 6573.0208 | 4.0852 | 45 | 0.00016364 | 3.6364e-06 | 3358 | 26070.2632 | 0.021131 | 8.5339e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7343 | ATASCADERO 1101CB | 182541101 | ATASCADERO 1101 | 61.191 | 0.03803 | 24 | 8.6724e-05 | 3.6135e-06 | 3359 | 26070.3012 | 0.021045 | 8.4989e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8700 | VIEJO 22029488 | 182852202 | VIEJO 2202 | 1460.401 | 0.90765 | 18 | 6.486e-05 | 3.6034e-06 | 3360 | 26071.2088 | 0.02098 | 8.4727e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3541 | SEACLIFF 0402558727 | 83500402 | SEACLIFF 0402 | 217.1494 | 0.13496 | 22 | 7.9037e-05 | 3.5926e-06 | 3361 | 26071.3438 | 0.020901 | 8.4407e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7420 | DEL MONTE 210342226 | 182222103 | DEL MONTE 2103 | 940.1806 | 0.58433 | 32 | 0.00011482 | 3.588e-06 | 3362 | 26071.9281 | 0.020786 | 8.3944e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7115 | LAS GALLINAS A 1104309087 | 42991104 | LAS GALLINAS A 1104 | 302.4969 | 0.188 | 6 | 2.145e-05 | 3.575e-06 | 3363 | 26072.1161 | 0.020764 | 8.3857e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5040 | TEMPLETON 2112238418 | 183052112 | TEMPLETON 2112 | 331.2384 | 0.20587 | 6 | 2.1369e-05 | 3.5615e-06 | 3364 | 26072.322 | 0.020743 | 8.3771e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
77 | ALTO 1124428 | 42031124 | ALTO 1124 | 0 | 0 | 21 | 7.3852e-05 | 3.5167e-06 | 3365 | 26072.322 | 0.020669 | 8.3473e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
288 | MORGAN HILL 2110XR326 | 83242110 | MORGAN HILL 2110 | 0 | 0 | 163 | 0.00057196 | 3.509e-06 | 3366 | 26072.322 | 0.020097 | 8.1163e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1912 | SANTA ROSA A 110439786 | 42151104 | SANTA ROSA A 1104 | 454.7368 | 0.28262 | 44 | 0.00015383 | 3.496e-06 | 3367 | 26072.6046 | 0.019943 | 8.0542e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6503 | VIEJO 22029118 | 182852202 | VIEJO 2202 | 1265.7827 | 0.78669 | 41 | 0.00014315 | 3.4915e-06 | 3368 | 26073.3913 | 0.0198 | 7.9963e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4440 | SANTA ROSA A 1104991788 | 42151104 | SANTA ROSA A 1104 | 1222.0634 | 0.75952 | 43 | 0.00014892 | 3.4631e-06 | 3369 | 26074.1508 | 0.019651 | 7.9362e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8382 | MORGAN HILL 2109XR246 | 83242109 | MORGAN HILL 2109 | 71.5932 | 0.044495 | 61 | 0.00021081 | 3.4559e-06 | 3370 | 26074.1953 | 0.019441 | 7.8511e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8657 | OCEANO 110376678 | 182601103 | OCEANO 1103 | 88.7522 | 0.05516 | 8 | 2.7609e-05 | 3.4511e-06 | 3371 | 26074.2505 | 0.019413 | 7.8399e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9324 | ECHO SUMMIT 1101741586 | 158031101 | ECHO SUMMIT 1101 | 1137.7952 | 0.70714 | 9 | 3.09e-05 | 3.4334e-06 | 3372 | 26074.9576 | 0.019382 | 7.8274e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
392 | BELMONT 11038958 | 24031103 | BELMONT 1103 | 5438.9297 | 3.3803 | 73 | 0.00024907 | 3.4119e-06 | 3373 | 26078.3379 | 0.019133 | 7.7268e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9058 | LOS GATOS 1101502026 | 82021101 | LOS GATOS 1101 | 180.5393 | 0.11221 | 17 | 5.784e-05 | 3.4024e-06 | 3374 | 26078.4502 | 0.019075 | 7.7035e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2028 | HICKS 1116LB16 | 83431116 | HICKS 1116 | 4399.0652 | 2.734 | 97 | 0.00032945 | 3.3964e-06 | 3375 | 26081.1842 | 0.018746 | 7.5704e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10450 | OAKLAND J 1102951816 | 12091102 | OAKLAND J 1102 | 539.1734 | 0.3351 | 6 | 2.0354e-05 | 3.3923e-06 | 3376 | 26081.5193 | 0.018725 | 7.5622e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3081 | SARATOGA 1103LC40 | 83371103 | SARATOGA 1103 | 26.7728 | 0.016639 | 28 | 9.4717e-05 | 3.3827e-06 | 3377 | 26081.5359 | 0.018631 | 7.524e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5298 | SAN LEANDRO U 1109CR182 | 13111109 | SAN LEANDRO U 1109 | 7768.8154 | 4.8284 | 56 | 0.00018928 | 3.38e-06 | 3378 | 26086.3643 | 0.018441 | 7.4475e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9781 | SAN LUIS OBISPO 1108903036 | 182631108 | SAN LUIS OBISPO 1108 | 306.6437 | 0.19058 | 5 | 1.6737e-05 | 3.3474e-06 | 3379 | 26086.5549 | 0.018425 | 7.4408e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1847 | ALTO 1122CB | 42031122 | ALTO 1122 | 3611.6831 | 2.2447 | 46 | 0.0001533 | 3.3325e-06 | 3380 | 26088.7995 | 0.018271 | 7.3789e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
559 | PACIFICA 110266732 | 22811102 | PACIFICA 1102 | 334.9483 | 0.20817 | 23 | 7.6211e-05 | 3.3135e-06 | 3381 | 26089.0077 | 0.018195 | 7.3481e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7812 | LUCERNE 11062355 | 43351106 | LUCERNE 1106 | 644.3598 | 0.40047 | 13 | 4.2852e-05 | 3.2963e-06 | 3382 | 26089.4082 | 0.018152 | 7.3308e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9811 | PACIFICA 1103119798 | 22811103 | PACIFICA 1103 | 129.7041 | 0.080612 | 2 | 6.5735e-06 | 3.2867e-06 | 3383 | 26089.4888 | 0.018146 | 7.3281e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10195 | ALTO 112081716 | 42031120 | ALTO 1120 | 406.7505 | 0.2528 | 5 | 1.6345e-05 | 3.2689e-06 | 3384 | 26089.7416 | 0.018129 | 7.3215e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6620 | LOS GATOS 1101950286 | 82021101 | LOS GATOS 1101 | 1710.7995 | 1.0633 | 17 | 5.5462e-05 | 3.2625e-06 | 3385 | 26090.8049 | 0.018074 | 7.2991e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5964 | RALSTON 1102CB | 24141102 | RALSTON 1102 | 1520.1281 | 0.94477 | 66 | 0.00021451 | 3.2502e-06 | 3386 | 26091.7496 | 0.017859 | 7.2125e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8215 | GREENBRAE 1104107508 | 43091104 | GREENBRAE 1104 | 0 | 0 | 2 | 6.4279e-06 | 3.214e-06 | 3387 | 26091.7496 | 0.017853 | 7.2099e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1635 | OAKLAND K 1101CR172 | 12101101 | OAKLAND K 1101 | 904.9661 | 0.56244 | 30 | 9.6271e-05 | 3.209e-06 | 3388 | 26092.3121 | 0.017757 | 7.171e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3774 | PAUL SWEET 210411074 | 83252104 | PAUL SWEET 2104 | 4718.31 | 2.9324 | 41 | 0.00013081 | 3.1905e-06 | 3389 | 26095.2445 | 0.017626 | 7.1182e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8087 | SAN RAMON 2107MR441 | 14232107 | SAN RAMON 2107 | 40.2016 | 0.024985 | 8 | 2.5513e-05 | 3.1892e-06 | 3390 | 26095.2695 | 0.0176 | 7.1079e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7720 | SAN RAFAEL 1106764698 | 42011106 | SAN RAFAEL 1106 | 133.4071 | 0.082913 | 5 | 1.5933e-05 | 3.1867e-06 | 3391 | 26095.3524 | 0.017584 | 7.1014e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3736 | VALLEY VIEW 1105P126 | 14341105 | VALLEY VIEW 1105 | 1680.8363 | 1.0446 | 25 | 7.9621e-05 | 3.1848e-06 | 3392 | 26096.3971 | 0.017505 | 7.0693e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2670 | GREENBRAE 11037315 | 43091103 | GREENBRAE 1103 | 0 | 0 | 32 | 0.00010108 | 3.1589e-06 | 3393 | 26096.3971 | 0.017404 | 7.0285e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6253 | FORT BRAGG A 110233064 | 42761102 | FORT BRAGG A 1102 | 0 | 0 | 49 | 0.00015435 | 3.15e-06 | 3394 | 26096.3971 | 0.017249 | 6.9661e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4022 | EDES 1112CR100 | 13681112 | EDES 1112 | 5399.0675 | 3.3555 | 40 | 0.00012546 | 3.1366e-06 | 3395 | 26099.7526 | 0.017124 | 6.9155e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1730 | LOS GATOS 1101CB | 82021101 | LOS GATOS 1101 | 47.6524 | 0.029616 | 34 | 0.00010664 | 3.1364e-06 | 3396 | 26099.7822 | 0.017017 | 6.8724e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5067 | EL CERRITO G 1112BR178 | 12501112 | EL CERRITO G 1112 | 48.2003 | 0.029957 | 93 | 0.00029117 | 3.1309e-06 | 3397 | 26099.8122 | 0.016726 | 6.7548e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3732 | SOBRANTE 1101L534R | 14671101 | SOBRANTE 1101 | 1291.9266 | 0.80294 | 34 | 0.00010636 | 3.1282e-06 | 3398 | 26100.6151 | 0.01662 | 6.7119e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4550 | VALLEY VIEW 1106P176 | 14341106 | VALLEY VIEW 1106 | 354.4687 | 0.2203 | 44 | 0.00013758 | 3.1268e-06 | 3399 | 26100.8354 | 0.016482 | 6.6563e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7024 | VIEJO 220292792 | 182852202 | VIEJO 2202 | 0 | 0 | 21 | 6.5595e-05 | 3.1236e-06 | 3400 | 26100.8354 | 0.016416 | 6.6298e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8774 | TULUCAY 1101504524 | 42301101 | TULUCAY 1101 | 610.0991 | 0.37918 | 15 | 4.6823e-05 | 3.1216e-06 | 3401 | 26101.2146 | 0.01637 | 6.6109e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9561 | ATASCADERO 1101747522 | 182541101 | ATASCADERO 1101 | 412.9409 | 0.25664 | 16 | 4.9813e-05 | 3.1133e-06 | 3402 | 26101.4712 | 0.01632 | 6.5908e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1757 | OAKLAND X 1106121588 | 12541106 | OAKLAND X 1106 | 1356.1967 | 0.84288 | 27 | 8.3654e-05 | 3.0983e-06 | 3403 | 26102.3141 | 0.016236 | 6.557e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
641 | ALTO 11251256 | 42031125 | ALTO 1125 | 12003.1718 | 7.46 | 88 | 0.00027263 | 3.098e-06 | 3404 | 26109.7741 | 0.015964 | 6.4469e-07 | 0.015964 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7693 | SARATOGA 1103595689 | 83371103 | SARATOGA 1103 | 44.7654 | 0.027822 | 4 | 1.233e-05 | 3.0826e-06 | 3405 | 26109.802 | 0.015951 | 6.4419e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1201 | RINCON 1102640 | 43321102 | RINCON 1102 | 0 | 0 | 56 | 0.00017204 | 3.0722e-06 | 3406 | 26109.802 | 0.015779 | 6.3724e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8249 | VIEJO 22029089 | 182852202 | VIEJO 2202 | 2319.95 | 1.4419 | 20 | 6.1368e-05 | 3.0684e-06 | 3407 | 26111.2438 | 0.015718 | 6.3477e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4500 | PACIFICA 1102968736 | 22811102 | PACIFICA 1102 | 1132.2658 | 0.70371 | 9 | 2.7334e-05 | 3.0372e-06 | 3408 | 26111.9475 | 0.01569 | 6.3366e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5121 | BURNEY 110237284 | 103311102 | BURNEY 1102 | 303.068 | 0.18836 | 15 | 4.5299e-05 | 3.0199e-06 | 3409 | 26112.1359 | 0.015645 | 6.3183e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3124 | SAN RAFAEL 110648752 | 42011106 | SAN RAFAEL 1106 | 23.2085 | 0.014424 | 28 | 8.3928e-05 | 2.9974e-06 | 3410 | 26112.1503 | 0.015561 | 6.2844e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
292 | RIDGE 0402CB | 12840402 | RIDGE 0402 | 2930.2271 | 1.8211 | 31 | 9.2772e-05 | 2.9927e-06 | 3411 | 26113.9715 | 0.015468 | 6.247e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5812 | LAS GALLINAS A 11051218 | 42991105 | LAS GALLINAS A 1105 | 106.7452 | 0.066343 | 28 | 8.3731e-05 | 2.9904e-06 | 3412 | 26114.0378 | 0.015385 | 6.2131e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5928 | IGNACIO 110584764 | 42481105 | IGNACIO 1105 | 339.9136 | 0.21126 | 33 | 9.8398e-05 | 2.9818e-06 | 3413 | 26114.2491 | 0.015286 | 6.1734e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
231 | PAUL SWEET 210912828 | 83252109 | PAUL SWEET 2109 | 1834.1595 | 1.1399 | 66 | 0.0001957 | 2.9651e-06 | 3414 | 26115.389 | 0.015091 | 6.0944e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5926 | CASTRO VALLEY 1110CB | 14091110 | CASTRO VALLEY 1110 | 523.3275 | 0.32525 | 23 | 6.8153e-05 | 2.9632e-06 | 3415 | 26115.7142 | 0.015023 | 6.0669e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8452 | HARRIS 1108395498 | 192431108 | HARRIS 1108 | 171.0291 | 0.1063 | 8 | 2.3698e-05 | 2.9622e-06 | 3416 | 26115.8205 | 0.014999 | 6.0573e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8569 | IGNACIO 1105683542 | 42481105 | IGNACIO 1105 | 222.9115 | 0.13854 | 2 | 5.8935e-06 | 2.9468e-06 | 3417 | 26115.9591 | 0.014993 | 6.0549e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6289 | STAFFORD 1101405812 | 43201101 | STAFFORD 1101 | 295.2493 | 0.1835 | 7 | 2.0611e-05 | 2.9445e-06 | 3418 | 26116.1426 | 0.014972 | 6.0466e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8541 | ROSSMOOR 1106L541R | 14161106 | ROSSMOOR 1106 | 0 | 0 | 11 | 3.2256e-05 | 2.9324e-06 | 3419 | 26116.1426 | 0.01494 | 6.0336e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3241 | OAKLAND K 1101CB | 12101101 | OAKLAND K 1101 | 538.4598 | 0.33465 | 40 | 0.00011674 | 2.9186e-06 | 3420 | 26116.4772 | 0.014823 | 5.9864e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6045 | OAKLAND J 1105CR256 | 12091105 | OAKLAND J 1105 | 1965.4224 | 1.2215 | 27 | 7.879e-05 | 2.9181e-06 | 3421 | 26117.6987 | 0.014745 | 5.9546e-07 | 0.014745 | #N/A | #N/A | #N/A | #N/A | #VALUE!
8780 | SAN LUIS OBISPO 1108144690 | 182631108 | SAN LUIS OBISPO 1108 | 418.942 | 0.26037 | 10 | 2.905e-05 | 2.905e-06 | 3422 | 26117.9591 | 0.014715 | 5.9429e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10157 | CASTRO VALLEY 1108MR233 | 14091108 | CASTRO VALLEY 1108 | 370.9448 | 0.23054 | 7 | 2.0325e-05 | 2.9035e-06 | 3423 | 26118.1897 | 0.014695 | 5.9346e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3481 | IGNACIO 1105318 | 42481105 | IGNACIO 1105 | 2887.2825 | 1.7945 | 150 | 0.00043547 | 2.9031e-06 | 3424 | 26119.9841 | 0.01426 | 5.7588e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1523 | HAMILTON BRANCH 110187784 | 102361101 | HAMILTON BRANCH 1101 | 2328.7215 | 1.4473 | 23 | 6.6598e-05 | 2.8956e-06 | 3425 | 26121.4314 | 0.014193 | 5.7319e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10922 | PINECREST 0401CB | 163160401 | PINECREST 0401 | 22.2055 | 0.013801 | 1 | 2.8911e-06 | 2.8911e-06 | 3426 | 26121.4452 | 0.01419 | 5.7307e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1324 | SONOMA 11054456 | 42721105 | SONOMA 1105 | 0 | 0 | 62 | 0.00017803 | 2.8714e-06 | 3427 | 26121.4452 | 0.014012 | 5.6588e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8419 | SAN CARLOS 1103785521 | 24181103 | SAN CARLOS 1103 | 109.0213 | 0.067757 | 3 | 8.5962e-06 | 2.8654e-06 | 3428 | 26121.513 | 0.014004 | 5.6553e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6629 | BIG MEADOWS 21012246 | 102812101 | BIG MEADOWS 2101 | 2937.4924 | 1.8257 | 23 | 6.5676e-05 | 2.8555e-06 | 3429 | 26123.3387 | 0.013938 | 5.6288e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
692 | ECHO SUMMIT 11018922 | 158031101 | ECHO SUMMIT 1101 | 1940.3902 | 1.206 | 11 | 3.1372e-05 | 2.852e-06 | 3430 | 26124.5446 | 0.013907 | 5.6162e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5593 | SNEATH LANE 1102CB | 22721102 | SNEATH LANE 1102 | 2195.0074 | 1.3642 | 37 | 0.0001053 | 2.8459e-06 | 3431 | 26125.9088 | 0.013801 | 5.5736e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7382 | VIEJO 220235388 | 182852202 | VIEJO 2202 | 517.0139 | 0.32133 | 8 | 2.2676e-05 | 2.8344e-06 | 3432 | 26126.2301 | 0.013779 | 5.5645e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5265 | IGNACIO 1103CB | 42481103 | IGNACIO 1103 | 350.3296 | 0.21773 | 34 | 9.5817e-05 | 2.8181e-06 | 3433 | 26126.4479 | 0.013683 | 5.5258e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9102 | HICKS 1116733078 | 83431116 | HICKS 1116 | 551.871 | 0.34299 | 7 | 1.9439e-05 | 2.777e-06 | 3434 | 26126.7909 | 0.013663 | 5.5179e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
199 | OAKLAND K 1103CB | 12101103 | OAKLAND K 1103 | 769.1621 | 0.47804 | 66 | 0.00018203 | 2.758e-06 | 3435 | 26127.2689 | 0.013481 | 5.4444e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2072 | RALSTON 1101420730 | 24141101 | RALSTON 1101 | 1292.6324 | 0.80338 | 21 | 5.7777e-05 | 2.7513e-06 | 3436 | 26128.0723 | 0.013423 | 5.4211e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8913 | WOOD 0401880795 | 13380401 | WOOD 0401 | 163.9752 | 0.10191 | 6 | 1.6447e-05 | 2.7412e-06 | 3437 | 26128.1742 | 0.013407 | 5.4144e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7811 | VIEJO 2203947314 | 182852203 | VIEJO 2203 | 461.4011 | 0.28676 | 22 | 5.9761e-05 | 2.7164e-06 | 3438 | 26128.461 | 0.013347 | 5.3903e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8336 | OLEMA 110137074 | 42291101 | OLEMA 1101 | 21.9456 | 0.013639 | 6 | 1.628e-05 | 2.7134e-06 | 3439 | 26128.4746 | 0.013331 | 5.3837e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6224 | SAN CARLOS 110479774 | 24181104 | SAN CARLOS 1104 | 1435.8821 | 0.89241 | 24 | 6.4753e-05 | 2.698e-06 | 3440 | 26129.367 | 0.013266 | 5.3576e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2094 | ROB ROY 210512586 | 83692105 | ROB ROY 2105 | 3041.3304 | 1.8902 | 85 | 0.00022925 | 2.697e-06 | 3441 | 26131.2572 | 0.013037 | 5.265e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8276 | OAKLAND J 1102CR254 | 12091102 | OAKLAND J 1102 | 1687.0283 | 1.0485 | 20 | 5.3882e-05 | 2.6941e-06 | 3442 | 26132.3057 | 0.012983 | 5.2432e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5380 | CASTROVILLE 210436922 | 182352104 | CASTROVILLE 2104 | 0 | 0 | 37 | 9.8808e-05 | 2.6705e-06 | 3443 | 26132.3057 | 0.012884 | 5.2033e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6593 | FOOTHILL 1101798137 | 182951101 | FOOTHILL 1101 | 68.0149 | 0.042272 | 5 | 1.3319e-05 | 2.6637e-06 | 3444 | 26132.348 | 0.012871 | 5.198e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1687 | BIG MEADOWS 21012016 | 102812101 | BIG MEADOWS 2101 | 150.9724 | 0.09383 | 65 | 0.00017299 | 2.6614e-06 | 3445 | 26132.4418 | 0.012698 | 5.1281e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10145 | GREENBRAE 1104317890 | 43091104 | GREENBRAE 1104 | 125.8315 | 0.078205 | 2 | 5.3133e-06 | 2.6567e-06 | 3446 | 26132.52 | 0.012693 | 5.1259e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3009 | GREENBRAE 1102CB | 43091102 | GREENBRAE 1102 | 0 | 0 | 28 | 7.4348e-05 | 2.6553e-06 | 3447 | 26132.52 | 0.012618 | 5.0959e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9193 | LOS GATOS 1106CB | 82021106 | LOS GATOS 1106 | 164.2523 | 0.10208 | 11 | 2.9161e-05 | 2.651e-06 | 3448 | 26132.6221 | 0.012589 | 5.0841e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6430 | FORT BRAGG A 110465894 | 42761104 | FORT BRAGG A 1104 | 0 | 0 | 12 | 3.1761e-05 | 2.6468e-06 | 3449 | 26132.6221 | 0.012557 | 5.0713e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6292 | RIO DEL MAR 0401931192 | 83260401 | RIO DEL MAR 0401 | 3615.6701 | 2.2472 | 87 | 0.00023026 | 2.6467e-06 | 3450 | 26134.8692 | 0.012327 | 4.9783e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8372 | LAURELES 11122142 | 182371112 | LAURELES 1112 | 151.8851 | 0.094397 | 26 | 6.8383e-05 | 2.6301e-06 | 3451 | 26134.9636 | 0.012259 | 4.9507e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4353 | FLORENCE 0401CB | 12690401 | FLORENCE 0401 | 1041.2537 | 0.64714 | 39 | 0.0001023 | 2.6231e-06 | 3452 | 26135.6108 | 0.012156 | 4.9094e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1560 | SANTA ROSA A 1104CB | 42151104 | SANTA ROSA A 1104 | 369.0017 | 0.22934 | 76 | 0.00019889 | 2.617e-06 | 3453 | 26135.8401 | 0.011958 | 4.8291e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9790 | PAUL SWEET 2109680537 | 83252109 | PAUL SWEET 2109 | 362.7293 | 0.22544 | 9 | 2.3381e-05 | 2.5979e-06 | 3454 | 26136.0656 | 0.011934 | 4.8196e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9764 | PACIFICA 1102512070 | 22811102 | PACIFICA 1102 | 279.6247 | 0.17379 | 5 | 1.293e-05 | 2.586e-06 | 3455 | 26136.2393 | 0.011921 | 4.8144e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2324 | ALTO 1124CB | 42031124 | ALTO 1124 | 2733.348 | 1.6988 | 81 | 0.00020929 | 2.5838e-06 | 3456 | 26137.9381 | 0.011712 | 4.7299e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2547 | CASTRO VALLEY 1102MR204 | 14091102 | CASTRO VALLEY 1102 | 326.5252 | 0.20294 | 46 | 0.00011849 | 2.5759e-06 | 3457 | 26138.1411 | 0.011593 | 4.682e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
885 | EDES 1112CR308 | 13681112 | EDES 1112 | 5168.8003 | 3.2124 | 53 | 0.00013527 | 2.5524e-06 | 3458 | 26141.3535 | 0.011458 | 4.6274e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7145 | HICKS 111512494 | 83431115 | HICKS 1115 | 220.1167 | 0.1368 | 35 | 8.9268e-05 | 2.5505e-06 | 3459 | 26141.4903 | 0.011369 | 4.5914e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
970 | CAYUCOS 1102CB | 182551102 | CAYUCOS 1102 | 0 | 0 | 41 | 0.00010442 | 2.5468e-06 | 3460 | 26141.4903 | 0.011265 | 4.5492e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7960 | LOS GATOS 1101206248 | 82021101 | LOS GATOS 1101 | 83.0039 | 0.051587 | 10 | 2.5435e-05 | 2.5435e-06 | 3461 | 26141.5419 | 0.011239 | 4.5389e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2461 | HAMILTON BRANCH 110137436 | 102361101 | HAMILTON BRANCH 1101 | 1208.0743 | 0.75082 | 33 | 8.3735e-05 | 2.5374e-06 | 3462 | 26142.2927 | 0.011155 | 4.5051e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5208 | VIEJO 22029120 | 182852202 | VIEJO 2202 | 2858.0041 | 1.7763 | 112 | 0.00028404 | 2.5361e-06 | 3463 | 26144.069 | 0.010871 | 4.3904e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10027 | PACIFICA 1103398620 | 22811103 | PACIFICA 1103 | 758.0837 | 0.47115 | 7 | 1.7717e-05 | 2.531e-06 | 3464 | 26144.5401 | 0.010854 | 4.3832e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4053 | OAKLAND X 1105184672 | 12541105 | OAKLAND X 1105 | 2666.0437 | 1.657 | 46 | 0.00011617 | 2.5255e-06 | 3465 | 26146.1971 | 0.010737 | 4.3363e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5327 | FAIRVIEW 2207CB | 13432207 | FAIRVIEW 2207 | 387.1496 | 0.24062 | 57 | 0.00014314 | 2.5112e-06 | 3466 | 26146.4377 | 0.010594 | 4.2785e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1098 | VIEJO 22012064 | 182852201 | VIEJO 2201 | 1409.3976 | 0.87595 | 15 | 3.729e-05 | 2.486e-06 | 3467 | 26147.3136 | 0.010557 | 4.2635e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3180 | STAFFORD 110242542 | 43201102 | STAFFORD 1102 | 862.3483 | 0.53595 | 52 | 0.00012818 | 2.465e-06 | 3468 | 26147.8496 | 0.010429 | 4.2117e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4684 | SNEATH LANE 110134438 | 22721101 | SNEATH LANE 1101 | 3709.6211 | 2.3055 | 67 | 0.00016445 | 2.4545e-06 | 3469 | 26150.1551 | 0.010264 | 4.1453e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5609 | BURNEY 110297318 | 103311102 | BURNEY 1102 | 294.9732 | 0.18333 | 18 | 4.4019e-05 | 2.4455e-06 | 3470 | 26150.3385 | 0.01022 | 4.1275e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3808 | HAMILTON BRANCH 11013049 | 102361101 | HAMILTON BRANCH 1101 | 1650.9947 | 1.0261 | 23 | 5.6224e-05 | 2.4445e-06 | 3471 | 26151.3646 | 0.010164 | 4.1048e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10978 | ALTO 1124965060 | 42031124 | ALTO 1124 | 99.6543 | 0.061936 | 1 | 2.4396e-06 | 2.4396e-06 | 3472 | 26151.4265 | 0.010162 | 4.1038e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10767 | SAUSALITO 1102758798 | 42491102 | SAUSALITO 1102 | 53.2652 | 0.033105 | 2 | 4.8318e-06 | 2.4159e-06 | 3473 | 26151.4596 | 0.010157 | 4.1019e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2223 | PAUL SWEET 2109CB | 83252109 | PAUL SWEET 2109 | 20.7388 | 0.012889 | 171 | 0.00040951 | 2.3948e-06 | 3474 | 26151.4725 | 0.0097474 | 3.9365e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4848 | VALLEY VIEW 1103P160 | 14341103 | VALLEY VIEW 1103 | 0 | 0 | 96 | 0.00022785 | 2.3734e-06 | 3475 | 26151.4725 | 0.0095195 | 3.8445e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1157 | MORAGA 1105116034 | 13801105 | MORAGA 1105 | 539.5091 | 0.33531 | 41 | 9.6928e-05 | 2.3641e-06 | 3476 | 26151.8078 | 0.0094226 | 3.8053e-07 | 0.0094226 | #N/A | #N/A | #N/A | #N/A | #VALUE!
6537 | SNEATH LANE 110275844 | 22721102 | SNEATH LANE 1102 | 272.6844 | 0.16947 | 10 | 2.3271e-05 | 2.3271e-06 | 3477 | 26151.9773 | 0.0093993 | 3.7959e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1692 | SAN CARLOS 11048846 | 24181104 | SAN CARLOS 1104 | 3588.6165 | 2.2303 | 61 | 0.00014163 | 2.3218e-06 | 3478 | 26154.2076 | 0.0092577 | 3.7387e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5922 | SNEATH LANE 1101CB | 22721101 | SNEATH LANE 1101 | 745.3166 | 0.46322 | 19 | 4.3942e-05 | 2.3127e-06 | 3479 | 26154.6708 | 0.0092137 | 3.721e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3263 | SAN LEANDRO U 1109936988 | 13111109 | SAN LEANDRO U 1109 | 10891.0554 | 6.7688 | 86 | 0.00019824 | 2.3051e-06 | 3480 | 26161.4397 | 0.0090155 | 3.6409e-07 | 0.0090155 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7536 | WILLITS 11021270 | 42661102 | WILLITS 1102 | 0 | 0 | 21 | 4.8357e-05 | 2.3027e-06 | 3481 | 26161.4397 | 0.0089671 | 3.6214e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2607 | WALDO 0402258792 | 13350402 | WALDO 0402 | 4793.9751 | 2.9795 | 36 | 8.287e-05 | 2.3019e-06 | 3482 | 26164.4191 | 0.0088843 | 3.5879e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2976 | STAFFORD 1101902998 | 43201101 | STAFFORD 1101 | 1732.2882 | 1.0766 | 81 | 0.00018615 | 2.2981e-06 | 3483 | 26165.4958 | 0.0086981 | 3.5127e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
28 | RALSTON 110148936 | 24141101 | RALSTON 1101 | 7437.214 | 4.6223 | 86 | 0.00019731 | 2.2943e-06 | 3484 | 26170.118 | 0.0085008 | 3.4331e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6723 | VALLEY VIEW 1106P128 | 14341106 | VALLEY VIEW 1106 | 190.9091 | 0.11865 | 31 | 7.0301e-05 | 2.2678e-06 | 3485 | 26170.2367 | 0.0084305 | 3.4047e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6528 | LAS GALLINAS A 1106206332 | 42991106 | LAS GALLINAS A 1106 | 488.8653 | 0.30383 | 7 | 1.5798e-05 | 2.2569e-06 | 3486 | 26170.5405 | 0.0084147 | 3.3983e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2106 | SPRUCE 0402BR304 | 13340402 | SPRUCE 0402 | 2392.7287 | 1.4871 | 53 | 0.00011921 | 2.2492e-06 | 3487 | 26172.0276 | 0.0082955 | 3.3501e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3661 | LAS GALLINAS A 1106685656 | 42991106 | LAS GALLINAS A 1106 | 1923.4165 | 1.1954 | 43 | 9.5996e-05 | 2.2325e-06 | 3488 | 26173.223 | 0.0081995 | 3.3114e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3471 | LOS GATOS 110160136 | 82021101 | LOS GATOS 1101 | 0 | 0 | 57 | 0.00012684 | 2.2252e-06 | 3489 | 26173.223 | 0.0080727 | 3.2602e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4292 | EMERALD LAKE 04028872 | 24080402 | EMERALD LAKE 0402 | 7244.0552 | 4.5022 | 77 | 0.00016952 | 2.2015e-06 | 3490 | 26177.7252 | 0.0079032 | 3.1917e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1116 | SNEATH LANE 110168070 | 22721101 | SNEATH LANE 1101 | 373.7094 | 0.23226 | 30 | 6.5858e-05 | 2.1953e-06 | 3491 | 26177.9575 | 0.0078373 | 3.1651e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9555 | IGNACIO 1103504941 | 42481103 | IGNACIO 1103 | 663.24 | 0.41221 | 6 | 1.3164e-05 | 2.194e-06 | 3492 | 26178.3697 | 0.0078241 | 3.1598e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4494 | VIEJO 22019704 | 182852201 | VIEJO 2201 | 786.5986 | 0.48887 | 29 | 6.3429e-05 | 2.1872e-06 | 3493 | 26178.8586 | 0.0077607 | 3.1342e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3505 | WOODSIDE 11049030 | 24251104 | WOODSIDE 1104 | 3272.4558 | 2.0338 | 37 | 8.0902e-05 | 2.1865e-06 | 3494 | 26180.8924 | 0.0076798 | 3.1015e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4601 | HATTON 11022070 | 182291102 | HATTON 1102 | 843.4628 | 0.52422 | 26 | 5.6595e-05 | 2.1767e-06 | 3495 | 26181.4166 | 0.0076232 | 3.0786e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10245 | GREENBRAE 1104972264 | 43091104 | GREENBRAE 1104 | 0 | 0 | 4 | 8.6927e-06 | 2.1732e-06 | 3496 | 26181.4166 | 0.0076145 | 3.0751e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6525 | HAMILTON BRANCH 11012082 | 102361101 | HAMILTON BRANCH 1101 | 2445.1965 | 1.5197 | 46 | 9.9139e-05 | 2.1552e-06 | 3497 | 26182.9363 | 0.0075154 | 3.0351e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7268 | HICKS 1116203897 | 83431116 | HICKS 1116 | 367.9073 | 0.22866 | 9 | 1.9358e-05 | 2.1509e-06 | 3498 | 26183.165 | 0.007496 | 3.0273e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5472 | CHESTER 1101656108 | 103181101 | CHESTER 1101 | 838.7097 | 0.52126 | 10 | 2.1478e-05 | 2.1478e-06 | 3499 | 26183.6862 | 0.0074745 | 3.0186e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
659 | EL CERRITO G 1112BR196 | 12501112 | EL CERRITO G 1112 | 0 | 0 | 51 | 0.00010848 | 2.127e-06 | 3500 | 26183.6862 | 0.0073661 | 2.9748e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
286 | OAKLAND X 1106CB | 12541106 | OAKLAND X 1106 | 5284.9861 | 3.2846 | 136 | 0.00028825 | 2.1195e-06 | 3501 | 26186.9709 | 0.0070778 | 2.8584e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3401 | VIEJO 22029104 | 182852202 | VIEJO 2202 | 9148.567 | 5.6859 | 79 | 0.00016692 | 2.113e-06 | 3502 | 26192.6567 | 0.0069109 | 2.791e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
617 | OAK 0401CB | 12600401 | OAK 0401 | 5585.5806 | 3.4715 | 68 | 0.00014192 | 2.0871e-06 | 3503 | 26196.1282 | 0.006769 | 2.7337e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5991 | VIEJO 22019698 | 182852201 | VIEJO 2201 | 929.6624 | 0.57779 | 10 | 2.0607e-05 | 2.0607e-06 | 3504 | 26196.706 | 0.0067484 | 2.7253e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2044 | SPRUCE 0401BR316 | 13340401 | SPRUCE 0401 | 6608.6922 | 4.1073 | 56 | 0.00011529 | 2.0588e-06 | 3505 | 26200.8133 | 0.0066331 | 2.6788e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7179 | EL CERRITO G 111257953 | 12501112 | EL CERRITO G 1112 | 353.2769 | 0.21956 | 11 | 2.2566e-05 | 2.0515e-06 | 3506 | 26201.0329 | 0.0066105 | 2.6697e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5036 | FRANKLIN 1104CB | 13921104 | FRANKLIN 1104 | 466.2641 | 0.28979 | 63 | 0.00012831 | 2.0367e-06 | 3507 | 26201.3227 | 0.0064822 | 2.6178e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6325 | LOS GATOS 1108CB | 82021108 | LOS GATOS 1108 | 0 | 0 | 15 | 3.0501e-05 | 2.0334e-06 | 3508 | 26201.3227 | 0.0064517 | 2.6055e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6874 | LOS GATOS 1102CB | 82021102 | LOS GATOS 1102 | 0 | 0 | 70 | 0.00014108 | 2.0154e-06 | 3509 | 26201.3227 | 0.0063106 | 2.5485e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1424 | PACIFICA 1103CB | 22811103 | PACIFICA 1103 | 109.5296 | 0.068073 | 62 | 0.00012428 | 2.0046e-06 | 3510 | 26201.3907 | 0.0061863 | 2.4984e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10000 | ALTO 1125781759 | 42031125 | ALTO 1125 | 210.4887 | 0.13082 | 4 | 8.0105e-06 | 2.0026e-06 | 3511 | 26201.5216 | 0.0061783 | 2.4951e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
254 | HICKS 1116CB | 83431116 | HICKS 1116 | 336.1648 | 0.20893 | 165 | 0.00032262 | 1.9553e-06 | 3512 | 26201.7305 | 0.0058557 | 2.3648e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1238 | STAFFORD 11021019 | 43201102 | STAFFORD 1102 | 432.0709 | 0.26853 | 10 | 1.946e-05 | 1.946e-06 | 3513 | 26201.999 | 0.0058362 | 2.357e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10590 | CHESTER 1102546744 | 103181102 | CHESTER 1102 | 428.8696 | 0.26654 | 7 | 1.3538e-05 | 1.934e-06 | 3514 | 26202.2656 | 0.0058227 | 2.3515e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6891 | ALTO 1124994213 | 42031124 | ALTO 1124 | 198.7798 | 0.12354 | 8 | 1.5241e-05 | 1.9051e-06 | 3515 | 26202.3891 | 0.0058075 | 2.3453e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9434 | BERKELEY F 1105849701 | 12061105 | BERKELEY F 1105 | 213.7724 | 0.13286 | 2 | 3.7788e-06 | 1.8894e-06 | 3516 | 26202.522 | 0.0058037 | 2.3438e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6092 | VIEJO 22049540 | 182852204 | VIEJO 2204 | 2319.7097 | 1.4417 | 32 | 6.0431e-05 | 1.8885e-06 | 3517 | 26203.9637 | 0.0057433 | 2.3194e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9394 | ALTO 1124884949 | 42031124 | ALTO 1124 | 312.7335 | 0.19437 | 5 | 9.3841e-06 | 1.8768e-06 | 3518 | 26204.1581 | 0.0057339 | 2.3156e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8014 | WALDO 0401965216 | 13350401 | WALDO 0401 | 2642.7419 | 1.6425 | 21 | 3.9227e-05 | 1.868e-06 | 3519 | 26205.8005 | 0.0056946 | 2.2998e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4883 | LAS PULGAS 0401104588 | 24120401 | LAS PULGAS 0401 | 581.4114 | 0.36135 | 11 | 2.0518e-05 | 1.8653e-06 | 3520 | 26206.1619 | 0.0056741 | 2.2915e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8033 | MORAGA 110531512 | 13801105 | MORAGA 1105 | 0 | 0 | 29 | 5.3819e-05 | 1.8558e-06 | 3521 | 26206.1619 | 0.0056203 | 2.2698e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4423 | SAN RAFAEL 1105344 | 42011105 | SAN RAFAEL 1105 | 1314.7551 | 0.81713 | 97 | 0.00017996 | 1.8552e-06 | 3522 | 26206.979 | 0.0054403 | 2.1971e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3011 | PERRY 1101W52 | 183071101 | PERRY 1101 | 5033.3373 | 3.1282 | 51 | 9.4548e-05 | 1.8539e-06 | 3523 | 26210.1072 | 0.0053458 | 2.1589e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2767 | EL CERRITO G 1112BR180 | 12501112 | EL CERRITO G 1112 | 675.0712 | 0.41956 | 25 | 4.6282e-05 | 1.8513e-06 | 3524 | 26210.5268 | 0.0052995 | 2.1402e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7505 | EDES 1112CR306 | 13681112 | EDES 1112 | 1619.5833 | 1.0066 | 16 | 2.9404e-05 | 1.8377e-06 | 3525 | 26211.5334 | 0.0052701 | 2.1283e-07 | 0.0052701 | #N/A | #N/A | #N/A | #N/A | #VALUE!
349 | ALHAMBRA 1102CB | 14101102 | ALHAMBRA 1102 | 431.1151 | 0.26794 | 75 | 0.00013376 | 1.7835e-06 | 3526 | 26211.8013 | 0.0051363 | 2.0743e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5900 | CHESTER 1102CB | 103181102 | CHESTER 1102 | 40.2966 | 0.025045 | 38 | 6.751e-05 | 1.7766e-06 | 3527 | 26211.8264 | 0.0050688 | 2.0471e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6024 | WOODSIDE 11028862 | 24251102 | WOODSIDE 1102 | 0 | 0 | 38 | 6.7125e-05 | 1.7665e-06 | 3528 | 26211.8264 | 0.0050017 | 2.0199e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4122 | BURNEY 110257046 | 103311102 | BURNEY 1102 | 48.9091 | 0.030397 | 12 | 2.1104e-05 | 1.7587e-06 | 3529 | 26211.8568 | 0.0049806 | 2.0114e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2110 | CASTRO VALLEY 1108MR205 | 14091108 | CASTRO VALLEY 1108 | 0 | 0 | 73 | 0.00012759 | 1.7478e-06 | 3530 | 26211.8568 | 0.004853 | 1.9599e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2448 | VIEJO 22029112 | 182852202 | VIEJO 2202 | 1359.4094 | 0.84488 | 43 | 7.4909e-05 | 1.7421e-06 | 3531 | 26212.7016 | 0.0047781 | 1.9296e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8885 | EL CERRITO G 1110BR236 | 12501110 | EL CERRITO G 1110 | 819.8964 | 0.50957 | 7 | 1.2161e-05 | 1.7373e-06 | 3532 | 26213.2112 | 0.004766 | 1.9247e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7598 | ALTO 1123820379 | 42031123 | ALTO 1123 | 245.2911 | 0.15245 | 2 | 3.4724e-06 | 1.7362e-06 | 3533 | 26213.3637 | 0.0047625 | 1.9233e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1294 | VIEJO 2203573610 | 182852203 | VIEJO 2203 | 0 | 0 | 41 | 7.0764e-05 | 1.7259e-06 | 3534 | 26213.3637 | 0.0046917 | 1.8948e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2844 | SAN CARLOS 11039148 | 24181103 | SAN CARLOS 1103 | 0 | 0 | 51 | 8.7791e-05 | 1.7214e-06 | 3535 | 26213.3637 | 0.0046039 | 1.8593e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
469 | VIEJO 22039094 | 182852203 | VIEJO 2203 | 160.2742 | 0.099611 | 32 | 5.4823e-05 | 1.7132e-06 | 3536 | 26213.4633 | 0.0045491 | 1.8372e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7298 | VIEJO 22032634 | 182852203 | VIEJO 2203 | 0 | 0 | 23 | 3.8458e-05 | 1.6721e-06 | 3537 | 26213.4633 | 0.0045106 | 1.8216e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8157 | OAKLAND J 1105CR150 | 12091105 | OAKLAND J 1105 | 348.5421 | 0.21662 | 6 | 1.0002e-05 | 1.667e-06 | 3538 | 26213.6799 | 0.0045006 | 1.8176e-07 | 0.0045006 | #N/A | #N/A | #N/A | #N/A | #VALUE!
7733 | FORT BRAGG A 1103CB | 42761103 | FORT BRAGG A 1103 | 151.4693 | 0.094139 | 40 | 6.6534e-05 | 1.6633e-06 | 3539 | 26213.774 | 0.0044341 | 1.7907e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9029 | MORGAN HILL 2105375239 | 83242105 | MORGAN HILL 2105 | 145.1624 | 0.090219 | 4 | 6.5821e-06 | 1.6455e-06 | 3540 | 26213.8642 | 0.0044275 | 1.7881e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9198 | MORGAN HILL 2105345099 | 83242105 | MORGAN HILL 2105 | 293.3262 | 0.1823 | 5 | 8.156e-06 | 1.6312e-06 | 3541 | 26214.0465 | 0.0044194 | 1.7848e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8274 | SALT SPRINGS 21013116 | 163692101 | SALT SPRINGS 2101 | 1250.9687 | 0.77748 | 10 | 1.6267e-05 | 1.6267e-06 | 3542 | 26214.824 | 0.0044031 | 1.7782e-07 | 0.0044031 | #N/A | #N/A | #N/A | #N/A | #VALUE!
1788 | BERKELEY F 0402502466 | 12060402 | BERKELEY F 0402 | 226.0238 | 0.14047 | 10 | 1.6151e-05 | 1.6151e-06 | 3543 | 26214.9645 | 0.004387 | 1.7717e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2459 | BERKELEY F 1105CB | 12061105 | BERKELEY F 1105 | 1669.1452 | 1.0374 | 103 | 0.00016514 | 1.6033e-06 | 3544 | 26216.0019 | 0.0042218 | 1.705e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
179 | EL CERRITO G 1108BR346 | 12501108 | EL CERRITO G 1108 | 0 | 0 | 102 | 0.00016212 | 1.5894e-06 | 3545 | 26216.0019 | 0.0040597 | 1.6395e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1332 | HOLLYWOOD 0401CB | 13170401 | HOLLYWOOD 0401 | 4604.9325 | 2.862 | 70 | 0.00010933 | 1.5619e-06 | 3546 | 26218.8639 | 0.0039504 | 1.5954e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6502 | ESTUDILLO 0401850884 | 13480401 | ESTUDILLO 0401 | 1368.1711 | 0.85032 | 19 | 2.9549e-05 | 1.5552e-06 | 3547 | 26219.7142 | 0.0039208 | 1.5834e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1386 | PACIFICA 1103915474 | 22811103 | PACIFICA 1103 | 697.4237 | 0.43345 | 98 | 0.00014771 | 1.5073e-06 | 3548 | 26220.1476 | 0.0037731 | 1.5238e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1210 | COTATI 110283200 | 42271102 | COTATI 1102 | 0 | 0 | 48 | 7.0606e-05 | 1.471e-06 | 3549 | 26220.1476 | 0.0037025 | 1.4953e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7453 | SNEATH LANE 110748338 | 22721107 | SNEATH LANE 1107 | 181.1517 | 0.11259 | 17 | 2.4768e-05 | 1.4569e-06 | 3550 | 26220.2602 | 0.0036777 | 1.4853e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4821 | RALSTON 11029126 | 24141102 | RALSTON 1102 | 1621.4045 | 1.0077 | 25 | 3.5823e-05 | 1.4329e-06 | 3551 | 26221.2679 | 0.0036419 | 1.4708e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7237 | PACIFIC GROVE 04222614 | 182440422 | PACIFIC GROVE 0422 | 1037.2147 | 0.64463 | 28 | 4.0087e-05 | 1.4317e-06 | 3552 | 26221.9126 | 0.0036018 | 1.4546e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1100 | DEL MONTE 210386496 | 182222103 | DEL MONTE 2103 | 1600.54 | 0.99474 | 94 | 0.00013413 | 1.4269e-06 | 3553 | 26222.9073 | 0.0034677 | 1.4004e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8851 | SAN CARLOS 1103888954 | 24181103 | SAN CARLOS 1103 | 0 | 0 | 6 | 8.4914e-06 | 1.4152e-06 | 3554 | 26222.9073 | 0.0034592 | 1.397e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2645 | OAKLAND J 1106CR164 | 12091106 | OAKLAND J 1106 | 2405.3877 | 1.495 | 85 | 0.00011967 | 1.4079e-06 | 3555 | 26224.4023 | 0.0033395 | 1.3487e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7417 | EL CERRITO G 1112209865 | 12501112 | EL CERRITO G 1112 | 423.0102 | 0.2629 | 11 | 1.5482e-05 | 1.4074e-06 | 3556 | 26224.6652 | 0.003324 | 1.3424e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
45 | OAKLAND J 1105153228 | 12091105 | OAKLAND J 1105 | 463.496 | 0.28806 | 54 | 7.5821e-05 | 1.4041e-06 | 3557 | 26224.9532 | 0.0032482 | 1.3118e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8437 | SWIFT 2109XR300 | 83392109 | SWIFT 2109 | 526.7556 | 0.32738 | 14 | 1.9531e-05 | 1.3951e-06 | 3558 | 26225.2806 | 0.0032287 | 1.3039e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10517 | EL CERRITO G 1110173396 | 12501110 | EL CERRITO G 1110 | 265.7346 | 0.16516 | 3 | 4.1666e-06 | 1.3889e-06 | 3559 | 26225.4458 | 0.0032245 | 1.3022e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9170 | SAN CARLOS 1103313472 | 24181103 | SAN CARLOS 1103 | 43.1608 | 0.026825 | 9 | 1.2158e-05 | 1.3509e-06 | 3560 | 26225.4726 | 0.0032124 | 1.2973e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9880 | IGNACIO 1103151462 | 42481103 | IGNACIO 1103 | 247.7748 | 0.15399 | 3 | 4.025e-06 | 1.3417e-06 | 3561 | 26225.6266 | 0.0032083 | 1.2957e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8103 | WOODSIDE 1102472928 | 24251102 | WOODSIDE 1102 | 124.8253 | 0.077579 | 14 | 1.8663e-05 | 1.3331e-06 | 3562 | 26225.7042 | 0.0031897 | 1.2882e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
657 | OAKLAND J 1102CR252 | 12091102 | OAKLAND J 1102 | 1765.2604 | 1.0971 | 92 | 0.0001213 | 1.3184e-06 | 3563 | 26226.8013 | 0.0030684 | 1.2392e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
146 | CASTRO VALLEY 1110MR379 | 14091110 | CASTRO VALLEY 1110 | 1749.5827 | 1.0874 | 22 | 2.8794e-05 | 1.3088e-06 | 3564 | 26227.8887 | 0.0030396 | 1.2275e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9441 | MORRO BAY 11013487 | 183011101 | MORRO BAY 1101 | 0 | 0 | 20 | 2.5244e-05 | 1.2622e-06 | 3565 | 26227.8887 | 0.0030143 | 1.2173e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5751 | FORT BRAGG A 1104CB | 42761104 | FORT BRAGG A 1104 | 118.7443 | 0.0738 | 41 | 5.1642e-05 | 1.2596e-06 | 3566 | 26227.9625 | 0.0029627 | 1.1965e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8075 | ALTO 1124246034 | 42031124 | ALTO 1124 | 202.2758 | 0.12572 | 4 | 5.0314e-06 | 1.2578e-06 | 3567 | 26228.0882 | 0.0029577 | 1.1945e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
447 | OCEANO 1105V44 | 182601105 | OCEANO 1105 | 1259.7645 | 0.78295 | 17 | 2.1378e-05 | 1.2575e-06 | 3568 | 26228.8711 | 0.0029363 | 1.1858e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3262 | OAKLAND J 1106CR330 | 12091106 | OAKLAND J 1106 | 1155.5838 | 0.7182 | 31 | 3.8635e-05 | 1.2463e-06 | 3569 | 26229.5893 | 0.0028977 | 1.1702e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
650 | OAKLAND J 1116CR328 | 12091116 | OAKLAND J 1116 | 956.1241 | 0.59424 | 68 | 8.4712e-05 | 1.2458e-06 | 3570 | 26230.1836 | 0.0028129 | 1.136e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4530 | VIEJO 220285904 | 182852202 | VIEJO 2202 | 1684.9898 | 1.0472 | 24 | 2.9864e-05 | 1.2443e-06 | 3571 | 26231.2308 | 0.0027831 | 1.1239e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4873 | ALHAMBRA 110213333 | 14101102 | ALHAMBRA 1102 | 70.7861 | 0.043994 | 4 | 4.9594e-06 | 1.2398e-06 | 3572 | 26231.2748 | 0.0027781 | 1.1219e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5686 | MORRO BAY 1102V80 | 183011102 | MORRO BAY 1102 | 222.7519 | 0.13844 | 28 | 3.3939e-05 | 1.2121e-06 | 3573 | 26231.4132 | 0.0027442 | 1.1082e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
495 | BELMONT 11109090 | 24031110 | BELMONT 1110 | 0 | 0 | 38 | 4.5748e-05 | 1.2039e-06 | 3574 | 26231.4132 | 0.0026984 | 1.0898e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1032 | ALTO 1123CB | 42031123 | ALTO 1123 | 893.6462 | 0.5554 | 84 | 9.7839e-05 | 1.1648e-06 | 3575 | 26231.9686 | 0.0026006 | 1.0503e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4356 | BELMONT 11038956 | 24031103 | BELMONT 1103 | 474.6132 | 0.29497 | 18 | 2.0752e-05 | 1.1529e-06 | 3576 | 26232.2636 | 0.0025798 | 1.0419e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3862 | GREENBRAE 1104751 | 43091104 | GREENBRAE 1104 | 264.612 | 0.16446 | 31 | 3.5714e-05 | 1.1521e-06 | 3577 | 26232.4281 | 0.0025441 | 1.0274e-07 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3522 | CHESTER 1101CB | 103181101 | CHESTER 1101 | 128.9588 | 0.080148 | 69 | 7.9023e-05 | 1.1453e-06 | 3578 | 26232.5082 | 0.0024651 | 9.9554e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1797 | BERKELEY F 1103BR110 | 12061103 | BERKELEY F 1103 | 0 | 0 | 45 | 5.1365e-05 | 1.1415e-06 | 3579 | 26232.5082 | 0.0024137 | 9.7479e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3950 | MONTEREY 04022644 | 182090402 | MONTEREY 0402 | 1828.1218 | 1.1362 | 23 | 2.6115e-05 | 1.1355e-06 | 3580 | 26233.6444 | 0.0023876 | 9.6424e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3110 | KIRKER 2104CB | 14452104 | KIRKER 2104 | 74.5132 | 0.04631 | 140 | 0.0001576 | 1.1257e-06 | 3581 | 26233.6907 | 0.00223 | 9.006e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
973 | DEL MONTE 110138582 | 182221101 | DEL MONTE 1101 | 853.8778 | 0.53069 | 53 | 5.9598e-05 | 1.1245e-06 | 3582 | 26234.2214 | 0.0021704 | 8.7653e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
72 | PACIFICA 11026783 | 22811102 | PACIFICA 1102 | 0 | 0 | 50 | 5.6147e-05 | 1.1229e-06 | 3583 | 26234.2214 | 0.0021143 | 8.5386e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6129 | PERRY 1101W12 | 183071101 | PERRY 1101 | 6046.1264 | 3.7577 | 70 | 7.5829e-05 | 1.0833e-06 | 3584 | 26237.9791 | 0.0020385 | 8.2323e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3828 | ALTO 1120500 | 42031120 | ALTO 1120 | 426.2211 | 0.2649 | 39 | 4.203e-05 | 1.0777e-06 | 3585 | 26238.244 | 0.0019964 | 8.0626e-08 | 0.0019964 | #N/A | #N/A | #N/A | #N/A | #VALUE!
2036 | SAN LEANDRO U 1114MR218 | 13111114 | SAN LEANDRO U 1114 | 10386.8132 | 6.4554 | 134 | 0.00014329 | 1.0693e-06 | 3586 | 26244.6994 | 0.0018531 | 7.4839e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
66 | OAKLAND X 1105CB | 12541105 | OAKLAND X 1105 | 1675.1277 | 1.0411 | 153 | 0.00016184 | 1.0578e-06 | 3587 | 26245.7405 | 0.0016913 | 6.8303e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3740 | BERKELEY F 0402CB | 12060402 | BERKELEY F 0402 | 47.0231 | 0.029225 | 21 | 2.2159e-05 | 1.0552e-06 | 3588 | 26245.7698 | 0.0016691 | 6.7408e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2665 | VALLEY VIEW 1105P190 | 14341105 | VALLEY VIEW 1105 | 0 | 0 | 28 | 2.951e-05 | 1.0539e-06 | 3589 | 26245.7698 | 0.0016396 | 6.6216e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
62 | BAY MEADOWS 2102CB | 24012102 | BAY MEADOWS 2102 | 159.3502 | 0.099037 | 95 | 9.8546e-05 | 1.0373e-06 | 3590 | 26245.8688 | 0.0015411 | 6.2236e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3225 | VALLEY VIEW 1105CB | 14341105 | VALLEY VIEW 1105 | 0 | 0 | 59 | 5.9995e-05 | 1.0169e-06 | 3591 | 26245.8688 | 0.0014811 | 5.9814e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1682 | OAKLAND J 1118CR198 | 12091118 | OAKLAND J 1118 | 515.4771 | 0.32037 | 70 | 7.0418e-05 | 1.006e-06 | 3592 | 26246.1892 | 0.0014107 | 5.697e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6551 | EL CERRITO G 1111760530 | 12501111 | EL CERRITO G 1111 | 342.5788 | 0.21291 | 13 | 1.2511e-05 | 9.624e-07 | 3593 | 26246.4021 | 0.0013982 | 5.6465e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
838 | MORRO BAY 1102W22 | 183011102 | MORRO BAY 1102 | 4174.2289 | 2.5943 | 85 | 8.1495e-05 | 9.5877e-07 | 3594 | 26248.9964 | 0.0013167 | 5.3173e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2660 | CASTRO VALLEY 1105MR201 | 14091105 | CASTRO VALLEY 1105 | 2014.3888 | 1.252 | 112 | 0.00010718 | 9.5698e-07 | 3595 | 26250.2483 | 0.0012095 | 4.8845e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6961 | SAUSALITO 11021224 | 42491102 | SAUSALITO 1102 | 17.2769 | 0.010738 | 29 | 2.7124e-05 | 9.3531e-07 | 3596 | 26250.2591 | 0.0011824 | 4.7749e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2515 | EL CERRITO G 1113CB | 12501113 | EL CERRITO G 1113 | 158.1749 | 0.098306 | 63 | 5.7843e-05 | 9.1814e-07 | 3597 | 26250.3574 | 0.0011245 | 4.5413e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3037 | EL CERRITO G 1108CB | 12501108 | EL CERRITO G 1108 | 4.3429 | 0.0026991 | 99 | 8.9911e-05 | 9.0819e-07 | 3598 | 26250.3601 | 0.0010346 | 4.1782e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2758 | VALLEY VIEW 1105P124 | 14341105 | VALLEY VIEW 1105 | 0 | 0 | 43 | 3.8877e-05 | 9.0411e-07 | 3599 | 26250.3601 | 0.00099572 | 4.0212e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3672 | EDES 1112CB | 13681112 | EDES 1112 | 70.4619 | 0.043792 | 16 | 1.4384e-05 | 8.9903e-07 | 3600 | 26250.4039 | 0.00098134 | 3.9631e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2376 | VIEJO 22049110 | 182852204 | VIEJO 2204 | 472.9116 | 0.29392 | 58 | 5.0966e-05 | 8.7872e-07 | 3601 | 26250.6978 | 0.00093037 | 3.7573e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
552 | ALTO 112088190 | 42031120 | ALTO 1120 | 163.0348 | 0.10133 | 34 | 2.9159e-05 | 8.5763e-07 | 3602 | 26250.7991 | 0.00090121 | 3.6396e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5498 | VIEJO 22049440 | 182852204 | VIEJO 2204 | 123.7395 | 0.076905 | 55 | 4.6991e-05 | 8.5438e-07 | 3603 | 26250.876 | 0.00085422 | 3.4498e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10858 | SOLEDAD 2101125484 | 182052101 | SOLEDAD 2101 | 1202.5462 | 0.74739 | 4 | 3.3971e-06 | 8.4928e-07 | 3604 | 26251.6234 | 0.00085082 | 3.4361e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
10655 | OCEANO 1104793774 | 182601104 | OCEANO 1104 | 111.8888 | 0.069539 | 3 | 2.52e-06 | 8.3998e-07 | 3605 | 26251.6929 | 0.0008483 | 3.4259e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4160 | EL CERRITO G 1110CB | 12501110 | EL CERRITO G 1110 | 423.1153 | 0.26297 | 35 | 2.8819e-05 | 8.2339e-07 | 3606 | 26251.9559 | 0.00081949 | 3.3095e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5087 | EDES 1112714759 | 13681112 | EDES 1112 | 361.9191 | 0.22493 | 11 | 8.9178e-06 | 8.1071e-07 | 3607 | 26252.1808 | 0.00081057 | 3.2735e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2691 | BOSTON 0401CR242 | 13320401 | BOSTON 0401 | 499.489 | 0.31043 | 59 | 4.7517e-05 | 8.0537e-07 | 3608 | 26252.4913 | 0.00076305 | 3.0816e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
425 | CASTRO VALLEY 1105MR236 | 14091105 | CASTRO VALLEY 1105 | 2212.8784 | 1.3753 | 112 | 8.9816e-05 | 8.0193e-07 | 3609 | 26253.8666 | 0.00067323 | 2.7189e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5569 | MORRO BAY 1101CB | 183011101 | MORRO BAY 1101 | 0 | 0 | 28 | 2.2429e-05 | 8.0102e-07 | 3610 | 26253.8666 | 0.00065081 | 2.6283e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
513 | OAKLAND J 1116CB | 12091116 | OAKLAND J 1116 | 0 | 0 | 253 | 0.00019978 | 7.8965e-07 | 3611 | 26253.8666 | 0.00045102 | 1.8215e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4433 | MONTEREY 04012642 | 182090401 | MONTEREY 0401 | 0 | 0 | 28 | 2.2062e-05 | 7.8793e-07 | 3612 | 26253.8666 | 0.00042896 | 1.7324e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1060 | SAN LEANDRO U 1114MR545 | 13111114 | SAN LEANDRO U 1114 | 3496.0754 | 2.1728 | 66 | 5.0766e-05 | 7.6919e-07 | 3613 | 26256.0394 | 0.0003782 | 1.5273e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8159 | SAN LUIS OBISPO 1103191498 | 182631103 | SAN LUIS OBISPO 1103 | 189.8568 | 0.118 | 2 | 1.4559e-06 | 7.2794e-07 | 3614 | 26256.1574 | 0.00037674 | 1.5215e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
749 | WALDO 0401CB | 13350401 | WALDO 0401 | 0 | 0 | 56 | 3.8386e-05 | 6.8547e-07 | 3615 | 26256.1574 | 0.00033835 | 1.3664e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8960 | OCEANO 1104337754 | 182601104 | OCEANO 1104 | 97.7177 | 0.060732 | 3 | 1.8316e-06 | 6.1054e-07 | 3616 | 26256.2181 | 0.00033652 | 1.359e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11035 | SOLEDAD 2101404754 | 182052101 | SOLEDAD 2101 | 1388.0334 | 0.86267 | 2 | 1.141e-06 | 5.7048e-07 | 3617 | 26257.0808 | 0.00033538 | 1.3544e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
2616 | DEL MONTE 21029060 | 182222102 | DEL MONTE 2102 | 1524.9134 | 0.94774 | 98 | 5.4254e-05 | 5.5361e-07 | 3618 | 26258.0285 | 0.00028113 | 1.1353e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3316 | SAN LEANDRO U 1114501762 | 13111114 | SAN LEANDRO U 1114 | 775.0508 | 0.4817 | 23 | 1.2672e-05 | 5.5098e-07 | 3619 | 26258.5102 | 0.00026845 | 1.0842e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
9297 | PACIFICA 1102934870 | 22811102 | PACIFICA 1102 | 147.5524 | 0.091704 | 7 | 3.8472e-06 | 5.496e-07 | 3620 | 26258.602 | 0.00026461 | 1.0686e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
7940 | SAN LEANDRO U 1109CR284 | 13111109 | SAN LEANDRO U 1109 | 1235.8311 | 0.76807 | 14 | 7.191e-06 | 5.1364e-07 | 3621 | 26259.37 | 0.00025742 | 1.0396e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3930 | SAN LEANDRO U 1109CR002 | 13111109 | SAN LEANDRO U 1109 | 269.8408 | 0.16771 | 16 | 8.2173e-06 | 5.1358e-07 | 3622 | 26259.5377 | 0.0002492 | 1.0064e-08 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
5801 | BELMONT 1110330790 | 24031110 | BELMONT 1110 | 199.5624 | 0.12403 | 8 | 4.0799e-06 | 5.0999e-07 | 3623 | 26259.6618 | 0.00024512 | 9.8991e-09 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
915 | WALDO 0402CB | 13350402 | WALDO 0402 | 0 | 0 | 27 | 1.3673e-05 | 5.064e-07 | 3624 | 26259.6618 | 0.00023145 | 9.3469e-09 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
472 | BANCROFT 0401CB | 13030401 | BANCROFT 0401 | 69.3073 | 0.043075 | 103 | 5.1467e-05 | 4.9968e-07 | 3625 | 26259.7048 | 0.00017998 | 7.2685e-09 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4940 | BERKELEY T 0404CB | 12660404 | BERKELEY T 0404 | 0 | 0 | 20 | 9.8213e-06 | 4.9106e-07 | 3626 | 26259.7048 | 0.00017016 | 6.8718e-09 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
206 | PACIFICA 110252715 | 22811102 | PACIFICA 1102 | 0 | 0 | 60 | 2.8824e-05 | 4.8039e-07 | 3627 | 26259.7048 | 0.00014133 | 5.7078e-09 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
4875 | OCEANO 1105V48 | 182601105 | OCEANO 1105 | 198.7298 | 0.12351 | 39 | 1.8e-05 | 4.6154e-07 | 3628 | 26259.8283 | 0.00012333 | 4.9808e-09 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3910 | SAN LEANDRO U 1114458451 | 13111114 | SAN LEANDRO U 1114 | 1967.4653 | 1.2228 | 29 | 1.3134e-05 | 4.5289e-07 | 3629 | 26261.0511 | 0.0001102 | 4.4504e-09 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1300 | BANCROFT 0402CB | 13030402 | BANCROFT 0402 | 597.2084 | 0.37117 | 58 | 2.5211e-05 | 4.3467e-07 | 3630 | 26261.4223 | 8.4989e-05 | 3.4323e-09 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
1186 | VIEJO 220436948 | 182852204 | VIEJO 2204 | 809.6273 | 0.50319 | 109 | 4.34e-05 | 3.9816e-07 | 3631 | 26261.9255 | 4.1589e-05 | 1.6796e-09 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
8981 | CASTRO VALLEY 1105132304 | 14091105 | CASTRO VALLEY 1105 | 118.6631 | 0.07375 | 13 | 4.9205e-06 | 3.785e-07 | 3632 | 26261.9992 | 3.6669e-05 | 1.4809e-09 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
3358 | FORT BRAGG A 110436526 | 42761104 | FORT BRAGG A 1104 | 72.2645 | 0.044913 | 84 | 3.0574e-05 | 3.6398e-07 | 3633 | 26262.0442 | 6.0945e-06 | 2.4613e-10 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
6760 | MORRO BAY 1101W04 | 183011101 | MORRO BAY 1101 | 437.2441 | 0.27175 | 26 | 6.0945e-06 | 2.344e-07 | 3634 | 26262.3159 | 2.6486e-11 | 1.0696e-15 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!
11118 | DIABLO CANYON 1101CB | 189001101 | DIABLO CANYON 1101 | 0 | 0 |  | 0 |  | 3635 | 26262.3159 | 2.6486e-11 | 1.0696e-15 | #N/A | #N/A | #N/A | #N/A | #N/A | #VALUE!

## Dx - EVM
Dx Prioritization Output - Enhanced Vegetation Management | [8 empty] | Planned 2019 implementation
Circuit Information |  |  | Independent Variables |  |  |  | Dependent Variable | Risk Scoring |  |  |  |  | Risk Tiers
Feeder name | District | Tier 2/3 OH Miles | Tagged trees per mile | # of tagged trees | HFTD Miles per Total Miles | Tier 3 per HFTD Miles | Ignition Indicator (1+ ignition occurred) | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Consolidated Risk Score | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Rank Cons Risk | Rank P*C | P*C
MIWUK 1701 | YOSEMITE | 77.1453 | 7.4105 | 571.3 | 100% | 97.77% | 1 | 0.84354 | 102.1389 | 2.7773 | 239.2862 | High | High | High | 1 | 2 | 86.1578
WOODACRE 1101 | NORTH BAY | 36.2703 | 156.5268 | 6651.2 | 85.36% | 71.43% | 0 | 0.6809 | 102.1389 | 3.1852 | 221.5201 | High | High | High | 2 | 10 | 69.546
MONTE RIO 1113 | SONOMA | 61.2941 | 99.1695 | 6079.1 | 99.99% | 100% | 1 | 0.93391 | 85.4511 | 2.601 | 207.5661 | High | High | High | 3 | 4 | 79.8036
STANISLAUS 1702 | YOSEMITE | 85.5755 | 16.3403 | 1397.79 | 100% | 92.5% | 0 | 0.76675 | 102.1389 | 2.4941 | 195.3255 | High | High | High | 4 | 5 | 78.3147
ORO FINO 1102 | NORTH VALLEY | 109.5969 | 17.2976 | 1899 | 99.83% | 75.7% | 1 | 0.68219 | 102.1389 | 2.501 | 174.2643 | High | High | High | 5 | 9 | 69.6785
MIWUK 1702 | YOSEMITE | 75.7688 | 0.82734 | 62.7 | 99.98% | 98.32% | 0 | 0.55447 | 102.1389 | 3.0491 | 172.6822 | High | High | High | 6 | 18 | 56.6335
WOODSIDE 1101 | PENINSULA | 42.209 | 285.1669 | 17974.3 | 66.97% | 99.11% | 0 | 0.89308 | 65.3912 | 2.8786 | 168.1085 | High | High | High | 7 | 17 | 58.3993
EL DORADO PH 2101 | SIERRA | 156.2859 | 130.0322 | 21677.5 | 93.75% | 82.3% | 0 | 0.97524 | 102.1389 | 1.4541 | 144.8389 | High | High | Low | 8 | 1 | 99.6103
MIDDLETOWN 1101 | HUMBOLDT | 93.5404 | 50.0386 | 5602.4 | 83.55% | 90.53% | 1 | 0.70848 | 102.1389 | 1.8992 | 137.4312 | High | High | Medium | 9 | 7 | 72.3631
MOLINO 1102 | SONOMA | 111.6641 | 99.4196 | 17711.5 | 62.68% | 81.73% | 1 | 0.97108 | 65.3912 | 2.116 | 134.3658 | High | High | Medium | 10 | 15 | 63.5003
ORO FINO 1101 | NORTH VALLEY | 46.3606 | 286.837 | 13336.6 | 99.71% | 100% | 1 | 0.45474 | 102.1389 | 2.8711 | 133.3506 | High | High | High | 11 | 26 | 46.4462
BRUNSWICK 1105 | SIERRA | 121.3812 | 4.8689 | 592.5 | 99.75% | 93.48% | 1 | 0.8365 | 102.1389 | 1.5525 | 132.6436 | High | High | Low | 12 | 3 | 85.4388
BRUNSWICK 1106 | SIERRA | 171.6273 | 45.8179 | 8382.6 | 93.81% | 72.18% | 1 | 0.84416 | 85.4511 | 1.8009 | 129.9055 | High | High | Medium | 13 | 8 | 72.1347
FITCH MOUNTAIN 1113 | SONOMA | 71.7242 | 123.815 | 18517.3 | 47.96% | 38.48% | 1 | 0.7917 | 85.4511 | 1.8073 | 122.2658 | High | High | Medium | 14 | 11 | 67.652
MONTE RIO 1112 | SONOMA | 20.2317 | 256.0419 | 5214.6 | 99.34% | 100% | 0 | 0.56345 | 85.4511 | 2.5369 | 122.1459 | High | High | High | 15 | 23 | 48.1473
SALT SPRINGS 2102 | STOCKTON | 52.0669 | 274.3811 | 14280.22 | 100% | 78.88% | 0 | 0.65297 | 102.1389 | 1.7662 | 117.7973 | High | High | Medium | 16 | 12 | 66.6938
BRUNSWICK 1103 | SIERRA | 55.5518 | 74.8354 | 4688.5 | 88.67% | 72.71% | 1 | 0.6063 | 102.1389 | 1.874 | 116.0496 | High | High | Medium | 17 | 16 | 61.9267
WEST POINT 1101 | STOCKTON | 63.0247 | 94.79 | 5975.19 | 99.98% | 100% | 0 | 0.54643 | 102.1389 | 2.0741 | 115.7578 | High | High | Medium | 18 | 19 | 55.8118
CHALLENGE 1102 | NORTH VALLEY | 63.9131 | 158.4626 | 10015.8 | 100% | 97.43% | 0 | 0.62542 | 102.1389 | 1.7937 | 114.581 | High | High | Medium | 19 | 14 | 63.8802
FORESTHILL 1101 | SIERRA | 65.2463 | 222.4185 | 14478 | 100% | 100% | 1 | 0.63906 | 102.1389 | 1.6905 | 110.3457 | High | High | Medium | 20 | 13 | 65.273
APPLE HILL 1104 | SIERRA | 91.8994 | 113.5688 | 10941.58 | 95.39% | 63.88% | 1 | 0.75734 | 102.1389 | 1.4126 | 109.2734 | High | High | Low | 21 | 6 | 77.3537
BRUNSWICK 1104 | SIERRA | 56.553 | 156.2805 | 9029.4 | 97.88% | 51.09% | 1 | 0.53349 | 102.1389 | 1.987 | 108.2731 | High | High | Medium | 22 | 20 | 54.4906
MIRABEL 1101 | SONOMA | 29.3053 | 373.4114 | 19421.8 | 56.34% | 71.1% | 1 | 0.45576 | 85.4511 | 2.3345 | 90.9172 | High | High | Medium | 23 | 29 | 38.9449
SYCAMORE CREEK 1111 | NORTH VALLEY | 53.4772 | 106.1279 | 6944.7 | 81.72% | 52.39% | 1 | 0.37047 | 102.1389 | 2.1453 | 81.1785 | High | High | Medium | 24 | 30 | 37.8399
BRUNSWICK 1102 | SIERRA | 51.0222 | 117.5978 | 6332.9 | 94.74% | 90.55% | 0 | 0.47031 | 102.1389 | 1.6284 | 78.2224 | High | High | Low | 25 | 24 | 48.037
PARADISE 1106 | NORTH VALLEY | 24.5474 | 22.3524 | 1315 | 41.73% | 100% | 1 | 0.21864 | 102.1389 | 3.2416 | 72.3904 | Medium | High | High | 26 | 45 | 22.3317
EL DORADO PH 2102 | SIERRA | 34.253 | 248.1202 | 8500.5 | 99.98% | 100% | 0 | 0.43516 | 102.1389 | 1.6274 | 72.332 | High | High | Low | 27 | 27 | 44.4472
WILLITS 1104 | HUMBOLDT | 84.9199 | 117.6971 | 11210.5 | 89.16% | 56.68% | 1 | 0.79745 | 65.3912 | 1.33 | 69.3522 | High | High | Low | 28 | 21 | 52.146
PIKE CITY 1101 | SIERRA | 34.5379 | 200.5189 | 6925.5 | 100% | 100% | 1 | 0.46619 | 102.1389 | 1.3946 | 66.4074 | High | High | Low | 29 | 25 | 47.616
CHALLENGE 1101 | NORTH VALLEY | 48.3743 | 117.1487 | 5684.5 | 99.69% | 99.37% | 0 | 0.47698 | 102.1389 | 1.3623 | 66.3697 | High | High | Low | 30 | 22 | 48.7187
PARADISE 1101 | NORTH VALLEY | 23.8829 | 180.1078 | 5230.6 | 82.24% | 100% | 0 | 0.34527 | 65.3912 | 2.9331 | 66.2224 | High | High | High | 31 | 44 | 22.5779
BIG BEND 1102 | NORTH VALLEY | 38.1787 | 184.083 | 7027 | 100% | 100% | 0 | 0.35413 | 85.4511 | 2.0415 | 61.7771 | High | High | Medium | 32 | 34 | 30.2604
SILVERADO 2105 | NORTH BAY | 37.4725 | 150.701 | 9686.5 | 58.3% | 94.51% | 1 | 0.38023 | 65.3912 | 2.3865 | 59.3371 | High | High | Medium | 33 | 41 | 24.8635
PUEBLO 2102 | NORTH BAY | 21.5581 | 127.4127 | 12684 | 21.66% | 93.12% | 0 | 0.32308 | 85.4511 | 1.9904 | 54.9503 | High | High | Medium | 34 | 37 | 27.6079
SHADY GLEN 1102 | SIERRA | 39.0599 | 97.1034 | 4076.4 | 93.04% | 34.11% | 0 | 0.39355 | 85.4511 | 1.5463 | 51.9996 | High | High | Low | 35 | 32 | 33.6292
MOLINO 1101 | SONOMA | 33.6923 | 133.9868 | 12117.7 | 37.25% | 24.8% | 0 | 0.43165 | 65.3912 | 1.7461 | 49.2861 | High | High | Medium | 36 | 35 | 28.2264
SHINGLE SPRINGS 1104 | SIERRA | 42.6451 | 204.2501 | 12204.6 | 71.37% | 86.51% | 0 | 0.36466 | 65.3912 | 2.0063 | 47.8425 | High | High | Medium | 37 | 42 | 23.8458
BONNIE NOOK 1102 | SIERRA | 34.3352 | 243.2045 | 8351.4 | 99.99% | 100% | 0 | 0.39869 | 102.1389 | 1.155 | 47.034 | High | High | Low | 38 | 28 | 40.7222
PENRYN 1103 | SIERRA | 67.0371 | 107.5792 | 8477.8 | 85.07% | 0% | 0 | 0.46834 | 47.6367 | 2.0579 | 45.9118 | High | High | Medium | 39 | 46 | 22.3103
DIAMOND SPRINGS 1107 | SIERRA | 53.8326 | 183.5826 | 10826.6 | 91.28% | 63% | 0 | 0.39258 | 65.3912 | 1.7838 | 45.7924 | High | High | Medium | 40 | 39 | 25.6711
RINCON 1103 | SONOMA | 45.4469 | 162.6005 | 7799.7 | 94.74% | 89.85% | 0 | 0.54363 | 47.6367 | 1.7507 | 45.3385 | High | High | Medium | 41 | 38 | 25.8967
FORESTHILL 1102 | SIERRA | 29.7452 | 330.0154 | 9817.1 | 99.99% | 72.96% | 0 | 0.27132 | 102.1389 | 1.6253 | 45.0397 | Medium | High | Low | 42 | 36 | 27.7119
CLARKSVILLE 2104 | SIERRA | 65.9498 | 68.6078 | 5311.9 | 85.18% | 68.08% | 1 | 0.39857 | 47.6367 | 2.2889 | 43.4576 | High | High | Medium | 43 | 51 | 18.9864
TIGER CREEK 0201 | STOCKTON | 3.8998 | 49.9154 | 194.7 | 99.98% | 66.65% | 0 | 0.32439 | 65.3912 | 1.939 | 41.1306 | High | High | Medium | 44 | 48 | 21.2124
HIGHLANDS 1103 | HUMBOLDT | 111.6966 | 53.6769 | 6675.8 | 89.81% | 0% | 1 | 0.52144 | 35.3263 | 2.1747 | 40.059 | High | High | Medium | 45 | 52 | 18.4205
MORAGA 1105 | DIABLO | 9.2376 | 70.5672 | 1398 | 46.63% | 72.19% | 1 | 0.12304 | 102.1389 | 2.9115 | 36.5908 | Medium | High | High | 46 | 62 | 12.5675
SPANISH CREEK 4401 | NORTH VALLEY | 7.9163 | 52.7192 | 418 | 99.84% | 0% | 0 | 0.22342 | 85.4511 | 1.7867 | 34.1108 | Medium | High | Medium | 47 | 50 | 19.0912
CORRAL 1101 | STOCKTON | 121.6695 | 22.4845 | 4245 | 64.44% | 0% | 1 | 0.32273 | 47.6367 | 2.1917 | 33.6945 | High | High | Medium | 48 | 57 | 15.3737
BELL 1107 | SIERRA | 42.044 | 0.27863 | 14 | 83.68% | 0% | 1 | 0.27859 | 65.3912 | 1.8316 | 33.3663 | Medium | High | Medium | 49 | 53 | 18.2174
LAS GALLINAS A 1105 | NORTH BAY | 12.199 | 104.5283 | 2254.3 | 56.56% | 74.01% | 0 | 0.15567 | 65.3912 | 3.2653 | 33.238 | Medium | High | High | 50 | 69 | 10.1793
RACETRACK 1704 | YOSEMITE | 45.5677 | 97.5233 | 4506.3 | 98.62% | 0% | 1 | 0.3278 | 47.6367 | 2.0613 | 32.1874 | High | High | Medium | 51 | 56 | 15.6152
FULTON 1107 | SONOMA | 37.7898 | 9.2877 | 482 | 72.82% | 100% | 1 | 0.33283 | 47.6367 | 1.9961 | 31.647 | High | High | Medium | 52 | 55 | 15.8548
SAN RAMON 2108 | MISSION | 16.5718 | 120.3107 | 2100 | 94.94% | 100% | 0 | 0.21818 | 47.6367 | 2.8147 | 29.254 | Medium | High | High | 53 | 66 | 10.3932
PARADISE 1105 | NORTH VALLEY | 13.5303 | 193.9796 | 3835.5 | 68.43% | 100% | 1 | 0.15371 | 65.3912 | 2.9097 | 29.2471 | Medium | High | High | 54 | 70 | 10.0515
BEN LOMOND 1101 | CENTRAL COAST | 15.4019 | 408.4071 | 6255 | 100% | 100% | 0 | 0.31249 | 26.5534 | 3.5017 | 29.0556 | High | High | High | 55 | 75 | 8.2976
BONNIE NOOK 1101 | SIERRA | 24.4427 | 203.2987 | 4894.7 | 100% | 100% | 0 | 0.27204 | 85.4511 | 1.2213 | 28.3918 | Medium | High | Low | 56 | 43 | 23.2464
PARADISE 1102 | NORTH VALLEY | 15.078 | 209.2721 | 6818 | 46.28% | 100% | 0 | 0.13414 | 65.3912 | 3.0258 | 26.5402 | Medium | High | High | 57 | 73 | 8.7714
RINCON 1101 | SONOMA | 21.5282 | 78.8433 | 2741.8 | 61.91% | 82.79% | 0 | 0.22435 | 65.3912 | 1.7747 | 26.0369 | Medium | High | Medium | 58 | 60 | 14.6708
BRUNSWICK 1110 | SIERRA | 24.5712 | 64.2735 | 2208 | 71.53% | 0% | 0 | 0.2574 | 47.6367 | 2.1175 | 25.9649 | Medium | High | Medium | 59 | 64 | 12.2619
PETALUMA C 1108 | SONOMA | 73.6987 | 44.0843 | 5229.6 | 62.13% | 0% | 0 | 0.29967 | 65.3912 | 1.2912 | 25.3025 | High | High | Low | 60 | 49 | 19.5957
COTTONWOOD 1103 | NORTH VALLEY | 126.1767 | 75.3761 | 12151 | 78.27% | 0% | 1 | 0.57016 | 26.5534 | 1.5299 | 23.1621 | High | High | Low | 61 | 58 | 15.1397
PENNGROVE 1101 | SONOMA | 19.2167 | 0.1925 | 8 | 46.24% | 0% | 0 | 0.21065 | 65.3912 | 1.6185 | 22.2941 | Medium | High | Low | 62 | 61 | 13.7748
BELLEVUE 2103 | SONOMA | 28.6386 | 4.3285 | 306 | 40.51% | 33.51% | 0 | 0.19058 | 65.3912 | 1.6105 | 20.071 | Medium | High | Low | 63 | 63 | 12.4623
ROSSMOOR 1108 | DIABLO | 12.7515 | 167.0344 | 3459.5 | 61.57% | 55.79% | 0 | 0.099586 | 65.3912 | 2.9972 | 19.5179 | Low | High | High | 64 | 81 | 6.512
LAYTONVILLE 1101 | HUMBOLDT | 51.196 | 53.2824 | 4252.7 | 64.14% | 0% | 1 | 0.47695 | 65.3912 | 0.62176 | 19.3917 | High | High | Low | 65 | 33 | 31.1882
BUCKS CREEK 1103 | NORTH VALLEY | 11.1849 | 94.6553 | 1236 | 85.66% | 78.68% | 0 | 0.29586 | 85.4511 | 0.75889 | 19.1861 | Medium | High | Low | 66 | 40 | 25.2817
BELL 1110 | SIERRA | 0.30639 | 0.52971 | 6 | 2.705% | 0% | 0 | 0.10309 | 85.4511 | 2.0427 | 17.994 | Low | High | Medium | 67 | 72 | 8.809
CAMP EVERS 2104 | CENTRAL COAST | 27.8231 | 223.757 | 8211.5 | 75.82% | 98.69% | 0 | 0.49604 | 11.2183 | 3.2209 | 17.9234 | High | High | High | 68 | 85 | 5.5647
LAKEVILLE 1102 | SONOMA | 20.015 | 22.2542 | 1116.7 | 39.89% | 0% | 0 | 0.15735 | 65.3912 | 1.6756 | 17.2413 | Medium | High | Medium | 69 | 68 | 10.2894
WILLOW CREEK 1102 | HUMBOLDT | 9.6275 | 111.4738 | 1072.3 | 100% | 52.31% | 0 | 0.33882 | 65.3912 | 0.75226 | 16.667 | High | High | Low | 70 | 47 | 22.1559
BERKELEY F 1103 | EAST BAY | 1.8512 | 114.7029 | 715.7 | 29.67% | 100% | 0 | 0.07875 | 65.3912 | 3.1071 | 16.0001 | Low | High | High | 71 | 90 | 5.1495
PIKE CITY 1102 | SIERRA | 9.4149 | 129.3375 | 1217.7 | 100% | 100% | 0 | 0.2477 | 65.3912 | 0.96632 | 15.6516 | Medium | High | Low | 72 | 54 | 16.1971
PACIFICA 1101 | PENINSULA | 2.9053 | 0.10906 | 1 | 31.69% | 85.89% | 0 | 0.11762 | 47.6367 | 2.6487 | 14.8406 | Medium | High | High | 73 | 84 | 5.6029
VACA DIXON 1101 | SACRAMENTO | 0.82637 | 34.1483 | 320 | 8.819% | 0% | 0 | 0.098707 | 85.4511 | 1.7286 | 14.5797 | Low | High | Medium | 74 | 74 | 8.4346
CORNING 1101 | NORTH VALLEY | 50.3181 | 28.4447 | 4598 | 31.13% | 0% | 1 | 0.22804 | 35.3263 | 1.75 | 14.0977 | Medium | High | Medium | 75 | 76 | 8.0558
ALLEGHANY 1102 | SIERRA | 18.0939 | 139.6914 | 2490 | 100% | 100% | 1 | 0.22668 | 65.3912 | 0.94709 | 14.0387 | Medium | High | Low | 76 | 59 | 14.823
COTATI 1105 | SONOMA | 37.492 | 0.33385 | 44 | 28.45% | 0% | 0 | 0.15878 | 65.3912 | 1.2994 | 13.4908 | Medium | High | Low | 77 | 67 | 10.3826
VINEYARD 2108 | MISSION | 3.1184 | 96.4724 | 1296 | 23.21% | 100% | 1 | 0.075819 | 65.3912 | 2.5523 | 12.6542 | Low | High | High | 78 | 91 | 4.9579
PANORAMA 1101 | NORTH VALLEY | 11.7268 | 41.5904 | 1624 | 30.03% | 0% | 0 | 0.14741 | 35.3263 | 2.3726 | 12.3554 | Medium | High | Medium | 79 | 89 | 5.2075
GARCIA 0401 | HUMBOLDT | 2.4735 | 195.6161 | 483.7 | 100% | 0% | 0 | 0.18633 | 65.3912 | 1.0043 | 12.2362 | Medium | High | Low | 80 | 65 | 12.1844
PASO ROBLES 1103 | LOS PADRES | 39.5134 | 0.016068 | 1 | 63.49% | 0% | 1 | 0.19775 | 35.3263 | 1.726 | 12.0574 | Medium | High | Medium | 81 | 78 | 6.9856
BRIDGEVILLE 1101 | HUMBOLDT | 22.5401 | 93.278 | 2318.5 | 90.68% | 3.572% | 1 | 0.40628 | 85.4511 | 0.34191 | 11.8701 | High | High | Low | 82 | 31 | 34.7173
PUTAH CREEK 1102 | SACRAMENTO | 26.0826 | 58.6358 | 3017.2 | 50.69% | 0% | 0 | 0.20919 | 47.6367 | 1.1824 | 11.7826 | Medium | High | Low | 83 | 71 | 9.965
TASSAJARA 2108 | DIABLO | 1.2025 | 139.2395 | 2985.1 | 5.609% | 100% | 0 | 0.050229 | 85.4511 | 2.63 | 11.2884 | Low | High | High | 84 | 95 | 4.2922
SANTA ROSA A 1111 | SONOMA | 5.593 | 74.3305 | 1937.5 | 21.46% | 0.05081% | 0 | 0.1018 | 65.3912 | 1.6309 | 10.857 | Low | High | Low | 85 | 80 | 6.657
SONOMA 1106 | SONOMA | 1.1258 | 52.424 | 576.9 | 10.23% | 100% | 0 | 0.094417 | 47.6367 | 2.3971 | 10.7815 | Low | High | High | 86 | 94 | 4.4977
EAST QUINCY 1101 | NORTH VALLEY | 3.3666 | 62.1461 | 1079 | 19.39% | 17.1% | 0 | 0.10361 | 47.6367 | 2.1529 | 10.6262 | Low | High | Medium | 87 | 92 | 4.9357
BUELLTON 1102 | LOS PADRES | 15.6243 | 87.2194 | 2386.2 | 57.11% | 0% | 0 | 0.15557 | 47.6367 | 1.3574 | 10.059 | Medium | High | Low | 88 | 77 | 7.4107
JARVIS 1101 | MISSION | 0.45193 | 32.174 | 452 | 3.217% | 0% | 0 | 0.075561 | 47.6367 | 2.7563 | 9.9213 | Low | High | High | 89 | 102 | 3.5995
PEABODY 2113 | SACRAMENTO | 1.6686 | 4.5925 | 44 | 17.42% | 0% | 0 | 0.1134 | 47.6367 | 1.8105 | 9.7799 | Medium | High | Medium | 90 | 86 | 5.4018
PUTAH CREEK 1103 | SACRAMENTO | 3.6658 | 57.1436 | 2096.9 | 9.99% | 0% | 0 | 0.10677 | 65.3912 | 1.3925 | 9.7223 | Low | High | Low | 91 | 79 | 6.9821
MEADOW LANE 2106 | DIABLO | 0.20712 | 132.7473 | 3117 | 0.8821% | 100% | 0 | 0.03891 | 85.4511 | 2.7735 | 9.2215 | Low | High | High | 92 | 104 | 3.3249
SAN RAMON 2102 | MISSION | 1.535 | 2.1422 | 5 | 65.77% | 0% | 0 | 0.15119 | 19.9979 | 2.9688 | 8.9761 | Medium | High | High | 93 | 107 | 3.0235
RED BLUFF 1104 | NORTH VALLEY | 69.4411 | 32.3911 | 3034.7 | 74.12% | 0% | 0 | 0.32066 | 19.9979 | 1.3797 | 8.8475 | High | High | Low | 94 | 82 | 6.4126
RESEARCH 2102 | DIABLO | 1.2814 | 172.3046 | 3568.6 | 6.187% | 100% | 0 | 0.038888 | 85.4511 | 2.5899 | 8.6062 | Low | High | High | 95 | 105 | 3.323
COTATI 1102 | SONOMA | 15.7671 | 4.0219 | 141 | 44.97% | 0% | 0 | 0.15222 | 35.3263 | 1.5958 | 8.5813 | Medium | High | Low | 96 | 87 | 5.3775
FREMONT 1104 | MISSION | 2.6857 | 58.4301 | 1782.9 | 8.802% | 0% | 0 | 0.057909 | 65.3912 | 2.222 | 8.4141 | Low | High | Medium | 97 | 99 | 3.7867
MOLINO 1104 | SONOMA | 2.046 | 50.0802 | 3069.1 | 3.339% | 0% | 0 | 0.08155 | 65.3912 | 1.5463 | 8.2461 | Low | High | Low | 98 | 88 | 5.3326
UKIAH 1113 | HUMBOLDT | 6.3928 | 0.2519 | 4 | 40.26% | 0% | 0 | 0.17238 | 35.3263 | 1.3023 | 7.9304 | Medium | High | Low | 99 | 83 | 6.0894
SILVERADO 2103 | NORTH BAY | 9.8107 | 404.0574 | 13434.1 | 29.51% | 100% | 0 | 0.07608 | 47.6367 | 2.0797 | 7.5371 | Low | High | Medium | 100 | 101 | 3.6242
FULTON 1104 | SONOMA | 0.51664 | 11.6356 | 111 | 5.416% | 0% | 0 | 0.089226 | 47.6367 | 1.7166 | 7.2964 | Low | High | Medium | 101 | 96 | 4.2504
ROSSMOOR 1102 | DIABLO | 0.0028423 | 80.7015 | 115.5 | 0.1986% | 100% | 0 | 0.036984 | 65.3912 | 2.9669 | 7.1754 | Low | High | High | 102 | 109 | 2.4185
SAN RAMON 2101 | MISSION | 0.57317 | 20.5147 | 22 | 53.45% | 0% | 0 | 0.11568 | 19.9979 | 2.9563 | 6.839 | Medium | High | High | 103 | 110 | 2.3134
WYANDOTTE 1106 | NORTH VALLEY | 1.9508 | 33.0439 | 3091 | 2.086% | 0% | 0 | 0.11761 | 26.5534 | 2.1542 | 6.7275 | Medium | High | Medium | 104 | 106 | 3.123
VALLEY VIEW 1103 | EAST BAY | 0.34789 | 2.2678 | 41 | 1.924% | 100% | 0 | 0.057126 | 35.3263 | 3.2827 | 6.6246 | Low | High | High | 105 | 113 | 2.018
RESERVATION ROAD 1101 | CENTRAL COAST | 25.5742 | 163.2438 | 5215.1 | 80.05% | 0% | 1 | 0.21014 | 19.9979 | 1.5502 | 6.5145 | Medium | High | Low | 106 | 97 | 4.2025
PEABODY 2108 | SACRAMENTO | 0.82253 | 26.141 | 90.5 | 23.76% | 0% | 0 | 0.099538 | 35.3263 | 1.7932 | 6.3054 | Low | High | Medium | 107 | 103 | 3.5163
JAMESON 1102 | SACRAMENTO | 8.3727 | 110.5885 | 2231.1 | 41.5% | 0% | 0 | 0.11003 | 19.9979 | 2.8442 | 6.2585 | Low | High | High | 108 | 111 | 2.2004
MILPITAS 1108 | SAN JOSE | 0.28331 | 52.0143 | 691 | 2.133% | 0% | 0 | 0.047221 | 85.4511 | 1.432 | 5.7784 | Low | High | Low | 109 | 98 | 4.0351
JARVIS 1110 | MISSION | 0.094443 | 35.6649 | 214 | 1.574% | 0% | 0 | 0.048533 | 35.3263 | 3.0938 | 5.3042 | Low | High | High | 110 | 117 | 1.7145
SAN LUIS OBISPO 1108 | LOS PADRES | 1.2137 | 27.6591 | 435 | 7.717% | 0% | 0 | 0.073268 | 26.5534 | 2.3814 | 4.633 | Low | High | Medium | 111 | 114 | 1.9455
SANTA ROSA A 1108 | SONOMA | 0.13621 | 25.5587 | 183 | 1.902% | 0% | 0 | 0.051292 | 47.6367 | 1.6989 | 4.151 | Low | High | Medium | 112 | 108 | 2.4434
SEACLIFF 0402 | CENTRAL COAST | 0.96395 | 343.4682 | 533.2 | 62.09% | 63.7% | 0 | 0.032259 | 47.6367 | 2.6022 | 3.9989 | Low | High | High | 113 | 118 | 1.5367
CLEAR LAKE 1102 | HUMBOLDT | 3.7822 | 75.1062 | 2804 | 10.13% | 0% | 0 | 0.07809 | 26.5534 | 1.8761 | 3.8902 | Low | High | Medium | 114 | 112 | 2.0735
VACAVILLE 1109 | SACRAMENTO | 0.50066 | 60.9601 | 239 | 12.77% | 0% | 0 | 0.054836 | 35.3263 | 1.8589 | 3.6009 | Low | High | Medium | 115 | 115 | 1.9372
CAMP EVERS 2105 | CENTRAL COAST | 88.8213 | 214.3597 | 19560.9 | 97.34% | 98.85% | 1 | 0.99887 | 1 | 3.4754 | 3.4715 | High | Low | High | 116 | 123 | 0.99887
HORSESHOE 1104 | SIERRA | 1.0628 | 302.2247 | 3511.7 | 9.146% | 0% | 0 | 0.032736 | 35.3263 | 2.7724 | 3.2061 | Low | High | High | 117 | 120 | 1.1565
CAMP EVERS 2106 | CENTRAL COAST | 128.2102 | 99.8162 | 13913.2 | 91.98% | 98.66% | 1 | 0.99814 | 1 | 3.0301 | 3.0244 | High | Low | High | 118 | 124 | 0.99814
BIG BASIN 1101 | CENTRAL COAST | 56.1051 | 224.865 | 12617.6 | 99.99% | 100% | 0 | 0.97503 | 1 | 3.0189 | 2.9435 | High | Low | High | 119 | 129 | 0.97503
TASSAJARA 2106 | DIABLO | 0.13696 | 100.7735 | 314 | 4.395% | 0% | 0 | 0.043626 | 19.9979 | 3.279 | 2.8607 | Low | High | High | 120 | 145 | 0.87242
SAN MIGUEL 1105 | LOS PADRES | 0.96596 | 35.4496 | 719 | 4.763% | 0% | 0 | 0.095887 | 19.9979 | 1.399 | 2.6826 | Low | High | Low | 121 | 116 | 1.9175
BIG BASIN 1102 | CENTRAL COAST | 73.4523 | 685.0537 | 53077 | 94.8% | 94.78% | 1 | 0.99803 | 1 | 2.6614 | 2.6562 | High | Low | High | 122 | 125 | 0.99803
GOLDTREE 1105 | LOS PADRES | 7.1045 | 84.8773 | 1221.3 | 49.37% | 0% | 0 | 0.10706 | 11.2183 | 2.1281 | 2.5561 | Low | High | Medium | 123 | 119 | 1.2011
SILVERADO 2104 | NORTH BAY | 121.7013 | 168.4106 | 24366 | 84.12% | 64.08% | 1 | 0.93788 | 1 | 2.6952 | 2.5278 | High | Low | High | 124 | 137 | 0.93788
LOS GATOS 1106 | DE ANZA | 70.6799 | 255.34 | 18225.3 | 99.02% | 99.2% | 1 | 0.94316 | 1 | 2.548 | 2.4032 | High | Low | High | 125 | 136 | 0.94316
HALF MOON BAY 1103 | PENINSULA | 138.142 | 86.2493 | 15111.05 | 78.85% | 1.152% | 1 | 0.9705 | 1 | 2.4043 | 2.3334 | High | Low | High | 126 | 130 | 0.9705
ROB ROY 2104 | CENTRAL COAST | 102.3975 | 30.1005 | 4036.8 | 76.35% | 40.31% | 1 | 0.99347 | 1 | 2.3478 | 2.3325 | High | Low | Medium | 127 | 126 | 0.99347
PINE GROVE 1102 | STOCKTON | 177.6802 | 155.3906 | 27670.22 | 99.78% | 52.09% | 0 | 0.95059 | 1 | 2.448 | 2.3271 | High | Low | High | 128 | 133 | 0.95059
LOS GATOS 1107 | DE ANZA | 94.47 | 201.9318 | 19473.6 | 97.96% | 87.06% | 1 | 0.9298 | 1 | 2.42 | 2.2501 | High | Low | High | 129 | 138 | 0.9298
ROB ROY 2105 | CENTRAL COAST | 42.0766 | 296.2096 | 21276.5 | 58.58% | 71.18% | 1 | 0.84093 | 1 | 2.5914 | 2.1792 | High | Low | High | 130 | 154 | 0.84093
GOLDTREE 1107 | LOS PADRES | 1.1277 | 18.9072 | 69 | 30.9% | 0% | 0 | 0.085536 | 11.2183 | 2.2378 | 2.1473 | Low | High | Medium | 131 | 132 | 0.95957
SAN RAFAEL 1108 | NORTH BAY | 37.3748 | 160.2128 | 7528.8 | 79.53% | 97.7% | 1 | 0.54286 | 1 | 3.8165 | 2.0718 | High | Low | High | 132 | 196 | 0.54286
MONTE RIO 1111 | SONOMA | 58.0584 | 184.273 | 11931.2 | 89.67% | 78.57% | 0 | 0.86945 | 1 | 2.3469 | 2.0405 | High | Low | Medium | 133 | 147 | 0.86945
CLARKSVILLE 2110 | SIERRA | 0.17765 | 63.769 | 448.5 | 2.526% | 0% | 0 | 0.043535 | 19.9979 | 2.3396 | 2.0369 | Low | High | Medium | 134 | 146 | 0.8706
MORAGA 1102 | DIABLO | 3.3475 | 136.8517 | 1274.5 | 35.94% | 35.27% | 0 | 0.061173 | 11.2183 | 2.9081 | 1.9957 | Low | High | High | 135 | 168 | 0.68626
WEST POINT 1102 | STOCKTON | 230.9017 | 86.5887 | 22278.25 | 89.74% | 72% | 1 | 0.96739 | 1 | 2.0586 | 1.9915 | High | Low | Medium | 136 | 131 | 0.96739
ELECTRA 1102 | STOCKTON | 83.9596 | 134.607 | 2625.2 | 100% | 28.82% | 0 | 0.99252 | 1 | 1.9171 | 1.9028 | High | Low | Medium | 137 | 127 | 0.99252
OLEMA 1101 | NORTH BAY | 61.001 | 71.2227 | 8664.6 | 50.14% | 18.76% | 1 | 0.80779 | 1 | 2.3211 | 1.875 | High | Low | Medium | 138 | 156 | 0.80779
BIG RIVER 1101 | HUMBOLDT | 71.4583 | 101.7584 | 8757.6 | 83.03% | 0% | 1 | 0.88115 | 1 | 2.0103 | 1.7714 | High | Low | Medium | 139 | 142 | 0.88115
BEN LOMOND 0401 | CENTRAL COAST | 21.1277 | 328.4372 | 6922.7 | 100% | 100% | 0 | 0.50343 | 1 | 3.4434 | 1.7335 | High | Low | High | 140 | 211 | 0.50343
LAKEWOOD 2110 | DIABLO | 0.42837 | 128.5111 | 2940.5 | 1.872% | 100% | 0 | 0.04951 | 11.2183 | 3.0948 | 1.7189 | Low | High | High | 141 | 194 | 0.55542
BANGOR 1101 | NORTH VALLEY | 197.9775 | 62.6538 | 14347.5 | 86.45% | 0.7535% | 1 | 0.75918 | 1 | 2.2417 | 1.7019 | High | Low | Medium | 142 | 162 | 0.75918
ALTO 1125 | NORTH BAY | 37.0494 | 129.6468 | 5802.2 | 82.78% | 77.44% | 1 | 0.52563 | 1 | 3.2314 | 1.6985 | High | Low | High | 143 | 199 | 0.52563
GREEN VALLEY 2101 | CENTRAL COAST | 43.1017 | 158.6756 | 24887.3 | 27.48% | 83.01% | 1 | 0.85678 | 1 | 1.9816 | 1.6978 | High | Low | Medium | 144 | 150 | 0.85678
BRYANT 0402 | DIABLO | 1.2282 | 150.9373 | 1168.3 | 15.87% | 0% | 0 | 0.037528 | 14.9507 | 2.9149 | 1.6355 | Low | High | High | 145 | 192 | 0.56107
CALISTOGA 1101 | NORTH BAY | 91.75 | 165.8288 | 18630.5 | 81.67% | 85.96% | 1 | 0.84787 | 1 | 1.8867 | 1.5996 | High | Low | Medium | 146 | 152 | 0.84787
CLARKSVILLE 2109 | SIERRA | 5.0217 | 328.5061 | 4024.2 | 40.99% | 37.96% | 0 | 0.044201 | 14.9507 | 2.3528 | 1.5548 | Low | High | Medium | 147 | 170 | 0.66083
BELLEVUE 1102 | SONOMA | 0.13708 | 0.045922 | 2 | 0.3148% | 0% | 0 | 0.056099 | 19.9979 | 1.3772 | 1.5451 | Low | High | Low | 148 | 121 | 1.1219
PARADISE 1103 | NORTH VALLEY | 41.0163 | 140.6142 | 6365.1 | 90.61% | 65.43% | 1 | 0.54801 | 1 | 2.7927 | 1.5304 | High | Low | High | 149 | 195 | 0.54801
WOODACRE 1102 | NORTH BAY | 32.7082 | 184.4969 | 5733 | 100% | 49.48% | 0 | 0.39711 | 1 | 3.8248 | 1.5189 | High | Low | High | 150 | 246 | 0.39711
APPLE HILL 2102 | SIERRA | 336.4685 | 64.7636 | 22557.2 | 96.6% | 31.51% | 1 | 0.98048 | 1 | 1.5121 | 1.4826 | High | Low | Low | 151 | 128 | 0.98048
CURTIS 1702 | YOSEMITE | 111.3399 | 13.2129 | 1563.61 | 94.08% | 22.51% | 1 | 0.51745 | 1 | 2.8567 | 1.4782 | High | Low | High | 152 | 202 | 0.51745
MIRABEL 1102 | SONOMA | 36.4964 | 215.8593 | 12523.9 | 62.9% | 86.71% | 1 | 0.64889 | 1 | 2.2561 | 1.464 | High | Low | Medium | 153 | 172 | 0.64889
PLACERVILLE 2106 | SIERRA | 276.5055 | 0.40168 | 111 | 100% | 68.24% | 1 | 0.858 | 1 | 1.6591 | 1.4235 | High | Low | Low | 154 | 148 | 0.858
WYANDOTTE 1107 | NORTH VALLEY | 100.7594 | 72.3283 | 10326.7 | 70.57% | 2.23% | 1 | 0.52043 | 1 | 2.7345 | 1.4231 | High | Low | High | 155 | 201 | 0.52043
FORT BRAGG A 1102 | HUMBOLDT | 64.6396 | 143.498 | 11604.9 | 79.93% | 0% | 1 | 0.9048 | 1 | 1.5679 | 1.4186 | High | Low | Low | 156 | 141 | 0.9048
SARATOGA 1107 | DE ANZA | 33.2409 | 226.5397 | 10305.7 | 73.07% | 48.48% | 0 | 0.53711 | 1 | 2.6156 | 1.4049 | High | Low | High | 157 | 197 | 0.53711
DIAMOND SPRINGS 1106 | SIERRA | 109.9116 | 247.6294 | 30350.4 | 89.68% | 0% | 0 | 0.87448 | 1 | 1.5783 | 1.3801 | High | Low | Low | 158 | 144 | 0.87448
NEWBURG 1132 | HUMBOLDT | 2.1979 | 0.043554 | 1 | 9.573% | 0% | 0 | 0.074726 | 14.9507 | 1.235 | 1.3797 | Low | High | Low | 159 | 122 | 1.1172
OCEANO 1104 | LOS PADRES | 87.6347 | 97.8791 | 11070.7 | 77.48% | 5.106% | 1 | 0.66048 | 1 | 2.0827 | 1.3756 | High | Low | Medium | 160 | 171 | 0.66048
HALSEY 1101 | SIERRA | 72.6826 | 281.9943 | 20821.7 | 98.44% | 0% | 1 | 0.69793 | 1 | 1.9508 | 1.3615 | High | Low | Medium | 161 | 167 | 0.69793
PUEBLO 2103 | NORTH BAY | 47.1879 | 166.9581 | 13136 | 59.98% | 82.28% | 1 | 0.64259 | 1 | 2.1163 | 1.3599 | High | Low | Medium | 162 | 175 | 0.64259
FORT ROSS 1121 | SONOMA | 93.2788 | 115.3428 | 10761 | 99.98% | 23.24% | 0 | 0.78851 | 1 | 1.6844 | 1.3282 | High | Low | Medium | 163 | 159 | 0.78851
NARROWS 2102 | SIERRA | 95.95 | 97.6526 | 11434.5 | 81.94% | 0% | 0 | 0.59701 | 1 | 2.209 | 1.3188 | High | Low | Medium | 164 | 182 | 0.59701
PAUL SWEET 2106 | CENTRAL COAST | 37.5441 | 251.8505 | 13205.3 | 71.6% | 84.81% | 1 | 0.46936 | 1 | 2.7736 | 1.3018 | High | Low | High | 165 | 226 | 0.46936
CURTIS 1703 | YOSEMITE | 195.8329 | 2.5397 | 510.69 | 97.39% | 8.933% | 1 | 0.62304 | 1 | 2.059 | 1.2828 | High | Low | Medium | 166 | 177 | 0.62304
KANAKA 1101 | NORTH VALLEY | 92.5364 | 7.1724 | 663.5 | 100% | 69.28% | 1 | 0.6185 | 1 | 2.0603 | 1.2743 | High | Low | Medium | 167 | 178 | 0.6185
CURTIS 1704 | YOSEMITE | 75.6221 | 24.9869 | 1911.21 | 98.87% | 32.9% | 0 | 0.51399 | 1 | 2.4706 | 1.2698 | High | Low | High | 168 | 204 | 0.51399
WYANDOTTE 1103 | NORTH VALLEY | 84.2744 | 37.6969 | 3685 | 86.21% | 80.44% | 1 | 0.48799 | 1 | 2.5396 | 1.2393 | High | Low | High | 169 | 218 | 0.48799
KONOCTI 1102 | HUMBOLDT | 119.7343 | 3.8196 | 562 | 81.38% | 49.82% | 1 | 0.5617 | 1 | 2.206 | 1.2391 | High | Low | Medium | 170 | 191 | 0.5617
PINE GROVE 1101 | STOCKTON | 73.0596 | 140.622 | 10247.6 | 100% | 0% | 0 | 0.56237 | 1 | 2.1837 | 1.2281 | High | Low | Medium | 171 | 190 | 0.56237
PINECREST 0401 | YOSEMITE | 1.957 | 323.5331 | 1031.1 | 61.41% | 49.36% | 0 | 0.058551 | 14.9507 | 1.3947 | 1.2209 | Low | High | Low | 172 | 143 | 0.87538
COLUMBIA HILL 1101 | SIERRA | 90.9452 | 2.545 | 230.7 | 100% | 81.67% | 1 | 0.74379 | 1 | 1.6251 | 1.2088 | High | Low | Low | 173 | 164 | 0.74379
GARBERVILLE 1102 | HUMBOLDT | 124.8867 | 8.5849 | 1151.7 | 93.09% | 0% | 1 | 0.9451 | 1 | 1.2368 | 1.1689 | High | Low | Low | 174 | 135 | 0.9451
BIG BEND 1101 | NORTH VALLEY | 56.7162 | 126.4735 | 7308.5 | 98.15% | 73.8% | 1 | 0.48296 | 1 | 2.4179 | 1.1677 | High | Low | High | 175 | 220 | 0.48296
MENLO 1103 | PENINSULA | 39.9636 | 46.9951 | 2660.2 | 70.6% | 0% | 1 | 0.57213 | 1 | 2.0361 | 1.1649 | High | Low | Medium | 176 | 188 | 0.57213
CURTIS 1705 | YOSEMITE | 84.6611 | 15.4976 | 1385.3 | 94.71% | 17.45% | 0 | 0.42065 | 1 | 2.7589 | 1.1605 | High | Low | High | 177 | 241 | 0.42065
MOUNTAIN QUARRIES 2101 | SIERRA | 224.6216 | 0.72682 | 164 | 99.55% | 11.18% | 1 | 0.60078 | 1 | 1.9176 | 1.1521 | High | Low | Medium | 178 | 181 | 0.60078
PARADISE 1104 | NORTH VALLEY | 37.9174 | 166.7696 | 8590 | 73.61% | 96.14% | 1 | 0.38991 | 1 | 2.9513 | 1.1508 | High | Low | High | 179 | 249 | 0.38991
FORT BRAGG A 1101 | HUMBOLDT | 70.4672 | 18.613 | 1514.3 | 86.61% | 0% | 1 | 0.77591 | 1 | 1.4603 | 1.133 | High | Low | Low | 180 | 161 | 0.77591
WISE 1102 | SIERRA | 114.9602 | 105.724 | 12547.7 | 96.86% | 0% | 1 | 0.62726 | 1 | 1.7985 | 1.1281 | High | Low | Medium | 181 | 176 | 0.62726
PERRY 1101 | LOS PADRES | 67.3591 | 69.6209 | 5626.6 | 83.35% | 9.487% | 1 | 0.49166 | 1 | 2.2943 | 1.128 | High | Low | Medium | 182 | 216 | 0.49166
STANISLAUS 1701 | YOSEMITE | 45.3745 | 171.8414 | 7829.23 | 99.59% | 52.72% | 0 | 0.43032 | 1 | 2.5728 | 1.1071 | High | Low | High | 183 | 238 | 0.43032
ELECTRA 1101 | STOCKTON | 83.2829 | 63.2177 | 5412.5 | 97.27% | 0% | 1 | 0.51415 | 1 | 2.1328 | 1.0966 | High | Low | Medium | 184 | 203 | 0.51415
BIG TREES 0402 | CENTRAL COAST | 16.1073 | 434.8182 | 7278.9 | 96.22% | 98.33% | 0 | 0.31612 | 1 | 3.4226 | 1.082 | High | Low | High | 185 | 298 | 0.31612
ELK 1101 | HUMBOLDT | 76.2893 | 43.1063 | 4571.1 | 71.94% | 0% | 1 | 0.80648 | 1 | 1.3373 | 1.0785 | High | Low | Low | 186 | 157 | 0.80648
GRASS VALLEY 1103 | SIERRA | 86.1203 | 94.5478 | 8361.3 | 97.38% | 0% | 0 | 0.52251 | 1 | 2.0518 | 1.0721 | High | Low | Medium | 187 | 200 | 0.52251
MONTICELLO 1101 | NORTH BAY | 109.7815 | 85.5856 | 10807.2 | 86.94% | 0% | 1 | 0.60413 | 1 | 1.7603 | 1.0634 | High | Low | Medium | 188 | 180 | 0.60413
MARTELL 1101 | STOCKTON | 73.5469 | 102.7281 | 8640.4 | 87.44% | 0% | 1 | 0.48855 | 1 | 2.176 | 1.0631 | High | Low | Medium | 189 | 217 | 0.48855
ALTO 1124 | NORTH BAY | 30.5495 | 331.9086 | 11694.3 | 86.71% | 100% | 0 | 0.3069 | 1 | 3.4528 | 1.0597 | High | Low | High | 190 | 304 | 0.3069
OREGON TRAIL 1103 | NORTH VALLEY | 116.3748 | 66.5339 | 7999.7 | 96.79% | 0% | 1 | 0.5573 | 1 | 1.8758 | 1.0454 | High | Low | Medium | 191 | 193 | 0.5573
VOLTA 1102 | NORTH VALLEY | 128.1663 | 157.4847 | 20468.8 | 98.61% | 66.76% | 1 | 0.85728 | 1 | 1.2176 | 1.0438 | High | Low | Low | 192 | 149 | 0.85728
OAKHURST 1103 | YOSEMITE | 128.8237 | 0.19057 | 25 | 98.2% | 69.49% | 1 | 0.64287 | 1 | 1.6217 | 1.0425 | High | Low | Low | 193 | 174 | 0.64287
FRUITLAND 1142 | HUMBOLDT | 59.3604 | 139.7042 | 9479.1 | 87.49% | 0% | 1 | 0.8564 | 1 | 1.2147 | 1.0403 | High | Low | Low | 194 | 151 | 0.8564
DOBBINS 1101 | SIERRA | 80.2916 | 165.4492 | 13557.7 | 97.98% | 35.11% | 0 | 0.58245 | 1 | 1.7818 | 1.0378 | High | Low | Medium | 195 | 184 | 0.58245
LAURELES 1111 | CENTRAL COAST | 105.4438 | 167.2407 | 17867.5 | 98.7% | 5.882% | 1 | 0.75833 | 1 | 1.3268 | 1.0062 | High | Low | Low | 196 | 163 | 0.75833
EMERALD LAKE 0402 | PENINSULA | 7.9738 | 1.2715 | 12 | 84.49% | 0% | 0 | 0.22432 | 1 | 4.4394 | 0.99583 | Medium | Low | High | 197 | 364 | 0.22432
GARBERVILLE 1101 | HUMBOLDT | 84.4121 | 19.9292 | 3227.6 | 52.12% | 0% | 1 | 0.81691 | 1 | 1.2027 | 0.98246 | High | Low | Low | 198 | 155 | 0.81691
COARSEGOLD 2104 | YOSEMITE | 248.3114 | 15.5338 | 4129.1 | 93.42% | 1.219% | 1 | 0.58022 | 1 | 1.6845 | 0.97737 | High | Low | Medium | 199 | 185 | 0.58022
MARIPOSA 2101 | YOSEMITE | 261.2126 | 13.1443 | 3482.59 | 98.59% | 34.76% | 1 | 0.78157 | 1 | 1.2358 | 0.96586 | High | Low | Low | 200 | 160 | 0.78157
OAKLAND X 1104 | EAST BAY | 12.9831 | 115.3827 | 1626.7 | 92.09% | 92.36% | 0 | 0.32976 | 1 | 2.8926 | 0.95388 | High | Low | High | 201 | 287 | 0.32976
WILLITS 1103 | HUMBOLDT | 141.581 | 101.7383 | 15609.56 | 92.28% | 34.63% | 1 | 0.94802 | 1 | 0.99475 | 0.94305 | High | Low | Low | 202 | 134 | 0.94802
STELLING 1110 | DE ANZA | 36.507 | 0.39919 | 20 | 72.87% | 36.18% | 0 | 0.42956 | 1 | 2.1628 | 0.92904 | High | Low | Medium | 203 | 239 | 0.42956
OTTER 1101 | CENTRAL COAST | 24.3091 | 146.8885 | 3957.5 | 90.23% | 61.35% | 1 | 0.49892 | 1 | 1.837 | 0.91651 | High | Low | Medium | 204 | 213 | 0.49892
HIGGINS 1103 | SIERRA | 75.3648 | 0.18705 | 15 | 93.98% | 0% | 1 | 0.46833 | 1 | 1.9391 | 0.90816 | High | Low | Medium | 205 | 227 | 0.46833
STILLWATER 1102 | NORTH VALLEY | 77.8002 | 106.8573 | 8440.1 | 98.5% | 0% | 0 | 0.49291 | 1 | 1.8073 | 0.89082 | High | Low | Medium | 206 | 215 | 0.49291
VIEJO 2201 | CENTRAL COAST | 15.761 | 271.832 | 5043 | 84.96% | 0% | 1 | 0.31308 | 1 | 2.8441 | 0.89045 | High | Low | High | 207 | 301 | 0.31308
RACETRACK 1703 | YOSEMITE | 56.2669 | 0.38757 | 24 | 90.87% | 2.511% | 1 | 0.37971 | 1 | 2.3259 | 0.88318 | High | Low | Medium | 208 | 256 | 0.37971
KESWICK 1101 | NORTH VALLEY | 50.8481 | 20.8645 | 1092 | 97.15% | 93.98% | 0 | 0.37921 | 1 | 2.294 | 0.86992 | High | Low | Medium | 209 | 257 | 0.37921
AUBERRY 1101 | FRESNO | 243.3723 | 57.7119 | 14182.11 | 99.04% | 14.06% | 1 | 0.84142 | 1 | 1.032 | 0.86836 | High | Low | Low | 210 | 153 | 0.84142
COARSEGOLD 2102 | YOSEMITE | 69.5656 | 83.9889 | 5882.5 | 99.32% | 79.94% | 0 | 0.57582 | 1 | 1.5055 | 0.86691 | High | Low | Low | 211 | 187 | 0.57582
FROGTOWN 1701 | STOCKTON | 70.5021 | 3.62 | 260.4 | 98.01% | 11.51% | 0 | 0.35892 | 1 | 2.4075 | 0.86409 | High | Low | High | 212 | 270 | 0.35892
CLARK ROAD 1102 | NORTH VALLEY | 117.7302 | 0.21135 | 29 | 85.8% | 28.19% | 1 | 0.37067 | 1 | 2.2993 | 0.85229 | High | Low | Medium | 213 | 260 | 0.37067
DUNBAR 1102 | SONOMA | 48.6409 | 0.94499 | 59 | 77.91% | 12.82% | 1 | 0.36183 | 1 | 2.3412 | 0.84711 | High | Low | Medium | 214 | 266 | 0.36183
ATASCADERO 1101 | LOS PADRES | 48.0205 | 175.2943 | 11084.4 | 75.94% | 30.41% | 1 | 0.4038 | 1 | 2.0754 | 0.83804 | High | Low | Medium | 215 | 244 | 0.4038
WILLOW CREEK 1103 | HUMBOLDT | 84.7815 | 171.8351 | 14798.7 | 98.44% | 0.5494% | 1 | 0.90591 | 1 | 0.92024 | 0.83365 | High | Low | Low | 216 | 140 | 0.90591
HALF MOON BAY 1101 | PENINSULA | 30.1489 | 94.6023 | 4633.8 | 61.55% | 62.01% | 1 | 0.28848 | 1 | 2.889 | 0.83344 | Medium | Low | High | 217 | 315 | 0.28848
SAN RAFAEL 1107 | NORTH BAY | 20.6975 | 176.315 | 4719.9 | 77.32% | 89.65% | 0 | 0.22296 | 1 | 3.7235 | 0.83019 | Medium | Low | High | 218 | 367 | 0.22296
LUCERNE 1106 | HUMBOLDT | 35.3522 | 69.4187 | 3263.9 | 75.19% | 0% | 1 | 0.33667 | 1 | 2.4545 | 0.82635 | High | Low | High | 219 | 282 | 0.33667
MORGAN HILL 2111 | SAN JOSE | 51.2335 | 89.7023 | 6563.3 | 70.02% | 29.88% | 1 | 0.44389 | 1 | 1.8491 | 0.82077 | High | Low | Medium | 220 | 234 | 0.44389
CLAYTON 2212 | DIABLO | 47.4011 | 1.4599 | 84 | 82.38% | 50.62% | 0 | 0.33511 | 1 | 2.4353 | 0.81609 | High | Low | High | 221 | 285 | 0.33511
HIGGINS 1109 | SIERRA | 140.5007 | 11.1731 | 1582.3 | 99.21% | 0% | 1 | 0.47196 | 1 | 1.7034 | 0.80392 | High | Low | Medium | 222 | 225 | 0.47196
HIGGINS 1110 | SIERRA | 51.0959 | 357.0037 | 20576.8 | 88.65% | 0% | 0 | 0.45253 | 1 | 1.7562 | 0.79475 | High | Low | Medium | 223 | 232 | 0.45253
HALSEY 1102 | SIERRA | 57.8088 | 0.48483 | 33 | 84.93% | 0% | 1 | 0.43624 | 1 | 1.8153 | 0.79189 | High | Low | Medium | 224 | 235 | 0.43624
OAKLAND X 1106 | EAST BAY | 16.5816 | 141.7435 | 3332.9 | 70.52% | 43.14% | 0 | 0.28371 | 1 | 2.791 | 0.79183 | Medium | Low | High | 225 | 318 | 0.28371
STILLWATER 1101 | NORTH VALLEY | 34.9345 | 118.2002 | 4354.2 | 94.83% | 0% | 0 | 0.40123 | 1 | 1.9609 | 0.78677 | High | Low | Medium | 226 | 245 | 0.40123
CASTRO VALLEY 1108 | MISSION | 22.9915 | 6.5541 | 168 | 89.7% | 69.23% | 0 | 0.28196 | 1 | 2.7723 | 0.78169 | Medium | Low | High | 227 | 320 | 0.28196
OAKLAND K 1102 | EAST BAY | 15.6371 | 153.4327 | 2398 | 100% | 100% | 1 | 0.27319 | 1 | 2.8557 | 0.78016 | Medium | Low | High | 228 | 326 | 0.27319
GIRVAN 1101 | NORTH VALLEY | 105.6311 | 61.117 | 6709.25 | 96.22% | 40.56% | 0 | 0.47263 | 1 | 1.6353 | 0.77289 | High | Low | Low | 229 | 224 | 0.47263
SHINGLE SPRINGS 2105 | SIERRA | 31.7746 | 67.1179 | 2235.2 | 95.41% | 85.39% | 0 | 0.33572 | 1 | 2.293 | 0.76981 | High | Low | Medium | 230 | 283 | 0.33572
TEMPLETON 2110 | LOS PADRES | 131.8393 | 37.268 | 6618 | 74.24% | 24.45% | 1 | 0.48709 | 1 | 1.5652 | 0.76238 | High | Low | Low | 231 | 219 | 0.48709
BEAR VALLEY 2105 | YOSEMITE | 133.2806 | 5.2436 | 697.9 | 100% | 9.068% | 1 | 0.56239 | 1 | 1.351 | 0.75981 | High | Low | Low | 232 | 189 | 0.56239
DESCHUTES 1101 | NORTH VALLEY | 109.6858 | 74.8939 | 9783.9 | 83.96% | 5.359% | 1 | 0.49693 | 1 | 1.5211 | 0.75589 | High | Low | Low | 233 | 214 | 0.49693
VOLTA 1101 | NORTH VALLEY | 153.0474 | 52.4817 | 8055.6 | 99.71% | 6.239% | 0 | 0.72021 | 1 | 1.0395 | 0.74866 | High | Low | Low | 234 | 165 | 0.72021
BIG MEADOWS 2101 | NORTH VALLEY | 57.1862 | 64.6614 | 5021 | 73.65% | 0% | 0 | 0.39165 | 1 | 1.9107 | 0.74835 | High | Low | Medium | 235 | 247 | 0.39165
NARROWS 2101 | SIERRA | 61.1189 | 1.0306 | 63 | 99.99% | 0% | 0 | 0.38331 | 1 | 1.9498 | 0.74739 | High | Low | Medium | 236 | 253 | 0.38331
SPRUCE 0401 | EAST BAY | 4.123 | 93.7879 | 386.5 | 100% | 23.86% | 0 | 0.18844 | 1 | 3.9252 | 0.73968 | Medium | Low | High | 237 | 406 | 0.18844
EL CERRITO G 1105 | EAST BAY | 18.498 | 89.1521 | 2163 | 76.24% | 31.71% | 0 | 0.20445 | 1 | 3.6127 | 0.73862 | Medium | Low | High | 238 | 385 | 0.20445
WEIMAR 1101 | SIERRA | 74.3116 | 6.8492 | 509 | 100% | 0% | 0 | 0.44451 | 1 | 1.6561 | 0.73613 | High | Low | Low | 239 | 233 | 0.44451
SAN LUIS OBISPO 1107 | LOS PADRES | 47.5671 | 128.564 | 6830.9 | 89.53% | 58.19% | 0 | 0.34103 | 1 | 2.1508 | 0.73348 | High | Low | Medium | 240 | 278 | 0.34103
ATASCADERO 1103 | LOS PADRES | 93.8432 | 106.8884 | 14248.6 | 70.4% | 41.58% | 0 | 0.50034 | 1 | 1.4655 | 0.73326 | High | Low | Low | 241 | 212 | 0.50034
OREGON TRAIL 1102 | NORTH VALLEY | 43.9113 | 52.4522 | 2580.5 | 89.26% | 0% | 0 | 0.34709 | 1 | 2.11 | 0.73237 | High | Low | Medium | 242 | 275 | 0.34709
GUALALA 1112 | HUMBOLDT | 46.2029 | 5.6547 | 265 | 98.59% | 0% | 1 | 0.50419 | 1 | 1.452 | 0.73207 | High | Low | Low | 243 | 209 | 0.50419
GUALALA 1111 | HUMBOLDT | 35.7279 | 5.0047 | 188.5 | 94.86% | 0% | 0 | 0.51384 | 1 | 1.4212 | 0.73027 | High | Low | Low | 244 | 205 | 0.51384
HOOPA 1101 | HUMBOLDT | 103.3689 | 45.8592 | 6148.1 | 77.1% | 2.741% | 1 | 0.92115 | 1 | 0.7914 | 0.729 | High | Low | Low | 245 | 139 | 0.92115
BOLINAS 1101 | NORTH BAY | 36.2161 | 152.1348 | 7849 | 70.2% | 79.57% | 1 | 0.24155 | 1 | 3.0084 | 0.72668 | Medium | Low | High | 246 | 352 | 0.24155
HAMILTON BRANCH 1101 | NORTH VALLEY | 26.7473 | 33.2133 | 1140 | 77.93% | 0% | 0 | 0.29319 | 1 | 2.4741 | 0.72539 | Medium | Low | High | 247 | 311 | 0.29319
SAND CREEK 1103 | FRESNO | 149.2192 | 22.7349 | 3443.9 | 98.51% | 0% | 0 | 0.50802 | 1 | 1.4193 | 0.72104 | High | Low | Low | 248 | 208 | 0.50802
TEMPLETON 2111 | LOS PADRES | 45.7387 | 252.6481 | 16081.1 | 71.86% | 0.6756% | 0 | 0.43041 | 1 | 1.6439 | 0.70754 | High | Low | Low | 249 | 237 | 0.43041
ANNAPOLIS 1101 | HUMBOLDT | 51.2424 | 153.2835 | 7851.9 | 100% | 0% | 0 | 0.69873 | 1 | 1.0113 | 0.7066 | High | Low | Low | 250 | 166 | 0.69873
SANTA ROSA A 1104 | SONOMA | 44.3006 | 126.4689 | 7084.8 | 79.08% | 85.89% | 0 | 0.38767 | 1 | 1.8117 | 0.70235 | High | Low | Medium | 251 | 250 | 0.38767
PHILO 1102 | HUMBOLDT | 87.2659 | 0.078916 | 8 | 86.08% | 0% | 1 | 0.6461 | 1 | 1.0843 | 0.70058 | High | Low | Low | 252 | 173 | 0.6461
ALHAMBRA 1105 | DIABLO | 37.4334 | 94.8612 | 4257 | 83.42% | 1.365% | 1 | 0.27084 | 1 | 2.579 | 0.69848 | Medium | Low | High | 253 | 327 | 0.27084
SOBRANTE 1102 | DIABLO | 27.4867 | 152.1974 | 4215 | 99.25% | 6.682% | 0 | 0.2569 | 1 | 2.6964 | 0.6927 | Medium | Low | High | 254 | 338 | 0.2569
DEL MONTE 2104 | CENTRAL COAST | 60.5977 | 162.8902 | 12940 | 76.28% | 0% | 0 | 0.38584 | 1 | 1.7925 | 0.69161 | High | Low | Medium | 255 | 252 | 0.38584
OLETA 1101 | STOCKTON | 89.0724 | 16.341 | 1902.7 | 76.5% | 6.991% | 0 | 0.30681 | 1 | 2.2468 | 0.68934 | High | Low | Medium | 256 | 305 | 0.30681
OLETA 1102 | STOCKTON | 58.6793 | 93.0145 | 9270.4 | 58.88% | 1.085% | 0 | 0.33146 | 1 | 2.0749 | 0.68774 | High | Low | Medium | 257 | 286 | 0.33146
CORRAL 1102 | STOCKTON | 49.8209 | 0.031174 | 2 | 77.66% | 0% | 1 | 0.28896 | 1 | 2.3748 | 0.68624 | Medium | Low | Medium | 258 | 313 | 0.28896
DESCHUTES 1104 | NORTH VALLEY | 80.0303 | 55.7135 | 7294.1 | 61.13% | 0% | 1 | 0.36212 | 1 | 1.8914 | 0.68492 | High | Low | Medium | 259 | 265 | 0.36212
PEORIA 1701 | YOSEMITE | 80.3858 | 2.7552 | 234 | 94.65% | 0% | 1 | 0.33799 | 1 | 2.0046 | 0.67751 | High | Low | Medium | 260 | 281 | 0.33799
PLACERVILLE 1112 | SIERRA | 27.7534 | 0.6342 | 19 | 92.64% | 0.05594% | 1 | 0.36226 | 1 | 1.862 | 0.67452 | High | Low | Medium | 261 | 264 | 0.36226
FELTON 0401 | CENTRAL COAST | 2.2987 | 63.2591 | 162.5 | 89.49% | 100% | 0 | 0.19109 | 1 | 3.5174 | 0.67216 | Medium | Low | High | 262 | 403 | 0.19109
WEIMAR 1102 | SIERRA | 23.0263 | 2.3451 | 54 | 100% | 0% | 0 | 0.3916 | 1 | 1.7125 | 0.67062 | High | Low | Medium | 263 | 248 | 0.3916
POINT ARENA 1101 | HUMBOLDT | 43.137 | 151.6844 | 10042.9 | 65.15% | 0% | 0 | 0.59484 | 1 | 1.0925 | 0.64989 | High | Low | Low | 264 | 183 | 0.59484
GIRVAN 1102 | NORTH VALLEY | 44.1977 | 51.5354 | 3919.7 | 58.11% | 74.49% | 1 | 0.3243 | 1 | 2.0036 | 0.64977 | High | Low | Medium | 265 | 289 | 0.3243
GANSNER 1101 | NORTH VALLEY | 38.7574 | 38.6947 | 1867 | 80.33% | 1.24% | 1 | 0.35862 | 1 | 1.8076 | 0.64822 | High | Low | Medium | 266 | 271 | 0.35862
MIDDLETOWN 1102 | HUMBOLDT | 39.5462 | 48.716 | 2738.7 | 70.34% | 0.6611% | 0 | 0.27646 | 1 | 2.3228 | 0.64216 | Medium | Low | Medium | 267 | 322 | 0.27646
OTTER 1102 | CENTRAL COAST | 53.8017 | 139.1766 | 7616.4 | 98.31% | 6.912% | 1 | 0.47954 | 1 | 1.332 | 0.63873 | High | Low | Low | 268 | 221 | 0.47954
WOODSIDE 1104 | PENINSULA | 13.9759 | 265.3381 | 9679.4 | 38.31% | 28.63% | 0 | 0.16337 | 1 | 3.8964 | 0.63657 | Medium | Low | High | 269 | 432 | 0.16337
WYANDOTTE 1109 | NORTH VALLEY | 52.4768 | 57.8365 | 7001.3 | 43.35% | 0% | 0 | 0.25504 | 1 | 2.495 | 0.63633 | Medium | Low | High | 270 | 342 | 0.25504
ANTLER 1101 | NORTH VALLEY | 60.0715 | 11.1936 | 704 | 95.51% | 6.842% | 1 | 0.46349 | 1 | 1.3699 | 0.63494 | High | Low | Low | 271 | 229 | 0.46349
SHADY GLEN 1101 | SIERRA | 41.667 | 138.676 | 6500.3 | 88.89% | 1.898% | 0 | 0.35351 | 1 | 1.7857 | 0.63127 | High | Low | Medium | 272 | 273 | 0.35351
OREGON TRAIL 1104 | NORTH VALLEY | 45.1213 | 128.9869 | 7087.6 | 82.12% | 0% | 1 | 0.3403 | 1 | 1.8465 | 0.62838 | High | Low | Medium | 273 | 279 | 0.3403
PEORIA 1705 | YOSEMITE | 59.0992 | 0.069953 | 5 | 82.68% | 0% | 1 | 0.29754 | 1 | 2.1069 | 0.62688 | High | Low | Medium | 274 | 309 | 0.29754
MARIPOSA 2102 | YOSEMITE | 245.1385 | 6.3765 | 1661.56 | 94.08% | 22.38% | 1 | 0.50363 | 1 | 1.2175 | 0.61319 | High | Low | Low | 275 | 210 | 0.50363
EMERALD LAKE 0401 | PENINSULA | 15.5314 | 136.1011 | 2877.3 | 73.47% | 27.29% | 0 | 0.15761 | 1 | 3.8666 | 0.60944 | Medium | Low | High | 276 | 439 | 0.15761
OCEANO 1102 | LOS PADRES | 36.4985 | 170.6492 | 9154 | 68.04% | 0% | 1 | 0.30224 | 1 | 2.0104 | 0.60762 | High | Low | Medium | 277 | 307 | 0.30224
PLACERVILLE 1110 | SIERRA | 34.3071 | 3.7768 | 132 | 98.16% | 4.685% | 1 | 0.34903 | 1 | 1.7162 | 0.59902 | High | Low | Medium | 278 | 274 | 0.34903
NORTH BRANCH 1101 | STOCKTON | 59.7793 | 24.8834 | 2229.9 | 66.71% | 0% | 0 | 0.25616 | 1 | 2.3237 | 0.59524 | Medium | Low | Medium | 279 | 340 | 0.25616
CALISTOGA 1102 | NORTH BAY | 23.8756 | 172.9752 | 7974 | 51.79% | 92.34% | 1 | 0.2553 | 1 | 2.3058 | 0.58866 | Medium | Low | Medium | 280 | 341 | 0.2553
DUNBAR 1103 | SONOMA | 30.1397 | 7.1433 | 388 | 55.49% | 92.61% | 0 | 0.23869 | 1 | 2.4649 | 0.58835 | Medium | Low | High | 281 | 357 | 0.23869
OILFIELDS 1103 | CENTRAL COAST | 115.2449 | 27.8747 | 4007.6 | 80.16% | 0% | 1 | 0.36659 | 1 | 1.5686 | 0.57502 | High | Low | Low | 282 | 261 | 0.36659
CLAYTON 2213 | DIABLO | 3.8789 | 30.8603 | 191.3 | 62.57% | 0% | 0 | 0.2147 | 1 | 2.6752 | 0.57436 | Medium | Low | High | 283 | 375 | 0.2147
NORTH DUBLIN 2103 | MISSION | 18.9008 | 73.7274 | 1635 | 85.23% | 0.2897% | 0 | 0.20907 | 1 | 2.7439 | 0.57368 | Medium | Low | High | 284 | 380 | 0.20907
MENLO 1102 | PENINSULA | 27.048 | 142.3143 | 9172.5 | 41.97% | 0.9515% | 0 | 0.24042 | 1 | 2.3772 | 0.57153 | Medium | Low | Medium | 285 | 353 | 0.24042
FORT SEWARD 1121 | HUMBOLDT | 38.0083 | 88.0582 | 4240.9 | 78.92% | 0% | 0 | 0.51133 | 1 | 1.1175 | 0.57139 | High | Low | Low | 286 | 207 | 0.51133
BUCKS CREEK 1101 | NORTH VALLEY | 20.005 | 20.9987 | 420 | 100% | 23.08% | 0 | 0.27046 | 1 | 2.0923 | 0.56587 | Medium | Low | Medium | 287 | 328 | 0.27046
SAN JOAQUIN #2 1103 | YOSEMITE | 82.7368 | 75.5396 | 6261.9 | 99.81% | 11.29% | 0 | 0.45754 | 1 | 1.2364 | 0.56572 | High | Low | Low | 288 | 230 | 0.45754
NOTRE DAME 1104 | NORTH VALLEY | 27.4274 | 59.5612 | 2333 | 70.02% | 63.41% | 1 | 0.22274 | 1 | 2.5324 | 0.56407 | Medium | Low | High | 289 | 368 | 0.22274
OAK 0401 | EAST BAY | 4.3198 | 91.1427 | 493 | 79.86% | 0% | 0 | 0.13597 | 1 | 4.1407 | 0.563 | Medium | Low | High | 290 | 460 | 0.13597
MORAGA 1104 | DIABLO | 16.8835 | 142.8466 | 3110 | 77.55% | 2.528% | 0 | 0.19957 | 1 | 2.8198 | 0.56276 | Medium | Low | High | 291 | 393 | 0.19957
REDBUD 1101 | HUMBOLDT | 47.7517 | 2.8354 | 199.5 | 67.87% | 51.84% | 0 | 0.2763 | 1 | 2.0254 | 0.55961 | Medium | Low | Medium | 292 | 323 | 0.2763
JESSUP 1101 | NORTH VALLEY | 65.0048 | 68.0599 | 5453 | 81.13% | 0.4339% | 1 | 0.36291 | 1 | 1.5369 | 0.55775 | High | Low | Low | 293 | 262 | 0.36291
OAKLAND K 1104 | EAST BAY | 15.128 | 222.4716 | 3360.9 | 100% | 68.04% | 0 | 0.1901 | 1 | 2.8976 | 0.55083 | Medium | Low | High | 294 | 404 | 0.1901
APPLE HILL 1103 | SIERRA | 58.8848 | 16.9136 | 1213.13 | 82.1% | 28.25% | 1 | 0.35946 | 1 | 1.5186 | 0.54587 | High | Low | Low | 295 | 268 | 0.35946
SARATOGA 1105 | DE ANZA | 9.8848 | 0.84274 | 14 | 59.5% | 0% | 0 | 0.20932 | 1 | 2.5772 | 0.53948 | Medium | Low | High | 296 | 379 | 0.20932
CABRILLO 1103 | LOS PADRES | 53.8552 | 28.4006 | 2761.5 | 55.39% | 0% | 1 | 0.21429 | 1 | 2.5143 | 0.5388 | Medium | Low | High | 297 | 377 | 0.21429
GEYSERVILLE 1101 | SONOMA | 69.1228 | 71.1042 | 9890.2 | 49.69% | 0% | 1 | 0.38011 | 1 | 1.4138 | 0.53738 | High | Low | Low | 298 | 255 | 0.38011
EDES 1112 | EAST BAY | 15.8364 | 103.0601 | 1771.5 | 92.13% | 4.695% | 0 | 0.22246 | 1 | 2.4124 | 0.53666 | Medium | Low | High | 299 | 369 | 0.22246
DUNBAR 1101 | SONOMA | 40.6225 | 4.3182 | 280 | 62.65% | 58.74% | 0 | 0.26425 | 1 | 2.0305 | 0.53655 | Medium | Low | Medium | 300 | 333 | 0.26425
NORTH DUBLIN 2101 | MISSION | 3.6193 | 9.24 | 40 | 83.61% | 0% | 0 | 0.19317 | 1 | 2.7631 | 0.53375 | Medium | Low | High | 301 | 401 | 0.19317
SONOMA 1103 | SONOMA | 13.7402 | 0.07711 | 2 | 52.98% | 100% | 0 | 0.24035 | 1 | 2.2177 | 0.53302 | Medium | Low | Medium | 302 | 354 | 0.24035
ARCATA 1122 | HUMBOLDT | 20.5455 | 163.2894 | 11115.5 | 30.18% | 0% | 1 | 0.2388 | 1 | 2.2303 | 0.5326 | Medium | Low | Medium | 303 | 355 | 0.2388
DUNLAP 1103 | FRESNO | 70.8013 | 75.8838 | 5398.1 | 99.53% | 0% | 0 | 0.53449 | 1 | 0.99361 | 0.53107 | High | Low | Low | 304 | 198 | 0.53449
SAN LUIS OBISPO 1104 | LOS PADRES | 50.6677 | 83.4369 | 7050 | 59.97% | 44.06% | 1 | 0.26401 | 1 | 2.0087 | 0.53031 | Medium | Low | Medium | 305 | 334 | 0.26401
CAYETANO 2109 | MISSION | 35.4993 | 13.1584 | 659 | 70.88% | 35.99% | 1 | 0.22211 | 1 | 2.3856 | 0.52985 | Medium | Low | Medium | 306 | 370 | 0.22211
DIAMOND SPRINGS 1103 | SIERRA | 33.9542 | 144.2323 | 7367.5 | 66.47% | 27.9% | 1 | 0.28798 | 1 | 1.8342 | 0.5282 | Medium | Low | Medium | 307 | 316 | 0.28798
FRENCH GULCH 1102 | NORTH VALLEY | 22.3415 | 79.3501 | 1770 | 100% | 13.78% | 0 | 0.32691 | 1 | 1.6111 | 0.5267 | High | Low | Low | 308 | 288 | 0.32691
WILLOW CREEK 1101 | HUMBOLDT | 47.0234 | 171.5062 | 9921.6 | 81.29% | 61.34% | 1 | 0.80386 | 1 | 0.65498 | 0.52651 | High | Low | Low | 309 | 158 | 0.80386
VIEJO 2202 | CENTRAL COAST | 14.2864 | 4.3971 | 206 | 30.49% | 0% | 1 | 0.19509 | 1 | 2.695 | 0.52576 | Medium | Low | High | 310 | 400 | 0.19509
FRENCH GULCH 1101 | NORTH VALLEY | 18.8732 | 86.0309 | 1622.5 | 100% | 0% | 0 | 0.33821 | 1 | 1.5534 | 0.52539 | High | Low | Low | 311 | 280 | 0.33821
PHILO 1101 | HUMBOLDT | 73.7188 | 0.24667 | 23 | 79.06% | 0% | 1 | 0.47445 | 1 | 1.1048 | 0.5242 | High | Low | Low | 312 | 222 | 0.47445
CLARKSVILLE 2103 | SIERRA | 33.626 | 35.6071 | 1778.5 | 67.32% | 59.03% | 1 | 0.27558 | 1 | 1.8952 | 0.52227 | Medium | Low | Medium | 313 | 324 | 0.27558
WALDO 0402 | EAST BAY | 3.0716 | 42.0757 | 216 | 59.83% | 0% | 0 | 0.13537 | 1 | 3.8554 | 0.5219 | Medium | Low | High | 314 | 461 | 0.13537
BROWNS VALLEY 1101 | SIERRA | 37.7491 | 47.3498 | 3021.8 | 59.15% | 0% | 1 | 0.26976 | 1 | 1.9284 | 0.5202 | Medium | Low | Medium | 315 | 330 | 0.26976
SAN JOAQUIN #3 1103 | YOSEMITE | 54.5173 | 108.2787 | 5905.4 | 99.96% | 58.36% | 0 | 0.46504 | 1 | 1.1123 | 0.51727 | High | Low | Low | 316 | 228 | 0.46504
CURTIS 1701 | YOSEMITE | 13.4152 | 1.2008 | 24.9 | 64.69% | 0% | 0 | 0.20009 | 1 | 2.5773 | 0.51568 | Medium | Low | High | 317 | 390 | 0.20009
HATTON 1102 | CENTRAL COAST | 10.7188 | 3.349 | 75 | 47.86% | 0% | 0 | 0.23467 | 1 | 2.1903 | 0.51402 | Medium | Low | Medium | 318 | 360 | 0.23467
CLAY 1101 | STOCKTON | 26.5733 | 64.6332 | 2666.8 | 64.4% | 0% | 0 | 0.23659 | 1 | 2.1529 | 0.50936 | Medium | Low | Medium | 319 | 358 | 0.23659
AUBERRY 1102 | FRESNO | 127.9128 | 35.9165 | 4605.1 | 99.76% | 0% | 1 | 0.45711 | 1 | 1.1132 | 0.50884 | High | Low | Low | 320 | 231 | 0.45711
LOS GATOS 1108 | DE ANZA | 4.2689 | 49.7215 | 303.5 | 69.94% | 12.91% | 0 | 0.17492 | 1 | 2.9083 | 0.50871 | Medium | Low | High | 321 | 421 | 0.17492
CASTRO VALLEY 1109 | MISSION | 5.7287 | 0.12153 | 1 | 69.62% | 49.57% | 0 | 0.18308 | 1 | 2.7674 | 0.50666 | Medium | Low | High | 322 | 414 | 0.18308
BELL 1108 | SIERRA | 66.6823 | 0.074134 | 6 | 82.39% | 0% | 0 | 0.28608 | 1 | 1.7453 | 0.49931 | Medium | Low | Medium | 323 | 317 | 0.28608
WYANDOTTE 1105 | NORTH VALLEY | 20.9182 | 45.9165 | 1101 | 87.24% | 0.3284% | 1 | 0.19533 | 1 | 2.5559 | 0.49925 | Medium | Low | High | 324 | 399 | 0.19533
LOW GAP 1101 | HUMBOLDT | 71.107 | 2.249 | 164 | 97.51% | 0% | 0 | 0.57857 | 1 | 0.86126 | 0.4983 | High | Low | Low | 325 | 186 | 0.57857
MARTELL 1103 | STOCKTON | 20.372 | 30.2173 | 893.9 | 68.87% | 0% | 0 | 0.22697 | 1 | 2.1763 | 0.49395 | Medium | Low | Medium | 326 | 362 | 0.22697
LAYTONVILLE 1102 | HUMBOLDT | 111.1176 | 22.1416 | 2687.9 | 91.53% | 2.684% | 1 | 0.66913 | 1 | 0.73466 | 0.49159 | High | Low | Low | 327 | 169 | 0.66913
JESSUP 1102 | NORTH VALLEY | 51.0333 | 64.1412 | 5572 | 58.75% | 0% | 0 | 0.32267 | 1 | 1.521 | 0.49077 | High | Low | Low | 328 | 292 | 0.32267
FORT BRAGG A 1104 | HUMBOLDT | 25.9146 | 98.8899 | 3769 | 67.99% | 0% | 0 | 0.31064 | 1 | 1.5649 | 0.48612 | High | Low | Low | 329 | 302 | 0.31064
RIDGE 0401 | EAST BAY | 2.662 | 150.4115 | 400.2 | 100% | 0% | 0 | 0.14736 | 1 | 3.2957 | 0.48566 | Medium | Low | High | 330 | 449 | 0.14736
HIGHLANDS 1102 | HUMBOLDT | 35.815 | 38.7995 | 2335.5 | 59.5% | 23.07% | 0 | 0.20558 | 1 | 2.3412 | 0.48129 | Medium | Low | Medium | 331 | 384 | 0.20558
WHITMORE 1101 | NORTH VALLEY | 92.5696 | 60.8238 | 5627.04 | 100% | 35.14% | 0 | 0.51164 | 1 | 0.93924 | 0.48055 | High | Low | Low | 332 | 206 | 0.51164
BELL 1109 | SIERRA | 13.433 | 0.4486 | 8 | 75.33% | 0% | 0 | 0.25005 | 1 | 1.9218 | 0.48055 | Medium | Low | Medium | 333 | 344 | 0.25005
RALSTON 1101 | PENINSULA | 8.6411 | 0.69774 | 10 | 60.29% | 0% | 0 | 0.1857 | 1 | 2.5532 | 0.47412 | Medium | Low | High | 334 | 408 | 0.1857
SAN RAFAEL 1109 | NORTH BAY | 10.8025 | 134.9188 | 3525.9 | 41.34% | 0% | 0 | 0.1313 | 1 | 3.5715 | 0.46894 | Medium | Low | High | 335 | 465 | 0.1313
CENTERVILLE 1101 | NORTH VALLEY | 36.3928 | 0 | 5396.6 | 0% | 96.65% | 1 | 0.17029 | 1 | 2.7454 | 0.46751 | Medium | Low | High | 336 | 425 | 0.17029
BUELLTON 1101 | LOS PADRES | 77.7776 | 37.5644 | 3943 | 74.1% | 2.521% | 1 | 0.2926 | 1 | 1.5921 | 0.46585 | Medium | Low | Low | 337 | 312 | 0.2926
COTTONWOOD 1102 | NORTH VALLEY | 59.3351 | 49.5356 | 4117.5 | 71.38% | 0% | 1 | 0.31871 | 1 | 1.4441 | 0.46026 | High | Low | Low | 338 | 294 | 0.31871
SUNOL 1101 | MISSION | 34.5067 | 79.6588 | 4405.1 | 62.4% | 34.83% | 0 | 0.2083 | 1 | 2.2066 | 0.45963 | Medium | Low | Medium | 339 | 381 | 0.2083
PAUL SWEET 2104 | CENTRAL COAST | 17.3184 | 177.171 | 6289.5 | 48.78% | 100% | 0 | 0.17204 | 1 | 2.666 | 0.45867 | Medium | Low | High | 340 | 423 | 0.17204
REDBUD 1102 | HUMBOLDT | 27.3864 | 27.6857 | 1619 | 46.83% | 5.522% | 0 | 0.19984 | 1 | 2.2912 | 0.45789 | Medium | Low | Medium | 341 | 392 | 0.19984
MORAGA 1101 | DIABLO | 18.7524 | 231.2458 | 4714.5 | 91.98% | 84.96% | 0 | 0.15195 | 1 | 2.9884 | 0.45408 | Medium | Low | High | 342 | 442 | 0.15195
LUCERNE 1103 | HUMBOLDT | 31.8489 | 0.075386 | 4 | 60.02% | 0% | 0 | 0.21456 | 1 | 2.0942 | 0.44933 | Medium | Low | Medium | 343 | 376 | 0.21456
HARRIS 1109 | HUMBOLDT | 13.0569 | 90.5332 | 4585.5 | 25.78% | 0% | 0 | 0.16591 | 1 | 2.7044 | 0.4487 | Medium | Low | High | 344 | 428 | 0.16591
LOS GATOS 1101 | DE ANZA | 9.9179 | 0.4769 | 10 | 47.3% | 0% | 0 | 0.16551 | 1 | 2.6755 | 0.44281 | Medium | Low | High | 345 | 429 | 0.16551
MORGAN HILL 2105 | SAN JOSE | 49.4076 | 60.3391 | 4988.4 | 59.76% | 26.88% | 1 | 0.24901 | 1 | 1.7734 | 0.4416 | Medium | Low | Medium | 346 | 347 | 0.24901
VALLEY VIEW 1106 | EAST BAY | 8.5618 | 3.2562 | 68 | 41% | 0% | 0 | 0.13774 | 1 | 3.1897 | 0.43936 | Medium | Low | High | 347 | 458 | 0.13774
COTATI 1103 | SONOMA | 82.6114 | 2.9792 | 332 | 74.13% | 0% | 1 | 0.33531 | 1 | 1.31 | 0.43924 | High | Low | Low | 348 | 284 | 0.33531
CRESCENT MILLS 2101 | NORTH VALLEY | 43.6463 | 62.7115 | 4950 | 55.3% | 0% | 0 | 0.28184 | 1 | 1.5412 | 0.43438 | Medium | Low | Low | 349 | 321 | 0.28184
STAFFORD 1102 | NORTH BAY | 21.3206 | 92.1724 | 3462.9 | 56.75% | 4.149% | 1 | 0.17116 | 1 | 2.5212 | 0.43153 | Medium | Low | High | 350 | 424 | 0.17116
INDIAN FLAT 1104 | YOSEMITE | 16.7358 | 46.4525 | 780.7 | 99.58% | 0% | 0 | 0.31705 | 1 | 1.3602 | 0.43126 | High | Low | Low | 351 | 295 | 0.31705
BURNEY 1101 | NORTH VALLEY | 51.5022 | 48.9487 | 2928.5 | 86.08% | 0% | 0 | 0.38258 | 1 | 1.1254 | 0.43057 | High | Low | Low | 352 | 254 | 0.38258
CLOVERDALE 1102 | SONOMA | 80.9762 | 48.6873 | 5260.3 | 74.95% | 58.94% | 0 | 0.41198 | 1 | 1.0437 | 0.42998 | High | Low | Low | 353 | 242 | 0.41198
TASSAJARA 2104 | DIABLO | 7.2573 | 128.4661 | 1249.5 | 74.62% | 25.11% | 0 | 0.14744 | 1 | 2.8959 | 0.42696 | Medium | Low | High | 354 | 448 | 0.14744
DUNLAP 1102 | FRESNO | 55.7604 | 79.3908 | 4445.3 | 99.59% | 0% | 1 | 0.47294 | 1 | 0.89144 | 0.42159 | High | Low | Low | 355 | 223 | 0.47294
SWIFT 2110 | SAN JOSE | 83.3204 | 0.95201 | 79 | 100% | 0% | 0 | 0.36227 | 1 | 1.1587 | 0.41975 | High | Low | Low | 356 | 263 | 0.36227
PUEBLO 1104 | NORTH BAY | 30.8506 | 212.953 | 11215.7 | 58.58% | 0% | 1 | 0.19921 | 1 | 2.1042 | 0.41918 | Medium | Low | Medium | 357 | 394 | 0.19921
COTTONWOOD 1101 | NORTH VALLEY | 70.4171 | 16.6714 | 1666 | 70.47% | 0% | 1 | 0.34668 | 1 | 1.202 | 0.4167 | High | Low | Low | 358 | 276 | 0.34668
CEDAR CREEK 1101 | NORTH VALLEY | 110.9 | 74 | 8214 | 99.91% | 16.25% | 0 | 0.60431 | 1 | 0.68853 | 0.41609 | High | Low | Low | 359 | 179 | 0.60431
GREENBRAE 1102 | NORTH BAY | 7.1787 | 133.0435 | 1734.9 | 55.05% | 100% | 0 | 0.126 | 1 | 3.2978 | 0.41551 | Medium | Low | High | 360 | 473 | 0.126
DEL MONTE 2103 | CENTRAL COAST | 12.8349 | 162.3707 | 5647.4 | 36.9% | 0% | 0 | 0.17404 | 1 | 2.3874 | 0.41549 | Medium | Low | High | 361 | 422 | 0.17404
SAN RAMON 2107 | MISSION | 13.2045 | 78.7075 | 2176.6 | 47.75% | 97.71% | 0 | 0.14562 | 1 | 2.8353 | 0.41289 | Medium | Low | High | 362 | 452 | 0.14562
SAN LEANDRO U 1109 | MISSION | 12.917 | 50.8296 | 1000.5 | 65.62% | 7.254% | 0 | 0.21802 | 1 | 1.8932 | 0.41274 | Medium | Low | Medium | 363 | 372 | 0.21802
CASTRO VALLEY 1106 | MISSION | 19.2033 | 76.1582 | 3117.1 | 46.92% | 76.11% | 0 | 0.14998 | 1 | 2.707 | 0.406 | Medium | Low | High | 364 | 445 | 0.14998
HIGHLANDS 1104 | HUMBOLDT | 11.8923 | 0.23778 | 7 | 40.4% | 0% | 0 | 0.16341 | 1 | 2.4665 | 0.40305 | Medium | Low | High | 365 | 431 | 0.16341
CALPELLA 1101 | HUMBOLDT | 72.0108 | 65.4062 | 6000.3 | 78.5% | 5.015% | 1 | 0.38639 | 1 | 1.0408 | 0.40215 | High | Low | Low | 366 | 251 | 0.38639
LAS GALLINAS A 1106 | NORTH BAY | 4.998 | 42.8648 | 675 | 31.74% | 39.74% | 0 | 0.1226 | 1 | 3.2664 | 0.40047 | Medium | Low | High | 367 | 475 | 0.1226
RALSTON 1102 | PENINSULA | 3.2655 | 0.09353 | 1 | 30.54% | 0% | 0 | 0.11938 | 1 | 3.3318 | 0.39776 | Medium | Low | High | 368 | 488 | 0.11938
HIGGINS 1107 | SIERRA | 16.8285 | 2.8864 | 94 | 51.67% | 0% | 0 | 0.22612 | 1 | 1.7548 | 0.39679 | Medium | Low | Medium | 369 | 363 | 0.22612
SAN LUIS OBISPO 1101 | LOS PADRES | 27.4591 | 61.777 | 2353.4 | 72.08% | 37.5% | 0 | 0.20369 | 1 | 1.9385 | 0.39484 | Medium | Low | Medium | 370 | 386 | 0.20369
MAPLE CREEK 1101 | HUMBOLDT | 9.8748 | 0.39268 | 13 | 29.83% | 0% | 0 | 0.2005 | 1 | 1.9619 | 0.39336 | Medium | Low | Medium | 371 | 389 | 0.2005
SANTA MARIA 1108 | LOS PADRES | 73.0359 | 41.6543 | 3939.8 | 77.22% | 60.25% | 1 | 0.3454 | 1 | 1.1384 | 0.39321 | High | Low | Low | 372 | 277 | 0.3454
SAN JOAQUIN #3 1101 | YOSEMITE | 24.668 | 172.7328 | 4259.4 | 100% | 94.57% | 0 | 0.28198 | 1 | 1.3766 | 0.38818 | Medium | Low | Low | 373 | 319 | 0.28198
WYANDOTTE 1110 | NORTH VALLEY | 13.8013 | 69.0873 | 2755.5 | 34.6% | 0% | 0 | 0.12906 | 1 | 2.989 | 0.38577 | Medium | Low | High | 374 | 470 | 0.12906
SAN CARLOS 1104 | PENINSULA | 8.3888 | 79.6449 | 1757.5 | 38.02% | 0% | 0 | 0.10317 | 1 | 3.7132 | 0.38309 | Low | Low | High | 375 | 527 | 0.10317
SARATOGA 1106 | DE ANZA | 13.394 | 184.9638 | 4935 | 50.2% | 4.959% | 0 | 0.12542 | 1 | 3.0513 | 0.38269 | Medium | Low | High | 376 | 474 | 0.12542
MERCED FALLS 1102 | YOSEMITE | 120.7817 | 9.0416 | 1726.7 | 63.25% | 0% | 1 | 0.25626 | 1 | 1.4882 | 0.38136 | Medium | Low | Low | 377 | 339 | 0.25626
TAR FLAT 0402 | YOSEMITE | 5.4986 | 73.2444 | 485.2 | 83% | 23.55% | 0 | 0.16545 | 1 | 2.2965 | 0.37995 | Medium | Low | Medium | 378 | 430 | 0.16545
TAMARACK 1101 | SIERRA | 16.4477 | 84.0596 | 1509.4 | 91.6% | 0% | 0 | 0.41125 | 1 | 0.9203 | 0.37847 | High | Low | Low | 379 | 243 | 0.41125
PETALUMA C 1109 | SONOMA | 47.7751 | 37.3436 | 2497.5 | 71.44% | 0% | 0 | 0.24335 | 1 | 1.5475 | 0.37658 | Medium | Low | Low | 380 | 351 | 0.24335
PASO ROBLES 1104 | LOS PADRES | 37.5318 | 122.939 | 8272.1 | 55.78% | 0% | 0 | 0.23873 | 1 | 1.5762 | 0.3763 | Medium | Low | Low | 381 | 356 | 0.23873
PLACERVILLE 1111 | SIERRA | 13.2951 | 129.5107 | 2399.6 | 71.76% | 0% | 0 | 0.18947 | 1 | 1.9744 | 0.3741 | Medium | Low | Medium | 382 | 405 | 0.18947
SOBRANTE 1101 | DIABLO | 15.9136 | 157.462 | 3382 | 74.09% | 0.7306% | 0 | 0.13531 | 1 | 2.7637 | 0.37397 | Medium | Low | High | 383 | 462 | 0.13531
PALO SECO 0401 | EAST BAY | 4.7078 | 182.9243 | 867.5 | 99.27% | 18.75% | 0 | 0.12716 | 1 | 2.9264 | 0.37214 | Medium | Low | High | 384 | 471 | 0.12716
WISHON 1101 | YOSEMITE | 7.7822 | 27.8513 | 216.8 | 99.97% | 51.22% | 0 | 0.32238 | 1 | 1.1392 | 0.36726 | High | Low | Low | 385 | 293 | 0.32238
SUMMIT 1102 | SIERRA | 5.1556 | 81.6334 | 421 | 99.97% | 0% | 0 | 0.24499 | 1 | 1.4982 | 0.36703 | Medium | Low | Low | 386 | 350 | 0.24499
ZACA 1102 | LOS PADRES | 64.9618 | 56.5808 | 4540 | 80.96% | 36.17% | 1 | 0.31531 | 1 | 1.1576 | 0.365 | High | Low | Low | 387 | 299 | 0.31531
SONOMA 1102 | SONOMA | 5.4359 | 0.43651 | 8 | 29.66% | 100% | 0 | 0.14754 | 1 | 2.4622 | 0.36326 | Medium | Low | High | 388 | 447 | 0.14754
UPPER LAKE 1101 | HUMBOLDT | 53.0863 | 91.0265 | 7983.8 | 60.53% | 1.399% | 0 | 0.31613 | 1 | 1.1472 | 0.36268 | High | Low | Low | 389 | 297 | 0.31613
SOBRANTE 1103 | DIABLO | 3.7247 | 134.2739 | 695.7 | 71.89% | 15.89% | 0 | 0.1215 | 1 | 2.9819 | 0.36231 | Medium | Low | High | 390 | 480 | 0.1215
GRAYS FLAT 0401 | NORTH VALLEY | 10.7057 | 75.9501 | 813 | 100% | 0% | 0 | 0.29592 | 1 | 1.2228 | 0.36185 | Medium | Low | Low | 391 | 310 | 0.29592
MENDOCINO 1101 | HUMBOLDT | 40.8852 | 96.2417 | 8109.4 | 48.52% | 30.15% | 0 | 0.30054 | 1 | 1.2002 | 0.36072 | High | Low | Low | 392 | 308 | 0.30054
TIVY VALLEY 1107 | FRESNO | 118.6456 | 22.2285 | 3890.3 | 67.79% | 0% | 1 | 0.32304 | 1 | 1.1078 | 0.35787 | High | Low | Low | 393 | 291 | 0.32304
LAURELES 1112 | CENTRAL COAST | 28.5944 | 269.5468 | 9658.4 | 79.8% | 0% | 0 | 0.19579 | 1 | 1.8213 | 0.35659 | Medium | Low | Medium | 394 | 397 | 0.19579
VACAVILLE 1108 | SACRAMENTO | 28.2253 | 17.9844 | 872.1 | 58.21% | 0% | 0 | 0.22757 | 1 | 1.5528 | 0.35338 | Medium | Low | Low | 395 | 361 | 0.22757
TEJON 1102 | KERN | 32.2059 | 17.6568 | 1105.5 | 51.44% | 0% | 0 | 0.18524 | 1 | 1.9041 | 0.35273 | Medium | Low | Medium | 396 | 410 | 0.18524
SPRUCE 0402 | EAST BAY | 1.905 | 68.1248 | 244.5 | 53.08% | 19.04% | 0 | 0.095782 | 1 | 3.6749 | 0.35199 | Low | Low | High | 397 | 554 | 0.095782
EL CERRITO G 1113 | EAST BAY | 0.20892 | 22.2103 | 212 | 2.189% | 0% | 0 | 0.093665 | 1 | 3.7545 | 0.35167 | Low | Low | High | 398 | 560 | 0.093665
IONE 1101 | STOCKTON | 15.6336 | 68.2479 | 1976.2 | 53.99% | 0% | 0 | 0.18325 | 1 | 1.9134 | 0.35064 | Medium | Low | Medium | 399 | 413 | 0.18325
CABRILLO 1104 | LOS PADRES | 30.2749 | 13.5021 | 1030.25 | 39.68% | 0% | 1 | 0.13172 | 1 | 2.6604 | 0.35043 | Medium | Low | High | 400 | 464 | 0.13172
FOOTHILL 1101 | LOS PADRES | 17.8092 | 85.4395 | 3318.4 | 45.85% | 0% | 0 | 0.13992 | 1 | 2.5032 | 0.35024 | Medium | Low | High | 401 | 455 | 0.13992
MORRO BAY 1102 | LOS PADRES | 21.4127 | 32.5118 | 1876.5 | 37.1% | 18.72% | 1 | 0.11824 | 1 | 2.9365 | 0.3472 | Medium | Low | High | 402 | 493 | 0.11824
SAN RAFAEL 1105 | NORTH BAY | 4.1168 | 79.9253 | 1839.6 | 17.89% | 0% | 0 | 0.10483 | 1 | 3.311 | 0.34708 | Low | Low | High | 403 | 522 | 0.10483
SONOMA 1104 | SONOMA | 19.5383 | 0.053642 | 3 | 34.94% | 0% | 1 | 0.15663 | 1 | 2.1994 | 0.34448 | Medium | Low | Medium | 404 | 441 | 0.15663
KING CITY 1103 | CENTRAL COAST | 17.5881 | 88.4434 | 2428 | 64.07% | 0% | 0 | 0.20663 | 1 | 1.6667 | 0.34439 | Medium | Low | Low | 405 | 383 | 0.20663
KERCKHOFF 1101 | YOSEMITE | 34.5924 | 140.6862 | 4795.4 | 100% | 0% | 0 | 0.26925 | 1 | 1.2691 | 0.3417 | Medium | Low | Low | 406 | 332 | 0.26925
PUEBLO 1105 | NORTH BAY | 23.9073 | 36.3841 | 2583.5 | 33.67% | 0% | 0 | 0.1782 | 1 | 1.9065 | 0.33975 | Medium | Low | Medium | 407 | 417 | 0.1782
LAS AROMAS 0401 | DIABLO | 5.9862 | 211.8395 | 1323.7 | 95.8% | 0% | 0 | 0.11738 | 1 | 2.8362 | 0.33291 | Medium | Low | High | 408 | 495 | 0.11738
VALLEY VIEW 1105 | EAST BAY | 5.4093 | 0.69571 | 13 | 28.95% | 0% | 0 | 0.1088 | 1 | 3.0206 | 0.32865 | Low | Low | High | 409 | 513 | 0.1088
VIEJO 2203 | CENTRAL COAST | 3.5033 | 132.9307 | 1846.5 | 25.22% | 0% | 0 | 0.12942 | 1 | 2.5288 | 0.32727 | Medium | Low | High | 410 | 469 | 0.12942
TAR FLAT 0401 | YOSEMITE | 3.5092 | 140.2515 | 519.8 | 94.68% | 18.46% | 0 | 0.13406 | 1 | 2.4385 | 0.32691 | Medium | Low | High | 411 | 463 | 0.13406
SALMON CREEK 1101 | SONOMA | 26.7666 | 46.0934 | 2187.8 | 56.39% | 34.84% | 0 | 0.17748 | 1 | 1.8364 | 0.32592 | Medium | Low | Medium | 412 | 418 | 0.17748
SAN RAFAEL 1101 | NORTH BAY | 8.619 | 100.8045 | 2375.8 | 36.57% | 75.53% | 1 | 0.095181 | 1 | 3.4172 | 0.32525 | Low | Low | High | 413 | 556 | 0.095181
PURISIMA 1101 | LOS PADRES | 15.9907 | 3.8902 | 230 | 27.05% | 0% | 0 | 0.10891 | 1 | 2.9811 | 0.32467 | Low | Low | High | 414 | 512 | 0.10891
CARLOTTA 1121 | HUMBOLDT | 21.1982 | 72.3697 | 3511.9 | 43.68% | 0% | 1 | 0.26139 | 1 | 1.2391 | 0.32387 | Medium | Low | Low | 415 | 335 | 0.26139
FRUITLAND 1141 | HUMBOLDT | 24.0637 | 134.2847 | 3692.4 | 87.51% | 0% | 1 | 0.36081 | 1 | 0.89333 | 0.32232 | High | Low | Low | 416 | 267 | 0.36081
TASSAJARA 2109 | DIABLO | 0.80761 | 2.0601 | 4 | 41.59% | 0% | 0 | 0.10579 | 1 | 3.0369 | 0.32126 | Low | Low | High | 417 | 518 | 0.10579
SO. CAL. EDISON #3 1101 | FRESNO | 6.4255 | 1.9313 | 11 | 100% | 34.58% | 0 | 0.30414 | 1 | 1.0515 | 0.3198 | High | Low | Low | 418 | 306 | 0.30414
RIDGE 0402 | EAST BAY | 1.6674 | 151.6823 | 362.9 | 69.69% | 0% | 0 | 0.098308 | 1 | 3.2442 | 0.31893 | Low | Low | High | 419 | 548 | 0.098308
PAUL SWEET 2105 | CENTRAL COAST | 8.6024 | 84.5429 | 3445.9 | 21.11% | 85.61% | 0 | 0.11899 | 1 | 2.6738 | 0.31815 | Medium | Low | High | 420 | 490 | 0.11899
UKIAH 1114 | HUMBOLDT | 51.9619 | 68.1974 | 7022.4 | 50.46% | 0% | 1 | 0.31473 | 1 | 1.0096 | 0.31773 | High | Low | Low | 421 | 300 | 0.31473
LAS PULGAS 0401 | PENINSULA | 0.063561 | 48.5621 | 294 | 1.05% | 0% | 0 | 0.081206 | 1 | 3.8914 | 0.31601 | Low | Low | High | 422 | 585 | 0.081206
VACAVILLE 1104 | SACRAMENTO | 15.6565 | 122.8252 | 2194.1 | 87.64% | 0% | 0 | 0.18224 | 1 | 1.7281 | 0.31493 | Medium | Low | Medium | 423 | 416 | 0.18224
LONE TREE 2105 | DIABLO | 9.5646 | 12.3004 | 256.5 | 45.87% | 0% | 0 | 0.18285 | 1 | 1.7206 | 0.31462 | Medium | Low | Medium | 424 | 415 | 0.18285
MILPITAS 1109 | SAN JOSE | 29.4495 | 0.22548 | 11 | 60.37% | 0% | 0 | 0.24961 | 1 | 1.2599 | 0.31449 | Medium | Low | Low | 425 | 345 | 0.24961
TASSAJARA 2112 | DIABLO | 10.4417 | 108.27 | 2017.6 | 56.03% | 73.38% | 0 | 0.11268 | 1 | 2.7879 | 0.31414 | Medium | Low | High | 426 | 506 | 0.11268
EL CERRITO G 1112 | EAST BAY | 4.6851 | 47.8544 | 1170.5 | 19.15% | 89.29% | 0 | 0.084501 | 1 | 3.7125 | 0.31371 | Low | Low | High | 427 | 580 | 0.084501
HOLLYWOOD 0401 | EAST BAY | 2.9599 | 45.3292 | 240 | 55.9% | 0% | 0 | 0.10852 | 1 | 2.884 | 0.31296 | Low | Low | High | 428 | 515 | 0.10852
SAUSALITO 1102 | NORTH BAY | 8.6501 | 55.5336 | 984.6 | 48.79% | 0% | 0 | 0.12034 | 1 | 2.5917 | 0.31188 | Medium | Low | High | 429 | 484 | 0.12034
BEAR VALLEY 2101 | YOSEMITE | 108.2666 | 7.661 | 1277.1 | 64.95% | 0% | 0 | 0.27005 | 1 | 1.1403 | 0.30793 | Medium | Low | Low | 430 | 329 | 0.27005
ROSSMOOR 1101 | DIABLO | 12.9199 | 148.0625 | 4521 | 42.31% | 16.47% | 0 | 0.11909 | 1 | 2.5847 | 0.30782 | Medium | Low | High | 431 | 489 | 0.11909
STAFFORD 1101 | NORTH BAY | 7.6052 | 129.288 | 2835.7 | 34.67% | 0% | 0 | 0.12031 | 1 | 2.5554 | 0.30745 | Medium | Low | High | 432 | 485 | 0.12031
FOOTHILL 1102 | LOS PADRES | 10.2766 | 105.2891 | 2223.2 | 48.67% | 0% | 0 | 0.13118 | 1 | 2.3401 | 0.30697 | Medium | Low | Medium | 433 | 466 | 0.13118
RIO DEL MAR 0401 | CENTRAL COAST | 1.702 | 49.8711 | 176 | 48.23% | 0% | 0 | 0.12014 | 1 | 2.5466 | 0.30594 | Medium | Low | High | 434 | 486 | 0.12014
HALF MOON BAY 1102 | PENINSULA | 7.682 | 93.825 | 4052.2 | 17.79% | 72.22% | 0 | 0.094603 | 1 | 3.2201 | 0.30463 | Low | Low | High | 435 | 558 | 0.094603
WALDO 0401 | EAST BAY | 1.6612 | 31.6439 | 180 | 29.2% | 0% | 0 | 0.082439 | 1 | 3.673 | 0.3028 | Low | Low | High | 436 | 581 | 0.082439
HUMBOLDT BAY 1102 | HUMBOLDT | 7.0458 | 0.31454 | 13 | 17.05% | 0% | 0 | 0.10093 | 1 | 2.9917 | 0.30196 | Low | Low | High | 437 | 536 | 0.10093
FAIRMOUNT 0401 | EAST BAY | 1.4849 | 13.3911 | 77 | 25.82% | 0% | 0 | 0.078967 | 1 | 3.8023 | 0.30026 | Low | Low | High | 438 | 590 | 0.078967
PAUL SWEET 2107 | CENTRAL COAST | 10.6088 | 137.878 | 6735.2 | 21.72% | 44.56% | 0 | 0.11338 | 1 | 2.6376 | 0.29905 | Medium | Low | High | 439 | 505 | 0.11338
PRUNEDALE 1110 | CENTRAL COAST | 0.046537 | 177.6947 | 14170 | 0.05836% | 0% | 0 | 0.16321 | 1 | 1.8248 | 0.29784 | Medium | Low | Medium | 440 | 433 | 0.16321
FULTON 1102 | SONOMA | 28.1813 | 0.26946 | 17 | 44.67% | 12.65% | 0 | 0.18719 | 1 | 1.5859 | 0.29685 | Medium | Low | Low | 441 | 407 | 0.18719
CLEAR LAKE 1101 | HUMBOLDT | 18.1143 | 29.5531 | 3379.6 | 15.84% | 31.9% | 0 | 0.13818 | 1 | 2.1474 | 0.29672 | Medium | Low | Medium | 442 | 457 | 0.13818
VACAVILLE 1111 | SACRAMENTO | 12.1732 | 94.4466 | 1657 | 69.39% | 0% | 0 | 0.15702 | 1 | 1.8873 | 0.29636 | Medium | Low | Medium | 443 | 440 | 0.15702
COAST RD 0401 | CENTRAL COAST | 1.6617 | 17.5143 | 54 | 53.9% | 0% | 0 | 0.11855 | 1 | 2.4967 | 0.29599 | Medium | Low | High | 444 | 492 | 0.11855
CAMBRIA 1102 | LOS PADRES | 17.1255 | 61.511 | 1658.7 | 63.51% | 0% | 0 | 0.16048 | 1 | 1.844 | 0.29593 | Medium | Low | Medium | 445 | 436 | 0.16048
SAN LEANDRO U 1114 | MISSION | 13.8938 | 32.3118 | 935.2 | 48% | 0% | 0 | 0.14809 | 1 | 1.9911 | 0.29486 | Medium | Low | Medium | 446 | 446 | 0.14809
PLACER 1103 | SIERRA | 12.2492 | 68.8595 | 2024.4 | 41.67% | 0% | 0 | 0.13769 | 1 | 2.1392 | 0.29455 | Medium | Low | Medium | 447 | 459 | 0.13769
FRANKLIN 1104 | EAST BAY | 5.6687 | 0.06576 | 1 | 37.28% | 0% | 0 | 0.11211 | 1 | 2.6229 | 0.29404 | Medium | Low | High | 448 | 507 | 0.11211
OAKLAND K 1103 | EAST BAY | 6.0941 | 141.8873 | 1523.6 | 56.75% | 36.68% | 0 | 0.10303 | 1 | 2.8454 | 0.29317 | Low | Low | High | 449 | 528 | 0.10303
MORAGA 1103 | DIABLO | 3.4716 | 77.9372 | 1410 | 19.19% | 4.457% | 1 | 0.091048 | 1 | 3.2148 | 0.2927 | Low | Low | High | 450 | 566 | 0.091048
GEYSERVILLE 1102 | SONOMA | 54.2117 | 50.389 | 5951.9 | 45.9% | 34.72% | 0 | 0.27337 | 1 | 1.065 | 0.29113 | Medium | Low | Low | 451 | 325 | 0.27337
CHESTER 1102 | NORTH VALLEY | 2.4094 | 54.9614 | 296 | 44.74% | 0% | 0 | 0.15173 | 1 | 1.9144 | 0.29046 | Medium | Low | Medium | 452 | 443 | 0.15173
FAIRVIEW 2207 | DIABLO | 18.7684 | 16.7938 | 853 | 36.95% | 0% | 1 | 0.11443 | 1 | 2.5257 | 0.28901 | Medium | Low | High | 453 | 504 | 0.11443
HICKS 1116 | SAN JOSE | 10.7423 | 155.6132 | 5361.7 | 31.18% | 0% | 0 | 0.11205 | 1 | 2.5723 | 0.28823 | Low | Low | High | 454 | 508 | 0.11205
CAROLANDS 0404 | PENINSULA | 3.9545 | 1.1721 | 12 | 38.63% | 0% | 0 | 0.11531 | 1 | 2.4872 | 0.28679 | Medium | Low | High | 455 | 500 | 0.11531
HARTLEY 1101 | HUMBOLDT | 28.4012 | 30.64 | 1997.2 | 43.57% | 0% | 0 | 0.18458 | 1 | 1.5501 | 0.28612 | Medium | Low | Low | 456 | 411 | 0.18458
CAYETANO 2111 | MISSION | 5.4093 | 22.3271 | 272 | 44.4% | 0% | 0 | 0.12049 | 1 | 2.3726 | 0.28587 | Medium | Low | Medium | 457 | 483 | 0.12049
SAN CARLOS 1103 | PENINSULA | 3.983 | 76.8569 | 1260 | 24.3% | 0% | 0 | 0.073453 | 1 | 3.8842 | 0.28531 | Low | Low | High | 458 | 603 | 0.073453
HICKS 2103 | SAN JOSE | 10.8958 | 136.6541 | 3729.4 | 39.92% | 27.73% | 0 | 0.13059 | 1 | 2.1701 | 0.2834 | Medium | Low | Medium | 459 | 468 | 0.13059
CAMBRIA 1101 | LOS PADRES | 27.64 | 26.6582 | 858 | 85.88% | 0% | 1 | 0.20082 | 1 | 1.4064 | 0.28243 | Medium | Low | Low | 460 | 388 | 0.20082
HORSESHOE 1101 | SIERRA | 6.4051 | 60.2483 | 2184.9 | 17.66% | 0% | 0 | 0.10362 | 1 | 2.7162 | 0.28145 | Low | Low | High | 461 | 526 | 0.10362
OAKLAND J 1102 | EAST BAY | 6.2044 | 46.5645 | 857.5 | 33.69% | 0% | 0 | 0.10164 | 1 | 2.7444 | 0.27893 | Low | Low | High | 462 | 534 | 0.10164
RIO DELL 1102 | HUMBOLDT | 47.0229 | 106.5689 | 7819.8 | 64.08% | 0% | 1 | 0.42685 | 1 | 0.65331 | 0.27887 | High | Low | Low | 463 | 240 | 0.42685
PANORAMA 1102 | NORTH VALLEY | 32.1467 | 56.945 | 4816.4 | 38.01% | 0% | 0 | 0.17497 | 1 | 1.5851 | 0.27735 | Medium | Low | Low | 464 | 420 | 0.17497
PIERCY 2110 | SAN JOSE | 14.4387 | 57.4246 | 1584 | 52.34% | 0% | 0 | 0.20709 | 1 | 1.3322 | 0.2759 | Medium | Low | Low | 465 | 382 | 0.20709
WILDWOOD 1101 | NORTH VALLEY | 32.6037 | 56.7915 | 1691 | 100% | 0% | 1 | 0.43227 | 1 | 0.62979 | 0.27224 | High | Low | Low | 466 | 236 | 0.43227
LAKEWOOD 2107 | DIABLO | 7.3667 | 88.4957 | 2558.5 | 25.48% | 1.068% | 0 | 0.092658 | 1 | 2.8742 | 0.26632 | Low | Low | High | 467 | 561 | 0.092658
UKIAH 1115 | HUMBOLDT | 17.5263 | 38.8731 | 977.3 | 69.71% | 0% | 0 | 0.22334 | 1 | 1.1842 | 0.26447 | Medium | Low | Low | 468 | 366 | 0.22334
ANDERSON 1101 | NORTH VALLEY | 9.8615 | 58.5247 | 1174 | 49.16% | 0% | 0 | 0.15133 | 1 | 1.7454 | 0.26413 | Medium | Low | Medium | 469 | 444 | 0.15133
CAYUCOS 1102 | LOS PADRES | 13.8993 | 42.5264 | 2457.9 | 24.05% | 62.92% | 0 | 0.14223 | 1 | 1.8563 | 0.26402 | Medium | Low | Medium | 470 | 453 | 0.14223
EL CERRITO G 1110 | EAST BAY | 1.9753 | 34.2051 | 347 | 19.47% | 0% | 0 | 0.070004 | 1 | 3.765 | 0.26356 | Low | Low | High | 471 | 617 | 0.070004
RED BLUFF 1101 | NORTH VALLEY | 46.1055 | 0.040201 | 3 | 61.78% | 0% | 1 | 0.24502 | 1 | 1.0703 | 0.26225 | Medium | Low | Low | 472 | 349 | 0.24502
EEL RIVER 1102 | HUMBOLDT | 38.97 | 71.5696 | 10410.2 | 26.79% | 0% | 0 | 0.35914 | 1 | 0.72131 | 0.25905 | High | Low | Low | 473 | 269 | 0.35914
PACIFICA 1103 | PENINSULA | 4.0354 | 3.1893 | 60 | 21.45% | 74.37% | 0 | 0.090312 | 1 | 2.8097 | 0.25375 | Low | Low | High | 474 | 568 | 0.090312
RISING RIVER 1101 | NORTH VALLEY | 46.3641 | 41.1784 | 2451.5 | 77.88% | 0% | 0 | 0.35847 | 1 | 0.7054 | 0.25286 | High | Low | Low | 475 | 272 | 0.35847
SAN LUIS OBISPO 1102 | LOS PADRES | 0.61698 | 77.5643 | 991.9 | 4.825% | 0% | 0 | 0.079225 | 1 | 3.1792 | 0.25187 | Low | Low | High | 476 | 589 | 0.079225
ALTO 1122 | NORTH BAY | 8.8537 | 263.1656 | 4654.4 | 50.06% | 65.63% | 0 | 0.079305 | 1 | 3.1723 | 0.25158 | Low | Low | High | 477 | 588 | 0.079305
SEACLIFF 0401 | CENTRAL COAST | 8.5745 | 367.0421 | 3398.7 | 92.6% | 81.87% | 0 | 0.092298 | 1 | 2.6626 | 0.24576 | Low | Low | High | 478 | 562 | 0.092298
LOYOLA 1102 | DE ANZA | 0.10967 | 139.6629 | 7116.9 | 0.2152% | 0% | 0 | 0.10013 | 1 | 2.4497 | 0.24529 | Low | Low | High | 479 | 541 | 0.10013
SARATOGA 1115 | DE ANZA | 2.7261 | 0.7909 | 10 | 21.56% | 0% | 0 | 0.097367 | 1 | 2.5049 | 0.2439 | Low | Low | High | 480 | 551 | 0.097367
SAN MIGUEL 1106 | LOS PADRES | 37.1788 | 14.6587 | 1058.2 | 51.5% | 0% | 0 | 0.21893 | 1 | 1.1061 | 0.24216 | Medium | Low | Low | 481 | 371 | 0.21893
TYLER 1105 | NORTH VALLEY | 60.5727 | 42.7408 | 4721 | 54.84% | 0% | 0 | 0.2697 | 1 | 0.89474 | 0.24131 | Medium | Low | Low | 482 | 331 | 0.2697
CORNING 1102 | NORTH VALLEY | 81.1492 | 15.9848 | 3210 | 40.41% | 0% | 1 | 0.21678 | 1 | 1.1124 | 0.24114 | Medium | Low | Low | 483 | 374 | 0.21678
SAN RAFAEL 1104 | NORTH BAY | 11.3584 | 303.4563 | 7546.2 | 45.68% | 4.206% | 0 | 0.063863 | 1 | 3.7706 | 0.2408 | Low | Low | High | 484 | 632 | 0.063863
HATTON 1101 | CENTRAL COAST | 14.8111 | 258.8027 | 5969 | 64.22% | 9.429% | 1 | 0.12167 | 1 | 1.9413 | 0.23619 | Medium | Low | Medium | 485 | 479 | 0.12167
HOPLAND 1101 | HUMBOLDT | 82.4026 | 0.25226 | 33 | 62.99% | 0% | 0 | 0.24946 | 1 | 0.94514 | 0.23577 | Medium | Low | Low | 486 | 346 | 0.24946
PACIFICA 1102 | PENINSULA | 5.0009 | 3.4984 | 70 | 24.99% | 58.95% | 0 | 0.084575 | 1 | 2.7714 | 0.2344 | Low | Low | High | 487 | 578 | 0.084575
CHESTER 1101 | NORTH VALLEY | 2.5695 | 64.7245 | 521 | 31.92% | 0% | 0 | 0.12056 | 1 | 1.9366 | 0.23348 | Medium | Low | Medium | 488 | 481 | 0.12056
UKIAH 1111 | HUMBOLDT | 22.4731 | 19.3083 | 744.6 | 58.28% | 0% | 0 | 0.23588 | 1 | 0.98939 | 0.23338 | Medium | Low | Low | 489 | 359 | 0.23588
EL CERRITO G 1111 | EAST BAY | 0.94606 | 22.2933 | 281 | 7.506% | 0% | 0 | 0.059807 | 1 | 3.8959 | 0.233 | Low | Low | High | 490 | 640 | 0.059807
SNEATH LANE 1107 | PENINSULA | 2.5458 | 15.7601 | 167 | 24.03% | 0% | 0 | 0.10236 | 1 | 2.2761 | 0.23298 | Low | Low | Medium | 491 | 530 | 0.10236
VASCO 1102 | MISSION | 41.9238 | 27.6714 | 2461.1 | 47.14% | 0% | 0 | 0.20194 | 1 | 1.1484 | 0.23191 | Medium | Low | Low | 492 | 387 | 0.20194
LAS POSITAS 2108 | MISSION | 7.3474 | 5.525 | 112 | 36.25% | 0% | 0 | 0.11452 | 1 | 2.0246 | 0.23186 | Medium | Low | Medium | 493 | 503 | 0.11452
PALMER 1101 | LOS PADRES | 37.0218 | 21.6138 | 1331 | 60.12% | 0% | 0 | 0.1844 | 1 | 1.245 | 0.22959 | Medium | Low | Low | 494 | 412 | 0.1844
HARRIS 1108 | HUMBOLDT | 2.5554 | 18.9526 | 618.7 | 7.828% | 0% | 0 | 0.070432 | 1 | 3.2534 | 0.22914 | Low | Low | High | 495 | 616 | 0.070432
CLAYTON 2215 | DIABLO | 8.5821 | 88.5228 | 2717.5 | 27.96% | 13.23% | 0 | 0.077122 | 1 | 2.97 | 0.22905 | Low | Low | High | 496 | 591 | 0.077122
BALCH NO 1 1101 | FRESNO | 14.6983 | 24.0733 | 354 | 99.95% | 0% | 0 | 0.32415 | 1 | 0.70256 | 0.22774 | High | Low | Low | 497 | 290 | 0.32415
SANTA ROSA A 1107 | SONOMA | 2.9541 | 140.0185 | 861.1 | 48.03% | 100% | 0 | 0.115 | 1 | 1.9794 | 0.22762 | Medium | Low | Medium | 498 | 501 | 0.115
LLAGAS 2101 | SAN JOSE | 19.8062 | 31.8184 | 3239.5 | 19.45% | 0% | 0 | 0.16055 | 1 | 1.4164 | 0.22741 | Medium | Low | Low | 499 | 435 | 0.16055
ORINDA 0401 | DIABLO | 9.3864 | 287.0654 | 3454 | 78.01% | 25.23% | 0 | 0.075976 | 1 | 2.9927 | 0.22737 | Low | Low | High | 500 | 594 | 0.075976
SHINGLE SPRINGS 1103 | SIERRA | 8.4534 | 233.596 | 3206.9 | 61.58% | 64.3% | 1 | 0.099664 | 1 | 2.279 | 0.22713 | Low | Low | Medium | 501 | 543 | 0.099664
WYANDOTTE 1102 | NORTH VALLEY | 4.5597 | 46.3866 | 1089 | 19.42% | 0% | 0 | 0.089417 | 1 | 2.5358 | 0.22674 | Low | Low | High | 502 | 570 | 0.089417
WILLOW PASS 2107 | DIABLO | 0.15832 | 0.84686 | 3 | 4.469% | 0% | 0 | 0.10569 | 1 | 2.1198 | 0.22404 | Low | Low | Medium | 503 | 519 | 0.10569
BERKELEY F 1105 | EAST BAY | 1.7869 | 64.7043 | 735.5 | 15.72% | 0% | 0 | 0.068434 | 1 | 3.2675 | 0.22361 | Low | Low | High | 504 | 619 | 0.068434
DOLAN ROAD 1101 | CENTRAL COAST | 3.8209 | 57.6437 | 3956.9 | 5.566% | 0% | 0 | 0.10527 | 1 | 2.1109 | 0.22221 | Low | Low | Medium | 505 | 520 | 0.10527
SONOMA 1105 | SONOMA | 14.5812 | 0.73753 | 46 | 23.38% | 31.42% | 0 | 0.11057 | 1 | 1.9985 | 0.22098 | Low | Low | Medium | 506 | 510 | 0.11057
ARCATA 1121 | HUMBOLDT | 6.629 | 2.6967 | 78 | 22.92% | 0% | 0 | 0.1205 | 1 | 1.8296 | 0.22047 | Medium | Low | Medium | 507 | 482 | 0.1205
SMARTVILLE 1101 | SIERRA | 15.8868 | 404.905 | 6432.2 | 100% | 0% | 0 | 0.10646 | 1 | 2.0689 | 0.22024 | Low | Low | Medium | 508 | 516 | 0.10646
OAKLAND X 1105 | EAST BAY | 3.475 | 52.0985 | 770 | 23.51% | 0% | 0 | 0.075775 | 1 | 2.8409 | 0.21527 | Low | Low | High | 509 | 596 | 0.075775
SANTA YNEZ 1101 | LOS PADRES | 30.6514 | 98.3916 | 7214.7 | 41.8% | 44.97% | 0 | 0.19903 | 1 | 1.0807 | 0.21509 | Medium | Low | Low | 510 | 395 | 0.19903
COTATI 1104 | SONOMA | 7.1785 | 3.6067 | 69 | 37.52% | 0% | 0 | 0.13107 | 1 | 1.6408 | 0.21507 | Medium | Low | Low | 511 | 467 | 0.13107
CLOVERDALE 1101 | SONOMA | 24.0395 | 83.1986 | 3030.8 | 65.99% | 0% | 0 | 0.22357 | 1 | 0.95033 | 0.21246 | Medium | Low | Low | 512 | 365 | 0.22357
OAKLAND D 1112 | EAST BAY | 2.6688 | 89.2166 | 1061 | 22.44% | 77.45% | 0 | 0.071051 | 1 | 2.99 | 0.21244 | Low | Low | High | 513 | 614 | 0.071051
JAMESON 1103 | SACRAMENTO | 3.6313 | 77.1526 | 840.3 | 33.34% | 0% | 0 | 0.11642 | 1 | 1.8208 | 0.21198 | Medium | Low | Medium | 514 | 498 | 0.11642
BELMONT 1103 | PENINSULA | 1.5331 | 86.6921 | 1624.8 | 8.18% | 0% | 0 | 0.061024 | 1 | 3.4689 | 0.21169 | Low | Low | High | 515 | 639 | 0.061024
SUMMIT 1101 | SIERRA | 8.7537 | 84.6905 | 1442.5 | 51.39% | 0% | 0 | 0.14736 | 1 | 1.4297 | 0.21068 | Medium | Low | Low | 516 | 450 | 0.14736
FORT SEWARD 1122 | HUMBOLDT | 17.3427 | 44.8588 | 983 | 79.14% | 0% | 0 | 0.28852 | 1 | 0.72632 | 0.20956 | Medium | Low | Low | 517 | 314 | 0.28852
ROSSMOOR 1106 | DIABLO | 4.0278 | 131.4697 | 2771.5 | 19.11% | 34.23% | 0 | 0.071194 | 1 | 2.9421 | 0.20946 | Low | Low | High | 518 | 613 | 0.071194
KIRKER 2104 | DIABLO | 5.4258 | 48.97 | 944.5 | 28.13% | 0% | 0 | 0.095285 | 1 | 2.1972 | 0.20936 | Low | Low | Medium | 519 | 555 | 0.095285
TIDEWATER 2106 | DIABLO | 8.1253 | 1.26 | 42 | 24.38% | 0% | 0 | 0.088717 | 1 | 2.3405 | 0.20764 | Low | Low | Medium | 520 | 572 | 0.088717
JARVIS 1108 | MISSION | 2.1719 | 39.8668 | 748 | 11.58% | 0% | 0 | 0.072228 | 1 | 2.8739 | 0.20757 | Low | Low | High | 521 | 609 | 0.072228
MARTELL 1102 | STOCKTON | 8.6112 | 263.8696 | 3200 | 71.01% | 0% | 0 | 0.088743 | 1 | 2.3343 | 0.20715 | Low | Low | Medium | 522 | 571 | 0.088743
LOS GATOS 1102 | DE ANZA | 1.1034 | 103.8413 | 635 | 18.04% | 0% | 0 | 0.067648 | 1 | 3.0578 | 0.20686 | Low | Low | High | 523 | 620 | 0.067648
MORGAN HILL 2104 | SAN JOSE | 4.9492 | 65.5542 | 1382 | 23.48% | 0% | 0 | 0.11704 | 1 | 1.7652 | 0.2066 | Medium | Low | Medium | 524 | 497 | 0.11704
OAKLAND J 1106 | EAST BAY | 1.9819 | 31.0726 | 613 | 10.05% | 0% | 0 | 0.081922 | 1 | 2.5071 | 0.20539 | Low | Low | High | 525 | 583 | 0.081922
OAKLAND K 1101 | EAST BAY | 2.7602 | 98.8794 | 720 | 37.91% | 65.54% | 0 | 0.075188 | 1 | 2.6645 | 0.20034 | Low | Low | High | 526 | 597 | 0.075188
CASTRO VALLEY 1101 | MISSION | 2.976 | 55.911 | 1242.6 | 13.39% | 0% | 0 | 0.072256 | 1 | 2.7708 | 0.2002 | Low | Low | High | 527 | 608 | 0.072256
SARATOGA 1103 | DE ANZA | 4.2157 | 183.5114 | 1906.5 | 40.58% | 0% | 0 | 0.071804 | 1 | 2.7531 | 0.19768 | Low | Low | High | 528 | 611 | 0.071804
HICKS 2101 | SAN JOSE | 11.134 | 65.1711 | 2767.7 | 26.22% | 17.93% | 0 | 0.11737 | 1 | 1.6776 | 0.19691 | Medium | Low | Medium | 529 | 496 | 0.11737
NOVATO 1104 | NORTH BAY | 4.2213 | 51.7699 | 1264.2 | 17.29% | 0% | 0 | 0.080358 | 1 | 2.4233 | 0.19473 | Low | Low | High | 530 | 587 | 0.080358
LLAGAS 2107 | SAN JOSE | 7.8323 | 69.5229 | 1556.5 | 34.98% | 39.23% | 0 | 0.11554 | 1 | 1.672 | 0.19317 | Medium | Low | Medium | 531 | 499 | 0.11554
BUTTE 1105 | NORTH VALLEY | 1.8432 | 87.173 | 1304.5 | 12.32% | 0% | 0 | 0.084537 | 1 | 2.2799 | 0.19273 | Low | Low | Medium | 532 | 579 | 0.084537
FLORENCE 0401 | EAST BAY | 1.7158 | 140.8044 | 604.6 | 39.96% | 0% | 0 | 0.06431 | 1 | 2.9373 | 0.1889 | Low | Low | High | 533 | 631 | 0.06431
LAKEWOOD 2109 | DIABLO | 0.21818 | 138.8407 | 999.5 | 3.031% | 100% | 0 | 0.056491 | 1 | 3.3292 | 0.18807 | Low | Low | High | 534 | 650 | 0.056491
VIEJO 2204 | CENTRAL COAST | 3.9584 | 200.1178 | 4925 | 16.08% | 0% | 0 | 0.07302 | 1 | 2.5741 | 0.18796 | Low | Low | High | 535 | 605 | 0.07302
JOLON 1102 | CENTRAL COAST | 66.2788 | 0.018962 | 2 | 62.84% | 0% | 0 | 0.20003 | 1 | 0.93912 | 0.18785 | Medium | Low | Low | 536 | 391 | 0.20003
PAUL SWEET 2102 | CENTRAL COAST | 5.198 | 260.6733 | 4746.6 | 28.55% | 80.79% | 0 | 0.064706 | 1 | 2.9017 | 0.18776 | Low | Low | High | 537 | 630 | 0.064706
EL CERRITO G 1108 | EAST BAY | 0.57918 | 52.4668 | 756 | 4.02% | 0% | 0 | 0.048895 | 1 | 3.8114 | 0.18636 | Low | Low | High | 538 | 667 | 0.048895
SAN LEANDRO U 1107 | MISSION | 0.061986 | 25.3999 | 381.1 | 0.4131% | 0% | 0 | 0.091216 | 1 | 2.0325 | 0.1854 | Low | Low | Medium | 539 | 565 | 0.091216
OAKLAND J 1105 | EAST BAY | 3.7186 | 38.6359 | 904.4 | 15.89% | 0% | 0 | 0.069116 | 1 | 2.6711 | 0.18462 | Low | Low | High | 540 | 618 | 0.069116
ECHO SUMMIT 1101 | xx | 6.1677 | 89.7501 | 1320 | 41.94% | 0% | 0 | 0.17692 | 1 | 1.0356 | 0.18321 | Medium | Low | Low | 541 | 419 | 0.17692
MONROE 2107 | SONOMA | 0.75479 | 28.657 | 308.2 | 7.018% | 100% | 0 | 0.098586 | 1 | 1.8538 | 0.18275 | Low | Low | Medium | 542 | 546 | 0.098586
MONROE 2103 | SONOMA | 1.4327 | 24.5777 | 432.6 | 8.14% | 100% | 0 | 0.09636 | 1 | 1.8837 | 0.18151 | Low | Low | Medium | 543 | 553 | 0.09636
FRANKLIN 1101 | EAST BAY | 1.5325 | 0.31796 | 3 | 16.24% | 0% | 0 | 0.072128 | 1 | 2.5025 | 0.1805 | Low | Low | High | 544 | 610 | 0.072128
OCEANO 1103 | LOS PADRES | 1.291 | 64.1861 | 733.5 | 11.3% | 0% | 0 | 0.086198 | 1 | 2.093 | 0.18041 | Low | Low | Medium | 545 | 576 | 0.086198
ANDERSON 1103 | NORTH VALLEY | 5.8182 | 84.3714 | 2668.5 | 18.4% | 0% | 0 | 0.10874 | 1 | 1.6553 | 0.18 | Low | Low | Low | 546 | 514 | 0.10874
SALT SPRINGS 2101 | STOCKTON | 16.764 | 106.976 | 2344.4 | 76.49% | 0% | 0 | 0.26125 | 1 | 0.68887 | 0.17997 | Medium | Low | Low | 547 | 336 | 0.26125
BERKELEY F 0402 | EAST BAY | 0.47631 | 102.5882 | 218 | 22.41% | 0% | 0 | 0.05592 | 1 | 3.1937 | 0.17859 | Low | Low | High | 548 | 652 | 0.05592
MORGAN HILL 2109 | SAN JOSE | 1.7684 | 37.4103 | 998.2 | 6.628% | 0% | 0 | 0.10014 | 1 | 1.7654 | 0.17679 | Low | Low | Medium | 549 | 540 | 0.10014
IGNACIO 1101 | NORTH BAY | 5.4039 | 248.3226 | 3068.1 | 43.74% | 11.33% | 0 | 0.058178 | 1 | 3.0082 | 0.17501 | Low | Low | High | 550 | 646 | 0.058178
SAN MIGUEL 1104 | LOS PADRES | 25.5295 | 7.7017 | 1102.6 | 17.83% | 0% | 0 | 0.13821 | 1 | 1.2642 | 0.17473 | Medium | Low | Low | 551 | 456 | 0.13821
BAY MEADOWS 2102 | PENINSULA | 4.2519 | 111.0862 | 1584.9 | 29.8% | 0% | 0 | 0.074656 | 1 | 2.337 | 0.17447 | Low | Low | Medium | 552 | 598 | 0.074656
MORRO BAY 1101 | LOS PADRES | 6.3279 | 64.6413 | 2970.7 | 13.77% | 10.63% | 0 | 0.076002 | 1 | 2.2858 | 0.17372 | Low | Low | Medium | 553 | 593 | 0.076002
SAN RAFAEL 1106 | NORTH BAY | 2.8567 | 156.7324 | 3281.6 | 13.64% | 0% | 0 | 0.048872 | 1 | 3.5064 | 0.17137 | Low | Low | High | 554 | 668 | 0.048872
JESSUP 1103 | NORTH VALLEY | 3.7231 | 134.3412 | 5113.2 | 9.782% | 0% | 0 | 0.10265 | 1 | 1.6574 | 0.17012 | Low | Low | Low | 555 | 529 | 0.10265
RED BLUFF 1105 | NORTH VALLEY | 15.2954 | 41.808 | 1578 | 40.52% | 0% | 0 | 0.16165 | 1 | 1.0496 | 0.16967 | Medium | Low | Low | 556 | 434 | 0.16165
VINEYARD 2107 | MISSION | 1.7807 | 64.4641 | 883.5 | 12.99% | 0% | 0 | 0.074528 | 1 | 2.2733 | 0.16942 | Low | Low | Medium | 557 | 599 | 0.074528
ZACA 1101 | LOS PADRES | 18.6848 | 28.6781 | 743 | 72.12% | 7.874% | 0 | 0.19189 | 1 | 0.87943 | 0.16876 | Medium | Low | Low | 558 | 402 | 0.19189
BRIDGEVILLE 1102 | HUMBOLDT | 33.3457 | 109.1054 | 5095.2 | 71.4% | 64.9% | 0 | 0.37184 | 1 | 0.44802 | 0.16659 | High | Low | Low | 559 | 259 | 0.37184
PACIFICA 1104 | PENINSULA | 0.50255 | 0.27895 | 2 | 7.009% | 0% | 0 | 0.06234 | 1 | 2.6655 | 0.16617 | Low | Low | High | 560 | 636 | 0.06234
SARATOGA 1104 | DE ANZA | 1.7714 | 181.8242 | 3279.2 | 9.822% | 0% | 0 | 0.051455 | 1 | 3.2268 | 0.16604 | Low | Low | High | 561 | 662 | 0.051455
DIVIDE 1103 | LOS PADRES | 2.2423 | 26.329 | 537 | 10.99% | 0% | 0 | 0.07382 | 1 | 2.2453 | 0.16575 | Low | Low | Medium | 562 | 602 | 0.07382
WOOD 0401 | EAST BAY | 0.4018 | 105.8273 | 352.5 | 12.06% | 0% | 0 | 0.055516 | 1 | 2.9705 | 0.16491 | Low | Low | High | 563 | 654 | 0.055516
ALTO 1123 | NORTH BAY | 2.3955 | 75.8605 | 1564.6 | 11.61% | 4.121% | 0 | 0.054202 | 1 | 3.0362 | 0.16457 | Low | Low | High | 564 | 657 | 0.054202
TULE POWER HOUSE 1101 | FRESNO | 4.0927 | 126.3618 | 517.3 | 99.97% | 0% | 0 | 0.14702 | 1 | 1.0868 | 0.15979 | Medium | Low | Low | 565 | 451 | 0.14702
OAKHURST 1102 | YOSEMITE | 11.3331 | 352.2874 | 5880.1 | 67.9% | 11.35% | 1 | 0.094676 | 1 | 1.6857 | 0.1596 | Low | Low | Medium | 566 | 557 | 0.094676
POSO MOUNTAIN 2101 | KERN | 49.4434 | 6.8941 | 413 | 82.53% | 0% | 1 | 0.25701 | 1 | 0.61759 | 0.15873 | Medium | Low | Low | 567 | 337 | 0.25701
PEABODY 2106 | SACRAMENTO | 0.58049 | 41.6388 | 112 | 21.58% | 0% | 0 | 0.08699 | 1 | 1.7615 | 0.15323 | Low | Low | Medium | 568 | 574 | 0.08699
MORGAN HILL 2110 | SAN JOSE | 2.054 | 25.1241 | 826.3 | 6.245% | 0% | 0 | 0.084977 | 1 | 1.7964 | 0.15265 | Low | Low | Medium | 569 | 577 | 0.084977
CASTRO VALLEY 1104 | MISSION | 3.6017 | 32.9628 | 916.5 | 12.95% | 0% | 0 | 0.067374 | 1 | 2.2554 | 0.15196 | Low | Low | Medium | 570 | 621 | 0.067374
BUCKS CREEK 1102 | NORTH VALLEY | 29.5609 | 41.7418 | 1233.7 | 100% | 23.04% | 0 | 0.30696 | 1 | 0.49433 | 0.15174 | High | Low | Low | 571 | 303 | 0.30696
ARLINGTON 0401 | EAST BAY | 0.76473 | 112.5678 | 446.5 | 19.28% | 0% | 0 | 0.044083 | 1 | 3.4267 | 0.15106 | Low | Low | High | 572 | 676 | 0.044083
STELLING 1109 | DE ANZA | 0.52786 | 116.8956 | 1926.1 | 3.204% | 0% | 0 | 0.061968 | 1 | 2.4341 | 0.15084 | Low | Low | High | 573 | 637 | 0.061968
OROVILLE 1104 | NORTH VALLEY | 0.2392 | 56.2036 | 556.5 | 2.416% | 0% | 0 | 0.056784 | 1 | 2.6537 | 0.15069 | Low | Low | High | 574 | 649 | 0.056784
MC KEE 1111 | SAN JOSE | 8.3733 | 46.2158 | 1247.3 | 31.03% | 0% | 0 | 0.11942 | 1 | 1.2586 | 0.15031 | Medium | Low | Low | 575 | 487 | 0.11942
OAKLAND J 1118 | EAST BAY | 0.38627 | 16.6579 | 196.5 | 3.275% | 0% | 0 | 0.067359 | 1 | 2.2214 | 0.14963 | Low | Low | Medium | 576 | 622 | 0.067359
CORONA 1103 | SONOMA | 0.968 | 36.1818 | 623.8 | 5.615% | 0% | 0 | 0.087372 | 1 | 1.711 | 0.14949 | Low | Low | Medium | 577 | 573 | 0.087372
MONTEREY 0402 | CENTRAL COAST | 0.7655 | 61.7929 | 241.4 | 19.59% | 0% | 0 | 0.058548 | 1 | 2.553 | 0.14947 | Low | Low | High | 578 | 645 | 0.058548
PIT NO 1 1101 | NORTH VALLEY | 25.7108 | 31.6065 | 1677.5 | 48.44% | 0% | 0 | 0.19615 | 1 | 0.75692 | 0.14847 | Medium | Low | Low | 579 | 396 | 0.19615
BAYWOOD 1101 | LOS PADRES | 1.4233 | 61.3561 | 1783.1 | 4.897% | 0% | 0 | 0.06584 | 1 | 2.2327 | 0.147 | Low | Low | Medium | 580 | 628 | 0.06584
AUBURN 1102 | SIERRA | 2.2817 | 92.0082 | 812 | 25.85% | 0% | 0 | 0.066602 | 1 | 2.193 | 0.14606 | Low | Low | Medium | 581 | 625 | 0.066602
SAN LUIS OBISPO 1105 | LOS PADRES | 1.9887 | 111.0125 | 1301 | 16.97% | 0% | 0 | 0.06651 | 1 | 2.1947 | 0.14597 | Low | Low | Medium | 582 | 626 | 0.06651
EAST MARYSVILLE 1108 | SIERRA | 0.35809 | 22.6124 | 1522.8 | 0.5317% | 0% | 0 | 0.10377 | 1 | 1.4017 | 0.14545 | Low | Low | Low | 583 | 525 | 0.10377
SYCAMORE CREEK 1109 | NORTH VALLEY | 0.58228 | 131.795 | 1758 | 4.365% | 0% | 0 | 0.064735 | 1 | 2.2449 | 0.14532 | Low | Low | Medium | 584 | 629 | 0.064735
TASSAJARA 2103 | DIABLO | 1.7119 | 125.7307 | 2473.5 | 8.702% | 35.07% | 0 | 0.046769 | 1 | 3.1066 | 0.1453 | Low | Low | High | 585 | 671 | 0.046769
TEMPLETON 2112 | LOS PADRES | 2.5848 | 16.2347 | 613 | 6.845% | 0% | 0 | 0.101 | 1 | 1.4381 | 0.14525 | Low | Low | Low | 586 | 535 | 0.101
LAKEWOOD 2224 | DIABLO | 0.72014 | 122.1338 | 2970 | 2.961% | 100% | 0 | 0.0494 | 1 | 2.9387 | 0.14517 | Low | Low | High | 587 | 665 | 0.0494
OAKLAND J 1116 | EAST BAY | 0.031861 | 22.9977 | 429.5 | 0.1706% | 0% | 0 | 0.051875 | 1 | 2.7948 | 0.14498 | Low | Low | High | 588 | 661 | 0.051875
OCEANO 1105 | LOS PADRES | 3.6627 | 45.7122 | 1133 | 14.78% | 0% | 0 | 0.063148 | 1 | 2.2953 | 0.14494 | Low | Low | Medium | 589 | 634 | 0.063148
DRUM 1101 | SIERRA | 18.8373 | 140.8712 | 2654 | 99.99% | 100% | 0 | 0.31704 | 1 | 0.45622 | 0.14464 | High | Low | Low | 590 | 296 | 0.31704
LAS GALLINAS A 1104 | NORTH BAY | 1.1639 | 140.8806 | 1822.6 | 8.996% | 0% | 0 | 0.041798 | 1 | 3.4288 | 0.14332 | Low | Low | High | 591 | 678 | 0.041798
LLAGAS 2104 | SAN JOSE | 1.6348 | 32.5627 | 979.5 | 5.435% | 0% | 0 | 0.10085 | 1 | 1.4196 | 0.14318 | Low | Low | Low | 592 | 537 | 0.10085
NEWBURG 1131 | HUMBOLDT | 6.672 | 10.1068 | 399 | 16.9% | 0% | 0 | 0.10164 | 1 | 1.4078 | 0.14308 | Low | Low | Low | 593 | 533 | 0.10164
VASONA 1102 | DE ANZA | 0.06716 | 101.8373 | 1570.3 | 0.4355% | 0% | 0 | 0.038682 | 1 | 3.6689 | 0.14192 | Low | Low | High | 594 | 681 | 0.038682
GREENBRAE 1104 | NORTH BAY | 0.079918 | 41.4788 | 757.1 | 0.4378% | 0% | 0 | 0.048912 | 1 | 2.8879 | 0.14125 | Low | Low | High | 595 | 666 | 0.048912
WOODWARD 2108 | FRESNO | 30.1544 | 19.2531 | 1994 | 29.12% | 0% | 0 | 0.16813 | 1 | 0.83522 | 0.14042 | Medium | Low | Low | 596 | 427 | 0.16813
TEJON 1103 | KERN | 2.7582 | 0.046004 | 2 | 6.344% | 0% | 0 | 0.10915 | 1 | 1.2829 | 0.14003 | Low | Low | Low | 597 | 511 | 0.10915
RINCON 1104 | SONOMA | 2.6764 | 69.3638 | 835.3 | 22.23% | 77.17% | 0 | 0.075816 | 1 | 1.8389 | 0.13942 | Low | Low | Medium | 598 | 595 | 0.075816
ESTUDILLO 0401 | MISSION | 0.69789 | 24.7934 | 117 | 14.79% | 0% | 0 | 0.073357 | 1 | 1.8893 | 0.1386 | Low | Low | Medium | 599 | 604 | 0.073357
SNEATH LANE 1101 | PENINSULA | 2.4892 | 147.801 | 1391 | 26.45% | 0% | 0 | 0.056375 | 1 | 2.4318 | 0.13709 | Low | Low | High | 600 | 651 | 0.056375
OAKLAND X 1101 | EAST BAY | 0.53647 | 122.1199 | 644.5 | 10.17% | 0% | 0 | 0.045316 | 1 | 2.9835 | 0.1352 | Low | Low | High | 601 | 674 | 0.045316
TULUCAY 1101 | NORTH BAY | 4.4167 | 81.0638 | 1556.4 | 23% | 0% | 0 | 0.07244 | 1 | 1.8524 | 0.13419 | Low | Low | Medium | 602 | 607 | 0.07244
WESTLEY 1103 | YOSEMITE | 0.92376 | 11.6299 | 1127 | 0.9533% | 0% | 0 | 0.10608 | 1 | 1.2637 | 0.13405 | Low | Low | Low | 603 | 517 | 0.10608
PIT NO 5 1101 | NORTH VALLEY | 23.7942 | 87.3832 | 2066.5 | 100% | 0% | 1 | 0.37222 | 1 | 0.35683 | 0.13282 | High | Low | Low | 604 | 258 | 0.37222
RINCON 1102 | SONOMA | 3.5536 | 62.5648 | 1236.9 | 17.97% | 7.097% | 1 | 0.07654 | 1 | 1.7248 | 0.13202 | Low | Low | Medium | 605 | 592 | 0.07654
JARVIS 1111 | MISSION | 1.1185 | 51.7293 | 995.5 | 5.812% | 100% | 0 | 0.053741 | 1 | 2.4441 | 0.13135 | Low | Low | High | 606 | 658 | 0.053741
WOODSIDE 1102 | PENINSULA | 0.10582 | 135.7016 | 2319.1 | 0.6192% | 0% | 0 | 0.03505 | 1 | 3.7245 | 0.13054 | Low | Low | High | 607 | 683 | 0.03505
WILLITS 1102 | HUMBOLDT | 5.2584 | 82.94 | 931.4 | 46.83% | 0% | 0 | 0.097209 | 1 | 1.3417 | 0.13043 | Low | Low | Low | 608 | 552 | 0.097209
EDENVALE 2107 | SAN JOSE | 0.76864 | 12.2993 | 451 | 2.096% | 0% | 0 | 0.097415 | 1 | 1.3381 | 0.13035 | Low | Low | Low | 609 | 550 | 0.097415
HARTLEY 1102 | HUMBOLDT | 4.13 | 61.8764 | 1709.2 | 14.95% | 0% | 0 | 0.086633 | 1 | 1.4904 | 0.12911 | Low | Low | Low | 610 | 575 | 0.086633
SNEATH LANE 1106 | PENINSULA | 1.101 | 134.6382 | 1541.5 | 9.617% | 0% | 0 | 0.054926 | 1 | 2.3506 | 0.12911 | Low | Low | Medium | 611 | 655 | 0.054926
FITCH MOUNTAIN 1111 | SONOMA | 2.7214 | 0.49011 | 15 | 8.892% | 0% | 0 | 0.081834 | 1 | 1.5662 | 0.12817 | Low | Low | Low | 612 | 584 | 0.081834
CALPELLA 1102 | HUMBOLDT | 5.8421 | 60.5445 | 1573.2 | 22.48% | 0% | 1 | 0.1146 | 1 | 1.1094 | 0.12713 | Medium | Low | Low | 613 | 502 | 0.1146
GOLDTREE 1108 | LOS PADRES | 2.5563 | 123.4945 | 1809.8 | 17.44% | 0% | 0 | 0.059088 | 1 | 2.1453 | 0.12676 | Low | Low | Medium | 614 | 643 | 0.059088
MC KEE 1108 | SAN JOSE | 1.0836 | 60.3492 | 632.2 | 10.34% | 0% | 0 | 0.091388 | 1 | 1.3857 | 0.12664 | Low | Low | Low | 615 | 564 | 0.091388
LLAGAS 2106 | SAN JOSE | 1.5959 | 27.4852 | 909 | 4.825% | 0% | 0 | 0.10177 | 1 | 1.2297 | 0.12515 | Low | Low | Low | 616 | 531 | 0.10177
PACIFIC GROVE 0422 | CENTRAL COAST | 0.61996 | 84.4855 | 586 | 8.938% | 0% | 0 | 0.045387 | 1 | 2.7492 | 0.12478 | Low | Low | High | 617 | 673 | 0.045387
LLAGAS 2105 | SAN JOSE | 0.40589 | 48.4729 | 901 | 2.184% | 0% | 0 | 0.074274 | 1 | 1.6756 | 0.12445 | Low | Low | Medium | 618 | 601 | 0.074274
AUBURN 1101 | SIERRA | 3.1166 | 253.2817 | 1242.6 | 63.53% | 0% | 0 | 0.054328 | 1 | 2.2625 | 0.12292 | Low | Low | Medium | 619 | 656 | 0.054328
SONOMA 1107 | SONOMA | 2.3737 | 0.78936 | 41 | 4.57% | 0% | 0 | 0.072608 | 1 | 1.6698 | 0.12124 | Low | Low | Medium | 620 | 606 | 0.072608
MC KEE 1107 | SAN JOSE | 2.6945 | 49.4006 | 1880 | 7.08% | 0% | 0 | 0.093763 | 1 | 1.2862 | 0.1206 | Low | Low | Low | 621 | 559 | 0.093763
ALTO 1120 | NORTH BAY | 2.2169 | 197.8696 | 3705.9 | 11.84% | 0% | 0 | 0.03938 | 1 | 3.0547 | 0.12029 | Low | Low | High | 622 | 680 | 0.03938
BURNEY 1102 | NORTH VALLEY | 0.71383 | 41.7807 | 168 | 17.75% | 0% | 0 | 0.089873 | 1 | 1.3275 | 0.1193 | Low | Low | Low | 623 | 569 | 0.089873
PLACER 1104 | SIERRA | 1.3434 | 89.4281 | 1228 | 9.783% | 0% | 0 | 0.05272 | 1 | 2.2618 | 0.11924 | Low | Low | Medium | 624 | 659 | 0.05272
ALTO 1121 | NORTH BAY | 0.013093 | 76.5651 | 663 | 0.1512% | 0% | 0 | 0.040029 | 1 | 2.9783 | 0.11922 | Low | Low | High | 625 | 679 | 0.040029
GREENBRAE 1103 | NORTH BAY | 5.1674 | 390.2998 | 5709.5 | 35.32% | 45.87% | 0 | 0.032461 | 1 | 3.627 | 0.11774 | Low | Low | High | 626 | 684 | 0.032461
OCEANO 1106 | LOS PADRES | 1.8831 | 156.8283 | 5341.1 | 5.529% | 0% | 0 | 0.052641 | 1 | 2.2321 | 0.1175 | Low | Low | Medium | 627 | 660 | 0.052641
WILLOW PASS 2108 | DIABLO | 0.047227 | 1.9853 | 36 | 0.2604% | 0% | 0 | 0.05568 | 1 | 2.1011 | 0.11699 | Low | Low | Medium | 628 | 653 | 0.05568
LAKEWOOD 1102 | DIABLO | 0.47236 | 89.9728 | 863.1 | 4.924% | 0% | 0 | 0.045836 | 1 | 2.5521 | 0.11698 | Low | Low | High | 629 | 672 | 0.045836
BANCROFT 0402 | EAST BAY | 1.0716 | 53.641 | 245 | 23.46% | 0% | 0 | 0.063524 | 1 | 1.8404 | 0.11691 | Low | Low | Medium | 630 | 633 | 0.063524
BERESFORD 0403 | PENINSULA | 4.1458 | 234.4513 | 2838.9 | 34.24% | 0% | 0 | 0.049683 | 1 | 2.3346 | 0.11599 | Low | Low | Medium | 631 | 664 | 0.049683
REEDLEY 1104 | FRESNO | 1.9028 | 5.211 | 625.1 | 1.586% | 0% | 0 | 0.10427 | 1 | 1.0862 | 0.11325 | Low | Low | Low | 632 | 524 | 0.10427
TEMPLETON 2108 | LOS PADRES | 2.5794 | 242.7456 | 8795.5 | 7.119% | 0% | 0 | 0.059186 | 1 | 1.8973 | 0.11229 | Low | Low | Medium | 633 | 642 | 0.059186
SAN BERNARD 1101 | KERN | 0.91753 | 39.6888 | 1758 | 2.071% | 0% | 0 | 0.099863 | 1 | 1.1206 | 0.11191 | Low | Low | Low | 634 | 542 | 0.099863
RADUM 1105 | MISSION | 2.1702 | 211.3073 | 2499.3 | 18.35% | 37.28% | 0 | 0.047243 | 1 | 2.3277 | 0.10997 | Low | Low | Medium | 635 | 670 | 0.047243
MONTEREY 0401 | CENTRAL COAST | 0.26645 | 75.7453 | 373 | 5.411% | 0% | 0 | 0.042472 | 1 | 2.5698 | 0.10914 | Low | Low | High | 636 | 677 | 0.042472
ALHAMBRA 1102 | DIABLO | 0.24414 | 57.5853 | 812.5 | 1.73% | 0% | 0 | 0.048128 | 1 | 2.1796 | 0.1049 | Low | Low | Medium | 637 | 669 | 0.048128
SO. CAL. EDISON #2 1101 | YOSEMITE | 1.1766 | 0 | 10 | 0% | 37.67% | 0 | 0.099229 | 1 | 1.0317 | 0.10237 | Low | Low | Low | 638 | 545 | 0.099229
CAYUCOS 1101 | LOS PADRES | 2.0954 | 62.8302 | 2897 | 4.545% | 0% | 0 | 0.071036 | 1 | 1.4406 | 0.10233 | Low | Low | Low | 639 | 615 | 0.071036
ROSSMOOR 1104 | DIABLO | 0.24893 | 134.119 | 2611.9 | 1.278% | 0% | 0 | 0.036855 | 1 | 2.749 | 0.10132 | Low | Low | High | 640 | 682 | 0.036855
GLENN 1101 | NORTH VALLEY | 2.3498 | 17.4579 | 2361 | 1.737% | 0% | 0 | 0.11765 | 1 | 0.82835 | 0.097452 | Medium | Low | Low | 641 | 494 | 0.11765
FORT BRAGG A 1103 | HUMBOLDT | 0.37656 | 35.7437 | 95.5 | 14.09% | 0% | 0 | 0.058574 | 1 | 1.6248 | 0.095172 | Low | Low | Low | 642 | 644 | 0.058574
BRENTWOOD 2105 | DIABLO | 9.8403 | 32.0715 | 2821 | 11.19% | 0% | 0 | 0.11866 | 1 | 0.79064 | 0.093818 | Medium | Low | Low | 643 | 491 | 0.11866
MC KEE 1103 | SAN JOSE | 2.8083 | 59.3192 | 1308 | 12.74% | 0% | 0 | 0.062858 | 1 | 1.449 | 0.091084 | Low | Low | Low | 644 | 635 | 0.062858
SWIFT 2107 | SAN JOSE | 2.6821 | 54.8728 | 659 | 22.33% | 0% | 0 | 0.08203 | 1 | 1.0702 | 0.087785 | Low | Low | Low | 645 | 582 | 0.08203
NEWBURG 1133 | HUMBOLDT | 3.7712 | 114.96 | 1933.5 | 22.42% | 0% | 0 | 0.071452 | 1 | 1.1791 | 0.084247 | Low | Low | Low | 646 | 612 | 0.071452
SAUSALITO 1101 | NORTH BAY | 0.58117 | 157.5989 | 1070.9 | 8.553% | 0% | 0 | 0.032166 | 1 | 2.5729 | 0.08276 | Low | Low | High | 647 | 686 | 0.032166
SANTA YNEZ 1102 | LOS PADRES | 6.558 | 324.4663 | 6258.5 | 34% | 0% | 0 | 0.057906 | 1 | 1.3121 | 0.07598 | Low | Low | Low | 648 | 648 | 0.057906
ELK CREEK 1101 | NORTH VALLEY | 82.7232 | 10.5621 | 1916 | 45.6% | 0% | 0 | 0.21711 | 1 | 0.34119 | 0.074075 | Medium | Low | Low | 649 | 373 | 0.21711
SNEATH LANE 1102 | PENINSULA | 0.30787 | 146.875 | 1546.3 | 2.924% | 0% | 0 | 0.032278 | 1 | 2.2678 | 0.073201 | Low | Low | Medium | 650 | 685 | 0.032278
SWIFT 2109 | SAN JOSE | 0.30955 | 52.0533 | 280 | 5.755% | 0% | 0 | 0.059782 | 1 | 1.1399 | 0.068145 | Low | Low | Low | 651 | 641 | 0.059782
CARMEL 0405 | CENTRAL COAST | 0.33684 | 180.2265 | 1052 | 5.771% | 0% | 0 | 0.026235 | 1 | 2.4979 | 0.065534 | Low | Low | High | 652 | 688 | 0.026235
REEDLEY 1112 | FRESNO | 0.0028032 | 9.4725 | 852.5 | 0.003115% | 0% | 0 | 0.058029 | 1 | 1.1037 | 0.064046 | Low | Low | Low | 653 | 647 | 0.058029
COPPERMINE 1104 | FRESNO | 8.1519 | 24.5997 | 2161 | 9.28% | 0% | 0 | 0.12252 | 1 | 0.48792 | 0.059782 | Medium | Low | Low | 654 | 477 | 0.12252
PLACER 1101 | SIERRA | 0.77573 | 233.8154 | 1771.9 | 10.24% | 0% | 0 | 0.023381 | 1 | 2.3548 | 0.055058 | Low | Low | Medium | 655 | 689 | 0.023381
CAMPHORA 1101 | CENTRAL COAST | 1.4665 | 0.11504 | 5 | 3.374% | 0% | 0 | 0.10435 | 1 | 0.51261 | 0.053489 | Low | Low | Low | 656 | 523 | 0.10435
GRASS VALLEY 1101 | SIERRA | 17.394 | 833.7564 | 15666.7 | 92.57% | 14.84% | 1 | 0.026844 | 1 | 1.9915 | 0.05346 | Low | Low | Medium | 657 | 687 | 0.026844
RED BLUFF 1103 | NORTH VALLEY | 15.929 | 13.8952 | 526.5 | 42.04% | 0% | 1 | 0.18556 | 1 | 0.26903 | 0.04992 | Medium | Low | Low | 658 | 409 | 0.18556
POTTER VALLEY PH 1105 | HUMBOLDT | 0.0052407 | 78.6372 | 5732 | 0.00719% | 0% | 0 | 0.066957 | 1 | 0.64735 | 0.043345 | Low | Low | Low | 659 | 624 | 0.066957
SISQUOC 1102 | LOS PADRES | 48.4935 | 11.2634 | 1326.5 | 41.18% | 65.24% | 0 | 0.15775 | 1 | 0.2606 | 0.041108 | Medium | Low | Low | 660 | 438 | 0.15775
GONZALES 1103 | CENTRAL COAST | 1.0413 | 25.8595 | 560 | 4.808% | 0% | 0 | 0.074278 | 1 | 0.55053 | 0.040892 | Low | Low | Low | 661 | 600 | 0.074278
COVELO 1101 | HUMBOLDT | 9.9189 | 6.0057 | 675.5 | 8.819% | 0% | 1 | 0.14085 | 1 | 0.27513 | 0.038751 | Medium | Low | Low | 662 | 454 | 0.14085
SOLEDAD 1114 | CENTRAL COAST | 0.90872 | 104.7796 | 1950.2 | 4.882% | 0% | 0 | 0.044957 | 1 | 0.75791 | 0.034073 | Low | Low | Low | 663 | 675 | 0.044957
LOS COCHES 1101 | CENTRAL COAST | 2.6219 | 149.6639 | 4542 | 8.639% | 0% | 0 | 0.050557 | 1 | 0.66337 | 0.033538 | Low | Low | Low | 664 | 663 | 0.050557
CLAY 1102 | STOCKTON | 1.1664 | 433.7192 | 895.5 | 56.49% | 0% | 0 | 0.015108 | 1 | 2.1257 | 0.032116 | Low | Low | Medium | 665 | 690 | 0.015108
OROSI 1102 | FRESNO | 0.26307 | 6.3215 | 221 | 0.7525% | 0% | 0 | 0.099308 | 1 | 0.31434 | 0.031216 | Low | Low | Low | 666 | 544 | 0.099308
DIAMOND SPRINGS 1104 | SIERRA | 14.2466 | 902.6983 | 16914.4 | 76.03% | 61.8% | 0 | 0.013622 | 1 | 2.013 | 0.027421 | Low | Low | Medium | 667 | 691 | 0.013622
CARMEL 0402 | CENTRAL COAST | 0.30828 | 437.2599 | 1343 | 10.04% | 0% | 0 | 0.0071403 | 1 | 2.5278 | 0.018049 | Low | Low | High | 668 | 692 | 0.0071403
MC ARTHUR 1102 | NORTH VALLEY | 0.91154 | 10.5192 | 316 | 3.034% | 0% | 0 | 0.10164 | 1 | 0.16368 | 0.016637 | Low | Low | Low | 669 | 532 | 0.10164
RAWSON 1103 | NORTH VALLEY | 2.3781 | 43.8034 | 1730.3 | 6.02% | 0% | 0 | 0.091986 | 1 | 0.16783 | 0.015438 | Low | Low | Low | 670 | 563 | 0.091986
EEL RIVER 1103 | HUMBOLDT | 2.3658 | 38.1115 | 2275.5 | 3.962% | 0% | 0 | 0.061664 | 1 | 0.16129 | 0.0099458 | Low | Low | Low | 671 | 638 | 0.061664
BRUNSWICK 1107 | SIERRA | 7.6934 | 1170.784 | 22715.2 | 39.65% | 25.27% | 1 | 0.0033153 | 1 | 2.1776 | 0.0072194 | Low | Low | Medium | 672 | 693 | 0.0033153
SPAULDING 1101 | SIERRA | 20.1063 | 68.9488 | 1688.7 | 82.09% | 8.84% | 1 | 0.24777 | 1 | 0.028551 | 0.0070739 | Medium | Low | Low | 673 | 348 | 0.24777
MC ARTHUR 1101 | NORTH VALLEY | 68.9373 | 20.8696 | 3705.5 | 38.83% | 0% | 0 | 0.21153 | 1 | 0.0054002 | 0.0011423 | Medium | Low | Low | 674 | 378 | 0.21153
HOLLISTER 2104 | CENTRAL COAST | 6.0574 | 25.3778 | 3075 | 4.999% | 0% | 0 | 0.12715 | 1 | 0.0080867 | 0.0010282 | Medium | Low | Low | 675 | 472 | 0.12715
FLINT 1102 | SIERRA | 0.092844 | 16120.6897 | 1496 | 100% | 0% | 0 | 2.2204e-16 | 1 | 2.2896 | 5.0839e-16 | Low | Low | Medium | 676 | 694 | 2.2204e-16
PLACERVILLE 1109 | SIERRA | 0.020146 | 22114.4279 | 444.5 | 100% | 0% | 0 | 2.2204e-16 | 1 | 1.7652 | 3.9196e-16 | Low | Low | Medium | 677 | 694 | 2.2204e-16
HIGGINS 1108 | SIERRA | 0.020411 | 627063.7255 | 12792.1 | 100% | 0% | 0 | 2.2204e-16 | 1 | 1.6813 | 3.7332e-16 | Low | Low | Medium | 678 | 694 | 2.2204e-16
GONZALES 1104 | CENTRAL COAST | 0.90277 | 0.074226 | 4 | 1.675% | 0% | 0 | 0.1017 | 47.6367 | 0 | 0 | Low | High | Low | 679 | 93 | 4.8445
CORTINA 1101 | SACRAMENTO | 1.036 | 11.8 | 902 | 1.355% | 0% | 0 | 0.1043 | 35.3263 | 0 | 0 | Low | High | Low | 679 | 100 | 3.6847
HOLLISTER 2105 | CENTRAL COAST | 61.272 | 46.1925 | 7314.4 | 38.69% | 0% | 1 | 0.25084 | 1 | 0 | 0 | Medium | Low | Low | 679 | 343 | 0.25084
MADISON 2101 | SACRAMENTO | 7.647 | 37.6304 | 6246.5 | 4.607% | 0% | 0 | 0.15967 | 1 | 0 | 0 | Medium | Low | Low | 679 | 437 | 0.15967
GONZALES 1101 | CENTRAL COAST | 3.5612 | 14.01 | 362 | 13.78% | 0% | 0 | 0.12168 | 1 | 0 | 0 | Medium | Low | Low | 679 | 478 | 0.12168
CAL WATER 1102 | KERN | 2.9688 | 22.0304 | 583 | 11.22% | 0% | 0 | 0.11156 | 1 | 0 | 0 | Low | Low | Low | 679 | 509 | 0.11156
LOS MOLINOS 1101 | NORTH VALLEY | 0.1275 | 17.4317 | 974 | 0.2282% | 0% | 0 | 0.10041 | 1 | 0 | 0 | Low | Low | Low | 679 | 538 | 0.10041
STONE CORRAL 1110 | FRESNO | 2.3189 | 12.2808 | 771.1 | 3.693% | 0% | 0 | 0.080627 | 1 | 0 | 0 | Low | Low | Low | 679 | 586 | 0.080627
SISQUOC 1103 | LOS PADRES | 27.7554 | 31.2985 | 1567 | 55.44% | 86.45% | 1 | 0.19534 | 1 | 0 | 0 | Medium | Low | Low | 679 | 398 | 0.19534
KERN OIL 1106 | KERN | 1.5124 | 22.8666 | 1025 | 3.374% | 0% | 0 | 0.067355 | 1 | 0 | 0 | Low | Low | Low | 679 | 623 | 0.067355
SPENCE 1123 | CENTRAL COAST | 2.0801 | 63.6257 | 2140 | 6.184% | 0% | 0 | 0.097986 | 1 | 0 | 0 | Low | Low | Low | 679 | 549 | 0.097986
CHOLAME 2102 | LOS PADRES | 58.4006 | 6.9776 | 1509 | 27% | 0% | 0 | 0.16972 | 1 | 0 | 0 | Medium | Low | Low | 679 | 426 | 0.16972
SPENCE 1122 | CENTRAL COAST | 9.9861 | 4.7822 | 251 | 19.03% | 0% | 0 | 0.098373 | 1 | 0 | 0 | Low | Low | Low | 679 | 547 | 0.098373
STONE CORRAL 1108 | FRESNO | 2.9159 | 7.9922 | 611 | 3.814% | 0% | 0 | 0.065911 | 1 | 0 | 0 | Low | Low | Low | 679 | 627 | 0.065911
LAMONT 1102 | KERN | 0.50063 | 0.98972 | 73 | 0.6787% | 0% | 0 | 0.10039 | 1 | 0 | 0 | Low | Low | Low | 679 | 539 | 0.10039
ANTELOPE 1101 | KERN | 0.75322 | 113.4018 | 4500 | 1.898% | 0% | 0 | 0.090369 | 1 | 0 | 0 | Low | Low | Low | 679 | 567 | 0.090369
CUYAMA 1103 | KERN | 2.3769 | 4.7667 | 377.5 | 3.001% | 0% | 0 | 0.10517 | 1 | 0 | 0 | Low | Low | Low | 679 | 521 | 0.10517
LOGAN CREEK 2102 | NORTH VALLEY | 3.7103 | 10.2135 | 2448.2 | 1.548% | 0% | 0 | 0.12256 | 1 | 0 | 0 | Medium | Low | Low | 679 | 476 | 0.12256

## Dx - SH
Dx Prioritization Output - System Hardening | [5 empty] | Planned 2019 implementation
Circuit Information |  |  |  | Independent Variables | [5 empty] | Dependent Variable | Risk Scoring |  |  |  |  | Risk Tiers
Protection Zone | Feeder Name | District | Tier 2/3 OH Miles | Env Risk Component | Material A - % of total miles | Vegetation Outages | Company Outages | HFTD Miles per Total Miles | Tier 3 per HFTD Miles | Ignition Indicator (1+ ignition occurred) | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Consolidated Risk Score | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Rank Cons Risk | Rank P*C | P*C
MIWUK 170110600 | MIWUK 1701 | YOSEMITE | 10.9092 | 90.0653 | 100% | 20 | 16 | 100% | 100% | 1 | 0.80002 | 102.1389 | 3.3891 | 276.9352 | High | High | High | 1 | 1 | 81.7128 | 22199.0735
MIWUK 1701CB | MIWUK 1701 | YOSEMITE | 17.9054 | 91.659 | 81.59% | 16 | 15 | 100% | 100% | 0 | 0.65411 | 102.1389 | 2.9532 | 197.3013 | High | High | Medium | 2 | 4 | 66.8104 | 21922.1383
ORO FINO 1101CB | ORO FINO 1101 | NORTH VALLEY | 22.1887 | 87.2953 | 86.14% | 9 | 11 | 100% | 100% | 0 | 0.48349 | 102.1389 | 3.5195 | 173.8066 | High | High | High | 3 | 14 | 49.3837 | 21724.837
STANISLAUS 17021888 | STANISLAUS 1702 | YOSEMITE | 18.9533 | 77.9476 | 99.71% | 9 | 14 | 100% | 100% | 0 | 0.44468 | 102.1389 | 2.9998 | 136.2467 | High | High | Medium | 4 | 19 | 45.4193 | 21551.0304
PINE GROVE 110245292 | PINE GROVE 1102 | STOCKTON | 10.8778 | 85.9329 | 100% | 1 | 11 | 100% | 99.38% | 0 | 0.44757 | 102.1389 | 2.8406 | 129.855 | High | High | Medium | 5 | 18 | 45.714 | 21414.7837
BRUNSWICK 11021010 | BRUNSWICK 1102 | SIERRA | 44.041 | 87.3695 | 84.93% | 12 | 13 | 100% | 98.91% | 0 | 0.59607 | 102.1389 | 2.1263 | 129.4525 | High | High | Low | 6 | 6 | 60.8822 | 21284.9287
BRUNSWICK 110350070 | BRUNSWICK 1103 | SIERRA | 28.1191 | 94.0552 | 99.83% | 13 | 12 | 100% | 100% | 1 | 0.54169 | 102.1389 | 2.325 | 128.6353 | High | High | Medium | 7 | 8 | 55.3273 | 21155.4761
SALT SPRINGS 21023142 | SALT SPRINGS 2102 | STOCKTON | 16.894 | 90.205 | 100% | 15 | 9 | 100% | 100% | 0 | 0.62396 | 102.1389 | 2.0116 | 128.2018 | High | High | Low | 8 | 5 | 63.7309 | 21026.8409
BRUNSWICK 110532536 | BRUNSWICK 1105 | SIERRA | 21.7333 | 94.8632 | 99.08% | 11 | 14 | 100% | 100% | 0 | 0.54536 | 102.1389 | 2.2664 | 126.2441 | High | High | Medium | 9 | 7 | 55.7026 | 20898.6391
ORO FINO 11012022 | ORO FINO 1101 | NORTH VALLEY | 24.1719 | 81.0032 | 94.33% | 6 | 13 | 100% | 100% | 1 | 0.36043 | 102.1389 | 3.4228 | 126.0056 | High | High | High | 10 | 35 | 36.814 | 20772.395
WYANDOTTE 11031974 | WYANDOTTE 1103 | NORTH VALLEY | 22.8741 | 92.9076 | 99.55% | 6 | 6 | 100% | 100% | 1 | 0.45135 | 102.1389 | 2.7281 | 125.7679 | High | High | Medium | 11 | 16 | 46.1001 | 20646.3894
MIWUK 17018060 | MIWUK 1701 | YOSEMITE | 11.8537 | 93.2164 | 72.89% | 5 | 17 | 100% | 100% | 0 | 0.41847 | 102.1389 | 2.916 | 124.6332 | High | High | Medium | 12 | 23 | 42.7418 | 20520.6216
EL DORADO PH 210119752 | EL DORADO PH 2101 | SIERRA | 38.577 | 80.8747 | 99.99% | 20 | 11 | 100% | 99.16% | 1 | 0.69086 | 102.1389 | 1.6995 | 119.922 | High | High | Low | 13 | 2 | 70.5639 | 20395.9884
PARADISE 11062084 | PARADISE 1106 | NORTH VALLEY | 11.3566 | 77.2193 | 100% | 4 | 9 | 100% | 100% | 1 | 0.28289 | 102.1389 | 4.0673 | 117.5206 | High | High | High | 14 | 69 | 28.8939 | 20276.0664
LOS GATOS 110760114 | LOS GATOS 1107 | DE ANZA | 24.3274 | 75.5493 | 92.99% | 9 | 3 | 100% | 100% | 1 | 0.66312 | 65.3912 | 2.5859 | 112.1303 | High | High | Medium | 15 | 21 | 43.362 | 20158.5458
PLACERVILLE 21061104 | PLACERVILLE 2106 | SIERRA | 50.3628 | 96.0676 | 90.37% | 13 | 6 | 100% | 100% | 1 | 0.49422 | 102.1389 | 2.2151 | 111.8183 | High | High | Low | 16 | 13 | 50.479 | 20046.4155
MONTE RIO 1113524 | MONTE RIO 1113 | SONOMA | 6.2702 | 72.7249 | 28.23% | 16 | 4 | 100% | 100% | 0 | 0.30334 | 102.1389 | 3.5196 | 109.0471 | High | High | High | 17 | 55 | 30.9824 | 19934.5972
EL DORADO PH 21016852 | EL DORADO PH 2101 | SIERRA | 25.3514 | 89.3624 | 96.21% | 18 | 8 | 100% | 100% | 0 | 0.52183 | 102.1389 | 2.0051 | 106.8716 | High | High | Low | 18 | 10 | 53.299 | 19825.5501
STANISLAUS 17021804 | STANISLAUS 1702 | YOSEMITE | 8.3693 | 84.6121 | 100% | 9 | 6 | 100% | 100% | 0 | 0.38328 | 102.1389 | 2.7274 | 106.7718 | High | High | Medium | 19 | 29 | 39.1474 | 19718.6785
PINE GROVE 11021222 | PINE GROVE 1102 | STOCKTON | 17.2284 | 80.3851 | 88.79% | 6 | 14 | 100% | 93.15% | 0 | 0.35881 | 102.1389 | 2.8894 | 105.8932 | High | High | Medium | 20 | 36 | 36.6489 | 19611.9067
BRUNSWICK 11052210 | BRUNSWICK 1105 | SIERRA | 22.8031 | 97.1876 | 99.8% | 8 | 12 | 100% | 100% | 0 | 0.53048 | 102.1389 | 1.9441 | 105.3388 | High | High | Low | 21 | 9 | 54.1827 | 19506.0136
BRUNSWICK 11052140 | BRUNSWICK 1105 | SIERRA | 34.5645 | 95.4853 | 99.76% | 25 | 10 | 100% | 100% | 0 | 0.50651 | 102.1389 | 1.9239 | 99.5327 | High | High | Low | 22 | 12 | 51.7342 | 19400.6748
MIWUK 17026018 | MIWUK 1702 | YOSEMITE | 19.5117 | 86.3615 | 100% | 3 | 8 | 100% | 100% | 0 | 0.28867 | 102.1389 | 3.358 | 99.0086 | High | High | High | 23 | 64 | 29.4843 | 19301.1421
CALISTOGA 1101736 | CALISTOGA 1101 | NORTH BAY | 33.5094 | 79.1543 | 66.69% | 16 | 14 | 100% | 100% | 1 | 0.74565 | 47.6367 | 2.7749 | 98.5658 | High | High | Medium | 24 | 38 | 35.5203 | 19202.1335
MIWUK 1702CB | MIWUK 1702 | YOSEMITE | 10.2382 | 90.3115 | 82.25% | 5 | 6 | 100% | 100% | 0 | 0.28839 | 102.1389 | 3.3177 | 97.7246 | High | High | High | 25 | 65 | 29.4558 | 19103.5677
MIWUK 1702S2247 | MIWUK 1702 | YOSEMITE | 1.4764 | 81.7159 | 100% | 2 | 2 | 100% | 100% | 0 | 0.23034 | 102.1389 | 4.1204 | 96.9423 | High | High | High | 26 | 106 | 23.5271 | 19005.8431
ORO FINO 110276008 | ORO FINO 1102 | NORTH VALLEY | 15.9665 | 80.1873 | 99.98% | 4 | 7 | 100% | 100% | 1 | 0.36557 | 102.1389 | 2.5923 | 96.7928 | High | High | Medium | 27 | 33 | 37.3387 | 18908.9008
PARADISE 11062234 | PARADISE 1106 | NORTH VALLEY | 8.8367 | 79.1592 | 100% | 3 | 8 | 100% | 100% | 0 | 0.30628 | 85.4511 | 3.6642 | 95.9005 | High | High | High | 28 | 87 | 26.1721 | 18812.108
FORESTHILL 11011802 | FORESTHILL 1101 | SIERRA | 22.1758 | 72.9192 | 91.83% | 12 | 21 | 100% | 100% | 0 | 0.40081 | 102.1389 | 2.3329 | 95.5024 | High | High | Medium | 29 | 26 | 40.9378 | 18716.2075
MIDDLETOWN 1101548 | MIDDLETOWN 1101 | HUMBOLDT | 22.1669 | 84.1532 | 73.95% | 13 | 16 | 88.6% | 97.32% | 1 | 0.42028 | 102.1389 | 2.2085 | 94.8039 | High | High | Low | 30 | 22 | 42.9273 | 18620.7051
WEST POINT 11014706 | WEST POINT 1101 | STOCKTON | 11.5214 | 90.5528 | 100% | 4 | 4 | 100% | 100% | 0 | 0.36745 | 102.1389 | 2.5195 | 94.5581 | High | High | Medium | 31 | 32 | 37.5307 | 18525.9012
MIWUK 170238218 | MIWUK 1702 | YOSEMITE | 10.8246 | 77.698 | 74.49% | 4 | 9 | 100% | 100% | 0 | 0.26818 | 102.1389 | 3.4335 | 94.0487 | High | High | High | 32 | 79 | 27.3914 | 18431.3431
WOODACRE 1101404 | WOODACRE 1101 | NORTH BAY | 12.4182 | 78.1166 | 26.88% | 20 | 20 | 100% | 92.07% | 0 | 0.22897 | 102.1389 | 3.9584 | 92.5757 | High | High | High | 33 | 107 | 23.3871 | 18337.2945
CALISTOGA 110143924 | CALISTOGA 1101 | NORTH BAY | 4.45 | 80.4513 | 94.31% | 6 | 6 | 47.81% | 100% | 0 | 0.32892 | 85.4511 | 3.2727 | 91.9855 | High | High | High | 34 | 73 | 28.1068 | 18244.7188
BRUNSWICK 110651486 | BRUNSWICK 1106 | SIERRA | 56.6992 | 84.1552 | 88.14% | 22 | 15 | 100% | 87.68% | 1 | 0.49605 | 85.4511 | 2.1451 | 90.9285 | High | High | Low | 35 | 24 | 42.3883 | 18152.7333
SILVERADO 2104632 | SILVERADO 2104 | NORTH BAY | 18.1239 | 77.5447 | 73.72% | 15 | 5 | 96.09% | 100% | 1 | 0.42045 | 65.3912 | 3.2929 | 90.5343 | High | High | High | 36 | 78 | 27.494 | 18061.8048
STANISLAUS 170237276 | STANISLAUS 1702 | YOSEMITE | 11.7226 | 82.7291 | 100% | 8 | 9 | 100% | 100% | 0 | 0.30163 | 102.1389 | 2.8831 | 88.8242 | High | High | Medium | 37 | 57 | 30.8083 | 17971.2705
WEST POINT 110136674 | WEST POINT 1101 | STOCKTON | 9.4896 | 86.8002 | 98.6% | 2 | 6 | 100% | 100% | 0 | 0.39381 | 102.1389 | 2.2058 | 88.7227 | High | High | Low | 38 | 27 | 40.2233 | 17882.4463
MOLINO 1102318 | MOLINO 1102 | SONOMA | 19.2803 | 89.5364 | 61.35% | 11 | 8 | 100% | 100% | 1 | 0.39524 | 85.4511 | 2.6124 | 88.2297 | High | High | Medium | 39 | 45 | 33.7736 | 17793.7235
PUEBLO 2102792 | PUEBLO 2102 | NORTH BAY | 17.9619 | 85.883 | 96.12% | 13 | 4 | 86.21% | 100% | 0 | 0.41118 | 85.4511 | 2.4971 | 87.7383 | High | High | Medium | 40 | 40 | 35.1362 | 17705.4938
EL DORADO PH 210219542 | EL DORADO PH 2102 | SIERRA | 9.4332 | 77.5631 | 77.77% | 6 | 4 | 100% | 100% | 0 | 0.31239 | 102.1389 | 2.74 | 87.4241 | High | High | Medium | 41 | 52 | 31.907 | 17617.7555
FORESTHILL 110150486 | FORESTHILL 1101 | SIERRA | 11.6566 | 81.112 | 97.86% | 4 | 8 | 100% | 100% | 0 | 0.43184 | 102.1389 | 1.9713 | 86.9475 | High | High | Low | 42 | 20 | 44.1076 | 17530.3315
MIRABEL 1101298 | MIRABEL 1101 | SONOMA | 12.8273 | 89.1513 | 37.51% | 16 | 9 | 99.59% | 100% | 0 | 0.33734 | 85.4511 | 2.9749 | 85.7551 | High | High | Medium | 43 | 70 | 28.8258 | 17443.384
MARIPOSA 210110170 | MARIPOSA 2101 | YOSEMITE | 16.3113 | 93.2169 | 77.6% | 14 | 34 | 100% | 100% | 1 | 0.51304 | 102.1389 | 1.5869 | 83.1571 | High | High | Low | 44 | 11 | 52.4012 | 17357.6289
MIWUK 17018050 | MIWUK 1701 | YOSEMITE | 12.1253 | 91.2725 | 97.35% | 8 | 4 | 100% | 100% | 1 | 0.26086 | 102.1389 | 3.1093 | 82.8459 | High | High | High | 45 | 85 | 26.6441 | 17274.4718
CAMP EVERS 21065020 | CAMP EVERS 2106 | CENTRAL COAST | 15.2094 | 69.3374 | 87.56% | 19 | 11 | 100% | 100% | 1 | 0.52218 | 65.3912 | 2.4231 | 82.7401 | High | High | Medium | 46 | 44 | 34.1458 | 17191.6259
CHALLENGE 1101CB | CHALLENGE 1101 | NORTH VALLEY | 16.6203 | 96.135 | 99.73% | 4 | 3 | 100% | 100% | 0 | 0.37094 | 102.1389 | 2.1782 | 82.5265 | High | High | Low | 47 | 31 | 37.8874 | 17108.8858
MIWUK 1702S1547 | MIWUK 1702 | YOSEMITE | 2.7688 | 85.4231 | 100% | 1 | 5 | 100% | 100% | 0 | 0.24392 | 102.1389 | 3.3077 | 82.4079 | High | High | High | 48 | 95 | 24.9141 | 17026.3593
PINE GROVE 110213438 | PINE GROVE 1102 | STOCKTON | 16.4176 | 84.6476 | 100% | 6 | 6 | 100% | 85.87% | 0 | 0.38268 | 102.1389 | 2.1023 | 82.1729 | High | High | Low | 49 | 30 | 39.087 | 16943.9514
WILLITS 110434008 | WILLITS 1104 | HUMBOLDT | 22.9278 | 77.1143 | 100% | 14 | 12 | 100% | 97.76% | 0 | 0.3764 | 85.4511 | 2.5543 | 82.1564 | High | High | Medium | 50 | 49 | 32.1635 | 16861.7785
WYANDOTTE 11031976 | WYANDOTTE 1103 | NORTH VALLEY | 23.9896 | 86.4323 | 100% | 4 | 6 | 100% | 100% | 0 | 0.43481 | 85.4511 | 2.2058 | 81.9573 | High | High | Low | 51 | 34 | 37.155 | 16779.6221
EL DORADO PH 210219562 | EL DORADO PH 2102 | SIERRA | 14.8519 | 89.5871 | 100% | 10 | 7 | 100% | 100% | 0 | 0.33748 | 102.1389 | 2.3227 | 80.0616 | High | High | Medium | 52 | 42 | 34.4696 | 16697.6647
STANISLAUS 170275348 | STANISLAUS 1702 | YOSEMITE | 5.3962 | 93.3092 | 100% | 1 | 9 | 100% | 100% | 0 | 0.29738 | 102.1389 | 2.6132 | 79.3742 | High | High | Medium | 53 | 59 | 30.3738 | 16617.6032
MONTE RIO 1112120 | MONTE RIO 1112 | SONOMA | 6.8692 | 90.5188 | 64.49% | 17 | 9 | 100% | 100% | 0 | 0.33336 | 85.4511 | 2.7822 | 79.2535 | High | High | Medium | 54 | 72 | 28.4857 | 16538.2289
ALLEGHANY 1101VR816 | ALLEGHANY 1101 | SIERRA | 4.1512 | 96.2894 | 73.9% | 6 | 8 | 100% | 100% | 0 | 0.294 | 102.1389 | 2.6166 | 78.5756 | High | High | Medium | 55 | 60 | 30.0293 | 16458.9755
PIKE CITY 1101CB | PIKE CITY 1101 | SIERRA | 19.8554 | 96.0592 | 99.76% | 13 | 13 | 100% | 100% | 1 | 0.38542 | 102.1389 | 1.982 | 78.0243 | High | High | Low | 56 | 28 | 39.3662 | 16380.3999
CAMP EVERS 210660124 | CAMP EVERS 2106 | CENTRAL COAST | 22.5394 | 63.6568 | 80.34% | 20 | 3 | 100% | 100% | 1 | 0.4923 | 65.3912 | 2.4068 | 77.4809 | High | High | Medium | 57 | 48 | 32.1923 | 16302.3755
MONTE RIO 1113202 | MONTE RIO 1113 | SONOMA | 5.2496 | 89.4483 | 68.59% | 13 | 9 | 100% | 100% | 0 | 0.2988 | 85.4511 | 3.0343 | 77.4749 | High | High | Medium | 58 | 92 | 25.5328 | 16224.8946
WOODSIDE 11018974 | WOODSIDE 1101 | PENINSULA | 13.435 | 54.2631 | 29.29% | 40 | 16 | 100% | 100% | 0 | 0.50532 | 47.6367 | 3.1586 | 76.0338 | High | High | High | 59 | 99 | 24.0717 | 16147.4197
RINCON 1103474 | RINCON 1103 | SONOMA | 18.561 | 87.2265 | 99.41% | 8 | 6 | 100% | 100% | 0 | 0.44799 | 65.3912 | 2.5873 | 75.7944 | High | High | Medium | 60 | 67 | 29.2949 | 16071.3859
ORO FINO 11022560 | ORO FINO 1102 | NORTH VALLEY | 16.7196 | 97.5242 | 100% | 5 | 6 | 100% | 81.54% | 1 | 0.26733 | 102.1389 | 2.775 | 75.7698 | High | High | Medium | 61 | 81 | 27.3045 | 15995.5915
COLUMBIA HILL 110135424 | COLUMBIA HILL 1101 | SIERRA | 13.9113 | 71.6588 | 100% | 8 | 11 | 100% | 100% | 1 | 0.44882 | 65.3912 | 2.5252 | 74.113 | High | High | Medium | 62 | 66 | 29.3488 | 15919.8217
WEST POINT 110113444 | WEST POINT 1101 | STOCKTON | 16.633 | 82.1566 | 100% | 5 | 15 | 100% | 100% | 0 | 0.31924 | 102.1389 | 2.2583 | 73.6364 | High | High | Medium | 63 | 46 | 32.6072 | 15845.7087
SILVERADO 210478268 | SILVERADO 2104 | NORTH BAY | 11.9793 | 67.2464 | 60.11% | 10 | 4 | 100% | 100% | 0 | 0.3351 | 65.3912 | 3.3562 | 73.5434 | High | High | High | 64 | 126 | 21.9127 | 15772.0723
CHALLENGE 1102CB | CHALLENGE 1102 | NORTH VALLEY | 15.5217 | 96.52 | 90.77% | 6 | 5 | 100% | 100% | 0 | 0.4019 | 102.1389 | 1.7913 | 73.5318 | High | High | Low | 65 | 25 | 41.0501 | 15698.5289
STANISLAUS 17021850 | STANISLAUS 1702 | YOSEMITE | 13.465 | 54.7158 | 83.98% | 13 | 14 | 100% | 100% | 0 | 0.32626 | 65.3912 | 3.431 | 73.1995 | High | High | High | 66 | 135 | 21.3346 | 15624.9971
EL DORADO PH 210126000 | EL DORADO PH 2101 | SIERRA | 34.0468 | 93.5067 | 99.32% | 9 | 8 | 100% | 100% | 0 | 0.57184 | 85.4511 | 1.4969 | 73.1469 | High | High | Low | 67 | 15 | 48.8647 | 15551.7976
BIG BEND 11021972 | BIG BEND 1102 | NORTH VALLEY | 21.0549 | 95.6632 | 96.1% | 4 | 6 | 100% | 100% | 0 | 0.40978 | 85.4511 | 2.086 | 73.0443 | High | High | Low | 68 | 41 | 35.0163 | 15478.6507
WEST POINT 1101L373 | WEST POINT 1101 | STOCKTON | 7.4413 | 94.6949 | 100% | 2 | 9 | 100% | 100% | 0 | 0.30215 | 102.1389 | 2.361 | 72.8632 | High | High | Medium | 69 | 56 | 30.8608 | 15405.6063
SAN RAFAEL 11081250 | SAN RAFAEL 1108 | NORTH BAY | 3.5796 | 93.2481 | 59.75% | 1 | 1 | 100% | 100% | 1 | 0.20419 | 85.4511 | 4.1107 | 71.7241 | High | High | High | 70 | 180 | 17.4483 | 15332.7432
BONNIE NOOK 1102CB | BONNIE NOOK 1102 | SIERRA | 34.3352 | 94.488 | 85.18% | 18 | 16 | 100% | 100% | 0 | 0.44981 | 102.1389 | 1.5484 | 71.1385 | High | High | Low | 71 | 17 | 45.9434 | 15261.019
ORO FINO 11022090 | ORO FINO 1102 | NORTH VALLEY | 14.7385 | 94.0575 | 68.97% | 5 | 5 | 100% | 100% | 1 | 0.1964 | 102.1389 | 3.5409 | 71.0314 | High | High | High | 72 | 151 | 20.0604 | 15189.8805
STANISLAUS 1702L611 | STANISLAUS 1702 | YOSEMITE | 2.9906 | 79.5104 | 100% | 2 | 2 | 100% | 100% | 0 | 0.27802 | 85.4511 | 2.9655 | 70.4504 | High | High | Medium | 73 | 103 | 23.757 | 15118.849
SYCAMORE CREEK 11112268 | SYCAMORE CREEK 1111 | NORTH VALLEY | 22.2352 | 96.7379 | 99.96% | 3 | 8 | 100% | 99.53% | 1 | 0.2744 | 102.1389 | 2.495 | 69.9295 | High | High | Medium | 74 | 75 | 28.0273 | 15048.3986
BIG TREES 04025300 | BIG TREES 0402 | CENTRAL COAST | 9.8017 | 22.3436 | 42.94% | 37 | 4 | 100% | 100% | 1 | 0.37529 | 47.6367 | 3.9078 | 69.8624 | High | High | High | 75 | 173 | 17.8776 | 14978.4691
EL DORADO PH 2101CB | EL DORADO PH 2101 | SIERRA | 16.7983 | 90.3781 | 74.43% | 12 | 5 | 100% | 100% | 0 | 0.3182 | 102.1389 | 2.1319 | 69.2868 | High | High | Low | 76 | 47 | 32.5001 | 14908.6068
BRUNSWICK 11041020 | BRUNSWICK 1104 | SIERRA | 28.7777 | 77.1 | 87.63% | 9 | 9 | 100% | 83.4% | 1 | 0.27484 | 102.1389 | 2.4581 | 69.005 | High | High | Medium | 77 | 74 | 28.0721 | 14839.3199
MOLINO 1102104 | MOLINO 1102 | SONOMA | 21.7365 | 84.6047 | 53.29% | 22 | 10 | 100% | 100% | 1 | 0.38423 | 65.3912 | 2.69 | 67.5877 | High | High | Medium | 78 | 93 | 25.1255 | 14770.3149
PARADISE 11011155 | PARADISE 1101 | NORTH VALLEY | 0.42051 | 84.3729 | 100% | 5 | 1 | 100% | 100% | 0 | 0.21365 | 85.4511 | 3.701 | 67.5683 | High | High | High | 79 | 167 | 18.257 | 14702.7272
PINE GROVE 11023172 | PINE GROVE 1102 | STOCKTON | 36.8095 | 74.2107 | 73.54% | 9 | 20 | 100% | 71.26% | 1 | 0.23027 | 85.4511 | 3.4298 | 67.4865 | High | High | High | 80 | 154 | 19.6764 | 14635.1589
BIG BEND 1101CB | BIG BEND 1101 | NORTH VALLEY | 23.102 | 80.4105 | 77.16% | 7 | 10 | 100% | 100% | 1 | 0.34627 | 85.4511 | 2.2328 | 66.0668 | High | High | Medium | 81 | 62 | 29.5895 | 14567.6724
STANISLAUS 17024905 | STANISLAUS 1702 | YOSEMITE | 2.3422 | 97.8548 | 99.88% | 2 | 2 | 100% | 100% | 0 | 0.25032 | 102.1389 | 2.5717 | 65.75 | High | High | Medium | 82 | 91 | 25.567 | 14501.6057
MIWUK 17028130 | MIWUK 1702 | YOSEMITE | 9.8769 | 52.0925 | 100% | 2 | 8 | 100% | 100% | 0 | 0.29268 | 65.3912 | 3.427 | 65.5898 | High | High | High | 83 | 160 | 19.1389 | 14435.8556
KANAKA 110165606 | KANAKA 1101 | NORTH VALLEY | 12.8238 | 91.9272 | 96.33% | 13 | 4 | 100% | 100% | 1 | 0.30035 | 85.4511 | 2.5523 | 65.5039 | High | High | Medium | 84 | 89 | 25.6651 | 14370.2658
DOWNIEVILLE DIESEL 1101CB | DOWNIEVILLE DIESEL 1101 | SIERRA | 0.022979 | 98 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21467 | 102.1389 | 2.9787 | 65.3131 | High | High | Medium | 85 | 123 | 21.9265 | 14304.7619
DOWNIEVILLE DIESEL 11011101/2 | DOWNIEVILLE DIESEL 1101 | SIERRA | 0.0097328 | 98 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21467 | 102.1389 | 2.9743 | 65.2163 | High | High | Medium | 86 | 124 | 21.9265 | 14239.4488
ORO FINO 110265932 | ORO FINO 1102 | NORTH VALLEY | 4.3114 | 96.8708 | 92.73% | 3 | 5 | 100% | 100% | 0 | 0.25228 | 102.1389 | 2.5076 | 64.6157 | High | High | Medium | 87 | 88 | 25.7678 | 14174.2325
CHALLENGE 11021064 | CHALLENGE 1102 | NORTH VALLEY | 19.9876 | 84.0327 | 100% | 6 | 2 | 100% | 94.93% | 0 | 0.33496 | 102.1389 | 1.8763 | 64.191 | High | High | Low | 88 | 43 | 34.2124 | 14109.6169
STANISLAUS 1702L5381 | STANISLAUS 1702 | YOSEMITE | 1.2094 | 89.7596 | 100% | 0 | 1 | 100% | 100% | 0 | 0.20877 | 102.1389 | 2.9893 | 63.7424 | High | High | Medium | 89 | 136 | 21.3233 | 14045.4258
BRUNSWICK 11052130 | BRUNSWICK 1105 | SIERRA | 14.272 | 96.3517 | 99.69% | 5 | 6 | 100% | 100% | 0 | 0.29909 | 102.1389 | 2.0794 | 63.5253 | High | High | Low | 90 | 58 | 30.5492 | 13981.6834
STANISLAUS 170237278 | STANISLAUS 1702 | YOSEMITE | 6.8063 | 74.4331 | 100% | 1 | 5 | 100% | 100% | 0 | 0.2075 | 102.1389 | 2.9637 | 62.8122 | High | High | Medium | 91 | 137 | 21.1942 | 13918.1582
MONTE RIO 11138299 | MONTE RIO 1113 | SONOMA | 1.1981 | 94.52 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21069 | 102.1389 | 2.9055 | 62.524 | High | High | Medium | 92 | 133 | 21.5193 | 13855.3459
ORO FINO 110239154 | ORO FINO 1102 | NORTH VALLEY | 0.88251 | 98 | 100% | 3 | 0 | 100% | 100% | 1 | 0.22144 | 102.1389 | 2.7583 | 62.3862 | High | High | Medium | 93 | 114 | 22.618 | 13792.8219
WOODACRE 11011238 | WOODACRE 1101 | NORTH BAY | 3.6828 | 94.4368 | 22.55% | 16 | 2 | 100% | 100% | 0 | 0.19161 | 85.4511 | 3.808 | 62.3489 | High | High | High | 94 | 198 | 16.373 | 13730.4357
BIG BASIN 110110720 | BIG BASIN 1101 | CENTRAL COAST | 4.6838 | 66.6097 | 31.56% | 7 | 1 | 100% | 100% | 0 | 0.21501 | 85.4511 | 3.3585 | 61.7049 | High | High | High | 95 | 164 | 18.3729 | 13668.0867
WEST POINT 110112256 | WEST POINT 1101 | STOCKTON | 6.5157 | 90.9675 | 74.92% | 4 | 4 | 100% | 100% | 0 | 0.21727 | 102.1389 | 2.7434 | 60.8819 | High | High | Medium | 96 | 119 | 22.192 | 13606.3819
SILVERADO 2104645 | SILVERADO 2104 | NORTH BAY | 1.0113 | 86.4283 | 53.43% | 4 | 2 | 100% | 100% | 0 | 0.17771 | 85.4511 | 3.9922 | 60.6227 | High | High | High | 97 | 215 | 15.1851 | 13545.4999
STANISLAUS 1702 | STANISLAUS 1702 | YOSEMITE | 0.0021222 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 102.1389 | 2.8405 | 59.6463 | High | High | Medium | 98 | 140 | 20.9988 | 13484.8772
APPLE HILL 110413512 | APPLE HILL 1104 | SIERRA | 27.848 | 80.8375 | 86.09% | 15 | 14 | 89.98% | 77.01% | 0 | 0.27338 | 102.1389 | 2.12 | 59.1969 | High | High | Low | 99 | 76 | 27.9228 | 13425.231
CAMP EVERS 210510214 | CAMP EVERS 2105 | CENTRAL COAST | 14.0274 | 70.1914 | 71.02% | 31 | 1 | 100% | 100% | 0 | 0.29021 | 65.3912 | 3.1151 | 59.1158 | High | High | High | 100 | 161 | 18.9774 | 13366.034
MONTE RIO 111164758 | MONTE RIO 1111 | SONOMA | 10.5474 | 85.3267 | 35.52% | 9 | 6 | 100% | 100% | 0 | 0.26838 | 85.4511 | 2.5622 | 58.7581 | High | High | Medium | 101 | 112 | 22.933 | 13306.9182
MIWUK 17028090 | MIWUK 1702 | YOSEMITE | 4.0244 | 68.0843 | 40.03% | 1 | 7 | 100% | 100% | 0 | 0.1541 | 102.1389 | 3.6986 | 58.2148 | High | High | High | 102 | 204 | 15.7396 | 13248.1601
WEST POINT 1101L1969 | WEST POINT 1101 | STOCKTON | 1.0816 | 86.0606 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20122 | 102.1389 | 2.8277 | 58.1165 | High | High | Medium | 103 | 143 | 20.5528 | 13189.9453
SILVERADO 2105658898 | SILVERADO 2105 | NORTH BAY | 17.239 | 89.5362 | 92.68% | 6 | 3 | 99.53% | 97.17% | 1 | 0.28431 | 65.3912 | 3.1133 | 57.8818 | High | High | High | 104 | 162 | 18.5917 | 13131.8288
COLUMBIA HILL 1101764 | COLUMBIA HILL 1101 | SIERRA | 14.8572 | 87.6214 | 100% | 5 | 10 | 100% | 100% | 1 | 0.36409 | 85.4511 | 1.8603 | 57.8773 | High | High | Low | 105 | 54 | 31.1119 | 13073.947
HALF MOON BAY 11012500 | HALF MOON BAY 1101 | PENINSULA | 5.7745 | 85.7148 | 84.59% | 4 | 6 | 82.94% | 96.61% | 1 | 0.2396 | 65.3912 | 3.6617 | 57.3712 | High | High | High | 106 | 207 | 15.668 | 13016.0697
VOLTA 110253130 | VOLTA 1102 | NORTH VALLEY | 13.8858 | 76.696 | 100% | 3 | 7 | 100% | 92.09% | 0 | 0.29929 | 85.4511 | 2.2396 | 57.2769 | High | High | Medium | 107 | 90 | 25.5745 | 12958.6985
PARADISE 110195728 | PARADISE 1101 | NORTH VALLEY | 5.026 | 85.7627 | 38.06% | 1 | 6 | 100% | 100% | 0 | 0.18459 | 85.4511 | 3.6211 | 57.1177 | High | High | High | 108 | 203 | 15.7736 | 12901.4216
STANISLAUS 17026028 | STANISLAUS 1702 | YOSEMITE | 5.3481 | 47.3801 | 91.01% | 3 | 4 | 100% | 100% | 0 | 0.28374 | 65.3912 | 3.0384 | 56.3747 | High | High | Medium | 109 | 163 | 18.5544 | 12844.3039
MONTE RIO 11131991 | MONTE RIO 1113 | SONOMA | 7.0583 | 93.2573 | 64.98% | 0 | 4 | 100% | 100% | 0 | 0.19767 | 102.1389 | 2.7908 | 56.3455 | High | High | Medium | 110 | 146 | 20.1896 | 12787.9292
KANAKA 110183288 | KANAKA 1101 | NORTH VALLEY | 17.5828 | 90.1927 | 100% | 7 | 4 | 100% | 100% | 0 | 0.26111 | 102.1389 | 2.1087 | 56.2379 | High | High | Low | 111 | 84 | 26.6692 | 12731.5836
SHINGLE SPRINGS 210912392 | SHINGLE SPRINGS 2109 | SIERRA | 14.9169 | 46.1952 | 91.69% | 7 | 8 | 100% | 100% | 0 | 0.31183 | 65.3912 | 2.7319 | 55.7055 | High | High | Medium | 112 | 144 | 20.3908 | 12675.3457
STELLING 111060094 | STELLING 1110 | DE ANZA | 13.9579 | 79.5 | 89.71% | 7 | 6 | 100% | 94.63% | 1 | 0.27357 | 65.3912 | 3.1124 | 55.6768 | High | High | High | 113 | 172 | 17.8888 | 12619.6402
WEST POINT 11021303 | WEST POINT 1102 | STOCKTON | 15.8188 | 90.4672 | 99.8% | 4 | 11 | 100% | 100% | 0 | 0.28235 | 85.4511 | 2.2984 | 55.4538 | High | High | Medium | 114 | 98 | 24.1273 | 12563.9634
MONTE RIO 1113652 | MONTE RIO 1113 | SONOMA | 1.6252 | 74.26 | 59.28% | 4 | 0 | 100% | 100% | 0 | 0.16674 | 102.1389 | 3.2389 | 55.1604 | High | High | High | 115 | 187 | 17.0307 | 12508.5096
PUEBLO 21033583 | PUEBLO 2103 | NORTH BAY | 9.4952 | 94.4646 | 44.31% | 6 | 11 | 100% | 100% | 1 | 0.25545 | 85.4511 | 2.5196 | 54.9993 | High | High | Medium | 116 | 129 | 21.8289 | 12453.3492
BRUNSWICK 11032200 | BRUNSWICK 1103 | SIERRA | 5.571 | 90.9239 | 99.7% | 2 | 4 | 100% | 100% | 0 | 0.22488 | 102.1389 | 2.3873 | 54.8339 | High | High | Medium | 117 | 111 | 22.9688 | 12398.3499
CAMP EVERS 210574170 | CAMP EVERS 2105 | CENTRAL COAST | 3.5599 | 43.1898 | 71.52% | 10 | 5 | 100% | 100% | 0 | 0.19742 | 65.3912 | 4.2334 | 54.6522 | High | High | High | 118 | 254 | 12.9096 | 12343.516
MOUNTAIN QUARRIES 21011184 | MOUNTAIN QUARRIES 2101 | SIERRA | 11.7903 | 85.233 | 82.22% | 1 | 4 | 100% | 100% | 0 | 0.21412 | 85.4511 | 2.9723 | 54.3825 | High | High | Medium | 119 | 166 | 18.2964 | 12288.8638
ALTO 11243121 | ALTO 1124 | NORTH BAY | 2.756 | 78.1169 | 17.87% | 3 | 11 | 100% | 100% | 0 | 0.1536 | 85.4511 | 4.1251 | 54.1442 | High | High | High | 120 | 247 | 13.1255 | 12234.4814
EL DORADO PH 21026645 | EL DORADO PH 2102 | SIERRA | 4.2976 | 91.6097 | 86.84% | 4 | 3 | 100% | 100% | 0 | 0.23151 | 102.1389 | 2.2842 | 54.0125 | High | High | Medium | 121 | 105 | 23.6465 | 12180.3372
ORO FINO 11022096 | ORO FINO 1102 | NORTH VALLEY | 14.098 | 93.7734 | 100% | 8 | 2 | 100% | 100% | 0 | 0.28682 | 85.4511 | 2.1974 | 53.8569 | High | High | Low | 122 | 96 | 24.5089 | 12126.3247
OAKHURST 110310190 | OAKHURST 1103 | YOSEMITE | 11.5271 | 95.517 | 27.67% | 12 | 10 | 100% | 100% | 1 | 0.26739 | 102.1389 | 1.9347 | 52.8379 | High | High | Low | 123 | 80 | 27.311 | 12072.4678
BRUNSWICK 1105 | BRUNSWICK 1105 | SIERRA | 0.032568 | 98 | 100% | 2 | 0 | 100% | 100% | 0 | 0.21917 | 102.1389 | 2.3469 | 52.5372 | High | High | Medium | 124 | 116 | 22.3858 | 12019.6299
SILVERADO 21051421 | SILVERADO 2105 | NORTH BAY | 9.2052 | 85.2373 | 78.89% | 5 | 4 | 92.75% | 100% | 1 | 0.22901 | 65.3912 | 3.5009 | 52.427 | High | High | High | 125 | 220 | 14.9751 | 11967.0927
WEST POINT 11021535 | WEST POINT 1102 | STOCKTON | 3.0651 | 85.9665 | 100% | 1 | 1 | 100% | 100% | 0 | 0.2539 | 85.4511 | 2.4158 | 52.4127 | High | High | Medium | 126 | 131 | 21.6957 | 11914.6657
MIDDLETOWN 11011079 | MIDDLETOWN 1101 | HUMBOLDT | 3.6508 | 95.1699 | 100% | 2 | 3 | 100% | 100% | 1 | 0.22672 | 102.1389 | 2.2574 | 52.2754 | High | High | Medium | 127 | 108 | 23.1571 | 11862.253
PARADISE 11052214 | PARADISE 1105 | NORTH VALLEY | 9.8398 | 58.7584 | 53.2% | 6 | 6 | 86.04% | 100% | 1 | 0.14771 | 102.1389 | 3.4298 | 51.746 | High | High | High | 128 | 217 | 15.0873 | 11809.9776
PINE GROVE 110235576 | PINE GROVE 1102 | STOCKTON | 7.978 | 78.3459 | 100% | 3 | 1 | 100% | 100% | 0 | 0.22493 | 85.4511 | 2.6836 | 51.5795 | High | High | Medium | 129 | 159 | 19.2204 | 11758.2315
FORESTHILL 11022106 | FORESTHILL 1102 | SIERRA | 28.0974 | 67.1045 | 99.85% | 8 | 14 | 100% | 71.38% | 1 | 0.26076 | 102.1389 | 1.936 | 51.5625 | High | High | Low | 130 | 86 | 26.6336 | 11706.652
MOLINO 110266006 | MOLINO 1102 | SONOMA | 9.0487 | 82.4735 | 54.27% | 8 | 4 | 100% | 100% | 1 | 0.25799 | 65.3912 | 3.052 | 51.4882 | High | High | Medium | 131 | 189 | 16.8704 | 11655.0896
CURTIS 17022123 | CURTIS 1702 | YOSEMITE | 1.861 | 56.934 | 100% | 1 | 0 | 100% | 100% | 0 | 0.19293 | 65.3912 | 4.0222 | 50.7428 | High | High | High | 132 | 260 | 12.6157 | 11603.6013
SALT SPRINGS 21024796 | SALT SPRINGS 2102 | STOCKTON | 7.1845 | 85.6584 | 100% | 4 | 1 | 100% | 100% | 0 | 0.34533 | 102.1389 | 1.4356 | 50.6348 | High | High | Low | 133 | 39 | 35.2718 | 11552.8585
FORESTHILL 1101CB | FORESTHILL 1101 | SIERRA | 9.3514 | 78.4608 | 92.08% | 4 | 4 | 100% | 100% | 0 | 0.33375 | 65.3912 | 2.3144 | 50.5099 | High | High | Medium | 134 | 130 | 21.8245 | 11502.2237
MOLINO 1102658 | MOLINO 1102 | SONOMA | 10.901 | 83.5071 | 77.94% | 19 | 4 | 100% | 73.87% | 0 | 0.26881 | 65.3912 | 2.8576 | 50.2302 | High | High | Medium | 135 | 176 | 17.5775 | 11451.7138
SAN RAFAEL 110863598 | SAN RAFAEL 1108 | NORTH BAY | 1.9128 | 87.2214 | 45.64% | 1 | 1 | 100% | 100% | 0 | 0.14368 | 85.4511 | 4.0853 | 50.1574 | High | High | High | 136 | 268 | 12.2776 | 11401.4836
WEST POINT 1101L2219 | WEST POINT 1101 | STOCKTON | 3.4094 | 90.8965 | 100% | 0 | 2 | 100% | 100% | 0 | 0.26183 | 85.4511 | 2.2217 | 49.7088 | High | High | Low | 137 | 117 | 22.3739 | 11351.3262
MONTE RIO 1113320 | MONTE RIO 1113 | SONOMA | 2.745 | 95.3298 | 21.97% | 16 | 1 | 100% | 100% | 1 | 0.16899 | 102.1389 | 2.8782 | 49.6792 | High | High | Medium | 138 | 182 | 17.2604 | 11301.6174
MIWUK 170111800 | MIWUK 1701 | YOSEMITE | 9.4843 | 50.073 | 65.97% | 8 | 9 | 100% | 100% | 0 | 0.20689 | 65.3912 | 3.6538 | 49.4316 | High | High | High | 139 | 239 | 13.5287 | 11251.9382
ALTO 1125510 | ALTO 1125 | NORTH BAY | 7.3822 | 55.9602 | 19.39% | 13 | 14 | 100% | 100% | 0 | 0.45487 | 26.5534 | 4.0428 | 48.8305 | High | High | High | 140 | 272 | 12.0783 | 11202.5066
MIWUK 170219772 | MIWUK 1702 | YOSEMITE | 3.8508 | 59.5505 | 82.54% | 2 | 3 | 100% | 100% | 0 | 0.16594 | 85.4511 | 3.4321 | 48.6675 | High | High | High | 141 | 229 | 14.1801 | 11153.6761
MONTE RIO 1113180 | MONTE RIO 1113 | SONOMA | 1.9463 | 80.579 | 66.84% | 3 | 0 | 100% | 100% | 0 | 0.1611 | 102.1389 | 2.9572 | 48.6589 | High | High | Medium | 142 | 197 | 16.4543 | 11105.0086
ALLEGHANY 1101806 | ALLEGHANY 1101 | SIERRA | 11.8065 | 97.171 | 100% | 0 | 7 | 100% | 100% | 0 | 0.2646 | 102.1389 | 1.7958 | 48.5336 | High | High | Low | 143 | 82 | 27.0262 | 11056.3497
MONTE RIO 1113678 | MONTE RIO 1113 | SONOMA | 1.8444 | 89.0499 | 49.28% | 0 | 1 | 100% | 100% | 0 | 0.20505 | 85.4511 | 2.7668 | 48.4785 | High | High | Medium | 144 | 179 | 17.5214 | 11007.816
WOODSIDE 11018884 | WOODSIDE 1101 | PENINSULA | 7.7125 | 85.1128 | 91.16% | 13 | 3 | 100% | 100% | 0 | 0.30526 | 65.3912 | 2.4202 | 48.3096 | High | High | Medium | 145 | 152 | 19.9613 | 10959.3376
OAKHURST 110310723 | OAKHURST 1103 | YOSEMITE | 0.0026429 | 95 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21123 | 102.1389 | 2.2385 | 48.2953 | High | High | Medium | 146 | 132 | 21.5751 | 10911.0279
CAMP EVERS 210510294 | CAMP EVERS 2105 | CENTRAL COAST | 8.3995 | 27.1368 | 59.21% | 34 | 11 | 100% | 100% | 0 | 0.26177 | 47.6367 | 3.864 | 48.1828 | High | High | High | 147 | 264 | 12.4698 | 10862.7326
APPLE HILL 110497086 | APPLE HILL 1104 | SIERRA | 25.6232 | 83.1632 | 99.98% | 8 | 5 | 100% | 100% | 1 | 0.28482 | 102.1389 | 1.6526 | 48.0777 | High | High | Low | 148 | 68 | 29.0916 | 10814.5498
CURTIS 1705843 | CURTIS 1705 | YOSEMITE | 6.6016 | 54.6165 | 100% | 2 | 2 | 100% | 93.53% | 0 | 0.18286 | 85.4511 | 3.052 | 47.6886 | High | High | Medium | 149 | 209 | 15.6252 | 10766.4721
ELECTRA 110277204 | ELECTRA 1102 | STOCKTON | 18.6351 | 80.9647 | 100% | 2 | 8 | 100% | 100% | 0 | 0.27848 | 85.4511 | 1.9943 | 47.458 | High | High | Low | 150 | 101 | 23.7964 | 10718.7835
WILLITS 1104504 | WILLITS 1104 | HUMBOLDT | 22.5336 | 70.0895 | 92.93% | 13 | 8 | 100% | 60.82% | 1 | 0.2605 | 85.4511 | 2.1292 | 47.3973 | High | High | Low | 151 | 118 | 22.2602 | 10671.3255
MIDDLETOWN 1101614 | MIDDLETOWN 1101 | HUMBOLDT | 1.393 | 87.6673 | 76.7% | 0 | 1 | 100% | 100% | 0 | 0.19696 | 85.4511 | 2.8133 | 47.348 | High | High | Medium | 152 | 191 | 16.8302 | 10623.9282
KONOCTI 1102532 | KONOCTI 1102 | HUMBOLDT | 9.613 | 73.4923 | 78.9% | 8 | 7 | 100% | 100% | 1 | 0.20006 | 85.4511 | 2.7651 | 47.2701 | High | High | Medium | 153 | 186 | 17.0951 | 10576.5802
WEST POINT 11024790 | WEST POINT 1102 | STOCKTON | 28.9338 | 75.0976 | 91.62% | 9 | 12 | 100% | 75.46% | 1 | 0.35051 | 65.3912 | 2.0584 | 47.1793 | High | High | Low | 154 | 113 | 22.92 | 10529.3101
MIWUK 170193062 | MIWUK 1701 | YOSEMITE | 8.21 | 73.287 | 98.21% | 5 | 3 | 100% | 79.03% | 0 | 0.17366 | 85.4511 | 3.1781 | 47.1632 | High | High | High | 155 | 223 | 14.8399 | 10482.1308
PINE GROVE 11029145 | PINE GROVE 1102 | STOCKTON | 2.9225 | 81.0955 | 99.74% | 0 | 0 | 100% | 100% | 0 | 0.19549 | 85.4511 | 2.812 | 46.973 | High | High | Medium | 156 | 193 | 16.7046 | 10434.9675
MONTE RIO 111264682 | MONTE RIO 1112 | SONOMA | 1.7634 | 73.4411 | 19.23% | 8 | 4 | 100% | 100% | 0 | 0.12546 | 102.1389 | 3.654 | 46.8247 | High | High | High | 157 | 257 | 12.8145 | 10387.9946
FORESTHILL 11011820 | FORESTHILL 1101 | SIERRA | 5.5828 | 97.995 | 99.82% | 0 | 0 | 100% | 100% | 1 | 0.23777 | 102.1389 | 1.9221 | 46.6794 | High | High | Low | 158 | 97 | 24.2855 | 10341.1699
SALT SPRINGS 2102L485 | SALT SPRINGS 2102 | STOCKTON | 0.82893 | 87.1462 | 100% | 0 | 2 | 100% | 100% | 0 | 0.23224 | 102.1389 | 1.9664 | 46.6444 | High | High | Low | 159 | 104 | 23.721 | 10294.4905
SILVERADO 2104722 | SILVERADO 2104 | NORTH BAY | 7.8999 | 65.7561 | 63.09% | 2 | 4 | 100% | 100% | 0 | 0.17105 | 85.4511 | 3.1898 | 46.6231 | High | High | High | 160 | 224 | 14.6165 | 10247.8462
MOLINO 1102396 | MOLINO 1102 | SONOMA | 16.1282 | 58.4363 | 35.51% | 9 | 10 | 100% | 100% | 0 | 0.275 | 65.3912 | 2.5855 | 46.494 | High | High | Medium | 161 | 171 | 17.9823 | 10201.223
WOODACRE 110196844 | WOODACRE 1101 | NORTH BAY | 5.9237 | 87.2691 | 22.46% | 5 | 8 | 100% | 88.33% | 0 | 0.12278 | 102.1389 | 3.7061 | 46.4791 | High | High | High | 162 | 261 | 12.5411 | 10154.7291
MONTE RIO 1113CB | MONTE RIO 1113 | SONOMA | 4.5623 | 78.3408 | 32.43% | 11 | 4 | 100% | 100% | 0 | 0.18356 | 85.4511 | 2.9514 | 46.2948 | High | High | Medium | 163 | 206 | 15.6855 | 10108.25
STANISLAUS 17011331 | STANISLAUS 1701 | YOSEMITE | 4.3931 | 65.9467 | 100% | 5 | 0 | 100% | 100% | 0 | 0.18999 | 85.4511 | 2.846 | 46.2045 | High | High | Medium | 164 | 201 | 16.2348 | 10061.9551
MIWUK 17021808 | MIWUK 1702 | YOSEMITE | 1.8341 | 72.798 | 17.3% | 1 | 2 | 100% | 100% | 0 | 0.10942 | 102.1389 | 4.1225 | 46.0745 | High | High | High | 165 | 288 | 11.1764 | 10015.7506
PIKE CITY 11011730 | PIKE CITY 1101 | SIERRA | 8.599 | 94.8581 | 99.91% | 4 | 2 | 100% | 100% | 0 | 0.33402 | 85.4511 | 1.6102 | 45.9608 | High | High | Low | 166 | 71 | 28.5428 | 9969.6761
PINE GROVE 110283098 | PINE GROVE 1102 | STOCKTON | 8.0988 | 80.2841 | 100% | 2 | 7 | 100% | 98.1% | 0 | 0.21828 | 65.3912 | 3.1987 | 45.6583 | High | High | High | 167 | 228 | 14.2738 | 9923.7153
VOLTA 11021504 | VOLTA 1102 | NORTH VALLEY | 8.3043 | 82.9659 | 100% | 2 | 3 | 100% | 100% | 0 | 0.23562 | 85.4511 | 2.2543 | 45.389 | High | High | Medium | 168 | 149 | 20.1342 | 9878.057
LOS GATOS 110760118 | LOS GATOS 1107 | DE ANZA | 20.0923 | 57.6089 | 83.76% | 25 | 2 | 100% | 100% | 1 | 0.5667 | 47.6367 | 1.6789 | 45.3221 | High | High | Low | 169 | 83 | 26.9958 | 9832.668
CAMP EVERS 210510225 | CAMP EVERS 2105 | CENTRAL COAST | 0.18205 | 47.7189 | 100% | 3 | 0 | 100% | 100% | 0 | 0.1873 | 65.3912 | 3.6862 | 45.1466 | High | High | High | 170 | 269 | 12.2475 | 9787.3459
CAMP EVERS 21061625 | CAMP EVERS 2106 | CENTRAL COAST | 0.904 | 67.0004 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18108 | 65.3912 | 3.8121 | 45.1386 | High | High | High | 171 | 277 | 11.841 | 9742.1993
SPRING GAP 17029690 | SPRING GAP 1702 | YOSEMITE | 17.3345 | 90.5752 | 98.76% | 12 | 12 | 100% | 100% | 0 | 0.65826 | 102.1389 | 0.67026 | 45.0638 | High | High | Low | 172 | 3 | 67.2336 | 9697.0607
SAN RAFAEL 11081247 | SAN RAFAEL 1108 | NORTH BAY | 0.2757 | 81.1642 | 57.56% | 3 | 0 | 100% | 100% | 0 | 0.16951 | 65.3912 | 4.0604 | 45.007 | High | High | High | 173 | 292 | 11.0844 | 9651.9968
EL DORADO PH 2102CB | EL DORADO PH 2102 | SIERRA | 5.6703 | 93.9988 | 79.03% | 2 | 2 | 100% | 100% | 0 | 0.19325 | 102.1389 | 2.2785 | 44.974 | High | High | Medium | 174 | 153 | 19.7388 | 9606.9898
ORO FINO 1102CB | ORO FINO 1102 | NORTH VALLEY | 2.0939 | 90.4736 | 31.39% | 1 | 0 | 100% | 100% | 0 | 0.1458 | 102.1389 | 3.0047 | 44.7473 | High | High | Medium | 175 | 221 | 14.8924 | 9562.0158
WEST POINT 1101L3355 | WEST POINT 1101 | STOCKTON | 2.2225 | 89.0928 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20458 | 102.1389 | 2.1399 | 44.7134 | High | High | Low | 176 | 141 | 20.8954 | 9517.2685
MONTE RIO 11131313 | MONTE RIO 1113 | SONOMA | 1.2316 | 65.332 | 67.8% | 0 | 1 | 100% | 100% | 0 | 0.14614 | 85.4511 | 3.5696 | 44.576 | High | High | High | 177 | 262 | 12.4876 | 9472.5552
FULTON 1107214 | FULTON 1107 | SONOMA | 12.2376 | 47.3525 | 63.1% | 7 | 19 | 100% | 100% | 0 | 0.43673 | 47.6367 | 2.1422 | 44.5667 | High | High | Low | 178 | 142 | 20.8046 | 9427.9791
MONTE RIO 11131989 | MONTE RIO 1113 | SONOMA | 0.72387 | 90 | 37.43% | 0 | 0 | 100% | 100% | 0 | 0.13376 | 102.1389 | 3.26 | 44.5399 | High | High | High | 179 | 234 | 13.6625 | 9383.4125
BRUNSWICK 11062796 | BRUNSWICK 1106 | SIERRA | 19.8739 | 59.7898 | 71.67% | 4 | 4 | 100% | 99.1% | 0 | 0.19738 | 85.4511 | 2.6385 | 44.5007 | High | High | Medium | 180 | 190 | 16.8661 | 9338.8726
WILLITS 110391810 | WILLITS 1103 | HUMBOLDT | 29.3984 | 69.6626 | 100% | 19 | 14 | 100% | 85.03% | 1 | 0.25809 | 85.4511 | 2.0026 | 44.1654 | High | High | Low | 181 | 121 | 22.0543 | 9294.3719
WOODACRE 1102851 | WOODACRE 1102 | NORTH BAY | 1.2766 | 60.3664 | 19.35% | 1 | 3 | 100% | 100% | 0 | 0.10492 | 85.4511 | 4.9245 | 44.1492 | High | High | High | 182 | 340 | 8.9652 | 9250.2065
ALLEGHANY 1102CB | ALLEGHANY 1102 | SIERRA | 18.0939 | 92.7974 | 39.16% | 4 | 24 | 100% | 100% | 1 | 0.48104 | 65.3912 | 1.4 | 44.0392 | High | High | Low | 183 | 53 | 31.4559 | 9206.0573
BONNIE NOOK 1101CB | BONNIE NOOK 1101 | SIERRA | 14.7401 | 89.8232 | 47.01% | 8 | 12 | 100% | 100% | 0 | 0.28941 | 102.1389 | 1.4893 | 44.0242 | High | High | Low | 184 | 63 | 29.5604 | 9162.0181
PAUL SWEET 2104 | PAUL SWEET 2104 | CENTRAL COAST | 0.043661 | 75 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18934 | 65.3912 | 3.5423 | 43.8565 | High | High | High | 185 | 266 | 12.3809 | 9117.9938
SILVERADO 2103CB | SILVERADO 2103 | NORTH BAY | 8.6664 | 84.0044 | 89.49% | 1 | 4 | 46.48% | 100% | 0 | 0.27216 | 47.6367 | 3.3783 | 43.8001 | High | High | High | 186 | 252 | 12.965 | 9074.1373
MONTE RIO 11111703 | MONTE RIO 1111 | SONOMA | 1.2714 | 84.0743 | 95.02% | 2 | 1 | 100% | 100% | 0 | 0.20007 | 85.4511 | 2.5488 | 43.5738 | High | High | Medium | 187 | 185 | 17.096 | 9030.3372
BRUNSWICK 110584480 | BRUNSWICK 1105 | SIERRA | 4.5786 | 96.5256 | 65.31% | 1 | 0 | 100% | 100% | 0 | 0.17078 | 102.1389 | 2.4965 | 43.5454 | High | High | Medium | 188 | 181 | 17.4429 | 8986.7634
MIRABEL 11027347 | MIRABEL 1102 | SONOMA | 0.81707 | 70.8306 | 59.55% | 4 | 1 | 100% | 100% | 0 | 0.14897 | 102.1389 | 2.8575 | 43.4787 | High | High | Medium | 189 | 213 | 15.2154 | 8943.218
FORESTHILL 110175340 | FORESTHILL 1101 | SIERRA | 4.974 | 93.375 | 69.57% | 0 | 2 | 100% | 100% | 0 | 0.19715 | 102.1389 | 2.1578 | 43.4515 | High | High | Low | 190 | 148 | 20.1366 | 8899.7393
PAUL SWEET 21045394 | PAUL SWEET 2104 | CENTRAL COAST | 14.2856 | 38.4642 | 72.86% | 5 | 2 | 93.82% | 100% | 0 | 0.25339 | 47.6367 | 3.5996 | 43.4504 | High | High | High | 191 | 274 | 12.0708 | 8856.2878
WEST POINT 1101 | WEST POINT 1101 | STOCKTON | 0.004924 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 85.4511 | 2.4491 | 43.0255 | High | High | Medium | 192 | 178 | 17.5679 | 8812.8374
PARADISE 11011212 | PARADISE 1101 | NORTH VALLEY | 8.5723 | 27.6396 | 21.52% | 13 | 13 | 100% | 100% | 0 | 0.17074 | 65.3912 | 3.8308 | 42.7709 | High | High | High | 193 | 289 | 11.1651 | 8769.8119
WEST POINT 110234416 | WEST POINT 1102 | STOCKTON | 10.524 | 86.8553 | 100% | 7 | 3 | 100% | 100% | 1 | 0.25274 | 65.3912 | 2.5592 | 42.2967 | High | High | Medium | 194 | 194 | 16.5271 | 8727.041
WEST POINT 1102L3733 | WEST POINT 1102 | STOCKTON | 1.754 | 90.0843 | 100% | 0 | 0 | 100% | 94.99% | 0 | 0.19267 | 85.4511 | 2.5527 | 42.0286 | High | High | Medium | 195 | 195 | 16.464 | 8684.7443
VOLTA 110280982 | VOLTA 1102 | NORTH VALLEY | 0.52007 | 92.783 | 99.45% | 2 | 0 | 100% | 100% | 1 | 0.23557 | 85.4511 | 2.084 | 41.9505 | High | High | Low | 196 | 150 | 20.1294 | 8642.7157
LOS GATOS 1107LA60 | LOS GATOS 1107 | DE ANZA | 8.6011 | 90.5119 | 96.22% | 1 | 0 | 100% | 100% | 0 | 0.24993 | 85.4511 | 1.9634 | 41.9315 | High | High | Low | 197 | 134 | 21.3565 | 8600.7652
COLUMBIA HILL 11012212 | COLUMBIA HILL 1101 | SIERRA | 9.1875 | 95.8225 | 100% | 9 | 3 | 100% | 100% | 0 | 0.35537 | 102.1389 | 1.1517 | 41.805 | High | High | Low | 198 | 37 | 36.2974 | 8558.8338
COLUMBIA HILL 11018233 | COLUMBIA HILL 1101 | SIERRA | 5.0061 | 92.4069 | 99.94% | 1 | 3 | 100% | 100% | 0 | 0.27044 | 102.1389 | 1.5103 | 41.7175 | High | High | Low | 199 | 77 | 27.6227 | 8517.0287
CHALLENGE 11015460 | CHALLENGE 1101 | NORTH VALLEY | 11.8115 | 93.9312 | 100% | 4 | 4 | 100% | 100% | 0 | 0.31277 | 102.1389 | 1.2968 | 41.4261 | High | High | Low | 200 | 51 | 31.9457 | 8475.3112
CLARKSVILLE 210419772 | CLARKSVILLE 2104 | SIERRA | 18.3365 | 58.7112 | 99.97% | 3 | 3 | 99.31% | 100% | 1 | 0.20806 | 65.3912 | 3.04 | 41.3598 | High | High | Medium | 201 | 236 | 13.6054 | 8433.885
CURTIS 17048140 | CURTIS 1704 | YOSEMITE | 26.2498 | 65.6672 | 76.6% | 12 | 12 | 100% | 76.04% | 0 | 0.17401 | 85.4511 | 2.7756 | 41.2728 | High | High | Medium | 202 | 222 | 14.8696 | 8392.5252
OAKLAND X 1106CR020 | OAKLAND X 1106 | EAST BAY | 2.4457 | 82.3898 | 55.47% | 10 | 1 | 100% | 99.48% | 0 | 0.18349 | 65.3912 | 3.4295 | 41.1503 | High | High | High | 203 | 276 | 11.9989 | 8351.2524
MONTE RIO 111215401 | MONTE RIO 1112 | SONOMA | 0.86292 | 85.2793 | 87.8% | 1 | 3 | 100% | 100% | 0 | 0.19647 | 85.4511 | 2.4508 | 41.1456 | High | High | Medium | 204 | 192 | 16.7884 | 8310.1021
RINCON 1103198 | RINCON 1103 | SONOMA | 6.4573 | 72.5696 | 80.26% | 6 | 3 | 100% | 100% | 0 | 0.20459 | 65.3912 | 3.0723 | 41.1018 | High | High | Medium | 205 | 244 | 13.3782 | 8268.9565
MIWUK 17029270 | MIWUK 1702 | YOSEMITE | 5.8553 | 48.3944 | 46.92% | 2 | 9 | 100% | 95.13% | 0 | 0.12583 | 85.4511 | 3.8062 | 40.9252 | High | High | High | 206 | 301 | 10.7524 | 8227.8546
BURNS 2101 | BURNS 2101 | CENTRAL COAST | 0.0053489 | 65 | 100% | 0 | 0 | 100% | 100% | 0 | 0.17906 | 65.3912 | 3.488 | 40.84 | High | High | High | 207 | 279 | 11.7089 | 8186.9295
POINT MORETTI 1101 | POINT MORETTI 1101 | CENTRAL COAST | 0.0096753 | 65 | 100% | 0 | 0 | 100% | 100% | 0 | 0.17906 | 65.3912 | 3.4875 | 40.8347 | High | High | High | 208 | 279 | 11.7089 | 8146.0895
FITCH MOUNTAIN 111324918 | FITCH MOUNTAIN 1113 | SONOMA | 5.4494 | 96.6209 | 46.61% | 13 | 1 | 100% | 100% | 0 | 0.17452 | 102.1389 | 2.2832 | 40.6989 | High | High | Medium | 209 | 174 | 17.8255 | 8105.2547
ORO FINO 11022556 | ORO FINO 1102 | NORTH VALLEY | 6.6623 | 79.6419 | 97.8% | 0 | 4 | 100% | 100% | 0 | 0.25169 | 65.3912 | 2.4528 | 40.3695 | High | High | Medium | 210 | 196 | 16.4582 | 8064.5558
BRUNSWICK 11052204 | BRUNSWICK 1105 | SIERRA | 7.2073 | 87.5526 | 78.12% | 3 | 0 | 100% | 100% | 0 | 0.2017 | 85.4511 | 2.3292 | 40.1437 | High | High | Medium | 211 | 183 | 17.2351 | 8024.1864
RINCON 1103568 | RINCON 1103 | SONOMA | 12.8289 | 71.6958 | 48.67% | 11 | 11 | 100% | 100% | 0 | 0.32682 | 47.6367 | 2.5697 | 40.0064 | High | High | Medium | 212 | 210 | 15.5685 | 7984.0427
LAS GALLINAS A 110599904 | LAS GALLINAS A 1105 | NORTH BAY | 5.5637 | 84.5434 | 55.29% | 2 | 2 | 100% | 100% | 0 | 0.17422 | 65.3912 | 3.4864 | 39.7192 | High | High | High | 213 | 283 | 11.3927 | 7944.0362
CALISTOGA 11011085 | CALISTOGA 1101 | NORTH BAY | 2.0832 | 81.9335 | 72.65% | 1 | 1 | 100% | 100% | 0 | 0.23189 | 65.3912 | 2.6122 | 39.6091 | High | High | Medium | 214 | 216 | 15.1634 | 7904.3171
FORESTHILL 110137238 | FORESTHILL 1101 | SIERRA | 11.5057 | 97.4901 | 100% | 2 | 5 | 100% | 100% | 1 | 0.26202 | 85.4511 | 1.7672 | 39.5663 | High | High | Low | 215 | 115 | 22.3899 | 7864.7079
ROSSMOOR 110837848 | ROSSMOOR 1108 | DIABLO | 5.9561 | 79.6593 | 23.72% | 0 | 5 | 100% | 88.12% | 0 | 0.14934 | 65.3912 | 4.0336 | 39.3891 | High | High | High | 216 | 322 | 9.7653 | 7825.1416
PARADISE 11022098 | PARADISE 1102 | NORTH VALLEY | 4.2185 | 79.6766 | 65.19% | 0 | 7 | 42.14% | 100% | 0 | 0.13292 | 85.4511 | 3.448 | 39.1629 | High | High | High | 217 | 284 | 11.3582 | 7785.7526
FITCH MOUNTAIN 11136751 | FITCH MOUNTAIN 1113 | SONOMA | 22.3305 | 96.8838 | 61.93% | 21 | 1 | 100% | 75.68% | 1 | 0.19015 | 85.4511 | 2.409 | 39.1424 | High | High | Medium | 218 | 200 | 16.2482 | 7746.5897
PARADISE 1106CB | PARADISE 1106 | NORTH VALLEY | 4.354 | 81.9365 | 3.23% | 2 | 3 | 96.39% | 100% | 0 | 0.10412 | 102.1389 | 3.6651 | 38.9782 | High | High | High | 219 | 302 | 10.6351 | 7707.4473
DUNBAR 1101343 | DUNBAR 1101 | SONOMA | 4.4643 | 78.5129 | 81.48% | 1 | 3 | 100% | 97.94% | 0 | 0.21869 | 65.3912 | 2.7227 | 38.9349 | High | High | Medium | 220 | 227 | 14.3001 | 7668.4691
SHINGLE SPRINGS 210961892 | SHINGLE SPRINGS 2109 | SIERRA | 30.1835 | 48.4981 | 100% | 2 | 8 | 100% | 100% | 0 | 0.31574 | 47.6367 | 2.5856 | 38.8898 | High | High | Medium | 221 | 219 | 15.0409 | 7629.5342
BRUNSWICK 11062104 | BRUNSWICK 1106 | SIERRA | 9.719 | 86.4087 | 57.37% | 4 | 1 | 100% | 100% | 0 | 0.17938 | 85.4511 | 2.5365 | 38.8801 | High | High | Medium | 222 | 212 | 15.3282 | 7590.6445
PARADISE 110135976 | PARADISE 1101 | NORTH VALLEY | 3.5298 | 50.3669 | 45.43% | 3 | 2 | 100% | 100% | 0 | 0.1201 | 85.4511 | 3.7758 | 38.7488 | High | High | High | 223 | 308 | 10.2625 | 7551.7644
ALLEGHANY 1101CB | ALLEGHANY 1101 | SIERRA | 4.3289 | 94.1851 | 45.96% | 2 | 2 | 100% | 100% | 0 | 0.23753 | 85.4511 | 1.9061 | 38.6887 | High | High | Low | 224 | 145 | 20.2969 | 7513.0156
FULTON 1107604 | FULTON 1107 | SONOMA | 17.5324 | 71.8219 | 64.8% | 2 | 17 | 100% | 100% | 0 | 0.3284 | 47.6367 | 2.4442 | 38.2377 | High | High | Medium | 225 | 208 | 15.6441 | 7474.3269
APPLE HILL 21027502 | APPLE HILL 2102 | SIERRA | 23.0839 | 77.5827 | 99.99% | 4 | 7 | 100% | 82.95% | 0 | 0.24712 | 85.4511 | 1.8048 | 38.1112 | High | High | Low | 226 | 138 | 21.1165 | 7436.0892
SALT SPRINGS 210237300 | SALT SPRINGS 2102 | STOCKTON | 6.9933 | 87.6909 | 82.66% | 1 | 2 | 100% | 100% | 0 | 0.21052 | 85.4511 | 2.1022 | 37.8154 | High | High | Low | 227 | 170 | 17.9888 | 7397.978
CHALLENGE 11025462 | CHALLENGE 1102 | NORTH VALLEY | 23.3648 | 66.9386 | 100% | 8 | 5 | 100% | 97.29% | 1 | 0.30821 | 65.3912 | 1.8735 | 37.7585 | High | High | Low | 228 | 147 | 20.154 | 7360.1626
VOLTA 11029742 | VOLTA 1102 | NORTH VALLEY | 9.1189 | 78.986 | 100% | 1 | 2 | 100% | 94.08% | 0 | 0.25585 | 85.4511 | 1.7244 | 37.6993 | High | High | Low | 229 | 127 | 21.8624 | 7322.4042
KANAKA 11011034 | KANAKA 1101 | NORTH VALLEY | 13.1567 | 96.9359 | 65.02% | 4 | 2 | 100% | 100% | 0 | 0.22603 | 85.4511 | 1.9382 | 37.4363 | High | High | Low | 230 | 158 | 19.3146 | 7284.7049
PARADISE 11042472 | PARADISE 1104 | NORTH VALLEY | 7.3384 | 31.16 | 42.96% | 7 | 6 | 100% | 100% | 0 | 0.14941 | 65.3912 | 3.8266 | 37.3865 | High | High | High | 231 | 321 | 9.7702 | 7247.2686
WEST POINT 1102CB | WEST POINT 1102 | STOCKTON | 17.7809 | 76.7324 | 62.09% | 5 | 4 | 100% | 79.61% | 1 | 0.19732 | 65.3912 | 2.8754 | 37.101 | High | High | Medium | 232 | 255 | 12.9027 | 7209.882
RINCON 1101578 | RINCON 1101 | SONOMA | 17.3381 | 67.0315 | 100% | 2 | 9 | 93.38% | 92.03% | 0 | 0.20486 | 65.3912 | 2.768 | 37.0801 | High | High | Medium | 233 | 243 | 13.3958 | 7172.781
MORAGA 1105CB | MORAGA 1105 | DIABLO | 7.1365 | 67.7298 | 20.75% | 5 | 12 | 65.86% | 77.06% | 1 | 0.092052 | 102.1389 | 3.9271 | 36.9227 | High | High | High | 234 | 329 | 9.4021 | 7135.7009
MIDDLETOWN 11014646 | MIDDLETOWN 1101 | HUMBOLDT | 18.5612 | 85.1867 | 99.86% | 4 | 10 | 100% | 100% | 0 | 0.35694 | 47.6367 | 2.1685 | 36.8721 | High | High | Low | 235 | 188 | 17.0035 | 7098.7782
DUNBAR 1103534 | DUNBAR 1103 | SONOMA | 15.5924 | 79.0775 | 96.69% | 3 | 12 | 89.43% | 96.98% | 1 | 0.28566 | 47.6367 | 2.69 | 36.606 | High | High | Medium | 236 | 235 | 13.6079 | 7061.9061
FORT ROSS 112170288 | FORT ROSS 1121 | SONOMA | 11.744 | 93.8091 | 82.61% | 5 | 5 | 100% | 100% | 0 | 0.2145 | 85.4511 | 1.9739 | 36.1799 | High | High | Low | 237 | 165 | 18.3292 | 7025.3
EL DORADO PH 210119612 | EL DORADO PH 2101 | SIERRA | 9.1713 | 87.7197 | 45.56% | 7 | 1 | 100% | 100% | 0 | 0.19221 | 102.1389 | 1.8339 | 36.0017 | High | High | Low | 238 | 155 | 19.6316 | 6989.1201
WOODSIDE 11018601 | WOODSIDE 1101 | PENINSULA | 0.59795 | 81.8692 | 48.65% | 2 | 0 | 100% | 100% | 0 | 0.14129 | 65.3912 | 3.8817 | 35.8642 | High | High | High | 239 | 335 | 9.2392 | 6953.1184
HIGHLANDS 1103520 | HIGHLANDS 1103 | HUMBOLDT | 46.4816 | 67.4675 | 99% | 5 | 17 | 100% | 0% | 0 | 0.27204 | 47.6367 | 2.7667 | 35.8548 | High | High | Medium | 240 | 253 | 12.9592 | 6917.2542
WILLITS 1104934 | WILLITS 1104 | HUMBOLDT | 30.5846 | 72.5028 | 89.66% | 17 | 12 | 100% | 39.29% | 1 | 0.29588 | 65.3912 | 1.8491 | 35.7756 | High | High | Low | 241 | 157 | 19.3479 | 6881.3994
MOLINO 1101322 | MOLINO 1101 | SONOMA | 15.8907 | 58.1086 | 71.61% | 14 | 10 | 100% | 44.47% | 0 | 0.22351 | 65.3912 | 2.4422 | 35.6935 | High | High | Medium | 242 | 225 | 14.6154 | 6845.6239
AUBERRY 1101R324 | AUBERRY 1101 | FRESNO | 10.7908 | 83.7222 | 99.89% | 3 | 1 | 100% | 100% | 0 | 0.25584 | 85.4511 | 1.6256 | 35.538 | High | High | Low | 243 | 128 | 21.8618 | 6809.9303
DIAMOND SPRINGS 11071402 | DIAMOND SPRINGS 1107 | SIERRA | 44.1487 | 51.2712 | 86.92% | 1 | 21 | 100% | 76.75% | 0 | 0.24689 | 65.3912 | 2.1929 | 35.4032 | High | High | Low | 244 | 202 | 16.1444 | 6774.3923
WILLITS 1103 | WILLITS 1103 | HUMBOLDT | 0.065999 | 98 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21467 | 102.1389 | 1.6051 | 35.1936 | High | High | Low | 245 | 124 | 21.9265 | 6738.9892
MORGAN HILL 21114461 | MORGAN HILL 2111 | SAN JOSE | 2.2769 | 88.7487 | 84.71% | 4 | 2 | 100% | 100% | 0 | 0.19916 | 65.3912 | 2.6877 | 35.0025 | High | High | Medium | 246 | 249 | 13.0233 | 6703.7956
MONTE RIO 111153477 | MONTE RIO 1111 | SONOMA | 2.1403 | 90.336 | 44.25% | 6 | 1 | 100% | 100% | 0 | 0.21276 | 85.4511 | 1.9244 | 34.9877 | High | High | Low | 247 | 168 | 18.1807 | 6668.7931
SHINGLE SPRINGS 210519522 | SHINGLE SPRINGS 2105 | SIERRA | 9.9042 | 70.9474 | 99.53% | 2 | 6 | 96.11% | 80.98% | 0 | 0.17524 | 65.3912 | 2.9822 | 34.1738 | High | High | Medium | 248 | 281 | 11.4593 | 6633.8054
WEST POINT 110236676 | WEST POINT 1102 | STOCKTON | 16.994 | 84.9293 | 78.04% | 3 | 4 | 100% | 93.46% | 0 | 0.24051 | 65.3912 | 2.1683 | 34.1012 | High | High | Low | 249 | 205 | 15.7272 | 6599.6316
SILVERADO 210258626 | SILVERADO 2102 | NORTH BAY | 15.2462 | 83.9933 | 97.52% | 2 | 7 | 100% | 88.88% | 0 | 0.23976 | 47.6367 | 2.967 | 33.8868 | High | High | Medium | 250 | 282 | 11.4212 | 6565.5304
SALT SPRINGS 2102L491 | SALT SPRINGS 2102 | STOCKTON | 2.2143 | 88.9765 | 100% | 2 | 2 | 100% | 100% | 0 | 0.21581 | 102.1389 | 1.5318 | 33.7654 | High | High | Low | 251 | 122 | 22.0423 | 6531.6436
MIRABEL 1101116 | MIRABEL 1101 | SONOMA | 9.7562 | 60.7427 | 68.47% | 10 | 5 | 91.79% | 57.41% | 1 | 0.21711 | 47.6367 | 3.2592 | 33.7085 | High | High | High | 252 | 306 | 10.3426 | 6497.8783
WILLITS 1103968 | WILLITS 1103 | HUMBOLDT | 24.6966 | 68.3381 | 85.93% | 14 | 10 | 88.86% | 68.54% | 1 | 0.21234 | 85.4511 | 1.8563 | 33.6814 | High | High | Low | 253 | 169 | 18.1447 | 6464.1698
AUBERRY 1101D4982 | AUBERRY 1101 | FRESNO | 2.6789 | 91.9989 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20783 | 85.4511 | 1.8789 | 33.3678 | High | High | Low | 254 | 175 | 17.7595 | 6430.4884
APPLE HILL 210297982 | APPLE HILL 2102 | SIERRA | 10.1443 | 88.7232 | 100% | 1 | 1 | 100% | 100% | 0 | 0.23278 | 102.1389 | 1.3898 | 33.0445 | High | High | Low | 255 | 102 | 23.7764 | 6397.1206
OAKLAND K 110217430 | OAKLAND K 1102 | EAST BAY | 2.0764 | 84.0676 | 31.48% | 0 | 1 | 100% | 100% | 0 | 0.12601 | 85.4511 | 3.0426 | 32.7603 | High | High | Medium | 256 | 300 | 10.7674 | 6364.0761
BEN LOMOND 04015144 | BEN LOMOND 0401 | CENTRAL COAST | 3.9861 | 45.8832 | 59.52% | 1 | 1 | 100% | 100% | 0 | 0.13946 | 65.3912 | 3.5854 | 32.6969 | High | High | High | 257 | 337 | 9.1195 | 6331.3158
BRUNSWICK 11053611 | BRUNSWICK 1105 | SIERRA | 1.6138 | 98 | 100% | 0 | 3 | 100% | 100% | 0 | 0.22548 | 102.1389 | 1.4025 | 32.3002 | High | High | Low | 258 | 110 | 23.03 | 6298.6189
CHALLENGE 11021902 | CHALLENGE 1102 | NORTH VALLEY | 5.0391 | 84.0879 | 100% | 3 | 2 | 100% | 100% | 0 | 0.21241 | 65.3912 | 2.2968 | 31.9012 | High | High | Medium | 259 | 231 | 13.8896 | 6266.3187
BRUNSWICK 110663124 | BRUNSWICK 1106 | SIERRA | 5.9024 | 71.9691 | 59.9% | 2 | 1 | 100% | 94.93% | 0 | 0.17164 | 65.3912 | 2.8195 | 31.6447 | High | High | Medium | 260 | 286 | 11.2236 | 6234.4175
PARADISE 11015185 | PARADISE 1101 | NORTH VALLEY | 0.8075 | 38.303 | 73.08% | 0 | 1 | 100% | 100% | 0 | 0.12937 | 65.3912 | 3.7374 | 31.6174 | High | High | High | 261 | 349 | 8.4598 | 6202.7728
PLACERVILLE 21062224 | PLACERVILLE 2106 | SIERRA | 10.4972 | 65.7358 | 76.35% | 3 | 1 | 100% | 100% | 0 | 0.2002 | 47.6367 | 3.3086 | 31.5533 | High | High | High | 262 | 325 | 9.5368 | 6171.1554
CABRILLO 1103Y12 | CABRILLO 1103 | LOS PADRES | 26.1562 | 62.7349 | 69.42% | 1 | 11 | 84.42% | 0% | 0 | 0.20939 | 47.6367 | 3.1607 | 31.5264 | High | High | High | 263 | 315 | 9.9744 | 6139.6021
ROB ROY 21055166 | ROB ROY 2105 | CENTRAL COAST | 5.4938 | 45.154 | 99.95% | 6 | 2 | 100% | 100% | 0 | 0.19719 | 47.6367 | 3.3223 | 31.2078 | High | High | High | 264 | 330 | 9.3933 | 6108.0757
OAKLAND K 1102CB | OAKLAND K 1102 | EAST BAY | 3.0081 | 48.3984 | 19.08% | 4 | 5 | 100% | 100% | 0 | 0.11788 | 65.3912 | 4.048 | 31.203 | High | High | High | 265 | 368 | 7.7083 | 6076.8679
OAKHURST 11015490 | OAKHURST 1101 | YOSEMITE | 24.9631 | 65.8497 | 73.62% | 1 | 51 | 100% | 0% | 0 | 0.18555 | 65.3912 | 2.5688 | 31.1673 | High | High | Medium | 266 | 271 | 12.1331 | 6045.6649
CLAYTON 22122951 | CLAYTON 2212 | DIABLO | 10.1032 | 61.4187 | 78.88% | 4 | 1 | 100% | 100% | 0 | 0.27294 | 35.3263 | 3.2196 | 31.0433 | High | High | High | 267 | 323 | 9.6421 | 6014.4976
MONTE RIO 11131137 | MONTE RIO 1113 | SONOMA | 2.8427 | 88.9858 | 48.94% | 0 | 5 | 100% | 100% | 0 | 0.15775 | 65.3912 | 2.9968 | 30.9141 | High | High | Medium | 268 | 307 | 10.3156 | 5983.4543
LOS GATOS 110712041 | LOS GATOS 1107 | DE ANZA | 6.3296 | 61.8932 | 100% | 5 | 1 | 100% | 100% | 0 | 0.28444 | 47.6367 | 2.2717 | 30.7809 | High | High | Medium | 269 | 238 | 13.5499 | 5952.5401
MIRABEL 1102332 | MIRABEL 1102 | SONOMA | 5.7552 | 66.9134 | 43.76% | 9 | 11 | 100% | 100% | 1 | 0.16469 | 65.3912 | 2.8565 | 30.7615 | High | High | Medium | 270 | 299 | 10.7691 | 5921.7592
PARADISE 11022206 | PARADISE 1102 | NORTH VALLEY | 5.1983 | 53.3962 | 55.37% | 4 | 4 | 89% | 100% | 0 | 0.12523 | 65.3912 | 3.7528 | 30.7318 | High | High | High | 271 | 358 | 8.1891 | 5890.9978
MIRABEL 11014859 | MIRABEL 1101 | SONOMA | 1.8526 | 77.0765 | 99.9% | 8 | 0 | 100% | 100% | 0 | 0.23121 | 47.6367 | 2.7808 | 30.6275 | High | High | Medium | 272 | 296 | 11.014 | 5860.2659
MONTE RIO 111137520 | MONTE RIO 1111 | SONOMA | 2.1617 | 88.6545 | 55.37% | 6 | 0 | 100% | 100% | 0 | 0.18002 | 85.4511 | 1.984 | 30.52 | High | High | Low | 273 | 211 | 15.383 | 5829.6384
CLARKSVILLE 210413352 | CLARKSVILLE 2104 | SIERRA | 32.6724 | 49.7642 | 94.33% | 3 | 19 | 89.71% | 64.9% | 0 | 0.20162 | 47.6367 | 3.1662 | 30.4103 | High | High | High | 274 | 324 | 9.6046 | 5799.1185
APPLE HILL 2102CB | APPLE HILL 2102 | SIERRA | 41.3043 | 54.0794 | 88.14% | 11 | 9 | 100% | 60.25% | 1 | 0.23023 | 65.3912 | 1.9699 | 29.6561 | High | High | Low | 275 | 218 | 15.0548 | 5768.7082
MONTE RIO 11111701 | MONTE RIO 1111 | SONOMA | 1.3661 | 76.5396 | 84.13% | 0 | 0 | 100% | 100% | 0 | 0.17154 | 65.3912 | 2.6378 | 29.5889 | High | High | Medium | 276 | 287 | 11.217 | 5739.052
SALT SPRINGS 2102L7283 | SALT SPRINGS 2102 | STOCKTON | 0.66272 | 87.1614 | 100% | 0 | 1 | 100% | 100% | 0 | 0.20585 | 102.1389 | 1.3967 | 29.3663 | High | High | Low | 277 | 139 | 21.0249 | 5709.4631
GRASS VALLEY 11012766 | GRASS VALLEY 1101 | SIERRA | 3.3601 | 83.6304 | 59.47% | 0 | 1 | 100% | 75.75% | 0 | 0.10872 | 102.1389 | 2.6373 | 29.2861 | High | High | Medium | 278 | 291 | 11.1047 | 5680.0969
CAMP EVERS 210611533 | CAMP EVERS 2106 | CENTRAL COAST | 2.6563 | 88.3756 | 100% | 3 | 0 | 100% | 100% | 0 | 0.2103 | 65.3912 | 2.1282 | 29.2669 | High | High | Low | 279 | 233 | 13.7518 | 5650.8108
POINT MORETTI 110136516 | POINT MORETTI 1101 | CENTRAL COAST | 4.1652 | 32.5436 | 68.9% | 12 | 2 | 100% | 100% | 0 | 0.17749 | 47.6367 | 3.4455 | 29.1317 | High | High | High | 280 | 350 | 8.4551 | 5621.5439
APPLE HILL 110412832 | APPLE HILL 1104 | SIERRA | 15.3272 | 73.0049 | 95.88% | 8 | 6 | 99.79% | 19.25% | 1 | 0.22229 | 65.3912 | 1.9946 | 28.9929 | High | High | Low | 281 | 226 | 14.536 | 5592.4122
PARADISE 110136042 | PARADISE 1101 | NORTH VALLEY | 2.7098 | 42.4595 | 41.3% | 5 | 3 | 86.87% | 100% | 0 | 0.11607 | 65.3912 | 3.8047 | 28.8767 | High | High | High | 282 | 372 | 7.5898 | 5563.4193
VOLTA 11021648 | VOLTA 1102 | NORTH VALLEY | 4.8649 | 85.7622 | 100% | 2 | 2 | 100% | 79.51% | 0 | 0.16163 | 85.4511 | 2.0849 | 28.7959 | High | High | Low | 283 | 232 | 13.8114 | 5534.5426
ALTO 11221212 | ALTO 1122 | NORTH BAY | 1.5919 | 41.9573 | 53.59% | 1 | 4 | 67.44% | 92.64% | 0 | 0.09288 | 85.4511 | 3.6174 | 28.7098 | High | High | High | 284 | 363 | 7.9367 | 5505.7467
BELLEVUE 2103646 | BELLEVUE 2103 | SONOMA | 9.4191 | 67.7942 | 94.53% | 3 | 3 | 77.28% | 93.12% | 0 | 0.17965 | 65.3912 | 2.4439 | 28.7093 | High | High | Medium | 285 | 278 | 11.7473 | 5477.0369
MOLINO 11026917 | MOLINO 1102 | SONOMA | 7.1386 | 86.8229 | 45.11% | 6 | 1 | 100% | 100% | 0 | 0.18864 | 65.3912 | 2.3255 | 28.6861 | High | High | Medium | 286 | 267 | 12.3355 | 5448.3276
KONOCTI 11024300 | KONOCTI 1102 | HUMBOLDT | 26.3294 | 77.3617 | 62.75% | 9 | 28 | 97.14% | 84.42% | 1 | 0.28482 | 47.6367 | 2.1132 | 28.6726 | High | High | Low | 287 | 237 | 13.5681 | 5419.6415
MONTE RIO 1112999 | MONTE RIO 1112 | SONOMA | 0.78347 | 81.1849 | 29.39% | 4 | 2 | 100% | 100% | 0 | 0.13014 | 85.4511 | 2.5578 | 28.4436 | High | High | Medium | 288 | 290 | 11.1202 | 5390.9689
MIRABEL 11022043 | MIRABEL 1102 | SONOMA | 0.56871 | 88.7155 | 17.22% | 0 | 1 | 100% | 100% | 0 | 0.11685 | 85.4511 | 2.8327 | 28.2828 | High | High | Medium | 289 | 314 | 9.9846 | 5362.5253
SALT SPRINGS 210297924 | SALT SPRINGS 2102 | STOCKTON | 5.0873 | 68.1168 | 100% | 5 | 4 | 100% | 100% | 0 | 0.22834 | 85.4511 | 1.4445 | 28.1851 | High | High | Low | 290 | 156 | 19.5118 | 5334.2424
MIWUK 170236888 | MIWUK 1702 | YOSEMITE | 0.61573 | 72.472 | 39.92% | 0 | 2 | 100% | 100% | 0 | 0.12726 | 65.3912 | 3.3823 | 28.1466 | High | High | High | 291 | 353 | 8.3216 | 5306.0573
BRUNSWICK 1106CB | BRUNSWICK 1106 | SIERRA | 8.5018 | 76.2711 | 34.63% | 3 | 2 | 96.43% | 63.8% | 0 | 0.11976 | 85.4511 | 2.733 | 27.9679 | High | High | Medium | 292 | 309 | 10.2335 | 5277.9108
VOLTA 11021502 | VOLTA 1102 | NORTH VALLEY | 7.6156 | 84.4703 | 99.46% | 2 | 2 | 100% | 100% | 0 | 0.2099 | 47.6367 | 2.778 | 27.777 | High | High | Medium | 293 | 313 | 9.999 | 5249.9428
VINEYARD 2108MR172 | VINEYARD 2108 | MISSION | 3.1156 | 86.4654 | 47.06% | 1 | 2 | 35.54% | 100% | 1 | 0.13362 | 65.3912 | 3.178 | 27.7695 | High | High | High | 294 | 342 | 8.7379 | 5222.1658
SILVERADO 2104563322 | SILVERADO 2104 | NORTH BAY | 3.653 | 77.3083 | 48.88% | 3 | 1 | 100% | 100% | 1 | 0.14188 | 65.3912 | 2.9772 | 27.6225 | High | High | Medium | 295 | 334 | 9.2779 | 5194.3964
CAMP EVERS 210660120 | CAMP EVERS 2106 | CENTRAL COAST | 4.3678 | 67.866 | 79.91% | 12 | 0 | 100% | 100% | 0 | 0.20157 | 65.3912 | 2.0826 | 27.4498 | High | High | Low | 296 | 246 | 13.1807 | 5166.7738
SARATOGA 1107167792 | SARATOGA 1107 | DE ANZA | 4.6876 | 89.4882 | 89.82% | 13 | 1 | 100% | 18.23% | 0 | 0.1289 | 65.3912 | 3.2524 | 27.4146 | High | High | High | 297 | 352 | 8.429 | 5139.324
MONTE RIO 1113532 | MONTE RIO 1113 | SONOMA | 0.51993 | 90.7851 | 10.39% | 0 | 0 | 100% | 100% | 0 | 0.11048 | 85.4511 | 2.896 | 27.3401 | High | High | Medium | 298 | 327 | 9.4408 | 5111.9094
LOS GATOS 11072917 | LOS GATOS 1107 | DE ANZA | 7.7152 | 64.4105 | 89.16% | 10 | 1 | 100% | 100% | 0 | 0.23223 | 65.3912 | 1.7943 | 27.2488 | High | High | Low | 299 | 214 | 15.1861 | 5084.5693
PLACERVILLE 210692012 | PLACERVILLE 2106 | SIERRA | 18.5713 | 72.0312 | 64.51% | 6 | 1 | 100% | 92.15% | 0 | 0.22084 | 47.6367 | 2.5843 | 27.1879 | High | High | Medium | 300 | 303 | 10.5203 | 5057.3205
MONTE RIO 1111240 | MONTE RIO 1111 | SONOMA | 3.0687 | 71.6003 | 66.68% | 5 | 7 | 100% | 100% | 0 | 0.21886 | 47.6367 | 2.6045 | 27.1546 | High | High | Medium | 301 | 304 | 10.4259 | 5030.1326
CAMP EVERS 21059031 | CAMP EVERS 2105 | CENTRAL COAST | 1.0934 | 18.456 | 18.86% | 2 | 2 | 100% | 100% | 0 | 0.10201 | 65.3912 | 4.0458 | 26.9866 | High | High | High | 302 | 388 | 6.6703 | 5002.978
MONTE RIO 1112212 | MONTE RIO 1112 | SONOMA | 2.2491 | 44.7156 | 75.38% | 4 | 1 | 100% | 100% | 0 | 0.14298 | 65.3912 | 2.8824 | 26.9492 | High | High | Medium | 303 | 332 | 9.3496 | 4975.9914
KANAKA 110175744 | KANAKA 1101 | NORTH VALLEY | 10.5898 | 74.5656 | 100% | 3 | 3 | 100% | 74.87% | 0 | 0.16375 | 85.4511 | 1.9254 | 26.9403 | High | High | Low | 304 | 230 | 13.9922 | 4949.0422
BIG BASIN 1101CB | BIG BASIN 1101 | CENTRAL COAST | 4.7811 | 77.9416 | 33.87% | 2 | 0 | 100% | 100% | 0 | 0.13944 | 65.3912 | 2.9497 | 26.897 | High | High | Medium | 305 | 338 | 9.1184 | 4922.102
WOODSIDE 11018912 | WOODSIDE 1101 | PENINSULA | 3.8497 | 42.1497 | 27.37% | 5 | 2 | 96.59% | 100% | 0 | 0.15841 | 47.6367 | 3.5396 | 26.7098 | High | High | High | 306 | 373 | 7.5459 | 4895.205
OAKLAND X 1104CR214 | OAKLAND X 1104 | EAST BAY | 2.8836 | 10 | 25.8% | 4 | 2 | 100% | 100% | 0 | 0.13215 | 47.6367 | 4.2427 | 26.7088 | High | High | High | 307 | 396 | 6.2952 | 4868.4951
BURNS 2101CB | BURNS 2101 | CENTRAL COAST | 1.6587 | 56.6807 | 25.38% | 1 | 0 | 100% | 100% | 0 | 0.11419 | 65.3912 | 3.5716 | 26.6705 | High | High | High | 308 | 375 | 7.4673 | 4841.7864
DUNBAR 11021249 | DUNBAR 1102 | SONOMA | 13.5745 | 82.3664 | 58.44% | 5 | 8 | 100% | 36.11% | 1 | 0.11715 | 85.4511 | 2.6217 | 26.2453 | High | High | Medium | 309 | 312 | 10.0108 | 4815.1159
WEST POINT 110293116 | WEST POINT 1102 | STOCKTON | 24.1031 | 66.8044 | 100% | 9 | 9 | 100% | 51.27% | 1 | 0.16857 | 65.3912 | 2.3737 | 26.1657 | High | High | Medium | 310 | 295 | 11.0231 | 4788.8706
SHINGLE SPRINGS 110419502 | SHINGLE SPRINGS 1104 | SIERRA | 42.2119 | 45.6817 | 99.02% | 5 | 5 | 73.54% | 87.16% | 0 | 0.15459 | 65.3912 | 2.57 | 25.9791 | High | High | Medium | 311 | 310 | 10.1086 | 4762.7049
MONTE RIO 111123916 | MONTE RIO 1111 | SONOMA | 5.2149 | 69.8916 | 48.27% | 12 | 5 | 100% | 100% | 0 | 0.20017 | 65.3912 | 1.981 | 25.9302 | High | High | Low | 312 | 248 | 13.0895 | 4736.7258
WOODACRE 11011456 | WOODACRE 1101 | NORTH BAY | 3.8267 | 75.1652 | 37.76% | 1 | 5 | 100% | 88.56% | 0 | 0.14581 | 85.4511 | 2.0696 | 25.7865 | High | High | Low | 313 | 265 | 12.4595 | 4710.7957
BEN LOMOND 1101BL 1101 | BEN LOMOND 1101 | CENTRAL COAST | 8.6011 | 33.9399 | 41.85% | 31 | 2 | 100% | 100% | 0 | 0.22644 | 26.5534 | 4.227 | 25.4156 | High | High | High | 314 | 400 | 6.0127 | 4685.0091
CASTRO VALLEY 1108MR748 | CASTRO VALLEY 1108 | MISSION | 6.2273 | 76.3747 | 18.01% | 3 | 1 | 100% | 95.99% | 0 | 0.13481 | 47.6367 | 3.945 | 25.335 | High | High | High | 315 | 394 | 6.422 | 4659.5936
VOLTA 110254932 | VOLTA 1102 | NORTH VALLEY | 4.3783 | 73.0618 | 100% | 0 | 1 | 100% | 95.18% | 0 | 0.19916 | 65.3912 | 1.937 | 25.2264 | High | High | Low | 316 | 250 | 13.0232 | 4634.2586
WEST POINT 11021391 | WEST POINT 1102 | STOCKTON | 3.974 | 89.103 | 100% | 2 | 3 | 100% | 100% | 0 | 0.26869 | 65.3912 | 1.4346 | 25.2057 | High | High | Low | 317 | 177 | 17.57 | 4609.0322
STANISLAUS 1702L3151 | STANISLAUS 1702 | YOSEMITE | 0.9933 | 86.9694 | 85.25% | 0 | 0 | 100% | 100% | 0 | 0.1833 | 47.6367 | 2.8637 | 25.0046 | High | High | Medium | 318 | 343 | 8.7317 | 4583.8264
MORAGA 1101108540 | MORAGA 1101 | DIABLO | 4.7825 | 66.0707 | 6.533% | 0 | 5 | 99.19% | 93.66% | 1 | 0.10343 | 65.3912 | 3.6968 | 25.0018 | High | High | High | 319 | 385 | 6.7632 | 4558.8219
APPLE HILL 110412842 | APPLE HILL 1104 | SIERRA | 15.4186 | 86.4877 | 86.23% | 1 | 6 | 91.92% | 56.31% | 0 | 0.11821 | 102.1389 | 2.0647 | 24.9288 | High | High | Low | 320 | 273 | 12.0736 | 4533.82
MOLINO 1102178 | MOLINO 1102 | SONOMA | 13.3443 | 48.7979 | 52.24% | 13 | 10 | 88.89% | 58.63% | 0 | 0.18298 | 47.6367 | 2.8177 | 24.5608 | High | High | Medium | 321 | 345 | 8.7167 | 4508.8913
BIG BASIN 11015000 | BIG BASIN 1101 | CENTRAL COAST | 1.9973 | 72.3321 | 15.8% | 2 | 1 | 100% | 100% | 0 | 0.10717 | 65.3912 | 3.5025 | 24.5467 | High | High | High | 322 | 380 | 7.0083 | 4484.3305
BIG BEND 1101180398 | BIG BEND 1101 | NORTH VALLEY | 5.6176 | 75.1769 | 68.58% | 0 | 2 | 100% | 100% | 0 | 0.15837 | 65.3912 | 2.3657 | 24.4991 | High | High | Medium | 323 | 305 | 10.3561 | 4459.7837
MONTE RIO 1111 | MONTE RIO 1111 | SONOMA | 0.032125 | 95 | 0% | 0 | 1 | 100% | 100% | 0 | 0.107 | 85.4511 | 2.6749 | 24.4578 | High | High | Medium | 324 | 336 | 9.1434 | 4435.2847
BRUNSWICK 11052102 | BRUNSWICK 1105 | SIERRA | 3.6478 | 67.9602 | 63.58% | 1 | 3 | 100% | 48.36% | 1 | 0.091021 | 102.1389 | 2.6251 | 24.4045 | High | High | Medium | 325 | 333 | 9.2968 | 4410.8268
MONTE RIO 1111256 | MONTE RIO 1111 | SONOMA | 7.2865 | 62.779 | 22.47% | 12 | 6 | 100% | 100% | 1 | 0.22703 | 35.3263 | 3.0231 | 24.2464 | High | High | Medium | 326 | 361 | 8.0203 | 4386.4224
WOODSIDE 11018972 | WOODSIDE 1101 | PENINSULA | 6.2078 | 92.0365 | 25.89% | 9 | 0 | 100% | 100% | 1 | 0.17321 | 65.3912 | 2.1359 | 24.1909 | High | High | Low | 327 | 285 | 11.3261 | 4362.176
PARADISE 1101CB | PARADISE 1101 | NORTH VALLEY | 2.6336 | 51.0801 | 25.12% | 2 | 4 | 70.38% | 100% | 0 | 0.092062 | 65.3912 | 4.0044 | 24.1067 | High | High | High | 328 | 399 | 6.02 | 4337.9851
CASTRO VALLEY 110810315 | CASTRO VALLEY 1108 | MISSION | 5.494 | 83.0408 | 14.23% | 2 | 0 | 100% | 100% | 0 | 0.14022 | 47.6367 | 3.6086 | 24.1042 | High | High | High | 329 | 387 | 6.6796 | 4313.8784
SHINGLE SPRINGS 21092679 | SHINGLE SPRINGS 2109 | SIERRA | 7.0526 | 59.0742 | 100% | 0 | 2 | 100% | 100% | 1 | 0.17927 | 47.6367 | 2.7934 | 23.8549 | High | High | Medium | 330 | 348 | 8.5398 | 4289.7742
BEAR VALLEY 210513430 | BEAR VALLEY 2105 | YOSEMITE | 13.3191 | 78.8388 | 99.94% | 4 | 1 | 100% | 48.72% | 0 | 0.12752 | 85.4511 | 2.1818 | 23.7734 | High | High | Low | 331 | 298 | 10.8965 | 4265.9193
BUCKS CREEK 11032414 | BUCKS CREEK 1103 | NORTH VALLEY | 6.1362 | 87.0222 | 100% | 6 | 5 | 76.6% | 80.44% | 0 | 0.28097 | 85.4511 | 0.98592 | 23.6715 | High | High | Low | 332 | 100 | 24.0095 | 4242.1459
ORO FINO 1102127563 | ORO FINO 1102 | NORTH VALLEY | 6.9027 | 86.7717 | 100% | 0 | 2 | 100% | 100% | 1 | 0.23179 | 47.6367 | 2.1334 | 23.5558 | High | High | Low | 333 | 294 | 11.0415 | 4218.4744
ATASCADERO 1103A06 | ATASCADERO 1103 | LOS PADRES | 34.0507 | 59.0569 | 96.54% | 3 | 5 | 91.06% | 64.46% | 1 | 0.13601 | 65.3912 | 2.647 | 23.5413 | High | High | Medium | 334 | 341 | 8.8937 | 4194.9187
PIKE CITY 11011720 | PIKE CITY 1101 | SIERRA | 6.0835 | 93.4602 | 100% | 4 | 2 | 100% | 100% | 0 | 0.24982 | 65.3912 | 1.4389 | 23.5061 | High | High | Low | 335 | 199 | 16.3363 | 4171.3774
CLARKSVILLE 210419632 | CLARKSVILLE 2104 | SIERRA | 5.4715 | 65.8905 | 97.91% | 0 | 0 | 60.07% | 97.91% | 1 | 0.12258 | 65.3912 | 2.9244 | 23.441 | High | High | Medium | 336 | 362 | 8.0156 | 4147.8713
SPRING GAP 170210720 | SPRING GAP 1702 | YOSEMITE | 4.7512 | 90.1119 | 100% | 2 | 3 | 100% | 100% | 0 | 0.27005 | 85.4511 | 1.0152 | 23.4266 | High | High | Low | 337 | 109 | 23.076 | 4124.4303
CAMP EVERS 210510786 | CAMP EVERS 2105 | CENTRAL COAST | 4.5287 | 29.7458 | 98.51% | 7 | 0 | 100% | 100% | 1 | 0.21707 | 26.5534 | 4.044 | 23.3096 | High | High | High | 338 | 408 | 5.764 | 4101.0037
MONTE RIO 1112CB | MONTE RIO 1112 | SONOMA | 3.7135 | 57.2951 | 17.86% | 14 | 2 | 100% | 100% | 0 | 0.14693 | 47.6367 | 3.2898 | 23.026 | High | High | High | 339 | 381 | 6.9992 | 4077.6941
OAKLAND X 1106CR266 | OAKLAND X 1106 | EAST BAY | 1.1822 | 88.5589 | 1.895% | 0 | 0 | 100% | 100% | 0 | 0.10237 | 65.3912 | 3.4355 | 22.9974 | High | High | High | 340 | 386 | 6.6941 | 4054.6682
ALLEGHANY 1101804 | ALLEGHANY 1101 | SIERRA | 21.9183 | 93.3631 | 99.35% | 2 | 14 | 100% | 31.47% | 0 | 0.15061 | 85.4511 | 1.7753 | 22.8471 | High | High | Low | 341 | 256 | 12.8696 | 4031.6707
LOS GATOS 110760024 | LOS GATOS 1107 | DE ANZA | 3.9994 | 92.5853 | 100% | 0 | 0 | 100% | 100% | 0 | 0.28225 | 47.6367 | 1.6969 | 22.8161 | High | High | Low | 342 | 240 | 13.4456 | 4008.8236
REDBUD 1101323962 | REDBUD 1101 | HUMBOLDT | 18.9728 | 78.4739 | 90.21% | 1 | 14 | 68.24% | 71.99% | 0 | 0.19082 | 65.3912 | 1.8051 | 22.5244 | High | High | Low | 343 | 263 | 12.4782 | 3986.0075
WHITMORE 11011598 | WHITMORE 1101 | NORTH VALLEY | 33.6511 | 71.823 | 81.12% | 6 | 5 | 100% | 75.5% | 0 | 0.37493 | 85.4511 | 0.69773 | 22.3538 | High | High | Low | 344 | 50 | 32.038 | 3963.4832
TIGER CREEK 0201CB | TIGER CREEK 0201 | STOCKTON | 3.8998 | 93.0419 | 100% | 1 | 1 | 100% | 66.65% | 0 | 0.15361 | 65.3912 | 2.2115 | 22.2145 | High | High | Low | 345 | 311 | 10.0449 | 3941.1294
CHALLENGE 110198174 | CHALLENGE 1101 | NORTH VALLEY | 12.1176 | 88.3942 | 100% | 4 | 1 | 100% | 100% | 0 | 0.34958 | 85.4511 | 0.74174 | 22.157 | High | High | Low | 346 | 61 | 29.8716 | 3918.9149
MONTE RIO 11113891 | MONTE RIO 1111 | SONOMA | 3.5454 | 89.5117 | 50.47% | 2 | 0 | 100% | 100% | 1 | 0.14965 | 65.3912 | 2.2281 | 21.8036 | High | High | Low | 347 | 320 | 9.7859 | 3896.7579
BEN LOMOND 110196738 | BEN LOMOND 1101 | CENTRAL COAST | 6.8007 | 19.3556 | 74.88% | 14 | 2 | 100% | 100% | 0 | 0.21743 | 26.5534 | 3.7528 | 21.6668 | High | High | High | 348 | 407 | 5.7735 | 3874.9543
SHADY GLEN 1102CB | SHADY GLEN 1102 | SIERRA | 20.4139 | 69.5808 | 89.02% | 6 | 13 | 95.14% | 27.66% | 0 | 0.14313 | 85.4511 | 1.7682 | 21.6268 | High | High | Low | 349 | 270 | 12.231 | 3853.2876
PUEBLO 2103 | PUEBLO 2103 | NORTH BAY | 0.012243 | 90 | 0% | 0 | 0 | 100% | 100% | 0 | 0.11472 | 65.3912 | 2.8801 | 21.6062 | High | High | Medium | 350 | 374 | 7.502 | 3831.6608
BRUNSWICK 11051030 | BRUNSWICK 1105 | SIERRA | 4.9418 | 79.0296 | 79.8% | 3 | 3 | 100% | 45.4% | 0 | 0.084675 | 102.1389 | 2.4972 | 21.5975 | High | High | Medium | 351 | 347 | 8.6486 | 3810.0546
BRUNSWICK 11032784 | BRUNSWICK 1103 | SIERRA | 14.361 | 51.6275 | 64.59% | 9 | 6 | 93.84% | 32.3% | 0 | 0.11661 | 65.3912 | 2.7674 | 21.1031 | High | High | Medium | 352 | 371 | 7.6256 | 3788.4571
DRUM 1101CB | DRUM 1101 | SIERRA | 2.1059 | 96.8742 | 100% | 2 | 0 | 100% | 100% | 0 | 0.2937 | 85.4511 | 0.83984 | 21.0773 | High | High | Low | 353 | 94 | 25.0967 | 3767.354
BIG BASIN 110110296 | BIG BASIN 1101 | CENTRAL COAST | 14.4399 | 15.6542 | 52.28% | 39 | 5 | 100% | 100% | 0 | 0.45917 | 14.9507 | 3.0498 | 20.9366 | High | High | Medium | 354 | 384 | 6.8649 | 3746.2768
MONTE RIO 11125040 | MONTE RIO 1112 | SONOMA | 3.9901 | 73.555 | 15.29% | 9 | 5 | 100% | 100% | 1 | 0.12574 | 65.3912 | 2.5232 | 20.7454 | High | High | Medium | 355 | 357 | 8.222 | 3725.3402
BRUNSWICK 1105CB | BRUNSWICK 1105 | SIERRA | 2.0209 | 50.1126 | 64.77% | 1 | 2 | 85.09% | 53.11% | 0 | 0.075406 | 102.1389 | 2.6516 | 20.4226 | High | High | Medium | 356 | 369 | 7.7019 | 3704.5947
OLEMA 110150396 | OLEMA 1101 | NORTH BAY | 12.5505 | 59.0331 | 35.48% | 29 | 15 | 95.94% | 0% | 0 | 0.11931 | 65.3912 | 2.6117 | 20.3759 | High | High | Medium | 357 | 367 | 7.8017 | 3684.1721
CAMP EVERS 210533542 | CAMP EVERS 2105 | CENTRAL COAST | 2.4779 | 18.5991 | 43.01% | 16 | 2 | 100% | 100% | 0 | 0.1603 | 35.3263 | 3.5621 | 20.1718 | High | High | High | 358 | 410 | 5.6629 | 3663.7963
CALISTOGA 1102706 | CALISTOGA 1102 | NORTH BAY | 0.14479 | 80 | 100% | 0 | 1 | 2.91% | 100% | 0 | 0.085322 | 65.3912 | 3.5861 | 20.0081 | High | High | High | 359 | 411 | 5.5793 | 3643.6244
PARADISE 1105CB | PARADISE 1105 | NORTH VALLEY | 3.6905 | 42.5038 | 17.46% | 4 | 4 | 44.69% | 100% | 0 | 0.058684 | 85.4511 | 3.9436 | 19.7758 | Medium | Medium | High | 360 | 427 | 5.0146 | 3623.6163
FULTON 110777670 | FULTON 1107 | SONOMA | 6.8809 | 26.8333 | 74.89% | 3 | 6 | 100% | 100% | 0 | 0.17389 | 47.6367 | 2.3868 | 19.7715 | High | High | Medium | 361 | 354 | 8.2837 | 3603.8405
BRUNSWICK 11052100 | BRUNSWICK 1105 | SIERRA | 3.9656 | 82.5395 | 61.98% | 2 | 1 | 100% | 39.89% | 0 | 0.074817 | 102.1389 | 2.5653 | 19.6029 | High | High | Medium | 362 | 370 | 7.6417 | 3584.069
LOS GATOS 1106LA46 | LOS GATOS 1106 | DE ANZA | 1.5345 | 25.7114 | 95.32% | 1 | 0 | 100% | 100% | 0 | 0.15665 | 47.6367 | 2.6204 | 19.5546 | High | High | Medium | 363 | 376 | 7.4623 | 3564.466
COARSEGOLD 21045310 | COARSEGOLD 2104 | YOSEMITE | 17.6177 | 41.6297 | 82.56% | 2 | 60 | 100% | 0% | 0 | 0.18205 | 47.6367 | 2.2493 | 19.5069 | High | High | Medium | 364 | 346 | 8.6723 | 3544.9114
SILVERADO 2102 | SILVERADO 2102 | NORTH BAY | 0.0045192 | 80 | 100% | 0 | 0 | 100% | 100% | 0 | 0.19464 | 35.3263 | 2.7872 | 19.1644 | High | High | Medium | 365 | 383 | 6.876 | 3525.4045
MIRABEL 11021139 | MIRABEL 1102 | SONOMA | 2.0153 | 64.752 | 50.11% | 2 | 2 | 100% | 100% | 0 | 0.1338 | 47.6367 | 2.9996 | 19.1194 | High | High | Medium | 366 | 395 | 6.374 | 3506.2401
MONTE RIO 1111506 | MONTE RIO 1111 | SONOMA | 1.1523 | 40.8732 | 25.9% | 6 | 0 | 100% | 100% | 0 | 0.097983 | 47.6367 | 4.0934 | 19.1062 | High | High | High | 367 | 446 | 4.6676 | 3487.1207
PARADISE 110476064 | PARADISE 1104 | NORTH VALLEY | 6.3823 | 13.6814 | 48.59% | 6 | 11 | 100% | 100% | 1 | 0.13538 | 35.3263 | 3.9849 | 19.0574 | High | High | High | 368 | 440 | 4.7824 | 3468.0145
MENDOCINO 110148750 | MENDOCINO 1101 | HUMBOLDT | 17.302 | 87.2326 | 98.93% | 5 | 5 | 100% | 70.23% | 0 | 0.19367 | 65.3912 | 1.5047 | 19.056 | High | High | Low | 369 | 259 | 12.6646 | 3448.9571
KANAKA 11011044 | KANAKA 1101 | NORTH VALLEY | 6.134 | 63.1535 | 33.69% | 2 | 5 | 100% | 70.49% | 0 | 0.080757 | 102.1389 | 2.2945 | 18.9261 | High | High | Medium | 370 | 355 | 8.2484 | 3429.901
SHINGLE SPRINGS 21092053 | SHINGLE SPRINGS 2109 | SIERRA | 5.7202 | 32.6339 | 100% | 0 | 1 | 100% | 100% | 0 | 0.16944 | 47.6367 | 2.343 | 18.912 | High | High | Medium | 371 | 360 | 8.0716 | 3410.975
SAN RAMON 2108CB | SAN RAMON 2108 | MISSION | 8.6488 | 65.614 | 48.13% | 2 | 4 | 90.54% | 100% | 0 | 0.12664 | 47.6367 | 3.1076 | 18.7479 | High | High | High | 372 | 398 | 6.0329 | 3392.063
SILVERADO 2104 | SILVERADO 2104 | NORTH BAY | 0.061489 | 85 | 0% | 0 | 0 | 100% | 100% | 0 | 0.098754 | 65.3912 | 2.8976 | 18.7118 | High | High | Medium | 373 | 391 | 6.4577 | 3373.3151
CASTRO VALLEY 11068971 | CASTRO VALLEY 1106 | MISSION | 7.918 | 68.6499 | 16.36% | 0 | 1 | 100% | 100% | 0 | 0.11574 | 47.6367 | 3.3887 | 18.6837 | High | High | High | 374 | 414 | 5.5135 | 3354.6034
MIDDLETOWN 110148212 | MIDDLETOWN 1101 | HUMBOLDT | 10.2049 | 74.7586 | 62.81% | 5 | 4 | 94.29% | 99.65% | 0 | 0.19647 | 47.6367 | 1.9845 | 18.5737 | High | High | Low | 375 | 331 | 9.3592 | 3335.9197
BERKELEY F 1103BR110 | BERKELEY F 1103 | EAST BAY | 1.8512 | 58.149 | 51.38% | 3 | 2 | 32.55% | 100% | 0 | 0.071417 | 65.3912 | 3.9728 | 18.5534 | High | High | High | 376 | 445 | 4.67 | 3317.346
OAKLAND K 110491060 | OAKLAND K 1104 | EAST BAY | 0.36025 | 77.0512 | 0% | 0 | 0 | 100% | 100% | 0 | 0.094019 | 47.6367 | 4.1348 | 18.5187 | High | High | High | 377 | 457 | 4.4788 | 3298.7926
WASHINGTON CITY GEN. 1101CB | WASHINGTON CITY GEN. 1101 | SIERRA | 0.012645 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 65.3912 | 1.3761 | 18.5003 | High | High | Low | 378 | 241 | 13.4438 | 3280.2739
WASHINGTON CITY GEN. 11011101/2 | WASHINGTON CITY GEN. 1101 | SIERRA | 0.0035486 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 65.3912 | 1.3746 | 18.4792 | High | High | Low | 379 | 241 | 13.4438 | 3261.7736
KONOCTI 11024421 | KONOCTI 1102 | HUMBOLDT | 0.36385 | 69.0599 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18318 | 47.6367 | 2.1152 | 18.4571 | High | High | Low | 380 | 344 | 8.726 | 3243.2944
WILLOW CREEK 11015002 | WILLOW CREEK 1101 | HUMBOLDT | 12.8071 | 51.1134 | 93.52% | 24 | 21 | 94.53% | 2.43% | 0 | 0.18408 | 65.3912 | 1.5331 | 18.4537 | High | High | Low | 381 | 275 | 12.0369 | 3224.8373
BRUNSWICK 110750010 | BRUNSWICK 1107 | SIERRA | 4.0845 | 61.0721 | 60.14% | 3 | 2 | 43.91% | 47.61% | 1 | 0.056677 | 102.1389 | 3.1817 | 18.4187 | Medium | Medium | High | 382 | 405 | 5.789 | 3206.3836
CALPINE 1146200-G | CALPINE 1146 | SONOMA | 0.0085256 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 47.6367 | 1.8538 | 18.1558 | High | High | Low | 383 | 317 | 9.7937 | 3187.9649
CALPINE 1146394G | CALPINE 1146 | SONOMA | 0.011293 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 47.6367 | 1.8534 | 18.1516 | High | High | Low | 384 | 317 | 9.7937 | 3169.8091
CORRAL 1101CB | CORRAL 1101 | STOCKTON | 26.1508 | 58.878 | 76.15% | 2 | 13 | 95.28% | 0% | 0 | 0.12599 | 65.3912 | 2.1911 | 18.0518 | High | High | Low | 385 | 356 | 8.2388 | 3151.6575
POINT MORETTI 11015401 | POINT MORETTI 1101 | CENTRAL COAST | 2.5449 | 35.7837 | 49.53% | 3 | 0 | 100% | 100% | 0 | 0.12284 | 47.6367 | 3.0798 | 18.0223 | High | High | High | 386 | 402 | 5.8517 | 3133.6057
ORO FINO 11022040 | ORO FINO 1102 | NORTH VALLEY | 9.1589 | 98 | 100% | 4 | 1 | 100% | 12.34% | 0 | 0.10744 | 102.1389 | 1.639 | 17.9858 | High | High | Low | 387 | 297 | 10.9734 | 3115.5835
PINE GROVE 1102CB | PINE GROVE 1102 | STOCKTON | 10.707 | 66.221 | 86.49% | 3 | 11 | 100% | 3.567% | 1 | 0.074056 | 65.3912 | 3.6625 | 17.7359 | High | High | High | 388 | 434 | 4.8426 | 3097.5977
POINT MORETTI 11015078 | POINT MORETTI 1101 | CENTRAL COAST | 14.6844 | 28.4071 | 32.64% | 18 | 2 | 100% | 99.93% | 1 | 0.2007 | 26.5534 | 3.3009 | 17.5911 | High | High | High | 389 | 418 | 5.3293 | 3079.8618
PUEBLO 2102618 | PUEBLO 2102 | NORTH BAY | 2.0485 | 88.1559 | 93.93% | 0 | 0 | 12.3% | 100% | 0 | 0.11649 | 47.6367 | 3.1658 | 17.5673 | High | High | High | 390 | 412 | 5.5491 | 3062.2707
SAN RAMON 210853732 | SAN RAMON 2108 | MISSION | 7.923 | 73.3065 | 51.9% | 0 | 2 | 100% | 100% | 0 | 0.15613 | 35.3263 | 3.1822 | 17.5521 | High | High | High | 391 | 413 | 5.5156 | 3044.7033
CAMP EVERS 210510912 | CAMP EVERS 2105 | CENTRAL COAST | 4.9849 | 57.147 | 56.28% | 17 | 4 | 100% | 100% | 0 | 0.22661 | 19.9979 | 3.8168 | 17.2965 | High | High | High | 392 | 456 | 4.5316 | 3027.1513
WOODSIDE 11011922 | WOODSIDE 1101 | PENINSULA | 3.7722 | 56.2856 | 79.83% | 3 | 6 | 79.05% | 92.98% | 1 | 0.14505 | 47.6367 | 2.5025 | 17.2916 | High | High | Medium | 393 | 382 | 6.9098 | 3009.8548
SHINGLE SPRINGS 210551738 | SHINGLE SPRINGS 2105 | SIERRA | 0.38011 | 59.0013 | 92.98% | 0 | 0 | 33.17% | 96.59% | 0 | 0.087308 | 65.3912 | 3.0193 | 17.2376 | High | High | Medium | 394 | 409 | 5.7091 | 2992.5631
TASSAJARA 21126392 | TASSAJARA 2112 | DIABLO | 5.4625 | 75.7434 | 2.892% | 0 | 3 | 100% | 100% | 0 | 0.10087 | 47.6367 | 3.5168 | 16.8979 | High | High | High | 395 | 438 | 4.8049 | 2975.3255
OAKLAND K 1104CR326 | OAKLAND K 1104 | EAST BAY | 1.3049 | 10 | 98.1% | 3 | 0 | 100% | 100% | 0 | 0.14914 | 26.5534 | 4.2299 | 16.7511 | High | High | High | 396 | 480 | 3.9602 | 2958.4276
MONTE RIO 1111140 | MONTE RIO 1111 | SONOMA | 2.6327 | 49.961 | 28.63% | 14 | 1 | 100% | 100% | 0 | 0.18634 | 26.5534 | 3.3089 | 16.3721 | High | High | High | 397 | 432 | 4.9479 | 2941.6766
SHADY GLEN 11022232 | SHADY GLEN 1102 | SIERRA | 10.57 | 94.8997 | 90.23% | 5 | 11 | 100% | 60.37% | 0 | 0.14836 | 85.4511 | 1.2808 | 16.2381 | High | High | Low | 398 | 258 | 12.6776 | 2925.3045
OTTER 11012052 | OTTER 1101 | CENTRAL COAST | 4.8416 | 80.234 | 20.15% | 9 | 2 | 100% | 100% | 0 | 0.14395 | 65.3912 | 1.7174 | 16.1669 | High | High | Low | 399 | 328 | 9.4134 | 2909.0664
SANTA ROSA A 1104642 | SANTA ROSA A 1104 | SONOMA | 13.3386 | 23.4287 | 85.18% | 3 | 22 | 100% | 84.73% | 0 | 0.24187 | 26.5534 | 2.5097 | 16.1186 | High | High | Medium | 400 | 393 | 6.4225 | 2892.8995
BEN LOMOND 04015206 | BEN LOMOND 0401 | CENTRAL COAST | 7.179 | 20.3543 | 52.81% | 22 | 2 | 100% | 100% | 0 | 0.16558 | 26.5534 | 3.6563 | 16.0757 | High | High | High | 401 | 463 | 4.3967 | 2876.7809
FORT ROSS 11212987 | FORT ROSS 1121 | SONOMA | 2.0798 | 87.0149 | 100% | 0 | 1 | 100% | 83.64% | 0 | 0.16552 | 47.6367 | 2.0189 | 15.9187 | High | High | Low | 402 | 366 | 7.8847 | 2860.7053
POINT MORETTI 110139126 | POINT MORETTI 1101 | CENTRAL COAST | 2.2477 | 14.3797 | 26.31% | 9 | 1 | 100% | 100% | 0 | 0.099437 | 47.6367 | 3.3437 | 15.8387 | High | High | High | 403 | 443 | 4.7369 | 2844.7866
OAKHURST 11035120 | OAKHURST 1103 | YOSEMITE | 6.3491 | 97.3123 | 0.04473% | 0 | 2 | 100% | 100% | 0 | 0.11061 | 85.4511 | 1.6703 | 15.7864 | High | High | Low | 404 | 326 | 9.4514 | 2828.9478
POINT MORETTI 110110726 | POINT MORETTI 1101 | CENTRAL COAST | 10.5855 | 11.8484 | 44.34% | 15 | 5 | 100% | 100% | 1 | 0.18125 | 26.5534 | 3.2767 | 15.7704 | High | High | High | 405 | 436 | 4.8128 | 2813.1615
PINE GROVE 11021765 | PINE GROVE 1102 | STOCKTON | 1.4479 | 48.9693 | 100% | 0 | 0 | 100% | 66.6% | 0 | 0.10186 | 47.6367 | 3.2382 | 15.7126 | High | High | High | 406 | 433 | 4.8523 | 2797.3911
WILLITS 1103826 | WILLITS 1103 | HUMBOLDT | 7.7428 | 68.4696 | 97.36% | 4 | 8 | 100% | 35.78% | 0 | 0.11113 | 65.3912 | 2.1617 | 15.7088 | High | High | Low | 407 | 377 | 7.267 | 2781.6785
SCE REFUGIO 1101CB | SCE REFUGIO 1101 | LOS PADRES | 0.29161 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 47.6367 | 1.5755 | 15.4297 | High | High | Low | 408 | 317 | 9.7937 | 2765.9698
MORAGA 110118216 | MORAGA 1101 | DIABLO | 5.0361 | 38.4811 | 22.22% | 5 | 16 | 100% | 100% | 0 | 0.24183 | 19.9979 | 3.1723 | 15.3416 | High | High | High | 409 | 435 | 4.8362 | 2750.5401
PIKE CITY 1102CB | PIKE CITY 1102 | SIERRA | 9.4149 | 96.7439 | 75.24% | 4 | 3 | 100% | 100% | 0 | 0.19876 | 65.3912 | 1.1735 | 15.2521 | High | High | Low | 410 | 251 | 12.9975 | 2735.1985
PARADISE 1103CB | PARADISE 1103 | NORTH VALLEY | 2.4339 | 10 | 32.27% | 5 | 0 | 48.95% | 100% | 0 | 0.058983 | 65.3912 | 3.9165 | 15.1058 | Medium | Medium | High | 411 | 483 | 3.857 | 2719.9464
TASSAJARA 210865438 | TASSAJARA 2108 | DIABLO | 0.52908 | 90 | 0% | 0 | 2 | 14.01% | 100% | 0 | 0.054006 | 85.4511 | 3.2509 | 15.0026 | Medium | Medium | High | 412 | 451 | 4.6148 | 2704.8406
MIDDLETOWN 1101CB | MIDDLETOWN 1101 | HUMBOLDT | 8.5904 | 74.5605 | 79.65% | 0 | 4 | 45.66% | 67.1% | 0 | 0.067737 | 85.4511 | 2.5869 | 14.9736 | High | High | Medium | 413 | 406 | 5.7882 | 2689.838
DUNBAR 1101302 | DUNBAR 1101 | SONOMA | 7.7166 | 55.3691 | 64.87% | 1 | 11 | 75.08% | 68.56% | 0 | 0.15076 | 35.3263 | 2.7974 | 14.8986 | High | High | Medium | 414 | 419 | 5.3259 | 2674.8644
OAKHURST 11035470 | OAKHURST 1103 | YOSEMITE | 9.6183 | 65.532 | 32.55% | 7 | 21 | 100% | 20.07% | 0 | 0.090249 | 65.3912 | 2.5209 | 14.8769 | High | High | Medium | 415 | 401 | 5.9015 | 2659.9659
WEST POINT 110272036 | WEST POINT 1102 | STOCKTON | 2.3575 | 87.7642 | 47.51% | 4 | 2 | 100% | 22.74% | 0 | 0.055692 | 85.4511 | 3.115 | 14.8241 | Medium | Medium | High | 416 | 441 | 4.759 | 2645.089
CLAYTON 22127758 | CLAYTON 2212 | DIABLO | 3.2393 | 62.3034 | 85.96% | 2 | 0 | 100% | 100% | 0 | 0.16375 | 26.5534 | 3.2939 | 14.3225 | High | High | High | 417 | 466 | 4.3482 | 2630.2649
SHINGLE SPRINGS 210851476 | SHINGLE SPRINGS 2108 | SIERRA | 2.9778 | 55.1791 | 91.84% | 0 | 4 | 47.94% | 85.32% | 1 | 0.09969 | 47.6367 | 3.0157 | 14.3213 | High | High | Medium | 418 | 442 | 4.7489 | 2615.9424
BIG BASIN 11029741 | BIG BASIN 1102 | CENTRAL COAST | 0.65144 | 10 | 32.18% | 5 | 0 | 100% | 100% | 0 | 0.10666 | 47.6367 | 2.8083 | 14.2687 | High | High | Medium | 419 | 425 | 5.0809 | 2601.621
SANTA ROSA A 1104716 | SANTA ROSA A 1104 | SONOMA | 8.9162 | 55.6538 | 91.58% | 1 | 3 | 100% | 100% | 0 | 0.19056 | 26.5534 | 2.7943 | 14.1391 | High | High | Medium | 420 | 426 | 5.06 | 2587.3523
POINT MORETTI 110110722 | POINT MORETTI 1101 | CENTRAL COAST | 0.60606 | 15.6405 | 41.46% | 0 | 0 | 100% | 100% | 0 | 0.087584 | 47.6367 | 3.3583 | 14.0116 | High | High | High | 421 | 473 | 4.1722 | 2573.2133
VOLTA 110237350 | VOLTA 1102 | NORTH VALLEY | 24.2981 | 64.1392 | 95.8% | 2 | 5 | 100% | 58.24% | 1 | 0.17108 | 47.6367 | 1.7111 | 13.9446 | High | High | Low | 422 | 359 | 8.1495 | 2559.2017
WILLOW CREEK 1102CB | WILLOW CREEK 1102 | HUMBOLDT | 7.3308 | 78.4297 | 99.3% | 9 | 9 | 100% | 47.32% | 0 | 0.15188 | 65.3912 | 1.3937 | 13.8422 | High | High | Low | 423 | 316 | 9.9319 | 2545.2571
CAMP EVERS 210616000 | CAMP EVERS 2106 | CENTRAL COAST | 2.1434 | 16.7013 | 23.49% | 1 | 3 | 54.85% | 97.54% | 1 | 0.067002 | 65.3912 | 3.147 | 13.7878 | High | High | High | 424 | 464 | 4.3813 | 2531.4149
CAMP EVERS 210511384 | CAMP EVERS 2105 | CENTRAL COAST | 4.1064 | 10 | 25.57% | 1 | 1 | 100% | 100% | 0 | 0.11123 | 26.5534 | 4.6612 | 13.7668 | High | High | High | 425 | 535 | 2.9535 | 2517.6271
EAST QUINCY 11012452 | EAST QUINCY 1101 | NORTH VALLEY | 1.102 | 63.1536 | 79.93% | 0 | 1 | 13.25% | 52.23% | 1 | 0.04476 | 102.1389 | 3.0006 | 13.7179 | Medium | Medium | Medium | 426 | 455 | 4.5718 | 2503.8602
VOLTA 11021646 | VOLTA 1102 | NORTH VALLEY | 22.2648 | 70.368 | 99.98% | 0 | 4 | 92.24% | 75.72% | 0 | 0.14906 | 47.6367 | 1.9175 | 13.6151 | High | High | Low | 427 | 379 | 7.1006 | 2490.1424
ELECTRA 11017104 | ELECTRA 1101 | STOCKTON | 12.3464 | 47.2231 | 81.14% | 1 | 3 | 100% | 0% | 0 | 0.072301 | 65.3912 | 2.8473 | 13.4619 | High | High | Medium | 428 | 444 | 4.7279 | 2476.5272
MONTE RIO 1111CB | MONTE RIO 1111 | SONOMA | 0.26962 | 44.4262 | 0% | 0 | 1 | 100% | 100% | 0 | 0.078152 | 47.6367 | 3.5806 | 13.3304 | High | High | High | 429 | 491 | 3.7229 | 2463.0654
MIWUK 170179118 | MIWUK 1701 | YOSEMITE | 0.019355 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 26.5534 | 3.7802 | 13.0713 | High | High | High | 430 | 507 | 3.4578 | 2449.7349
ANNAPOLIS 1101554 | ANNAPOLIS 1101 | HUMBOLDT | 27.1366 | 85.1288 | 100% | 26 | 12 | 100% | 0% | 0 | 0.1656 | 47.6367 | 1.6533 | 13.0418 | High | High | Low | 431 | 365 | 7.8886 | 2436.6636
SONOMA 1106376 | SONOMA 1106 | SONOMA | 0.6618 | 42.582 | 100% | 0 | 0 | 12.23% | 100% | 0 | 0.072044 | 47.6367 | 3.7402 | 12.8361 | High | High | High | 432 | 508 | 3.4319 | 2423.6218
SALMON CREEK 110188998 | SALMON CREEK 1101 | SONOMA | 8.1183 | 72.1541 | 32.11% | 1 | 1 | 59.97% | 96.61% | 1 | 0.10072 | 47.6367 | 2.6582 | 12.7544 | High | High | Medium | 433 | 439 | 4.7981 | 2410.7857
VOLTA 1102CB | VOLTA 1102 | NORTH VALLEY | 3.2998 | 84.686 | 16.79% | 3 | 0 | 100% | 100% | 0 | 0.11557 | 47.6367 | 2.3012 | 12.6696 | High | High | Medium | 434 | 415 | 5.5056 | 2398.0314
OAKLAND X 1104CR022 | OAKLAND X 1104 | EAST BAY | 5.946 | 14.8032 | 44.25% | 8 | 4 | 100% | 100% | 0 | 0.14986 | 19.9979 | 4.2262 | 12.6657 | High | High | High | 435 | 532 | 2.997 | 2385.3618
MONTE RIO 1113250 | MONTE RIO 1113 | SONOMA | 1.2254 | 74.4629 | 18.87% | 1 | 1 | 100% | 100% | 0 | 0.1235 | 35.3263 | 2.8957 | 12.6334 | High | High | Medium | 436 | 465 | 4.3628 | 2372.6961
CAMP EVERS 21045096 | CAMP EVERS 2104 | CENTRAL COAST | 20.6359 | 43.5028 | 64.15% | 34 | 7 | 100% | 100% | 0 | 0.33163 | 11.2183 | 3.3817 | 12.581 | High | High | High | 437 | 492 | 3.7203 | 2360.0626
BRUNSWICK 110456468 | BRUNSWICK 1104 | SIERRA | 5.7301 | 68.1683 | 52.05% | 5 | 6 | 95.81% | 0% | 0 | 0.070779 | 65.3912 | 2.7112 | 12.5481 | High | High | Medium | 438 | 449 | 4.6283 | 2347.4817
SILVERADO 21038401 | SILVERADO 2103 | NORTH BAY | 0.63211 | 87.9301 | 93.73% | 0 | 0 | 9.105% | 100% | 0 | 0.088787 | 65.3912 | 2.1595 | 12.5377 | High | High | Low | 439 | 404 | 5.8059 | 2334.9336
RINCON 11035152 | RINCON 1103 | SONOMA | 1.5925 | 84.6014 | 46.06% | 2 | 0 | 100% | 100% | 0 | 0.14097 | 35.3263 | 2.5132 | 12.5158 | High | High | Medium | 440 | 430 | 4.9799 | 2322.3959
CAMP EVERS 210511010 | CAMP EVERS 2105 | CENTRAL COAST | 2.2251 | 32.8132 | 34.55% | 4 | 3 | 100% | 100% | 0 | 0.11572 | 26.5534 | 3.9822 | 12.2369 | High | High | High | 441 | 526 | 3.0729 | 2309.8801
CRESCENT MILLS 21013113 | CRESCENT MILLS 2101 | NORTH VALLEY | 1.193 | 94.468 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049705 | 85.4511 | 2.837 | 12.0498 | Medium | Medium | Medium | 442 | 472 | 4.2473 | 2297.6432
MEADOW LANE 2106C558R | MEADOW LANE 2106 | DIABLO | 0.20712 | 95 | 0% | 0 | 0 | 1.459% | 100% | 0 | 0.041876 | 85.4511 | 3.36 | 12.0232 | Medium | Medium | High | 443 | 501 | 3.5783 | 2285.5934
MIDDLETOWN 11011325 | MIDDLETOWN 1101 | HUMBOLDT | 8.5949 | 66.5337 | 99.94% | 1 | 2 | 100% | 100% | 0 | 0.23318 | 26.5534 | 1.9402 | 12.0132 | High | High | Low | 444 | 397 | 6.1918 | 2273.5702
BIG BASIN 110165444 | BIG BASIN 1101 | CENTRAL COAST | 0.47094 | 48.0736 | 0% | 2 | 0 | 100% | 100% | 0 | 0.090816 | 35.3263 | 3.743 | 12.0083 | High | High | High | 445 | 518 | 3.2082 | 2261.557
GARBERVILLE 11022500 | GARBERVILLE 1102 | HUMBOLDT | 16.0185 | 91.6655 | 50.61% | 18 | 6 | 100% | 0% | 0 | 0.098692 | 85.4511 | 1.4185 | 11.9622 | High | High | Low | 446 | 351 | 8.4333 | 2249.5487
CORRAL 110112608 | CORRAL 1101 | STOCKTON | 35.0176 | 52.1044 | 87.04% | 0 | 19 | 100% | 0% | 0 | 0.16618 | 47.6367 | 1.4909 | 11.8026 | High | High | Low | 447 | 364 | 7.9163 | 2237.5864
MIDDLETOWN 1101622 | MIDDLETOWN 1101 | HUMBOLDT | 15.6831 | 77.1942 | 76.84% | 4 | 8 | 78.63% | 70.55% | 1 | 0.1922 | 26.5534 | 2.3118 | 11.7983 | High | High | Medium | 448 | 424 | 5.1034 | 2225.7839
DUNBAR 11021285 | DUNBAR 1102 | SONOMA | 4.061 | 83.8717 | 58.26% | 1 | 2 | 100% | 27.24% | 1 | 0.053737 | 65.3912 | 3.3515 | 11.7769 | Medium | Medium | High | 449 | 505 | 3.5139 | 2213.9856
PETALUMA C 1108208 | PETALUMA C 1108 | SONOMA | 12.4029 | 84.7631 | 33.65% | 1 | 1 | 100% | 0% | 0 | 0.07858 | 65.3912 | 2.287 | 11.7516 | High | High | Medium | 450 | 423 | 5.1384 | 2202.2086
RESEARCH 21029746 | RESEARCH 2102 | DIABLO | 0.70252 | 57.1565 | 2.503% | 0 | 3 | 24.99% | 100% | 0 | 0.044375 | 85.4511 | 3.091 | 11.7205 | Medium | Medium | High | 451 | 487 | 3.7919 | 2190.457
MONTE RIO 11135024 | MONTE RIO 1113 | SONOMA | 0.33932 | 27.3622 | 58.73% | 2 | 0 | 100% | 100% | 0 | 0.10965 | 35.3263 | 3.0239 | 11.7136 | High | High | Medium | 452 | 482 | 3.8736 | 2178.7365
PARADISE 110181966 | PARADISE 1101 | NORTH VALLEY | 0.1834 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 47.6367 | 3.9719 | 11.6474 | High | High | High | 453 | 540 | 2.9325 | 2167.0229
COTATI 1105CB | COTATI 1105 | SONOMA | 3.1602 | 63.5412 | 54.85% | 1 | 0 | 100% | 0% | 0 | 0.061793 | 65.3912 | 2.8768 | 11.6244 | High | High | Medium | 454 | 477 | 4.0407 | 2155.3755
BRUNSWICK 1102CB | BRUNSWICK 1102 | SIERRA | 6.3271 | 51.9471 | 61.35% | 4 | 0 | 99.87% | 31.38% | 0 | 0.047536 | 85.4511 | 2.763 | 11.2233 | Medium | Medium | Medium | 455 | 476 | 4.062 | 2143.7511
BONNIE NOOK 110186696 | BONNIE NOOK 1101 | SIERRA | 9.7026 | 94.616 | 77.04% | 2 | 5 | 100% | 100% | 0 | 0.2013 | 85.4511 | 0.64933 | 11.1691 | High | High | Low | 456 | 184 | 17.2011 | 2132.5278
KONOCTI 110275382 | KONOCTI 1102 | HUMBOLDT | 21.8665 | 65.7136 | 85.11% | 11 | 7 | 94.25% | 84.3% | 0 | 0.27016 | 19.9979 | 2.0627 | 11.1439 | High | High | Low | 457 | 417 | 5.4025 | 2121.3586
PARADISE 110236656 | PARADISE 1102 | NORTH VALLEY | 3.3309 | 17.0477 | 19.52% | 3 | 5 | 87.51% | 100% | 0 | 0.076178 | 35.3263 | 4.1355 | 11.129 | High | High | High | 458 | 552 | 2.6911 | 2110.2147
HAMILTON BRANCH 110190334 | HAMILTON BRANCH 1101 | NORTH VALLEY | 3.3715 | 83.9014 | 99.76% | 0 | 0 | 100% | 0% | 0 | 0.046313 | 85.4511 | 2.8026 | 11.0913 | Medium | Medium | Medium | 459 | 481 | 3.9575 | 2099.0857
WILLOW CREEK 11013050 | WILLOW CREEK 1101 | HUMBOLDT | 2.7741 | 81.978 | 100% | 0 | 2 | 100% | 100% | 1 | 0.20349 | 65.3912 | 0.83142 | 11.0633 | High | High | Low | 460 | 245 | 13.3065 | 2087.9944
FORT ROSS 1121204 | FORT ROSS 1121 | SONOMA | 18.7577 | 93.0498 | 90.41% | 0 | 2 | 100% | 39.05% | 1 | 0.10967 | 65.3912 | 1.5385 | 11.0336 | High | High | Low | 461 | 378 | 7.1716 | 2076.9311
OLEMA 11011252 | OLEMA 1101 | NORTH BAY | 4.0529 | 83.346 | 14.42% | 10 | 5 | 98.65% | 0% | 0 | 0.042756 | 85.4511 | 3.0154 | 11.0171 | Medium | Medium | Medium | 462 | 494 | 3.6535 | 2065.8974
WILLOW CREEK 110237374 | WILLOW CREEK 1102 | HUMBOLDT | 2.2967 | 96.0041 | 99.34% | 1 | 0 | 100% | 68.24% | 0 | 0.13938 | 65.3912 | 1.2034 | 10.9677 | High | High | Low | 463 | 339 | 9.1142 | 2054.8804
BELL 11072400 | BELL 1107 | SIERRA | 24.3699 | 40.733 | 58.06% | 2 | 11 | 87.78% | 0% | 0 | 0.061332 | 65.3912 | 2.7006 | 10.8308 | Medium | Medium | Medium | 464 | 479 | 4.0106 | 2043.9127
BIG MEADOWS 21012474 | BIG MEADOWS 2101 | NORTH VALLEY | 8.0369 | 74.0553 | 100% | 0 | 14 | 96.17% | 0% | 0 | 0.062896 | 65.3912 | 2.6243 | 10.7933 | High | High | Medium | 465 | 474 | 4.1128 | 2033.0818
APPLE HILL 110412947 | APPLE HILL 1104 | SIERRA | 3.4561 | 89.425 | 100% | 0 | 1 | 100% | 0% | 0 | 0.04907 | 102.1389 | 2.1335 | 10.6933 | Medium | Medium | Low | 466 | 429 | 5.012 | 2022.2886
PENNGROVE 1101170 | PENNGROVE 1101 | SONOMA | 18.4109 | 61.4183 | 85.26% | 5 | 17 | 81.28% | 0% | 0 | 0.065227 | 65.3912 | 2.4598 | 10.4915 | High | High | Medium | 467 | 468 | 4.2653 | 2011.5952
TASSAJARA 210812712 | TASSAJARA 2108 | DIABLO | 0.60405 | 70.6966 | 76.13% | 0 | 2 | 18.42% | 100% | 0 | 0.089254 | 35.3263 | 3.2876 | 10.366 | High | High | High | 468 | 520 | 3.153 | 2001.1037
PASO ROBLES 1103N04 | PASO ROBLES 1103 | LOS PADRES | 0.58532 | 54.1264 | 3.167% | 0 | 8 | 100% | 0% | 0 | 0.051036 | 65.3912 | 3.1021 | 10.3524 | Medium | Medium | High | 469 | 514 | 3.3373 | 1990.7377
RACETRACK 1704CB | RACETRACK 1704 | YOSEMITE | 22.0312 | 55.84 | 32.56% | 4 | 25 | 99.99% | 0% | 0 | 0.18885 | 26.5534 | 2.0435 | 10.2471 | High | High | Low | 470 | 428 | 5.0145 | 1980.3852
OAKHURST 110363334 | OAKHURST 1103 | YOSEMITE | 17.2522 | 47.378 | 100% | 1 | 11 | 100% | 10.77% | 0 | 0.054511 | 65.3912 | 2.871 | 10.2339 | Medium | Medium | Medium | 471 | 503 | 3.5646 | 1970.1382
PINE GROVE 1101CB | PINE GROVE 1101 | STOCKTON | 4.2594 | 78.3336 | 50.63% | 0 | 5 | 100% | 0% | 0 | 0.038055 | 85.4511 | 3.1345 | 10.1928 | Medium | Medium | High | 472 | 517 | 3.2518 | 1959.9042
CAMP EVERS 21055577 | CAMP EVERS 2105 | CENTRAL COAST | 1.1615 | 10 | 45.86% | 6 | 1 | 100% | 100% | 0 | 0.10796 | 19.9979 | 4.695 | 10.1361 | High | High | High | 473 | 595 | 2.1589 | 1949.7114
WEST POINT 11025357 | WEST POINT 1102 | STOCKTON | 3.286 | 83.7938 | 100% | 3 | 2 | 100% | 17.3% | 0 | 0.065365 | 65.3912 | 2.3603 | 10.0887 | High | High | Medium | 474 | 467 | 4.2743 | 1939.5753
BRUNSWICK 1104761310 | BRUNSWICK 1104 | SIERRA | 0.029625 | 37.5776 | 100% | 0 | 0 | 100% | 100% | 0 | 0.15312 | 26.5534 | 2.4455 | 9.9432 | High | High | Medium | 475 | 475 | 4.0659 | 1929.4866
OLEMA 11011318 | OLEMA 1101 | NORTH BAY | 6.3563 | 77.6358 | 7.161% | 18 | 6 | 61.46% | 0% | 0 | 0.045105 | 85.4511 | 2.535 | 9.7705 | Medium | Medium | Medium | 476 | 484 | 3.8543 | 1919.5434
SILVERADO 210365334 | SILVERADO 2103 | NORTH BAY | 0.51221 | 90 | 100% | 0 | 0 | 7.915% | 100% | 0 | 0.093253 | 47.6367 | 2.1963 | 9.7565 | High | High | Low | 477 | 458 | 4.4422 | 1909.7729
LOW GAP 1101CB | LOW GAP 1101 | HUMBOLDT | 2.17 | 82.2052 | 100% | 6 | 1 | 100% | 0% | 0 | 0.073547 | 65.3912 | 2.01 | 9.6669 | High | High | Low | 478 | 437 | 4.8093 | 1900.0164
TASSAJARA 21123202 | TASSAJARA 2112 | DIABLO | 0.99352 | 84.671 | 60.56% | 0 | 0 | 100% | 100% | 0 | 0.15269 | 19.9979 | 3.1551 | 9.6344 | High | High | High | 479 | 530 | 3.0536 | 1890.3495
REDBUD 1101708166 | REDBUD 1101 | HUMBOLDT | 10.1809 | 81.1955 | 96.21% | 0 | 3 | 49.7% | 53.54% | 1 | 0.096142 | 47.6367 | 2.1005 | 9.6203 | High | High | Low | 480 | 454 | 4.5799 | 1880.7151
SIERRA CITY GEN 1101CB | SIERRA CITY GEN 1101 | SIERRA | 0.013222 | 95 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049877 | 85.4511 | 2.24 | 9.5471 | Medium | Medium | Medium | 481 | 469 | 4.262 | 1871.0948
SIERRA CITY GEN 11011101/2 | SIERRA CITY GEN 1101 | SIERRA | 0.0052893 | 95 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049877 | 85.4511 | 2.2291 | 9.5007 | Medium | Medium | Low | 482 | 469 | 4.262 | 1861.5478
SANTA ROSA A 1104220 | SANTA ROSA A 1104 | SONOMA | 9.5297 | 27.599 | 64.91% | 1 | 14 | 100% | 64.31% | 0 | 0.11149 | 26.5534 | 3.1942 | 9.4563 | High | High | High | 483 | 534 | 2.9604 | 1852.0471
PARADISE 11041571 | PARADISE 1104 | NORTH VALLEY | 0.64266 | 10 | 49.69% | 2 | 2 | 100% | 100% | 0 | 0.10792 | 19.9979 | 4.3768 | 9.4463 | High | High | High | 484 | 596 | 2.1582 | 1842.5907
SILVERADO 21051306 | SILVERADO 2105 | NORTH BAY | 2.7442 | 84.7075 | 83.99% | 0 | 2 | 34.98% | 54.43% | 0 | 0.068801 | 47.6367 | 2.8813 | 9.4434 | High | High | Medium | 485 | 516 | 3.2775 | 1833.1445
MIDDLETOWN 1102998 | MIDDLETOWN 1102 | HUMBOLDT | 14.694 | 30.2565 | 100% | 0 | 1 | 86% | 0% | 0 | 0.055128 | 47.6367 | 3.5751 | 9.3887 | Medium | Medium | High | 486 | 555 | 2.6261 | 1823.701
MENLO 11028952 | MENLO 1102 | PENINSULA | 6.6194 | 37.3674 | 79.3% | 6 | 6 | 97.26% | 0% | 0 | 0.07359 | 35.3263 | 3.5512 | 9.2318 | High | High | High | 487 | 557 | 2.5996 | 1814.3124
MOUNTAIN QUARRIES 2101CB | MOUNTAIN QUARRIES 2101 | SIERRA | 24.9741 | 44.4478 | 67.2% | 2 | 3 | 100% | 0% | 0 | 0.056988 | 65.3912 | 2.4457 | 9.1138 | Medium | Medium | Medium | 488 | 490 | 3.7265 | 1805.0806
MESA 11016111 | MESA 1101 | LOS PADRES | 23.8724 | 66.2721 | 84.61% | 0 | 7 | 92.83% | 48.37% | 0 | 0.23056 | 19.9979 | 1.9723 | 9.0938 | High | High | Low | 489 | 452 | 4.6108 | 1795.9668
HATTON 1101 | HATTON 1101 | CENTRAL COAST | 0.058169 | 90 | 100% | 0 | 0 | 100% | 0% | 0 | 0.054802 | 65.3912 | 2.5228 | 9.0405 | Medium | Medium | Medium | 490 | 500 | 3.5836 | 1786.8729
FORT ROSS 11214947 | FORT ROSS 1121 | SONOMA | 10.2762 | 93.0727 | 99.97% | 4 | 1 | 100% | 8.448% | 0 | 0.11096 | 47.6367 | 1.71 | 9.0384 | High | High | Low | 491 | 421 | 5.2856 | 1777.8324
DESCHUTES 110449024 | DESCHUTES 1104 | NORTH VALLEY | 16.4286 | 33.9792 | 100% | 0 | 7 | 97.93% | 0% | 0 | 0.055326 | 65.3912 | 2.4946 | 9.0253 | Medium | Medium | Medium | 492 | 499 | 3.6179 | 1768.794
BRUNSWICK 11042112 | BRUNSWICK 1104 | SIERRA | 19.306 | 55.1614 | 89% | 4 | 7 | 100% | 25.18% | 0 | 0.10285 | 35.3263 | 2.4774 | 9.0016 | High | High | Medium | 493 | 497 | 3.6335 | 1759.7688
CAMP EVERS 210595394 | CAMP EVERS 2105 | CENTRAL COAST | 0.49589 | 10 | 8.806% | 0 | 0 | 100% | 100% | 0 | 0.065893 | 35.3263 | 3.8628 | 8.9916 | High | High | High | 494 | 575 | 2.3278 | 1750.7671
MENLO 11038512 | MENLO 1103 | PENINSULA | 16.8652 | 73.7343 | 67.92% | 14 | 5 | 100% | 0% | 0 | 0.10603 | 35.3263 | 2.3875 | 8.9425 | High | High | Medium | 495 | 489 | 3.7456 | 1741.7755
MORAGA 110183424 | MORAGA 1101 | DIABLO | 1.6164 | 79.1593 | 0% | 0 | 0 | 100% | 62.3% | 0 | 0.053892 | 47.6367 | 3.4366 | 8.8227 | Medium | Medium | High | 496 | 560 | 2.5672 | 1732.833
WISE 11022230 | WISE 1102 | SIERRA | 22.0893 | 25.2486 | 59.65% | 3 | 10 | 89.01% | 0% | 0 | 0.09262 | 47.6367 | 1.9917 | 8.7874 | High | High | Low | 497 | 461 | 4.4121 | 1724.0103
BIG BASIN 110112838 | BIG BASIN 1101 | CENTRAL COAST | 2.3481 | 22.8055 | 19.65% | 7 | 1 | 100% | 100% | 0 | 0.097327 | 26.5534 | 3.3758 | 8.7244 | High | High | High | 498 | 559 | 2.5844 | 1715.2229
HOOPA 11017468 | HOOPA 1101 | HUMBOLDT | 5.6936 | 54.3189 | 96.19% | 3 | 8 | 47.51% | 49.77% | 1 | 0.076067 | 65.3912 | 1.7487 | 8.6983 | High | High | Low | 499 | 431 | 4.9741 | 1706.4985
GARBERVILLE 11028652 | GARBERVILLE 1102 | HUMBOLDT | 13.0139 | 91.1649 | 97.21% | 18 | 2 | 100% | 0% | 0 | 0.11424 | 47.6367 | 1.5713 | 8.5506 | High | High | Low | 500 | 416 | 5.4418 | 1697.8002
FITCH MOUNTAIN 1113356 | FITCH MOUNTAIN 1113 | SONOMA | 9.9757 | 80.7752 | 75.25% | 5 | 1 | 65.83% | 51.2% | 1 | 0.073371 | 47.6367 | 2.443 | 8.5386 | High | High | Medium | 501 | 506 | 3.4951 | 1689.2497
CALPINE 1144962 | CALPINE 1144 | SONOMA | 4.058 | 94.9648 | 64.72% | 0 | 0 | 100% | 100% | 0 | 0.16674 | 26.5534 | 1.9214 | 8.5068 | High | High | Low | 502 | 460 | 4.4275 | 1680.7111
MIRABEL 110213597 | MIRABEL 1102 | SONOMA | 0.47204 | 30.1701 | 51.63% | 3 | 0 | 100% | 100% | 0 | 0.10712 | 26.5534 | 2.9615 | 8.4237 | High | High | Medium | 503 | 546 | 2.8444 | 1672.2043
SANTA ROSA A 1111114 | SANTA ROSA A 1111 | SONOMA | 5.593 | 82.824 | 61.55% | 3 | 5 | 48.78% | 0.05081% | 0 | 0.039882 | 65.3912 | 3.2275 | 8.4172 | Medium | Medium | High | 504 | 556 | 2.608 | 1663.7806
PENRYN 1103604 | PENRYN 1103 | SIERRA | 26.4899 | 35.3404 | 72.55% | 7 | 11 | 100% | 0% | 0 | 0.061577 | 47.6367 | 2.8611 | 8.3925 | High | High | Medium | 505 | 539 | 2.9333 | 1655.3634
CHALLENGE 110113026 | CHALLENGE 1101 | NORTH VALLEY | 7.8248 | 63.8642 | 100% | 1 | 1 | 97.67% | 96.11% | 0 | 0.25947 | 85.4511 | 0.3778 | 8.3764 | High | High | Low | 506 | 120 | 22.1717 | 1646.9709
PINE GROVE 11011021 | PINE GROVE 1101 | STOCKTON | 4.1934 | 79.4355 | 93.37% | 0 | 1 | 100% | 0% | 0 | 0.043638 | 65.3912 | 2.9314 | 8.3647 | Medium | Medium | Medium | 507 | 545 | 2.8535 | 1638.5945
SANTA YNEZ 1104Y66 | SANTA YNEZ 1104 | LOS PADRES | 16.6796 | 85.1619 | 76.69% | 1 | 3 | 92.13% | 26.5% | 0 | 0.10816 | 35.3263 | 2.1886 | 8.3621 | High | High | Low | 508 | 485 | 3.8208 | 1630.2298
MONROE 2103CB | MONROE 2103 | SONOMA | 0.73533 | 61.5712 | 100% | 0 | 0 | 5.132% | 100% | 0 | 0.076074 | 47.6367 | 2.2963 | 8.3215 | High | High | Medium | 509 | 498 | 3.6239 | 1621.8676
DIAMOND SPRINGS 110518935 | DIAMOND SPRINGS 1105 | SIERRA | 6.6942 | 21.2209 | 100% | 2 | 4 | 100% | 72.5% | 0 | 0.11646 | 26.5534 | 2.6792 | 8.2855 | High | High | Medium | 510 | 523 | 3.0925 | 1613.5461
CORNING 110185152 | CORNING 1101 | NORTH VALLEY | 23.0821 | 26.0719 | 100% | 2 | 8 | 100% | 0% | 0 | 0.11691 | 26.5534 | 2.6425 | 8.2029 | High | High | Medium | 511 | 521 | 3.1042 | 1605.2606
PACIFICA 1101CB | PACIFICA 1101 | PENINSULA | 1.1754 | 10 | 25.99% | 0 | 0 | 43.55% | 100% | 0 | 0.044128 | 47.6367 | 3.8732 | 8.142 | Medium | Medium | High | 512 | 598 | 2.1021 | 1597.0577
SILVERADO 21051308 | SILVERADO 2105 | NORTH BAY | 0.01945 | 80.9995 | 16% | 3 | 1 | 0.3576% | 100% | 0 | 0.045462 | 47.6367 | 3.7584 | 8.1396 | Medium | Medium | High | 513 | 594 | 2.1657 | 1588.9157
DUNBAR 11014817 | DUNBAR 1101 | SONOMA | 3.1798 | 21.7127 | 52.45% | 3 | 3 | 100% | 100% | 0 | 0.15344 | 19.9979 | 2.6498 | 8.1309 | High | High | Medium | 514 | 527 | 3.0685 | 1580.7761
GIRVAN 11021028 | GIRVAN 1102 | NORTH VALLEY | 17.4682 | 30.4656 | 99.97% | 3 | 19 | 100% | 100% | 1 | 0.28494 | 14.9507 | 1.8976 | 8.084 | High | High | Low | 515 | 471 | 4.26 | 1572.6452
ATASCADERO 11012537 | ATASCADERO 1101 | LOS PADRES | 15.4143 | 42.2463 | 87.6% | 5 | 1 | 100% | 82.31% | 1 | 0.15256 | 19.9979 | 2.6276 | 8.0166 | High | High | Medium | 516 | 531 | 3.0509 | 1564.5612
COTATI 110379140 | COTATI 1103 | SONOMA | 9.8425 | 61.4372 | 48.82% | 7 | 2 | 79.77% | 0% | 0 | 0.047459 | 65.3912 | 2.5749 | 7.9908 | Medium | Medium | Medium | 517 | 522 | 3.1034 | 1556.5447
CAMP EVERS 21035753 | CAMP EVERS 2103 | CENTRAL COAST | 2.4228 | 18.1993 | 27.31% | 10 | 4 | 100% | 100% | 0 | 0.13875 | 14.9507 | 3.8491 | 7.9846 | High | High | High | 518 | 600 | 2.0744 | 1548.5538
MIDDLETOWN 11011314 | MIDDLETOWN 1101 | HUMBOLDT | 0.82482 | 85.7951 | 100% | 0 | 0 | 88.81% | 5.14% | 1 | 0.051914 | 65.3912 | 2.3199 | 7.8754 | Medium | Medium | Medium | 519 | 512 | 3.3947 | 1540.5692
BRUNSWICK 11102664 | BRUNSWICK 1110 | SIERRA | 9.7807 | 42.9965 | 66.17% | 2 | 0 | 90.12% | 0% | 0 | 0.042278 | 65.3912 | 2.8403 | 7.8524 | Medium | Medium | Medium | 520 | 549 | 2.7646 | 1532.6939
KONOCTI 110264664 | KONOCTI 1102 | HUMBOLDT | 27.2111 | 54.3183 | 71% | 3 | 9 | 94.13% | 22.47% | 0 | 0.10647 | 26.5534 | 2.7454 | 7.7618 | High | High | Medium | 521 | 547 | 2.8272 | 1524.8415
FRUITLAND 114293234 | FRUITLAND 1142 | HUMBOLDT | 11.3813 | 94.4975 | 76.78% | 16 | 5 | 100% | 0% | 0 | 0.081313 | 65.3912 | 1.4517 | 7.7189 | High | High | Low | 522 | 420 | 5.3172 | 1517.0796
CALISTOGA 11011087 | CALISTOGA 1101 | NORTH BAY | 1.9847 | 74.7271 | 70.51% | 0 | 0 | 100% | 100% | 0 | 0.15452 | 19.9979 | 2.4735 | 7.6433 | High | High | Medium | 523 | 524 | 3.0901 | 1509.3608
FORT SEWARD 11211690 | FORT SEWARD 1121 | HUMBOLDT | 10.4929 | 86.5731 | 100% | 15 | 3 | 64.42% | 0% | 0 | 0.055586 | 65.3912 | 2.046 | 7.4369 | Medium | Medium | Low | 524 | 496 | 3.6348 | 1501.7175
CLOVERDALE 1101 | CLOVERDALE 1101 | SONOMA | 0.067026 | 85 | 100% | 0 | 0 | 100% | 0% | 0 | 0.046733 | 65.3912 | 2.4317 | 7.4312 | Medium | Medium | Medium | 525 | 529 | 3.0559 | 1494.2806
SHADY GLEN 11012768 | SHADY GLEN 1101 | SIERRA | 7.6983 | 67.5569 | 97.78% | 0 | 5 | 95.39% | 10.27% | 0 | 0.057683 | 65.3912 | 1.9636 | 7.4066 | Medium | Medium | Low | 526 | 488 | 3.7719 | 1486.8494
TEMPLETON 2113A10 | TEMPLETON 2113 | LOS PADRES | 30.9401 | 69.101 | 70.57% | 5 | 5 | 100% | 93.66% | 0 | 0.21943 | 26.5534 | 1.2694 | 7.3966 | High | High | Low | 527 | 403 | 5.8266 | 1479.4427
BRUNSWICK 1102940 | BRUNSWICK 1102 | SIERRA | 0.6541 | 82.3173 | 27.04% | 0 | 0 | 18.81% | 100% | 0 | 0.056253 | 47.6367 | 2.7437 | 7.3523 | Medium | Medium | Medium | 528 | 553 | 2.6797 | 1472.0462
WILLOW CREEK 1101CB | WILLOW CREEK 1101 | HUMBOLDT | 0.28035 | 73.844 | 25.25% | 2 | 0 | 100% | 100% | 0 | 0.11379 | 35.3263 | 1.829 | 7.3523 | High | High | Low | 529 | 478 | 4.0198 | 1464.6939
CAMP EVERS 21055188 | CAMP EVERS 2105 | CENTRAL COAST | 1.985 | 10 | 58.42% | 1 | 0 | 100% | 100% | 0 | 0.10955 | 19.9979 | 3.3123 | 7.2566 | High | High | High | 530 | 592 | 2.1908 | 1457.3416
BRUNSWICK 11047181 | BRUNSWICK 1104 | SIERRA | 0.77307 | 57.8754 | 100% | 1 | 1 | 100% | 0% | 0 | 0.040435 | 65.3912 | 2.6834 | 7.0953 | Medium | Medium | Medium | 531 | 554 | 2.6441 | 1450.085
NORTH BRANCH 110111206 | NORTH BRANCH 1101 | STOCKTON | 17.2475 | 65.0034 | 87.98% | 1 | 4 | 96.4% | 0% | 0 | 0.057888 | 35.3263 | 3.4658 | 7.0874 | Medium | Medium | High | 532 | 601 | 2.045 | 1442.9897
OCEANO 1104Q10 | OCEANO 1104 | LOS PADRES | 23.5484 | 28.2238 | 59% | 7 | 3 | 100% | 0% | 0 | 0.065893 | 35.3263 | 3.0376 | 7.0708 | High | High | Medium | 533 | 576 | 2.3277 | 1435.9023
MOLINO 1101338 | MOLINO 1101 | SONOMA | 7.3596 | 75.7123 | 66.21% | 4 | 4 | 51.47% | 0% | 0 | 0.035347 | 65.3912 | 3.0506 | 7.0511 | Medium | Medium | Medium | 534 | 579 | 2.3114 | 1428.8316
COTATI 110599720 | COTATI 1105 | SONOMA | 7.8564 | 53.7004 | 71.89% | 3 | 7 | 63.87% | 0% | 0 | 0.042996 | 65.3912 | 2.5058 | 7.0451 | Medium | Medium | Medium | 535 | 548 | 2.8115 | 1421.7804
BIG BASIN 11026219 | BIG BASIN 1102 | CENTRAL COAST | 0.89903 | 23.7161 | 100% | 1 | 0 | 100% | 100% | 0 | 0.14284 | 19.9979 | 2.4506 | 6.9999 | High | High | Medium | 536 | 544 | 2.8564 | 1414.7354
BIG BASIN 110212758 | BIG BASIN 1102 | CENTRAL COAST | 6.1262 | 42.4144 | 40.92% | 12 | 2 | 100% | 100% | 0 | 0.21481 | 11.2183 | 2.8889 | 6.9619 | High | High | Medium | 537 | 570 | 2.4099 | 1407.7355
PETALUMA C 1108296 | PETALUMA C 1108 | SONOMA | 14.7729 | 78.7625 | 21.22% | 3 | 7 | 100% | 0% | 0 | 0.037166 | 65.3912 | 2.8405 | 6.9034 | Medium | Medium | Medium | 538 | 566 | 2.4303 | 1400.7736
DUNBAR 11022359 | DUNBAR 1102 | SONOMA | 4.5098 | 82.5925 | 84.36% | 0 | 1 | 100% | 0% | 0 | 0.041489 | 47.6367 | 3.4865 | 6.8907 | Medium | Medium | High | 539 | 606 | 1.9764 | 1393.8702
LOW GAP 110186816 | LOW GAP 1101 | HUMBOLDT | 4.4169 | 87.0623 | 100% | 0 | 8 | 100% | 0% | 0 | 0.071339 | 65.3912 | 1.4627 | 6.8232 | High | High | Low | 540 | 447 | 4.6649 | 1386.9795
CLARKSVILLE 2104CB | CLARKSVILLE 2104 | SIERRA | 9.4695 | 34.2727 | 54.5% | 0 | 3 | 89.57% | 0% | 0 | 0.028962 | 65.3912 | 3.5993 | 6.8166 | Medium | Medium | High | 541 | 618 | 1.8939 | 1380.1563
COTATI 110536536 | COTATI 1105 | SONOMA | 14.0222 | 66.9943 | 49.66% | 3 | 4 | 71.19% | 0% | 0 | 0.039741 | 65.3912 | 2.6116 | 6.7868 | Medium | Medium | Medium | 542 | 558 | 2.5987 | 1373.3397
RACETRACK 170455798 | RACETRACK 1704 | YOSEMITE | 15.7881 | 56.8107 | 46.06% | 3 | 13 | 100% | 0% | 0 | 0.064582 | 47.6367 | 2.1973 | 6.7599 | High | High | Low | 543 | 525 | 3.0765 | 1366.5529
SPANISH CREEK 4401CB | SPANISH CREEK 4401 | NORTH VALLEY | 7.9163 | 94.7918 | 10.89% | 2 | 9 | 99.83% | 0% | 0 | 0.034339 | 85.4511 | 2.2893 | 6.7174 | Medium | Medium | Medium | 544 | 538 | 2.9343 | 1359.793
PHILO 11022600 | PHILO 1102 | HUMBOLDT | 19.2386 | 94.0358 | 55.52% | 12 | 3 | 96.16% | 0% | 0 | 0.060847 | 85.4511 | 1.2847 | 6.6795 | Medium | Medium | Low | 545 | 422 | 5.1995 | 1353.0756
OCEANO 1104V36 | OCEANO 1104 | LOS PADRES | 8.9209 | 45.6964 | 61.88% | 2 | 5 | 67.02% | 0% | 0 | 0.047581 | 47.6367 | 2.9332 | 6.6484 | Medium | Medium | Medium | 546 | 586 | 2.2666 | 1346.396
PASO ROBLES 1103N50 | PASO ROBLES 1103 | LOS PADRES | 2.1383 | 48.485 | 34.16% | 0 | 1 | 100% | 0% | 0 | 0.042301 | 47.6367 | 3.2748 | 6.599 | Medium | Medium | High | 547 | 603 | 2.0151 | 1339.7477
DUNBAR 1102246 | DUNBAR 1102 | SONOMA | 14.7102 | 40.7068 | 52.1% | 6 | 13 | 100% | 1.558% | 0 | 0.064871 | 35.3263 | 2.8342 | 6.495 | High | High | Medium | 548 | 583 | 2.2917 | 1333.1487
MORAGA 110531512 | MORAGA 1105 | DIABLO | 1.6381 | 82.7006 | 6.913% | 0 | 1 | 35.45% | 68.16% | 0 | 0.035075 | 47.6367 | 3.886 | 6.493 | Medium | Medium | High | 549 | 633 | 1.6709 | 1326.6536
BELLEVUE 2103478 | BELLEVUE 2103 | SONOMA | 7.8213 | 71.5626 | 88.7% | 0 | 2 | 38.92% | 0% | 0 | 0.02921 | 65.3912 | 3.3117 | 6.3256 | Medium | Medium | High | 550 | 615 | 1.9101 | 1320.1606
PACIFICA 11015001 | PACIFICA 1101 | PENINSULA | 1.7299 | 13.6047 | 57.13% | 0 | 0 | 33.8% | 76.31% | 0 | 0.036346 | 47.6367 | 3.6453 | 6.3114 | Medium | Medium | High | 551 | 628 | 1.7314 | 1313.835
JESSUP 110276068 | JESSUP 1102 | NORTH VALLEY | 15.5129 | 23.0172 | 100% | 2 | 4 | 80.72% | 0% | 0 | 0.061753 | 47.6367 | 2.125 | 6.2511 | High | High | Low | 552 | 537 | 2.9417 | 1307.5236
MOLINO 11015042 | MOLINO 1101 | SONOMA | 5.4336 | 70.9721 | 53.86% | 5 | 2 | 79.32% | 0% | 0 | 0.030542 | 65.3912 | 3.0912 | 6.1735 | Medium | Medium | High | 553 | 605 | 1.9971 | 1301.2725
SHINGLE SPRINGS 21099372 | SHINGLE SPRINGS 2109 | SIERRA | 17.5824 | 48.8833 | 68.76% | 2 | 5 | 100% | 52.97% | 0 | 0.1201 | 26.5534 | 1.9275 | 6.147 | High | High | Low | 554 | 519 | 3.1891 | 1295.0989
BIG BASIN 11019773 | BIG BASIN 1101 | CENTRAL COAST | 0.4507 | 10 | 17.07% | 7 | 0 | 100% | 100% | 0 | 0.097654 | 19.9979 | 3.1187 | 6.0905 | High | High | High | 555 | 611 | 1.9529 | 1288.952
LAYTONVILLE 1101CB | LAYTONVILLE 1101 | HUMBOLDT | 7.0679 | 79.2729 | 100% | 10 | 7 | 78.03% | 0% | 0 | 0.054066 | 85.4511 | 1.3144 | 6.0728 | Medium | Medium | Low | 556 | 450 | 4.62 | 1282.8615
CAMP EVERS 2105BL 2101 | CAMP EVERS 2105 | CENTRAL COAST | 0.0032282 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 26.5534 | 3.7013 | 6.0502 | High | High | High | 557 | 638 | 1.6346 | 1276.7887
GREENBRAE 1103 | GREENBRAE 1103 | NORTH BAY | 0.019268 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 26.5534 | 3.6958 | 6.0412 | High | High | High | 558 | 638 | 1.6346 | 1270.7385
PETALUMA C 1108628 | PETALUMA C 1108 | SONOMA | 9.0995 | 58.7807 | 34.73% | 0 | 3 | 82.01% | 0% | 0 | 0.035008 | 65.3912 | 2.6389 | 6.041 | Medium | Medium | Medium | 559 | 584 | 2.2892 | 1264.6973
ROSSMOOR 1102CB | ROSSMOOR 1102 | DIABLO | 0.0028423 | 10 | 0% | 0 | 0 | 0.1985% | 100% | 0 | 0.023559 | 65.3912 | 3.8658 | 5.9555 | Medium | Medium | High | 560 | 645 | 1.5406 | 1258.6563
HIGHLANDS 1103828 | HIGHLANDS 1103 | HUMBOLDT | 6.7375 | 63.3162 | 90.74% | 0 | 3 | 64.07% | 0% | 0 | 0.032181 | 65.3912 | 2.8231 | 5.9408 | Medium | Medium | Medium | 561 | 597 | 2.1043 | 1252.7008
ZACA 1102CB | ZACA 1102 | LOS PADRES | 15.8871 | 63.476 | 75.75% | 0 | 4 | 76.4% | 37.44% | 0 | 0.096438 | 35.3263 | 1.7385 | 5.9226 | High | High | Low | 562 | 510 | 3.4068 | 1246.76
BRUNSWICK 110378862 | BRUNSWICK 1103 | SIERRA | 0.84386 | 75.0835 | 56.54% | 0 | 0 | 62.09% | 0% | 0 | 0.021418 | 85.4511 | 3.1475 | 5.7606 | Low | Low | High | 563 | 621 | 1.8302 | 1240.8374
REDBUD 1102CB | REDBUD 1102 | HUMBOLDT | 15.5011 | 65.2981 | 72.86% | 2 | 2 | 77.01% | 9.757% | 0 | 0.048504 | 47.6367 | 2.492 | 5.7579 | Medium | Medium | Medium | 564 | 580 | 2.3106 | 1235.0768
VALLEY VIEW 1103CB | VALLEY VIEW 1103 | EAST BAY | 0.06028 | 65 | 0% | 0 | 0 | 0.9308% | 100% | 0 | 0.034198 | 35.3263 | 4.6903 | 5.6663 | Medium | Medium | High | 565 | 682 | 1.2081 | 1229.3189
COARSEGOLD 2104570682 | COARSEGOLD 2104 | YOSEMITE | 2.0271 | 37.4462 | 79.77% | 2 | 5 | 100% | 0% | 0 | 0.037588 | 65.3912 | 2.2997 | 5.6525 | Medium | Medium | Medium | 566 | 565 | 2.4579 | 1223.6526
MOLINO 110279306 | MOLINO 1102 | SONOMA | 3.6243 | 55.9348 | 57.2% | 3 | 2 | 44.33% | 48.34% | 1 | 0.037109 | 65.3912 | 2.3082 | 5.6012 | Medium | Medium | Medium | 567 | 567 | 2.4266 | 1218.0001
MIRABEL 11027401 | MIRABEL 1102 | SONOMA | 1.0644 | 17.3394 | 6.536% | 3 | 1 | 100% | 100% | 0 | 0.071799 | 26.5534 | 2.9335 | 5.5928 | High | High | Medium | 568 | 616 | 1.9065 | 1212.399
COTATI 1103CB | COTATI 1103 | SONOMA | 12.0212 | 77.6953 | 26.01% | 1 | 5 | 100% | 0% | 0 | 0.046374 | 47.6367 | 2.5255 | 5.5791 | Medium | Medium | Medium | 569 | 591 | 2.2091 | 1206.8062
LAYTONVILLE 1102CB | LAYTONVILLE 1102 | HUMBOLDT | 10.2076 | 95.4582 | 95.78% | 0 | 7 | 78.57% | 0% | 0 | 0.051516 | 85.4511 | 1.2662 | 5.5739 | Medium | Medium | Low | 570 | 462 | 4.4021 | 1201.2271
PARADISE 110299226 | PARADISE 1102 | NORTH VALLEY | 0.94174 | 38.0724 | 24.71% | 0 | 0 | 9.702% | 100% | 0 | 0.037935 | 35.3263 | 4.1275 | 5.5313 | Medium | Medium | High | 571 | 664 | 1.3401 | 1195.6532
SEACLIFF 0402CB | SEACLIFF 0402 | CENTRAL COAST | 0.96395 | 10 | 24.34% | 2 | 0 | 62.04% | 63.7% | 0 | 0.030212 | 47.6367 | 3.8167 | 5.4929 | Medium | Medium | High | 572 | 653 | 1.4392 | 1190.1219
PETALUMA C 1108636 | PETALUMA C 1108 | SONOMA | 9.2277 | 74.6783 | 45.5% | 1 | 1 | 100% | 0% | 0 | 0.048927 | 47.6367 | 2.3419 | 5.4583 | Medium | Medium | Medium | 573 | 574 | 2.3307 | 1184.629
HALF MOON BAY 11038894 | HALF MOON BAY 1103 | PENINSULA | 11.2938 | 71.3584 | 49.24% | 24 | 2 | 100% | 0% | 0 | 0.052113 | 47.6367 | 2.1795 | 5.4107 | Medium | Medium | Low | 574 | 562 | 2.4825 | 1179.1707
NORTH DUBLIN 210311101 | NORTH DUBLIN 2103 | MISSION | 3.6926 | 66.2488 | 89.68% | 0 | 0 | 100% | 0% | 0 | 0.05582 | 26.5534 | 3.6138 | 5.3564 | Medium | Medium | High | 575 | 650 | 1.4822 | 1173.76
FORESTHILL 1102CB | FORESTHILL 1102 | SIERRA | 1.6478 | 87.6992 | 97.59% | 0 | 0 | 100% | 100% | 0 | 0.19983 | 11.2183 | 2.3825 | 5.3411 | High | High | Medium | 576 | 589 | 2.2418 | 1168.4036
BRUNSWICK 111063100 | BRUNSWICK 1110 | SIERRA | 4.1271 | 39.6111 | 66.99% | 1 | 2 | 100% | 0% | 0 | 0.041392 | 47.6367 | 2.706 | 5.3357 | Medium | Medium | Medium | 577 | 607 | 1.9718 | 1163.0625
SAN LUIS OBISPO 110342344 | SAN LUIS OBISPO 1103 | LOS PADRES | 7.6647 | 51.698 | 64.08% | 0 | 1 | 70.58% | 0% | 0 | 0.031898 | 65.3912 | 2.5342 | 5.286 | Medium | Medium | Medium | 578 | 599 | 2.0859 | 1157.7268
SHADY GLEN 1101CB | SHADY GLEN 1101 | SIERRA | 4.4237 | 59.4195 | 32.95% | 0 | 5 | 80.65% | 0% | 0 | 0.027502 | 85.4511 | 2.2374 | 5.2579 | Medium | Medium | Medium | 579 | 573 | 2.3501 | 1152.4408
VACA DIXON 110540092 | VACA DIXON 1105 | SACRAMENTO | 23.831 | 65.7788 | 89.52% | 2 | 6 | 55.42% | 0% | 0 | 0.036947 | 65.3912 | 2.1635 | 5.227 | Medium | Medium | Low | 580 | 569 | 2.416 | 1147.1829
CRESCENT MILLS 2101CB | CRESCENT MILLS 2101 | NORTH VALLEY | 4.0564 | 89.8056 | 75.4% | 0 | 1 | 71.09% | 0% | 0 | 0.030639 | 65.3912 | 2.6018 | 5.2128 | Medium | Medium | Medium | 581 | 604 | 2.0035 | 1141.9559
SILVERADO 2104726 | SILVERADO 2104 | NORTH BAY | 29.6312 | 77.5719 | 85.35% | 3 | 1 | 83.81% | 20.91% | 0 | 0.072604 | 26.5534 | 2.6935 | 5.1927 | High | High | Medium | 582 | 614 | 1.9279 | 1136.7431
HIGHLANDS 1102628 | HIGHLANDS 1102 | HUMBOLDT | 14.1896 | 81.6211 | 32.89% | 0 | 6 | 100% | 58.23% | 1 | 0.095308 | 19.9979 | 2.6661 | 5.0814 | High | High | Medium | 583 | 617 | 1.906 | 1131.5504
LAYTONVILLE 1102572 | LAYTONVILLE 1102 | HUMBOLDT | 21.4369 | 82.6922 | 96.68% | 7 | 18 | 100% | 0% | 0 | 0.14346 | 26.5534 | 1.3283 | 5.0602 | High | High | Low | 584 | 486 | 3.8094 | 1126.469
COTATI 1105634 | COTATI 1105 | SONOMA | 6.9392 | 85.5117 | 61.91% | 2 | 3 | 100% | 0% | 0 | 0.037803 | 65.3912 | 2.0438 | 5.0522 | Medium | Medium | Low | 585 | 563 | 2.472 | 1121.4088
PENRYN 11032198 | PENRYN 1103 | SIERRA | 19.8234 | 39.0911 | 53.27% | 4 | 16 | 94.86% | 0% | 0 | 0.048469 | 47.6367 | 2.1684 | 5.0067 | Medium | Medium | Low | 586 | 582 | 2.3089 | 1116.3565
VACA DIXON 110118292 | VACA DIXON 1101 | SACRAMENTO | 0.82637 | 74.5954 | 100% | 0 | 2 | 13.83% | 0% | 0 | 0.019682 | 85.4511 | 2.9566 | 4.9725 | Low | Low | Medium | 587 | 631 | 1.6818 | 1111.3499
GARCIA 0401666 | GARCIA 0401 | HUMBOLDT | 2.4311 | 97.9965 | 100% | 2 | 2 | 100% | 0% | 0 | 0.054265 | 65.3912 | 1.3953 | 4.9513 | Medium | Medium | Low | 588 | 504 | 3.5484 | 1106.3774
CORNING 110164090 | CORNING 1101 | NORTH VALLEY | 13.6992 | 19.4323 | 100% | 1 | 9 | 100% | 0% | 0 | 0.061365 | 35.3263 | 2.2782 | 4.9386 | Medium | Medium | Medium | 589 | 593 | 2.1678 | 1101.4261
VACAVILLE 111113652 | VACAVILLE 1111 | SACRAMENTO | 4.3673 | 25.6376 | 64.23% | 1 | 3 | 100% | 0% | 0 | 0.033137 | 47.6367 | 3.0974 | 4.8893 | Medium | Medium | High | 590 | 643 | 1.5785 | 1096.4875
STELLING 11102243 | STELLING 1110 | DE ANZA | 1.8981 | 73.5691 | 46.49% | 9 | 0 | 100% | 0% | 0 | 0.031796 | 47.6367 | 3.2106 | 4.8628 | Medium | Medium | High | 591 | 646 | 1.5146 | 1091.5982
IGNACIO 11042447 | IGNACIO 1104 | NORTH BAY | 0.96609 | 32.7068 | 67.19% | 4 | 5 | 90.01% | 0% | 0 | 0.034924 | 47.6367 | 2.9164 | 4.852 | Medium | Medium | Medium | 592 | 634 | 1.6637 | 1086.7354
GIRVAN 11019732 | GIRVAN 1101 | NORTH VALLEY | 21.139 | 36.4737 | 100% | 2 | 6 | 100% | 100% | 0 | 0.1928 | 14.9507 | 1.6805 | 4.844 | High | High | Low | 593 | 542 | 2.8825 | 1081.8834
GARBERVILLE 110135706 | GARBERVILLE 1101 | HUMBOLDT | 9.7846 | 69.4909 | 86.47% | 18 | 6 | 100% | 0% | 0 | 0.099644 | 65.3912 | 0.74027 | 4.8235 | High | High | Low | 594 | 390 | 6.5159 | 1077.0395
MORAGA 110518396 | MORAGA 1105 | DIABLO | 0.21093 | 45.5725 | 100% | 0 | 2 | 18.41% | 0% | 0 | 0.016943 | 65.3912 | 4.3309 | 4.7983 | Low | Low | High | 595 | 698 | 1.1079 | 1072.216
TIVY VALLEY 1107869946 | TIVY VALLEY 1107 | FRESNO | 29.8533 | 31.5996 | 100% | 0 | 2 | 100% | 0% | 0 | 0.044292 | 65.3912 | 1.6429 | 4.7585 | Medium | Medium | Low | 596 | 541 | 2.8963 | 1067.4177
OILFIELDS 1103N46 | OILFIELDS 1103 | CENTRAL COAST | 5.8257 | 79.2916 | 67.5% | 0 | 4 | 100% | 0% | 0 | 0.062709 | 35.3263 | 2.1379 | 4.736 | High | High | Low | 597 | 590 | 2.2153 | 1062.6592
GARCIA 0401CB | GARCIA 0401 | HUMBOLDT | 0.042407 | 98 | 100% | 0 | 0 | 100% | 0% | 0 | 0.050859 | 65.3912 | 1.4156 | 4.7078 | Medium | Medium | Low | 598 | 515 | 3.3257 | 1057.9232
COARSEGOLD 2104369777 | COARSEGOLD 2104 | YOSEMITE | 18.4298 | 46.1002 | 90.43% | 1 | 34 | 100% | 0% | 0 | 0.066997 | 35.3263 | 1.9853 | 4.6987 | High | High | Low | 599 | 572 | 2.3668 | 1053.2153
CRESCENT MILLS 21012232 | CRESCENT MILLS 2101 | NORTH VALLEY | 17.0798 | 82.544 | 99.96% | 2 | 0 | 84.55% | 0% | 0 | 0.052465 | 65.3912 | 1.3664 | 4.6879 | Medium | Medium | Low | 600 | 509 | 3.4308 | 1048.5166
FORT ROSS 1121124 | FORT ROSS 1121 | SONOMA | 18.5728 | 86.0744 | 76.02% | 1 | 2 | 100% | 0% | 0 | 0.077065 | 47.6367 | 1.2649 | 4.6437 | High | High | Low | 601 | 493 | 3.6711 | 1043.8287
BELL 111056214 | BELL 1110 | SIERRA | 0.30639 | 85 | 100% | 0 | 0 | 4.593% | 0% | 0 | 0.018495 | 85.4511 | 2.9334 | 4.636 | Low | Low | Medium | 602 | 642 | 1.5804 | 1039.1849
LAURELES 111110141 | LAURELES 1111 | CENTRAL COAST | 2.922 | 83.2816 | 100% | 0 | 0 | 100% | 100% | 0 | 0.22027 | 11.2183 | 1.8674 | 4.6144 | High | High | Low | 603 | 564 | 2.471 | 1034.549
HALF MOON BAY 11038089 | HALF MOON BAY 1103 | PENINSULA | 2.9815 | 77.4451 | 41.57% | 4 | 4 | 100% | 0% | 0 | 0.036303 | 65.3912 | 1.9337 | 4.5903 | Medium | Medium | Low | 604 | 571 | 2.3739 | 1029.9346
HALF MOON BAY 110398440 | HALF MOON BAY 1103 | PENINSULA | 8.1037 | 78.0886 | 41.99% | 8 | 1 | 100% | 0% | 0 | 0.041193 | 47.6367 | 2.3386 | 4.589 | Medium | Medium | Medium | 605 | 608 | 1.9623 | 1025.3443
HIGHLANDS 11031282 | HIGHLANDS 1103 | HUMBOLDT | 15.0139 | 42.6416 | 99.84% | 3 | 8 | 89.98% | 0% | 0 | 0.050585 | 35.3263 | 2.5601 | 4.5749 | Medium | Medium | Medium | 606 | 623 | 1.787 | 1020.7553
PARADISE 1104CB | PARADISE 1104 | NORTH VALLEY | 0.54287 | 10 | 13.72% | 1 | 1 | 13.43% | 100% | 0 | 0.030938 | 35.3263 | 4.1742 | 4.5621 | Medium | Medium | High | 607 | 700 | 1.0929 | 1016.1804
WILLITS 110337506 | WILLITS 1103 | HUMBOLDT | 11.4286 | 90.7952 | 60.25% | 4 | 3 | 100% | 0% | 0 | 0.04503 | 65.3912 | 1.5483 | 4.5592 | Medium | Medium | Low | 608 | 536 | 2.9446 | 1011.6183
COARSEGOLD 210210207 | COARSEGOLD 2102 | YOSEMITE | 3.5762 | 10 | 99.5% | 3 | 11 | 100% | 100% | 0 | 0.20336 | 11.2183 | 1.996 | 4.5536 | High | High | Low | 609 | 585 | 2.2814 | 1007.0592
WILLOW CREEK 11037514 | WILLOW CREEK 1103 | HUMBOLDT | 9.2339 | 70.9692 | 70.67% | 10 | 14 | 91.91% | 2.029% | 1 | 0.062494 | 47.6367 | 1.4859 | 4.4235 | High | High | Low | 610 | 533 | 2.977 | 1002.5056
SHADY GLEN 110248894 | SHADY GLEN 1102 | SIERRA | 8.076 | 49.6205 | 67.94% | 0 | 5 | 80.69% | 16.07% | 0 | 0.038596 | 65.3912 | 1.7515 | 4.4204 | Medium | Medium | Low | 611 | 561 | 2.5239 | 998.0821
OLEMA 11011200 | OLEMA 1101 | NORTH BAY | 2.8963 | 61.7343 | 11.72% | 2 | 7 | 100% | 0% | 0 | 0.026697 | 65.3912 | 2.5297 | 4.4162 | Medium | Medium | Medium | 612 | 627 | 1.7458 | 993.6617
SILVERADO 2104CB | SILVERADO 2104 | NORTH BAY | 1.8059 | 23.2702 | 84.92% | 2 | 1 | 36.1% | 66.89% | 0 | 0.044573 | 26.5534 | 3.6993 | 4.3783 | Medium | Medium | High | 613 | 686 | 1.1836 | 989.2455
OCEANO 1104Q08 | OCEANO 1104 | LOS PADRES | 12.4392 | 24.3462 | 67.44% | 7 | 8 | 100% | 0% | 0 | 0.040257 | 35.3263 | 3.0746 | 4.3725 | Medium | Medium | Medium | 614 | 657 | 1.4221 | 984.8672
COTTONWOOD 11031344 | COTTONWOOD 1103 | NORTH VALLEY | 7.7962 | 44.5024 | 98.83% | 0 | 5 | 62.89% | 0% | 0 | 0.035503 | 65.3912 | 1.8686 | 4.338 | Medium | Medium | Low | 615 | 577 | 2.3216 | 980.4946
PUTAH CREEK 11033851 | PUTAH CREEK 1103 | SACRAMENTO | 3.6658 | 82.0611 | 100% | 0 | 0 | 70.81% | 0% | 0 | 0.034621 | 65.3912 | 1.8797 | 4.2555 | Medium | Medium | Low | 616 | 587 | 2.2639 | 976.1566
BUELLTON 1102Y50 | BUELLTON 1102 | LOS PADRES | 11.1963 | 40.402 | 55.79% | 1 | 7 | 87.11% | 0% | 0 | 0.037194 | 47.6367 | 2.389 | 4.2328 | Medium | Medium | Medium | 617 | 624 | 1.7718 | 971.9011
MOUNTAIN QUARRIES 21016953 | MOUNTAIN QUARRIES 2101 | SIERRA | 5.7089 | 53.1337 | 100% | 0 | 0 | 100% | 0% | 0 | 0.037926 | 35.3263 | 3.1367 | 4.2025 | Medium | Medium | High | 618 | 665 | 1.3398 | 967.6682
COTTONWOOD 11039072 | COTTONWOOD 1103 | NORTH VALLEY | 28.4061 | 60.3164 | 100% | 4 | 3 | 99.13% | 0% | 0 | 0.06438 | 47.6367 | 1.3689 | 4.1983 | High | High | Low | 619 | 528 | 3.0669 | 963.4657
LAKEVILLE 11023341 | LAKEVILLE 1102 | SONOMA | 8.3809 | 81.4101 | 63.14% | 2 | 0 | 66.79% | 0% | 0 | 0.02532 | 65.3912 | 2.4798 | 4.1058 | Medium | Medium | Medium | 620 | 635 | 1.6557 | 959.2674
HICKS 2101XR250 | HICKS 2101 | SAN JOSE | 7.0147 | 55.6197 | 44.17% | 2 | 7 | 53.71% | 28.46% | 0 | 0.042978 | 26.5534 | 3.5951 | 4.1027 | Medium | Medium | High | 621 | 692 | 1.1412 | 955.1617
ORO FINO 110238698 | ORO FINO 1102 | NORTH VALLEY | 15.5224 | 87.0508 | 99.92% | 2 | 6 | 100% | 0% | 0 | 0.070272 | 65.3912 | 0.89227 | 4.1001 | High | High | Low | 622 | 453 | 4.5952 | 951.0589
CAMP EVERS 2106834583 | CAMP EVERS 2106 | CENTRAL COAST | 0.60497 | 39.087 | 36.91% | 0 | 0 | 100% | 69.26% | 0 | 0.069915 | 14.9507 | 3.9087 | 4.0857 | High | High | High | 623 | 714 | 1.0453 | 946.9588
COTATI 1103132 | COTATI 1103 | SONOMA | 25.3022 | 74.6812 | 24.81% | 4 | 9 | 100% | 0% | 0 | 0.073801 | 26.5534 | 2.0508 | 4.0188 | High | High | Low | 624 | 609 | 1.9597 | 942.8731
APPLE HILL 1104CB | APPLE HILL 1104 | SIERRA | 4.2262 | 51.4608 | 51.9% | 3 | 4 | 100% | 0% | 0 | 0.03278 | 47.6367 | 2.5597 | 3.9971 | Medium | Medium | Medium | 625 | 644 | 1.5616 | 938.8542
PAUL SWEET 2102 | PAUL SWEET 2102 | CENTRAL COAST | 0.085046 | 10 | 0% | 3 | 0 | 100% | 100% | 0 | 0.063894 | 19.9979 | 3.0738 | 3.9275 | High | High | Medium | 626 | 669 | 1.2777 | 934.8571
EL CERRITO G 1112BR180 | EL CERRITO G 1112 | EAST BAY | 1.3621 | 12.166 | 3.332% | 1 | 0 | 71.61% | 74.96% | 0 | 0.038138 | 19.9979 | 5.1411 | 3.9211 | Medium | Medium | High | 627 | 766 | 0.76268 | 930.9297
RINCON 1103CB | RINCON 1103 | SONOMA | 2.6796 | 27.7294 | 25.63% | 1 | 1 | 89.08% | 47% | 0 | 0.034549 | 35.3263 | 3.169 | 3.8678 | Medium | Medium | High | 628 | 679 | 1.2205 | 927.0086
LOW GAP 11012094 | LOW GAP 1101 | HUMBOLDT | 15.318 | 83.9747 | 100% | 2 | 4 | 90.42% | 0% | 0 | 0.077716 | 35.3263 | 1.4008 | 3.8459 | High | High | Low | 629 | 550 | 2.7454 | 923.1408
SHINGLE SPRINGS 211051800 | SHINGLE SPRINGS 2110 | SIERRA | 9.4169 | 11.4226 | 65.37% | 2 | 2 | 96.5% | 41.26% | 0 | 0.049018 | 26.5534 | 2.9295 | 3.813 | Medium | Medium | Medium | 630 | 666 | 1.3016 | 919.2949
TAR FLAT 0401 | TAR FLAT 0401 | YOSEMITE | 0.026649 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 19.9979 | 3.0633 | 3.771 | High | High | Medium | 631 | 676 | 1.2311 | 915.482
BUCKS CREEK 11031131 | BUCKS CREEK 1103 | NORTH VALLEY | 2.7493 | 88.8735 | 99.9% | 0 | 1 | 100% | 56.92% | 0 | 0.12924 | 85.4511 | 0.34069 | 3.7624 | High | High | Low | 632 | 293 | 11.0435 | 911.7109
BASALT 11065039 | BASALT 1106 | NORTH BAY | 1.6775 | 85.8937 | 60.16% | 0 | 1 | 30.77% | 0% | 0 | 0.017795 | 65.3912 | 3.2158 | 3.7421 | Low | Low | High | 633 | 688 | 1.1636 | 907.9485
ALTO 1125935 | ALTO 1125 | NORTH BAY | 3.0231 | 20.8124 | 24.9% | 7 | 7 | 94.09% | 0% | 0 | 0.038197 | 35.3263 | 2.7615 | 3.7263 | Medium | Medium | Medium | 634 | 663 | 1.3494 | 904.2064
UKIAH 1113CB | UKIAH 1113 | HUMBOLDT | 6.3928 | 56.8513 | 87.48% | 1 | 9 | 40.25% | 0% | 0 | 0.040164 | 35.3263 | 2.6035 | 3.694 | Medium | Medium | Medium | 635 | 658 | 1.4188 | 900.4802
MORAGA 11058354 | MORAGA 1105 | DIABLO | 0.25208 | 83.2522 | 100% | 0 | 0 | 8.053% | 20.65% | 0 | 0.026277 | 35.3263 | 3.9671 | 3.6826 | Medium | Medium | High | 636 | 732 | 0.92827 | 896.7862
COTTONWOOD 11031616 | COTTONWOOD 1103 | NORTH VALLEY | 45.6614 | 47.3529 | 99.79% | 2 | 10 | 92.93% | 0% | 0 | 0.10209 | 26.5534 | 1.3519 | 3.6648 | High | High | Low | 637 | 551 | 2.7109 | 893.1036
WISE 1102307494 | WISE 1102 | SIERRA | 32.9312 | 34.3215 | 79.46% | 1 | 9 | 98.67% | 0% | 0 | 0.082577 | 19.9979 | 2.2151 | 3.6579 | High | High | Low | 638 | 636 | 1.6514 | 889.4388
MONTE RIO 1113477 | MONTE RIO 1113 | SONOMA | 1.8187 | 34.6297 | 52.03% | 0 | 3 | 100% | 100% | 0 | 0.11271 | 11.2183 | 2.8387 | 3.5893 | High | High | Medium | 639 | 673 | 1.2644 | 885.7809
BRIDGEVILLE 110137484 | BRIDGEVILLE 1101 | HUMBOLDT | 7.5279 | 94.876 | 100% | 3 | 6 | 74.55% | 0% | 0 | 0.051968 | 85.4511 | 0.80668 | 3.5822 | Medium | Medium | Low | 640 | 459 | 4.4407 | 882.1916
DESCHUTES 11049726 | DESCHUTES 1104 | NORTH VALLEY | 14.9653 | 23.7872 | 88.61% | 1 | 3 | 89% | 0% | 0 | 0.03574 | 35.3263 | 2.837 | 3.5819 | Medium | Medium | Medium | 641 | 674 | 1.2626 | 878.6094
TEMPLETON 2113A70 | TEMPLETON 2113 | LOS PADRES | 22.5502 | 49.7318 | 87.96% | 0 | 9 | 33.69% | 0% | 0 | 0.03134 | 47.6367 | 2.3941 | 3.5742 | Medium | Medium | Medium | 642 | 648 | 1.4929 | 875.0275
BRIDGEVILLE 110169866 | BRIDGEVILLE 1101 | HUMBOLDT | 6.5416 | 93.8748 | 99.88% | 6 | 2 | 100% | 0% | 0 | 0.071282 | 65.3912 | 0.75814 | 3.5339 | High | High | Low | 643 | 448 | 4.6612 | 871.4533
LAYTONVILLE 110268436 | LAYTONVILLE 1102 | HUMBOLDT | 9.1013 | 91.8828 | 93.46% | 1 | 2 | 100% | 32.77% | 1 | 0.091162 | 26.5534 | 1.4538 | 3.5192 | High | High | Low | 644 | 568 | 2.4207 | 867.9194
BIG BASIN 1102 | BIG BASIN 1102 | CENTRAL COAST | 0.014511 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 11.2183 | 2.3875 | 3.4878 | High | High | Medium | 645 | 651 | 1.4609 | 864.4002
WISE 11022054 | WISE 1102 | SIERRA | 12.9562 | 34.6019 | 54.65% | 2 | 5 | 100% | 0% | 0 | 0.030193 | 47.6367 | 2.4077 | 3.463 | Medium | Medium | Medium | 646 | 654 | 1.4383 | 860.9124
FULTON 1107CB | FULTON 1107 | SONOMA | 0.65239 | 10 | 62.57% | 2 | 0 | 4.947% | 100% | 0 | 0.053816 | 26.5534 | 2.4231 | 3.4626 | Medium | Medium | Medium | 647 | 656 | 1.429 | 857.4495
SAND CREEK 11037140 | SAND CREEK 1103 | FRESNO | 26.314 | 18.5001 | 91.83% | 0 | 4 | 100% | 0% | 0 | 0.03967 | 35.3263 | 2.47 | 3.4614 | Medium | Medium | Medium | 648 | 661 | 1.4014 | 853.9869
RACETRACK 170423195 | RACETRACK 1704 | YOSEMITE | 7.7484 | 59.3101 | 42.51% | 0 | 0 | 100% | 0% | 0 | 0.036794 | 47.6367 | 1.973 | 3.4581 | Medium | Medium | Low | 649 | 626 | 1.7528 | 850.5255
CLARKSVILLE 210575884 | CLARKSVILLE 2105 | SIERRA | 10.3522 | 19.5403 | 73.75% | 1 | 8 | 92.27% | 38.69% | 1 | 0.049935 | 19.9979 | 3.4349 | 3.4301 | Medium | Medium | High | 650 | 721 | 0.9986 | 847.0674
GANSNER 110199388 | GANSNER 1101 | NORTH VALLEY | 2.0835 | 75.9591 | 98.87% | 1 | 0 | 93.65% | 0% | 0 | 0.041605 | 26.5534 | 3.0558 | 3.3759 | Medium | Medium | Medium | 651 | 699 | 1.1048 | 843.6373
CORRAL 110112612 | CORRAL 1101 | STOCKTON | 18.7862 | 47.6011 | 68.25% | 0 | 10 | 93.49% | 0% | 0 | 0.042229 | 35.3263 | 2.2608 | 3.3727 | Medium | Medium | Medium | 652 | 649 | 1.4918 | 840.2615
SHEPHERD 2111R1400 | SHEPHERD 2111 | FRESNO | 19.9144 | 43.3803 | 100% | 0 | 4 | 86.57% | 0% | 0 | 0.063987 | 35.3263 | 1.487 | 3.3613 | High | High | Low | 653 | 588 | 2.2604 | 836.8888
WEIMER 1101 | WEIMER 1101 | (blank) | 0.15676 | 70 | 100% | 0 | 0 | 100% | 0% | 0 | 0.042368 | 47.6367 | 1.6634 | 3.3572 | Medium | Medium | Low | 654 | 602 | 2.0183 | 833.5275
TEMPLETON 21136055 | TEMPLETON 2113 | LOS PADRES | 39.7266 | 74.9616 | 83.37% | 3 | 5 | 100% | 12.3% | 1 | 0.24234 | 26.5534 | 0.51413 | 3.3084 | High | High | Low | 655 | 392 | 6.435 | 830.1704
PUEBLO 11042802 | PUEBLO 1104 | NORTH BAY | 9.7765 | 58.2394 | 48.14% | 0 | 5 | 89.72% | 0% | 0 | 0.072026 | 14.9507 | 3.0683 | 3.3041 | High | High | Medium | 656 | 705 | 1.0768 | 826.8619
PEORIA 170411232 | PEORIA 1704 | YOSEMITE | 13.0063 | 19.4612 | 87.58% | 0 | 2 | 75.44% | 0% | 0 | 0.029217 | 35.3263 | 3.195 | 3.2976 | Medium | Medium | High | 657 | 715 | 1.0321 | 823.5579
CRESCENT MILLS 21012056 | CRESCENT MILLS 2101 | NORTH VALLEY | 2.8566 | 93.184 | 33.06% | 0 | 0 | 44.02% | 0% | 0 | 0.016743 | 85.4511 | 2.3025 | 3.2941 | Low | Low | Medium | 658 | 655 | 1.4307 | 820.2603
HAMILTON BRANCH 11012046 | HAMILTON BRANCH 1101 | NORTH VALLEY | 9.1511 | 77.8147 | 51.04% | 2 | 2 | 99.57% | 0% | 0 | 0.036581 | 35.3263 | 2.517 | 3.2527 | Medium | Medium | Medium | 659 | 667 | 1.2923 | 816.9661
STAFFORD 1102524 | STAFFORD 1102 | NORTH BAY | 3.4472 | 66.1749 | 51.31% | 1 | 2 | 26.91% | 0% | 0 | 0.024387 | 47.6367 | 2.779 | 3.2285 | Medium | Medium | Medium | 660 | 689 | 1.1617 | 813.7134
DUNBAR 11033135 | DUNBAR 1103 | SONOMA | 0.22216 | 10 | 100% | 0 | 0 | 29.43% | 100% | 0 | 0.068741 | 11.2183 | 4.1817 | 3.2247 | High | High | High | 661 | 764 | 0.77116 | 810.4849
MOLINO 110241392 | MOLINO 1102 | SONOMA | 3.7264 | 58.0945 | 65.77% | 1 | 0 | 25.48% | 0% | 0 | 0.016595 | 65.3912 | 2.9568 | 3.2086 | Low | Low | Medium | 662 | 704 | 1.0852 | 807.2602
OAKHURST 110348842 | OAKHURST 1103 | YOSEMITE | 2.3666 | 32.8421 | 100% | 0 | 9 | 82.85% | 0% | 0 | 0.033725 | 35.3263 | 2.6913 | 3.2064 | Medium | Medium | Medium | 663 | 685 | 1.1914 | 804.0515
EAST QUINCY 1101CB | EAST QUINCY 1101 | NORTH VALLEY | 2.2646 | 54.1438 | 97.01% | 0 | 2 | 28.47% | 0% | 0 | 0.022042 | 47.6367 | 3.0485 | 3.2009 | Medium | Medium | Medium | 664 | 711 | 1.05 | 800.8452
CORRAL 110112606 | CORRAL 1101 | STOCKTON | 22.4607 | 31.7729 | 96.48% | 1 | 4 | 100% | 0% | 0 | 0.040006 | 35.3263 | 2.252 | 3.1827 | Medium | Medium | Medium | 665 | 659 | 1.4133 | 797.6443
PETALUMA C 1108618 | PETALUMA C 1108 | SONOMA | 8.1405 | 67.3719 | 25.14% | 5 | 1 | 74.64% | 0% | 0 | 0.022157 | 47.6367 | 3.0104 | 3.1775 | Medium | Medium | Medium | 666 | 709 | 1.0555 | 794.4616
JESSUP 11011993 | JESSUP 1101 | NORTH VALLEY | 2.9672 | 23.0128 | 100% | 0 | 1 | 100% | 0% | 0 | 0.031722 | 47.6367 | 2.0979 | 3.1701 | Medium | Medium | Low | 667 | 647 | 1.5111 | 791.2841
FOOTHILL 1101CB | FOOTHILL 1101 | LOS PADRES | 10.7012 | 70.0715 | 52.58% | 0 | 2 | 48.74% | 0% | 0 | 0.039956 | 26.5534 | 2.9872 | 3.1694 | Medium | Medium | Medium | 668 | 708 | 1.061 | 788.1139
FLINT 1101750 | FLINT 1101 | SIERRA | 3.8545 | 52.6304 | 83.81% | 0 | 0 | 41.31% | 0% | 0 | 0.018732 | 65.3912 | 2.5792 | 3.1593 | Low | Low | Medium | 669 | 678 | 1.2249 | 784.9446
BOLINAS 11011232 | BOLINAS 1101 | NORTH BAY | 2.4469 | 73.1714 | 0% | 0 | 1 | 100% | 0% | 0 | 0.019829 | 47.6367 | 3.3269 | 3.1425 | Low | Low | High | 670 | 729 | 0.94457 | 781.7853
FRUITLAND 1142CB | FRUITLAND 1142 | HUMBOLDT | 10.4822 | 87.3271 | 88.71% | 7 | 4 | 68.32% | 0% | 0 | 0.071375 | 47.6367 | 0.91967 | 3.1269 | High | High | Low | 671 | 511 | 3.4 | 778.6428
VACAVILLE 1108 | VACAVILLE 1108 | SACRAMENTO | 0.027876 | 65 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041002 | 47.6367 | 1.5966 | 3.1185 | Medium | Medium | Low | 672 | 610 | 1.9532 | 775.5159
NAPA 1112 | NAPA 1112 | NORTH BAY | 0.032215 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 35.3263 | 3.0858 | 3.108 | Medium | Medium | High | 673 | 717 | 1.0072 | 772.3974
CAMP EVERS 210510996 | CAMP EVERS 2105 | CENTRAL COAST | 0.7626 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 4.4922 | 3.1023 | High | High | High | 674 | 786 | 0.69059 | 769.2894
COARSEGOLD 21046288 | COARSEGOLD 2104 | YOSEMITE | 10.4247 | 64.6171 | 98.8% | 1 | 30 | 100% | 0% | 0 | 0.084064 | 19.9979 | 1.84 | 3.0932 | High | High | Low | 675 | 632 | 1.6811 | 766.1872
DEL MAR 210975802 | DEL MAR 2109 | SIERRA | 0.35089 | 17.4936 | 85.01% | 0 | 1 | 84.46% | 0% | 0 | 0.026543 | 47.6367 | 2.444 | 3.0902 | Medium | Medium | Medium | 676 | 672 | 1.2644 | 763.0939
CORRAL 1101 | CORRAL 1101 | STOCKTON | 0.001152 | 75 | 100% | 0 | 0 | 100% | 0% | 0 | 0.043778 | 65.3912 | 1.0736 | 3.0735 | Medium | Medium | Low | 677 | 543 | 2.8627 | 760.0037
PASO ROBLES 1103N54 | PASO ROBLES 1103 | LOS PADRES | 19.5682 | 48.3867 | 60.55% | 1 | 29 | 90.91% | 0% | 0 | 0.065373 | 35.3263 | 1.33 | 3.0715 | High | High | Low | 678 | 581 | 2.3094 | 756.9302
BELL 110750172 | BELL 1107 | SIERRA | 17.5892 | 13.0992 | 68.99% | 0 | 6 | 94.29% | 0% | 0 | 0.046234 | 26.5534 | 2.5016 | 3.0712 | Medium | Medium | Medium | 679 | 677 | 1.2277 | 753.8587
LAURELES 111184523 | LAURELES 1111 | CENTRAL COAST | 1.2223 | 80.6528 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045426 | 35.3263 | 1.8947 | 3.0405 | Medium | Medium | Low | 680 | 640 | 1.6047 | 750.7875
WOODSIDE 11012299 | WOODSIDE 1101 | PENINSULA | 1.6209 | 33.6689 | 6.985% | 2 | 3 | 88.38% | 100% | 0 | 0.073666 | 11.2183 | 3.6727 | 3.0352 | High | High | High | 681 | 749 | 0.82641 | 747.747
CORRAL 110214026 | CORRAL 1102 | STOCKTON | 10.1342 | 44.5079 | 47.19% | 1 | 3 | 100% | 0% | 0 | 0.03277 | 35.3263 | 2.6188 | 3.0316 | Medium | Medium | Medium | 682 | 690 | 1.1576 | 744.7119
OAKHURST 1101CB | OAKHURST 1101 | YOSEMITE | 2.8974 | 35.5621 | 74.52% | 0 | 12 | 97.3% | 1.934% | 0 | 0.040153 | 26.5534 | 2.8286 | 3.0158 | Medium | Medium | Medium | 683 | 707 | 1.0662 | 741.6802
VACAVILLE 110838316 | VACAVILLE 1108 | SACRAMENTO | 14.7024 | 65.6281 | 99.57% | 1 | 4 | 63.02% | 0% | 0 | 0.052621 | 35.3263 | 1.6146 | 3.0014 | Medium | Medium | Low | 684 | 620 | 1.8589 | 738.6644
MENLO 11028896 | MENLO 1102 | PENINSULA | 0.53492 | 85.6249 | 0.9567% | 0 | 0 | 34.58% | 0% | 0 | 0.01116 | 65.3912 | 4.0778 | 2.9759 | Low | Low | High | 685 | 776 | 0.72979 | 735.663
BRUNSWICK 110633050 | BRUNSWICK 1106 | SIERRA | 1.709 | 18.2327 | 78.9% | 2 | 0 | 44.77% | 0% | 0 | 0.015167 | 65.3912 | 2.9867 | 2.9622 | Low | Low | Medium | 686 | 722 | 0.99181 | 732.6871
CORRAL 110336680 | CORRAL 1103 | STOCKTON | 9.9701 | 19.0488 | 89.57% | 1 | 2 | 49.8% | 0% | 0 | 0.017976 | 47.6367 | 3.438 | 2.944 | Low | Low | High | 687 | 744 | 0.85633 | 729.7249
WOODSIDE 1101 | WOODSIDE 1101 | PENINSULA | 0.091557 | 33.2557 | 52.71% | 3 | 2 | 100% | 100% | 0 | 0.1142 | 11.2183 | 2.2665 | 2.9039 | High | High | Medium | 688 | 668 | 1.2812 | 726.7808
FROGTOWN 1702 | FROGTOWN 1702 | STOCKTON | 0.0028747 | 65 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041002 | 26.5534 | 2.6562 | 2.8919 | Medium | Medium | Medium | 689 | 702 | 1.0887 | 723.877
OLETA 1101CB | OLETA 1101 | STOCKTON | 3.1205 | 69.4789 | 19.21% | 0 | 0 | 92.33% | 0% | 0 | 0.02053 | 47.6367 | 2.9528 | 2.8878 | Low | Low | Medium | 690 | 726 | 0.97799 | 720.9851
EL CERRITO G 1105R6998 | EL CERRITO G 1105 | EAST BAY | 0.025405 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 4.1798 | 2.8865 | High | High | High | 691 | 786 | 0.69059 | 718.0973
LAYTONVILLE 1102500 | LAYTONVILLE 1102 | HUMBOLDT | 20.1821 | 81.3832 | 99.67% | 9 | 6 | 69.04% | 0% | 0 | 0.048589 | 47.6367 | 1.2335 | 2.855 | Medium | Medium | Low | 692 | 578 | 2.3146 | 715.2108
LINCOLN 11045391 | LINCOLN 1104 | SIERRA | 0.95086 | 68.8646 | 19.08% | 0 | 0 | 100% | 0% | 0 | 0.022019 | 47.6367 | 2.7141 | 2.8468 | Medium | Medium | Medium | 693 | 712 | 1.0489 | 712.3557
SANTA YNEZ 1104Y04 | SANTA YNEZ 1104 | LOS PADRES | 15.3206 | 51.8152 | 75.91% | 0 | 12 | 68.36% | 0% | 0 | 0.033153 | 35.3263 | 2.4224 | 2.837 | Medium | Medium | Medium | 694 | 687 | 1.1712 | 709.509
SPRING GAP 17029280 | SPRING GAP 1702 | YOSEMITE | 6.3606 | 34.7112 | 42.89% | 5 | 5 | 100% | 100% | 0 | 0.14642 | 11.2183 | 1.7184 | 2.8225 | High | High | Low | 695 | 637 | 1.6426 | 706.672
BELLEVUE 2103648 | BELLEVUE 2103 | SONOMA | 2.2962 | 73.8161 | 100% | 0 | 2 | 14.14% | 0% | 0 | 0.019638 | 47.6367 | 2.9986 | 2.8051 | Low | Low | Medium | 696 | 730 | 0.93548 | 703.8494
MONTICELLO 1101720 | MONTICELLO 1101 | NORTH BAY | 7.5573 | 64.5271 | 99.74% | 1 | 2 | 90.69% | 0% | 0 | 0.057594 | 19.9979 | 2.4222 | 2.7897 | Medium | Medium | Medium | 697 | 691 | 1.1518 | 701.0443
GRASS VALLEY 1101CB | GRASS VALLEY 1101 | SIERRA | 1.7504 | 55.588 | 24.73% | 1 | 1 | 65.41% | 2.088% | 0 | 0.027071 | 35.3263 | 2.9159 | 2.7885 | Medium | Medium | Medium | 698 | 727 | 0.9563 | 698.2546
BRUNSWICK 11038918 | BRUNSWICK 1103 | SIERRA | 0.62743 | 83.4132 | 18.44% | 0 | 0 | 29.2% | 0% | 0 | 0.012022 | 85.4511 | 2.7121 | 2.7862 | Low | Low | Medium | 699 | 716 | 1.0273 | 695.4661
PUTAH CREEK 110267858 | PUTAH CREEK 1102 | SACRAMENTO | 11.5068 | 51.7319 | 80.2% | 2 | 0 | 99.07% | 0% | 0 | 0.037122 | 47.6367 | 1.5751 | 2.7854 | Medium | Medium | Low | 700 | 625 | 1.7684 | 692.6799
LINCOLN 11042070 | LINCOLN 1104 | SIERRA | 21.0429 | 49.8208 | 65.19% | 5 | 11 | 72.52% | 0% | 0 | 0.042249 | 26.5534 | 2.4592 | 2.7588 | Medium | Medium | Medium | 701 | 695 | 1.1219 | 689.8945
VALLEY VIEW 1103P160 | VALLEY VIEW 1103 | EAST BAY | 0.28761 | 80 | 0% | 0 | 0 | 7.876% | 100% | 0 | 0.040365 | 14.9507 | 4.5675 | 2.7565 | Medium | Medium | High | 702 | 821 | 0.60349 | 687.1357
CORRAL 110136652 | CORRAL 1101 | STOCKTON | 18.0317 | 36.0873 | 87.44% | 1 | 8 | 100% | 0% | 0 | 0.053562 | 35.3263 | 1.4501 | 2.7438 | Medium | Medium | Low | 703 | 619 | 1.8922 | 684.3792
ELECTRA 1101L1697 | ELECTRA 1101 | STOCKTON | 5.4545 | 12.0564 | 100% | 1 | 2 | 100% | 0% | 0 | 0.039464 | 26.5534 | 2.6165 | 2.7419 | Medium | Medium | Medium | 704 | 713 | 1.0479 | 681.6355
BRUNSWICK 1106 | BRUNSWICK 1106 | SIERRA | 0.037997 | 60 | 100% | 0 | 0 | 100% | 0% | 0 | 0.039678 | 26.5534 | 2.6004 | 2.7397 | Medium | Medium | Medium | 705 | 710 | 1.0536 | 678.8936
SAN RAFAEL 11071415 | SAN RAFAEL 1107 | NORTH BAY | 0.70882 | 10 | 28.8% | 0 | 0 | 59.59% | 100% | 0 | 0.059639 | 11.2183 | 4.0649 | 2.7196 | Medium | Medium | High | 706 | 799 | 0.66905 | 676.1539
MOLINO 1101891 | MOLINO 1101 | SONOMA | 3.0063 | 38.1554 | 45.65% | 1 | 1 | 95.38% | 41.51% | 0 | 0.054529 | 19.9979 | 2.4796 | 2.7039 | Medium | Medium | Medium | 707 | 701 | 1.0905 | 673.4342
SANTA YNEZ 110477098 | SANTA YNEZ 1104 | LOS PADRES | 10.6194 | 59.0619 | 89.18% | 0 | 4 | 81.31% | 0% | 0 | 0.037257 | 26.5534 | 2.7174 | 2.6883 | Medium | Medium | Medium | 708 | 723 | 0.98931 | 670.7303
TEMPLETON 21132949 | TEMPLETON 2113 | LOS PADRES | 0.47714 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 35.3263 | 2.6464 | 2.6655 | Medium | Medium | Medium | 709 | 717 | 1.0072 | 668.042
HAMILTON BRANCH 11013049 | HAMILTON BRANCH 1101 | NORTH VALLEY | 0.54973 | 41.4686 | 100% | 0 | 1 | 32.98% | 0% | 0 | 0.018634 | 65.3912 | 2.1667 | 2.6401 | Low | Low | Low | 710 | 680 | 1.2185 | 665.3765
BELLEVUE 2103552 | BELLEVUE 2103 | SONOMA | 9.102 | 59.5579 | 60.22% | 2 | 0 | 60.99% | 9.086% | 0 | 0.023335 | 35.3263 | 3.2018 | 2.6393 | Medium | Medium | High | 711 | 750 | 0.82433 | 662.7363
GUALALA 11124431 | GUALALA 1112 | HUMBOLDT | 1.4123 | 70.1709 | 0% | 0 | 4 | 100% | 0% | 0 | 0.02067 | 65.3912 | 1.946 | 2.6304 | Low | Low | Low | 712 | 662 | 1.3517 | 660.097
SAUSALITO 110284278 | SAUSALITO 1102 | NORTH BAY | 1.3711 | 32.8864 | 5.777% | 0 | 2 | 90.29% | 0% | 0 | 0.021793 | 35.3263 | 3.3996 | 2.6173 | Low | Low | High | 713 | 765 | 0.76987 | 657.4666
PUTAH CREEK 1102CB | PUTAH CREEK 1102 | SACRAMENTO | 4.8366 | 82.2611 | 100% | 0 | 0 | 37.85% | 0% | 0 | 0.025161 | 47.6367 | 2.1795 | 2.6123 | Medium | Medium | Low | 714 | 683 | 1.1986 | 654.8494
LAYTONVILLE 110189606 | LAYTONVILLE 1101 | HUMBOLDT | 11.3479 | 67.7426 | 99.65% | 4 | 7 | 95.33% | 0% | 0 | 0.048183 | 35.3263 | 1.5294 | 2.6033 | Medium | Medium | Low | 715 | 629 | 1.7021 | 652.2371
GIRVAN 1102 | GIRVAN 1102 | NORTH VALLEY | 0.038598 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 11.2183 | 1.7778 | 2.5971 | High | High | Low | 716 | 651 | 1.4609 | 649.6338
LAYTONVILLE 1102682 | LAYTONVILLE 1102 | HUMBOLDT | 14.8214 | 90.6873 | 91.3% | 5 | 3 | 100% | 0% | 0 | 0.051212 | 65.3912 | 0.7707 | 2.5809 | Medium | Medium | Low | 717 | 513 | 3.3488 | 647.0367
PASO ROBLES 1103N02 | PASO ROBLES 1103 | LOS PADRES | 0.044146 | 10 | 36.23% | 0 | 0 | 100% | 0% | 0 | 0.017045 | 47.6367 | 3.1571 | 2.5634 | Low | Low | High | 718 | 752 | 0.81194 | 644.4557
PEORIA 170413494 | PEORIA 1704 | YOSEMITE | 3.2575 | 18.8459 | 98.09% | 0 | 1 | 43.79% | 0% | 0 | 0.017531 | 47.6367 | 3.0588 | 2.5544 | Low | Low | Medium | 719 | 747 | 0.8351 | 641.8924
SILVERADO 210437632 | SILVERADO 2104 | NORTH BAY | 22.9342 | 51.0024 | 44.2% | 16 | 15 | 100% | 100% | 0 | 0.67223 | 1 | 3.7875 | 2.5461 | High | High | High | 720 | 798 | 0.67223 | 639.338
COARSEGOLD 2104CB | COARSEGOLD 2104 | YOSEMITE | 2.4475 | 54.0073 | 41.51% | 0 | 3 | 100% | 0% | 0 | 0.025403 | 47.6367 | 2.1019 | 2.5435 | Medium | Medium | Low | 721 | 681 | 1.2101 | 636.7919
MOLINO 1104380 | MOLINO 1104 | SONOMA | 2.046 | 71.2548 | 46.79% | 0 | 0 | 7.207% | 0% | 0 | 0.011223 | 65.3912 | 3.36 | 2.4657 | Low | Low | High | 722 | 773 | 0.73385 | 634.2484
CLOVERDALE 110247214 | CLOVERDALE 1102 | SONOMA | 0.027332 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 35.3263 | 2.4417 | 2.4593 | Medium | Medium | Medium | 723 | 717 | 1.0072 | 631.7827
HIGHLANDS 110280660 | HIGHLANDS 1102 | HUMBOLDT | 5.365 | 78.0742 | 39.2% | 1 | 2 | 71.03% | 0% | 0 | 0.021888 | 35.3263 | 3.1794 | 2.4584 | Medium | Medium | High | 724 | 763 | 0.77324 | 629.3234
ELK CREEK 11012008 | ELK CREEK 1101 | NORTH VALLEY | 2.1575 | 78.9163 | 100% | 0 | 1 | 11.89% | 0% | 0 | 0.019472 | 65.3912 | 1.9305 | 2.4581 | Low | Low | Low | 725 | 670 | 1.2733 | 626.865
MARIPOSA 210190130 | MARIPOSA 2101 | YOSEMITE | 0.091387 | 70 | 0% | 0 | 0 | 100% | 0% | 0 | 0.019016 | 47.6367 | 2.6983 | 2.4443 | Low | Low | Medium | 726 | 734 | 0.90585 | 624.4069
LAKEWOOD 2110W577R | LAKEWOOD 2110 | DIABLO | 0.42837 | 10 | 37.2% | 0 | 0 | 46.99% | 100% | 0 | 0.056527 | 11.2183 | 3.8435 | 2.4373 | Medium | Medium | High | 727 | 810 | 0.63414 | 621.9626
SHINGLE SPRINGS 210935598 | SHINGLE SPRINGS 2109 | SIERRA | 10.9289 | 31.2867 | 70.52% | 1 | 5 | 100% | 42.6% | 0 | 0.072647 | 14.9507 | 2.2274 | 2.4192 | High | High | Low | 728 | 703 | 1.0861 | 619.5253
JESSUP 11023105 | JESSUP 1102 | NORTH VALLEY | 5.7601 | 31.7951 | 100% | 0 | 2 | 92.48% | 0% | 0 | 0.031899 | 35.3263 | 2.1459 | 2.4181 | Medium | Medium | Low | 729 | 694 | 1.1269 | 617.1061
ATASCADERO 1101A02 | ATASCADERO 1101 | LOS PADRES | 11.1355 | 10.7743 | 66.74% | 2 | 2 | 100% | 7.928% | 0 | 0.044541 | 14.9507 | 3.626 | 2.4147 | Medium | Medium | High | 730 | 800 | 0.66592 | 614.688
MILPITAS 1108XR122 | MILPITAS 1108 | SAN JOSE | 0.28331 | 75 | 0% | 0 | 0 | 3.797% | 0% | 0 | 0.0075908 | 85.4511 | 3.7218 | 2.4142 | Low | Low | High | 731 | 806 | 0.64865 | 612.2733
STAFFORD 11021202 | STAFFORD 1102 | NORTH BAY | 7.2996 | 85.3549 | 21.22% | 0 | 3 | 92.36% | 0% | 0 | 0.031995 | 35.3263 | 2.1233 | 2.3999 | Medium | Medium | Low | 732 | 693 | 1.1303 | 609.8592
SONOMA 110310257 | SONOMA 1103 | SONOMA | 0.24108 | 10 | 100% | 0 | 0 | 12.38% | 100% | 0 | 0.058573 | 11.2183 | 3.6175 | 2.3771 | Medium | Medium | High | 733 | 803 | 0.65709 | 607.4593
PEABODY 2113CB | PEABODY 2113 | SACRAMENTO | 1.6686 | 58.5758 | 80.04% | 0 | 1 | 27.33% | 0% | 0 | 0.01682 | 47.6367 | 2.9585 | 2.3705 | Low | Low | Medium | 734 | 754 | 0.80125 | 605.0822
ELK CREEK 1101CB | ELK CREEK 1101 | NORTH VALLEY | 0.084247 | 80 | 68.8% | 0 | 0 | 100% | 0% | 0 | 0.035328 | 47.6367 | 1.406 | 2.3661 | Medium | Medium | Low | 735 | 630 | 1.6829 | 602.7117
PETALUMA C 1108600 | PETALUMA C 1108 | SONOMA | 4.0703 | 32.8182 | 38.32% | 2 | 6 | 47.11% | 0% | 0 | 0.020667 | 47.6367 | 2.3993 | 2.3621 | Low | Low | Medium | 736 | 725 | 0.98451 | 600.3456
RESERVATION ROAD 11013026 | RESERVATION ROAD 1101 | CENTRAL COAST | 21.8928 | 54.2364 | 36.93% | 7 | 8 | 96.87% | 0% | 0 | 0.070296 | 19.9979 | 1.6766 | 2.3569 | High | High | Low | 737 | 660 | 1.4058 | 597.9835
COTATI 1102282 | COTATI 1102 | SONOMA | 4.4441 | 39.13 | 50.31% | 2 | 2 | 88.16% | 0% | 0 | 0.025185 | 35.3263 | 2.6402 | 2.349 | Medium | Medium | Medium | 738 | 738 | 0.8897 | 595.6267
PARADISE 11022024 | PARADISE 1102 | NORTH VALLEY | 0.64392 | 10 | 28.85% | 0 | 1 | 39.71% | 100% | 0 | 0.044388 | 11.2183 | 4.7148 | 2.3477 | Medium | Medium | High | 739 | 859 | 0.49795 | 593.2777
LAKEWOOD 2224W544R | LAKEWOOD 2224 | DIABLO | 0.041988 | 10 | 100% | 0 | 0 | 0.7884% | 100% | 0 | 0.052488 | 11.2183 | 3.9642 | 2.3342 | Medium | Medium | High | 740 | 826 | 0.58883 | 590.93
ROB ROY 21045082 | ROB ROY 2104 | CENTRAL COAST | 24.4071 | 49.5744 | 97.38% | 64 | 6 | 98.22% | 97.15% | 0 | 0.73013 | 1 | 3.1854 | 2.3258 | High | High | High | 741 | 775 | 0.73013 | 588.5957
CLOVERDALE 110254760 | CLOVERDALE 1102 | SONOMA | 0.13003 | 10 | 100% | 0 | 0 | 93.87% | 0% | 0 | 0.026858 | 35.3263 | 2.4446 | 2.3195 | Medium | Medium | Medium | 742 | 728 | 0.94881 | 586.27
NARROWS 21052214 | NARROWS 2105 | SIERRA | 0.0028409 | 70 | 0% | 0 | 0 | 100% | 0% | 0 | 0.019016 | 47.6367 | 2.5602 | 2.3192 | Low | Low | Medium | 743 | 734 | 0.90585 | 583.9505
RED BLUFF 110451238 | RED BLUFF 1104 | NORTH VALLEY | 39.381 | 43.7242 | 96.09% | 3 | 21 | 100% | 0% | 0 | 0.089857 | 19.9979 | 1.2852 | 2.3095 | High | High | Low | 744 | 622 | 1.7969 | 581.6313
FULTON 110410281 | FULTON 1104 | SONOMA | 0.51664 | 22.43 | 74.95% | 0 | 1 | 49.63% | 0% | 0 | 0.015765 | 47.6367 | 3.068 | 2.3041 | Low | Low | Medium | 745 | 771 | 0.75099 | 579.3218
CLEAR LAKE 110192870 | CLEAR LAKE 1101 | HUMBOLDT | 1.0943 | 58.4315 | 90.41% | 0 | 0 | 6.07% | 0% | 0 | 0.016559 | 47.6367 | 2.9112 | 2.2964 | Low | Low | Medium | 746 | 760 | 0.78881 | 577.0177
GABILAN 11013090 | GABILAN 1101 | CENTRAL COAST | 1.8466 | 75 | 100% | 0 | 0 | 5.274% | 0% | 0 | 0.02262 | 35.3263 | 2.8398 | 2.2693 | Medium | Medium | Medium | 747 | 755 | 0.7991 | 574.7214
PASO ROBLES 110359763 | PASO ROBLES 1103 | LOS PADRES | 2.8193 | 65.7222 | 66.01% | 0 | 0 | 100% | 0% | 0 | 0.031437 | 35.3263 | 2.0367 | 2.2619 | Medium | Medium | Low | 748 | 697 | 1.1106 | 572.4521
OLETA 11011217 | OLETA 1101 | STOCKTON | 14.427 | 60.7702 | 100% | 1 | 3 | 83.71% | 43.16% | 1 | 0.071429 | 14.9507 | 2.1108 | 2.2542 | High | High | Low | 749 | 706 | 1.0679 | 570.1902
VINEYARD 21086952 | VINEYARD 2108 | MISSION | 0.0028424 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 3.2583 | 2.2502 | High | High | High | 750 | 786 | 0.69059 | 567.936
HORSESHOE 110450142 | HORSESHOE 1104 | SIERRA | 0.99943 | 10 | 98.77% | 0 | 1 | 24.44% | 0% | 0 | 0.015652 | 35.3263 | 3.9959 | 2.2095 | Low | Low | High | 751 | 837 | 0.55294 | 565.6859
BIG BASIN 11015479 | BIG BASIN 1101 | CENTRAL COAST | 0.17042 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 3.0984 | 2.1397 | High | High | High | 752 | 786 | 0.69059 | 563.4764
WILLITS 1103538 | WILLITS 1103 | HUMBOLDT | 6.4253 | 81.3489 | 100% | 3 | 1 | 100% | 27.62% | 0 | 0.083475 | 14.9507 | 1.7136 | 2.1386 | High | High | Low | 753 | 675 | 1.248 | 561.3366
MOLINO 1101152 | MOLINO 1101 | SONOMA | 2.0022 | 35.0368 | 46.62% | 3 | 1 | 17.51% | 2.1% | 0 | 0.012176 | 65.3912 | 2.6304 | 2.0944 | Low | Low | Medium | 754 | 757 | 0.79623 | 559.1981
PEORIA 170575274 | PEORIA 1705 | YOSEMITE | 0.58699 | 10 | 100% | 0 | 0 | 18.06% | 0% | 0 | 0.012746 | 47.6367 | 3.4448 | 2.0915 | Low | Low | High | 755 | 818 | 0.60716 | 557.1036
MONTICELLO 110165454 | MONTICELLO 1101 | NORTH BAY | 0.17975 | 75.7164 | 100% | 0 | 0 | 9.577% | 0% | 0 | 0.018251 | 47.6367 | 2.4012 | 2.0876 | Low | Low | Medium | 756 | 741 | 0.8694 | 555.0121
BRIDGEVILLE 1101CB | BRIDGEVILLE 1101 | HUMBOLDT | 8.4707 | 94.1626 | 99.27% | 7 | 0 | 100% | 9.505% | 1 | 0.10184 | 65.3912 | 0.31236 | 2.0801 | High | High | Low | 757 | 389 | 6.6593 | 552.9245
DESCHUTES 11019722 | DESCHUTES 1101 | NORTH VALLEY | 2.8886 | 47.2823 | 92.43% | 0 | 2 | 60.75% | 0% | 0 | 0.024427 | 35.3263 | 2.3843 | 2.0574 | Medium | Medium | Medium | 758 | 742 | 0.8629 | 550.8445
SANTA YNEZ 1101Y14 | SANTA YNEZ 1101 | LOS PADRES | 4.5467 | 84.753 | 58.25% | 0 | 0 | 27.67% | 0% | 0 | 0.016519 | 47.6367 | 2.6036 | 2.0488 | Low | Low | Medium | 759 | 761 | 0.78692 | 548.787
PUEBLO 2103678 | PUEBLO 2103 | NORTH BAY | 25.5805 | 63.7412 | 53.4% | 28 | 21 | 98.22% | 87.3% | 1 | 0.69166 | 1 | 2.9613 | 2.0482 | High | High | Medium | 760 | 784 | 0.69166 | 546.7382
PANORAMA 11019092 | PANORAMA 1101 | NORTH VALLEY | 9.7913 | 10 | 99.08% | 0 | 8 | 48.48% | 0% | 0 | 0.033887 | 35.3263 | 1.6659 | 1.9943 | Medium | Medium | Low | 761 | 684 | 1.1971 | 544.69
JAMESON 11057652 | JAMESON 1105 | SACRAMENTO | 15.7797 | 54.8992 | 80.61% | 0 | 3 | 36.24% | 0% | 0 | 0.021376 | 35.3263 | 2.6329 | 1.9882 | Low | Low | Medium | 762 | 770 | 0.75514 | 542.6958
VASCO 110211338 | VASCO 1102 | MISSION | 3.3669 | 79.9716 | 100% | 0 | 1 | 17.52% | 0% | 0 | 0.020726 | 35.3263 | 2.7006 | 1.9773 | Low | Low | Medium | 763 | 774 | 0.73217 | 540.7076
JARVIS 1101MR210 | JARVIS 1101 | MISSION | 0.45193 | 56.1032 | 64.09% | 0 | 0 | 5.821% | 0% | 0 | 0.011506 | 47.6367 | 3.5376 | 1.939 | Low | Low | High | 764 | 838 | 0.54812 | 538.7303
OAKHURST 1102CB | OAKHURST 1102 | YOSEMITE | 2.1514 | 10 | 95.52% | 0 | 10 | 44.96% | 59.79% | 0 | 0.050548 | 14.9507 | 2.5632 | 1.9371 | Medium | Medium | Medium | 765 | 769 | 0.75573 | 536.7913
CAMP EVERS 210612760 | CAMP EVERS 2106 | CENTRAL COAST | 26.714 | 47.9231 | 63.13% | 29 | 6 | 100% | 100% | 0 | 0.75098 | 1 | 2.5548 | 1.9186 | High | High | Medium | 766 | 772 | 0.75098 | 534.8541
SONOMA 1104414 | SONOMA 1104 | SONOMA | 0.58433 | 88.0945 | 100% | 0 | 0 | 3.279% | 0% | 0 | 0.018641 | 35.3263 | 2.89 | 1.9031 | Low | Low | Medium | 767 | 802 | 0.65851 | 532.9355
PINECREST 0401CB | PINECREST 0401 | YOSEMITE | 0.021247 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 14.9507 | 0.97713 | 1.9024 | High | High | Low | 768 | 612 | 1.9469 | 531.0324
PINECREST 0401 | PINECREST 0401 | YOSEMITE | 0.0016115 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 14.9507 | 0.97537 | 1.899 | High | High | Low | 769 | 612 | 1.9469 | 529.1301
STAFFORD 1102361952 | STAFFORD 1102 | NORTH BAY | 1.3655 | 84.7322 | 98.54% | 0 | 1 | 100% | 0% | 0 | 0.04705 | 14.9507 | 2.6948 | 1.8956 | Medium | Medium | Medium | 770 | 781 | 0.70344 | 527.2311
SALMON CREEK 1101196 | SALMON CREEK 1101 | SONOMA | 5.0547 | 72.9126 | 4.053% | 3 | 0 | 69.63% | 0% | 0 | 0.020086 | 35.3263 | 2.652 | 1.8817 | Low | Low | Medium | 771 | 780 | 0.70955 | 525.3354
HIGGINS 11032194 | HIGGINS 1103 | SIERRA | 1.6953 | 10 | 78.66% | 3 | 1 | 63.02% | 0% | 0 | 0.017732 | 35.3263 | 3.0035 | 1.8815 | Low | Low | Medium | 772 | 813 | 0.62642 | 523.4537
PETALUMA C 1109373772 | PETALUMA C 1109 | SONOMA | 0.017822 | 70 | 100% | 0 | 0 | 100% | 0% | 0 | 0.042368 | 14.9507 | 2.9557 | 1.8723 | Medium | Medium | Medium | 773 | 811 | 0.63344 | 521.5723
GARBERVILLE 11022124 | GARBERVILLE 1102 | HUMBOLDT | 3.1243 | 97.624 | 0% | 0 | 1 | 100% | 0% | 0 | 0.023355 | 47.6367 | 1.6787 | 1.8676 | Medium | Medium | Low | 774 | 696 | 1.1125 | 519.7
VACA DIXON 11059792 | VACA DIXON 1105 | SACRAMENTO | 2.2981 | 58.3899 | 100% | 0 | 0 | 7.932% | 0% | 0 | 0.015982 | 47.6367 | 2.4313 | 1.8511 | Low | Low | Medium | 775 | 767 | 0.76135 | 517.8324
PENRYN 110550548 | PENRYN 1105 | SIERRA | 4.6613 | 28.5134 | 63.43% | 0 | 1 | 38.43% | 0% | 0 | 0.013391 | 65.3912 | 2.1096 | 1.8472 | Low | Low | Low | 776 | 739 | 0.87563 | 515.9813
STAFFORD 11021943 | STAFFORD 1102 | NORTH BAY | 1.2184 | 10 | 29.26% | 2 | 0 | 100% | 0% | 0 | 0.016531 | 35.3263 | 3.1358 | 1.8312 | Low | Low | High | 777 | 830 | 0.58398 | 514.1341
GREEN VALLEY 210111054 | GREEN VALLEY 2101 | CENTRAL COAST | 24.5092 | 42.4361 | 63.08% | 38 | 3 | 95.34% | 97.52% | 1 | 0.59075 | 1 | 3.087 | 1.8236 | High | High | High | 778 | 824 | 0.59075 | 512.3029
OLETA 110163500 | OLETA 1101 | STOCKTON | 4.0006 | 22.1026 | 38.92% | 0 | 1 | 53.39% | 0% | 0 | 0.012178 | 65.3912 | 2.271 | 1.8085 | Low | Low | Medium | 779 | 756 | 0.79634 | 510.4792
STAFFORD 1102784704 | STAFFORD 1102 | NORTH BAY | 0.02728 | 80 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045233 | 14.9507 | 2.6732 | 1.8078 | Medium | Medium | Medium | 780 | 796 | 0.67626 | 508.6707
PACIFICA 11026783 | PACIFICA 1102 | PENINSULA | 1.5821 | 10 | 0% | 0 | 2 | 24.72% | 24.2% | 0 | 0.010579 | 47.6367 | 3.5634 | 1.7958 | Low | Low | High | 781 | 856 | 0.50395 | 506.863
COTATI 1102681 | COTATI 1102 | SONOMA | 3.8076 | 32.2436 | 43.14% | 1 | 3 | 100% | 0% | 0 | 0.025685 | 26.5534 | 2.6252 | 1.7904 | Medium | Medium | Medium | 782 | 793 | 0.68203 | 505.0672
RINCON 1102644 | RINCON 1102 | SONOMA | 0.010111 | 60 | 100% | 0 | 1 | 0.1009% | 0% | 0 | 0.015268 | 35.3263 | 3.2635 | 1.7602 | Low | Low | High | 783 | 843 | 0.53935 | 503.2768
SANTA YNEZ 1101CB | SANTA YNEZ 1101 | LOS PADRES | 0.10675 | 60 | 100% | 0 | 1 | 0.6877% | 0% | 0 | 0.015356 | 35.3263 | 3.2382 | 1.7567 | Low | Low | High | 784 | 841 | 0.54248 | 501.5166
PASO ROBLES 1104R56 | PASO ROBLES 1104 | LOS PADRES | 11.0427 | 56.2868 | 57.45% | 0 | 4 | 89.88% | 0% | 0 | 0.035115 | 26.5534 | 1.8717 | 1.7452 | Medium | Medium | Low | 785 | 731 | 0.93242 | 499.7599
FRUITLAND 11426064 | FRUITLAND 1142 | HUMBOLDT | 6.4216 | 80.9642 | 100% | 2 | 4 | 77.51% | 0% | 0 | 0.076552 | 47.6367 | 0.47828 | 1.7441 | High | High | Low | 786 | 495 | 3.6467 | 498.0147
PENRYN 11051342 | PENRYN 1105 | SIERRA | 20.5672 | 12.393 | 56.11% | 3 | 12 | 53.03% | 0% | 0 | 0.025263 | 35.3263 | 1.9483 | 1.7388 | Medium | Medium | Low | 787 | 736 | 0.89244 | 496.2706
CLARKSVILLE 21096502 | CLARKSVILLE 2109 | SIERRA | 2.6781 | 10 | 70.1% | 1 | 1 | 48.48% | 45.39% | 0 | 0.03731 | 14.9507 | 3.0964 | 1.7272 | Medium | Medium | High | 788 | 836 | 0.55781 | 494.5318
WOODACRE 110191900 | WOODACRE 1101 | NORTH BAY | 7.6804 | 74.1444 | 47.27% | 4 | 8 | 55.53% | 8.222% | 1 | 0.029825 | 26.5534 | 2.176 | 1.7233 | Medium | Medium | Low | 789 | 759 | 0.79194 | 492.8046
WISE 1102697216 | WISE 1102 | SIERRA | 13.1816 | 10.264 | 71.09% | 2 | 0 | 100% | 0% | 0 | 0.026461 | 26.5534 | 2.4483 | 1.7203 | Medium | Medium | Medium | 790 | 783 | 0.70264 | 491.0814
PETALUMA C 1109664732 | PETALUMA C 1109 | SONOMA | 0.8938 | 76.1937 | 84.67% | 0 | 0 | 100% | 0% | 0 | 0.039085 | 14.9507 | 2.9436 | 1.7201 | Medium | Medium | Medium | 791 | 829 | 0.58434 | 489.3611
TEMPLETON 2113A60 | TEMPLETON 2113 | LOS PADRES | 7.4093 | 57.7033 | 62.45% | 1 | 2 | 82.52% | 0.05121% | 0 | 0.025802 | 26.5534 | 2.47 | 1.6923 | Medium | Medium | Medium | 792 | 791 | 0.68512 | 487.641
HIGHLANDS 1102556 | HIGHLANDS 1102 | HUMBOLDT | 0.14444 | 10 | 100% | 0 | 0 | 1.909% | 0% | 0 | 0.010862 | 47.6367 | 3.2484 | 1.6809 | Low | Low | High | 793 | 852 | 0.51744 | 485.9488
JESSUP 110296554 | JESSUP 1102 | NORTH VALLEY | 6.2214 | 43.1199 | 99.72% | 1 | 1 | 41.3% | 0% | 0 | 0.030545 | 26.5534 | 2.0694 | 1.6784 | Medium | Medium | Low | 794 | 753 | 0.81106 | 484.2679
RESEARCH 210263274 | RESEARCH 2102 | DIABLO | 0.57886 | 29.7225 | 25.19% | 0 | 1 | 5.113% | 100% | 0 | 0.035184 | 14.9507 | 3.1898 | 1.6779 | Medium | Medium | High | 795 | 849 | 0.52603 | 482.5895
BUELLTON 1102CB | BUELLTON 1102 | LOS PADRES | 4.428 | 55.4455 | 60.97% | 0 | 2 | 34.48% | 0% | 0 | 0.02009 | 35.3263 | 2.346 | 1.6649 | Low | Low | Medium | 796 | 779 | 0.7097 | 480.9116
HARTLEY 110158095 | HARTLEY 1101 | HUMBOLDT | 0.15659 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 19.9979 | 2.9173 | 1.6633 | Medium | Medium | Medium | 797 | 832 | 0.57017 | 479.2467
SONOMA 11045661 | SONOMA 1104 | SONOMA | 2.0903 | 69.2654 | 50.64% | 0 | 1 | 41.25% | 0% | 0 | 0.016332 | 26.5534 | 3.8269 | 1.6596 | Low | Low | High | 798 | 879 | 0.43366 | 477.5833
STAFFORD 11011082 | STAFFORD 1101 | NORTH BAY | 2.5227 | 43.9762 | 98.79% | 0 | 0 | 81.83% | 0% | 0 | 0.029652 | 19.9979 | 2.7906 | 1.6547 | Medium | Medium | Medium | 799 | 823 | 0.59297 | 475.9238
HIGGINS 110432747 | HIGGINS 1104 | SIERRA | 1.0824 | 10 | 100% | 1 | 0 | 61.76% | 0% | 0 | 0.019868 | 26.5534 | 3.124 | 1.6482 | Low | Low | High | 800 | 848 | 0.52758 | 474.269
SAN JUSTO 11014339 | SAN JUSTO 1101 | CENTRAL COAST | 8.8141 | 41.5112 | 42.23% | 1 | 1 | 80.23% | 0% | 0 | 0.021456 | 35.3263 | 2.1555 | 1.6338 | Low | Low | Low | 801 | 768 | 0.75797 | 472.6208
MARTELL 11016074 | MARTELL 1101 | STOCKTON | 3.6867 | 10 | 89.99% | 1 | 1 | 100% | 0% | 0 | 0.030968 | 19.9979 | 2.6262 | 1.6264 | Medium | Medium | Medium | 802 | 816 | 0.6193 | 470.9871
CURTIS 1702 | CURTIS 1702 | YOSEMITE | 0.020195 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 14.9507 | 3.8121 | 1.625 | Medium | Medium | High | 803 | 883 | 0.42627 | 469.3607
FULTON 11024522 | FULTON 1102 | SONOMA | 7.7633 | 52.5177 | 82.8% | 0 | 6 | 63.13% | 6.863% | 0 | 0.037536 | 14.9507 | 2.8909 | 1.6223 | Medium | Medium | Medium | 804 | 835 | 0.56119 | 467.7357
DEL MONTE 21049500 | DEL MONTE 2104 | CENTRAL COAST | 6.5395 | 26.3217 | 40.33% | 0 | 7 | 96.32% | 0% | 0 | 0.03234 | 19.9979 | 2.4996 | 1.6166 | Medium | Medium | Medium | 805 | 808 | 0.64673 | 466.1134
ATASCADERO 1103A18 | ATASCADERO 1103 | LOS PADRES | 8.0258 | 28.4878 | 70.03% | 3 | 2 | 44.28% | 0% | 0 | 0.023538 | 35.3263 | 1.9037 | 1.583 | Medium | Medium | Low | 806 | 748 | 0.8315 | 464.4968
BIG MEADOWS 2101439 | BIG MEADOWS 2101 | NORTH VALLEY | 0.034644 | 85 | 100% | 0 | 0 | 3.714% | 0% | 0 | 0.018336 | 26.5534 | 3.2474 | 1.5811 | Low | Low | High | 807 | 862 | 0.48688 | 462.9138
BEN LOMOND 0401CB | BEN LOMOND 0401 | CENTRAL COAST | 7.8222 | 35.8204 | 30.8% | 32 | 5 | 100% | 100% | 0 | 0.3629 | 1 | 4.3533 | 1.5799 | High | High | High | 808 | 916 | 0.3629 | 461.3328
CORRAL 110313474 | CORRAL 1103 | STOCKTON | 3.1745 | 31.5086 | 69.33% | 0 | 0 | 44.02% | 0% | 0 | 0.019295 | 19.9979 | 3.99 | 1.5396 | Low | Low | High | 809 | 900 | 0.38586 | 459.7529
COARSEGOLD 210410335 | COARSEGOLD 2104 | YOSEMITE | 5.8238 | 24.9128 | 98.65% | 0 | 10 | 100% | 0% | 0 | 0.043347 | 14.9507 | 2.3565 | 1.5272 | Medium | Medium | Medium | 810 | 807 | 0.64806 | 458.2133
PENRYN 110551676 | PENRYN 1105 | SIERRA | 8.707 | 10 | 49.11% | 4 | 2 | 74.33% | 0% | 0 | 0.018392 | 35.3263 | 2.3475 | 1.5252 | Low | Low | Medium | 811 | 805 | 0.64971 | 456.6862
PUTAH CREEK 110546162 | PUTAH CREEK 1105 | SACRAMENTO | 0.70535 | 84.6256 | 100% | 0 | 0 | 10.52% | 0% | 0 | 0.019556 | 35.3263 | 2.1866 | 1.5106 | Low | Low | Low | 812 | 785 | 0.69085 | 455.161
NORTH DUBLIN 21039473 | NORTH DUBLIN 2103 | MISSION | 2.5582 | 55.4552 | 10.6% | 0 | 1 | 86.9% | 2.14% | 0 | 0.019896 | 19.9979 | 3.7737 | 1.5015 | Low | Low | High | 813 | 893 | 0.39788 | 453.6503
SALMON CREEK 1101 | SALMON CREEK 1101 | SONOMA | 0.026066 | 45.8588 | 0% | 0 | 0 | 100% | 51.23% | 0 | 0.036485 | 14.9507 | 2.7335 | 1.4911 | Medium | Medium | Medium | 814 | 839 | 0.54548 | 452.1489
HALSEY 1101 | HALSEY 1101 | SIERRA | 0.058617 | 10 | 52.88% | 0 | 0 | 100% | 0% | 0 | 0.019506 | 35.3263 | 2.1628 | 1.4903 | Low | Low | Low | 815 | 790 | 0.68906 | 450.6578
CLEAR LAKE 1102904 | CLEAR LAKE 1102 | HUMBOLDT | 3.3866 | 10 | 44.47% | 0 | 0 | 94.14% | 0% | 0 | 0.01961 | 26.5534 | 2.8334 | 1.4754 | Low | Low | Medium | 816 | 851 | 0.52071 | 449.1675
BIG BEND 11011704 | BIG BEND 1101 | NORTH VALLEY | 2.999 | 64.818 | 100% | 0 | 0 | 100% | 0% | 0 | 0.040953 | 19.9979 | 1.7926 | 1.4681 | Medium | Medium | Low | 817 | 751 | 0.81898 | 447.6921
SAN RAFAEL 11071166 | SAN RAFAEL 1107 | NORTH BAY | 8.1619 | 27.5709 | 35.32% | 8 | 36 | 90.61% | 87.37% | 0 | 0.30659 | 1 | 4.7682 | 1.4619 | High | High | High | 818 | 958 | 0.30659 | 446.224
SONOMA 1107294 | SONOMA 1107 | SONOMA | 0.1154 | 80 | 100% | 0 | 0 | 1.248% | 0% | 0 | 0.017305 | 35.3263 | 2.3851 | 1.458 | Low | Low | Medium | 819 | 817 | 0.61132 | 444.7621
OREGON TRAIL 1102CB | OREGON TRAIL 1102 | NORTH VALLEY | 9.1345 | 24.6852 | 60.79% | 2 | 5 | 97.5% | 0% | 0 | 0.028979 | 19.9979 | 2.4938 | 1.4452 | Medium | Medium | Medium | 820 | 831 | 0.57952 | 443.3041
OLEMA 11011686 | OLEMA 1101 | NORTH BAY | 0.41347 | 93.229 | 0% | 4 | 1 | 8.166% | 0% | 0 | 0.0096532 | 65.3912 | 2.2884 | 1.4445 | Low | Low | Medium | 821 | 812 | 0.63124 | 441.8589
SHINGLE SPRINGS 21107742 | SHINGLE SPRINGS 2110 | SIERRA | 45.6192 | 28.4995 | 92.18% | 17 | 14 | 99.89% | 99.12% | 1 | 0.53387 | 1 | 2.6864 | 1.4342 | High | High | Medium | 822 | 844 | 0.53387 | 440.4144
PUEBLO 2102698 | PUEBLO 2102 | NORTH BAY | 0.45229 | 80 | 34.45% | 0 | 0 | 2.749% | 0% | 0 | 0.0103 | 47.6367 | 2.9171 | 1.4313 | Low | Low | Medium | 823 | 861 | 0.49067 | 438.9802
PENRYN 110351658 | PENRYN 1103 | SIERRA | 7.9841 | 27.4219 | 66.1% | 1 | 2 | 91.67% | 0% | 0 | 0.027021 | 19.9979 | 2.6417 | 1.4274 | Medium | Medium | Medium | 824 | 842 | 0.54036 | 437.5488
PASO ROBLES 1103N58 | PASO ROBLES 1103 | LOS PADRES | 4.5123 | 48.6182 | 39.94% | 0 | 1 | 60.11% | 0% | 0 | 0.026481 | 26.5534 | 2.029 | 1.4267 | Medium | Medium | Low | 825 | 782 | 0.70315 | 436.1214
JAMESON 11028842 | JAMESON 1102 | SACRAMENTO | 0.46739 | 47.8727 | 32.07% | 0 | 0 | 8.162% | 0% | 0 | 0.0097873 | 47.6367 | 3.045 | 1.4197 | Low | Low | Medium | 826 | 866 | 0.46623 | 434.6947
BOLINAS 110146152 | BOLINAS 1101 | NORTH BAY | 0.43174 | 69.1568 | 0% | 0 | 0 | 4.254% | 0% | 0 | 0.0073288 | 47.6367 | 4.0187 | 1.403 | Low | Low | High | 827 | 920 | 0.34912 | 433.275
ANITA 1106CB | ANITA 1106 | NORTH VALLEY | 0.115 | 85 | 100% | 0 | 0 | 0.3281% | 0% | 0 | 0.017735 | 47.6367 | 1.6583 | 1.401 | Low | Low | Low | 828 | 745 | 0.84484 | 431.872
SAN RAFAEL 1108516 | SAN RAFAEL 1108 | NORTH BAY | 10.7797 | 42.2809 | 10.51% | 16 | 17 | 98.34% | 99.7% | 0 | 0.30979 | 1 | 4.4882 | 1.3904 | High | High | High | 829 | 956 | 0.30979 | 430.471
DESCHUTES 11043719 | DESCHUTES 1104 | NORTH VALLEY | 11.6781 | 40.3272 | 100% | 0 | 2 | 67.24% | 0% | 0 | 0.026406 | 19.9979 | 2.604 | 1.3751 | Medium | Medium | Medium | 830 | 847 | 0.52806 | 429.0806
GONZALES 110422418 | GONZALES 1104 | CENTRAL COAST | 0.8424 | 88.5066 | 100% | 0 | 0 | 6.858% | 0% | 0 | 0.019362 | 47.6367 | 1.4832 | 1.368 | Low | Low | Low | 831 | 733 | 0.92235 | 427.7055
BRUNSWICK 1104CB | BRUNSWICK 1104 | SIERRA | 1.9366 | 10 | 53.96% | 0 | 0 | 63.09% | 0% | 0 | 0.013676 | 35.3263 | 2.8083 | 1.3567 | Low | Low | Medium | 832 | 863 | 0.48311 | 426.3375
BRUNSWICK 11064639 | BRUNSWICK 1106 | SIERRA | 3.2486 | 31.5408 | 99.46% | 0 | 1 | 100% | 1.568% | 1 | 0.034254 | 14.9507 | 2.6487 | 1.3565 | Medium | Medium | Medium | 833 | 853 | 0.51212 | 424.9807
JAMESON 110265516 | JAMESON 1102 | SACRAMENTO | 7.9053 | 31.2245 | 60.83% | 1 | 6 | 69.63% | 0% | 0 | 0.023245 | 19.9979 | 2.861 | 1.3299 | Medium | Medium | Medium | 834 | 868 | 0.46484 | 423.6243
AUBERRY 110149122 | AUBERRY 1101 | FRESNO | 3.8865 | 26.9324 | 92.34% | 0 | 3 | 100% | 0% | 0 | 0.036287 | 14.9507 | 2.4472 | 1.3276 | Medium | Medium | Medium | 835 | 840 | 0.54251 | 422.2943
CAMP EVERS 210311046 | CAMP EVERS 2103 | CENTRAL COAST | 16.2531 | 44.8404 | 64.25% | 23 | 4 | 100% | 100% | 0 | 0.47552 | 1 | 2.7899 | 1.3267 | High | High | Medium | 836 | 864 | 0.47552 | 420.9667
VIEJO 2202CB | VIEJO 2202 | CENTRAL COAST | 2.1755 | 10 | 21.89% | 2 | 2 | 100% | 0% | 0 | 0.018504 | 19.9979 | 3.5811 | 1.3252 | Low | Low | High | 837 | 911 | 0.37005 | 419.6401
MADISON 210113372 | MADISON 2101 | SACRAMENTO | 3.7782 | 89.8591 | 100% | 0 | 0 | 99.16% | 0% | 0 | 0.047853 | 26.5534 | 1.0386 | 1.3197 | Medium | Medium | Low | 838 | 671 | 1.2706 | 418.3149
MOLINO 1102344 | MOLINO 1102 | SONOMA | 1.1141 | 30.1016 | 80.53% | 0 | 2 | 18.52% | 0% | 0 | 0.013045 | 35.3263 | 2.8566 | 1.3164 | Low | Low | Medium | 839 | 869 | 0.46084 | 416.9952
ATASCADERO 1101 | ATASCADERO 1101 | LOS PADRES | 0.011512 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 35.3263 | 2.9013 | 1.3012 | Low | Low | Medium | 840 | 872 | 0.44848 | 415.6788
LOS GATOS 1106LB44 | LOS GATOS 1106 | DE ANZA | 19.5005 | 14.2956 | 68.84% | 20 | 1 | 100% | 100% | 0 | 0.44075 | 1 | 2.9349 | 1.2936 | High | High | Medium | 841 | 876 | 0.44075 | 414.3776
ATASCADERO 1103CB | ATASCADERO 1103 | LOS PADRES | 7.2499 | 46.2369 | 39.81% | 0 | 1 | 74.99% | 13.24% | 0 | 0.025143 | 19.9979 | 2.5685 | 1.2915 | Medium | Medium | Medium | 842 | 858 | 0.50281 | 413.084
ELECTRA 11011238 | ELECTRA 1101 | STOCKTON | 4.7136 | 30.1636 | 44.85% | 1 | 1 | 66.69% | 0% | 0 | 0.015593 | 26.5534 | 3.1098 | 1.2876 | Low | Low | High | 843 | 888 | 0.41404 | 411.7925
ROB ROY 21055090 | ROB ROY 2105 | CENTRAL COAST | 21.1859 | 44.752 | 78.23% | 40 | 3 | 100% | 97.19% | 1 | 0.37924 | 1 | 3.3344 | 1.2646 | High | High | High | 844 | 906 | 0.37924 | 410.5049
VACAVILLE 110941782 | VACAVILLE 1109 | SACRAMENTO | 0.50066 | 79.3838 | 12.32% | 0 | 0 | 29.37% | 0% | 0 | 0.011149 | 35.3263 | 3.1982 | 1.2596 | Low | Low | High | 845 | 896 | 0.39386 | 409.2404
COTTONWOOD 110335470 | COTTONWOOD 1103 | NORTH VALLEY | 18.2496 | 46.5174 | 67.33% | 0 | 6 | 73.33% | 0% | 0 | 0.03595 | 19.9979 | 1.7492 | 1.2576 | Medium | Medium | Low | 846 | 778 | 0.71893 | 407.9807
GANSNER 110137550 | GANSNER 1101 | NORTH VALLEY | 0.5773 | 95.7309 | 100% | 0 | 0 | 12.36% | 0% | 0 | 0.021451 | 19.9979 | 2.9158 | 1.2508 | Low | Low | Medium | 847 | 880 | 0.42898 | 406.7232
GEYSERVILLE 1102274 | GEYSERVILLE 1102 | SONOMA | 4.0814 | 46.8618 | 69.12% | 1 | 0 | 22.13% | 0% | 0 | 0.013409 | 35.3263 | 2.6258 | 1.2438 | Low | Low | Medium | 848 | 865 | 0.47371 | 405.4723
CORRAL 110275622 | CORRAL 1102 | STOCKTON | 0.45257 | 14.2481 | 100% | 0 | 0 | 7.908% | 0% | 0 | 0.011863 | 35.3263 | 2.9665 | 1.2432 | Low | Low | Medium | 849 | 887 | 0.41909 | 404.2285
PEORIA 1705CB | PEORIA 1705 | YOSEMITE | 7.2378 | 70.7531 | 12.14% | 0 | 3 | 100% | 0% | 0 | 0.022424 | 26.5534 | 2.0773 | 1.2369 | Medium | Medium | Low | 850 | 822 | 0.59543 | 402.9853
SANTA ROSA A 1108626 | SANTA ROSA A 1108 | SONOMA | 0.13621 | 75 | 0% | 0 | 0 | 3.381% | 0% | 0 | 0.0075596 | 47.6367 | 3.4302 | 1.2353 | Low | Low | High | 851 | 917 | 0.36011 | 401.7484
COTATI 110387402 | COTATI 1103 | SONOMA | 11.4171 | 74.8765 | 25.02% | 0 | 0 | 100% | 0% | 0 | 0.031179 | 19.9979 | 1.9793 | 1.2341 | Medium | Medium | Low | 852 | 815 | 0.62351 | 400.5131
CLARKSVILLE 210551478 | CLARKSVILLE 2105 | SIERRA | 0.050363 | 10 | 0% | 0 | 0 | 89.86% | 0% | 0 | 0.011483 | 35.3263 | 3.0401 | 1.2332 | Low | Low | Medium | 853 | 890 | 0.40565 | 399.279
GEYSERVILLE 1102CB | GEYSERVILLE 1102 | SONOMA | 2.3641 | 61.3374 | 59.74% | 1 | 1 | 32.38% | 57.77% | 0 | 0.03873 | 19.9979 | 1.5774 | 1.2218 | Medium | Medium | Low | 854 | 762 | 0.77452 | 398.0458
MIDDLETOWN 1102414 | MIDDLETOWN 1102 | HUMBOLDT | 5.0571 | 54.0321 | 100% | 0 | 3 | 42.26% | 0% | 0 | 0.026354 | 14.9507 | 3.0843 | 1.2153 | Medium | Medium | High | 855 | 895 | 0.39402 | 396.8241
WOODSIDE 110147872 | WOODSIDE 1101 | PENINSULA | 4.1743 | 60.8207 | 75.33% | 12 | 4 | 100% | 100% | 0 | 0.39089 | 1 | 3.0893 | 1.2076 | High | High | High | 856 | 898 | 0.39089 | 395.6088
RED BLUFF 11011334 | RED BLUFF 1101 | NORTH VALLEY | 1.7587 | 68.6115 | 100% | 0 | 0 | 11.05% | 0% | 0 | 0.017653 | 35.3263 | 1.9337 | 1.2059 | Low | Low | Low | 857 | 814 | 0.62362 | 394.4012
COTATI 1104CB | COTATI 1104 | SONOMA | 2.3176 | 10.9581 | 56.63% | 1 | 1 | 30.19% | 0% | 0 | 0.010506 | 35.3263 | 3.2386 | 1.2019 | Low | Low | High | 858 | 910 | 0.37113 | 393.1953
PEABODY 2108CB | PEABODY 2108 | SACRAMENTO | 0.80945 | 40.6035 | 58.6% | 0 | 0 | 21.91% | 0% | 0 | 0.01162 | 35.3263 | 2.9033 | 1.1917 | Low | Low | Medium | 859 | 889 | 0.41049 | 391.9934
MARIPOSA 2102 | MARIPOSA 2102 | YOSEMITE | 0.0020154 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 19.9979 | 2.0892 | 1.1912 | Medium | Medium | Low | 860 | 832 | 0.57017 | 390.8016
JESSUP 11021314 | JESSUP 1102 | NORTH VALLEY | 5.6244 | 41.4572 | 97.17% | 0 | 1 | 39.97% | 0% | 0 | 0.022232 | 26.5534 | 2.005 | 1.1836 | Medium | Medium | Low | 861 | 825 | 0.59034 | 389.6104
ROSSMOOR 1106L522R | ROSSMOOR 1106 | DIABLO | 1.0378 | 10 | 19.41% | 3 | 11 | 24.6% | 0% | 0 | 0.011991 | 26.5534 | 3.6777 | 1.171 | Low | Low | High | 862 | 949 | 0.31841 | 388.4268
MARIPOSA 21019400 | MARIPOSA 2101 | YOSEMITE | 62.7736 | 22.0188 | 81.32% | 9 | 129 | 100% | 40.79% | 1 | 0.72296 | 1 | 1.619 | 1.1705 | High | High | Low | 863 | 777 | 0.72296 | 387.2558
WHEATLAND 110591170 | WHEATLAND 1105 | SIERRA | 9.9882 | 49.4424 | 100% | 0 | 0 | 18.55% | 0% | 0 | 0.019051 | 35.3263 | 1.7362 | 1.1684 | Low | Low | Low | 864 | 797 | 0.67299 | 386.0853
LINCOLN 110451756 | LINCOLN 1104 | SIERRA | 15.5512 | 62.1844 | 61.25% | 0 | 6 | 27.35% | 0% | 0 | 0.031506 | 26.5534 | 1.3793 | 1.1539 | Medium | Medium | Low | 865 | 746 | 0.8366 | 384.9168
WYANDOTTE 110641650 | WYANDOTTE 1106 | NORTH VALLEY | 1.9508 | 59.4004 | 100% | 0 | 0 | 12.07% | 0% | 0 | 0.01911 | 26.5534 | 2.2667 | 1.1502 | Low | Low | Medium | 866 | 855 | 0.50744 | 383.7629
FOOTHILL 1101549904 | FOOTHILL 1101 | LOS PADRES | 7.1079 | 49.5665 | 45.77% | 1 | 3 | 40.61% | 0% | 0 | 0.021381 | 14.9507 | 3.5842 | 1.1457 | Low | Low | High | 867 | 947 | 0.31966 | 382.6127
ALTO 1124430 | ALTO 1124 | NORTH BAY | 7.2931 | 30.5125 | 12.77% | 14 | 16 | 100% | 100% | 0 | 0.26455 | 1 | 4.3274 | 1.1448 | High | High | High | 868 | 984 | 0.26455 | 381.4669
CRESCENT MILLS 21012230 | CRESCENT MILLS 2101 | NORTH VALLEY | 1.0766 | 89.5687 | 97.05% | 0 | 1 | 9.699% | 0% | 0 | 0.022777 | 26.5534 | 1.8892 | 1.1426 | Medium | Medium | Low | 869 | 820 | 0.60481 | 380.3221
BIG BASIN 110212992 | BIG BASIN 1102 | CENTRAL COAST | 14.2865 | 29.6471 | 74.67% | 30 | 1 | 100% | 100% | 1 | 0.44527 | 1 | 2.5494 | 1.1352 | High | High | Medium | 870 | 873 | 0.44527 | 379.1795
UPPER LAKE 11016663 | UPPER LAKE 1101 | HUMBOLDT | 2.3336 | 74.5453 | 100% | 0 | 0 | 100% | 0% | 0 | 0.043648 | 19.9979 | 1.2971 | 1.1322 | Medium | Medium | Low | 871 | 740 | 0.87287 | 378.0444
WYANDOTTE 110932586 | WYANDOTTE 1109 | NORTH VALLEY | 1.4371 | 18.342 | 79.5% | 0 | 0 | 94.84% | 0% | 0 | 0.024309 | 11.2183 | 4.1406 | 1.1292 | Medium | Medium | High | 872 | 974 | 0.27271 | 376.9122
JARVIS 1108MR576 | JARVIS 1108 | MISSION | 1.3706 | 10 | 32.22% | 0 | 0 | 22.29% | 0% | 0 | 0.0076408 | 35.3263 | 4.1701 | 1.1256 | Low | Low | High | 873 | 977 | 0.26992 | 375.783
CLAYTON 22159765 | CLAYTON 2215 | DIABLO | 0.13991 | 10 | 100% | 0 | 0 | 14.93% | 0% | 0 | 0.012358 | 26.5534 | 3.3958 | 1.1143 | Low | Low | High | 874 | 936 | 0.32814 | 374.6574
SAN LUIS OBISPO 1108CB | SAN LUIS OBISPO 1108 | LOS PADRES | 0.74619 | 53.8272 | 22.96% | 0 | 1 | 8.668% | 0% | 0 | 0.012642 | 26.5534 | 3.3193 | 1.1142 | Low | Low | High | 875 | 931 | 0.33568 | 373.5431
STAFFORD 1102CB | STAFFORD 1102 | NORTH BAY | 0.24035 | 10 | 0% | 0 | 0 | 45.06% | 0% | 0 | 0.0084029 | 47.6367 | 2.7618 | 1.1055 | Low | Low | Medium | 876 | 892 | 0.40029 | 372.4289
JARVIS 1110CB | JARVIS 1110 | MISSION | 0.094443 | 65 | 0% | 0 | 0 | 1.965% | 0% | 0 | 0.0069643 | 35.3263 | 4.4419 | 1.0928 | Low | Low | High | 877 | 1006 | 0.24602 | 371.3234
CAMP EVERS 210510728 | CAMP EVERS 2105 | CENTRAL COAST | 10.465 | 15.413 | 38.24% | 13 | 4 | 100% | 100% | 0 | 0.2598 | 1 | 4.1867 | 1.0877 | High | High | High | 878 | 988 | 0.2598 | 370.2306
WEST POINT 11024788 | WEST POINT 1102 | STOCKTON | 70.3316 | 50.1461 | 97.21% | 9 | 19 | 100% | 60.3% | 0 | 0.45673 | 1 | 2.3714 | 1.0831 | High | High | Medium | 879 | 871 | 0.45673 | 369.1429
HOOPA 1101561116 | HOOPA 1101 | HUMBOLDT | 0.012979 | 85 | 0% | 0 | 0 | 100% | 0% | 0 | 0.021028 | 47.6367 | 1.0757 | 1.0775 | Low | Low | Low | 880 | 720 | 1.0017 | 368.0598
PUEBLO 21021326 | PUEBLO 2102 | NORTH BAY | 0.81465 | 66.7263 | 75.65% | 0 | 0 | 6.742% | 0% | 0 | 0.013708 | 26.5534 | 2.9185 | 1.0623 | Low | Low | Medium | 881 | 915 | 0.364 | 366.9823
CALISTOGA 1101734 | CALISTOGA 1101 | NORTH BAY | 11.7939 | 55.3179 | 62.25% | 13 | 12 | 73.13% | 81.49% | 0 | 0.39061 | 1 | 2.7018 | 1.0554 | High | High | Medium | 882 | 899 | 0.39061 | 365.92
INDIAN FLAT 11044440 | INDIAN FLAT 1104 | YOSEMITE | 0.21912 | 58.2464 | 100% | 0 | 0 | 100% | 0% | 0 | 0.039224 | 14.9507 | 1.7987 | 1.0548 | Medium | Medium | Low | 883 | 828 | 0.58642 | 364.8646
JESSUP 110141356 | JESSUP 1101 | NORTH VALLEY | 32.7394 | 40.1195 | 100% | 1 | 5 | 100% | 0% | 0 | 0.044331 | 14.9507 | 1.5857 | 1.051 | Medium | Medium | Low | 884 | 801 | 0.66278 | 363.8098
SAN RAFAEL 1108322 | SAN RAFAEL 1108 | NORTH BAY | 7.1088 | 25.427 | 14.01% | 10 | 9 | 95.89% | 89.81% | 0 | 0.21074 | 1 | 4.9853 | 1.0506 | High | High | High | 885 | 1041 | 0.21074 | 362.7588
ANDERSON 11012051 | ANDERSON 1101 | NORTH VALLEY | 4.6467 | 13.4745 | 100% | 0 | 2 | 87.22% | 0% | 0 | 0.030553 | 14.9507 | 2.2964 | 1.0489 | Medium | Medium | Medium | 886 | 870 | 0.45678 | 361.7082
WISE 11022234 | WISE 1102 | SIERRA | 15.1055 | 10 | 57.56% | 1 | 4 | 100% | 0% | 0 | 0.025382 | 19.9979 | 2.055 | 1.0431 | Medium | Medium | Low | 887 | 854 | 0.5076 | 360.6593
LAURELES 11116617 | LAURELES 1111 | CENTRAL COAST | 1.819 | 41.7117 | 100% | 1 | 0 | 100% | 0% | 0 | 0.040513 | 14.9507 | 1.7012 | 1.0304 | Medium | Medium | Low | 888 | 819 | 0.6057 | 359.6161
OAKHURST 110310140 | OAKHURST 1103 | YOSEMITE | 16.859 | 26.9049 | 99.84% | 3 | 44 | 100% | 99.31% | 0 | 0.52553 | 1 | 1.9527 | 1.0262 | High | High | Low | 889 | 850 | 0.52553 | 358.5857
MIRABEL 1101228 | MIRABEL 1101 | SONOMA | 2.2414 | 32.2817 | 68.07% | 3 | 1 | 22.76% | 0% | 0 | 0.012705 | 26.5534 | 3.0408 | 1.0258 | Low | Low | Medium | 890 | 928 | 0.33736 | 357.5595
CAMP EVERS 21065302 | CAMP EVERS 2106 | CENTRAL COAST | 5.9826 | 48.1403 | 77.43% | 11 | 0 | 100% | 95.97% | 0 | 0.25415 | 1 | 4.0058 | 1.0181 | High | High | High | 891 | 997 | 0.25415 | 356.5337
ALTO 11251226 | ALTO 1125 | NORTH BAY | 7.7199 | 13.4122 | 30.57% | 9 | 29 | 98.37% | 100% | 0 | 0.23095 | 1 | 4.3912 | 1.0142 | High | High | High | 892 | 1022 | 0.23095 | 355.5156
ALTO 11243745 | ALTO 1124 | NORTH BAY | 4.5809 | 48.7454 | 24.8% | 4 | 26 | 100% | 100% | 0 | 0.24571 | 1 | 4.1069 | 1.0091 | High | High | High | 893 | 1007 | 0.24571 | 354.5015
PASO ROBLES 1107CB | PASO ROBLES 1107 | LOS PADRES | 0.069192 | 75 | 100% | 0 | 0 | 0.6192% | 0% | 0 | 0.016629 | 47.6367 | 1.2733 | 1.0086 | Low | Low | Low | 894 | 758 | 0.79217 | 353.4923
DUNBAR 1103CB | DUNBAR 1103 | SONOMA | 1.9287 | 52.9434 | 74.35% | 2 | 2 | 15.81% | 20.29% | 0 | 0.029588 | 11.2183 | 3.0334 | 1.0069 | Medium | Medium | Medium | 895 | 934 | 0.33193 | 352.4837
COTATI 1105328 | COTATI 1105 | SONOMA | 0.42542 | 48.6287 | 27.07% | 0 | 1 | 3.098% | 0% | 0 | 0.0080325 | 47.6367 | 2.617 | 1.0014 | Low | Low | Medium | 896 | 904 | 0.38264 | 351.4768
FREMONT 1104MR339 | FREMONT 1104 | MISSION | 1.2378 | 84.498 | 6.265% | 0 | 0 | 17.79% | 0% | 0 | 0.0097922 | 65.3912 | 1.5544 | 0.99533 | Low | Low | Low | 897 | 809 | 0.64033 | 350.4754
DIAMOND SPRINGS 1105CB | DIAMOND SPRINGS 1105 | SIERRA | 1.4833 | 10 | 14.23% | 0 | 1 | 31.56% | 62.47% | 0 | 0.022985 | 14.9507 | 2.8916 | 0.99365 | Medium | Medium | Medium | 898 | 922 | 0.34364 | 349.4801
WILLITS 110391948 | WILLITS 1103 | HUMBOLDT | 6.1069 | 55.6867 | 72.29% | 1 | 4 | 82.53% | 5.563% | 0 | 0.035629 | 14.9507 | 1.8551 | 0.98814 | Medium | Medium | Low | 899 | 846 | 0.53267 | 348.4865
OAKLAND K 1102CR014 | OAKLAND K 1102 | EAST BAY | 10.5526 | 27.0866 | 16.24% | 14 | 8 | 100% | 100% | 1 | 0.23413 | 1 | 4.2072 | 0.98504 | High | High | High | 900 | 1017 | 0.23413 | 347.4983
PENRYN 11052406 | PENRYN 1105 | SIERRA | 3.0306 | 20.0804 | 58.87% | 1 | 0 | 24.58% | 0% | 0 | 0.012032 | 35.3263 | 2.2969 | 0.97632 | Low | Low | Medium | 901 | 885 | 0.42506 | 346.5133
VALLEY VIEW 1106P166 | VALLEY VIEW 1106 | EAST BAY | 3.4384 | 77.0381 | 8.804% | 5 | 1 | 75.32% | 0% | 0 | 0.020855 | 11.2183 | 4.1312 | 0.96654 | Low | Low | High | 902 | 1018 | 0.23396 | 345.537
MONTE RIO 1113346 | MONTE RIO 1113 | SONOMA | 10.1076 | 73.6223 | 44.96% | 12 | 4 | 100% | 100% | 0 | 0.29448 | 1 | 3.2807 | 0.9661 | High | High | High | 903 | 963 | 0.29448 | 344.5704
ALTO 1124432 | ALTO 1124 | NORTH BAY | 7.823 | 44.0512 | 43.81% | 6 | 19 | 100% | 100% | 0 | 0.22255 | 1 | 4.3312 | 0.96392 | High | High | High | 904 | 1028 | 0.22255 | 343.6043
CLARKSVILLE 210619642 | CLARKSVILLE 2106 | SIERRA | 0.81481 | 10 | 0% | 0 | 0 | 51.08% | 0% | 0 | 0.007814 | 35.3263 | 3.4847 | 0.96191 | Low | Low | High | 905 | 972 | 0.27604 | 342.6404
FITCH MOUNTAIN 1113406 | FITCH MOUNTAIN 1113 | SONOMA | 1.4439 | 43.4794 | 97.1% | 1 | 1 | 15.43% | 0% | 0 | 0.01793 | 19.9979 | 2.6791 | 0.96064 | Low | Low | Medium | 906 | 918 | 0.35857 | 341.6785
LLAGAS 2107XR178 | LLAGAS 2107 | SAN JOSE | 0.65323 | 27.1294 | 68.86% | 0 | 0 | 9.688% | 0% | 0 | 0.010217 | 26.5534 | 3.4762 | 0.94309 | Low | Low | High | 907 | 975 | 0.2713 | 340.7179
LOS GATOS 1106LA64 | LOS GATOS 1106 | DE ANZA | 12.775 | 27.6673 | 77.8% | 17 | 7 | 100% | 100% | 1 | 0.50336 | 1 | 1.8673 | 0.93994 | High | High | Low | 908 | 857 | 0.50336 | 339.7748
PENRYN 11072706 | PENRYN 1107 | SIERRA | 5.0792 | 12.8578 | 75.5% | 0 | 3 | 34.23% | 0% | 0 | 0.013291 | 26.5534 | 2.6628 | 0.93976 | Low | Low | Medium | 909 | 919 | 0.35292 | 338.8348
SHINGLE SPRINGS 2109CB | SHINGLE SPRINGS 2109 | SIERRA | 27.1022 | 21.2732 | 81.89% | 8 | 12 | 97.37% | 94.72% | 0 | 0.31197 | 1 | 3.0034 | 0.93698 | High | High | Medium | 910 | 955 | 0.31197 | 337.8951
VIEJO 220235388 | VIEJO 2202 | CENTRAL COAST | 0.45244 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.014786 | 14.9507 | 4.2357 | 0.93635 | Low | Low | High | 911 | 1030 | 0.22106 | 336.9581
OILFIELDS 1103N40 | OILFIELDS 1103 | CENTRAL COAST | 0.75328 | 20.1382 | 3.227% | 0 | 2 | 100% | 0% | 0 | 0.01659 | 19.9979 | 2.785 | 0.92399 | Low | Low | Medium | 912 | 935 | 0.33177 | 336.0217
PUTAH CREEK 110264044 | PUTAH CREEK 1102 | SACRAMENTO | 5.0213 | 75.9618 | 100% | 0 | 1 | 67.37% | 0% | 0 | 0.03282 | 14.9507 | 1.8721 | 0.91864 | Medium | Medium | Low | 913 | 860 | 0.49069 | 335.0978
STANISLAUS 17011812 | STANISLAUS 1701 | YOSEMITE | 19.5078 | 54.4191 | 60.13% | 9 | 15 | 100% | 99.79% | 0 | 0.30454 | 1 | 2.9903 | 0.91067 | High | High | Medium | 914 | 960 | 0.30454 | 334.1791
PENRYN 110790970 | PENRYN 1107 | SIERRA | 0.86048 | 10 | 69.3% | 0 | 0 | 20.31% | 0% | 0 | 0.011579 | 26.5534 | 2.9455 | 0.90563 | Low | Low | Medium | 915 | 957 | 0.30746 | 333.2684
CABRILLO 1103CB | CABRILLO 1103 | LOS PADRES | 0.14089 | 80 | 0% | 0 | 0 | 3.139% | 0% | 0 | 0.0078018 | 35.3263 | 3.2473 | 0.89498 | Low | Low | High | 916 | 973 | 0.27561 | 332.3628
LOS GATOS 110660116 | LOS GATOS 1106 | DE ANZA | 12.3794 | 30.6322 | 46% | 28 | 5 | 100% | 100% | 0 | 0.37151 | 1 | 2.4062 | 0.89393 | High | High | Medium | 917 | 909 | 0.37151 | 331.4678
NARROWS 21052216 | NARROWS 2105 | SIERRA | 56.6943 | 15.1323 | 85.75% | 7 | 36 | 98.06% | 0% | 0 | 0.28652 | 1 | 3.1152 | 0.89257 | High | High | High | 918 | 966 | 0.28652 | 330.5739
BIG BASIN 110169550 | BIG BASIN 1101 | CENTRAL COAST | 17.8925 | 32.0488 | 71.29% | 38 | 3 | 100% | 100% | 0 | 0.32055 | 1 | 2.7588 | 0.88433 | High | High | Medium | 919 | 940 | 0.32055 | 329.6813
GOLDTREE 1105551904 | GOLDTREE 1105 | LOS PADRES | 0.022237 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 2.7356 | 0.87498 | Medium | Medium | Medium | 920 | 942 | 0.31985 | 328.797
FROGTOWN 170113412 | FROGTOWN 1701 | STOCKTON | 38.8157 | 21.4669 | 89.5% | 2 | 31 | 100% | 20.91% | 0 | 0.31378 | 1 | 2.7876 | 0.8747 | High | High | Medium | 921 | 952 | 0.31378 | 327.922
MERCED FALLS 110285002 | MERCED FALLS 1102 | YOSEMITE | 35.632 | 29.6878 | 97.17% | 0 | 6 | 100% | 0% | 0 | 0.059691 | 26.5534 | 0.55157 | 0.87425 | Medium | Medium | Low | 922 | 641 | 1.585 | 327.0473
SAN RAMON 2102CB | SAN RAMON 2102 | MISSION | 1.535 | 41.2314 | 0% | 0 | 0 | 65.73% | 0% | 0 | 0.011168 | 19.9979 | 3.898 | 0.87053 | Low | Low | High | 923 | 1027 | 0.22333 | 326.1731
MONTICELLO 1101666 | MONTICELLO 1101 | NORTH BAY | 10.1625 | 67.7354 | 65.91% | 1 | 1 | 73.12% | 0% | 0 | 0.025333 | 14.9507 | 2.2961 | 0.86964 | Medium | Medium | Medium | 924 | 907 | 0.37875 | 325.3026
FOOTHILL 1102V06 | FOOTHILL 1102 | LOS PADRES | 1.4055 | 48.154 | 31.22% | 0 | 1 | 21.48% | 0% | 0 | 0.0099416 | 26.5534 | 3.2868 | 0.86767 | Low | Low | High | 925 | 985 | 0.26398 | 324.4329
SARATOGA 1107413816 | SARATOGA 1107 | DE ANZA | 11.1604 | 62.8545 | 90.16% | 13 | 7 | 100% | 89.94% | 0 | 0.25675 | 1 | 3.3738 | 0.86623 | High | High | High | 926 | 993 | 0.25675 | 323.5653
MONTICELLO 11011780 | MONTICELLO 1101 | NORTH BAY | 0.07232 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 19.9979 | 1.5173 | 0.86511 | Medium | Medium | Low | 927 | 832 | 0.57017 | 322.699
SHADY GLEN 110151696 | SHADY GLEN 1101 | SIERRA | 17.0578 | 38.8695 | 93.61% | 4 | 7 | 82.3% | 0% | 0 | 0.033526 | 11.2183 | 2.2918 | 0.86196 | Medium | Medium | Medium | 928 | 908 | 0.37611 | 321.8339
CAMP EVERS 210312990 | CAMP EVERS 2103 | CENTRAL COAST | 13.5574 | 33.1797 | 62.33% | 16 | 15 | 100% | 100% | 0 | 0.32668 | 1 | 2.6325 | 0.85998 | High | High | Medium | 929 | 937 | 0.32668 | 320.972
MESA 11016113 | MESA 1101 | LOS PADRES | 1.5145 | 57.2852 | 100% | 0 | 0 | 15.55% | 0% | 0 | 0.017101 | 19.9979 | 2.5121 | 0.85911 | Low | Low | Medium | 930 | 925 | 0.34199 | 320.112
NARROWS 2105 | NARROWS 2105 | SIERRA | 0.056021 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 2.6731 | 0.85501 | Medium | Medium | Medium | 931 | 942 | 0.31985 | 319.2529
MONTE RIO 11133970 | MONTE RIO 1113 | SONOMA | 7.3428 | 62.8724 | 47.81% | 13 | 10 | 100% | 100% | 0 | 0.25889 | 1 | 3.2812 | 0.84949 | High | High | High | 932 | 991 | 0.25889 | 318.3979
COARSEGOLD 210410110 | COARSEGOLD 2104 | YOSEMITE | 49.586 | 26.2952 | 95.51% | 5 | 92 | 100% | 6.102% | 1 | 0.36439 | 1 | 2.3299 | 0.84901 | High | High | Medium | 933 | 914 | 0.36439 | 317.5484
LAYTONVILLE 110264908 | LAYTONVILLE 1102 | HUMBOLDT | 3.5532 | 21.2702 | 61.98% | 6 | 8 | 55.85% | 0% | 0 | 0.021316 | 19.9979 | 1.9799 | 0.84396 | Low | Low | Low | 934 | 882 | 0.42627 | 316.6994
GARBERVILLE 11012026 | GARBERVILLE 1101 | HUMBOLDT | 6.3529 | 96.5509 | 100% | 5 | 1 | 100% | 0% | 0 | 0.05472 | 65.3912 | 0.23353 | 0.83563 | Medium | Medium | Low | 935 | 502 | 3.5782 | 315.8554
EEL RIVER 11024814 | EEL RIVER 1102 | HUMBOLDT | 27.3153 | 76.7361 | 63.94% | 7 | 10 | 97.55% | 0% | 0 | 0.42884 | 1 | 1.9361 | 0.83027 | High | High | Low | 936 | 881 | 0.42884 | 315.0198
SPRING GAP 170286032 | SPRING GAP 1702 | YOSEMITE | 1.0066 | 66.0059 | 100% | 0 | 0 | 34.72% | 25.18% | 0 | 0.037122 | 26.5534 | 0.83455 | 0.82263 | Medium | Medium | Low | 937 | 724 | 0.98571 | 314.1895
CAMP EVERS 210511004 | CAMP EVERS 2105 | CENTRAL COAST | 4.2954 | 13.9666 | 78.63% | 3 | 0 | 100% | 100% | 0 | 0.2074 | 1 | 3.9293 | 0.81496 | High | High | High | 938 | 1045 | 0.2074 | 313.3669
GREENBRAE 11021254 | GREENBRAE 1102 | NORTH BAY | 7.0201 | 10 | 37.52% | 8 | 16 | 74.16% | 100% | 0 | 0.21468 | 1 | 3.7891 | 0.81344 | High | High | High | 939 | 1038 | 0.21468 | 312.5519
MONTICELLO 110152910 | MONTICELLO 1101 | NORTH BAY | 2.1786 | 24.2187 | 98.28% | 0 | 1 | 69.32% | 0% | 0 | 0.026641 | 19.9979 | 1.5181 | 0.80879 | Medium | Medium | Low | 940 | 845 | 0.53277 | 311.7385
CAMP EVERS 210612518 | CAMP EVERS 2106 | CENTRAL COAST | 15.9361 | 56.9453 | 43.9% | 39 | 3 | 100% | 100% | 0 | 0.3407 | 1 | 2.3547 | 0.80224 | High | High | Medium | 941 | 926 | 0.3407 | 310.9297
ELECTRA 1101 | ELECTRA 1101 | STOCKTON | 0.02594 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 2.4984 | 0.79913 | Medium | Medium | Medium | 942 | 942 | 0.31985 | 310.1274
BIG TREES 0402CB | BIG TREES 0402 | CENTRAL COAST | 6.3055 | 27.5904 | 28.63% | 15 | 5 | 91.1% | 95.73% | 0 | 0.19443 | 1 | 4.0842 | 0.7941 | High | High | High | 943 | 1072 | 0.19443 | 309.3283
CLAYTON 221296224 | CLAYTON 2212 | DIABLO | 6.0784 | 53.8659 | 38.47% | 4 | 5 | 100% | 98.09% | 0 | 0.23534 | 1 | 3.3663 | 0.79223 | High | High | High | 944 | 1015 | 0.23534 | 308.5342
LOS GATOS 1106LB48 | LOS GATOS 1106 | DE ANZA | 14.9866 | 67.642 | 90.94% | 14 | 1 | 100% | 100% | 1 | 0.39219 | 1 | 2.0173 | 0.79115 | High | High | Low | 945 | 897 | 0.39219 | 307.742
PURISIMA 110154728 | PURISIMA 1101 | LOS PADRES | 0.37057 | 45.459 | 76.61% | 0 | 0 | 8.245% | 0% | 0 | 0.012146 | 19.9979 | 3.2328 | 0.78525 | Low | Low | High | 946 | 1011 | 0.2429 | 306.9508
COTATI 1102260 | COTATI 1102 | SONOMA | 1.6248 | 13.946 | 2.286% | 0 | 1 | 27.41% | 0% | 0 | 0.0075335 | 35.3263 | 2.9441 | 0.78353 | Low | Low | Medium | 947 | 983 | 0.26613 | 306.1656
WOODSIDE 11043583 | WOODSIDE 1104 | PENINSULA | 2.721 | 71.077 | 98.47% | 8 | 4 | 97.67% | 92.99% | 0 | 0.28756 | 1 | 2.7171 | 0.78133 | High | High | Medium | 948 | 965 | 0.28756 | 305.382
OAKHURST 1103CB | OAKHURST 1103 | YOSEMITE | 29.7308 | 28.0867 | 78.34% | 5 | 58 | 96.61% | 65.89% | 1 | 0.32601 | 1 | 2.3864 | 0.77799 | High | High | Medium | 949 | 938 | 0.32601 | 304.6007
OAKLAND X 1104CR288 | OAKLAND X 1104 | EAST BAY | 2.7135 | 13.3002 | 40.68% | 11 | 2 | 100% | 100% | 0 | 0.18087 | 1 | 4.2967 | 0.77715 | High | High | High | 950 | 1091 | 0.18087 | 303.8227
LLAGAS 2101XR264 | LLAGAS 2101 | SAN JOSE | 0.73019 | 64.4385 | 100% | 0 | 0 | 3.559% | 0% | 0 | 0.015944 | 19.9979 | 2.4255 | 0.77337 | Low | Low | Medium | 951 | 948 | 0.31885 | 303.0456
INDIAN FLAT 1104 | INDIAN FLAT 1104 | YOSEMITE | 0.0039208 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 14.9507 | 1.8025 | 0.76836 | Medium | Medium | Low | 952 | 883 | 0.42627 | 302.2722
HALF MOON BAY 1103H82 | HALF MOON BAY 1103 | PENINSULA | 53.0127 | 52.0051 | 39.35% | 29 | 11 | 92.34% | 3.002% | 1 | 0.29233 | 1 | 2.6229 | 0.76674 | High | High | Medium | 953 | 964 | 0.29233 | 301.5038
WOODACRE 1102137662 | WOODACRE 1102 | NORTH BAY | 8.5017 | 38.382 | 27.15% | 11 | 8 | 98.65% | 72.31% | 0 | 0.16033 | 1 | 4.753 | 0.76204 | High | High | High | 954 | 1129 | 0.16033 | 300.7371
WEST POINT 11021305 | WEST POINT 1102 | STOCKTON | 11.4284 | 52.5642 | 100% | 4 | 5 | 100% | 100% | 1 | 0.34333 | 1 | 2.218 | 0.76151 | High | High | Low | 955 | 923 | 0.34333 | 299.975
COLUMBIA HILL 1101CB | COLUMBIA HILL 1101 | SIERRA | 39.662 | 48.9114 | 99.72% | 21 | 18 | 100% | 77.89% | 0 | 0.46568 | 1 | 1.6227 | 0.75567 | High | High | Low | 956 | 867 | 0.46568 | 299.2135
DIAMOND SPRINGS 11052102 | DIAMOND SPRINGS 1105 | SIERRA | 37.6923 | 30.2782 | 83.99% | 5 | 15 | 95.84% | 86.14% | 1 | 0.30069 | 1 | 2.5037 | 0.75284 | High | High | Medium | 957 | 961 | 0.30069 | 298.4579
SAN JOAQUIN #3 110110010 | SAN JOAQUIN #3 1101 | YOSEMITE | 12.729 | 58.6534 | 88.53% | 3 | 19 | 100% | 90.16% | 0 | 0.42208 | 1 | 1.7707 | 0.74736 | High | High | Low | 958 | 886 | 0.42208 | 297.705
MIRABEL 110238514 | MIRABEL 1102 | SONOMA | 10.5875 | 61.5593 | 46.21% | 16 | 8 | 100% | 100% | 0 | 0.25422 | 1 | 2.9393 | 0.74724 | High | High | Medium | 959 | 996 | 0.25422 | 296.9577
TASSAJARA 2106CB | TASSAJARA 2106 | DIABLO | 0.13696 | 51.6086 | 30.65% | 0 | 2 | 4.465% | 0% | 0 | 0.0087354 | 19.9979 | 4.2753 | 0.74685 | Low | Low | High | 960 | 1104 | 0.17469 | 296.2104
CORTINA 1101302192 | CORTINA 1101 | SACRAMENTO | 1.036 | 90 | 100% | 0 | 0 | 5.795% | 0% | 0 | 0.019354 | 35.3263 | 1.0872 | 0.74333 | Low | Low | Low | 961 | 792 | 0.6837 | 295.4636
GEYSERVILLE 1101482 | GEYSERVILLE 1101 | SONOMA | 0.45328 | 77.9574 | 100% | 0 | 0 | 13.09% | 0% | 0 | 0.019179 | 35.3263 | 1.094 | 0.74117 | Low | Low | Low | 962 | 795 | 0.67751 | 294.7203
CURTIS 170268380 | CURTIS 1702 | YOSEMITE | 6.6498 | 16.4166 | 99.81% | 2 | 11 | 100% | 65.93% | 0 | 0.18443 | 1 | 4.0104 | 0.73965 | High | High | High | 963 | 1084 | 0.18443 | 293.9791
PENRYN 110550550 | PENRYN 1105 | SIERRA | 3.146 | 23.6879 | 96.13% | 0 | 1 | 22.41% | 0% | 0 | 0.014437 | 26.5534 | 1.9281 | 0.73914 | Low | Low | Low | 964 | 902 | 0.38336 | 293.2394
SNEATH LANE 110715341 | SNEATH LANE 1107 | PENINSULA | 0.71839 | 10 | 29.45% | 0 | 0 | 55.75% | 0% | 0 | 0.010414 | 19.9979 | 3.5461 | 0.73852 | Low | Low | High | 965 | 1043 | 0.20826 | 292.5003
FRUITLAND 1141CB | FRUITLAND 1141 | HUMBOLDT | 3.1926 | 94.3084 | 31.06% | 2 | 0 | 100% | 0% | 0 | 0.03355 | 26.5534 | 0.81784 | 0.72859 | Medium | Medium | Low | 966 | 737 | 0.89086 | 291.7618
SAN RAMON 2107MR284 | SAN RAMON 2107 | MISSION | 13.084 | 58.0067 | 71.73% | 0 | 4 | 87.08% | 97.71% | 0 | 0.20548 | 1 | 3.5403 | 0.72747 | High | High | High | 967 | 1051 | 0.20548 | 291.0332
WYANDOTTE 11091040 | WYANDOTTE 1109 | NORTH VALLEY | 0.63854 | 10 | 53.93% | 1 | 0 | 10.55% | 0% | 0 | 0.0082291 | 19.9979 | 4.416 | 0.72671 | Low | Low | High | 968 | 1121 | 0.16456 | 290.3057
LAKEVILLE 1102280 | LAKEVILLE 1102 | SONOMA | 2.0715 | 72.9124 | 15.25% | 0 | 2 | 23.31% | 0% | 0 | 0.010728 | 26.5534 | 2.5448 | 0.72494 | Low | Low | Medium | 969 | 968 | 0.28487 | 289.579
ALTO 1125902 | ALTO 1125 | NORTH BAY | 12.0705 | 57.5388 | 0.5919% | 9 | 8 | 100% | 85.9% | 1 | 0.21954 | 1 | 3.287 | 0.72162 | High | High | High | 970 | 1034 | 0.21954 | 288.8541
PINECREST 04011818 | PINECREST 0401 | YOSEMITE | 1.9342 | 47.9328 | 100% | 2 | 2 | 61.15% | 48.76% | 0 | 0.057579 | 14.9507 | 0.83639 | 0.72 | Medium | Medium | Low | 971 | 743 | 0.86084 | 288.1325
WILDWOOD 1101CB | WILDWOOD 1101 | NORTH VALLEY | 0.055929 | 81.1882 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045585 | 14.9507 | 1.052 | 0.71699 | Medium | Medium | Low | 972 | 794 | 0.68153 | 287.4125
HARTLEY 1102524 | HARTLEY 1102 | HUMBOLDT | 1.3594 | 63.3777 | 100% | 0 | 1 | 30.18% | 0% | 0 | 0.020999 | 14.9507 | 2.2759 | 0.71449 | Low | Low | Medium | 973 | 951 | 0.31394 | 286.6955
MIDDLETOWN 1102CB | MIDDLETOWN 1102 | HUMBOLDT | 4.3813 | 57.1831 | 32.04% | 0 | 1 | 66.6% | 5.967% | 1 | 0.023754 | 11.2183 | 2.6792 | 0.71397 | Medium | Medium | Medium | 974 | 982 | 0.26649 | 285.981
BOLINAS 1101530 | BOLINAS 1101 | NORTH BAY | 10.9693 | 95.0787 | 44.47% | 2 | 3 | 100% | 100% | 1 | 0.19488 | 1 | 3.6256 | 0.70654 | High | High | High | 975 | 1069 | 0.19488 | 285.267
HALF MOON BAY 11038898 | HALF MOON BAY 1103 | PENINSULA | 0.64191 | 18.722 | 22.54% | 0 | 1 | 100% | 0% | 0 | 0.016511 | 14.9507 | 2.8619 | 0.70648 | Low | Low | Medium | 976 | 1004 | 0.24685 | 284.5605
MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 2101 | SIERRA | 0.00097812 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 2.2083 | 0.70631 | Medium | Medium | Low | 977 | 942 | 0.31985 | 283.854
TEMPLETON 2111CB | TEMPLETON 2111 | LOS PADRES | 1.8275 | 10 | 27.26% | 0 | 0 | 16.54% | 0% | 0 | 0.0079104 | 35.3263 | 2.52 | 0.70419 | Low | Low | Medium | 978 | 970 | 0.27944 | 283.1477
MOLINO 110251788 | MOLINO 1102 | SONOMA | 5.6218 | 26.7859 | 66.33% | 10 | 1 | 38.47% | 5.373% | 0 | 0.021877 | 11.2183 | 2.8624 | 0.70251 | Medium | Medium | Medium | 979 | 1008 | 0.24543 | 282.4435
OCEANO 110391240 | OCEANO 1103 | LOS PADRES | 0.011387 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.014483 | 14.9507 | 3.2429 | 0.7022 | Low | Low | High | 980 | 1037 | 0.21654 | 281.741
KESWICK 110148480 | KESWICK 1101 | NORTH VALLEY | 10.8916 | 45.1063 | 95.79% | 1 | 7 | 100% | 100% | 0 | 0.2199 | 1 | 3.1927 | 0.70206 | High | High | High | 981 | 1031 | 0.2199 | 281.0387
CALISTOGA 1102634 | CALISTOGA 1102 | NORTH BAY | 11.7799 | 49.1315 | 63.48% | 13 | 6 | 61.37% | 93.22% | 1 | 0.23196 | 1 | 3.0202 | 0.70058 | High | High | Medium | 982 | 1019 | 0.23196 | 280.3367
SAN LUIS OBISPO 1101CB | SAN LUIS OBISPO 1101 | LOS PADRES | 6.447 | 57.4459 | 18.1% | 1 | 2 | 37.74% | 0% | 0 | 0.01156 | 19.9979 | 3.0286 | 0.70017 | Low | Low | Medium | 983 | 1020 | 0.23118 | 279.6361
BRUNSWICK 110750008 | BRUNSWICK 1107 | SIERRA | 3.5553 | 10 | 37.92% | 1 | 5 | 44.72% | 0% | 0 | 0.01283 | 14.9507 | 3.6273 | 0.69578 | Low | Low | High | 984 | 1078 | 0.19182 | 278.9359
CASTRO VALLEY 1108MR273 | CASTRO VALLEY 1108 | MISSION | 0.47624 | 26.7875 | 0% | 0 | 0 | 65.66% | 0% | 0 | 0.01155 | 14.9507 | 4.003 | 0.69126 | Low | Low | High | 985 | 1107 | 0.17268 | 278.2402
CURTIS 17039180 | CURTIS 1703 | YOSEMITE | 56.1725 | 23.1853 | 91.13% | 4 | 41 | 100% | 0% | 0 | 0.26987 | 1 | 2.515 | 0.67872 | High | High | Medium | 986 | 978 | 0.26987 | 277.5489
CAYETANO 21099504 | CAYETANO 2109 | MISSION | 14.1558 | 53.8418 | 95.53% | 0 | 2 | 97.78% | 75.62% | 1 | 0.20657 | 1 | 3.2662 | 0.67468 | High | High | High | 987 | 1047 | 0.20657 | 276.8702
CLARK ROAD 110290548 | CLARK ROAD 1102 | NORTH VALLEY | 18.3619 | 41.0434 | 98.73% | 0 | 11 | 100% | 100% | 0 | 0.25625 | 1 | 2.6272 | 0.67323 | High | High | Medium | 988 | 994 | 0.25625 | 276.1955
SAN RAMON 2119CB | SAN RAMON 2119 | MISSION | 0.46097 | 10 | 0% | 0 | 2 | 29.99% | 0% | 0 | 0.0066042 | 26.5534 | 3.8288 | 0.67144 | Low | Low | High | 989 | 1103 | 0.17536 | 275.5223
UPPER LAKE 1101452 | UPPER LAKE 1101 | HUMBOLDT | 1.5567 | 30.5905 | 77.99% | 1 | 7 | 7.943% | 0% | 0 | 0.019247 | 19.9979 | 1.7433 | 0.67099 | Low | Low | Low | 990 | 901 | 0.3849 | 274.8508
NARROWS 21021252 | NARROWS 2102 | SIERRA | 0.0028409 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 19.9979 | 2.6386 | 0.66989 | Low | Low | Medium | 991 | 998 | 0.25388 | 274.1798
POINT MORETTI 110136514 | POINT MORETTI 1101 | CENTRAL COAST | 6.8197 | 17.0171 | 90.44% | 21 | 1 | 100% | 87.46% | 0 | 0.19239 | 1 | 3.4814 | 0.66979 | High | High | High | 992 | 1077 | 0.19239 | 273.5099
COARSEGOLD 210410400 | COARSEGOLD 2104 | YOSEMITE | 42.0443 | 18.5406 | 94.25% | 4 | 95 | 94% | 0% | 0 | 0.26956 | 1 | 2.4779 | 0.66794 | High | High | Medium | 993 | 980 | 0.26956 | 272.8402
ROB ROY 210410298 | ROB ROY 2104 | CENTRAL COAST | 11.1938 | 57.3937 | 79.09% | 34 | 2 | 83.3% | 78.37% | 0 | 0.2019 | 1 | 3.3081 | 0.6679 | High | High | High | 994 | 1055 | 0.2019 | 272.1722
MORGAN HILL 2111XR398 | MORGAN HILL 2111 | SAN JOSE | 36.8919 | 62.4019 | 77.2% | 15 | 15 | 93.25% | 35.33% | 1 | 0.2433 | 1 | 2.7433 | 0.66742 | High | High | Medium | 995 | 1010 | 0.2433 | 271.5043
BIG BASIN 110195690 | BIG BASIN 1101 | CENTRAL COAST | 3.9003 | 22.8227 | 33.75% | 15 | 4 | 100% | 100% | 0 | 0.19661 | 1 | 3.3684 | 0.66225 | High | High | High | 996 | 1063 | 0.19661 | 270.8369
CLOVERDALE 1102672 | CLOVERDALE 1102 | SONOMA | 22.2941 | 69.8865 | 97.84% | 1 | 12 | 98.19% | 94.9% | 0 | 0.3373 | 1 | 1.9575 | 0.66027 | High | High | Low | 997 | 929 | 0.3373 | 270.1747
CORRAL 1103CB | CORRAL 1103 | STOCKTON | 5.566 | 15.4342 | 82.99% | 0 | 1 | 19.4% | 0% | 0 | 0.013588 | 14.9507 | 3.2433 | 0.65886 | Low | Low | High | 998 | 1054 | 0.20315 | 269.5144
SONOMA 11033052 | SONOMA 1103 | SONOMA | 13.4991 | 28.4052 | 91.89% | 6 | 9 | 83.64% | 100% | 0 | 0.18717 | 1 | 3.517 | 0.65829 | High | High | High | 999 | 1082 | 0.18717 | 268.8555
MORGAN HILL 2105CB | MORGAN HILL 2105 | SAN JOSE | 0.38186 | 10 | 60.48% | 0 | 1 | 21.31% | 0% | 0 | 0.0097345 | 19.9979 | 3.3616 | 0.65441 | Low | Low | High | 1000 | 1071 | 0.19467 | 268.1972
KESWICK 11019712 | KESWICK 1101 | NORTH VALLEY | 18.8507 | 17.0815 | 97.11% | 2 | 13 | 100% | 100% | 0 | 0.26099 | 1 | 2.4969 | 0.65166 | High | High | Medium | 1001 | 987 | 0.26099 | 267.5428
ROB ROY 2104CB | ROB ROY 2104 | CENTRAL COAST | 14.3247 | 30.9167 | 85.32% | 22 | 10 | 100% | 61.11% | 0 | 0.20721 | 1 | 3.1441 | 0.6515 | High | High | High | 1002 | 1046 | 0.20721 | 266.8912
SANTA YNEZ 1104Y30 | SANTA YNEZ 1104 | LOS PADRES | 0.89443 | 34.2503 | 70.68% | 0 | 2 | 6.535% | 0% | 0 | 0.010995 | 19.9979 | 2.9545 | 0.64959 | Low | Low | Medium | 1003 | 1032 | 0.21987 | 266.2397
LAS GALLINAS A 1105532 | LAS GALLINAS A 1105 | NORTH BAY | 3.6841 | 80.5371 | 66.72% | 3 | 5 | 83.44% | 94.05% | 0 | 0.19645 | 1 | 3.3042 | 0.64912 | High | High | High | 1004 | 1064 | 0.19645 | 265.5901
DEL MONTE 21042760 | DEL MONTE 2104 | CENTRAL COAST | 2.7139 | 31.1425 | 17.74% | 0 | 3 | 100% | 0% | 0 | 0.023371 | 11.2183 | 2.4707 | 0.64778 | Medium | Medium | Medium | 1005 | 986 | 0.26219 | 264.9409
OAKHURST 110377384 | OAKHURST 1103 | YOSEMITE | 4.7334 | 12.9583 | 82.83% | 5 | 23 | 100% | 100% | 0 | 0.25524 | 1 | 2.5373 | 0.64761 | High | High | Medium | 1006 | 995 | 0.25524 | 264.2932
WOODACRE 1102CB | WOODACRE 1102 | NORTH BAY | 12.3335 | 47.7292 | 17.58% | 11 | 6 | 98.44% | 71.03% | 1 | 0.14985 | 1 | 4.2881 | 0.64256 | High | High | High | 1007 | 1147 | 0.14985 | 263.6456
HORSESHOE 1101CB | HORSESHOE 1101 | SIERRA | 1.5163 | 10 | 43.57% | 1 | 0 | 28.38% | 0% | 0 | 0.010302 | 14.9507 | 4.1553 | 0.63998 | Low | Low | High | 1008 | 1139 | 0.15402 | 263.003
SAN JOAQUIN #2 1103CB | SAN JOAQUIN #2 1103 | YOSEMITE | 67.7251 | 13.3684 | 94.77% | 0 | 65 | 100% | 13.79% | 0 | 0.44439 | 1 | 1.4392 | 0.63957 | High | High | Low | 1009 | 874 | 0.44439 | 262.363
COARSEGOLD 210210040 | COARSEGOLD 2102 | YOSEMITE | 17.3327 | 15.2245 | 73.22% | 8 | 45 | 100% | 100% | 0 | 0.31716 | 1 | 2.0156 | 0.63929 | High | High | Low | 1010 | 950 | 0.31716 | 261.7234
FULTON 11024994 | FULTON 1102 | SONOMA | 1.7055 | 60.2868 | 44.56% | 0 | 1 | 40.25% | 0% | 0 | 0.014488 | 14.9507 | 2.9503 | 0.63906 | Low | Low | Medium | 1011 | 1036 | 0.21661 | 261.0842
BIG BASIN 11015028 | BIG BASIN 1101 | CENTRAL COAST | 4.9702 | 16.4741 | 66.18% | 6 | 3 | 100% | 100% | 0 | 0.1889 | 1 | 3.3403 | 0.63099 | High | High | High | 1012 | 1081 | 0.1889 | 260.4451
MIWUK 170247143 | MIWUK 1702 | YOSEMITE | 4.8917 | 41.2668 | 100% | 1 | 8 | 100% | 79.87% | 0 | 0.13801 | 1 | 4.5597 | 0.62928 | High | High | High | 1013 | 1174 | 0.13801 | 259.8141
SAN RAFAEL 1101310 | SAN RAFAEL 1101 | NORTH BAY | 1.3967 | 10 | 2.818% | 0 | 0 | 39.65% | 0% | 0 | 0.0071371 | 19.9979 | 4.4071 | 0.62902 | Low | Low | High | 1014 | 1159 | 0.14273 | 259.1848
WISE 1102 | WISE 1102 | SIERRA | 0.065469 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 1.9642 | 0.62826 | Medium | Medium | Low | 1015 | 942 | 0.31985 | 258.5558
PENRYN 1103660 | PENRYN 1103 | SIERRA | 10.4724 | 10.4096 | 69.5% | 2 | 4 | 53.75% | 0% | 0 | 0.018041 | 14.9507 | 2.329 | 0.62817 | Low | Low | Medium | 1016 | 979 | 0.26972 | 257.9276
MIDDLETOWN 1102878 | MIDDLETOWN 1102 | HUMBOLDT | 0.98449 | 64.5076 | 97.38% | 0 | 3 | 16.45% | 0% | 0 | 0.018862 | 11.2183 | 2.9665 | 0.6277 | Low | Low | Medium | 1017 | 1040 | 0.2116 | 257.2994
MIWUK 170153038 | MIWUK 1701 | YOSEMITE | 6.638 | 67.6188 | 100% | 3 | 9 | 100% | 100% | 0 | 0.26716 | 1 | 2.3412 | 0.62548 | High | High | Medium | 1018 | 981 | 0.26716 | 256.6717
TEMPLETON 2110901690 | TEMPLETON 2110 | LOS PADRES | 36.531 | 44.497 | 99.02% | 7 | 6 | 93.11% | 83.54% | 1 | 0.29843 | 1 | 2.0943 | 0.625 | High | High | Low | 1019 | 962 | 0.29843 | 256.0462
RED BLUFF 11051564 | RED BLUFF 1105 | NORTH VALLEY | 1.279 | 15.2296 | 100% | 0 | 0 | 12.04% | 0% | 0 | 0.012441 | 35.3263 | 1.4214 | 0.62469 | Low | Low | Low | 1020 | 877 | 0.43949 | 255.4212
SUNOL 1101MR196 | SUNOL 1101 | MISSION | 2.4505 | 75.1937 | 26.76% | 0 | 1 | 18.84% | 0% | 0 | 0.011214 | 35.3263 | 1.5737 | 0.6234 | Low | Low | Low | 1021 | 894 | 0.39615 | 254.7965
DUNBAR 11033127 | DUNBAR 1103 | SONOMA | 8.8393 | 48.2541 | 93.29% | 0 | 4 | 91.69% | 100% | 0 | 0.19391 | 1 | 3.2038 | 0.62125 | High | High | High | 1022 | 1074 | 0.19391 | 254.1731
CENTERVILLE 11012448 | CENTERVILLE 1101 | NORTH VALLEY | 24.8271 | 10 | 80.77% | 5 | 8 | 100% | 95.09% | 1 | 0.182 | 1 | 3.4115 | 0.62089 | High | High | High | 1023 | 1088 | 0.182 | 253.5519
MORAGA 1102CB | MORAGA 1102 | DIABLO | 3.3475 | 12.7577 | 17.22% | 0 | 6 | 36.14% | 35.27% | 0 | 0.015794 | 11.2183 | 3.4911 | 0.61857 | Low | Low | High | 1024 | 1097 | 0.17719 | 252.931
CAMP EVERS 2105CB | CAMP EVERS 2105 | CENTRAL COAST | 8.5381 | 22.2654 | 52.34% | 18 | 3 | 83.09% | 96.05% | 0 | 0.14927 | 1 | 4.1373 | 0.61755 | High | High | High | 1025 | 1149 | 0.14927 | 252.3124
SONOMA 1105138 | SONOMA 1105 | SONOMA | 0.57477 | 60.5779 | 43.92% | 0 | 0 | 3.3% | 0% | 0 | 0.0098109 | 19.9979 | 3.1352 | 0.61511 | Low | Low | High | 1026 | 1065 | 0.1962 | 251.6948
SAN RAMON 2101CB | SAN RAMON 2101 | MISSION | 0.57317 | 10 | 0% | 0 | 0 | 53.42% | 0% | 0 | 0.0079978 | 19.9979 | 3.8395 | 0.61409 | Low | Low | High | 1027 | 1131 | 0.15994 | 251.0797
MARTELL 110292172 | MARTELL 1102 | STOCKTON | 1.6199 | 10 | 31.25% | 0 | 0 | 49.18% | 0% | 0 | 0.0099007 | 19.9979 | 3.0995 | 0.61369 | Low | Low | High | 1028 | 1060 | 0.19799 | 250.4656
SANTA ROSA A 1104210 | SANTA ROSA A 1104 | SONOMA | 6.8749 | 10 | 33.39% | 9 | 10 | 88.77% | 100% | 0 | 0.17303 | 1 | 3.5409 | 0.61267 | High | High | High | 1029 | 1106 | 0.17303 | 249.852
SHINGLE SPRINGS 2105CB | SHINGLE SPRINGS 2105 | SIERRA | 19.4761 | 21.3342 | 76.42% | 1 | 7 | 100% | 96.24% | 0 | 0.20055 | 1 | 3.0516 | 0.612 | High | High | Medium | 1030 | 1056 | 0.20055 | 249.2393
HOPLAND 110180620 | HOPLAND 1101 | HUMBOLDT | 0.61898 | 10 | 82.97% | 0 | 0 | 11.01% | 0% | 0 | 0.010345 | 35.3263 | 1.672 | 0.61103 | Low | Low | Low | 1031 | 913 | 0.36545 | 248.6273
IGNACIO 11011264 | IGNACIO 1101 | NORTH BAY | 1.5242 | 13.9644 | 55.83% | 0 | 4 | 38.01% | 4.721% | 0 | 0.016971 | 11.2183 | 3.1948 | 0.60822 | Low | Low | High | 1032 | 1080 | 0.19038 | 248.0163
OAKHURST 11035480 | OAKHURST 1103 | YOSEMITE | 17.1484 | 38.4474 | 78.11% | 4 | 31 | 100% | 97.69% | 0 | 0.33517 | 1 | 1.8045 | 0.6048 | High | High | Low | 1033 | 932 | 0.33517 | 247.408
MARIPOSA 210237288 | MARIPOSA 2102 | YOSEMITE | 85.1145 | 35.7142 | 99.54% | 6 | 74 | 100% | 7.812% | 0 | 0.40262 | 1 | 1.5019 | 0.60469 | High | High | Low | 1034 | 891 | 0.40262 | 246.8032
PERRY 1101V88 | PERRY 1101 | LOS PADRES | 1.2286 | 10 | 3.935% | 0 | 0 | 39.45% | 0% | 0 | 0.0071884 | 26.5534 | 3.1534 | 0.6019 | Low | Low | High | 1035 | 1079 | 0.19088 | 246.1985
CALISTOGA 1101890 | CALISTOGA 1101 | NORTH BAY | 22.5646 | 51.954 | 60.75% | 7 | 3 | 89.13% | 61.5% | 0 | 0.25974 | 1 | 2.3028 | 0.59812 | High | High | Medium | 1036 | 989 | 0.25974 | 245.5966
CALISTOGA 110135588 | CALISTOGA 1101 | NORTH BAY | 3.0755 | 87.0174 | 100% | 0 | 0 | 100% | 100% | 0 | 0.24881 | 1 | 2.3966 | 0.59629 | High | High | Medium | 1037 | 1003 | 0.24881 | 244.9985
PARADISE 110445674 | PARADISE 1104 | NORTH VALLEY | 5.0463 | 10.402 | 42.33% | 2 | 14 | 100% | 100% | 0 | 0.16095 | 1 | 3.7001 | 0.59555 | High | High | High | 1038 | 1128 | 0.16095 | 244.4022
LLAGAS 2101XR244 | LLAGAS 2101 | SAN JOSE | 0.29573 | 10 | 100% | 0 | 1 | 2.088% | 0% | 0 | 0.01111 | 19.9979 | 2.6701 | 0.59322 | Low | Low | Medium | 1039 | 1029 | 0.22217 | 243.8067
SAN MIGUEL 1105CB | SAN MIGUEL 1105 | LOS PADRES | 0.96596 | 53.2217 | 100% | 0 | 0 | 9.014% | 0% | 0 | 0.015601 | 19.9979 | 1.882 | 0.58717 | Low | Low | Low | 1040 | 954 | 0.312 | 243.2135
SAN LUIS OBISPO 1104V46 | SAN LUIS OBISPO 1104 | LOS PADRES | 18.1965 | 66.1378 | 91.34% | 1 | 13 | 87.31% | 73.08% | 1 | 0.28268 | 1 | 2.0672 | 0.58435 | High | High | Low | 1041 | 969 | 0.28268 | 242.6263
DEL MONTE 21029060 | DEL MONTE 2102 | CENTRAL COAST | 0.0023123 | 10 | 0% | 0 | 0 | 0.0258% | 0% | 0 | 0.0046992 | 26.5534 | 4.6351 | 0.57837 | Low | Low | High | 1042 | 1216 | 0.12478 | 242.0419
CAMP EVERS 210610718 | CAMP EVERS 2106 | CENTRAL COAST | 8.4743 | 22.3341 | 66.06% | 7 | 3 | 100% | 100% | 0 | 0.17677 | 1 | 3.2715 | 0.57831 | High | High | High | 1043 | 1099 | 0.17677 | 241.4636
PAUL SWEET 21065178 | PAUL SWEET 2106 | CENTRAL COAST | 7.3151 | 10 | 46.38% | 7 | 0 | 100% | 100% | 0 | 0.17066 | 1 | 3.3829 | 0.57733 | High | High | High | 1044 | 1109 | 0.17066 | 240.8853
KESWICK 11011590 | KESWICK 1101 | NORTH VALLEY | 6.51 | 47.89 | 75.62% | 0 | 1 | 100% | 100% | 0 | 0.15625 | 1 | 3.693 | 0.57701 | High | High | High | 1045 | 1137 | 0.15625 | 240.3079
SANTA MARIA 1108M18 | SANTA MARIA 1108 | LOS PADRES | 14.6945 | 77.5423 | 92.38% | 1 | 8 | 82.48% | 56.56% | 1 | 0.21976 | 1 | 2.6052 | 0.57252 | High | High | Medium | 1046 | 1033 | 0.21976 | 239.7309
NORTH DUBLIN 2103 | NORTH DUBLIN 2103 | MISSION | 0.0011266 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 11.2183 | 4.0077 | 0.57078 | Low | Low | High | 1047 | 1161 | 0.14242 | 239.1584
PENRYN 1103CB | PENRYN 1103 | SIERRA | 2.2673 | 10 | 57.81% | 1 | 1 | 71.12% | 0% | 0 | 0.015799 | 14.9507 | 2.4019 | 0.56734 | Low | Low | Medium | 1048 | 1014 | 0.23621 | 238.5876
BRUNSWICK 11062416 | BRUNSWICK 1106 | SIERRA | 28.6672 | 22.1211 | 86.48% | 10 | 9 | 92.26% | 60.33% | 1 | 0.19856 | 1 | 2.8411 | 0.56415 | High | High | Medium | 1049 | 1059 | 0.19856 | 238.0203
SAN BENITO 210136912 | SAN BENITO 2101 | CENTRAL COAST | 2.942 | 68.099 | 74.6% | 0 | 1 | 23.25% | 0% | 0 | 0.016483 | 14.9507 | 2.2757 | 0.5608 | Low | Low | Medium | 1050 | 1005 | 0.24643 | 237.4561
WOODWARD 2108688294 | WOODWARD 2108 | FRESNO | 0.015135 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 26.5534 | 1.6587 | 0.55916 | Low | Low | Low | 1051 | 930 | 0.3371 | 236.8953
BRUNSWICK 11103907 | BRUNSWICK 1110 | SIERRA | 0.89347 | 10 | 0% | 2 | 0 | 100% | 0% | 0 | 0.013031 | 14.9507 | 2.8579 | 0.55681 | Low | Low | Medium | 1052 | 1070 | 0.19483 | 236.3362
SARATOGA 1107LC12 | SARATOGA 1107 | DE ANZA | 7.3147 | 36.5682 | 63.55% | 4 | 7 | 100% | 57.8% | 0 | 0.15388 | 1 | 3.6179 | 0.55673 | High | High | High | 1053 | 1141 | 0.15388 | 235.7793
OAKLAND X 1104 | OAKLAND X 1104 | EAST BAY | 0.11526 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 4.2748 | 0.55668 | High | High | High | 1054 | 1197 | 0.13022 | 235.2226
CAMP EVERS 21055146 | CAMP EVERS 2105 | CENTRAL COAST | 6.0305 | 10 | 32.63% | 11 | 6 | 100% | 100% | 0 | 0.14397 | 1 | 3.8493 | 0.55419 | High | High | High | 1055 | 1157 | 0.14397 | 234.6659
CURTIS 17028000 | CURTIS 1702 | YOSEMITE | 14.3249 | 17.4723 | 99.98% | 1 | 11 | 100% | 50.67% | 0 | 0.14933 | 1 | 3.7034 | 0.55303 | High | High | High | 1056 | 1148 | 0.14933 | 234.1117
PENRYN 1107CB | PENRYN 1107 | SIERRA | 5.4827 | 14.0733 | 57.47% | 3 | 1 | 34.07% | 0% | 0 | 0.01315 | 14.9507 | 2.8102 | 0.55251 | Low | Low | Medium | 1057 | 1062 | 0.19661 | 233.5587
FRUITLAND 11418746 | FRUITLAND 1141 | HUMBOLDT | 0.40721 | 85 | 7.434% | 0 | 0 | 50.57% | 0% | 0 | 0.013725 | 47.6367 | 0.84229 | 0.55071 | Low | Low | Low | 1058 | 804 | 0.65382 | 233.0062
PAUL SWEET 2106428102 | PAUL SWEET 2106 | CENTRAL COAST | 11.5695 | 14.0231 | 80.02% | 8 | 3 | 89.09% | 75.97% | 1 | 0.13775 | 1 | 3.9916 | 0.54983 | High | High | High | 1059 | 1176 | 0.13775 | 232.4555
VIEJO 22029112 | VIEJO 2202 | CENTRAL COAST | 0.78302 | 10 | 22.17% | 1 | 0 | 23.74% | 0% | 0 | 0.008258 | 14.9507 | 4.4379 | 0.54792 | Low | Low | High | 1060 | 1218 | 0.12346 | 231.9057
LLAGAS 2101XR584 | LLAGAS 2101 | SAN JOSE | 1.1341 | 38.093 | 49.38% | 0 | 3 | 12.45% | 0% | 0 | 0.010267 | 19.9979 | 2.6623 | 0.54662 | Low | Low | Medium | 1061 | 1052 | 0.20532 | 231.3577
BOLINAS 1101806 | BOLINAS 1101 | NORTH BAY | 3.0453 | 88.6877 | 5.762% | 0 | 3 | 100% | 100% | 0 | 0.14085 | 1 | 3.8778 | 0.54618 | High | High | High | 1062 | 1165 | 0.14085 | 230.8111
CLAYTON 2212CB | CLAYTON 2212 | DIABLO | 1.3959 | 28.1061 | 22.31% | 0 | 2 | 11% | 15.16% | 0 | 0.01235 | 11.2183 | 3.9394 | 0.5458 | Low | Low | High | 1063 | 1171 | 0.13855 | 230.265
PLACER 1102CB | PLACER 1102 | SIERRA | 2.1407 | 10 | 18.98% | 0 | 1 | 100% | 0% | 0 | 0.015126 | 11.2183 | 3.2057 | 0.54396 | Low | Low | High | 1064 | 1111 | 0.16968 | 229.7192
PLACERVILLE 21069712 | PLACERVILLE 2106 | SIERRA | 24.7737 | 54.0303 | 80.14% | 10 | 4 | 100% | 89.29% | 1 | 0.25885 | 1 | 2.0967 | 0.54273 | High | High | Low | 1065 | 992 | 0.25885 | 229.1752
SILVERADO 2104708 | SILVERADO 2104 | NORTH BAY | 4.377 | 40.803 | 65.23% | 1 | 8 | 88.72% | 99% | 0 | 0.16025 | 1 | 3.379 | 0.5415 | High | High | High | 1066 | 1130 | 0.16025 | 228.6325
PLACERVILLE 210611132 | PLACERVILLE 2106 | SIERRA | 43.1899 | 37.6905 | 78.66% | 11 | 29 | 100% | 66.95% | 0 | 0.3241 | 1 | 1.6694 | 0.54105 | High | High | Low | 1067 | 939 | 0.3241 | 228.091
PENRYN 11072704 | PENRYN 1107 | SIERRA | 1.9532 | 10 | 45.97% | 0 | 0 | 34.19% | 0% | 0 | 0.010983 | 14.9507 | 3.2851 | 0.53943 | Low | Low | High | 1068 | 1123 | 0.1642 | 227.5499
GUALALA 11121294 | GUALALA 1112 | HUMBOLDT | 19.9398 | 39.726 | 11.78% | 10 | 62 | 100% | 0% | 0 | 0.24042 | 1 | 2.2212 | 0.53402 | High | High | Low | 1069 | 1012 | 0.24042 | 227.0105
PUEBLO 1105716 | PUEBLO 1105 | NORTH BAY | 2.9378 | 34.7126 | 67.65% | 0 | 0 | 14.86% | 0% | 0 | 0.01121 | 14.9507 | 3.18 | 0.53295 | Low | Low | High | 1070 | 1117 | 0.16759 | 226.4765
COTATI 11055156 | COTATI 1105 | SONOMA | 3.6981 | 31.1041 | 18.22% | 1 | 1 | 37.15% | 0% | 0 | 0.012279 | 14.9507 | 2.8955 | 0.53156 | Low | Low | Medium | 1071 | 1085 | 0.18358 | 225.9435
HARTLEY 1101658 | HARTLEY 1101 | HUMBOLDT | 2.7971 | 52.1185 | 100% | 0 | 1 | 20.57% | 0% | 0 | 0.020197 | 11.2183 | 2.3275 | 0.52735 | Low | Low | Medium | 1072 | 1024 | 0.22658 | 225.412
WYANDOTTE 1109CB | WYANDOTTE 1109 | NORTH VALLEY | 2.5841 | 10 | 31.89% | 0 | 1 | 27.38% | 0% | 0 | 0.0081836 | 14.9507 | 4.3025 | 0.52641 | Low | Low | High | 1073 | 1221 | 0.12235 | 224.8846
SEACLIFF 0401CB | SEACLIFF 0401 | CENTRAL COAST | 5.8801 | 16.5923 | 59.63% | 6 | 2 | 97.46% | 83.75% | 0 | 0.13923 | 1 | 3.7795 | 0.52621 | High | High | High | 1074 | 1169 | 0.13923 | 224.3582
SAN RAFAEL 11071276 | SAN RAFAEL 1107 | NORTH BAY | 3.842 | 10 | 17.39% | 6 | 6 | 100% | 100% | 0 | 0.12189 | 1 | 4.3125 | 0.52565 | High | High | High | 1075 | 1223 | 0.12189 | 223.832
STAFFORD 110233692 | STAFFORD 1102 | NORTH BAY | 0.31495 | 10 | 16.33% | 0 | 0 | 14.09% | 0% | 0 | 0.0061817 | 26.5534 | 3.2 | 0.52527 | Low | Low | High | 1076 | 1124 | 0.16415 | 223.3063
APPLE HILL 21029722 | APPLE HILL 2102 | SIERRA | 38.3357 | 63.3481 | 100% | 10 | 4 | 100% | 82.49% | 1 | 0.36946 | 1 | 1.4151 | 0.52281 | High | High | Low | 1077 | 912 | 0.36946 | 222.7811
EMERALD LAKE 0401CB | EMERALD LAKE 0401 | PENINSULA | 15.5314 | 21.1198 | 27.73% | 5 | 20 | 73.41% | 27.29% | 1 | 0.11416 | 1 | 4.5679 | 0.52148 | High | High | High | 1078 | 1241 | 0.11416 | 222.2582
CAMP EVERS 21055232 | CAMP EVERS 2105 | CENTRAL COAST | 4.5381 | 18.453 | 49.44% | 6 | 6 | 100% | 100% | 0 | 0.14357 | 1 | 3.6265 | 0.52068 | High | High | High | 1079 | 1158 | 0.14357 | 221.7368
COARSEGOLD 210210050 | COARSEGOLD 2102 | YOSEMITE | 7.18 | 18.0295 | 97.64% | 2 | 12 | 100% | 100% | 0 | 0.25905 | 1 | 2.0066 | 0.51979 | High | High | Low | 1080 | 990 | 0.25905 | 221.2161
WEST POINT 11021341 | WEST POINT 1102 | STOCKTON | 10.0456 | 74.4483 | 100% | 1 | 5 | 100% | 100% | 0 | 0.33803 | 1 | 1.5377 | 0.51978 | High | High | Low | 1081 | 927 | 0.33803 | 220.6963
COTATI 110475972 | COTATI 1104 | SONOMA | 2.7371 | 10 | 35.68% | 0 | 3 | 41.48% | 0% | 0 | 0.015037 | 11.2183 | 3.0719 | 0.51821 | Low | Low | Medium | 1082 | 1115 | 0.1687 | 220.1765
ATASCADERO 1103A88 | ATASCADERO 1103 | LOS PADRES | 0.25306 | 10 | 42.36% | 0 | 0 | 9.428% | 0% | 0 | 0.0073051 | 26.5534 | 2.6184 | 0.50791 | Low | Low | Medium | 1083 | 1073 | 0.19397 | 219.6583
SAN LUIS OBISPO 1107V60 | SAN LUIS OBISPO 1107 | LOS PADRES | 16.0455 | 59.2942 | 63.57% | 4 | 4 | 100% | 91.12% | 0 | 0.23106 | 1 | 2.1951 | 0.5072 | High | High | Low | 1084 | 1021 | 0.23106 | 219.1504
COTTONWOOD 11011510 | COTTONWOOD 1101 | NORTH VALLEY | 0.7279 | 10 | 33.06% | 0 | 0 | 21.95% | 0% | 0 | 0.0076675 | 35.3263 | 1.8603 | 0.5039 | Low | Low | Low | 1085 | 976 | 0.27086 | 218.6432
WYANDOTTE 11031508 | WYANDOTTE 1103 | NORTH VALLEY | 25.7036 | 27.6675 | 92.16% | 3 | 8 | 99.06% | 81.42% | 1 | 0.17558 | 1 | 2.8465 | 0.49977 | High | High | Medium | 1086 | 1101 | 0.17558 | 218.1393
MORGAN HILL 210542348 | MORGAN HILL 2105 | SAN JOSE | 1.0024 | 17.5681 | 55.95% | 0 | 0 | 23.75% | 0% | 0 | 0.0099083 | 14.9507 | 3.3198 | 0.49179 | Low | Low | High | 1087 | 1151 | 0.14814 | 217.6395
BIG BASIN 1102CB | BIG BASIN 1102 | CENTRAL COAST | 6.2676 | 51.463 | 36.35% | 17 | 4 | 100% | 100% | 0 | 0.19295 | 1 | 2.5476 | 0.49156 | High | High | Medium | 1088 | 1076 | 0.19295 | 217.1477
CALISTOGA 110266730 | CALISTOGA 1102 | NORTH BAY | 1.1709 | 73.9432 | 93.25% | 0 | 0 | 100% | 100% | 0 | 0.17987 | 1 | 2.7269 | 0.49048 | High | High | Medium | 1089 | 1093 | 0.17987 | 216.6562
PARADISE 11032534 | PARADISE 1103 | NORTH VALLEY | 4.7177 | 10 | 61.75% | 3 | 6 | 100% | 100% | 0 | 0.12837 | 1 | 3.8138 | 0.48959 | High | High | High | 1090 | 1206 | 0.12837 | 216.1657
PLACERVILLE 21066512 | PLACERVILLE 2106 | SIERRA | 20.9994 | 19.5513 | 83.24% | 2 | 9 | 100% | 100% | 0 | 0.25186 | 1 | 1.9426 | 0.48926 | High | High | Low | 1091 | 1000 | 0.25186 | 215.6761
OTTER 11017611 | OTTER 1101 | CENTRAL COAST | 4.3976 | 73.491 | 75.26% | 4 | 3 | 100% | 100% | 1 | 0.3205 | 1 | 1.5238 | 0.48836 | High | High | Low | 1092 | 941 | 0.3205 | 215.1868
OAKLAND K 1104CR204 | OAKLAND K 1104 | EAST BAY | 3.7332 | 23.8088 | 27.59% | 6 | 1 | 100% | 100% | 0 | 0.11562 | 1 | 4.1768 | 0.48293 | High | High | High | 1093 | 1236 | 0.11562 | 214.6985
BIG BEND 1102CB | BIG BEND 1102 | NORTH VALLEY | 17.1238 | 77.0813 | 99.95% | 1 | 3 | 100% | 100% | 0 | 0.22606 | 1 | 2.1303 | 0.48158 | High | High | Low | 1094 | 1025 | 0.22606 | 214.2155
BIG BASIN 11025066 | BIG BASIN 1102 | CENTRAL COAST | 14.538 | 30.1342 | 55.77% | 35 | 1 | 100% | 92.59% | 1 | 0.20391 | 1 | 2.3602 | 0.48127 | High | High | Medium | 1095 | 1053 | 0.20391 | 213.734
CALISTOGA 110189150 | CALISTOGA 1101 | NORTH BAY | 9.6361 | 72.7174 | 50.49% | 2 | 3 | 100% | 93.01% | 1 | 0.18208 | 1 | 2.6306 | 0.47897 | High | High | Medium | 1096 | 1087 | 0.18208 | 213.2527
HORSESHOE 11011682 | HORSESHOE 1101 | SIERRA | 1.1361 | 10 | 70.68% | 0 | 0 | 11.64% | 0% | 0 | 0.010746 | 11.2183 | 3.9722 | 0.47887 | Low | Low | High | 1097 | 1224 | 0.12055 | 212.7737
PAUL SWEET 210411074 | PAUL SWEET 2104 | CENTRAL COAST | 2.9891 | 10 | 96.78% | 2 | 0 | 97.58% | 100% | 0 | 0.12749 | 1 | 3.7533 | 0.47849 | High | High | High | 1098 | 1209 | 0.12749 | 212.2948
LOS GATOS 1106LA42 | LOS GATOS 1106 | DE ANZA | 2.7943 | 10 | 80.03% | 3 | 2 | 100% | 100% | 1 | 0.15252 | 1 | 3.137 | 0.47846 | High | High | High | 1099 | 1143 | 0.15252 | 211.8164
PINE GROVE 11013170 | PINE GROVE 1101 | STOCKTON | 40.3025 | 15.3788 | 88.67% | 12 | 21 | 100% | 0% | 0 | 0.18 | 1 | 2.6168 | 0.47101 | High | High | Medium | 1100 | 1092 | 0.18 | 211.3379
SAN JOAQUIN #3 1103CB | SAN JOAQUIN #3 1103 | YOSEMITE | 28.2713 | 13.2744 | 82.63% | 4 | 63 | 100% | 35.67% | 0 | 0.37964 | 1 | 1.2383 | 0.47011 | High | High | Low | 1101 | 905 | 0.37964 | 210.8669
SAN RAMON 2117CB | SAN RAMON 2117 | MISSION | 0.44721 | 10 | 0% | 0 | 0 | 26.74% | 0% | 0 | 0.0061326 | 19.9979 | 3.8316 | 0.46991 | Low | Low | High | 1102 | 1220 | 0.12264 | 210.3968
SAUSALITO 1101CB | SAUSALITO 1101 | NORTH BAY | 0.084384 | 10 | 39.07% | 0 | 0 | 1.452% | 0% | 0 | 0.0074993 | 19.9979 | 3.1293 | 0.4693 | Low | Low | High | 1103 | 1146 | 0.14997 | 209.9269
SILVERADO 210234959 | SILVERADO 2102 | NORTH BAY | 24.7275 | 77.6516 | 100% | 5 | 11 | 91.78% | 69.47% | 1 | 0.34288 | 1 | 1.3442 | 0.46089 | High | High | Low | 1104 | 924 | 0.34288 | 209.4576
MORGAN HILL 2105XR268 | MORGAN HILL 2105 | SAN JOSE | 7.973 | 60.2912 | 70.21% | 1 | 2 | 100% | 100% | 0 | 0.14861 | 1 | 3.0893 | 0.45909 | High | High | High | 1105 | 1150 | 0.14861 | 208.9967
OTTER 1101CB | OTTER 1101 | CENTRAL COAST | 6.5139 | 35.3423 | 0.6325% | 8 | 1 | 96.47% | 87.12% | 1 | 0.20943 | 1 | 2.1919 | 0.45904 | High | High | Low | 1106 | 1042 | 0.20943 | 208.5376
COARSEGOLD 21025380 | COARSEGOLD 2102 | YOSEMITE | 14.1287 | 13.3143 | 99.57% | 3 | 25 | 100% | 100% | 0 | 0.23471 | 1 | 1.9542 | 0.45867 | High | High | Low | 1107 | 1016 | 0.23471 | 208.0785
GOLDTREE 1105CB | GOLDTREE 1105 | LOS PADRES | 7.0823 | 62.297 | 33.11% | 0 | 1 | 49.12% | 0% | 0 | 0.014604 | 11.2183 | 2.7587 | 0.45198 | Low | Low | Medium | 1108 | 1125 | 0.16384 | 207.6199
RED BLUFF 110176020 | RED BLUFF 1101 | NORTH VALLEY | 8.959 | 16.3023 | 99.96% | 0 | 1 | 62.16% | 0% | 0 | 0.020958 | 14.9507 | 1.44 | 0.45121 | Low | Low | Low | 1109 | 953 | 0.31334 | 207.1679
CAMP EVERS 210637210 | CAMP EVERS 2106 | CENTRAL COAST | 6.3592 | 23.8928 | 45.59% | 8 | 2 | 100% | 100% | 0 | 0.15389 | 1 | 2.9227 | 0.44978 | High | High | Medium | 1110 | 1140 | 0.15389 | 206.7167
SAN RAFAEL 11081262 | SAN RAFAEL 1108 | NORTH BAY | 4.0586 | 23.1286 | 14.29% | 3 | 8 | 91.28% | 100% | 0 | 0.094261 | 1 | 4.7701 | 0.44963 | High | High | High | 1111 | 1317 | 0.094261 | 206.2669
CENTERVILLE 1101 | CENTERVILLE 1101 | NORTH VALLEY | 0.0017292 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 3.4526 | 0.44961 | High | High | High | 1112 | 1197 | 0.13022 | 205.8173
WILLITS 1103964 | WILLITS 1103 | HUMBOLDT | 2.7651 | 34.3373 | 95.61% | 0 | 1 | 51.42% | 0% | 0 | 0.02055 | 11.2183 | 1.9496 | 0.44946 | Low | Low | Low | 1113 | 1023 | 0.23053 | 205.3677
SONOMA 1102118 | SONOMA 1102 | SONOMA | 5.4359 | 22.1228 | 81.08% | 2 | 7 | 71.73% | 100% | 0 | 0.11084 | 1 | 4.0423 | 0.44806 | High | High | High | 1114 | 1256 | 0.11084 | 204.9182
TASSAJARA 2113MR276 | TASSAJARA 2113 | DIABLO | 3.6023 | 62.8969 | 34.15% | 1 | 2 | 92.48% | 100% | 0 | 0.13782 | 1 | 3.251 | 0.44804 | High | High | High | 1115 | 1175 | 0.13782 | 204.4701
PLACERVILLE 210619552 | PLACERVILLE 2106 | SIERRA | 21.1288 | 10.9472 | 81.54% | 2 | 6 | 100% | 88.4% | 1 | 0.17549 | 1 | 2.5401 | 0.44577 | High | High | Medium | 1116 | 1102 | 0.17549 | 204.0221
REDBUD 11022013 | REDBUD 1102 | HUMBOLDT | 0.11285 | 35.1068 | 100% | 0 | 0 | 2.449% | 0% | 0 | 0.01294 | 11.2183 | 3.0608 | 0.44433 | Low | Low | Medium | 1117 | 1156 | 0.14517 | 203.5763
TASSAJARA 2112CB | TASSAJARA 2112 | DIABLO | 0.3541 | 10 | 9.426% | 1 | 0 | 26.89% | 0% | 0 | 0.0076765 | 14.9507 | 3.8616 | 0.4432 | Low | Low | High | 1118 | 1238 | 0.11477 | 203.132
DEL MONTE 21043066 | DEL MONTE 2104 | CENTRAL COAST | 0.016196 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 11.2183 | 3.1116 | 0.44316 | Low | Low | High | 1119 | 1161 | 0.14242 | 202.6888
NEWBURG 11323425 | NEWBURG 1132 | HUMBOLDT | 0.9717 | 21.9962 | 41.93% | 1 | 0 | 64.08% | 0% | 0 | 0.013757 | 11.2183 | 2.8658 | 0.44227 | Low | Low | Medium | 1120 | 1138 | 0.15433 | 202.2456
BIG BASIN 110276752 | BIG BASIN 1102 | CENTRAL COAST | 2.6798 | 26.5426 | 60.49% | 5 | 8 | 100% | 100% | 0 | 0.1665 | 1 | 2.6319 | 0.43821 | High | High | Medium | 1121 | 1120 | 0.1665 | 201.8034
WILLOW CREEK 11014904 | WILLOW CREEK 1101 | HUMBOLDT | 18.7302 | 84.4323 | 100% | 25 | 5 | 100% | 99.66% | 0 | 0.33351 | 1 | 1.3113 | 0.43732 | High | High | Low | 1122 | 933 | 0.33351 | 201.3652
PARADISE 11032488 | PARADISE 1103 | NORTH VALLEY | 3.2215 | 10 | 53.79% | 1 | 2 | 100% | 95.34% | 0 | 0.11569 | 1 | 3.766 | 0.43568 | High | High | High | 1123 | 1234 | 0.11569 | 200.9278
NARROWS 210248484 | NARROWS 2102 | SIERRA | 41.4937 | 26.7261 | 86.16% | 7 | 18 | 100% | 0% | 0 | 0.16958 | 1 | 2.5572 | 0.43366 | High | High | Medium | 1124 | 1112 | 0.16958 | 200.4922
MORAGA 1101CB | MORAGA 1101 | DIABLO | 6.145 | 55.6277 | 5.196% | 2 | 13 | 81.97% | 88.05% | 0 | 0.12886 | 1 | 3.3628 | 0.43333 | High | High | High | 1125 | 1203 | 0.12886 | 200.0585
VIEJO 22029118 | VIEJO 2202 | CENTRAL COAST | 0.57077 | 10 | 0.8969% | 1 | 0 | 19.02% | 0% | 0 | 0.0066199 | 14.9507 | 4.29 | 0.42459 | Low | Low | High | 1126 | 1298 | 0.098972 | 199.6252
MIDDLETOWN 1101612 | MIDDLETOWN 1101 | HUMBOLDT | 3.8703 | 82.8475 | 40.87% | 13 | 3 | 100% | 100% | 1 | 0.19998 | 1 | 2.1199 | 0.42394 | High | High | Low | 1127 | 1057 | 0.19998 | 199.2006
GIRVAN 11011636 | GIRVAN 1101 | NORTH VALLEY | 16.6216 | 29.0593 | 66.7% | 0 | 3 | 90.3% | 84.26% | 1 | 0.19797 | 1 | 2.1383 | 0.42331 | High | High | Low | 1128 | 1061 | 0.19797 | 198.7766
TIVY VALLEY 110737522 | TIVY VALLEY 1107 | FRESNO | 0.51792 | 52.3595 | 87.8% | 0 | 0 | 16.67% | 0% | 0 | 0.017278 | 11.2183 | 2.1794 | 0.42243 | Low | Low | Low | 1129 | 1075 | 0.19383 | 198.3533
REDBUD 11021212 | REDBUD 1102 | HUMBOLDT | 0.436 | 23.3209 | 21.35% | 0 | 1 | 11.49% | 0% | 0 | 0.0070167 | 19.9979 | 3.0081 | 0.42209 | Low | Low | Medium | 1130 | 1167 | 0.14032 | 197.9309
GIRVAN 11029012 | GIRVAN 1102 | NORTH VALLEY | 15.986 | 25.3548 | 93.5% | 4 | 4 | 100% | 96.14% | 1 | 0.18146 | 1 | 2.3257 | 0.42202 | High | High | Medium | 1131 | 1090 | 0.18146 | 197.5088
HALF MOON BAY 1101CB | HALF MOON BAY 1101 | PENINSULA | 8.298 | 59.005 | 12.7% | 3 | 2 | 59.24% | 75.84% | 1 | 0.11209 | 1 | 3.754 | 0.42078 | High | High | High | 1132 | 1248 | 0.11209 | 197.0868
SANTA MARIA 1108M80 | SANTA MARIA 1108 | LOS PADRES | 58.3414 | 79.2858 | 99.51% | 1 | 8 | 100% | 61.18% | 1 | 0.20649 | 1 | 2.0334 | 0.41988 | High | High | Low | 1133 | 1049 | 0.20649 | 196.666
MARIPOSA 21021960 | MARIPOSA 2102 | YOSEMITE | 24.6612 | 47.7521 | 99.87% | 3 | 23 | 100% | 69.1% | 1 | 0.25188 | 1 | 1.666 | 0.41964 | High | High | Low | 1134 | 999 | 0.25188 | 196.2461
FROGTOWN 170274648 | FROGTOWN 1702 | STOCKTON | 0.21722 | 10 | 30.03% | 0 | 0 | 4.115% | 0% | 0 | 0.0081651 | 26.5534 | 1.9245 | 0.41726 | Low | Low | Low | 1135 | 1035 | 0.21681 | 195.8265
SILVERADO 2102636 | SILVERADO 2102 | NORTH BAY | 3.9682 | 44.4482 | 89.35% | 2 | 0 | 70.53% | 80.46% | 1 | 0.11193 | 1 | 3.6989 | 0.41401 | High | High | High | 1136 | 1249 | 0.11193 | 195.4092
BIG BASIN 110296986 | BIG BASIN 1102 | CENTRAL COAST | 5.8731 | 33.0475 | 64.84% | 22 | 1 | 100% | 100% | 0 | 0.16999 | 1 | 2.3974 | 0.40753 | High | High | Medium | 1137 | 1110 | 0.16999 | 194.9952
NOTRE DAME 11042028 | NOTRE DAME 1104 | NORTH VALLEY | 10.9017 | 45.9089 | 89% | 0 | 3 | 100% | 100% | 0 | 0.15694 | 1 | 2.5912 | 0.40666 | High | High | Medium | 1138 | 1135 | 0.15694 | 194.5877
AUBERRY 1101R319 | AUBERRY 1101 | FRESNO | 21.0846 | 48.2226 | 98.48% | 8 | 8 | 100% | 93.05% | 1 | 0.30543 | 1 | 1.3298 | 0.40617 | High | High | Low | 1139 | 959 | 0.30543 | 194.181
BIG BASIN 11028403 | BIG BASIN 1102 | CENTRAL COAST | 4.9235 | 33.659 | 85.64% | 2 | 1 | 100% | 100% | 0 | 0.15781 | 1 | 2.5682 | 0.40531 | High | High | Medium | 1140 | 1133 | 0.15781 | 193.7749
OREGON TRAIL 110335002 | OREGON TRAIL 1103 | NORTH VALLEY | 57.2663 | 26.028 | 93.47% | 4 | 13 | 100% | 0% | 0 | 0.19614 | 1 | 2.0644 | 0.40491 | High | High | Low | 1141 | 1066 | 0.19614 | 193.3696
CAMP EVERS 210612840 | CAMP EVERS 2106 | CENTRAL COAST | 4.0602 | 32.5066 | 59.36% | 5 | 0 | 100% | 100% | 0 | 0.13232 | 1 | 3.057 | 0.40448 | High | High | Medium | 1142 | 1191 | 0.13232 | 192.9647
GREEN VALLEY 21011645 | GREEN VALLEY 2101 | CENTRAL COAST | 0.48374 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 3.1056 | 0.40442 | High | High | High | 1143 | 1197 | 0.13022 | 192.5602
CLARKSVILLE 210319572 | CLARKSVILLE 2103 | SIERRA | 33.5123 | 41.8595 | 99.97% | 3 | 7 | 77.35% | 59.23% | 1 | 0.15209 | 1 | 2.6524 | 0.40341 | High | High | Medium | 1144 | 1144 | 0.15209 | 192.1558
CAMP EVERS 210310946 | CAMP EVERS 2103 | CENTRAL COAST | 5.6138 | 10 | 43.31% | 5 | 3 | 66.4% | 100% | 0 | 0.14518 | 1 | 2.7721 | 0.40244 | High | High | Medium | 1145 | 1155 | 0.14518 | 191.7523
VIEJO 22019704 | VIEJO 2201 | CENTRAL COAST | 1.0374 | 10 | 50.89% | 1 | 2 | 40.52% | 0% | 0 | 0.011266 | 11.2183 | 3.1826 | 0.40224 | Low | Low | High | 1146 | 1212 | 0.12638 | 191.3499
PARADISE 11042034 | PARADISE 1104 | NORTH VALLEY | 10.6989 | 15.2166 | 88.93% | 0 | 6 | 94.14% | 86.31% | 1 | 0.10808 | 1 | 3.7081 | 0.40077 | High | High | High | 1147 | 1265 | 0.10808 | 190.9477
SUNOL 1101MR299 | SUNOL 1101 | MISSION | 4.988 | 63.7936 | 27.4% | 3 | 3 | 100% | 100% | 0 | 0.16428 | 1 | 2.4384 | 0.40057 | High | High | Medium | 1148 | 1122 | 0.16428 | 190.5469
SAN RAFAEL 110839156 | SAN RAFAEL 1108 | NORTH BAY | 3.0298 | 11.0786 | 11.96% | 3 | 10 | 63.16% | 96.57% | 0 | 0.083717 | 1 | 4.762 | 0.39866 | High | High | High | 1149 | 1373 | 0.083717 | 190.1463
LOS GATOS 110760092 | LOS GATOS 1107 | DE ANZA | 9.7412 | 27.0068 | 22.28% | 14 | 2 | 100% | 100% | 0 | 0.17816 | 1 | 2.2097 | 0.39367 | High | High | Low | 1150 | 1096 | 0.17816 | 189.7477
DUNBAR 110147964 | DUNBAR 1101 | SONOMA | 6.3806 | 61.1795 | 83.1% | 1 | 6 | 83.19% | 93% | 0 | 0.13803 | 1 | 2.8326 | 0.39097 | High | High | Medium | 1151 | 1173 | 0.13803 | 189.354
PLACERVILLE 21067522 | PLACERVILLE 2106 | SIERRA | 67.5844 | 32.7125 | 84.62% | 19 | 16 | 100% | 11.4% | 0 | 0.1992 | 1 | 1.9612 | 0.39066 | High | High | Low | 1152 | 1058 | 0.1992 | 188.963
CLARKSVILLE 2105CB | CLARKSVILLE 2105 | SIERRA | 0.54433 | 10 | 0% | 0 | 0 | 45.8% | 0% | 0 | 0.0074141 | 14.9507 | 3.5177 | 0.38992 | Low | Low | High | 1153 | 1255 | 0.11085 | 188.5724
ZACA 1102Y54 | ZACA 1102 | LOS PADRES | 34.3968 | 50.4695 | 82.24% | 0 | 23 | 99.37% | 51.02% | 1 | 0.23948 | 1 | 1.6279 | 0.38985 | High | High | Low | 1154 | 1013 | 0.23948 | 188.1824
DOBBINS 11011264 | DOBBINS 1101 | SIERRA | 34.6636 | 46.9951 | 96.43% | 5 | 9 | 99.16% | 60.09% | 0 | 0.17584 | 1 | 2.216 | 0.38966 | High | High | Low | 1155 | 1100 | 0.17584 | 187.7926
PLACERVILLE 210619732 | PLACERVILLE 2106 | SIERRA | 9.0659 | 10 | 43.47% | 3 | 13 | 100% | 82.12% | 1 | 0.12525 | 1 | 3.1037 | 0.38874 | High | High | High | 1156 | 1213 | 0.12525 | 187.4029
MONTE RIO 11131067 | MONTE RIO 1113 | SONOMA | 0.80536 | 36.8006 | 36.57% | 2 | 0 | 100% | 100% | 0 | 0.12505 | 1 | 3.1062 | 0.38843 | High | High | High | 1157 | 1214 | 0.12505 | 187.0142
FELTON 0401CB | FELTON 0401 | CENTRAL COAST | 2.2987 | 17.6192 | 4.577% | 5 | 0 | 89.41% | 100% | 0 | 0.093336 | 1 | 4.1567 | 0.38797 | High | High | High | 1158 | 1321 | 0.093336 | 186.6258
MONROE 210392868 | MONROE 2103 | SONOMA | 0.69734 | 10 | 73.35% | 0 | 3 | 74% | 100% | 0 | 0.11412 | 1 | 3.3766 | 0.38534 | High | High | High | 1159 | 1242 | 0.11412 | 186.2378
VINEYARD 2107MR332 | VINEYARD 2107 | MISSION | 0.086505 | 10 | 100% | 1 | 0 | 2.473% | 0% | 0 | 0.011067 | 11.2183 | 3.0685 | 0.38096 | Low | Low | Medium | 1160 | 1217 | 0.12415 | 185.8524
OAKLAND K 1103CR188 | OAKLAND K 1103 | EAST BAY | 3.5811 | 10 | 48.05% | 3 | 7 | 100% | 62.42% | 0 | 0.086851 | 1 | 4.3746 | 0.37994 | High | High | High | 1161 | 1352 | 0.086851 | 185.4715
REDBUD 1101454 | REDBUD 1101 | HUMBOLDT | 5.6455 | 80.3546 | 100% | 0 | 0 | 100% | 100% | 0 | 0.19502 | 1 | 1.9323 | 0.37684 | High | High | Low | 1162 | 1068 | 0.19502 | 185.0915
PAUL SWEET 21068091 | PAUL SWEET 2106 | CENTRAL COAST | 6.0187 | 18.6502 | 32.26% | 14 | 1 | 100% | 100% | 0 | 0.12726 | 1 | 2.9537 | 0.37589 | High | High | Medium | 1163 | 1210 | 0.12726 | 184.7147
ARBUCKLE 110447282 | ARBUCKLE 1104 | SACRAMENTO | 2.0417 | 83.3119 | 73.53% | 0 | 0 | 17.21% | 0% | 0 | 0.016706 | 14.9507 | 1.4871 | 0.37144 | Low | Low | Low | 1164 | 1002 | 0.24977 | 184.3388
CLAYTON 2215CB | CLAYTON 2215 | DIABLO | 2.6028 | 67.9246 | 0.2184% | 0 | 2 | 23.77% | 0% | 0 | 0.0092153 | 11.2183 | 3.5872 | 0.37085 | Low | Low | High | 1165 | 1283 | 0.10338 | 183.9674
CAMP EVERS 210611006 | CAMP EVERS 2106 | CENTRAL COAST | 2.073 | 10 | 22.12% | 2 | 1 | 100% | 100% | 0 | 0.086223 | 1 | 4.2738 | 0.3685 | High | High | High | 1166 | 1357 | 0.086223 | 183.5965
ALTO 1124428 | ALTO 1124 | NORTH BAY | 4.8403 | 17.2865 | 1.418% | 0 | 4 | 81.37% | 100% | 0 | 0.075976 | 1 | 4.8386 | 0.36762 | High | High | High | 1167 | 1434 | 0.075976 | 183.228
PUEBLO 1104 | PUEBLO 1104 | NORTH BAY | 0.072037 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 11.2183 | 2.568 | 0.36574 | Low | Low | Medium | 1168 | 1161 | 0.14242 | 182.8604
TAMARACK 1101CB | TAMARACK 1101 | SIERRA | 16.4477 | 32.6722 | 67.46% | 23 | 13 | 91.62% | 0% | 0 | 0.38292 | 1 | 0.95136 | 0.36429 | High | High | Low | 1169 | 903 | 0.38292 | 182.4947
CLAYTON 2212Y504R | CLAYTON 2212 | DIABLO | 11.7508 | 28.9647 | 42.97% | 1 | 6 | 100% | 29.53% | 1 | 0.10152 | 1 | 3.5819 | 0.36362 | High | High | High | 1170 | 1289 | 0.10152 | 182.1304
SAN LUIS OBISPO 1108V92 | SAN LUIS OBISPO 1108 | LOS PADRES | 0.46755 | 10 | 74.28% | 0 | 0 | 6.559% | 0% | 0 | 0.0092193 | 11.2183 | 3.5147 | 0.36351 | Low | Low | High | 1171 | 1282 | 0.10343 | 181.7667
BIG BEND 1101641808 | BIG BEND 1101 | NORTH VALLEY | 24.9976 | 36.2263 | 100% | 6 | 10 | 95.85% | 52.55% | 1 | 0.15307 | 1 | 2.3707 | 0.36288 | High | High | Medium | 1172 | 1142 | 0.15307 | 181.4032
PARADISE 11032486 | PARADISE 1103 | NORTH VALLEY | 6.2013 | 10 | 48.71% | 9 | 1 | 91.06% | 100% | 0 | 0.093491 | 1 | 3.8754 | 0.36232 | High | High | High | 1173 | 1320 | 0.093491 | 181.0404
BIG RIVER 1101952 | BIG RIVER 1101 | HUMBOLDT | 16.8032 | 42.8498 | 13.29% | 16 | 25 | 100% | 0% | 0 | 0.19578 | 1 | 1.848 | 0.36179 | High | High | Low | 1174 | 1067 | 0.19578 | 180.678
MIRABEL 110257840 | MIRABEL 1102 | SONOMA | 2.5892 | 51.5846 | 26.12% | 5 | 1 | 100% | 100% | 0 | 0.11884 | 1 | 3.0442 | 0.36177 | High | High | Medium | 1175 | 1227 | 0.11884 | 180.3162
CLARKSVILLE 2110CB | CLARKSVILLE 2110 | SIERRA | 0.17765 | 10 | 0% | 0 | 0 | 9.133% | 0% | 0 | 0.005146 | 19.9979 | 3.4965 | 0.35982 | Low | Low | High | 1176 | 1286 | 0.10291 | 179.9545
CLOVERDALE 1102 | CLOVERDALE 1102 | SONOMA | 0.015567 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 1 | 1.7488 | 0.35954 | High | High | Low | 1177 | 1050 | 0.20559 | 179.5947
CENTERVILLE 11011243 | CENTERVILLE 1101 | NORTH VALLEY | 5.1549 | 10 | 65.95% | 0 | 5 | 100% | 100% | 0 | 0.11154 | 1 | 3.2195 | 0.35911 | High | High | High | 1178 | 1251 | 0.11154 | 179.2351
STANISLAUS 17017144 | STANISLAUS 1701 | YOSEMITE | 4.4552 | 18.8557 | 79.41% | 0 | 8 | 100% | 0% | 0 | 0.10581 | 1 | 3.3929 | 0.359 | High | High | High | 1179 | 1271 | 0.10581 | 178.876
OLEMA 1101416 | OLEMA 1101 | NORTH BAY | 15.842 | 82.0626 | 5.587% | 9 | 6 | 97.77% | 72.25% | 1 | 0.13235 | 1 | 2.6915 | 0.35623 | High | High | Medium | 1180 | 1190 | 0.13235 | 178.517
MARIPOSA 210237282 | MARIPOSA 2102 | YOSEMITE | 48.8925 | 28.6255 | 92.59% | 4 | 51 | 82.09% | 39.78% | 0 | 0.20818 | 1 | 1.7072 | 0.35541 | High | High | Low | 1181 | 1044 | 0.20818 | 178.1608
MONTE RIO 11135026 | MONTE RIO 1113 | SONOMA | 1.8374 | 45.7535 | 31.21% | 4 | 1 | 100% | 100% | 0 | 0.1045 | 1 | 3.3938 | 0.35465 | High | High | High | 1182 | 1277 | 0.1045 | 177.8054
BELL 1107CB | BELL 1107 | SIERRA | 0.084936 | 10 | 100% | 0 | 1 | 2.211% | 0% | 0 | 0.011123 | 11.2183 | 2.8137 | 0.35111 | Low | Low | Medium | 1183 | 1215 | 0.12478 | 177.4507
PUEBLO 210378504 | PUEBLO 2103 | NORTH BAY | 7.9718 | 44.4313 | 84.9% | 7 | 4 | 65.86% | 87.65% | 1 | 0.11699 | 1 | 3.0008 | 0.35106 | High | High | Medium | 1184 | 1231 | 0.11699 | 177.0996
SANTA ROSA A 1107CB | SANTA ROSA A 1107 | SONOMA | 2.9541 | 10 | 71.96% | 6 | 3 | 60.44% | 100% | 0 | 0.095269 | 1 | 3.6663 | 0.34929 | High | High | High | 1185 | 1314 | 0.095269 | 176.7485
DUNBAR 1101416 | DUNBAR 1101 | SONOMA | 2.8528 | 67.3035 | 61.83% | 0 | 0 | 84.79% | 100% | 0 | 0.13696 | 1 | 2.5295 | 0.34643 | High | High | Medium | 1186 | 1178 | 0.13696 | 176.3993
DOBBINS 110169722 | DOBBINS 1101 | SIERRA | 6.6325 | 10 | 87.38% | 1 | 4 | 100% | 93.4% | 1 | 0.13241 | 1 | 2.5845 | 0.34221 | High | High | Medium | 1187 | 1189 | 0.13241 | 176.0528
HIGGINS 11102408 | HIGGINS 1110 | SIERRA | 35.5285 | 10.5577 | 99.97% | 6 | 7 | 100% | 0% | 0 | 0.12315 | 1 | 2.7776 | 0.34207 | High | High | Medium | 1188 | 1219 | 0.12315 | 175.7106
FULTON 1107 | FULTON 1107 | SONOMA | 0.4544 | 32.639 | 77.88% | 0 | 1 | 100% | 100% | 1 | 0.14528 | 1 | 2.3437 | 0.34049 | High | High | Medium | 1189 | 1153 | 0.14528 | 175.3685
EL CERRITO G 111257953 | EL CERRITO G 1112 | EAST BAY | 0.7567 | 10 | 0% | 0 | 1 | 100% | 100% | 0 | 0.062783 | 1 | 5.378 | 0.33765 | High | High | High | 1190 | 1534 | 0.062783 | 175.028
MIRABEL 1102841 | MIRABEL 1102 | SONOMA | 0.78827 | 21.9552 | 18.73% | 8 | 3 | 100% | 100% | 0 | 0.11386 | 1 | 2.9577 | 0.33677 | High | High | Medium | 1191 | 1243 | 0.11386 | 174.6904
BRYANT 0402CB | BRYANT 0402 | DIABLO | 1.2282 | 10 | 3.772% | 0 | 5 | 15.75% | 0% | 0 | 0.0062931 | 14.9507 | 3.572 | 0.33607 | Low | Low | High | 1192 | 1318 | 0.094086 | 174.3536
MARIPOSA 2101439030 | MARIPOSA 2101 | YOSEMITE | 19.5499 | 36.6756 | 99.56% | 7 | 29 | 100% | 98.19% | 0 | 0.28602 | 1 | 1.1748 | 0.33603 | High | High | Low | 1193 | 967 | 0.28602 | 174.0176
CAMP EVERS 210512590 | CAMP EVERS 2105 | CENTRAL COAST | 4.822 | 13.1146 | 60.2% | 9 | 1 | 87.03% | 85.9% | 0 | 0.091772 | 1 | 3.6609 | 0.33597 | High | High | High | 1194 | 1327 | 0.091772 | 173.6815
ALTO 11252243 | ALTO 1125 | NORTH BAY | 2.9262 | 21.9292 | 59.4% | 1 | 4 | 100% | 22.94% | 0 | 0.085029 | 1 | 3.926 | 0.33382 | High | High | High | 1195 | 1363 | 0.085029 | 173.3456
GABILAN 1101579969 | GABILAN 1101 | CENTRAL COAST | 4.2047 | 48.3297 | 40.21% | 0 | 0 | 62.81% | 0% | 0 | 0.01579 | 11.2183 | 1.8809 | 0.33318 | Low | Low | Low | 1196 | 1098 | 0.17714 | 173.0117
SAN JOAQUIN #3 11035100 | SAN JOAQUIN #3 1103 | YOSEMITE | 26.246 | 20.2846 | 88.04% | 8 | 29 | 100% | 82.8% | 0 | 0.25116 | 1 | 1.3193 | 0.33134 | High | High | Low | 1197 | 1001 | 0.25116 | 172.6786
HARTLEY 1101471 | HARTLEY 1101 | HUMBOLDT | 0.38585 | 10 | 33.51% | 0 | 1 | 31.01% | 0% | 0 | 0.0085975 | 14.9507 | 2.5669 | 0.32994 | Low | Low | Medium | 1198 | 1205 | 0.12854 | 172.3472
SAN RAFAEL 1107CB | SAN RAFAEL 1107 | NORTH BAY | 4.2653 | 10 | 28.65% | 2 | 4 | 53.65% | 97.72% | 0 | 0.077391 | 1 | 4.2548 | 0.32928 | High | High | High | 1199 | 1419 | 0.077391 | 172.0173
WILLITS 1103966 | WILLITS 1103 | HUMBOLDT | 1.3235 | 20.8407 | 41.93% | 0 | 1 | 57.92% | 0% | 0 | 0.012942 | 11.2183 | 2.2623 | 0.32845 | Low | Low | Medium | 1200 | 1154 | 0.14519 | 171.688
SHINGLE SPRINGS 211051790 | SHINGLE SPRINGS 2110 | SIERRA | 8.0868 | 16.0955 | 60.72% | 1 | 8 | 93.48% | 72.08% | 0 | 0.10718 | 1 | 3.0513 | 0.32703 | High | High | Medium | 1201 | 1268 | 0.10718 | 171.3595
PENNGROVE 1101554 | PENNGROVE 1101 | SONOMA | 0.80578 | 23.6637 | 31.41% | 1 | 1 | 6.241% | 0% | 0 | 0.0073444 | 14.9507 | 2.9765 | 0.32683 | Low | Low | Medium | 1202 | 1260 | 0.1098 | 171.0325
HALF MOON BAY 11018902 | HALF MOON BAY 1101 | PENINSULA | 14.8934 | 73.1287 | 41.51% | 11 | 3 | 82.58% | 40.17% | 0 | 0.097706 | 1 | 3.3332 | 0.32568 | High | High | High | 1203 | 1302 | 0.097706 | 170.7057
CALPINE 1146CB | CALPINE 1146 | SONOMA | 3.8475 | 90.2876 | 70.72% | 0 | 0 | 100% | 100% | 0 | 0.16919 | 1 | 1.9173 | 0.32438 | High | High | Low | 1204 | 1113 | 0.16919 | 170.38
CENTERVILLE 11012592 | CENTERVILLE 1101 | NORTH VALLEY | 6.3933 | 51.1304 | 7.659% | 2 | 0 | 100% | 100% | 0 | 0.098005 | 1 | 3.2954 | 0.32296 | High | High | High | 1205 | 1301 | 0.098005 | 170.0556
DIAMOND SPRINGS 110519910 | DIAMOND SPRINGS 1105 | SIERRA | 20.7681 | 27.6002 | 62.16% | 0 | 7 | 100% | 83.55% | 0 | 0.1574 | 1 | 2.0452 | 0.32192 | High | High | Low | 1206 | 1134 | 0.1574 | 169.7327
PASO ROBLES 1104P02 | PASO ROBLES 1104 | LOS PADRES | 0.077403 | 10 | 100% | 0 | 0 | 1.071% | 0% | 0 | 0.010772 | 14.9507 | 1.9918 | 0.32079 | Low | Low | Low | 1207 | 1127 | 0.16105 | 169.4107
CLARK ROAD 11022068 | CLARK ROAD 1102 | NORTH VALLEY | 10.7164 | 15.0462 | 99.79% | 0 | 2 | 100% | 90.22% | 1 | 0.13587 | 1 | 2.3575 | 0.32031 | High | High | Medium | 1208 | 1180 | 0.13587 | 169.09
BERKELEY F 1105BR100 | BERKELEY F 1105 | EAST BAY | 0.38346 | 10 | 26.17% | 0 | 2 | 14.66% | 0% | 0 | 0.0070264 | 11.2183 | 4.0468 | 0.31898 | Low | Low | High | 1209 | 1408 | 0.078824 | 168.7696
PUEBLO 1105696 | PUEBLO 1105 | NORTH BAY | 20.5418 | 62.3545 | 78.14% | 5 | 4 | 69.81% | 0% | 0 | 0.11569 | 1 | 2.755 | 0.31872 | High | High | Medium | 1210 | 1235 | 0.11569 | 168.4507
VACAVILLE 111112342 | VACAVILLE 1111 | SACRAMENTO | 0.015645 | 10 | 0% | 0 | 0 | 1.482% | 0% | 0 | 0.004768 | 19.9979 | 3.3367 | 0.31815 | Low | Low | High | 1211 | 1313 | 0.095349 | 168.1319
PARADISE 110317711 | PARADISE 1103 | NORTH VALLEY | 6.5808 | 11.9806 | 85.8% | 3 | 1 | 100% | 51.08% | 0 | 0.087993 | 1 | 3.594 | 0.31625 | High | High | High | 1212 | 1344 | 0.087993 | 167.8138
HARRIS 1109700 | HARRIS 1109 | HUMBOLDT | 13.0569 | 19.3799 | 29.7% | 17 | 20 | 44.54% | 0% | 0 | 0.086853 | 1 | 3.6202 | 0.31443 | High | High | High | 1213 | 1351 | 0.086853 | 167.4975
PARADISE 110439216 | PARADISE 1104 | NORTH VALLEY | 2.1396 | 10 | 44.98% | 1 | 0 | 59.38% | 100% | 0 | 0.07729 | 1 | 4.0674 | 0.31437 | High | High | High | 1214 | 1420 | 0.07729 | 167.1831
LAYTONVILLE 1101518 | LAYTONVILLE 1101 | HUMBOLDT | 1.7269 | 84.7584 | 100% | 0 | 1 | 7.655% | 0% | 0 | 0.02214 | 26.5534 | 0.53271 | 0.31317 | Medium | Medium | Low | 1215 | 827 | 0.58789 | 166.8687
MARIPOSA 210110240 | MARIPOSA 2101 | YOSEMITE | 21.4769 | 25.894 | 68.07% | 2 | 22 | 100% | 66.83% | 0 | 0.13718 | 1 | 2.2737 | 0.3119 | High | High | Medium | 1216 | 1177 | 0.13718 | 166.5556
SHINGLE SPRINGS 210913322 | SHINGLE SPRINGS 2109 | SIERRA | 41.4342 | 33.754 | 99.99% | 7 | 13 | 100% | 26.15% | 1 | 0.22465 | 1 | 1.3879 | 0.3118 | High | High | Low | 1217 | 1026 | 0.22465 | 166.2437
CURTIS 17026008 | CURTIS 1702 | YOSEMITE | 17.4763 | 49.3908 | 89.43% | 4 | 7 | 100% | 47.18% | 0 | 0.095869 | 1 | 3.2494 | 0.31152 | High | High | High | 1218 | 1309 | 0.095869 | 165.9319
COARSEGOLD 210210330 | COARSEGOLD 2102 | YOSEMITE | 9.5583 | 29.5023 | 99.75% | 4 | 3 | 100% | 94.16% | 0 | 0.20649 | 1 | 1.5084 | 0.31146 | High | High | Low | 1219 | 1048 | 0.20649 | 165.6204
RED BLUFF 1104CB | RED BLUFF 1104 | NORTH VALLEY | 2.0518 | 10 | 96.16% | 0 | 0 | 19.48% | 0% | 0 | 0.012529 | 11.2183 | 2.2135 | 0.31112 | Low | Low | Low | 1220 | 1166 | 0.14056 | 165.3089
CLARK ROAD 11022582 | CLARK ROAD 1102 | NORTH VALLEY | 20.3761 | 33.4275 | 100% | 2 | 6 | 97.24% | 8.705% | 1 | 0.10279 | 1 | 3.0257 | 0.311 | High | High | Medium | 1221 | 1287 | 0.10279 | 164.9978
CURTIS 17039210 | CURTIS 1703 | YOSEMITE | 23.0078 | 62.9555 | 99.96% | 11 | 7 | 100% | 0% | 0 | 0.11179 | 1 | 2.775 | 0.3102 | High | High | Medium | 1222 | 1250 | 0.11179 | 164.6868
LLAGAS 210740407 | LLAGAS 2107 | SAN JOSE | 4.4461 | 62.3794 | 79.11% | 0 | 0 | 69.99% | 65.8% | 1 | 0.080349 | 1 | 3.8574 | 0.30994 | High | High | High | 1223 | 1394 | 0.080349 | 164.3766
GRASS VALLEY 11032180 | GRASS VALLEY 1103 | SIERRA | 44.2075 | 22.3739 | 98.77% | 3 | 16 | 100% | 0% | 0 | 0.11816 | 1 | 2.6203 | 0.30961 | High | High | Medium | 1224 | 1228 | 0.11816 | 164.0666
BEAR VALLEY 21059560 | BEAR VALLEY 2105 | YOSEMITE | 36.2873 | 45.8774 | 99.97% | 7 | 2 | 100% | 13.33% | 1 | 0.13437 | 1 | 2.3028 | 0.30942 | High | High | Medium | 1225 | 1184 | 0.13437 | 163.757
HALF MOON BAY 110148868 | HALF MOON BAY 1101 | PENINSULA | 1.1515 | 26.9273 | 98.35% | 0 | 1 | 38.91% | 72.96% | 0 | 0.06326 | 1 | 4.8763 | 0.30847 | High | High | High | 1226 | 1529 | 0.06326 | 163.4476
SWIFT 2110XR254 | SWIFT 2110 | SAN JOSE | 24.8145 | 55.7178 | 60.2% | 2 | 3 | 100% | 0% | 0 | 0.084233 | 1 | 3.6541 | 0.30779 | High | High | High | 1227 | 1369 | 0.084233 | 163.1391
CALPINE 1146400 | CALPINE 1146 | SONOMA | 3.1435 | 89.9771 | 73.48% | 0 | 0 | 100% | 100% | 0 | 0.17211 | 1 | 1.7847 | 0.30717 | High | High | Low | 1228 | 1108 | 0.17211 | 162.8313
PARADISE 11032558 | PARADISE 1103 | NORTH VALLEY | 2.3505 | 10 | 33.28% | 3 | 2 | 78.43% | 100% | 0 | 0.079398 | 1 | 3.8466 | 0.30541 | High | High | High | 1229 | 1405 | 0.079398 | 162.5242
BOLINAS 110137034 | BOLINAS 1101 | NORTH BAY | 4.5303 | 84.6023 | 6.363% | 1 | 1 | 100% | 94.68% | 0 | 0.098509 | 1 | 3.0991 | 0.30529 | High | High | High | 1230 | 1300 | 0.098509 | 162.2188
SANTA ROSA A 110464565 | SANTA ROSA A 1104 | SONOMA | 0.80928 | 10 | 22.53% | 1 | 2 | 100% | 100% | 0 | 0.087105 | 1 | 3.4851 | 0.30357 | High | High | High | 1231 | 1350 | 0.087105 | 161.9135
SEACLIFF 040112946 | SEACLIFF 0401 | CENTRAL COAST | 2.6944 | 41.521 | 88.42% | 0 | 1 | 83.31% | 77.78% | 0 | 0.092179 | 1 | 3.282 | 0.30253 | High | High | High | 1232 | 1326 | 0.092179 | 161.6099
PARADISE 11042470 | PARADISE 1104 | NORTH VALLEY | 5.1264 | 10.5174 | 41.48% | 3 | 8 | 44.97% | 100% | 0 | 0.069868 | 1 | 4.3221 | 0.30197 | High | High | High | 1233 | 1472 | 0.069868 | 161.3074
BANGOR 110182350 | BANGOR 1101 | NORTH VALLEY | 20.6431 | 13.6369 | 91.07% | 2 | 31 | 93.75% | 0% | 0 | 0.091535 | 1 | 3.298 | 0.30188 | High | High | High | 1234 | 1329 | 0.091535 | 161.0054
SAN RAFAEL 11079532 | SAN RAFAEL 1107 | NORTH BAY | 0.83024 | 10 | 59.24% | 0 | 0 | 45.34% | 100% | 0 | 0.066016 | 1 | 4.5265 | 0.29882 | High | High | High | 1235 | 1507 | 0.066016 | 160.7035
WOODACRE 1101CB | WOODACRE 1101 | NORTH BAY | 2.7386 | 31.1084 | 27.17% | 14 | 8 | 96.75% | 56.15% | 0 | 0.068112 | 1 | 4.3841 | 0.29861 | High | High | High | 1236 | 1484 | 0.068112 | 160.4047
CAMP EVERS 210311056 | CAMP EVERS 2103 | CENTRAL COAST | 1.8179 | 16.722 | 18.6% | 7 | 3 | 97.69% | 100% | 0 | 0.083758 | 1 | 3.5617 | 0.29832 | High | High | High | 1237 | 1372 | 0.083758 | 160.1061
COARSEGOLD 210210610 | COARSEGOLD 2102 | YOSEMITE | 1.3639 | 10 | 100% | 0 | 1 | 100% | 100% | 0 | 0.13262 | 1 | 2.2478 | 0.29809 | High | High | Medium | 1238 | 1188 | 0.13262 | 159.8078
OAKHURST 110110090 | OAKHURST 1101 | YOSEMITE | 44.1093 | 32.6301 | 93.91% | 4 | 19 | 100% | 7.446% | 0 | 0.12831 | 1 | 2.3192 | 0.29759 | High | High | Medium | 1239 | 1208 | 0.12831 | 159.5097
SILVERADO 2105616 | SILVERADO 2105 | NORTH BAY | 7.7876 | 45.8077 | 54.02% | 4 | 6 | 42.79% | 95.93% | 0 | 0.097353 | 1 | 3.0537 | 0.29728 | High | High | Medium | 1240 | 1304 | 0.097353 | 159.2121
PETALUMA C 1109128 | PETALUMA C 1109 | SONOMA | 20.216 | 67.8419 | 37.87% | 1 | 18 | 85.88% | 0% | 0 | 0.1003 | 1 | 2.9612 | 0.29701 | High | High | Medium | 1241 | 1295 | 0.1003 | 158.9148
MORGAN HILL 2105XR176 | MORGAN HILL 2105 | SAN JOSE | 18.5618 | 37.9512 | 61.14% | 2 | 13 | 67.38% | 10.57% | 0 | 0.11466 | 1 | 2.5892 | 0.29688 | High | High | Medium | 1242 | 1240 | 0.11466 | 158.6178
BEN LOMOND 040116010 | BEN LOMOND 0401 | CENTRAL COAST | 1.6971 | 10 | 15.35% | 1 | 2 | 100% | 100% | 0 | 0.072945 | 1 | 4.0662 | 0.29661 | High | High | High | 1243 | 1449 | 0.072945 | 158.3209
SPRING GAP 1702693441 | SPRING GAP 1702 | YOSEMITE | 4.1995 | 35.8935 | 98.37% | 5 | 2 | 100% | 100% | 0 | 0.27702 | 1 | 1.0588 | 0.2933 | High | High | Low | 1244 | 971 | 0.27702 | 158.0243
PUEBLO 11041304 | PUEBLO 1104 | NORTH BAY | 19.9743 | 65.3191 | 45.92% | 2 | 4 | 100% | 0% | 0 | 0.10431 | 1 | 2.809 | 0.29302 | High | High | Medium | 1245 | 1280 | 0.10431 | 157.731
CAMP EVERS 210410442 | CAMP EVERS 2104 | CENTRAL COAST | 5.2532 | 33.0345 | 51.92% | 6 | 3 | 50.36% | 93.05% | 0 | 0.099232 | 1 | 2.9332 | 0.29106 | High | High | Medium | 1246 | 1297 | 0.099232 | 157.438
SAN RAFAEL 11081210 | SAN RAFAEL 1108 | NORTH BAY | 3.0269 | 13.7905 | 14.91% | 3 | 2 | 55.23% | 100% | 0 | 0.064455 | 1 | 4.5091 | 0.29063 | High | High | High | 1247 | 1521 | 0.064455 | 157.1469
GREENBRAE 11032371 | GREENBRAE 1103 | NORTH BAY | 0.40055 | 47.8608 | 0% | 1 | 4 | 90.05% | 100% | 0 | 0.078151 | 1 | 3.7079 | 0.28978 | High | High | High | 1248 | 1412 | 0.078151 | 156.8563
OAKLAND K 1101CR178 | OAKLAND K 1101 | EAST BAY | 0.32942 | 10 | 9.622% | 0 | 2 | 100% | 100% | 0 | 0.068955 | 1 | 4.1976 | 0.28945 | High | High | High | 1249 | 1478 | 0.068955 | 156.5665
SAN LUIS OBISPO 1107V02 | SAN LUIS OBISPO 1107 | LOS PADRES | 17.85 | 46.8397 | 49.77% | 4 | 7 | 97.96% | 39.87% | 0 | 0.12708 | 1 | 2.273 | 0.28886 | High | High | Medium | 1250 | 1211 | 0.12708 | 156.2771
SAN LUIS OBISPO 1107V62 | SAN LUIS OBISPO 1107 | LOS PADRES | 6.9341 | 31.5234 | 48.48% | 0 | 11 | 100% | 70.79% | 1 | 0.1315 | 1 | 2.1877 | 0.28768 | High | High | Low | 1251 | 1195 | 0.1315 | 155.9882
BIG BASIN 110210254 | BIG BASIN 1102 | CENTRAL COAST | 2.1303 | 79.74 | 23.5% | 0 | 1 | 100% | 100% | 1 | 0.11586 | 1 | 2.4798 | 0.28731 | High | High | Medium | 1252 | 1233 | 0.11586 | 155.7005
MIDDLETOWN 1103CB | MIDDLETOWN 1103 | HUMBOLDT | 0.052982 | 70.6148 | 0% | 0 | 0 | 32.86% | 0% | 0 | 0.009835 | 11.2183 | 2.601 | 0.28698 | Low | Low | Medium | 1253 | 1259 | 0.11033 | 155.4132
BANGOR 11011958 | BANGOR 1101 | NORTH VALLEY | 33.6731 | 10.1792 | 87.16% | 3 | 30 | 100% | 0% | 0 | 0.10317 | 1 | 2.7724 | 0.28603 | High | High | Medium | 1254 | 1284 | 0.10317 | 155.1262
COARSEGOLD 21025722 | COARSEGOLD 2102 | YOSEMITE | 1.9829 | 10 | 100% | 0 | 5 | 100% | 100% | 0 | 0.14258 | 1 | 2.0056 | 0.28595 | High | High | Low | 1255 | 1160 | 0.14258 | 154.8402
FITCH MOUNTAIN 1111CB | FITCH MOUNTAIN 1111 | SONOMA | 0.55902 | 10 | 52% | 0 | 0 | 3.182% | 0% | 0 | 0.0074291 | 14.9507 | 2.5563 | 0.28393 | Low | Low | Medium | 1256 | 1254 | 0.11107 | 154.5542
OAKLAND K 1104CR206 | OAKLAND K 1104 | EAST BAY | 1.7925 | 10 | 7.751% | 0 | 1 | 100% | 100% | 0 | 0.066653 | 1 | 4.2537 | 0.28352 | High | High | High | 1257 | 1500 | 0.066653 | 154.2703
BRUNSWICK 11067099 | BRUNSWICK 1106 | SIERRA | 7.5715 | 32.7231 | 90.35% | 0 | 3 | 100% | 52.26% | 0 | 0.1055 | 1 | 2.6802 | 0.28277 | High | High | Medium | 1258 | 1272 | 0.1055 | 153.9868
JESSUP 1103CB | JESSUP 1103 | NORTH VALLEY | 0.3876 | 22.4131 | 79.44% | 0 | 0 | 2.712% | 0% | 0 | 0.010068 | 11.2183 | 2.4954 | 0.28184 | Low | Low | Medium | 1259 | 1246 | 0.11295 | 153.704
PAUL SWEET 21025291 | PAUL SWEET 2102 | CENTRAL COAST | 3.3045 | 10 | 22.71% | 10 | 3 | 77.46% | 100% | 0 | 0.091104 | 1 | 3.0809 | 0.28068 | High | High | High | 1260 | 1334 | 0.091104 | 153.4222
MARIPOSA 21029590 | MARIPOSA 2102 | YOSEMITE | 36.36 | 19.6403 | 97.41% | 1 | 52 | 100% | 0% | 0 | 0.13645 | 1 | 2.0449 | 0.27902 | High | High | Low | 1261 | 1179 | 0.13645 | 153.1415
BIG BASIN 110212124 | BIG BASIN 1102 | CENTRAL COAST | 4.2617 | 10 | 33.1% | 2 | 2 | 100% | 100% | 0 | 0.1076 | 1 | 2.589 | 0.27858 | High | High | Medium | 1262 | 1267 | 0.1076 | 152.8625
OAKHURST 110310570 | OAKHURST 1103 | YOSEMITE | 9.7802 | 19.5863 | 100% | 0 | 5 | 100% | 83.62% | 0 | 0.13448 | 1 | 2.0684 | 0.27817 | High | High | Low | 1263 | 1183 | 0.13448 | 152.5839
NARROWS 21022220 | NARROWS 2102 | SIERRA | 27.523 | 12.681 | 87.5% | 7 | 17 | 97.87% | 0% | 0 | 0.084411 | 1 | 3.2946 | 0.2781 | High | High | High | 1264 | 1367 | 0.084411 | 152.3057
WEST POINT 1101CB | WEST POINT 1101 | STOCKTON | 4.7054 | 80.5028 | 15.54% | 1 | 1 | 100% | 100% | 0 | 0.11111 | 1 | 2.5021 | 0.27801 | High | High | Medium | 1265 | 1253 | 0.11111 | 152.0276
TASSAJARA 2104CB | TASSAJARA 2104 | DIABLO | 0.10747 | 10 | 0% | 0 | 1 | 9.092% | 0% | 0 | 0.0059985 | 11.2183 | 4.1264 | 0.27768 | Low | Low | High | 1266 | 1494 | 0.067293 | 151.7496
CURTIS 170510590 | CURTIS 1705 | YOSEMITE | 9.8062 | 25.1511 | 99.51% | 1 | 1 | 100% | 47.11% | 0 | 0.086282 | 1 | 3.2172 | 0.27758 | High | High | High | 1267 | 1355 | 0.086282 | 151.472
PAUL SWEET 2109CB | PAUL SWEET 2109 | CENTRAL COAST | 4.2704 | 10 | 67.66% | 4 | 1 | 34.14% | 43.22% | 0 | 0.068584 | 1 | 4.0374 | 0.2769 | High | High | High | 1268 | 1480 | 0.068584 | 151.1944
RIO DELL 1102CB | RIO DELL 1102 | HUMBOLDT | 0.14635 | 60 | 0% | 0 | 0 | 2.061% | 0% | 0 | 0.0067382 | 14.9507 | 2.7458 | 0.27662 | Low | Low | Medium | 1269 | 1292 | 0.10074 | 150.9175
CALISTOGA 1102769230 | CALISTOGA 1102 | NORTH BAY | 9.3152 | 56.0979 | 70.25% | 3 | 0 | 54.25% | 96.26% | 0 | 0.10199 | 1 | 2.7108 | 0.27647 | High | High | Medium | 1270 | 1288 | 0.10199 | 150.6409
DIAMOND SPRINGS 1103 | DIAMOND SPRINGS 1103 | SIERRA | 0.10469 | 10 | 100% | 0 | 0 | 70.96% | 100% | 0 | 0.10065 | 1 | 2.7444 | 0.27622 | High | High | Medium | 1271 | 1293 | 0.10065 | 150.3644
BELLEVUE 1102392 | BELLEVUE 1102 | SONOMA | 0.13708 | 10 | 0% | 0 | 0 | 2.019% | 0% | 0 | 0.0047936 | 19.9979 | 2.8755 | 0.27565 | Low | Low | Medium | 1272 | 1310 | 0.095862 | 150.0882
DRUM 11011602 | DRUM 1101 | SIERRA | 16.7313 | 80.5912 | 98.54% | 5 | 3 | 100% | 100% | 0 | 0.44264 | 1 | 0.6215 | 0.2751 | High | High | Low | 1273 | 875 | 0.44264 | 149.8125
CURTIS 17039330 | CURTIS 1703 | YOSEMITE | 41.1713 | 48.6933 | 100% | 9 | 13 | 100% | 41.49% | 1 | 0.1783 | 1 | 1.542 | 0.27494 | High | High | Low | 1274 | 1095 | 0.1783 | 149.5374
BEN LOMOND 04015400 | BEN LOMOND 0401 | CENTRAL COAST | 0.44316 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 4.4652 | 0.27487 | High | High | High | 1275 | 1542 | 0.061559 | 149.2625
OAKLAND X 1104CR101 | OAKLAND X 1104 | EAST BAY | 0.017651 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 4.4296 | 0.27268 | High | High | High | 1276 | 1542 | 0.061559 | 148.9876
CAMP EVERS 210694770 | CAMP EVERS 2106 | CENTRAL COAST | 2.6769 | 10 | 36.19% | 10 | 8 | 66.11% | 100% | 0 | 0.09995 | 1 | 2.7268 | 0.27255 | High | High | Medium | 1277 | 1296 | 0.09995 | 148.7149
LOS GATOS 1106CB | LOS GATOS 1106 | DE ANZA | 6.7095 | 14.253 | 23.95% | 2 | 3 | 87.56% | 91.62% | 0 | 0.083012 | 1 | 3.283 | 0.27253 | High | High | High | 1278 | 1374 | 0.083012 | 148.4424
CAMP EVERS 21067603 | CAMP EVERS 2106 | CENTRAL COAST | 0.9357 | 10 | 57.8% | 0 | 0 | 100% | 100% | 0 | 0.095589 | 1 | 2.8433 | 0.27179 | High | High | Medium | 1279 | 1311 | 0.095589 | 148.1698
SAN RAFAEL 11073323 | SAN RAFAEL 1107 | NORTH BAY | 0.13349 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 4.4049 | 0.27117 | High | High | High | 1280 | 1545 | 0.061559 | 147.8981
HIGHLANDS 110439458 | HIGHLANDS 1104 | HUMBOLDT | 0.83315 | 10 | 36.61% | 0 | 0 | 15.6% | 0% | 0 | 0.0084597 | 11.2183 | 2.8556 | 0.271 | Low | Low | Medium | 1281 | 1315 | 0.094904 | 147.6269
SAN RAFAEL 11081457 | SAN RAFAEL 1108 | NORTH BAY | 0.58979 | 10 | 0% | 0 | 0 | 77.17% | 100% | 0 | 0.056282 | 1 | 4.8134 | 0.27091 | Medium | Medium | High | 1282 | 1611 | 0.056282 | 147.3559
OAKLAND K 1101CR346 | OAKLAND K 1101 | EAST BAY | 0.18736 | 10 | 0% | 1 | 2 | 100% | 100% | 0 | 0.064827 | 1 | 4.1726 | 0.2705 | High | High | High | 1283 | 1515 | 0.064827 | 147.085
SCE VEGAS 1701CB | SCE VEGAS 1701 | LOS PADRES | 0.17032 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 2.0729 | 0.26993 | High | High | Low | 1284 | 1197 | 0.13022 | 146.8145
CORRAL 11012128 | CORRAL 1101 | STOCKTON | 0.10849 | 55.3351 | 0% | 0 | 0 | 0.5187% | 0% | 0 | 0.0064285 | 14.9507 | 2.8084 | 0.26992 | Low | Low | Medium | 1285 | 1307 | 0.09611 | 146.5445
ELECTRA 11022646 | ELECTRA 1102 | STOCKTON | 25.2162 | 27.1707 | 98.11% | 7 | 13 | 100% | 22.04% | 1 | 0.14592 | 1 | 1.8392 | 0.26838 | High | High | Low | 1286 | 1152 | 0.14592 | 146.2746
CAMP EVERS 210355638 | CAMP EVERS 2103 | CENTRAL COAST | 1.9801 | 10 | 57.05% | 1 | 0 | 56.59% | 100% | 0 | 0.082558 | 1 | 3.2291 | 0.26659 | High | High | High | 1287 | 1377 | 0.082558 | 146.0062
SAN RAFAEL 1107714160 | SAN RAFAEL 1107 | NORTH BAY | 2.7558 | 15.5208 | 10.99% | 0 | 10 | 98.34% | 63.23% | 0 | 0.060966 | 1 | 4.37 | 0.26642 | Medium | Medium | High | 1288 | 1558 | 0.060966 | 145.7397
TEMPLETON 2111A66 | TEMPLETON 2111 | LOS PADRES | 33.7371 | 15.0206 | 78.96% | 12 | 6 | 100% | 0.9159% | 0 | 0.091159 | 1 | 2.9193 | 0.26612 | High | High | Medium | 1289 | 1333 | 0.091159 | 145.4732
MIRABEL 1102CB | MIRABEL 1102 | SONOMA | 4.5501 | 24.245 | 39.21% | 4 | 11 | 40.5% | 94.81% | 0 | 0.080685 | 1 | 3.2843 | 0.26499 | High | High | High | 1290 | 1392 | 0.080685 | 145.2071
GARBERVILLE 11026084 | GARBERVILLE 1102 | HUMBOLDT | 15.3135 | 81.9421 | 99.24% | 23 | 2 | 100% | 0% | 0 | 0.18331 | 1 | 1.4373 | 0.26347 | High | High | Low | 1291 | 1086 | 0.18331 | 144.9421
NARROWS 2105CB | NARROWS 2105 | SIERRA | 35.605 | 11.8579 | 78.33% | 4 | 9 | 98.55% | 0% | 0 | 0.094041 | 1 | 2.7962 | 0.26296 | High | High | Medium | 1292 | 1319 | 0.094041 | 144.6786
MOUNTAIN QUARRIES 210192474 | MOUNTAIN QUARRIES 2101 | SIERRA | 14.6687 | 46.984 | 70.43% | 1 | 2 | 94.19% | 51.74% | 0 | 0.10478 | 1 | 2.4996 | 0.2619 | High | High | Medium | 1293 | 1276 | 0.10478 | 144.4157
CABRILLO 1104Y24 | CABRILLO 1104 | LOS PADRES | 18.0747 | 69.8881 | 25.08% | 0 | 8 | 92.92% | 0% | 0 | 0.080321 | 1 | 3.2604 | 0.26188 | High | High | High | 1294 | 1396 | 0.080321 | 144.1538
CAMP EVERS 210611044 | CAMP EVERS 2106 | CENTRAL COAST | 6.5538 | 10.6438 | 23.66% | 12 | 2 | 52.73% | 81.08% | 0 | 0.062668 | 1 | 4.1597 | 0.26068 | High | High | High | 1295 | 1536 | 0.062668 | 143.8919
CURTIS 170539256 | CURTIS 1705 | YOSEMITE | 26.4541 | 14.8561 | 72.89% | 2 | 39 | 100% | 0% | 0 | 0.087881 | 1 | 2.9559 | 0.25976 | High | High | Medium | 1296 | 1346 | 0.087881 | 143.6312
SUNOL 1101MR298 | SUNOL 1101 | MISSION | 5.4024 | 53.1471 | 44.07% | 1 | 5 | 100% | 100% | 0 | 0.1402 | 1 | 1.8521 | 0.25967 | High | High | Low | 1297 | 1168 | 0.1402 | 143.3715
MENLO 1102W80 | MENLO 1102 | PENINSULA | 17.326 | 69.2206 | 62.7% | 1 | 9 | 91.54% | 1.485% | 1 | 0.076689 | 1 | 3.3813 | 0.2593 | High | High | High | 1298 | 1427 | 0.076689 | 143.1118
BOLINAS 1101504 | BOLINAS 1101 | NORTH BAY | 6.5349 | 26.1981 | 0% | 2 | 2 | 100% | 100% | 0 | 0.082308 | 1 | 3.1479 | 0.2591 | High | High | High | 1299 | 1380 | 0.082308 | 142.8525
ORO FINO 11022236 | ORO FINO 1102 | NORTH VALLEY | 2.5402 | 88.3654 | 18.46% | 0 | 3 | 100% | 100% | 0 | 0.12209 | 1 | 2.1142 | 0.25812 | High | High | Low | 1300 | 1222 | 0.12209 | 142.5934
HALSEY 110239104 | HALSEY 1102 | SIERRA | 30.6401 | 10.3566 | 73.57% | 9 | 18 | 100% | 0% | 0 | 0.1288 | 1 | 2.0038 | 0.25809 | High | High | Low | 1301 | 1204 | 0.1288 | 142.3353
POINT ARENA 110137426 | POINT ARENA 1101 | HUMBOLDT | 0.081405 | 10 | 0% | 2 | 1 | 1.62% | 0% | 0 | 0.0057167 | 14.9507 | 2.9781 | 0.25453 | Low | Low | Medium | 1302 | 1362 | 0.085468 | 142.0772
DIAMOND SPRINGS 11039432 | DIAMOND SPRINGS 1103 | SIERRA | 17.0625 | 19.7634 | 81.43% | 3 | 12 | 84.57% | 8.24% | 1 | 0.093192 | 1 | 2.7267 | 0.2541 | High | High | Medium | 1303 | 1323 | 0.093192 | 141.8227
PENRYN 110651674 | PENRYN 1106 | SIERRA | 0.99996 | 10 | 36.11% | 0 | 0 | 8.247% | 0% | 0 | 0.0068595 | 11.2183 | 3.3008 | 0.254 | Low | Low | High | 1304 | 1423 | 0.076952 | 141.5686
SAN RAMON 2107CB | SAN RAMON 2107 | MISSION | 0.08762 | 60 | 100% | 0 | 0 | 0.9683% | 100% | 0 | 0.072467 | 1 | 3.5047 | 0.25397 | High | High | High | 1305 | 1455 | 0.072467 | 141.3145
HIGGINS 1103CB | HIGGINS 1103 | SIERRA | 27.5586 | 18.1402 | 77.71% | 6 | 7 | 99.3% | 0% | 0 | 0.085581 | 1 | 2.9579 | 0.25314 | High | High | Medium | 1306 | 1361 | 0.085581 | 141.0606
MARTELL 110191216 | MARTELL 1101 | STOCKTON | 41.3413 | 10.8803 | 100% | 3 | 13 | 100% | 0% | 0 | 0.10514 | 1 | 2.4019 | 0.25253 | High | High | Medium | 1307 | 1275 | 0.10514 | 140.8074
NEWBURG 11322074 | NEWBURG 1132 | HUMBOLDT | 1.2262 | 10 | 0% | 0 | 0 | 11.58% | 0% | 0 | 0.0060224 | 14.9507 | 2.7999 | 0.2521 | Low | Low | Medium | 1308 | 1337 | 0.090039 | 140.5549
HOOPA 110182542 | HOOPA 1101 | HUMBOLDT | 9.9783 | 60.316 | 90.42% | 13 | 6 | 65.67% | 0% | 0 | 0.10839 | 1 | 2.3143 | 0.25085 | High | High | Medium | 1309 | 1264 | 0.10839 | 140.3028
BIG BASIN 110211062 | BIG BASIN 1102 | CENTRAL COAST | 9.0842 | 63.1207 | 47.86% | 15 | 1 | 100% | 69.62% | 1 | 0.096095 | 1 | 2.6104 | 0.25085 | High | High | Medium | 1310 | 1308 | 0.096095 | 140.052
DIAMOND SPRINGS 11057722 | DIAMOND SPRINGS 1105 | SIERRA | 59.1027 | 30.4266 | 87.61% | 10 | 7 | 94.99% | 35.49% | 0 | 0.11755 | 1 | 2.1264 | 0.24995 | High | High | Low | 1311 | 1230 | 0.11755 | 139.8011
ELK 11011272 | ELK 1101 | HUMBOLDT | 22.2131 | 39.0938 | 18.17% | 28 | 27 | 99.76% | 0% | 0 | 0.15006 | 1 | 1.6636 | 0.24963 | High | High | Low | 1312 | 1145 | 0.15006 | 139.5512
GOLDTREE 1107CB | GOLDTREE 1107 | LOS PADRES | 1.1277 | 39.1961 | 5.234% | 0 | 0 | 30.84% | 0% | 0 | 0.008131 | 11.2183 | 2.7356 | 0.24953 | Low | Low | Medium | 1313 | 1332 | 0.091216 | 139.3015
CALPINE 1144CB | CALPINE 1144 | SONOMA | 26.2964 | 85.7305 | 55.05% | 0 | 0 | 100% | 92.09% | 0 | 0.1323 | 1 | 1.8843 | 0.24929 | High | High | Low | 1314 | 1192 | 0.1323 | 139.052
MARIPOSA 210210880 | MARIPOSA 2102 | YOSEMITE | 39.106 | 24.6164 | 88.93% | 0 | 41 | 98.36% | 24.49% | 0 | 0.13284 | 1 | 1.875 | 0.24909 | High | High | Low | 1315 | 1187 | 0.13284 | 138.8027
MORRO BAY 110247584 | MORRO BAY 1102 | LOS PADRES | 8.6089 | 11.2458 | 21.08% | 1 | 2 | 89.3% | 46.55% | 1 | 0.073801 | 1 | 3.3695 | 0.24868 | High | High | High | 1316 | 1447 | 0.073801 | 138.5536
SHINGLE SPRINGS 210819762 | SHINGLE SPRINGS 2108 | SIERRA | 4.2221 | 28.8991 | 60.1% | 3 | 6 | 78.12% | 39.2% | 0 | 0.077593 | 1 | 3.1989 | 0.24821 | High | High | High | 1317 | 1416 | 0.077593 | 138.305
SAN RAFAEL 1101CB | SAN RAFAEL 1101 | NORTH BAY | 1.7156 | 10 | 28.81% | 3 | 3 | 39.77% | 100% | 1 | 0.061788 | 1 | 4.0124 | 0.24792 | High | High | High | 1318 | 1541 | 0.061788 | 138.0567
PAUL SWEET 210610424 | PAUL SWEET 2106 | CENTRAL COAST | 5.7029 | 19.0788 | 48.59% | 2 | 1 | 80% | 79.15% | 0 | 0.067843 | 1 | 3.6484 | 0.24751 | High | High | High | 1319 | 1489 | 0.067843 | 137.8088
PASO ROBLES 11032731 | PASO ROBLES 1103 | LOS PADRES | 1.1994 | 24.9201 | 47.66% | 0 | 0 | 73.66% | 0% | 0 | 0.015948 | 11.2183 | 1.3825 | 0.24735 | Low | Low | Low | 1320 | 1094 | 0.17891 | 137.5613
SAN LUIS OBISPO 1107V58 | SAN LUIS OBISPO 1107 | LOS PADRES | 0.84617 | 10 | 0% | 0 | 0 | 37.96% | 0% | 0 | 0.006858 | 11.2183 | 3.2113 | 0.24706 | Low | Low | High | 1321 | 1424 | 0.076935 | 137.314
SANTA ROSA A 110432180 | SANTA ROSA A 1104 | SONOMA | 2.5189 | 19.7323 | 62.59% | 0 | 1 | 99.89% | 67.69% | 0 | 0.074867 | 1 | 3.2925 | 0.2465 | High | High | High | 1322 | 1440 | 0.074867 | 137.0669
MONTE RIO 111159046 | MONTE RIO 1111 | SONOMA | 2.6767 | 61.8101 | 0% | 1 | 1 | 70.69% | 0% | 0 | 0.013942 | 11.2183 | 1.5755 | 0.24642 | Low | Low | Low | 1323 | 1136 | 0.15641 | 136.8204
PARADISE 11031231 | PARADISE 1103 | NORTH VALLEY | 2.541 | 10 | 17.59% | 3 | 2 | 90.53% | 96.98% | 0 | 0.066519 | 1 | 3.6926 | 0.24563 | High | High | High | 1324 | 1501 | 0.066519 | 136.574
SAN JOAQUIN #3 110110060 | SAN JOAQUIN #3 1101 | YOSEMITE | 6.5306 | 43.2657 | 65.2% | 0 | 4 | 100% | 100% | 0 | 0.133 | 1 | 1.8456 | 0.24547 | High | High | Low | 1325 | 1186 | 0.133 | 136.3284
CAMP EVERS 210595050 | CAMP EVERS 2105 | CENTRAL COAST | 0.13882 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.9779 | 0.24488 | High | High | High | 1326 | 1545 | 0.061559 | 136.0829
EL CERRITO G 1105BR160 | EL CERRITO G 1105 | EAST BAY | 7.9453 | 33.1195 | 38.34% | 5 | 6 | 69.23% | 42.93% | 0 | 0.059441 | 1 | 4.1032 | 0.2439 | Medium | Medium | High | 1327 | 1571 | 0.059441 | 135.838
SHINGLE SPRINGS 2108CB | SHINGLE SPRINGS 2108 | SIERRA | 1.2634 | 35.9265 | 24.64% | 0 | 1 | 85.58% | 100% | 1 | 0.078196 | 1 | 3.1135 | 0.24347 | High | High | High | 1328 | 1411 | 0.078196 | 135.5941
OCEANO 1102CB | OCEANO 1102 | LOS PADRES | 20.8775 | 11.5809 | 41.43% | 7 | 19 | 75.87% | 0% | 0 | 0.081976 | 1 | 2.9691 | 0.2434 | High | High | Medium | 1329 | 1382 | 0.081976 | 135.3506
SAN LUIS OBISPO 11042293 | SAN LUIS OBISPO 1104 | LOS PADRES | 9.0237 | 83.3193 | 68.53% | 2 | 1 | 100% | 100% | 0 | 0.16663 | 1 | 1.4572 | 0.24281 | High | High | Low | 1330 | 1119 | 0.16663 | 135.1073
NARROWS 21011202 | NARROWS 2101 | SIERRA | 45.5016 | 16.7658 | 94.84% | 2 | 35 | 100% | 0% | 0 | 0.10949 | 1 | 2.2156 | 0.24258 | High | High | Low | 1331 | 1262 | 0.10949 | 134.8644
SHINGLE SPRINGS 1103CB | SHINGLE SPRINGS 1103 | SIERRA | 6.5783 | 25.7936 | 79.81% | 1 | 6 | 56.03% | 80.43% | 1 | 0.079857 | 1 | 3.0171 | 0.24094 | High | High | Medium | 1332 | 1400 | 0.079857 | 134.6219
GREENBRAE 11031260 | GREENBRAE 1103 | NORTH BAY | 2.3256 | 16.3667 | 42.46% | 2 | 2 | 86.56% | 70.2% | 0 | 0.060164 | 1 | 4.0042 | 0.24091 | Medium | Medium | High | 1333 | 1563 | 0.060164 | 134.3809
ALTO 1124CB | ALTO 1124 | NORTH BAY | 3.2561 | 10 | 7.135% | 1 | 6 | 46.3% | 100% | 0 | 0.050654 | 1 | 4.7415 | 0.24018 | Medium | Medium | High | 1334 | 1675 | 0.050654 | 134.14
EL CERRITO G 1112BR178 | EL CERRITO G 1112 | EAST BAY | 1.8955 | 10 | 57.49% | 2 | 1 | 23.53% | 92.74% | 0 | 0.049573 | 1 | 4.8314 | 0.23951 | Medium | Medium | High | 1335 | 1689 | 0.049573 | 133.8998
SONOMA 1105404 | SONOMA 1105 | SONOMA | 12.3578 | 22.8821 | 50.06% | 1 | 16 | 68.86% | 37.07% | 0 | 0.072855 | 1 | 3.2835 | 0.23922 | High | High | High | 1336 | 1451 | 0.072855 | 133.6603
KESWICK 11011586 | KESWICK 1101 | NORTH VALLEY | 7.6307 | 36.5577 | 16.39% | 0 | 2 | 100% | 100% | 1 | 0.085854 | 1 | 2.7857 | 0.23916 | High | High | Medium | 1337 | 1359 | 0.085854 | 133.4211
SAN LUIS OBISPO 1101V12 | SAN LUIS OBISPO 1101 | LOS PADRES | 21.0121 | 75.506 | 48.74% | 1 | 1 | 99.72% | 49% | 1 | 0.10534 | 1 | 2.27 | 0.23913 | High | High | Medium | 1338 | 1273 | 0.10534 | 133.1819
MC KEE 1111711900 | MC KEE 1111 | SAN JOSE | 8.3733 | 57.1059 | 68.22% | 0 | 5 | 66.5% | 0% | 0 | 0.059287 | 1 | 4.0165 | 0.23813 | Medium | Medium | High | 1339 | 1575 | 0.059287 | 132.9428
PINE GROVE 11023168 | PINE GROVE 1102 | STOCKTON | 30.4079 | 52.9502 | 87.84% | 3 | 16 | 100% | 16.23% | 0 | 0.091596 | 1 | 2.5997 | 0.23812 | High | High | Medium | 1340 | 1328 | 0.091596 | 132.7047
CURTIS 17058170 | CURTIS 1705 | YOSEMITE | 7.5122 | 10 | 100% | 1 | 19 | 95.23% | 28.76% | 0 | 0.063226 | 1 | 3.7646 | 0.23802 | High | High | High | 1341 | 1530 | 0.063226 | 132.4666
OCEANO 1104Q06 | OCEANO 1104 | LOS PADRES | 12.4604 | 18.1576 | 68.47% | 10 | 12 | 100% | 0% | 0 | 0.07261 | 1 | 3.274 | 0.23772 | High | High | High | 1342 | 1453 | 0.07261 | 132.2285
APPLE HILL 11038412 | APPLE HILL 1103 | SIERRA | 20.0804 | 56.3777 | 98.03% | 4 | 10 | 100% | 56.18% | 1 | 0.12834 | 1 | 1.8505 | 0.23749 | High | High | Low | 1343 | 1207 | 0.12834 | 131.9908
STELLING 111060080 | STELLING 1110 | DE ANZA | 9.1723 | 64.142 | 26.3% | 6 | 3 | 90.37% | 0% | 0 | 0.074583 | 1 | 3.1821 | 0.23733 | High | High | High | 1344 | 1442 | 0.074583 | 131.7533
PAUL SWEET 2106CB | PAUL SWEET 2106 | CENTRAL COAST | 5.2267 | 14.0145 | 33.08% | 1 | 5 | 37.05% | 92.49% | 0 | 0.057775 | 1 | 4.0611 | 0.23463 | Medium | Medium | High | 1345 | 1597 | 0.057775 | 131.516
SAN JOAQUIN #3 110210342 | SAN JOAQUIN #3 1102 | YOSEMITE | 1.8206 | 16.0634 | 100% | 0 | 4 | 100% | 100% | 0 | 0.16247 | 1 | 1.436 | 0.2333 | High | High | Low | 1346 | 1126 | 0.16247 | 131.2814
SAN JOAQUIN #3 1101CB | SAN JOAQUIN #3 1101 | YOSEMITE | 5.4085 | 45.9214 | 90.84% | 2 | 3 | 100% | 98.42% | 0 | 0.15907 | 1 | 1.4628 | 0.23269 | High | High | Low | 1347 | 1132 | 0.15907 | 131.0481
MONROE 210765424 | MONROE 2107 | SONOMA | 0.75479 | 10 | 100% | 0 | 0 | 14.79% | 100% | 0 | 0.067899 | 1 | 3.4252 | 0.23257 | High | High | High | 1348 | 1486 | 0.067899 | 130.8154
BOLINAS 1101CB | BOLINAS 1101 | NORTH BAY | 2.176 | 69.2661 | 1.123% | 3 | 1 | 100% | 77.9% | 0 | 0.077604 | 1 | 2.9867 | 0.23178 | High | High | Medium | 1349 | 1415 | 0.077604 | 130.5828
MARIPOSA 210110990 | MARIPOSA 2101 | YOSEMITE | 39.8367 | 17.0819 | 99.94% | 3 | 69 | 100% | 0% | 0 | 0.16909 | 1 | 1.36 | 0.22996 | High | High | Low | 1350 | 1114 | 0.16909 | 130.351
MORGAN HILL 2111XR186 | MORGAN HILL 2111 | SAN JOSE | 0.89677 | 65 | 0% | 0 | 0 | 5.591% | 0% | 0 | 0.0072203 | 11.2183 | 2.834 | 0.22955 | Low | Low | Medium | 1351 | 1390 | 0.080999 | 130.1211
SAN RAFAEL 1101494 | SAN RAFAEL 1101 | NORTH BAY | 4.1663 | 10 | 20.21% | 1 | 4 | 47.93% | 100% | 0 | 0.062096 | 1 | 3.6785 | 0.22842 | High | High | High | 1352 | 1538 | 0.062096 | 129.8915
FORT BRAGG A 110231304 | FORT BRAGG A 1102 | HUMBOLDT | 21.5206 | 61.6048 | 34.35% | 17 | 8 | 100% | 0% | 0 | 0.094856 | 1 | 2.3985 | 0.22751 | High | High | Medium | 1353 | 1316 | 0.094856 | 129.6631
LAKEWOOD 210964992 | LAKEWOOD 2109 | DIABLO | 0.21818 | 10 | 100% | 0 | 0 | 8.548% | 100% | 0 | 0.056493 | 1 | 4.016 | 0.22688 | Medium | Medium | High | 1354 | 1607 | 0.056493 | 129.4356
HIGGINS 110332120 | HIGGINS 1103 | SIERRA | 40.5815 | 16.4911 | 85.22% | 7 | 11 | 99.04% | 0% | 0 | 0.076505 | 1 | 2.9612 | 0.22655 | High | High | Medium | 1355 | 1429 | 0.076505 | 129.2087
NEWBURG 11313446 | NEWBURG 1131 | HUMBOLDT | 0.24063 | 10 | 0% | 0 | 0 | 2.893% | 0% | 0 | 0.0048356 | 19.9979 | 2.3426 | 0.22653 | Low | Low | Medium | 1356 | 1306 | 0.096701 | 128.9822
ALLEGHANY 1101808 | ALLEGHANY 1101 | SIERRA | 6.1403 | 95.663 | 12.49% | 0 | 2 | 100% | 100% | 0 | 0.13475 | 1 | 1.679 | 0.22625 | High | High | Low | 1357 | 1182 | 0.13475 | 128.7556
CALAVERAS CEMENT 11014786 | CALAVERAS CEMENT 1101 | STOCKTON | 18.0051 | 18.3515 | 89.75% | 0 | 8 | 100% | 55.25% | 1 | 0.076728 | 1 | 2.9429 | 0.22581 | High | High | Medium | 1358 | 1426 | 0.076728 | 128.5294
GREEN VALLEY 210190860 | GREEN VALLEY 2101 | CENTRAL COAST | 3.8052 | 10 | 95.69% | 0 | 0 | 20.73% | 93.04% | 0 | 0.070746 | 1 | 3.19 | 0.22568 | High | High | High | 1359 | 1468 | 0.070746 | 128.3036
CASTRO VALLEY 1108 | CASTRO VALLEY 1108 | MISSION | 0.019583 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.6623 | 0.22545 | High | High | High | 1360 | 1545 | 0.061559 | 128.0779
LAURELES 11112020 | LAURELES 1111 | CENTRAL COAST | 33.1343 | 48.734 | 70.7% | 2 | 9 | 100% | 9.9% | 1 | 0.11304 | 1 | 1.9922 | 0.2252 | High | High | Low | 1361 | 1245 | 0.11304 | 127.8524
KANAKA 1101CB | KANAKA 1101 | NORTH VALLEY | 4.6774 | 55.1611 | 80.24% | 0 | 1 | 100% | 79.67% | 1 | 0.11271 | 1 | 1.9968 | 0.22505 | High | High | Low | 1362 | 1247 | 0.11271 | 127.6273
GANSNER 11012006 | GANSNER 1101 | NORTH VALLEY | 17.1959 | 52.9981 | 98.77% | 5 | 5 | 100% | 2.795% | 0 | 0.086274 | 1 | 2.5916 | 0.22359 | High | High | Medium | 1363 | 1356 | 0.086274 | 127.4022
SANTA YNEZ 1101Y52 | SANTA YNEZ 1101 | LOS PADRES | 18.8234 | 75.9887 | 74.53% | 0 | 5 | 76.28% | 53.44% | 1 | 0.10447 | 1 | 2.1391 | 0.22348 | High | High | Low | 1364 | 1278 | 0.10447 | 127.1786
CENTERVILLE 1101CB | CENTERVILLE 1101 | NORTH VALLEY | 0.015747 | 10 | 0% | 0 | 1 | 100% | 100% | 0 | 0.071117 | 1 | 3.1314 | 0.2227 | High | High | High | 1365 | 1465 | 0.071117 | 126.9551
PENRYN 1105CB | PENRYN 1105 | SIERRA | 0.038025 | 10 | 0% | 0 | 0 | 3.678% | 0% | 0 | 0.0048736 | 14.9507 | 3.0534 | 0.22248 | Low | Low | Medium | 1366 | 1450 | 0.072863 | 126.7324
HALF MOON BAY 11028848 | HALF MOON BAY 1102 | PENINSULA | 3.8931 | 27.5705 | 29.99% | 4 | 3 | 38.64% | 80.42% | 0 | 0.051782 | 1 | 4.2924 | 0.22227 | Medium | Medium | High | 1367 | 1664 | 0.051782 | 126.51
LUCERNE 110638632 | LUCERNE 1106 | HUMBOLDT | 4.4543 | 54.342 | 100% | 6 | 8 | 95.13% | 0% | 0 | 0.076393 | 1 | 2.9038 | 0.22183 | High | High | Medium | 1368 | 1431 | 0.076393 | 126.2877
CASTRO VALLEY 1109MR334 | CASTRO VALLEY 1109 | MISSION | 5.7287 | 41.5825 | 24.73% | 0 | 3 | 90.6% | 49.57% | 0 | 0.052651 | 1 | 4.2098 | 0.22165 | Medium | Medium | High | 1369 | 1653 | 0.052651 | 126.0659
CORNING 11021900 | CORNING 1102 | NORTH VALLEY | 0.99921 | 77.9025 | 2.304% | 0 | 2 | 5.388% | 0% | 0 | 0.0083558 | 19.9979 | 1.3171 | 0.22009 | Low | Low | Low | 1370 | 1118 | 0.1671 | 125.8442
MORGAN HILL 2111CB | MORGAN HILL 2111 | SAN JOSE | 0.34374 | 10 | 12.74% | 0 | 0 | 12.6% | 0% | 0 | 0.0059141 | 11.2183 | 3.3152 | 0.21995 | Low | Low | High | 1371 | 1504 | 0.066347 | 125.6241
ROSSMOOR 1106CB | ROSSMOOR 1106 | DIABLO | 1.4865 | 10 | 68.08% | 0 | 8 | 30.91% | 92.75% | 0 | 0.057048 | 1 | 3.8412 | 0.21913 | Medium | Medium | High | 1372 | 1605 | 0.057048 | 125.4042
ATASCADERO 1101A50 | ATASCADERO 1101 | LOS PADRES | 19.8065 | 10 | 78.19% | 4 | 9 | 94.43% | 5.217% | 1 | 0.066857 | 1 | 3.2682 | 0.2185 | High | High | High | 1373 | 1497 | 0.066857 | 125.185
SISQUOC 1103M14 | SISQUOC 1103 | LOS PADRES | 21.2959 | 68.8259 | 69.24% | 0 | 10 | 65.02% | 94.4% | 0 | 0.21174 | 1 | 1.0317 | 0.21846 | High | High | Low | 1374 | 1039 | 0.21174 | 124.9665
CALAVERAS CEMENT 110180930 | CALAVERAS CEMENT 1101 | STOCKTON | 18.4785 | 30.1878 | 99.81% | 1 | 6 | 100% | 0% | 0 | 0.089656 | 1 | 2.4362 | 0.21842 | High | High | Medium | 1375 | 1338 | 0.089656 | 124.7481
PAUL SWEET 2105CB | PAUL SWEET 2105 | CENTRAL COAST | 8.1216 | 24.934 | 34.71% | 10 | 1 | 52.4% | 90.68% | 0 | 0.064304 | 1 | 3.3844 | 0.21763 | High | High | High | 1376 | 1522 | 0.064304 | 124.5297
CLOVERDALE 1102570 | CLOVERDALE 1102 | SONOMA | 17.3117 | 48.3271 | 69.88% | 1 | 6 | 81.35% | 95.94% | 0 | 0.11928 | 1 | 1.824 | 0.21757 | High | High | Low | 1377 | 1226 | 0.11928 | 124.312
CAMP EVERS 210411048 | CAMP EVERS 2104 | CENTRAL COAST | 0.87487 | 10 | 18.94% | 3 | 1 | 63.94% | 100% | 0 | 0.053728 | 1 | 4.0099 | 0.21544 | Medium | Medium | High | 1378 | 1640 | 0.053728 | 124.0945
SONOMA 1106CB | SONOMA 1106 | SONOMA | 0.46405 | 10 | 100% | 0 | 0 | 11.88% | 100% | 0 | 0.058298 | 1 | 3.6884 | 0.21503 | Medium | Medium | High | 1379 | 1590 | 0.058298 | 123.879
OAKLAND K 1101CR170 | OAKLAND K 1101 | EAST BAY | 1.2514 | 10 | 10.22% | 0 | 3 | 100% | 84.34% | 0 | 0.055611 | 1 | 3.8581 | 0.21455 | Medium | Medium | High | 1380 | 1616 | 0.055611 | 123.664
SANTA ROSA A 110439786 | SANTA ROSA A 1104 | SONOMA | 1.14 | 10 | 49.93% | 0 | 3 | 16.83% | 100% | 0 | 0.056488 | 1 | 3.7971 | 0.21449 | Medium | Medium | High | 1381 | 1608 | 0.056488 | 123.4494
MOUNTAIN QUARRIES 21011102 | MOUNTAIN QUARRIES 2101 | SIERRA | 44.4218 | 34.6112 | 86.6% | 0 | 15 | 100% | 0% | 0 | 0.11033 | 1 | 1.9411 | 0.21417 | High | High | Low | 1382 | 1258 | 0.11033 | 123.235
OREGON TRAIL 11031500 | OREGON TRAIL 1103 | NORTH VALLEY | 24.8639 | 16.6581 | 98.22% | 2 | 4 | 96.57% | 0% | 0 | 0.076799 | 1 | 2.7865 | 0.214 | High | High | Medium | 1383 | 1425 | 0.076799 | 123.0208
SOBRANTE 1102L510R | SOBRANTE 1102 | DIABLO | 9.7593 | 10 | 23.81% | 5 | 6 | 100% | 0% | 0 | 0.067265 | 1 | 3.176 | 0.21364 | High | High | High | 1384 | 1495 | 0.067265 | 122.8068
ROB ROY 210571630 | ROB ROY 2105 | CENTRAL COAST | 1.807 | 10 | 61.71% | 5 | 2 | 96.47% | 60.73% | 0 | 0.066075 | 1 | 3.2318 | 0.21354 | High | High | High | 1385 | 1506 | 0.066075 | 122.5932
SAN RAFAEL 1108CB | SAN RAFAEL 1108 | NORTH BAY | 3.0131 | 10 | 10.73% | 6 | 1 | 40.8% | 100% | 0 | 0.047654 | 1 | 4.4645 | 0.21275 | Medium | Medium | High | 1386 | 1711 | 0.047654 | 122.3796
DIAMOND SPRINGS 1103CB | DIAMOND SPRINGS 1103 | SIERRA | 16.7869 | 10 | 71.13% | 6 | 16 | 54.37% | 47.43% | 1 | 0.08564 | 1 | 2.4835 | 0.21268 | High | High | Medium | 1387 | 1360 | 0.08564 | 122.1669
OAKLAND D 1112CR192 | OAKLAND D 1112 | EAST BAY | 2.6688 | 25.8444 | 29.93% | 2 | 4 | 64.82% | 77.45% | 0 | 0.054951 | 1 | 3.8636 | 0.21231 | Medium | Medium | High | 1388 | 1626 | 0.054951 | 121.9542
AUBERRY 1101R2838 | AUBERRY 1101 | FRESNO | 20.2113 | 19.1577 | 100% | 5 | 21 | 100% | 0% | 0 | 0.10363 | 1 | 2.0481 | 0.21224 | High | High | Low | 1389 | 1281 | 0.10363 | 121.7419
PARADISE 1102CB | PARADISE 1102 | NORTH VALLEY | 0.74465 | 10 | 6.716% | 2 | 0 | 53.22% | 100% | 0 | 0.048451 | 1 | 4.3681 | 0.21164 | Medium | Medium | High | 1390 | 1701 | 0.048451 | 121.5296
PUEBLO 2102656 | PUEBLO 2102 | NORTH BAY | 0.064775 | 10 | 100% | 0 | 0 | 0.3672% | 100% | 0 | 0.059306 | 1 | 3.5617 | 0.21123 | Medium | Medium | High | 1391 | 1574 | 0.059306 | 121.318
SWIFT 2110XR366 | SWIFT 2110 | SAN JOSE | 8.8402 | 27.8534 | 70.07% | 1 | 1 | 80.04% | 0% | 0 | 0.04663 | 1 | 4.5152 | 0.21055 | Medium | Medium | High | 1392 | 1728 | 0.04663 | 121.1068
GRASS VALLEY 11032110 | GRASS VALLEY 1103 | SIERRA | 19.6542 | 17.5047 | 70.11% | 3 | 10 | 97.43% | 0% | 0 | 0.080807 | 1 | 2.6029 | 0.21033 | High | High | Medium | 1393 | 1391 | 0.080807 | 120.8962
APPLE HILL 21028372 | APPLE HILL 2102 | SIERRA | 56.1866 | 51.1532 | 100% | 7 | 2 | 89.5% | 31.4% | 1 | 0.11526 | 1 | 1.8245 | 0.2103 | High | High | Low | 1394 | 1237 | 0.11526 | 120.6859
BOLINAS 1101528 | BOLINAS 1101 | NORTH BAY | 2.2652 | 10 | 0% | 1 | 5 | 74.53% | 100% | 0 | 0.061356 | 1 | 3.4025 | 0.20876 | Medium | Medium | High | 1395 | 1553 | 0.061356 | 120.4756
CLOVERDALE 1102156 | CLOVERDALE 1102 | SONOMA | 6.0801 | 52.6986 | 63.14% | 2 | 11 | 52.14% | 81.66% | 0 | 0.091237 | 1 | 2.2861 | 0.20858 | High | High | Medium | 1396 | 1331 | 0.091237 | 120.2668
MILPITAS 1109XR082 | MILPITAS 1109 | SAN JOSE | 19.1832 | 53.2607 | 99.6% | 3 | 3 | 94.55% | 0% | 0 | 0.058023 | 1 | 3.5906 | 0.20834 | Medium | Medium | High | 1397 | 1596 | 0.058023 | 120.0582
HICKS 2103LB50 | HICKS 2103 | SAN JOSE | 10.8958 | 72.4633 | 80.45% | 3 | 2 | 82.11% | 27.73% | 0 | 0.058713 | 1 | 3.5349 | 0.20754 | Medium | Medium | High | 1398 | 1583 | 0.058713 | 119.8499
CALAVERAS CEMENT 1101502 | CALAVERAS CEMENT 1101 | STOCKTON | 38.3009 | 27.6645 | 90.32% | 2 | 8 | 92.84% | 0% | 0 | 0.10314 | 1 | 2.0117 | 0.20748 | High | High | Low | 1399 | 1285 | 0.10314 | 119.6424
STILLWATER 11011320 | STILLWATER 1101 | NORTH VALLEY | 18.8372 | 23.2893 | 80.24% | 9 | 10 | 93.78% | 0% | 0 | 0.10603 | 1 | 1.956 | 0.2074 | High | High | Low | 1400 | 1269 | 0.10603 | 119.4349
HALSEY 1101CB | HALSEY 1101 | SIERRA | 17.1561 | 10.5573 | 71.81% | 7 | 24 | 100% | 0% | 0 | 0.08631 | 1 | 2.3966 | 0.20685 | High | High | Medium | 1401 | 1354 | 0.08631 | 119.2275
AUBERRY 1102CB | AUBERRY 1102 | FRESNO | 34.5018 | 23.0923 | 82.62% | 0 | 22 | 100% | 0% | 0 | 0.089542 | 1 | 2.3016 | 0.20609 | High | High | Medium | 1402 | 1340 | 0.089542 | 119.0206
WILLITS 11032500 | WILLITS 1103 | HUMBOLDT | 29.9853 | 83.8453 | 100% | 11 | 13 | 100% | 0% | 0 | 0.14143 | 1 | 1.453 | 0.20549 | High | High | Low | 1403 | 1164 | 0.14143 | 118.8145
SAN BENITO 210488772 | SAN BENITO 2104 | CENTRAL COAST | 23.9825 | 25.5059 | 54.82% | 18 | 5 | 55.63% | 0% | 0 | 0.071687 | 1 | 2.854 | 0.2046 | High | High | Medium | 1404 | 1462 | 0.071687 | 118.609
ALHAMBRA 110582622 | ALHAMBRA 1105 | DIABLO | 25.9018 | 63.5576 | 53.56% | 4 | 18 | 100% | 1.973% | 1 | 0.072547 | 1 | 2.8047 | 0.20347 | High | High | Medium | 1405 | 1454 | 0.072547 | 118.4044
PLACERVILLE 111019582 | PLACERVILLE 1110 | SIERRA | 22.4014 | 26.1615 | 63.31% | 2 | 22 | 100% | 0% | 0 | 0.091322 | 1 | 2.2123 | 0.20203 | High | High | Low | 1406 | 1330 | 0.091322 | 118.201
COARSEGOLD 2102383092 | COARSEGOLD 2102 | YOSEMITE | 0.3809 | 10 | 73.97% | 0 | 0 | 100% | 100% | 0 | 0.10776 | 1 | 1.874 | 0.20194 | High | High | Low | 1407 | 1266 | 0.10776 | 117.9989
WEST POINT 11021369 | WEST POINT 1102 | STOCKTON | 10.5051 | 72.1066 | 100% | 1 | 0 | 98.44% | 18.78% | 0 | 0.073587 | 1 | 2.7416 | 0.20175 | High | High | Medium | 1408 | 1448 | 0.073587 | 117.797
FROGTOWN 17011623 | FROGTOWN 1701 | STOCKTON | 15.2549 | 27.6688 | 92.79% | 0 | 7 | 100% | 0% | 0 | 0.065843 | 1 | 3.0596 | 0.20145 | High | High | Medium | 1409 | 1508 | 0.065843 | 117.5952
CLARKSVILLE 210951744 | CLARKSVILLE 2109 | SIERRA | 0.69986 | 10 | 100% | 0 | 1 | 39% | 87.04% | 0 | 0.062946 | 1 | 3.1987 | 0.20135 | High | High | High | 1410 | 1533 | 0.062946 | 117.3938
BOLINAS 1101 | BOLINAS 1101 | NORTH BAY | 0.01843 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.2701 | 0.2013 | High | High | High | 1411 | 1545 | 0.061559 | 117.1924
CURTIS 170511790 | CURTIS 1705 | YOSEMITE | 0.014226 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.2679 | 0.20117 | High | High | High | 1412 | 1542 | 0.061559 | 116.9911
BIG BASIN 110212779 | BIG BASIN 1102 | CENTRAL COAST | 0.25335 | 10 | 27.94% | 0 | 0 | 100% | 100% | 0 | 0.076303 | 1 | 2.6324 | 0.20086 | High | High | Medium | 1413 | 1432 | 0.076303 | 116.79
KESWICK 1101CB | KESWICK 1101 | NORTH VALLEY | 0.016582 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.2562 | 0.20045 | High | High | High | 1414 | 1545 | 0.061559 | 116.5891
NOTRE DAME 11042537 | NOTRE DAME 1104 | NORTH VALLEY | 5.2925 | 55.6781 | 100% | 0 | 0 | 100% | 22.56% | 0 | 0.062104 | 1 | 3.2088 | 0.19928 | High | High | High | 1415 | 1537 | 0.062104 | 116.3887
SYCAMORE CREEK 11112014 | SYCAMORE CREEK 1111 | NORTH VALLEY | 22.6561 | 53.0217 | 99.04% | 1 | 4 | 99.97% | 25.97% | 0 | 0.069882 | 1 | 2.8512 | 0.19925 | High | High | Medium | 1416 | 1471 | 0.069882 | 116.1894
COARSEGOLD 21045300 | COARSEGOLD 2104 | YOSEMITE | 37.3624 | 19.4525 | 89.47% | 1 | 28 | 100% | 0% | 0 | 0.10447 | 1 | 1.9069 | 0.19922 | High | High | Low | 1417 | 1279 | 0.10447 | 115.9901
OCEANO 1103221092 | OCEANO 1103 | LOS PADRES | 1.2243 | 45.1389 | 92.5% | 0 | 2 | 95.43% | 0% | 0 | 0.049591 | 1 | 3.9902 | 0.19788 | Medium | Medium | High | 1418 | 1688 | 0.049591 | 115.7909
ROB ROY 210410714 | ROB ROY 2104 | CENTRAL COAST | 15.4812 | 20.2777 | 49.42% | 12 | 6 | 79.24% | 0% | 0 | 0.069343 | 1 | 2.8504 | 0.19765 | High | High | Medium | 1419 | 1475 | 0.069343 | 115.593
CURTIS 170234426 | CURTIS 1702 | YOSEMITE | 4.917 | 10 | 82.09% | 0 | 4 | 71.87% | 67.24% | 1 | 0.058493 | 1 | 3.3748 | 0.1974 | Medium | Medium | High | 1420 | 1587 | 0.058493 | 115.3954
CURTIS 17036064 | CURTIS 1703 | YOSEMITE | 19.198 | 23.357 | 96.92% | 3 | 15 | 97.54% | 0% | 0 | 0.069239 | 1 | 2.8169 | 0.19504 | High | High | Medium | 1421 | 1476 | 0.069239 | 115.198
AUBERRY 1101R2845 | AUBERRY 1101 | FRESNO | 17.7605 | 28.7565 | 100% | 4 | 13 | 100% | 0% | 0 | 0.10532 | 1 | 1.8477 | 0.19461 | High | High | Low | 1422 | 1274 | 0.10532 | 115.003
VASCO 1102MR176 | VASCO 1102 | MISSION | 38.5569 | 70.5523 | 85.5% | 0 | 7 | 89.92% | 0% | 0 | 0.084198 | 1 | 2.3104 | 0.19454 | High | High | Medium | 1423 | 1370 | 0.084198 | 114.8083
NARROWS 21057203 | NARROWS 2105 | SIERRA | 17.8971 | 13.4012 | 99.97% | 2 | 5 | 95.78% | 0% | 0 | 0.077172 | 1 | 2.5133 | 0.19395 | High | High | Medium | 1424 | 1422 | 0.077172 | 114.6138
OTTER 1102CB | OTTER 1102 | CENTRAL COAST | 6.6866 | 58.389 | 0% | 3 | 0 | 98.35% | 55.62% | 1 | 0.11663 | 1 | 1.6628 | 0.19393 | High | High | Low | 1425 | 1232 | 0.11663 | 114.4199
CASTRO VALLEY 1108MR243 | CASTRO VALLEY 1108 | MISSION | 5.5308 | 36.4789 | 12.29% | 0 | 3 | 99.61% | 62.99% | 0 | 0.054568 | 1 | 3.5499 | 0.19371 | Medium | Medium | High | 1426 | 1632 | 0.054568 | 114.2259
SOBRANTE 1103N510R | SOBRANTE 1103 | DIABLO | 0.050894 | 10 | 0% | 1 | 0 | 5.822% | 0% | 0 | 0.0050449 | 11.2183 | 3.422 | 0.19367 | Low | Low | High | 1427 | 1606 | 0.056595 | 114.0322
SOBRANTE 1102L520R | SOBRANTE 1102 | DIABLO | 7.4675 | 10 | 48.68% | 1 | 16 | 100% | 8.05% | 0 | 0.05711 | 1 | 3.39 | 0.19361 | Medium | Medium | High | 1428 | 1604 | 0.05711 | 113.8385
MOUNTAIN QUARRIES 21011130 | MOUNTAIN QUARRIES 2101 | SIERRA | 20.0304 | 57.0085 | 99.98% | 8 | 6 | 100% | 22.7% | 1 | 0.088009 | 1 | 2.1946 | 0.19314 | High | High | Low | 1429 | 1343 | 0.088009 | 113.6449
APPLE HILL 210277546 | APPLE HILL 2102 | SIERRA | 43.2651 | 10.0567 | 100% | 8 | 8 | 100% | 3.986% | 0 | 0.084095 | 1 | 2.293 | 0.19283 | High | High | Medium | 1430 | 1371 | 0.084095 | 113.4518
EL CERRITO G 1105CB | EL CERRITO G 1105 | EAST BAY | 7.4165 | 22.6789 | 12.34% | 2 | 5 | 100% | 20.23% | 0 | 0.040319 | 1 | 4.7752 | 0.19253 | Medium | Medium | High | 1431 | 1846 | 0.040319 | 113.259
NARROWS 21052228 | NARROWS 2105 | SIERRA | 20.4861 | 37.6865 | 94.14% | 3 | 11 | 96.44% | 0% | 0 | 0.06797 | 1 | 2.8311 | 0.19243 | High | High | Medium | 1432 | 1485 | 0.06797 | 113.0664
COARSEGOLD 210310820 | COARSEGOLD 2103 | YOSEMITE | 28.8124 | 11.1753 | 93.73% | 0 | 47 | 100% | 0% | 0 | 0.07927 | 1 | 2.4251 | 0.19224 | High | High | Medium | 1433 | 1406 | 0.07927 | 112.874
GREEN VALLEY 210112824 | GREEN VALLEY 2101 | CENTRAL COAST | 0.066956 | 70 | 0% | 0 | 0 | 0.5469% | 0% | 0 | 0.007104 | 11.2183 | 2.3989 | 0.19118 | Low | Low | Medium | 1434 | 1401 | 0.079695 | 112.6818
CURTIS 170247488 | CURTIS 1702 | YOSEMITE | 18.0809 | 16.9513 | 84.37% | 2 | 17 | 87.6% | 0% | 0 | 0.05643 | 1 | 3.3854 | 0.19104 | Medium | Medium | High | 1435 | 1609 | 0.05643 | 112.4906
HOOPA 1101CB | HOOPA 1101 | HUMBOLDT | 15.2475 | 59.0191 | 97.73% | 17 | 6 | 56.28% | 0% | 0 | 0.085954 | 1 | 2.2215 | 0.19095 | High | High | Low | 1436 | 1358 | 0.085954 | 112.2996
OAKLAND K 1104CR208 | OAKLAND K 1104 | EAST BAY | 2.4051 | 10 | 34.97% | 0 | 3 | 100% | 39.7% | 0 | 0.0436 | 1 | 4.378 | 0.19088 | Medium | Medium | High | 1437 | 1785 | 0.0436 | 112.1086
PAUL SWEET 210710986 | PAUL SWEET 2107 | CENTRAL COAST | 10.6088 | 30.4341 | 52.14% | 3 | 2 | 53.14% | 44.56% | 0 | 0.066361 | 1 | 2.8689 | 0.19038 | High | High | Medium | 1438 | 1503 | 0.066361 | 111.9177
ROB ROY 210538430 | ROB ROY 2105 | CENTRAL COAST | 4.0485 | 27.4617 | 42.48% | 11 | 1 | 61.21% | 68.36% | 0 | 0.05425 | 1 | 3.498 | 0.18976 | Medium | Medium | High | 1439 | 1636 | 0.05425 | 111.7273
PERRY 1101V78 | PERRY 1101 | LOS PADRES | 29.478 | 56.2687 | 60.85% | 2 | 3 | 100% | 21.68% | 1 | 0.081321 | 1 | 2.3311 | 0.18957 | High | High | Medium | 1440 | 1387 | 0.081321 | 111.5376
GREEN VALLEY 210136820 | GREEN VALLEY 2101 | CENTRAL COAST | 6.5982 | 36.5973 | 46.31% | 12 | 2 | 35.52% | 88.5% | 0 | 0.057708 | 1 | 3.2834 | 0.18948 | Medium | Medium | High | 1441 | 1598 | 0.057708 | 111.348
OILFIELDS 1103N44 | OILFIELDS 1103 | CENTRAL COAST | 18.7718 | 55.8541 | 96.36% | 0 | 0 | 100% | 0% | 0 | 0.079917 | 1 | 2.3613 | 0.18871 | High | High | Medium | 1442 | 1399 | 0.079917 | 111.1585
MORAGA 1104CB | MORAGA 1104 | DIABLO | 12.3977 | 11.1682 | 54.34% | 6 | 17 | 72.33% | 3.443% | 1 | 0.053103 | 1 | 3.5454 | 0.18827 | Medium | Medium | High | 1443 | 1646 | 0.053103 | 110.9698
LAURELES 1111432 | LAURELES 1111 | CENTRAL COAST | 49.1946 | 74.7913 | 100% | 10 | 10 | 100% | 0% | 0 | 0.11153 | 1 | 1.687 | 0.18815 | High | High | Low | 1444 | 1252 | 0.11153 | 110.7815
KESWICK 11011588 | KESWICK 1101 | NORTH VALLEY | 6.9485 | 28.4638 | 99.9% | 2 | 4 | 79.32% | 55.95% | 0 | 0.089394 | 1 | 2.1029 | 0.18799 | High | High | Low | 1445 | 1341 | 0.089394 | 110.5934
GIRVAN 11011330 | GIRVAN 1101 | NORTH VALLEY | 31.2468 | 42.7568 | 99.67% | 0 | 4 | 100% | 24.65% | 1 | 0.13164 | 1 | 1.4253 | 0.18763 | High | High | Low | 1446 | 1194 | 0.13164 | 110.4054
CASTRO VALLEY 1106MR337 | CASTRO VALLEY 1106 | MISSION | 10.471 | 41.4878 | 74.2% | 2 | 2 | 55.31% | 63.23% | 0 | 0.053395 | 1 | 3.5101 | 0.18742 | Medium | Medium | High | 1447 | 1642 | 0.053395 | 110.2178
CAMP EVERS 21035402 | CAMP EVERS 2103 | CENTRAL COAST | 2.8538 | 10 | 29.07% | 11 | 2 | 42.31% | 90.21% | 0 | 0.05912 | 1 | 3.1651 | 0.18712 | Medium | Medium | High | 1448 | 1580 | 0.05912 | 110.0304
DIAMOND SPRINGS 1104CB | DIAMOND SPRINGS 1104 | SIERRA | 6.9541 | 10 | 49.56% | 0 | 3 | 69.41% | 79.56% | 0 | 0.059614 | 1 | 3.1336 | 0.18681 | Medium | Medium | High | 1449 | 1570 | 0.059614 | 109.8432
VOLTA 110297816 | VOLTA 1102 | NORTH VALLEY | 5.2578 | 25.9131 | 100% | 2 | 2 | 100% | 80.28% | 1 | 0.11476 | 1 | 1.6244 | 0.18643 | High | High | Low | 1450 | 1239 | 0.11476 | 109.6564
CURTIS 17029220 | CURTIS 1702 | YOSEMITE | 11.0663 | 17.9965 | 77.35% | 2 | 13 | 99.21% | 0.02567% | 0 | 0.05548 | 1 | 3.3526 | 0.186 | Medium | Medium | High | 1451 | 1618 | 0.05548 | 109.47
HALF MOON BAY 11038920 | HALF MOON BAY 1103 | PENINSULA | 8.6186 | 37.4312 | 39.37% | 7 | 11 | 100% | 0% | 0 | 0.054692 | 1 | 3.3955 | 0.1857 | Medium | Medium | High | 1452 | 1629 | 0.054692 | 109.284
CURTIS 170411300 | CURTIS 1704 | YOSEMITE | 3.6591 | 33.4299 | 41.14% | 0 | 2 | 100% | 62.71% | 0 | 0.065584 | 1 | 2.8287 | 0.18552 | High | High | Medium | 1453 | 1511 | 0.065584 | 109.0983
DEL MONTE 21042624 | DEL MONTE 2104 | CENTRAL COAST | 18.1708 | 31.8719 | 33.21% | 2 | 17 | 94.85% | 0% | 0 | 0.05749 | 1 | 3.2193 | 0.18508 | Medium | Medium | High | 1454 | 1599 | 0.05749 | 108.9128
CAYUCOS 1102CB | CAYUCOS 1102 | LOS PADRES | 11.9239 | 72.3136 | 83.3% | 3 | 2 | 41.34% | 71.02% | 0 | 0.079048 | 1 | 2.3364 | 0.18468 | High | High | Medium | 1455 | 1407 | 0.079048 | 108.7277
WYANDOTTE 11071510 | WYANDOTTE 1107 | NORTH VALLEY | 25.4968 | 11.1229 | 100% | 1 | 4 | 100% | 0% | 0 | 0.05976 | 1 | 3.0899 | 0.18465 | Medium | Medium | High | 1456 | 1567 | 0.05976 | 108.543
SAN JUSTO 11014002 | SAN JUSTO 1101 | CENTRAL COAST | 18.1183 | 71.0394 | 96.75% | 4 | 7 | 95.15% | 0% | 0 | 0.089593 | 1 | 2.061 | 0.18465 | High | High | Low | 1457 | 1339 | 0.089593 | 108.3584
CAMP EVERS 2104CB | CAMP EVERS 2104 | CENTRAL COAST | 1.0591 | 10 | 55.62% | 0 | 2 | 23.71% | 100% | 0 | 0.05446 | 1 | 3.3876 | 0.18449 | Medium | Medium | High | 1458 | 1634 | 0.05446 | 108.1737
KANAKA 11011406 | KANAKA 1101 | NORTH VALLEY | 26.9635 | 16.7709 | 74.27% | 2 | 6 | 97.41% | 16.93% | 0 | 0.097652 | 1 | 1.8891 | 0.18448 | High | High | Low | 1459 | 1303 | 0.097652 | 107.9892
BRUNSWICK 11062790 | BRUNSWICK 1106 | SIERRA | 8.9258 | 13.4181 | 98.75% | 0 | 3 | 81.13% | 52.78% | 0 | 0.084645 | 1 | 2.178 | 0.18435 | High | High | Low | 1460 | 1364 | 0.084645 | 107.8048
APPLE HILL 2102186912 | APPLE HILL 2102 | SIERRA | 48.9257 | 16.1646 | 100% | 9 | 3 | 96.19% | 0% | 0 | 0.093311 | 1 | 1.9754 | 0.18433 | High | High | Low | 1461 | 1322 | 0.093311 | 107.6204
ALTO 1122CB | ALTO 1122 | NORTH BAY | 2.386 | 10 | 11.27% | 0 | 1 | 68.83% | 100% | 0 | 0.05105 | 1 | 3.5941 | 0.18348 | Medium | Medium | High | 1462 | 1671 | 0.05105 | 107.4361
CALPINE 1144304 | CALPINE 1144 | SONOMA | 0.046375 | 85 | 0% | 0 | 0 | 100% | 100% | 0 | 0.098754 | 1 | 1.8471 | 0.18241 | High | High | Low | 1463 | 1299 | 0.098754 | 107.2526
ANNAPOLIS 1101608 | ANNAPOLIS 1101 | HUMBOLDT | 17.8008 | 87.1454 | 94.8% | 10 | 5 | 100% | 0% | 0 | 0.13339 | 1 | 1.3674 | 0.1824 | High | High | Low | 1464 | 1185 | 0.13339 | 107.0702
ORINDA 0401CB | ORINDA 0401 | DIABLO | 0.11326 | 10 | 23.54% | 0 | 0 | 63.88% | 100% | 0 | 0.052555 | 1 | 3.4681 | 0.18227 | Medium | Medium | High | 1465 | 1656 | 0.052555 | 106.8878
OREGON TRAIL 11041634 | OREGON TRAIL 1104 | NORTH VALLEY | 17.7143 | 33.9199 | 93.56% | 1 | 0 | 97.56% | 0% | 0 | 0.067366 | 1 | 2.7053 | 0.18225 | High | High | Medium | 1466 | 1493 | 0.067366 | 106.7055
APPLE HILL 1103CB | APPLE HILL 1103 | SIERRA | 27.6878 | 21.3856 | 62.7% | 5 | 24 | 82.6% | 2.955% | 0 | 0.074928 | 1 | 2.43 | 0.18207 | High | High | Medium | 1467 | 1439 | 0.074928 | 106.5233
BANGOR 11017446 | BANGOR 1101 | NORTH VALLEY | 43.441 | 11.2625 | 85.83% | 3 | 18 | 100% | 0% | 0 | 0.081818 | 1 | 2.2193 | 0.18158 | High | High | Low | 1468 | 1384 | 0.081818 | 106.3412
ARCATA 11225384 | ARCATA 1122 | HUMBOLDT | 15.2841 | 39.9172 | 40.09% | 14 | 5 | 87.62% | 0% | 0 | 0.061973 | 1 | 2.9263 | 0.18135 | High | High | Medium | 1469 | 1540 | 0.061973 | 106.1596
FROGTOWN 170275252 | FROGTOWN 1702 | STOCKTON | 57.5264 | 53.766 | 80.82% | 0 | 20 | 95.14% | 0% | 0 | 0.087181 | 1 | 2.07 | 0.18046 | High | High | Low | 1470 | 1349 | 0.087181 | 105.9783
MONTICELLO 1101718 | MONTICELLO 1101 | NORTH BAY | 26.9011 | 60.1825 | 63.96% | 4 | 11 | 90.43% | 0% | 0 | 0.067428 | 1 | 2.6725 | 0.1802 | High | High | Medium | 1471 | 1491 | 0.067428 | 105.7978
CURTIS 1702CB | CURTIS 1702 | YOSEMITE | 21.952 | 21.1187 | 82.49% | 5 | 14 | 95.73% | 0% | 0 | 0.0532 | 1 | 3.3587 | 0.17868 | Medium | Medium | High | 1472 | 1644 | 0.0532 | 105.6176
HALSEY 11011704 | HALSEY 1101 | SIERRA | 12.7864 | 10 | 79.44% | 4 | 15 | 96.8% | 0% | 0 | 0.071684 | 1 | 2.4891 | 0.17843 | High | High | Medium | 1473 | 1463 | 0.071684 | 105.4389
VIEJO 22029104 | VIEJO 2202 | CENTRAL COAST | 5.9155 | 10 | 5.95% | 8 | 7 | 99.2% | 0% | 0 | 0.054282 | 1 | 3.2793 | 0.17801 | Medium | Medium | High | 1474 | 1635 | 0.054282 | 105.2605
FROGTOWN 170212282 | FROGTOWN 1702 | STOCKTON | 36.3191 | 39.3074 | 54.5% | 2 | 7 | 100% | 0% | 0 | 0.069451 | 1 | 2.557 | 0.17759 | High | High | Medium | 1475 | 1474 | 0.069451 | 105.0825
SONOMA 110478372 | SONOMA 1104 | SONOMA | 16.4405 | 56.415 | 74.14% | 3 | 12 | 96.01% | 0% | 0 | 0.051874 | 1 | 3.4088 | 0.17683 | Medium | Medium | High | 1476 | 1663 | 0.051874 | 104.9049
ECHO SUMMIT 11018922 | ECHO SUMMIT 1101 | (blank) | 2.2784 | 12.8457 | 99.62% | 6 | 2 | 64% | 0% | 0 | 0.13221 | 1 | 1.3369 | 0.17676 | High | High | Low | 1477 | 1193 | 0.13221 | 104.7281
RED BLUFF 11011556 | RED BLUFF 1101 | NORTH VALLEY | 35.2007 | 32.6588 | 100% | 1 | 11 | 88.02% | 0% | 0 | 0.10148 | 1 | 1.7409 | 0.17666 | High | High | Low | 1478 | 1290 | 0.10148 | 104.5513
SAN JOAQUIN #3 1102CB | SAN JOAQUIN #3 1102 | YOSEMITE | 9.6989 | 12.3012 | 62.24% | 3 | 14 | 100% | 56.8% | 0 | 0.1304 | 1 | 1.3465 | 0.17559 | High | High | Low | 1479 | 1196 | 0.1304 | 104.3747
HIGGINS 110950078 | HIGGINS 1109 | SIERRA | 48.4681 | 37.033 | 99.96% | 1 | 15 | 100% | 0% | 0 | 0.068168 | 1 | 2.5691 | 0.17513 | High | High | Medium | 1480 | 1483 | 0.068168 | 104.1991
SANTA YNEZ 1101Y16 | SANTA YNEZ 1101 | LOS PADRES | 7.1745 | 86.5871 | 96.55% | 0 | 1 | 49.62% | 51.9% | 0 | 0.082863 | 1 | 2.1114 | 0.17496 | High | High | Low | 1481 | 1375 | 0.082863 | 104.0239
HIGGINS 110950072 | HIGGINS 1109 | SIERRA | 42.3856 | 25.4799 | 92.02% | 2 | 15 | 100% | 0% | 0 | 0.068313 | 1 | 2.5573 | 0.1747 | High | High | Medium | 1482 | 1482 | 0.068313 | 103.849
TASSAJARA 210419042 | TASSAJARA 2104 | DIABLO | 7.0796 | 47.3825 | 57.65% | 1 | 2 | 83.81% | 25.74% | 0 | 0.045532 | 1 | 3.832 | 0.17448 | Medium | Medium | High | 1483 | 1755 | 0.045532 | 103.6743
OAKLAND X 1106CR006 | OAKLAND X 1106 | EAST BAY | 3.6093 | 38.5923 | 23.16% | 2 | 2 | 100% | 56.08% | 0 | 0.054619 | 1 | 3.186 | 0.17401 | Medium | Medium | High | 1484 | 1630 | 0.054619 | 103.4998
COARSEGOLD 21045525 | COARSEGOLD 2104 | YOSEMITE | 13.0444 | 10.8034 | 99.82% | 2 | 45 | 100% | 0% | 0 | 0.072179 | 1 | 2.4095 | 0.17392 | High | High | Medium | 1485 | 1460 | 0.072179 | 103.3258
SAN RAMON 2107MR287 | SAN RAMON 2107 | MISSION | 0.029952 | 10 | 100% | 0 | 0 | 0.9859% | 100% | 0 | 0.052586 | 1 | 3.3036 | 0.17373 | Medium | Medium | High | 1486 | 1654 | 0.052586 | 103.1519
BIG RIVER 110179628 | BIG RIVER 1101 | HUMBOLDT | 14.7546 | 28.3298 | 27.17% | 16 | 19 | 100% | 0% | 0 | 0.06147 | 1 | 2.8171 | 0.17317 | Medium | Medium | Medium | 1487 | 1551 | 0.06147 | 102.9781
OAKLAND X 1106CR008 | OAKLAND X 1106 | EAST BAY | 4.2343 | 10.8634 | 21.85% | 11 | 17 | 100% | 13.39% | 0 | 0.051531 | 1 | 3.3497 | 0.17261 | Medium | Medium | High | 1488 | 1667 | 0.051531 | 102.805
PACIFICA 1102CB | PACIFICA 1102 | PENINSULA | 2.2873 | 19.4 | 0% | 0 | 1 | 33.56% | 100% | 0 | 0.040266 | 1 | 4.2842 | 0.17251 | Medium | Medium | High | 1489 | 1849 | 0.040266 | 102.6324
CALAVERAS CEMENT 11011419 | CALAVERAS CEMENT 1101 | STOCKTON | 15.0795 | 14.8417 | 100% | 2 | 7 | 100% | 0% | 0 | 0.074427 | 1 | 2.3142 | 0.17224 | High | High | Medium | 1490 | 1443 | 0.074427 | 102.4599
PINE GROVE 11026080 | PINE GROVE 1102 | STOCKTON | 34.785 | 21.8457 | 100% | 6 | 11 | 100% | 0.6625% | 0 | 0.089074 | 1 | 1.9325 | 0.17213 | High | High | Low | 1491 | 1342 | 0.089074 | 102.2876
AUBERRY 1102R2850 | AUBERRY 1102 | FRESNO | 25.8464 | 30.8369 | 100% | 0 | 16 | 100% | 0% | 0 | 0.095456 | 1 | 1.8012 | 0.17193 | High | High | Low | 1492 | 1312 | 0.095456 | 102.1155
MOUNTAIN QUARRIES 21011346 | MOUNTAIN QUARRIES 2101 | SIERRA | 30.7365 | 10.3256 | 98.49% | 5 | 12 | 100% | 0% | 0 | 0.072232 | 1 | 2.3792 | 0.17186 | High | High | Medium | 1493 | 1458 | 0.072232 | 101.9436
CAMP EVERS 2103CB | CAMP EVERS 2103 | CENTRAL COAST | 0.092755 | 10 | 13.07% | 0 | 0 | 75.74% | 100% | 0 | 0.061458 | 1 | 2.7937 | 0.17169 | Medium | Medium | Medium | 1494 | 1552 | 0.061458 | 101.7717
PEORIA 17051834 | PEORIA 1705 | YOSEMITE | 22.9121 | 21.3201 | 69.84% | 0 | 15 | 96.15% | 0% | 0 | 0.076648 | 1 | 2.2374 | 0.17149 | High | High | Medium | 1495 | 1428 | 0.076648 | 101.6
ALTO 11251158 | ALTO 1125 | NORTH BAY | 2.2748 | 24.9991 | 11.61% | 1 | 1 | 41.4% | 88.18% | 0 | 0.041574 | 1 | 4.1164 | 0.17113 | Medium | Medium | High | 1496 | 1826 | 0.041574 | 101.4285
FORT BRAGG A 1102418 | FORT BRAGG A 1102 | HUMBOLDT | 13.7424 | 13.0618 | 15.86% | 29 | 14 | 98.4% | 0% | 0 | 0.053533 | 1 | 3.1937 | 0.17097 | Medium | Medium | High | 1497 | 1641 | 0.053533 | 101.2574
GEYSERVILLE 1102484 | GEYSERVILLE 1102 | SONOMA | 33.3601 | 63.5348 | 83.52% | 3 | 7 | 68.39% | 43.97% | 0 | 0.12892 | 1 | 1.3254 | 0.17087 | High | High | Low | 1498 | 1202 | 0.12892 | 101.0864
PLACERVILLE 2106CB | PLACERVILLE 2106 | SIERRA | 6.6569 | 17.5661 | 15.58% | 1 | 6 | 100% | 71.65% | 0 | 0.069168 | 1 | 2.4573 | 0.16996 | High | High | Medium | 1499 | 1477 | 0.069168 | 100.9155
TEMPLETON 2113CB | TEMPLETON 2113 | LOS PADRES | 0.49234 | 10 | 22.58% | 0 | 0 | 1.889% | 0% | 0 | 0.0057624 | 11.2183 | 2.6278 | 0.16987 | Low | Low | Medium | 1500 | 1517 | 0.064645 | 100.7456
DUNBAR 1103440 | DUNBAR 1103 | SONOMA | 3.5573 | 21.3081 | 50.04% | 0 | 2 | 25.85% | 93.78% | 0 | 0.045809 | 1 | 3.7008 | 0.16953 | Medium | Medium | High | 1501 | 1751 | 0.045809 | 100.5757
BIG BASIN 11022253 | BIG BASIN 1102 | CENTRAL COAST | 1.463 | 10 | 16.17% | 0 | 0 | 100% | 100% | 0 | 0.069736 | 1 | 2.4273 | 0.16927 | High | High | Medium | 1502 | 1473 | 0.069736 | 100.4062
BRUNSWICK 110651484 | BRUNSWICK 1106 | SIERRA | 20.7709 | 48.7311 | 68.62% | 4 | 3 | 82.69% | 37.09% | 0 | 0.070762 | 1 | 2.3766 | 0.16817 | High | High | Medium | 1503 | 1467 | 0.070762 | 100.2369
SILVERADO 2105CB | SILVERADO 2105 | NORTH BAY | 0.47706 | 10 | 63.84% | 0 | 1 | 10.39% | 100% | 0 | 0.044175 | 1 | 3.805 | 0.16809 | Medium | Medium | High | 1504 | 1773 | 0.044175 | 100.0687
VIEJO 22019114 | VIEJO 2201 | CENTRAL COAST | 6.3385 | 10 | 15.64% | 12 | 5 | 93.11% | 0% | 0 | 0.043315 | 1 | 3.8689 | 0.16758 | Medium | Medium | High | 1505 | 1789 | 0.043315 | 99.9006
CLAYTON 221355668 | CLAYTON 2213 | DIABLO | 3.8789 | 27.0823 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041308 | 1 | 4.0479 | 0.16721 | Medium | Medium | High | 1506 | 1829 | 0.041308 | 99.7331
GANSNER 11012424 | GANSNER 1101 | NORTH VALLEY | 18.9007 | 82.3071 | 77.09% | 4 | 10 | 100% | 0% | 0 | 0.081226 | 1 | 2.0492 | 0.16645 | High | High | Low | 1507 | 1389 | 0.081226 | 99.5658
OCEANO 1104V38 | OCEANO 1104 | LOS PADRES | 12.9054 | 24.0827 | 46.82% | 5 | 8 | 68.56% | 8.41% | 1 | 0.053152 | 1 | 3.1233 | 0.16601 | Medium | Medium | High | 1508 | 1645 | 0.053152 | 99.3994
SARATOGA 1103LC16 | SARATOGA 1103 | DE ANZA | 4.0893 | 10 | 47.33% | 3 | 10 | 80.63% | 0% | 0 | 0.042849 | 1 | 3.8592 | 0.16536 | Medium | Medium | High | 1509 | 1802 | 0.042849 | 99.2334
LUCERNE 110638436 | LUCERNE 1106 | HUMBOLDT | 4.6279 | 61.4353 | 100% | 0 | 7 | 96.43% | 0% | 0 | 0.044553 | 1 | 3.7075 | 0.16518 | Medium | Medium | High | 1510 | 1768 | 0.044553 | 99.068
CALPINE 1144276-G | CALPINE 1144 | SONOMA | 0.014761 | 75 | 0% | 0 | 0 | 100% | 100% | 0 | 0.092831 | 1 | 1.7759 | 0.16486 | High | High | Low | 1511 | 1324 | 0.092831 | 98.9028
WOODSIDE 110411555 | WOODSIDE 1104 | PENINSULA | 0.85806 | 10 | 96.59% | 0 | 1 | 100% | 0% | 0 | 0.032229 | 1 | 5.0953 | 0.16422 | Medium | Medium | High | 1512 | 2037 | 0.032229 | 98.738
MARIPOSA 21014410 | MARIPOSA 2101 | YOSEMITE | 22.8041 | 16.019 | 99.74% | 6 | 25 | 100% | 48.37% | 1 | 0.13823 | 1 | 1.1854 | 0.16386 | High | High | Low | 1513 | 1172 | 0.13823 | 98.5738
TIVY VALLEY 1107584840 | TIVY VALLEY 1107 | FRESNO | 44.9458 | 14.7533 | 99.99% | 0 | 18 | 100% | 0% | 0 | 0.079403 | 1 | 2.0582 | 0.16342 | High | High | Low | 1514 | 1404 | 0.079403 | 98.4099
ROSSMOOR 1108CB | ROSSMOOR 1108 | DIABLO | 3.0229 | 50.0663 | 2.294% | 0 | 11 | 53.4% | 61.71% | 0 | 0.040788 | 1 | 3.9971 | 0.16304 | Medium | Medium | High | 1515 | 1836 | 0.040788 | 98.2465
MARIPOSA 210110070 | MARIPOSA 2101 | YOSEMITE | 25.9306 | 26.9034 | 96.01% | 1 | 27 | 100% | 0% | 0 | 0.078332 | 1 | 2.0789 | 0.16285 | High | High | Low | 1516 | 1410 | 0.078332 | 98.0834
NORTH TOWER 2101CB | NORTH TOWER 2101 | NORTH BAY | 0.18972 | 10 | 0% | 0 | 0 | 4.663% | 0% | 0 | 0.0049217 | 11.2183 | 2.9474 | 0.16274 | Low | Low | Medium | 1517 | 1623 | 0.055213 | 97.9206
CLAY 110113442 | CLAY 1101 | STOCKTON | 25.1981 | 33.4611 | 98.28% | 1 | 6 | 81.01% | 0% | 0 | 0.059218 | 1 | 2.7463 | 0.16263 | Medium | Medium | Medium | 1518 | 1577 | 0.059218 | 97.7579
TEMPLETON 2110R90 | TEMPLETON 2110 | LOS PADRES | 27.6614 | 57.9463 | 69.12% | 2 | 5 | 77.95% | 0% | 0 | 0.077528 | 1 | 2.0934 | 0.1623 | High | High | Low | 1519 | 1417 | 0.077528 | 97.5952
BELL 11082202 | BELL 1108 | SIERRA | 31.9475 | 20.6823 | 70.59% | 0 | 8 | 96.19% | 0% | 0 | 0.059129 | 1 | 2.7384 | 0.16192 | Medium | Medium | Medium | 1520 | 1579 | 0.059129 | 97.4329
RACETRACK 1703CB | RACETRACK 1703 | YOSEMITE | 15.5569 | 10 | 47.8% | 4 | 26 | 86.61% | 0% | 0 | 0.05588 | 1 | 2.884 | 0.16116 | Medium | Medium | Medium | 1521 | 1613 | 0.05588 | 97.271
RINCON 1104CB | RINCON 1104 | SONOMA | 2.6764 | 10 | 22.48% | 3 | 5 | 47.86% | 77.17% | 0 | 0.046471 | 1 | 3.464 | 0.16098 | Medium | Medium | High | 1522 | 1731 | 0.046471 | 97.1099
KONOCTI 1102596 | KONOCTI 1102 | HUMBOLDT | 8.591 | 44.5897 | 35.58% | 1 | 10 | 63.73% | 0% | 0 | 0.046139 | 1 | 3.4882 | 0.16094 | Medium | Medium | High | 1523 | 1738 | 0.046139 | 96.9489
VOLTA 110293418 | VOLTA 1102 | NORTH VALLEY | 2.6513 | 65.9048 | 100% | 5 | 0 | 100% | 44.92% | 0 | 0.087226 | 1 | 1.8377 | 0.1603 | High | High | Low | 1524 | 1348 | 0.087226 | 96.7879
SANTA ROSA A 1104CB | SANTA ROSA A 1104 | SONOMA | 1.1731 | 10 | 48.07% | 0 | 1 | 19.25% | 100% | 0 | 0.042461 | 1 | 3.7672 | 0.15996 | Medium | Medium | High | 1525 | 1808 | 0.042461 | 96.6276
NORTH DUBLIN 2103CB | NORTH DUBLIN 2103 | MISSION | 12.6489 | 55.8047 | 31.35% | 1 | 2 | 83.95% | 0% | 0 | 0.043695 | 1 | 3.6462 | 0.15932 | Medium | Medium | High | 1526 | 1783 | 0.043695 | 96.4677
GUALALA 111135562 | GUALALA 1111 | HUMBOLDT | 14.2585 | 63.006 | 19.44% | 12 | 36 | 100% | 0% | 0 | 0.084547 | 1 | 1.8822 | 0.15913 | High | High | Low | 1527 | 1366 | 0.084547 | 96.3084
CURTIS 170463502 | CURTIS 1704 | YOSEMITE | 10.4605 | 25.8863 | 57.75% | 1 | 16 | 100% | 0% | 0 | 0.052892 | 1 | 3.0037 | 0.15887 | Medium | Medium | Medium | 1528 | 1650 | 0.052892 | 96.1492
ALTO 1125CB | ALTO 1125 | NORTH BAY | 0.27217 | 10 | 45.49% | 2 | 1 | 11.73% | 100% | 0 | 0.039699 | 1 | 3.9974 | 0.15869 | Medium | Medium | High | 1529 | 1865 | 0.039699 | 95.9904
HIGHLANDS 110448262 | HIGHLANDS 1104 | HUMBOLDT | 5.8216 | 10 | 84.42% | 0 | 6 | 100% | 0% | 0 | 0.047568 | 1 | 3.314 | 0.15764 | Medium | Medium | High | 1530 | 1716 | 0.047568 | 95.8317
ROSSMOOR 110168920 | ROSSMOOR 1101 | DIABLO | 5.9925 | 29.5829 | 31.67% | 8 | 11 | 82.31% | 24.74% | 0 | 0.047645 | 1 | 3.3031 | 0.15738 | Medium | Medium | High | 1531 | 1712 | 0.047645 | 95.674
ROB ROY 210410954 | ROB ROY 2104 | CENTRAL COAST | 7.1077 | 10 | 88.57% | 7 | 3 | 100% | 0% | 0 | 0.050548 | 1 | 3.1113 | 0.15727 | Medium | Medium | High | 1532 | 1676 | 0.050548 | 95.5166
HIGGINS 1109594 | HIGGINS 1109 | SIERRA | 14.2898 | 11.2028 | 80.24% | 1 | 11 | 100% | 0% | 0 | 0.051909 | 1 | 3.0273 | 0.15715 | Medium | Medium | Medium | 1533 | 1662 | 0.051909 | 95.3594
UKIAH 1114408 | UKIAH 1114 | HUMBOLDT | 37.0058 | 66.3521 | 67.33% | 5 | 13 | 97.48% | 0% | 0 | 0.071452 | 1 | 2.1941 | 0.15678 | High | High | Low | 1534 | 1464 | 0.071452 | 95.2022
FORT BRAGG A 11044690 | FORT BRAGG A 1104 | HUMBOLDT | 12.2439 | 49.0226 | 37.04% | 15 | 12 | 85.93% | 0% | 0 | 0.050332 | 1 | 3.1146 | 0.15677 | Medium | Medium | High | 1535 | 1680 | 0.050332 | 95.0454
PALO SECO 0401CB | PALO SECO 0401 | EAST BAY | 4.7078 | 10 | 0% | 4 | 1 | 100% | 18.75% | 0 | 0.035354 | 1 | 4.4285 | 0.15657 | Medium | Medium | High | 1536 | 1951 | 0.035354 | 94.8887
SHINGLE SPRINGS 2110CB | SHINGLE SPRINGS 2110 | SIERRA | 0.10881 | 10 | 92.58% | 0 | 0 | 8.524% | 92.58% | 0 | 0.047519 | 1 | 3.2729 | 0.15553 | Medium | Medium | High | 1537 | 1717 | 0.047519 | 94.7321
PACIFICA 11033907 | PACIFICA 1103 | PENINSULA | 3.5027 | 51.2022 | 0% | 4 | 0 | 72.69% | 71.75% | 0 | 0.042148 | 1 | 3.6814 | 0.15517 | Medium | Medium | High | 1538 | 1815 | 0.042148 | 94.5766
ECHO SUMMIT 11012500 | ECHO SUMMIT 1101 | (blank) | 2.8817 | 10 | 100% | 2 | 2 | 100% | 0% | 0 | 0.074119 | 1 | 2.0914 | 0.15501 | High | High | Low | 1539 | 1445 | 0.074119 | 94.4214
BIG RIVER 11013002 | BIG RIVER 1101 | HUMBOLDT | 6.8985 | 10 | 4.337% | 11 | 17 | 83.84% | 0% | 0 | 0.058669 | 1 | 2.6346 | 0.15457 | Medium | Medium | Medium | 1540 | 1584 | 0.058669 | 94.2664
CAMP EVERS 21035404 | CAMP EVERS 2103 | CENTRAL COAST | 2.6779 | 10 | 26.91% | 3 | 0 | 57.99% | 100% | 0 | 0.052978 | 1 | 2.9173 | 0.15455 | Medium | Medium | Medium | 1541 | 1649 | 0.052978 | 94.1118
BANGOR 11011804 | BANGOR 1101 | NORTH VALLEY | 42.8631 | 13.9127 | 93.17% | 8 | 9 | 100% | 3.48% | 0 | 0.064625 | 1 | 2.3914 | 0.15455 | High | High | Medium | 1542 | 1518 | 0.064625 | 93.9573
MORGAN HILL 2105XR070 | MORGAN HILL 2105 | SAN JOSE | 6.67 | 37.7183 | 68.61% | 0 | 0 | 76.77% | 50.18% | 1 | 0.046839 | 1 | 3.2954 | 0.15435 | Medium | Medium | High | 1543 | 1726 | 0.046839 | 93.8027
SHINGLE SPRINGS 210981390 | SHINGLE SPRINGS 2109 | SIERRA | 18.7493 | 21.0161 | 63.9% | 1 | 8 | 100% | 0% | 0 | 0.075764 | 1 | 2.0292 | 0.15374 | High | High | Low | 1544 | 1436 | 0.075764 | 93.6484
JARVIS 1111MR121 | JARVIS 1111 | MISSION | 1.1185 | 70.124 | 6.252% | 0 | 0 | 20.83% | 100% | 0 | 0.045013 | 1 | 3.4072 | 0.15337 | Medium | Medium | High | 1545 | 1765 | 0.045013 | 93.4946
ALTO 112278672 | ALTO 1122 | NORTH BAY | 2.7277 | 18.1694 | 27.03% | 6 | 9 | 33.13% | 66.64% | 0 | 0.042144 | 1 | 3.6273 | 0.15287 | Medium | Medium | High | 1546 | 1816 | 0.042144 | 93.3413
CORNING 11021622 | CORNING 1102 | NORTH VALLEY | 34.031 | 83.6384 | 99.67% | 1 | 6 | 100% | 0% | 0 | 0.11037 | 1 | 1.3788 | 0.15218 | High | High | Low | 1547 | 1257 | 0.11037 | 93.1884
PHILO 1101CB | PHILO 1101 | HUMBOLDT | 30.1647 | 49.3506 | 76.4% | 12 | 16 | 60.92% | 0% | 0 | 0.072449 | 1 | 2.0932 | 0.15165 | High | High | Low | 1548 | 1456 | 0.072449 | 93.0362
CLOVERDALE 1102674 | CLOVERDALE 1102 | SONOMA | 17.0598 | 62.482 | 68.42% | 4 | 8 | 84.92% | 25.35% | 0 | 0.082178 | 1 | 1.8325 | 0.15059 | High | High | Low | 1549 | 1381 | 0.082178 | 92.8846
DOBBINS 110191464 | DOBBINS 1101 | SIERRA | 7.0765 | 18.3456 | 88.34% | 2 | 2 | 100% | 2.371% | 0 | 0.050871 | 1 | 2.9545 | 0.1503 | Medium | Medium | Medium | 1550 | 1674 | 0.050871 | 92.734
STANISLAUS 170179826 | STANISLAUS 1701 | YOSEMITE | 10.1928 | 54.2786 | 66.14% | 1 | 7 | 100% | 0% | 0 | 0.044036 | 1 | 3.4104 | 0.15018 | Medium | Medium | High | 1551 | 1777 | 0.044036 | 92.5837
SAND CREEK 110345190 | SAND CREEK 1103 | FRESNO | 36.6214 | 13.3834 | 99.51% | 0 | 5 | 100% | 0% | 0 | 0.078024 | 1 | 1.9196 | 0.14977 | High | High | Low | 1552 | 1413 | 0.078024 | 92.4335
MONTICELLO 1101630 | MONTICELLO 1101 | NORTH BAY | 17.6986 | 68.0589 | 26.54% | 2 | 4 | 90.07% | 0% | 0 | 0.065491 | 1 | 2.2846 | 0.14962 | High | High | Medium | 1553 | 1513 | 0.065491 | 92.2837
SPRING GAP 1702CB | SPRING GAP 1702 | YOSEMITE | 7.418 | 94.1072 | 60.1% | 3 | 1 | 100% | 85.76% | 0 | 0.17407 | 1 | 0.85687 | 0.14916 | High | High | Low | 1554 | 1105 | 0.17407 | 92.1341
NOTRE DAME 11042408 | NOTRE DAME 1104 | NORTH VALLEY | 11.2331 | 23.0626 | 36.02% | 1 | 3 | 81.2% | 47.16% | 1 | 0.051652 | 1 | 2.8875 | 0.14914 | Medium | Medium | Medium | 1555 | 1665 | 0.051652 | 91.985
TASSAJARA 2112D514R | TASSAJARA 2112 | DIABLO | 3.458 | 10.5192 | 20.09% | 0 | 5 | 72.43% | 34.87% | 0 | 0.03721 | 1 | 4.003 | 0.14895 | Medium | Medium | High | 1556 | 1913 | 0.03721 | 91.8358
GRASS VALLEY 11012208 | GRASS VALLEY 1101 | SIERRA | 12.2835 | 20.913 | 70.74% | 4 | 7 | 96.31% | 0% | 0 | 0.053929 | 1 | 2.7592 | 0.1488 | Medium | Medium | Medium | 1557 | 1638 | 0.053929 | 91.6869
SAN LEANDRO U 1109CR182 | SAN LEANDRO U 1109 | MISSION | 4.81 | 10 | 62.88% | 5 | 1 | 100% | 19.48% | 0 | 0.046108 | 1 | 3.2168 | 0.14832 | Medium | Medium | High | 1558 | 1740 | 0.046108 | 91.5381
INDIAN FLAT 1104CB | INDIAN FLAT 1104 | YOSEMITE | 12.7115 | 39.8985 | 69.22% | 2 | 12 | 100% | 0% | 0 | 0.075983 | 1 | 1.9513 | 0.14826 | High | High | Low | 1559 | 1433 | 0.075983 | 91.3897
GREENBRAE 11036083 | GREENBRAE 1103 | NORTH BAY | 0.34152 | 10 | 10.92% | 0 | 0 | 100% | 67.56% | 0 | 0.040594 | 1 | 3.6438 | 0.14792 | Medium | Medium | High | 1560 | 1839 | 0.040594 | 91.2415
CALISTOGA 1101 | CALISTOGA 1101 | NORTH BAY | 0.0027683 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 2.3953 | 0.14745 | High | High | Medium | 1561 | 1545 | 0.061559 | 91.0936
CALPELLA 1101600 | CALPELLA 1101 | HUMBOLDT | 20.3203 | 63.0301 | 92.94% | 2 | 3 | 76.37% | 16.27% | 1 | 0.080296 | 1 | 1.8322 | 0.14712 | High | High | Low | 1562 | 1397 | 0.080296 | 90.9461
MORGAN HILL 2111XR292 | MORGAN HILL 2111 | SAN JOSE | 10.8242 | 23.3354 | 98.35% | 1 | 8 | 89.12% | 0% | 0 | 0.048423 | 1 | 3.0382 | 0.14712 | Medium | Medium | Medium | 1563 | 1702 | 0.048423 | 90.799
FORT BRAGG A 1102956 | FORT BRAGG A 1102 | HUMBOLDT | 10.8506 | 10 | 43.99% | 19 | 14 | 88.12% | 0% | 0 | 0.067263 | 1 | 2.1825 | 0.1468 | High | High | Low | 1564 | 1496 | 0.067263 | 90.6519
CURTIS 17058110 | CURTIS 1705 | YOSEMITE | 8.154 | 12.6611 | 71.8% | 0 | 7 | 100% | 22.12% | 0 | 0.043018 | 1 | 3.3987 | 0.14621 | Medium | Medium | High | 1565 | 1796 | 0.043018 | 90.5051
SARATOGA 1105LC14 | SARATOGA 1105 | DE ANZA | 9.6151 | 10 | 69.49% | 2 | 9 | 86.08% | 0% | 0 | 0.040305 | 1 | 3.6261 | 0.14615 | Medium | Medium | High | 1566 | 1847 | 0.040305 | 90.3589
LOS GATOS 1101LB40 | LOS GATOS 1101 | DE ANZA | 7.214 | 10 | 65.42% | 2 | 3 | 77.51% | 0% | 0 | 0.041155 | 1 | 3.5497 | 0.14609 | Medium | Medium | High | 1567 | 1832 | 0.041155 | 90.2127
SILVERADO 2104806 | SILVERADO 2104 | NORTH BAY | 20.224 | 80.8764 | 82.09% | 0 | 5 | 59.08% | 2.927% | 0 | 0.051436 | 1 | 2.8358 | 0.14586 | Medium | Medium | Medium | 1568 | 1668 | 0.051436 | 90.0666
RINCON 1101576 | RINCON 1101 | SONOMA | 2.0608 | 10 | 77.6% | 0 | 6 | 19.69% | 79.16% | 0 | 0.055451 | 1 | 2.6301 | 0.14585 | Medium | Medium | Medium | 1569 | 1619 | 0.055451 | 89.9208
GRASS VALLEY 11031700 | GRASS VALLEY 1103 | SIERRA | 21.5982 | 19.8547 | 93.5% | 3 | 7 | 99.55% | 0% | 0 | 0.057412 | 1 | 2.5384 | 0.14573 | Medium | Medium | Medium | 1570 | 1601 | 0.057412 | 89.7749
FROGTOWN 1702290609 | FROGTOWN 1702 | STOCKTON | 18.0385 | 28.1983 | 98.5% | 3 | 10 | 100% | 0% | 0 | 0.059181 | 1 | 2.4612 | 0.14566 | Medium | Medium | Medium | 1571 | 1578 | 0.059181 | 89.6292
WILLOW CREEK 110129362 | WILLOW CREEK 1101 | HUMBOLDT | 6.8106 | 67.3887 | 96.73% | 8 | 5 | 58.77% | 100% | 1 | 0.16769 | 1 | 0.86685 | 0.14536 | High | High | Low | 1572 | 1116 | 0.16769 | 89.4835
PAUL SWEET 2102CB | PAUL SWEET 2102 | CENTRAL COAST | 0.80988 | 10 | 58.15% | 0 | 0 | 13.51% | 100% | 0 | 0.042651 | 1 | 3.4078 | 0.14534 | Medium | Medium | High | 1573 | 1805 | 0.042651 | 89.3382
WILLOW CREEK 11032936 | WILLOW CREEK 1103 | HUMBOLDT | 32.9597 | 79.3849 | 82.84% | 19 | 24 | 100% | 0% | 0 | 0.12943 | 1 | 1.1228 | 0.14532 | High | High | Low | 1574 | 1201 | 0.12943 | 89.1928
MIDDLETOWN 11021312 | MIDDLETOWN 1102 | HUMBOLDT | 9.8496 | 13.9462 | 100% | 1 | 10 | 100% | 0% | 0 | 0.046919 | 1 | 3.0951 | 0.14522 | Medium | Medium | High | 1575 | 1725 | 0.046919 | 89.0475
MOUNTAIN QUARRIES 21011350 | MOUNTAIN QUARRIES 2101 | SIERRA | 21.7386 | 30.8372 | 63.86% | 7 | 7 | 100% | 0% | 0 | 0.058591 | 1 | 2.4681 | 0.14461 | Medium | Medium | Medium | 1576 | 1585 | 0.058591 | 88.9023
RED BLUFF 11031702 | RED BLUFF 1103 | NORTH VALLEY | 15.929 | 23.8535 | 100% | 1 | 4 | 87.44% | 0% | 0 | 0.073954 | 1 | 1.9176 | 0.14181 | High | High | Low | 1577 | 1446 | 0.073954 | 88.7577
OAKHURST 11035732 | OAKHURST 1103 | YOSEMITE | 3.391 | 10.7516 | 100% | 0 | 1 | 100% | 54.98% | 0 | 0.087919 | 1 | 1.6062 | 0.14122 | High | High | Low | 1578 | 1345 | 0.087919 | 88.6159
TEMPLETON 2110N32 | TEMPLETON 2110 | LOS PADRES | 28.0596 | 53.4927 | 95.78% | 1 | 9 | 94.62% | 0% | 0 | 0.061984 | 1 | 2.2723 | 0.14084 | High | High | Medium | 1579 | 1539 | 0.061984 | 88.4746
LAURELES 111268454 | LAURELES 1112 | CENTRAL COAST | 8.3342 | 11.1816 | 20.6% | 3 | 7 | 75.56% | 0% | 0 | 0.059265 | 1 | 2.3713 | 0.14054 | Medium | Medium | Medium | 1580 | 1576 | 0.059265 | 88.3338
WYANDOTTE 110777578 | WYANDOTTE 1107 | NORTH VALLEY | 21.5731 | 10.2179 | 61.38% | 5 | 2 | 66.83% | 0% | 0 | 0.036666 | 1 | 3.8294 | 0.14041 | Medium | Medium | High | 1581 | 1925 | 0.036666 | 88.1933
HOOPA 11013304 | HOOPA 1101 | HUMBOLDT | 16.9885 | 82.5702 | 98.71% | 15 | 4 | 100% | 0% | 0 | 0.086315 | 1 | 1.6263 | 0.14037 | High | High | Low | 1582 | 1353 | 0.086315 | 88.0529
OAKLAND K 1104CR210 | OAKLAND K 1104 | EAST BAY | 2.8215 | 10 | 11.97% | 1 | 0 | 100% | 42.91% | 0 | 0.032016 | 1 | 4.383 | 0.14033 | Medium | Medium | High | 1583 | 2047 | 0.032016 | 87.9125
MIDDLETOWN 1103830 | MIDDLETOWN 1103 | HUMBOLDT | 23.5041 | 79 | 88.01% | 1 | 2 | 60.51% | 36.87% | 0 | 0.059437 | 1 | 2.354 | 0.13991 | Medium | Medium | Medium | 1584 | 1572 | 0.059437 | 87.7722
CURTIS 1704803 | CURTIS 1704 | YOSEMITE | 9.5141 | 57.4155 | 65.91% | 1 | 6 | 100% | 27.61% | 0 | 0.05233 | 1 | 2.6661 | 0.13952 | Medium | Medium | Medium | 1585 | 1658 | 0.05233 | 87.6322
OREGON TRAIL 11021584 | OREGON TRAIL 1102 | NORTH VALLEY | 13.0863 | 23.8771 | 100% | 1 | 4 | 100% | 0% | 0 | 0.050417 | 1 | 2.7558 | 0.13894 | Medium | Medium | Medium | 1586 | 1677 | 0.050417 | 87.4927
CURTIS 1705CB | CURTIS 1705 | YOSEMITE | 13.2215 | 11.2937 | 56.4% | 2 | 15 | 96.23% | 0% | 0 | 0.040107 | 1 | 3.4615 | 0.13883 | Medium | Medium | High | 1587 | 1854 | 0.040107 | 87.3538
HIGGINS 1104324510 | HIGGINS 1104 | SIERRA | 12.4769 | 10 | 100% | 3 | 3 | 100% | 0% | 0 | 0.046303 | 1 | 2.9958 | 0.13872 | Medium | Medium | Medium | 1588 | 1735 | 0.046303 | 87.215
HALF MOON BAY 11022032 | HALF MOON BAY 1102 | PENINSULA | 3.27 | 24.2985 | 27.09% | 1 | 0 | 29.71% | 73.93% | 0 | 0.032761 | 1 | 4.2337 | 0.1387 | Medium | Medium | High | 1589 | 2017 | 0.032761 | 87.0762
LAURELES 11116421 | LAURELES 1111 | CENTRAL COAST | 1.7279 | 54.1809 | 100% | 1 | 1 | 100% | 0% | 0 | 0.065512 | 1 | 2.115 | 0.13856 | High | High | Low | 1590 | 1512 | 0.065512 | 86.9375
BUELLTON 1101Y06 | BUELLTON 1101 | LOS PADRES | 29.0172 | 49.4932 | 60.5% | 0 | 10 | 72.26% | 0% | 0 | 0.079416 | 1 | 1.7409 | 0.13826 | High | High | Low | 1591 | 1403 | 0.079416 | 86.799
SHINGLE SPRINGS 11038752 | SHINGLE SPRINGS 1103 | SIERRA | 1.8752 | 10 | 77.05% | 0 | 1 | 100% | 7.72% | 0 | 0.040295 | 1 | 3.4298 | 0.1382 | Medium | Medium | High | 1592 | 1848 | 0.040295 | 86.6607
STILLWATER 1102CB | STILLWATER 1102 | NORTH VALLEY | 25.0709 | 15.0844 | 83.36% | 3 | 7 | 99.96% | 0% | 0 | 0.066396 | 1 | 2.0763 | 0.13786 | High | High | Low | 1593 | 1502 | 0.066396 | 86.5225
BUELLTON 1101Y36 | BUELLTON 1101 | LOS PADRES | 33.0581 | 70.2256 | 71.54% | 1 | 11 | 92.67% | 5.931% | 1 | 0.081946 | 1 | 1.6819 | 0.13782 | High | High | Low | 1594 | 1383 | 0.081946 | 86.3847
DIAMOND SPRINGS 11062100 | DIAMOND SPRINGS 1106 | SIERRA | 38.9747 | 13.5244 | 95.18% | 3 | 8 | 100% | 0% | 0 | 0.064847 | 1 | 2.1227 | 0.13765 | High | High | Low | 1595 | 1514 | 0.064847 | 86.2468
WOODACRE 11021280 | WOODACRE 1102 | NORTH BAY | 10.5964 | 14.7487 | 31.13% | 2 | 14 | 100% | 0% | 0 | 0.034114 | 1 | 4.0304 | 0.1375 | Medium | Medium | High | 1596 | 1973 | 0.034114 | 86.1092
WEIMAR 11012740 | WEIMAR 1101 | SIERRA | 19.1962 | 52.0643 | 71.74% | 1 | 4 | 100% | 0% | 0 | 0.080042 | 1 | 1.7168 | 0.13742 | High | High | Low | 1597 | 1398 | 0.080042 | 85.9717
OAKLAND K 1104CB | OAKLAND K 1104 | EAST BAY | 2.7076 | 10 | 13.99% | 1 | 4 | 100% | 34.6% | 0 | 0.030956 | 1 | 4.4174 | 0.13675 | Medium | Medium | High | 1598 | 2071 | 0.030956 | 85.8343
SHINGLE SPRINGS 210911092 | SHINGLE SPRINGS 2109 | SIERRA | 22.1149 | 21.1094 | 82.77% | 7 | 7 | 100% | 0% | 0 | 0.081649 | 1 | 1.6738 | 0.13667 | High | High | Low | 1599 | 1386 | 0.081649 | 85.6975
FORT BRAGG A 110235592 | FORT BRAGG A 1102 | HUMBOLDT | 13.0568 | 10.5094 | 9.263% | 19 | 29 | 100% | 0% | 0 | 0.068352 | 1 | 1.999 | 0.13663 | High | High | Low | 1600 | 1481 | 0.068352 | 85.5609
FULTON 110746958 | FULTON 1107 | SONOMA | 0.032131 | 10 | 100% | 0 | 0 | 6.208% | 100% | 0 | 0.055255 | 1 | 2.4591 | 0.13588 | Medium | Medium | Medium | 1601 | 1622 | 0.055255 | 85.4242
LOS GATOS 1107CB | LOS GATOS 1107 | DE ANZA | 13.6639 | 15.4902 | 38.19% | 1 | 13 | 86.42% | 10.54% | 0 | 0.041286 | 1 | 3.2819 | 0.1355 | Medium | Medium | High | 1602 | 1831 | 0.041286 | 85.2884
BELL 11082226 | BELL 1108 | SIERRA | 24.7638 | 11.2765 | 87.34% | 1 | 8 | 97.2% | 0% | 0 | 0.057141 | 1 | 2.363 | 0.13503 | Medium | Medium | Medium | 1603 | 1603 | 0.057141 | 85.1529
GARBERVILLE 11011750 | GARBERVILLE 1101 | HUMBOLDT | 14.3678 | 85.1825 | 100% | 14 | 8 | 96.86% | 0% | 0 | 0.081262 | 1 | 1.6609 | 0.13497 | High | High | Low | 1604 | 1388 | 0.081262 | 85.0178
BUCKS CREEK 1101CB | BUCKS CREEK 1101 | NORTH VALLEY | 20.005 | 83.6146 | 6.119% | 5 | 12 | 100% | 23.08% | 0 | 0.080342 | 1 | 1.6795 | 0.13494 | High | High | Low | 1605 | 1395 | 0.080342 | 84.8829
PARADISE 110343008 | PARADISE 1103 | NORTH VALLEY | 12.9696 | 10 | 78.07% | 7 | 5 | 99.92% | 17.25% | 1 | 0.037995 | 1 | 3.5408 | 0.13453 | Medium | Medium | High | 1606 | 1898 | 0.037995 | 84.7479
STANISLAUS 1702CB | STANISLAUS 1702 | YOSEMITE | 7.977 | 43.3363 | 28.21% | 1 | 3 | 100% | 19.55% | 0 | 0.043216 | 1 | 3.112 | 0.13449 | Medium | Medium | High | 1607 | 1791 | 0.043216 | 84.6134
CORRAL 1102CB | CORRAL 1102 | STOCKTON | 17.6005 | 19.3826 | 70.6% | 2 | 10 | 83.31% | 0% | 0 | 0.04296 | 1 | 3.1263 | 0.13431 | Medium | Medium | High | 1608 | 1799 | 0.04296 | 84.4789
PINE GROVE 11013166 | PINE GROVE 1101 | STOCKTON | 12.5063 | 11.3177 | 79.03% | 1 | 18 | 100% | 0% | 0 | 0.045896 | 1 | 2.919 | 0.13397 | Medium | Medium | Medium | 1609 | 1747 | 0.045896 | 84.3446
SAN LEANDRO U 1109CR002 | SAN LEANDRO U 1109 | MISSION | 7.0761 | 10 | 24.57% | 6 | 16 | 90.45% | 0% | 0 | 0.040555 | 1 | 3.3026 | 0.13394 | Medium | Medium | High | 1610 | 1840 | 0.040555 | 84.2106
WILLOW CREEK 110347966 | WILLOW CREEK 1103 | HUMBOLDT | 17.0216 | 48.5214 | 76.15% | 20 | 19 | 100% | 0% | 0 | 0.11952 | 1 | 1.1197 | 0.13384 | High | High | Low | 1611 | 1225 | 0.11952 | 84.0767
SALMON CREEK 1101194 | SALMON CREEK 1101 | SONOMA | 6.5546 | 49.1883 | 4.108% | 3 | 3 | 77.1% | 22.41% | 0 | 0.053234 | 1 | 2.5104 | 0.13364 | Medium | Medium | Medium | 1612 | 1643 | 0.053234 | 83.9429
MONTICELLO 110137384 | MONTICELLO 1101 | NORTH BAY | 9.3433 | 47.0333 | 65.93% | 7 | 4 | 99.86% | 0% | 0 | 0.054846 | 1 | 2.4323 | 0.1334 | Medium | Medium | Medium | 1613 | 1627 | 0.054846 | 83.8092
PACIFICA 110311153 | PACIFICA 1103 | PENINSULA | 0.48816 | 27.9974 | 36.15% | 0 | 1 | 5.373% | 100% | 0 | 0.038047 | 1 | 3.4976 | 0.13307 | Medium | Medium | High | 1614 | 1897 | 0.038047 | 83.6758
CURTIS 170210940 | CURTIS 1702 | YOSEMITE | 9.3161 | 16.9626 | 82.71% | 2 | 8 | 88.08% | 0% | 0 | 0.036211 | 1 | 3.6749 | 0.13307 | Medium | Medium | High | 1615 | 1929 | 0.036211 | 83.5427
OAKHURST 110210100 | OAKHURST 1102 | YOSEMITE | 9.1816 | 28.1335 | 94.5% | 4 | 24 | 77.46% | 0% | 0 | 0.054576 | 1 | 2.4338 | 0.13282 | Medium | Medium | Medium | 1616 | 1631 | 0.054576 | 83.4097
COTATI 1103148 | COTATI 1103 | SONOMA | 14.0913 | 49.2874 | 1.408% | 9 | 10 | 90.64% | 0% | 0 | 0.066855 | 1 | 1.9842 | 0.13266 | High | High | Low | 1617 | 1498 | 0.066855 | 83.2768
WOODSIDE 1104555372 | WOODSIDE 1104 | PENINSULA | 4.1602 | 10 | 35.51% | 2 | 3 | 100% | 0% | 0 | 0.02737 | 1 | 4.8418 | 0.13252 | Medium | Medium | High | 1618 | 2182 | 0.02737 | 83.1442
MILPITAS 1109XR524 | MILPITAS 1109 | SAN JOSE | 7.8802 | 65.8723 | 90.15% | 0 | 1 | 82.17% | 0% | 0 | 0.042366 | 1 | 3.1206 | 0.13221 | Medium | Medium | High | 1619 | 1810 | 0.042366 | 83.0117
HOOPA 11013174 | HOOPA 1101 | HUMBOLDT | 17.6485 | 69.5085 | 99.93% | 19 | 10 | 80.04% | 0% | 0 | 0.11313 | 1 | 1.1672 | 0.13204 | High | High | Low | 1620 | 1244 | 0.11313 | 82.8795
LUCERNE 1103630 | LUCERNE 1103 | HUMBOLDT | 12.5736 | 13.6837 | 90.26% | 2 | 19 | 92.62% | 0% | 0 | 0.043155 | 1 | 3.0456 | 0.13143 | Medium | Medium | Medium | 1621 | 1794 | 0.043155 | 82.7474
STAFFORD 11021048 | STAFFORD 1102 | NORTH BAY | 4.9722 | 28.2651 | 55.55% | 1 | 7 | 93.63% | 17.79% | 1 | 0.042409 | 1 | 3.0962 | 0.13131 | Medium | Medium | High | 1622 | 1809 | 0.042409 | 82.616
LOS GATOS 1108LB86 | LOS GATOS 1108 | DE ANZA | 4.2689 | 10 | 37.07% | 3 | 5 | 80.57% | 12.91% | 0 | 0.033788 | 1 | 3.8848 | 0.13126 | Medium | Medium | High | 1623 | 1982 | 0.033788 | 82.4847
DUNBAR 110297160 | DUNBAR 1102 | SONOMA | 0.058569 | 82.8928 | 100% | 0 | 0 | 100% | 0% | 0 | 0.046095 | 1 | 2.8466 | 0.13122 | Medium | Medium | Medium | 1624 | 1741 | 0.046095 | 82.3534
WISHON 1101CB | WISHON 1101 | YOSEMITE | 7.7822 | 34.1369 | 78.45% | 1 | 2 | 100% | 51.22% | 1 | 0.074616 | 1 | 1.7546 | 0.13092 | High | High | Low | 1625 | 1441 | 0.074616 | 82.2222
EL CERRITO G 1112CB | EL CERRITO G 1112 | EAST BAY | 0.64797 | 10 | 0% | 0 | 0 | 9.809% | 100% | 0 | 0.02588 | 1 | 4.9956 | 0.12929 | Medium | Medium | High | 1626 | 2217 | 0.02588 | 82.0913
SILVERADO 2102CB | SILVERADO 2102 | NORTH BAY | 0.45935 | 10 | 0% | 0 | 0 | 26.76% | 100% | 0 | 0.034737 | 1 | 3.7165 | 0.1291 | Medium | Medium | High | 1627 | 1957 | 0.034737 | 81.962
DIAMOND SPRINGS 11042093 | DIAMOND SPRINGS 1104 | SIERRA | 7.2925 | 22.8545 | 79.86% | 0 | 2 | 83.65% | 44.87% | 0 | 0.053967 | 1 | 2.3806 | 0.12847 | Medium | Medium | Medium | 1628 | 1637 | 0.053967 | 81.8329
HALSEY 110176178 | HALSEY 1101 | SIERRA | 19.4389 | 10 | 66.26% | 6 | 14 | 96.3% | 0% | 0 | 0.050379 | 1 | 2.5491 | 0.12842 | Medium | Medium | Medium | 1629 | 1679 | 0.050379 | 81.7044
GARBERVILLE 11021510 | GARBERVILLE 1102 | HUMBOLDT | 13.0211 | 67.6864 | 30.88% | 5 | 7 | 100% | 0% | 0 | 0.063582 | 1 | 2.0147 | 0.1281 | High | High | Low | 1630 | 1527 | 0.063582 | 81.576
CLARK ROAD 110247006 | CLARK ROAD 1102 | NORTH VALLEY | 4.5495 | 10 | 42.4% | 2 | 3 | 100% | 41.72% | 0 | 0.037887 | 1 | 3.3709 | 0.12771 | Medium | Medium | High | 1631 | 1899 | 0.037887 | 81.4479
ORINDA 0401N545R | ORINDA 0401 | DIABLO | 4.3157 | 10 | 9.802% | 1 | 11 | 83.77% | 52.25% | 0 | 0.038927 | 1 | 3.2801 | 0.12768 | Medium | Medium | High | 1632 | 1882 | 0.038927 | 81.3202
OILFIELDS 1103N62 | OILFIELDS 1103 | CENTRAL COAST | 5.5689 | 75.4181 | 98.3% | 0 | 2 | 100% | 0% | 0 | 0.05809 | 1 | 2.1974 | 0.12764 | Medium | Medium | Low | 1633 | 1594 | 0.05809 | 81.1925
SOBRANTE 1102CB | SOBRANTE 1102 | DIABLO | 10.2599 | 28.2629 | 22.78% | 2 | 15 | 98.33% | 12.04% | 0 | 0.042314 | 1 | 3.0143 | 0.12755 | Medium | Medium | Medium | 1634 | 1812 | 0.042314 | 81.0649
TYLER 110585132 | TYLER 1105 | NORTH VALLEY | 30.9692 | 56.9117 | 100% | 0 | 21 | 100% | 0% | 0 | 0.075876 | 1 | 1.6764 | 0.1272 | High | High | Low | 1635 | 1435 | 0.075876 | 80.9373
CEDAR CREEK 11011710 | CEDAR CREEK 1101 | NORTH VALLEY | 0.076338 | 70.3009 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18445 | 1 | 0.68738 | 0.12679 | High | High | Low | 1636 | 1083 | 0.18445 | 80.8101
CABRILLO 1103Y46 | CABRILLO 1103 | LOS PADRES | 20.218 | 55.531 | 56.98% | 1 | 5 | 42.55% | 0% | 0 | 0.043329 | 1 | 2.9259 | 0.12678 | Medium | Medium | Medium | 1637 | 1788 | 0.043329 | 80.6833
COTTONWOOD 11011610 | COTTONWOOD 1101 | NORTH VALLEY | 38.431 | 59.7392 | 100% | 4 | 5 | 100% | 0% | 0 | 0.097181 | 1 | 1.3016 | 0.12649 | High | High | Low | 1638 | 1305 | 0.097181 | 80.5566
EL DORADO PH 210163464 | EL DORADO PH 2101 | SIERRA | 13.6531 | 63.9369 | 100% | 0 | 2 | 100% | 36.69% | 1 | 0.084238 | 1 | 1.4999 | 0.12635 | High | High | Low | 1639 | 1368 | 0.084238 | 80.4301
DIAMOND SPRINGS 110610587 | DIAMOND SPRINGS 1106 | SIERRA | 21.9902 | 32.7231 | 99.97% | 4 | 2 | 100% | 0% | 0 | 0.060422 | 1 | 2.0865 | 0.12607 | Medium | Medium | Low | 1640 | 1562 | 0.060422 | 80.3037
BROWNS VALLEY 11011268 | BROWNS VALLEY 1101 | SIERRA | 10.9063 | 24.7365 | 96.96% | 1 | 7 | 100% | 0% | 0 | 0.046288 | 1 | 2.7133 | 0.12559 | Medium | Medium | Medium | 1641 | 1736 | 0.046288 | 80.1777
CLEAR LAKE 1101406 | CLEAR LAKE 1101 | HUMBOLDT | 10.6464 | 76.543 | 93.36% | 0 | 1 | 32.19% | 54.28% | 0 | 0.052045 | 1 | 2.4044 | 0.12514 | Medium | Medium | Medium | 1642 | 1660 | 0.052045 | 80.0521
MILPITAS 110987800 | MILPITAS 1109 | SAN JOSE | 1.61 | 77.3424 | 100% | 0 | 0 | 100% | 0% | 0 | 0.044454 | 1 | 2.8069 | 0.12478 | Medium | Medium | Medium | 1643 | 1769 | 0.044454 | 79.9269
DEL MONTE 21043088 | DEL MONTE 2104 | CENTRAL COAST | 15.4442 | 31.6262 | 48.83% | 2 | 7 | 100% | 0% | 0 | 0.063303 | 1 | 1.9688 | 0.12463 | High | High | Low | 1644 | 1528 | 0.063303 | 79.8021
KING CITY 11037038 | KING CITY 1103 | CENTRAL COAST | 17.5881 | 72.8479 | 99.95% | 0 | 5 | 81.26% | 0% | 0 | 0.058354 | 1 | 2.1255 | 0.12403 | Medium | Medium | Low | 1645 | 1589 | 0.058354 | 79.6775
MARTELL 110111244 | MARTELL 1101 | STOCKTON | 21.6798 | 10 | 87.92% | 5 | 3 | 99.45% | 0% | 0 | 0.048788 | 1 | 2.5388 | 0.12386 | Medium | Medium | Medium | 1646 | 1698 | 0.048788 | 79.5535
WHITMORE 11011594 | WHITMORE 1101 | NORTH VALLEY | 24.2582 | 53.3221 | 84.24% | 2 | 1 | 100% | 29.39% | 0 | 0.09099 | 1 | 1.3571 | 0.12348 | High | High | Low | 1647 | 1335 | 0.09099 | 79.4296
WYANDOTTE 11031504 | WYANDOTTE 1103 | NORTH VALLEY | 11.3639 | 10 | 55.8% | 3 | 8 | 77.24% | 0% | 0 | 0.032944 | 1 | 3.7481 | 0.12348 | Medium | Medium | High | 1648 | 2011 | 0.032944 | 79.3061
WYANDOTTE 110796390 | WYANDOTTE 1107 | NORTH VALLEY | 8.1841 | 10 | 71.02% | 4 | 1 | 80.42% | 0% | 0 | 0.033709 | 1 | 3.6617 | 0.12343 | Medium | Medium | High | 1649 | 1987 | 0.033709 | 79.1827
CLOVERDALE 11024646 | CLOVERDALE 1102 | SONOMA | 14.4526 | 74.9071 | 80.61% | 2 | 4 | 97.6% | 0% | 0 | 0.059667 | 1 | 2.0674 | 0.12335 | Medium | Medium | Low | 1650 | 1569 | 0.059667 | 79.0592
OCEANO 1104Q12 | OCEANO 1104 | LOS PADRES | 9.3393 | 55.4094 | 73.47% | 0 | 5 | 57.92% | 27.55% | 0 | 0.051953 | 1 | 2.3715 | 0.12321 | Medium | Medium | Medium | 1651 | 1661 | 0.051953 | 78.9359
LOW GAP 11014086 | LOW GAP 1101 | HUMBOLDT | 11.4979 | 83.0021 | 100% | 1 | 2 | 100% | 0% | 0 | 0.090624 | 1 | 1.3559 | 0.12288 | High | High | Low | 1652 | 1336 | 0.090624 | 78.8127
SWIFT 2110XR332 | SWIFT 2110 | SAN JOSE | 49.6657 | 79.4868 | 80.03% | 0 | 0 | 100% | 0% | 0 | 0.049698 | 1 | 2.4667 | 0.12259 | Medium | Medium | Medium | 1653 | 1686 | 0.049698 | 78.6898
DEL MONTE 210436720 | DEL MONTE 2104 | CENTRAL COAST | 6.1198 | 15.0991 | 78.82% | 1 | 2 | 76.61% | 0% | 0 | 0.039935 | 1 | 3.0657 | 0.12243 | Medium | Medium | Medium | 1654 | 1860 | 0.039935 | 78.5672
GUALALA 111223444 | GUALALA 1112 | HUMBOLDT | 14.5206 | 71.4539 | 16.53% | 7 | 15 | 100% | 0% | 0 | 0.069914 | 1 | 1.7456 | 0.12204 | High | High | Low | 1655 | 1470 | 0.069914 | 78.4448
ROB ROY 210410960 | ROB ROY 2104 | CENTRAL COAST | 17.8204 | 13.6401 | 49.6% | 26 | 6 | 63.39% | 0% | 0 | 0.03619 | 1 | 3.3702 | 0.12197 | Medium | Medium | High | 1656 | 1930 | 0.03619 | 78.3227
APPLE HILL 110313312 | APPLE HILL 1103 | SIERRA | 11.1165 | 24.9201 | 69.91% | 1 | 7 | 61.36% | 40.78% | 0 | 0.055379 | 1 | 2.1929 | 0.12144 | Medium | Medium | Low | 1657 | 1621 | 0.055379 | 78.2008
SAN RAFAEL 110991742 | SAN RAFAEL 1109 | NORTH BAY | 5.7363 | 10 | 72.58% | 2 | 1 | 66.36% | 0% | 0 | 0.033036 | 1 | 3.657 | 0.12081 | Medium | Medium | High | 1658 | 2009 | 0.033036 | 78.0793
VALLEY VIEW 1106 | VALLEY VIEW 1106 | EAST BAY | 0.037566 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 4.232 | 0.12066 | Medium | Medium | High | 1659 | 2136 | 0.028512 | 77.9585
OAKHURST 11016220 | OAKHURST 1101 | YOSEMITE | 20.9199 | 34.4609 | 88.69% | 0 | 15 | 100% | 0% | 0 | 0.060711 | 1 | 1.9872 | 0.12065 | Medium | Medium | Low | 1660 | 1559 | 0.060711 | 77.8378
EDES 1112CR312 | EDES 1112 | EAST BAY | 3.6853 | 22.7087 | 18.65% | 2 | 11 | 99.92% | 20.18% | 0 | 0.036955 | 1 | 3.2611 | 0.12051 | Medium | Medium | High | 1661 | 1919 | 0.036955 | 77.7172
WYANDOTTE 110366146 | WYANDOTTE 1103 | NORTH VALLEY | 0.1568 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.032454 | 1 | 3.7133 | 0.12051 | Medium | Medium | High | 1662 | 2029 | 0.032454 | 77.5967
LAKEWOOD 2224D522R | LAKEWOOD 2224 | DIABLO | 0.67815 | 10 | 23.16% | 0 | 1 | 25.38% | 100% | 0 | 0.036972 | 1 | 3.2556 | 0.12036 | Medium | Medium | High | 1663 | 1918 | 0.036972 | 77.4762
CURTIS 1704CB | CURTIS 1704 | YOSEMITE | 13.7734 | 18.3001 | 79.09% | 1 | 5 | 96.53% | 0% | 0 | 0.035785 | 1 | 3.3627 | 0.12033 | Medium | Medium | High | 1664 | 1939 | 0.035785 | 77.3558
VIEJO 2203CB | VIEJO 2203 | CENTRAL COAST | 3.0922 | 10 | 21.75% | 26 | 9 | 92.05% | 0% | 0 | 0.039672 | 1 | 3.0156 | 0.11963 | Medium | Medium | Medium | 1665 | 1866 | 0.039672 | 77.2355
HAMILTON BRANCH 110187784 | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.4473 | 18.1172 | 99.8% | 0 | 3 | 100% | 0% | 0 | 0.031933 | 1 | 3.7387 | 0.11939 | Medium | Medium | High | 1666 | 2049 | 0.031933 | 77.1158
GEYSERVILLE 110179788 | GEYSERVILLE 1101 | SONOMA | 36.3345 | 85.553 | 97.66% | 5 | 7 | 86.55% | 0% | 0 | 0.081783 | 1 | 1.4593 | 0.11934 | High | High | Low | 1667 | 1385 | 0.081783 | 76.9965
MIRABEL 1102334 | MIRABEL 1102 | SONOMA | 5.6083 | 39.7869 | 41.25% | 2 | 2 | 61.12% | 47.7% | 0 | 0.038421 | 1 | 3.0999 | 0.1191 | Medium | Medium | High | 1668 | 1890 | 0.038421 | 76.8771
WYANDOTTE 110913052 | WYANDOTTE 1109 | NORTH VALLEY | 19.6896 | 23.3384 | 63.11% | 1 | 2 | 99.03% | 0% | 0 | 0.035725 | 1 | 3.319 | 0.11857 | Medium | Medium | High | 1669 | 1941 | 0.035725 | 76.758
EL CERRITO G 1105BR194 | EL CERRITO G 1105 | EAST BAY | 3.0539 | 15.352 | 23.01% | 1 | 2 | 58.3% | 30.42% | 0 | 0.026764 | 1 | 4.423 | 0.11838 | Medium | Medium | High | 1670 | 2196 | 0.026764 | 76.6394
DOBBINS 11015202 | DOBBINS 1101 | SIERRA | 15.7094 | 33.0821 | 86.66% | 1 | 6 | 92.01% | 0% | 0 | 0.059877 | 1 | 1.9749 | 0.11825 | Medium | Medium | Low | 1671 | 1565 | 0.059877 | 76.5211
RACETRACK 17038120 | RACETRACK 1703 | YOSEMITE | 8.8205 | 16.6525 | 57.46% | 3 | 10 | 100% | 16.02% | 1 | 0.03955 | 1 | 2.9886 | 0.1182 | Medium | Medium | Medium | 1672 | 1871 | 0.03955 | 76.4028
CAROLANDS 04049024 | CAROLANDS 0404 | PENINSULA | 3.5964 | 10 | 16.66% | 1 | 9 | 99.05% | 0% | 0 | 0.033705 | 1 | 3.5061 | 0.11817 | Medium | Medium | High | 1673 | 1988 | 0.033705 | 76.2846
MENLO 11031721 | MENLO 1103 | PENINSULA | 6.795 | 58.431 | 89.52% | 4 | 2 | 100% | 0% | 0 | 0.044995 | 1 | 2.626 | 0.11816 | Medium | Medium | Medium | 1674 | 1766 | 0.044995 | 76.1664
VOLTA 11021650 | VOLTA 1102 | NORTH VALLEY | 21.7066 | 54.4838 | 100% | 4 | 9 | 100% | 0% | 0 | 0.079578 | 1 | 1.4837 | 0.11807 | High | High | Low | 1675 | 1402 | 0.079578 | 76.0483
BRIDGEVILLE 110255612 | BRIDGEVILLE 1102 | HUMBOLDT | 22.2453 | 91.4485 | 100% | 11 | 10 | 100% | 97.29% | 1 | 0.34757 | 1 | 0.33885 | 0.11777 | High | High | Low | 1676 | 921 | 0.34757 | 75.9302
SARATOGA 1107LC26 | SARATOGA 1107 | DE ANZA | 5.6494 | 10 | 35.72% | 5 | 4 | 100% | 14.43% | 1 | 0.032092 | 1 | 3.6662 | 0.11766 | Medium | Medium | High | 1677 | 2043 | 0.032092 | 75.8124
FROGTOWN 170291134 | FROGTOWN 1702 | STOCKTON | 14.7309 | 23.5525 | 81.54% | 0 | 12 | 92.7% | 0% | 0 | 0.060562 | 1 | 1.9356 | 0.11722 | Medium | Medium | Low | 1678 | 1561 | 0.060562 | 75.6948
VACAVILLE 11088762 | VACAVILLE 1108 | SACRAMENTO | 13.206 | 54.7168 | 79.67% | 1 | 3 | 78.91% | 0% | 0 | 0.042096 | 1 | 2.7832 | 0.11716 | Medium | Medium | Medium | 1679 | 1817 | 0.042096 | 75.5776
LUCERNE 1106664 | LUCERNE 1106 | HUMBOLDT | 6.0536 | 25.8226 | 47.99% | 4 | 24 | 54.26% | 0% | 0 | 0.038531 | 1 | 3.0381 | 0.11706 | Medium | Medium | Medium | 1680 | 1889 | 0.038531 | 75.4604
PLACERVILLE 111219712 | PLACERVILLE 1112 | SIERRA | 12.7698 | 10 | 100% | 3 | 10 | 97.13% | 0% | 0 | 0.045629 | 1 | 2.5586 | 0.11675 | Medium | Medium | Medium | 1681 | 1753 | 0.045629 | 75.3433
UKIAH 1111534 | UKIAH 1111 | HUMBOLDT | 18.7979 | 74.5032 | 100% | 2 | 4 | 89.62% | 0% | 0 | 0.064153 | 1 | 1.8196 | 0.11673 | High | High | Low | 1682 | 1525 | 0.064153 | 75.2266
SPRUCE 0401BR316 | SPRUCE 0401 | EAST BAY | 4.123 | 16.22 | 7.456% | 3 | 5 | 100% | 23.86% | 0 | 0.02375 | 1 | 4.8945 | 0.11624 | Medium | Medium | High | 1683 | 2286 | 0.02375 | 75.1099
WILLITS 11032506 | WILLITS 1103 | HUMBOLDT | 12.7779 | 67.5224 | 88.76% | 15 | 4 | 100% | 16.88% | 0 | 0.06476 | 1 | 1.7937 | 0.11616 | High | High | Low | 1684 | 1516 | 0.06476 | 74.9936
AUBERRY 1101R2578 | AUBERRY 1101 | FRESNO | 46.349 | 12.9087 | 87.94% | 4 | 13 | 100% | 0% | 0 | 0.077203 | 1 | 1.5016 | 0.11593 | High | High | Low | 1685 | 1421 | 0.077203 | 74.8775
HIGGINS 11041374 | HIGGINS 1104 | SIERRA | 7.2163 | 10 | 85.17% | 5 | 6 | 86.29% | 0% | 0 | 0.030394 | 1 | 3.8118 | 0.11586 | Medium | Medium | High | 1686 | 2080 | 0.030394 | 74.7615
CALAVERAS CEMENT 110147968 | CALAVERAS CEMENT 1101 | STOCKTON | 17.4467 | 25.9867 | 99.97% | 0 | 4 | 100% | 6.1% | 1 | 0.055443 | 1 | 2.0882 | 0.11578 | Medium | Medium | Low | 1687 | 1620 | 0.055443 | 74.6457
DEL MONTE 21032000 | DEL MONTE 2103 | CENTRAL COAST | 8.9713 | 10 | 21.71% | 13 | 11 | 98.79% | 0% | 0 | 0.037343 | 1 | 3.097 | 0.11565 | Medium | Medium | High | 1688 | 1909 | 0.037343 | 74.5299
FORT BRAGG A 11041316 | FORT BRAGG A 1104 | HUMBOLDT | 13.2223 | 12.9501 | 11.54% | 9 | 10 | 96.48% | 0% | 0 | 0.036376 | 1 | 3.1775 | 0.11559 | Medium | Medium | High | 1689 | 1927 | 0.036376 | 74.4142
RACETRACK 17039190 | RACETRACK 1703 | YOSEMITE | 8.9165 | 23.5588 | 27.68% | 2 | 6 | 100% | 0% | 0 | 0.034029 | 1 | 3.3879 | 0.11529 | Medium | Medium | High | 1690 | 1974 | 0.034029 | 74.2987
AUBERRY 1101R314 | AUBERRY 1101 | FRESNO | 42.3727 | 21.0608 | 99.17% | 0 | 7 | 96.03% | 0% | 0 | 0.072346 | 1 | 1.5793 | 0.11426 | High | High | Low | 1691 | 1457 | 0.072346 | 74.1834
HATTON 11022010 | HATTON 1102 | CENTRAL COAST | 4.0217 | 30.548 | 30.01% | 17 | 5 | 100% | 0% | 0 | 0.043055 | 1 | 2.6454 | 0.1139 | Medium | Medium | Medium | 1692 | 1795 | 0.043055 | 74.0691
CORRAL 110236666 | CORRAL 1102 | STOCKTON | 17.3526 | 23.3821 | 99.95% | 1 | 2 | 96.21% | 0% | 0 | 0.046553 | 1 | 2.4463 | 0.11388 | Medium | Medium | Medium | 1693 | 1730 | 0.046553 | 73.9552
HIGHLANDS 1102CB | HIGHLANDS 1102 | HUMBOLDT | 7.3244 | 28.1149 | 80.17% | 1 | 6 | 100% | 0% | 0 | 0.035726 | 1 | 3.1836 | 0.11374 | Medium | Medium | High | 1694 | 1940 | 0.035726 | 73.8413
DUNBAR 1101CB | DUNBAR 1101 | SONOMA | 2.1801 | 23.6947 | 93.6% | 0 | 2 | 14.87% | 59.74% | 0 | 0.034709 | 1 | 3.2741 | 0.11364 | Medium | Medium | High | 1695 | 1958 | 0.034709 | 73.7276
WISE 1102CB | WISE 1102 | SIERRA | 18.631 | 17.4842 | 45.37% | 6 | 22 | 98.52% | 0% | 0 | 0.0417 | 1 | 2.7235 | 0.11357 | Medium | Medium | Medium | 1696 | 1821 | 0.0417 | 73.6139
HIGGINS 1104842642 | HIGGINS 1104 | SIERRA | 5.4882 | 10 | 100% | 3 | 1 | 94.43% | 0% | 0 | 0.032606 | 1 | 3.4791 | 0.11344 | Medium | Medium | High | 1697 | 2022 | 0.032606 | 73.5004
MORGAN HILL 2104XR018 | MORGAN HILL 2104 | SAN JOSE | 4.9492 | 19.6923 | 100% | 0 | 3 | 46.16% | 0% | 0 | 0.03658 | 1 | 3.0953 | 0.11323 | Medium | Medium | High | 1698 | 1926 | 0.03658 | 73.3869
SAND CREEK 11037420 | SAND CREEK 1103 | FRESNO | 23.394 | 10 | 99.98% | 4 | 4 | 100% | 0% | 0 | 0.04783 | 1 | 2.3612 | 0.11293 | Medium | Medium | Medium | 1699 | 1708 | 0.04783 | 73.2737
LOS OSITOS 21033010 | LOS OSITOS 2103 | CENTRAL COAST | 30.8565 | 64.7553 | 97.74% | 3 | 10 | 99.12% | 0% | 0 | 0.057419 | 1 | 1.9613 | 0.11262 | Medium | Medium | Low | 1700 | 1600 | 0.057419 | 73.1608
SCE TEHACHAPI 1101CB | SCE TEHACHAPI 1101 | KERN | 1.4276 | 82.1535 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045873 | 1 | 2.4463 | 0.11222 | Medium | Medium | Medium | 1701 | 1748 | 0.045873 | 73.0482
DESCHUTES 11011580 | DESCHUTES 1101 | NORTH VALLEY | 44.5215 | 20.6467 | 99.77% | 3 | 12 | 90.01% | 10.49% | 0 | 0.071696 | 1 | 1.5632 | 0.11207 | High | High | Low | 1702 | 1461 | 0.071696 | 72.9359
SARATOGA 11075696 | SARATOGA 1107 | DE ANZA | 4.0107 | 10 | 57.71% | 6 | 9 | 65.93% | 4.474% | 0 | 0.029972 | 1 | 3.7269 | 0.1117 | Medium | Medium | High | 1703 | 2100 | 0.029972 | 72.8239
HIGGINS 1104533648 | HIGGINS 1104 | SIERRA | 6.7529 | 10 | 96.99% | 2 | 3 | 100% | 0% | 0 | 0.034544 | 1 | 3.2267 | 0.11146 | Medium | Medium | High | 1704 | 1961 | 0.034544 | 72.7122
SHINGLE SPRINGS 210511172 | SHINGLE SPRINGS 2105 | SIERRA | 2.0141 | 10 | 66.76% | 1 | 3 | 82.66% | 0% | 0 | 0.029323 | 1 | 3.7968 | 0.11133 | Medium | Medium | High | 1705 | 2116 | 0.029323 | 72.6007
WOODSIDE 11018522 | WOODSIDE 1101 | PENINSULA | 0.74695 | 65.2984 | 0% | 1 | 0 | 7.949% | 85.4% | 0 | 0.029511 | 1 | 3.7573 | 0.11088 | Medium | Medium | High | 1706 | 2110 | 0.029511 | 72.4894
POSO MOUNTAIN 21014456 | POSO MOUNTAIN 2101 | KERN | 23.5359 | 61.9546 | 91.99% | 0 | 4 | 100% | 0% | 0 | 0.052745 | 1 | 2.0977 | 0.11064 | Medium | Medium | Low | 1707 | 1652 | 0.052745 | 72.3785
AUBERRY 1101CB | AUBERRY 1101 | FRESNO | 18.1441 | 19.2243 | 60.88% | 0 | 19 | 100% | 0% | 0 | 0.042195 | 1 | 2.6192 | 0.11052 | Medium | Medium | Medium | 1708 | 1813 | 0.042195 | 72.2678
OILFIELDS 1103N48 | OILFIELDS 1103 | CENTRAL COAST | 47.0468 | 56.1397 | 99.69% | 2 | 26 | 100% | 0% | 0 | 0.075176 | 1 | 1.4634 | 0.11001 | High | High | Low | 1709 | 1437 | 0.075176 | 72.1573
WEIMAR 11012084 | WEIMAR 1101 | SIERRA | 18.471 | 37.3973 | 99.11% | 2 | 13 | 100% | 0% | 0 | 0.066085 | 1 | 1.6608 | 0.10976 | High | High | Low | 1710 | 1505 | 0.066085 | 72.0473
HIGHLANDS 1103482 | HIGHLANDS 1103 | HUMBOLDT | 23.7709 | 84.3418 | 64.96% | 1 | 10 | 92.07% | 0% | 0 | 0.046005 | 1 | 2.3829 | 0.10963 | Medium | Medium | Medium | 1711 | 1744 | 0.046005 | 71.9376
SALT SPRINGS 21028442 | SALT SPRINGS 2102 | STOCKTON | 12.1299 | 48.4336 | 100% | 5 | 7 | 100% | 9.936% | 1 | 0.13919 | 1 | 0.78756 | 0.10962 | High | High | Low | 1712 | 1170 | 0.13919 | 71.8279
STANISLAUS 1701CB | STANISLAUS 1701 | YOSEMITE | 6.8255 | 50.7734 | 38.45% | 1 | 4 | 100% | 0.8907% | 0 | 0.032969 | 1 | 3.3185 | 0.10941 | Medium | Medium | High | 1713 | 2010 | 0.032969 | 71.7183
HIGHLANDS 1103CB | HIGHLANDS 1103 | HUMBOLDT | 10.5045 | 18.0278 | 65.06% | 2 | 6 | 87.07% | 0% | 0 | 0.034275 | 1 | 3.1863 | 0.10921 | Medium | Medium | High | 1714 | 1965 | 0.034275 | 71.6089
HIGGINS 1107746082 | HIGGINS 1107 | SIERRA | 0.84187 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.032454 | 1 | 3.3644 | 0.10919 | Medium | Medium | High | 1715 | 2029 | 0.032454 | 71.4997
FRUITLAND 114263170 | FRUITLAND 1142 | HUMBOLDT | 12.2406 | 74.2009 | 74.01% | 12 | 5 | 90.64% | 0% | 0 | 0.061047 | 1 | 1.7809 | 0.10872 | Medium | Medium | Low | 1716 | 1557 | 0.061047 | 71.3905
HIGGINS 1109CB | HIGGINS 1109 | SIERRA | 22.2012 | 22.658 | 81.89% | 2 | 4 | 95.77% | 0% | 0 | 0.037105 | 1 | 2.9246 | 0.10852 | Medium | Medium | Medium | 1717 | 1914 | 0.037105 | 71.2818
GREENBRAE 1103CB | GREENBRAE 1103 | NORTH BAY | 0.06411 | 10 | 0% | 0 | 0 | 1.278% | 100% | 0 | 0.02712 | 1 | 3.9968 | 0.10839 | Medium | Medium | High | 1718 | 2190 | 0.02712 | 71.1733
MENDOCINO 1101CB | MENDOCINO 1101 | HUMBOLDT | 11.0353 | 11.0346 | 86.58% | 0 | 6 | 81.55% | 0% | 0 | 0.046385 | 1 | 2.3319 | 0.10817 | Medium | Medium | Medium | 1719 | 1734 | 0.046385 | 71.0649
TEMPLETON 2113A12 | TEMPLETON 2113 | LOS PADRES | 40.4505 | 77.6946 | 67.36% | 2 | 5 | 100% | 23.89% | 1 | 0.092809 | 1 | 1.1655 | 0.10817 | High | High | Low | 1720 | 1325 | 0.092809 | 70.9567
CURTIS 17029111 | CURTIS 1702 | YOSEMITE | 5.6752 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.032454 | 1 | 3.3314 | 0.10812 | Medium | Medium | High | 1721 | 2029 | 0.032454 | 70.8486
HATTON 11019220 | HATTON 1101 | CENTRAL COAST | 2.6965 | 89.4573 | 0% | 1 | 3 | 100% | 51.79% | 0 | 0.059721 | 1 | 1.81 | 0.10809 | Medium | Medium | Low | 1722 | 1568 | 0.059721 | 70.7404
MOUNTAIN QUARRIES 21011180 | MOUNTAIN QUARRIES 2101 | SIERRA | 12.8441 | 30.3787 | 92.22% | 1 | 2 | 100% | 9.293% | 0 | 0.048359 | 1 | 2.2311 | 0.10789 | Medium | Medium | Medium | 1723 | 1705 | 0.048359 | 70.6323
OCEANO 1102V50 | OCEANO 1102 | LOS PADRES | 5.8788 | 10 | 32.53% | 6 | 4 | 56.2% | 0% | 0 | 0.031497 | 1 | 3.4105 | 0.10742 | Medium | Medium | High | 1724 | 2060 | 0.031497 | 70.5244
LOW GAP 11014160 | LOW GAP 1101 | HUMBOLDT | 21.5735 | 61.654 | 100% | 10 | 5 | 99.51% | 0% | 0 | 0.082527 | 1 | 1.298 | 0.10712 | High | High | Low | 1725 | 1378 | 0.082527 | 70.417
MARIPOSA 21029490 | MARIPOSA 2102 | YOSEMITE | 4.2707 | 19.9086 | 45.43% | 0 | 1 | 100% | 49.91% | 0 | 0.044074 | 1 | 2.4205 | 0.10668 | Medium | Medium | Medium | 1726 | 1776 | 0.044074 | 70.3099
FITCH MOUNTAIN 11134566 | FITCH MOUNTAIN 1113 | SONOMA | 10.4618 | 71.5628 | 83.49% | 1 | 5 | 60.29% | 0% | 0 | 0.042183 | 1 | 2.5279 | 0.10663 | Medium | Medium | Medium | 1727 | 1814 | 0.042183 | 70.2032
RACETRACK 17036014 | RACETRACK 1703 | YOSEMITE | 6.8384 | 27.2462 | 64.22% | 2 | 1 | 100% | 0% | 0 | 0.037053 | 1 | 2.8715 | 0.1064 | Medium | Medium | Medium | 1728 | 1916 | 0.037053 | 70.0966
CURTIS 170565908 | CURTIS 1705 | YOSEMITE | 12.8972 | 32.2499 | 79.87% | 2 | 10 | 77.15% | 0% | 0 | 0.036689 | 1 | 2.8987 | 0.10635 | Medium | Medium | Medium | 1729 | 1924 | 0.036689 | 69.9902
MAPLE CREEK 1101CB | MAPLE CREEK 1101 | HUMBOLDT | 9.8748 | 78.7819 | 78.72% | 13 | 5 | 66.88% | 0% | 0 | 0.059846 | 1 | 1.7771 | 0.10635 | Medium | Medium | Low | 1730 | 1566 | 0.059846 | 69.8838
POTTER VALLEY P H 11051904 | POTTER VALLEY P H 1105 | HUMBOLDT | 28.466 | 59.7756 | 95.28% | 1 | 23 | 70.74% | 17.93% | 1 | 0.078348 | 1 | 1.3548 | 0.10615 | High | High | Low | 1731 | 1409 | 0.078348 | 69.7775
CALISTOGA 1101CB | CALISTOGA 1101 | NORTH BAY | 2.6498 | 39.1806 | 43.07% | 2 | 0 | 27.62% | 49.7% | 0 | 0.036018 | 1 | 2.9421 | 0.10597 | Medium | Medium | Medium | 1732 | 1934 | 0.036018 | 69.6713
RACETRACK 170311270 | RACETRACK 1703 | YOSEMITE | 12.3885 | 27.441 | 56.51% | 3 | 6 | 100% | 0% | 0 | 0.03438 | 1 | 3.0786 | 0.10584 | Medium | Medium | High | 1733 | 1964 | 0.03438 | 69.5654
BURNEY 11019042 | BURNEY 1101 | NORTH VALLEY | 3.0554 | 28.762 | 87.06% | 1 | 1 | 96.72% | 0% | 0 | 0.048736 | 1 | 2.1708 | 0.1058 | Medium | Medium | Low | 1734 | 1699 | 0.048736 | 69.4595
FULTON 1102287172 | FULTON 1102 | SONOMA | 17.3701 | 47.5802 | 77.47% | 4 | 10 | 64.9% | 11.1% | 0 | 0.043179 | 1 | 2.4495 | 0.10577 | Medium | Medium | Medium | 1735 | 1793 | 0.043179 | 69.3537
RINCON 1102CB | RINCON 1102 | SONOMA | 3.4953 | 21.5241 | 28.33% | 2 | 6 | 98.07% | 7.215% | 1 | 0.032618 | 1 | 3.2363 | 0.10556 | Medium | Medium | High | 1736 | 2021 | 0.032618 | 69.248
BUCKS CREEK 1103CB | BUCKS CREEK 1103 | NORTH VALLEY | 2.2994 | 96.1203 | 100% | 2 | 1 | 100% | 100% | 0 | 0.24438 | 1 | 0.43068 | 0.10525 | High | High | Low | 1737 | 1009 | 0.24438 | 69.1424
COARSEGOLD 2103CB | COARSEGOLD 2103 | YOSEMITE | 38.4222 | 32.3373 | 83.55% | 1 | 26 | 100% | 0% | 0 | 0.056308 | 1 | 1.858 | 0.10462 | Medium | Medium | Low | 1738 | 1610 | 0.056308 | 69.0372
BIG MEADOWS 21012246 | BIG MEADOWS 2101 | NORTH VALLEY | 1.3711 | 10 | 100% | 1 | 20 | 75.1% | 0% | 0 | 0.082406 | 1 | 1.2663 | 0.10435 | High | High | Low | 1739 | 1379 | 0.082406 | 68.9325
ELECTRA 1101CB | ELECTRA 1101 | STOCKTON | 26.464 | 31.8119 | 57.82% | 4 | 8 | 100% | 0% | 0 | 0.042866 | 1 | 2.4294 | 0.10414 | Medium | Medium | Medium | 1740 | 1801 | 0.042866 | 68.8282
VOLTA 11011568 | VOLTA 1101 | NORTH VALLEY | 23.0081 | 45.5317 | 55% | 0 | 5 | 100% | 29.05% | 0 | 0.072817 | 1 | 1.4267 | 0.10388 | High | High | Low | 1741 | 1452 | 0.072817 | 68.7241
LAS GALLINAS A 1106CB | LAS GALLINAS A 1106 | NORTH BAY | 4.998 | 10 | 78.22% | 0 | 1 | 31.7% | 39.74% | 0 | 0.026841 | 1 | 3.8683 | 0.10383 | Medium | Medium | High | 1742 | 2195 | 0.026841 | 68.6202
SHINGLE SPRINGS 210985766 | SHINGLE SPRINGS 2109 | SIERRA | 18.4459 | 50.1321 | 99.71% | 3 | 4 | 100% | 0% | 0 | 0.06111 | 1 | 1.6977 | 0.10374 | Medium | Medium | Low | 1743 | 1556 | 0.06111 | 68.5163
SHADY GLEN 110132726 | SHADY GLEN 1101 | SIERRA | 12.4872 | 23.3088 | 84.95% | 3 | 6 | 100% | 0% | 0 | 0.047638 | 1 | 2.1742 | 0.10357 | Medium | Medium | Low | 1744 | 1713 | 0.047638 | 68.4126
CHESTER 11022564 | CHESTER 1102 | NORTH VALLEY | 2.0894 | 10 | 100% | 0 | 3 | 93.3% | 0% | 0 | 0.047498 | 1 | 2.1797 | 0.10353 | Medium | Medium | Low | 1745 | 1718 | 0.047498 | 68.309
GREENBRAE 1103434 | GREENBRAE 1103 | NORTH BAY | 0.79973 | 10 | 68.06% | 2 | 1 | 55.44% | 2.889% | 0 | 0.020293 | 1 | 5.0736 | 0.10296 | Low | Low | High | 1746 | 2394 | 0.020293 | 68.2055
BRUNSWICK 1103CB | BRUNSWICK 1103 | SIERRA | 6.0294 | 52.8154 | 37.6% | 9 | 3 | 59.53% | 34.21% | 0 | 0.031778 | 1 | 3.2375 | 0.10288 | Medium | Medium | High | 1747 | 2051 | 0.031778 | 68.1025
NARROWS 2102CB | NARROWS 2102 | SIERRA | 22.8974 | 13.8368 | 78.07% | 2 | 5 | 93.68% | 0% | 0 | 0.029841 | 1 | 3.4435 | 0.10276 | Medium | Medium | High | 1748 | 2103 | 0.029841 | 67.9997
VACAVILLE 11046542 | VACAVILLE 1104 | SACRAMENTO | 14.768 | 37.9322 | 37.99% | 1 | 5 | 100% | 0% | 0 | 0.034546 | 1 | 2.9717 | 0.10266 | Medium | Medium | Medium | 1749 | 1960 | 0.034546 | 67.8969
HALSEY 11012414 | HALSEY 1101 | SIERRA | 14.7964 | 13.1515 | 76.48% | 3 | 9 | 100% | 0% | 0 | 0.050299 | 1 | 2.0384 | 0.10253 | Medium | Medium | Low | 1750 | 1681 | 0.050299 | 67.7942
POSO MOUNTAIN 21033988 | POSO MOUNTAIN 2103 | KERN | 17.2368 | 49.5955 | 64.44% | 0 | 0 | 92.36% | 0% | 0 | 0.038161 | 1 | 2.6824 | 0.10236 | Medium | Medium | Medium | 1751 | 1895 | 0.038161 | 67.6917
WEIMAR 11012058 | WEIMAR 1101 | SIERRA | 21.2651 | 19.5754 | 79.75% | 4 | 16 | 100% | 0% | 0 | 0.055164 | 1 | 1.8526 | 0.1022 | Medium | Medium | Low | 1752 | 1625 | 0.055164 | 67.5893
PASO ROBLES 1104R12 | PASO ROBLES 1104 | LOS PADRES | 26.4117 | 63.4802 | 89.23% | 0 | 7 | 66.23% | 0% | 0 | 0.045549 | 1 | 2.2416 | 0.1021 | Medium | Medium | Medium | 1753 | 1754 | 0.045549 | 67.4871
OREGON TRAIL 11041574 | OREGON TRAIL 1104 | NORTH VALLEY | 16.4858 | 16.0641 | 94.5% | 2 | 4 | 88.21% | 0% | 0 | 0.04716 | 1 | 2.1636 | 0.10204 | Medium | Medium | Low | 1754 | 1723 | 0.04716 | 67.385
HIGGINS 11077559 | HIGGINS 1107 | SIERRA | 4.3177 | 10 | 100% | 0 | 6 | 97.65% | 0% | 0 | 0.031488 | 1 | 3.2282 | 0.10165 | Medium | Medium | High | 1755 | 2061 | 0.031488 | 67.283
PLACERVILLE 1111CB | PLACERVILLE 1111 | SIERRA | 5.5179 | 10 | 61.74% | 2 | 10 | 83.46% | 0% | 0 | 0.033153 | 1 | 3.064 | 0.10158 | Medium | Medium | Medium | 1756 | 2003 | 0.033153 | 67.1814
FORT BRAGG A 11014622 | FORT BRAGG A 1101 | HUMBOLDT | 13.4572 | 19.3216 | 4.804% | 12 | 12 | 100% | 0% | 0 | 0.066763 | 1 | 1.5197 | 0.10146 | High | High | Low | 1757 | 1499 | 0.066763 | 67.0798
ELECTRA 110161816 | ELECTRA 1101 | STOCKTON | 12.191 | 16.1858 | 89% | 5 | 6 | 100% | 0% | 0 | 0.03728 | 1 | 2.7215 | 0.10146 | Medium | Medium | Medium | 1758 | 1910 | 0.03728 | 66.9783
BRENTWOOD 2105B504R | BRENTWOOD 2105 | DIABLO | 7.4348 | 10 | 79.77% | 0 | 6 | 65.97% | 0% | 0 | 0.042733 | 1 | 2.3715 | 0.10134 | Medium | Medium | Medium | 1759 | 1804 | 0.042733 | 66.8769
COTTONWOOD 11031348 | COTTONWOOD 1103 | NORTH VALLEY | 25.9721 | 33.8083 | 99.17% | 2 | 10 | 81.37% | 0% | 0 | 0.065681 | 1 | 1.5413 | 0.10123 | High | High | Low | 1760 | 1510 | 0.065681 | 66.7755
HIGHLANDS 1103568 | HIGHLANDS 1103 | HUMBOLDT | 7.7314 | 14.5235 | 84.3% | 1 | 2 | 84.45% | 0% | 0 | 0.034657 | 1 | 2.9157 | 0.10105 | Medium | Medium | Medium | 1761 | 1959 | 0.034657 | 66.6743
HAMILTON BRANCH 110137436 | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.0486 | 10 | 99.62% | 2 | 5 | 51.07% | 0% | 0 | 0.025995 | 1 | 3.8843 | 0.10097 | Medium | Medium | High | 1762 | 2215 | 0.025995 | 66.5732
MORRO BAY 1102W22 | MORRO BAY 1102 | LOS PADRES | 4.8943 | 10 | 4.74% | 0 | 3 | 47.35% | 0% | 0 | 0.023875 | 1 | 4.2269 | 0.10092 | Medium | Medium | High | 1763 | 2280 | 0.023875 | 66.4723
CALAVERAS CEMENT 1101585 | CALAVERAS CEMENT 1101 | STOCKTON | 14.1114 | 60.1241 | 100% | 0 | 9 | 100% | 0% | 0 | 0.061249 | 1 | 1.6439 | 0.10069 | Medium | Medium | Low | 1764 | 1554 | 0.061249 | 66.3714
BIG RIVER 11015065 | BIG RIVER 1101 | HUMBOLDT | 2.2025 | 10 | 42.78% | 5 | 11 | 100% | 0% | 0 | 0.035469 | 1 | 2.8348 | 0.10055 | Medium | Medium | Medium | 1765 | 1947 | 0.035469 | 66.2707
ELECTRA 11026014 | ELECTRA 1102 | STOCKTON | 28.5875 | 15.0573 | 83.7% | 1 | 14 | 100% | 0% | 0 | 0.051142 | 1 | 1.9639 | 0.10044 | Medium | Medium | Low | 1766 | 1670 | 0.051142 | 66.1701
WYANDOTTE 110979932 | WYANDOTTE 1109 | NORTH VALLEY | 19.2875 | 10.6134 | 90.79% | 1 | 2 | 59.11% | 0% | 0 | 0.036019 | 1 | 2.7826 | 0.10022 | Medium | Medium | Medium | 1767 | 1933 | 0.036019 | 66.0697
CALISTOGA 1102CB | CALISTOGA 1102 | NORTH BAY | 1.4649 | 10 | 27.88% | 0 | 0 | 51.57% | 53.48% | 0 | 0.030163 | 1 | 3.3194 | 0.10012 | Medium | Medium | High | 1768 | 2094 | 0.030163 | 65.9695
MONTICELLO 11014360 | MONTICELLO 1101 | NORTH BAY | 7.4298 | 66.0263 | 57.84% | 4 | 3 | 80.69% | 0% | 0 | 0.035448 | 1 | 2.8213 | 0.10001 | Medium | Medium | Medium | 1769 | 1948 | 0.035448 | 65.8693
VACAVILLE 1111CB | VACAVILLE 1111 | SACRAMENTO | 7.7902 | 19.0495 | 34.16% | 0 | 5 | 64.21% | 0% | 0 | 0.030405 | 1 | 3.282 | 0.099788 | Medium | Medium | High | 1770 | 2079 | 0.030405 | 65.7693
MONTE RIO 1111292 | MONTE RIO 1111 | SONOMA | 14.6924 | 53.0276 | 14.56% | 3 | 9 | 74.19% | 33.55% | 0 | 0.046445 | 1 | 2.1476 | 0.099746 | Medium | Medium | Low | 1771 | 1733 | 0.046445 | 65.6695
LUCERNE 1103CB | LUCERNE 1103 | HUMBOLDT | 4.1876 | 10 | 56.07% | 0 | 12 | 95.22% | 0% | 0 | 0.036043 | 1 | 2.7667 | 0.09972 | Medium | Medium | Medium | 1772 | 1932 | 0.036043 | 65.5698
WOODSIDE 11049030 | WOODSIDE 1104 | PENINSULA | 2.2354 | 10 | 77.85% | 0 | 2 | 86.64% | 0% | 0 | 0.021812 | 1 | 4.57 | 0.099682 | Medium | Medium | High | 1773 | 2342 | 0.021812 | 65.4701
MARIPOSA 210135244 | MARIPOSA 2101 | YOSEMITE | 17.3356 | 16.4968 | 77.7% | 2 | 10 | 100% | 23.66% | 0 | 0.045381 | 1 | 2.1925 | 0.099495 | Medium | Medium | Low | 1774 | 1758 | 0.045381 | 65.3704
PURISIMA 1101Y44 | PURISIMA 1101 | LOS PADRES | 10.0257 | 87.5542 | 33.95% | 0 | 2 | 86.13% | 0% | 0 | 0.029127 | 1 | 3.4151 | 0.099473 | Medium | Medium | High | 1775 | 2118 | 0.029127 | 65.2709
NARROWS 21052748 | NARROWS 2105 | SIERRA | 11.8577 | 19.7377 | 85.36% | 3 | 6 | 60.51% | 0% | 0 | 0.02804 | 1 | 3.5416 | 0.099307 | Medium | Medium | High | 1776 | 2163 | 0.02804 | 65.1714
FOOTHILL 1102CB | FOOTHILL 1102 | LOS PADRES | 8.141 | 51.8091 | 56.43% | 3 | 6 | 82.95% | 0% | 0 | 0.034219 | 1 | 2.9019 | 0.099302 | Medium | Medium | Medium | 1777 | 1968 | 0.034219 | 65.0721
HICKS 111660050 | HICKS 1116 | SAN JOSE | 7.9799 | 10 | 69.56% | 2 | 6 | 100% | 0% | 0 | 0.02949 | 1 | 3.3545 | 0.098924 | Medium | Medium | High | 1778 | 2111 | 0.02949 | 64.9728
OCEANO 1102V56 | OCEANO 1102 | LOS PADRES | 9.7421 | 10 | 68.41% | 1 | 15 | 98.35% | 0% | 0 | 0.03877 | 1 | 2.5506 | 0.098886 | Medium | Medium | Medium | 1779 | 1885 | 0.03877 | 64.8739
CURTIS 170390320 | CURTIS 1703 | YOSEMITE | 27.855 | 17.0394 | 100% | 4 | 21 | 100% | 0% | 0 | 0.10108 | 1 | 0.97587 | 0.098641 | High | High | Low | 1780 | 1291 | 0.10108 | 64.775
DESCHUTES 11011654 | DESCHUTES 1101 | NORTH VALLEY | 17.3592 | 41.2096 | 100% | 1 | 5 | 100% | 6.956% | 0 | 0.063997 | 1 | 1.5357 | 0.098281 | High | High | Low | 1781 | 1526 | 0.063997 | 64.6764
PEORIA 170587222 | PEORIA 1705 | YOSEMITE | 5.2686 | 10 | 76.37% | 0 | 4 | 100% | 0% | 0 | 0.03317 | 1 | 2.9599 | 0.098179 | Medium | Medium | Medium | 1782 | 2002 | 0.03317 | 64.5781
OAKLAND X 11066669 | OAKLAND X 1106 | EAST BAY | 0.23409 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.4389 | 0.098048 | Medium | Medium | High | 1783 | 2136 | 0.028512 | 64.4799
CASTRO VALLEY 1108MR379 | CASTRO VALLEY 1108 | MISSION | 1.2345 | 10 | 98.65% | 0 | 0 | 78.3% | 9.302% | 0 | 0.026453 | 1 | 3.7001 | 0.09788 | Medium | Medium | High | 1784 | 2205 | 0.026453 | 64.3819
LOS OSITOS 21037062 | LOS OSITOS 2103 | CENTRAL COAST | 12.2332 | 84.1604 | 73.22% | 2 | 3 | 100% | 0% | 0 | 0.046568 | 1 | 2.1004 | 0.097814 | Medium | Medium | Low | 1785 | 1729 | 0.046568 | 64.284
CLOVERDALE 110112719 | CLOVERDALE 1101 | SONOMA | 4.9181 | 80.6066 | 85.19% | 0 | 3 | 67.33% | 0% | 0 | 0.040502 | 1 | 2.4017 | 0.097273 | Medium | Medium | Medium | 1786 | 1842 | 0.040502 | 64.1862
COARSEGOLD 21035020 | COARSEGOLD 2103 | YOSEMITE | 16.1848 | 19.8956 | 69.91% | 1 | 23 | 97.69% | 0% | 0 | 0.048835 | 1 | 1.987 | 0.097036 | Medium | Medium | Low | 1787 | 1697 | 0.048835 | 64.0889
OCEANO 1104CB | OCEANO 1104 | LOS PADRES | 8.0054 | 24.7481 | 22.23% | 2 | 9 | 52.54% | 10.2% | 1 | 0.025849 | 1 | 3.7493 | 0.096918 | Medium | Medium | High | 1788 | 2218 | 0.025849 | 63.9919
TEMPLETON 2110R06 | TEMPLETON 2110 | LOS PADRES | 5.1326 | 51.0168 | 86.51% | 3 | 1 | 19.81% | 33.5% | 0 | 0.040874 | 1 | 2.3652 | 0.096678 | Medium | Medium | Medium | 1789 | 1835 | 0.040874 | 63.8949
PEORIA 17056697 | PEORIA 1705 | YOSEMITE | 4.1363 | 14.6236 | 100% | 1 | 4 | 100% | 0% | 0 | 0.036751 | 1 | 2.6171 | 0.096184 | Medium | Medium | Medium | 1790 | 1923 | 0.036751 | 63.7983
SOBRANTE 1103CB | SOBRANTE 1103 | DIABLO | 3.6739 | 50.7835 | 26.28% | 3 | 6 | 85.25% | 16.11% | 0 | 0.030947 | 1 | 3.0955 | 0.095796 | Medium | Medium | High | 1791 | 2072 | 0.030947 | 63.7021
EMERALD LAKE 0402CB | EMERALD LAKE 0402 | PENINSULA | 1.9157 | 10 | 14.69% | 2 | 3 | 100% | 0% | 0 | 0.017819 | 1 | 5.3744 | 0.095764 | Low | Low | High | 1792 | 2498 | 0.017819 | 63.6063
SAN CARLOS 11049052 | SAN CARLOS 1104 | PENINSULA | 4.4833 | 10 | 33.62% | 0 | 5 | 90.23% | 0% | 0 | 0.021835 | 1 | 4.3823 | 0.095688 | Medium | Medium | High | 1793 | 2340 | 0.021835 | 63.5105
PETALUMA C 1109738866 | PETALUMA C 1109 | SONOMA | 2.2043 | 62.3821 | 15.29% | 1 | 1 | 81.79% | 0% | 0 | 0.029792 | 1 | 3.2084 | 0.095587 | Medium | Medium | High | 1794 | 2105 | 0.029792 | 63.4148
CURTIS 170411290 | CURTIS 1704 | YOSEMITE | 7.9015 | 12.4604 | 83.91% | 5 | 0 | 100% | 0% | 0 | 0.030926 | 1 | 3.0902 | 0.095569 | Medium | Medium | High | 1795 | 2073 | 0.030926 | 63.3192
HIGGINS 11097831 | HIGGINS 1109 | SIERRA | 5.5525 | 26.5829 | 100% | 4 | 1 | 100% | 0% | 0 | 0.038882 | 1 | 2.4524 | 0.095352 | Medium | Medium | Medium | 1796 | 1883 | 0.038882 | 63.2237
CALAVERAS CEMENT 1101544800 | CALAVERAS CEMENT 1101 | STOCKTON | 23.1954 | 36.7246 | 100% | 2 | 5 | 100% | 0% | 0 | 0.049871 | 1 | 1.9083 | 0.095168 | Medium | Medium | Low | 1797 | 1683 | 0.049871 | 63.1283
CORNING 110290036 | CORNING 1102 | NORTH VALLEY | 14.194 | 60.2901 | 81.06% | 0 | 11 | 98.89% | 0% | 0 | 0.054481 | 1 | 1.7462 | 0.095135 | Medium | Medium | Low | 1798 | 1633 | 0.054481 | 63.0331
CURTIS 17046060 | CURTIS 1704 | YOSEMITE | 4.0637 | 23.6511 | 61.76% | 0 | 3 | 100% | 0% | 0 | 0.031658 | 1 | 3.0016 | 0.095023 | Medium | Medium | Medium | 1799 | 2055 | 0.031658 | 62.938
HIGGINS 11044281 | HIGGINS 1104 | SIERRA | 13.3205 | 11.5983 | 77.05% | 5 | 5 | 100% | 0% | 0 | 0.032224 | 1 | 2.9395 | 0.094722 | Medium | Medium | Medium | 1800 | 2038 | 0.032224 | 62.843
EMERALD LAKE 04028872 | EMERALD LAKE 0402 | PENINSULA | 4.147 | 10 | 19.14% | 0 | 11 | 74.11% | 0% | 0 | 0.018758 | 1 | 5.0483 | 0.094694 | Low | Low | High | 1801 | 2458 | 0.018758 | 62.7483
OAK 0401CB | OAK 0401 | EAST BAY | 4.3198 | 10 | 1.236% | 2 | 7 | 79.82% | 0% | 0 | 0.018493 | 1 | 5.1168 | 0.094626 | Low | Low | High | 1802 | 2466 | 0.018493 | 62.6536
SILVERADO 2102808 | SILVERADO 2102 | NORTH BAY | 1.929 | 85.4925 | 100% | 0 | 0 | 40.02% | 25.27% | 0 | 0.039111 | 1 | 2.4149 | 0.094447 | Medium | Medium | Medium | 1803 | 1879 | 0.039111 | 62.5589
PETALUMA C 1109848654 | PETALUMA C 1109 | SONOMA | 13.3481 | 80.6017 | 79.77% | 0 | 10 | 97.01% | 0% | 0 | 0.045978 | 1 | 2.0505 | 0.094277 | Medium | Medium | Low | 1804 | 1745 | 0.045978 | 62.4645
SAN RAFAEL 1104802 | SAN RAFAEL 1104 | NORTH BAY | 7.826 | 10 | 18.94% | 3 | 4 | 72.62% | 0% | 0 | 0.021588 | 1 | 4.3551 | 0.094017 | Low | Low | High | 1805 | 2349 | 0.021588 | 62.3702
PHILO 1102920 | PHILO 1102 | HUMBOLDT | 17.5582 | 57.0245 | 91.25% | 3 | 12 | 67.45% | 0% | 0 | 0.075007 | 1 | 1.2527 | 0.093958 | High | High | Low | 1806 | 1438 | 0.075007 | 62.2762
CURTIS 17039240 | CURTIS 1703 | YOSEMITE | 10.9351 | 23.2344 | 88.01% | 0 | 12 | 100% | 3.336% | 0 | 0.063182 | 1 | 1.4789 | 0.093439 | High | High | Low | 1807 | 1531 | 0.063182 | 62.1822
FAIRVIEW 2207P304 | FAIRVIEW 2207 | DIABLO | 5.0581 | 10 | 29.34% | 0 | 2 | 82.96% | 0% | 0 | 0.027316 | 1 | 3.4133 | 0.093239 | Medium | Medium | High | 1808 | 2185 | 0.027316 | 62.0888
GEYSERVILLE 1102350 | GEYSERVILLE 1102 | SONOMA | 3.9586 | 50.2588 | 84.68% | 0 | 1 | 20.33% | 44.47% | 1 | 0.040497 | 1 | 2.3001 | 0.093146 | Medium | Medium | Medium | 1809 | 1843 | 0.040497 | 61.9956
CORNING 110182846 | CORNING 1101 | NORTH VALLEY | 5.0438 | 29.0672 | 100% | 1 | 5 | 99.85% | 0% | 0 | 0.046785 | 1 | 1.9907 | 0.093136 | Medium | Medium | Low | 1810 | 1727 | 0.046785 | 61.9024
TAR FLAT 04023144 | TAR FLAT 0402 | YOSEMITE | 4.9761 | 11.3882 | 27.07% | 0 | 3 | 96.83% | 26.03% | 1 | 0.032346 | 1 | 2.8761 | 0.093031 | Medium | Medium | Medium | 1811 | 2033 | 0.032346 | 61.8093
OLETA 110113478 | OLETA 1101 | STOCKTON | 13.3756 | 25.4349 | 51.06% | 1 | 4 | 86.71% | 0% | 0 | 0.02671 | 1 | 3.4668 | 0.092599 | Medium | Medium | High | 1812 | 2197 | 0.02671 | 61.7163
ELECTRA 110136816 | ELECTRA 1101 | STOCKTON | 16.3224 | 14.0317 | 85.78% | 2 | 8 | 100% | 0% | 0 | 0.035905 | 1 | 2.5788 | 0.092591 | Medium | Medium | Medium | 1813 | 1936 | 0.035905 | 61.6237
FROGTOWN 1701L3361 | FROGTOWN 1701 | STOCKTON | 1.8736 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.2429 | 0.092461 | Medium | Medium | High | 1814 | 2132 | 0.028512 | 61.5311
IONE 1101L3141 | IONE 1101 | STOCKTON | 13.6703 | 41.1561 | 100% | 0 | 0 | 97.4% | 0% | 0 | 0.034177 | 1 | 2.7017 | 0.092334 | Medium | Medium | Medium | 1815 | 1970 | 0.034177 | 61.4386
DOBBINS 11011808 | DOBBINS 1101 | SIERRA | 15.539 | 16.962 | 100% | 1 | 0 | 100% | 6.412% | 0 | 0.043272 | 1 | 2.1331 | 0.092302 | Medium | Medium | Low | 1816 | 1790 | 0.043272 | 61.3463
MORAGA 1104N532R | MORAGA 1104 | DIABLO | 4.4858 | 10 | 51.34% | 1 | 5 | 97.29% | 0% | 0 | 0.023997 | 1 | 3.8388 | 0.09212 | Medium | Medium | High | 1817 | 2277 | 0.023997 | 61.254
MESA 1103M72 | MESA 1103 | LOS PADRES | 9.6841 | 10 | 75.44% | 1 | 10 | 38.47% | 0% | 0 | 0.039556 | 1 | 2.326 | 0.092007 | Medium | Medium | Medium | 1818 | 1870 | 0.039556 | 61.1619
CORNING 110185162 | CORNING 1101 | NORTH VALLEY | 5.7561 | 60.2607 | 100% | 0 | 2 | 100% | 0% | 0 | 0.047015 | 1 | 1.9543 | 0.09188 | Medium | Medium | Low | 1819 | 1724 | 0.047015 | 61.0698
TEMPLETON 2110N30 | TEMPLETON 2110 | LOS PADRES | 20.4995 | 52.4771 | 52.2% | 1 | 3 | 100% | 0% | 0 | 0.040875 | 1 | 2.2426 | 0.091666 | Medium | Medium | Medium | 1820 | 1834 | 0.040875 | 60.978
POINT ARENA 1101474 | POINT ARENA 1101 | HUMBOLDT | 9.0104 | 63.6125 | 35.39% | 4 | 6 | 100% | 0% | 0 | 0.042479 | 1 | 2.1511 | 0.091377 | Medium | Medium | Low | 1821 | 1807 | 0.042479 | 60.8863
DESCHUTES 1104CB | DESCHUTES 1104 | NORTH VALLEY | 12.32 | 22.7091 | 100% | 1 | 6 | 50.17% | 0% | 0 | 0.028343 | 1 | 3.212 | 0.091036 | Medium | Medium | High | 1822 | 2158 | 0.028343 | 60.7949
SYCAMORE CREEK 1111 | SYCAMORE CREEK 1111 | NORTH VALLEY | 0.19166 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.1909 | 0.090978 | Medium | Medium | High | 1823 | 2136 | 0.028512 | 60.7039
BROWNS VALLEY 110193870 | BROWNS VALLEY 1101 | SIERRA | 16.0223 | 22.1517 | 92.34% | 3 | 17 | 47.1% | 0% | 0 | 0.037632 | 1 | 2.4175 | 0.090975 | Medium | Medium | Medium | 1824 | 1903 | 0.037632 | 60.6129
PLACERVILLE 1110CB | PLACERVILLE 1110 | SIERRA | 11.9057 | 10.8465 | 38.55% | 4 | 14 | 94.9% | 13.5% | 1 | 0.032906 | 1 | 2.7626 | 0.090907 | Medium | Medium | Medium | 1825 | 2014 | 0.032906 | 60.5219
VOLTA 110180454 | VOLTA 1101 | NORTH VALLEY | 31.4882 | 39.839 | 95.78% | 4 | 1 | 97.71% | 0.9246% | 0 | 0.076439 | 1 | 1.1851 | 0.090591 | High | High | Low | 1826 | 1430 | 0.076439 | 60.431
FROGTOWN 17021573 | FROGTOWN 1702 | STOCKTON | 18.0626 | 46.2084 | 95.86% | 0 | 3 | 100% | 0% | 0 | 0.042352 | 1 | 2.1385 | 0.090571 | Medium | Medium | Low | 1827 | 1811 | 0.042352 | 60.3404
FROGTOWN 1702L5407 | FROGTOWN 1702 | STOCKTON | 17.9809 | 33.0373 | 100% | 0 | 9 | 98.72% | 0% | 0 | 0.03936 | 1 | 2.2967 | 0.090399 | Medium | Medium | Medium | 1828 | 1875 | 0.03936 | 60.2499
ATASCADERO 11012379 | ATASCADERO 1101 | LOS PADRES | 0.72914 | 10 | 100% | 1 | 2 | 100% | 0% | 0 | 0.030081 | 1 | 3.0039 | 0.090361 | Medium | Medium | Medium | 1829 | 2097 | 0.030081 | 60.1595
MIDDLETOWN 1102514 | MIDDLETOWN 1102 | HUMBOLDT | 4.5797 | 10 | 100% | 1 | 1 | 86.53% | 0% | 0 | 0.025849 | 1 | 3.491 | 0.090241 | Medium | Medium | High | 1830 | 2219 | 0.025849 | 60.0691
REEDLEY 1104 | REEDLEY 1104 | FRESNO | 0.23841 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.1623 | 0.090163 | Medium | Medium | High | 1831 | 2136 | 0.028512 | 59.9789
FRUITLAND 11426054 | FRUITLAND 1142 | HUMBOLDT | 10.4759 | 81.7883 | 49.67% | 26 | 9 | 100% | 0% | 0 | 0.058078 | 1 | 1.5506 | 0.090055 | Medium | Medium | Low | 1832 | 1595 | 0.058078 | 59.8887
GRAYS FLAT 0401CB | GRAYS FLAT 0401 | NORTH VALLEY | 10.7057 | 82.9815 | 68.42% | 5 | 6 | 100% | 0% | 0 | 0.063148 | 1 | 1.4254 | 0.090014 | High | High | Low | 1833 | 1532 | 0.063148 | 59.7986
FROGTOWN 17027134 | FROGTOWN 1702 | STOCKTON | 19.267 | 44.0538 | 84.25% | 0 | 2 | 84.8% | 0% | 0 | 0.047354 | 1 | 1.8987 | 0.089911 | Medium | Medium | Low | 1834 | 1720 | 0.047354 | 59.7086
WILLOW CREEK 11035012 | WILLOW CREEK 1103 | HUMBOLDT | 10.8623 | 35.544 | 71.11% | 10 | 12 | 100% | 0% | 0 | 0.044176 | 1 | 2.0337 | 0.08984 | Medium | Medium | Low | 1835 | 1772 | 0.044176 | 59.6187
DIAMOND SPRINGS 110650324 | DIAMOND SPRINGS 1106 | SIERRA | 17.7246 | 10 | 70.6% | 6 | 3 | 87.05% | 0% | 0 | 0.038264 | 1 | 2.3467 | 0.089792 | Medium | Medium | Medium | 1836 | 1892 | 0.038264 | 59.5289
KONOCTI 1102716 | KONOCTI 1102 | HUMBOLDT | 12.6002 | 59.2136 | 49.34% | 2 | 6 | 73.82% | 22.04% | 1 | 0.033546 | 1 | 2.6664 | 0.089449 | Medium | Medium | Medium | 1837 | 1992 | 0.033546 | 59.4391
TEMPLETON 2113A20 | TEMPLETON 2113 | LOS PADRES | 7.0532 | 26.1549 | 66.41% | 2 | 0 | 89.65% | 0% | 0 | 0.033191 | 1 | 2.6768 | 0.088847 | Medium | Medium | Medium | 1838 | 2001 | 0.033191 | 59.3496
LAKEVILLE 110287432 | LAKEVILLE 1102 | SONOMA | 8.9371 | 82.9673 | 68.1% | 1 | 4 | 65.45% | 0% | 0 | 0.032044 | 1 | 2.7702 | 0.088771 | Medium | Medium | Medium | 1839 | 2045 | 0.032044 | 59.2608
ROSSMOOR 1101L503R | ROSSMOOR 1101 | DIABLO | 4.2657 | 11.5666 | 6.541% | 0 | 11 | 100% | 15.14% | 0 | 0.024651 | 1 | 3.5968 | 0.088666 | Medium | Medium | High | 1840 | 2252 | 0.024651 | 59.172
FRUITLAND 11422006 | FRUITLAND 1142 | HUMBOLDT | 8.3587 | 77.2327 | 73.06% | 6 | 2 | 90.12% | 0% | 0 | 0.041689 | 1 | 2.1223 | 0.088478 | Medium | Medium | Low | 1841 | 1824 | 0.041689 | 59.0834
ARCATA 11224218 | ARCATA 1122 | HUMBOLDT | 4.9191 | 35.3774 | 67.92% | 2 | 3 | 99.74% | 0% | 0 | 0.032319 | 1 | 2.7359 | 0.088422 | Medium | Medium | Medium | 1842 | 2035 | 0.032319 | 58.9949
GARBERVILLE 1101CB | GARBERVILLE 1101 | HUMBOLDT | 6.497 | 63.3643 | 74.83% | 4 | 3 | 74.77% | 0% | 0 | 0.037653 | 1 | 2.3445 | 0.088278 | Medium | Medium | Medium | 1843 | 1902 | 0.037653 | 58.9065
CEDAR CREEK 11011664 | CEDAR CREEK 1101 | NORTH VALLEY | 29.6947 | 28.7537 | 98.78% | 0 | 12 | 100% | 0% | 0 | 0.067598 | 1 | 1.3051 | 0.088223 | High | High | Low | 1844 | 1490 | 0.067598 | 58.8182
UKIAH 11143606 | UKIAH 1114 | HUMBOLDT | 9.6068 | 79.0327 | 97.2% | 3 | 5 | 58.23% | 0% | 0 | 0.033786 | 1 | 2.6108 | 0.088208 | Medium | Medium | Medium | 1845 | 1983 | 0.033786 | 58.73
REDBUD 1101CB | REDBUD 1101 | HUMBOLDT | 4.9191 | 32.5631 | 40.27% | 2 | 12 | 69.43% | 0% | 0 | 0.033542 | 1 | 2.6297 | 0.088206 | Medium | Medium | Medium | 1846 | 1993 | 0.033542 | 58.6417
PHILO 11021308 | PHILO 1102 | HUMBOLDT | 31.8312 | 64.2643 | 100% | 9 | 11 | 100% | 0% | 0 | 0.06454 | 1 | 1.3663 | 0.088181 | High | High | Low | 1847 | 1519 | 0.06454 | 58.5535
PEORIA 1705999 | PEORIA 1705 | YOSEMITE | 2.3082 | 18.7547 | 99.88% | 0 | 0 | 100% | 0% | 0 | 0.030188 | 1 | 2.9134 | 0.087952 | Medium | Medium | Medium | 1848 | 2093 | 0.030188 | 58.4654
PLACERVILLE 210623190 | PLACERVILLE 2106 | SIERRA | 3.6751 | 24.4138 | 66.27% | 0 | 8 | 100% | 2.399% | 0 | 0.033321 | 1 | 2.6363 | 0.087845 | Medium | Medium | Medium | 1849 | 1998 | 0.033321 | 58.3774
OLETA 11021204 | OLETA 1102 | STOCKTON | 24.7673 | 19.1315 | 95.37% | 0 | 4 | 83.58% | 2.402% | 0 | 0.036314 | 1 | 2.4177 | 0.087794 | Medium | Medium | Medium | 1850 | 1928 | 0.036314 | 58.2896
HIGGINS 1109 | HIGGINS 1109 | SIERRA | 0.056072 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.0741 | 0.087647 | Medium | Medium | Medium | 1851 | 2132 | 0.028512 | 58.2018
LAS POSITAS 2108MR182 | LAS POSITAS 2108 | MISSION | 6.1551 | 52.1024 | 25.77% | 0 | 0 | 85.34% | 0% | 0 | 0.030304 | 1 | 2.8822 | 0.087344 | Medium | Medium | Medium | 1852 | 2086 | 0.030304 | 58.1141
BIG MEADOWS 21012586 | BIG MEADOWS 2101 | NORTH VALLEY | 9.5691 | 78.6746 | 93% | 0 | 0 | 87.41% | 0% | 0 | 0.037594 | 1 | 2.3215 | 0.087275 | Medium | Medium | Medium | 1853 | 1904 | 0.037594 | 58.0268
NARROWS 210534069 | NARROWS 2105 | SIERRA | 15.7398 | 14.9961 | 98.66% | 0 | 6 | 100% | 0% | 0 | 0.048393 | 1 | 1.8027 | 0.087238 | Medium | Medium | Low | 1854 | 1704 | 0.048393 | 57.9395
DEL MONTE 21032654 | DEL MONTE 2103 | CENTRAL COAST | 1.8437 | 10 | 36.65% | 2 | 2 | 100% | 0% | 0 | 0.027064 | 1 | 3.2195 | 0.087132 | Medium | Medium | High | 1855 | 2191 | 0.027064 | 57.8523
WILLOW CREEK 1103CB | WILLOW CREEK 1103 | HUMBOLDT | 3.9217 | 18.1592 | 58.12% | 1 | 8 | 100% | 7.1% | 0 | 0.048009 | 1 | 1.8137 | 0.087072 | Medium | Medium | Low | 1856 | 1707 | 0.048009 | 57.7651
PERRY 1101V74 | PERRY 1101 | LOS PADRES | 2.9727 | 10 | 2.672% | 10 | 7 | 58.33% | 0% | 0 | 0.024878 | 1 | 3.4959 | 0.086972 | Medium | Medium | High | 1857 | 2247 | 0.024878 | 57.6781
PLACERVILLE 111219742 | PLACERVILLE 1112 | SIERRA | 7.3806 | 10 | 51.29% | 2 | 12 | 99.39% | 0% | 0 | 0.032573 | 1 | 2.6661 | 0.086842 | Medium | Medium | Medium | 1858 | 2025 | 0.032573 | 57.5911
POINT ARENA 110147952 | POINT ARENA 1101 | HUMBOLDT | 10.391 | 76.4518 | 10.32% | 20 | 9 | 100% | 0% | 0 | 0.043386 | 1 | 1.9987 | 0.086717 | Medium | Medium | Low | 1859 | 1787 | 0.043386 | 57.5042
KONOCTI 1108950 | KONOCTI 1108 | HUMBOLDT | 6.231 | 17.4671 | 73.5% | 1 | 1 | 84.02% | 0% | 0 | 0.031636 | 1 | 2.7401 | 0.086689 | Medium | Medium | Medium | 1860 | 2056 | 0.031636 | 57.4175
HIGGINS 1104498932 | HIGGINS 1104 | SIERRA | 3.4528 | 10 | 98.29% | 1 | 2 | 80.99% | 0% | 0 | 0.024651 | 1 | 3.516 | 0.086673 | Medium | Medium | High | 1861 | 2253 | 0.024651 | 57.3308
ALHAMBRA 11058302 | ALHAMBRA 1105 | DIABLO | 8.2556 | 10 | 24.97% | 0 | 12 | 100% | 0% | 0 | 0.029452 | 1 | 2.9395 | 0.086573 | Medium | Medium | Medium | 1862 | 2113 | 0.029452 | 57.2442
SAUSALITO 11021268 | SAUSALITO 1102 | NORTH BAY | 5.0112 | 23.3781 | 0.422% | 3 | 4 | 100% | 0% | 0 | 0.030259 | 1 | 2.8544 | 0.086372 | Medium | Medium | Medium | 1863 | 2088 | 0.030259 | 57.1576
KANAKA 11011036 | KANAKA 1101 | NORTH VALLEY | 0.60846 | 67.9249 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041796 | 1 | 2.0662 | 0.086358 | Medium | Medium | Low | 1864 | 1820 | 0.041796 | 57.0712
CORRAL 110359770 | CORRAL 1103 | STOCKTON | 4.5619 | 12.4013 | 100% | 1 | 1 | 62.81% | 0% | 0 | 0.02373 | 1 | 3.6376 | 0.086321 | Medium | Medium | High | 1865 | 2288 | 0.02373 | 56.9849
UPPER LAKE 1101CB | UPPER LAKE 1101 | HUMBOLDT | 1.1134 | 70.0562 | 95.06% | 2 | 2 | 100% | 0% | 0 | 0.049432 | 1 | 1.7447 | 0.086245 | Medium | Medium | Low | 1866 | 1690 | 0.049432 | 56.8985
CAYETANO 2111MR444 | CAYETANO 2111 | MISSION | 0.15169 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.0154 | 0.085973 | Medium | Medium | Medium | 1867 | 2132 | 0.028512 | 56.8123
PLACERVILLE 1112CB | PLACERVILLE 1112 | SIERRA | 7.6031 | 10 | 47.53% | 2 | 8 | 81.02% | 0.2042% | 0 | 0.027832 | 1 | 3.0844 | 0.085847 | Medium | Medium | High | 1868 | 2167 | 0.027832 | 56.7263
JAMESON 1103CB | JAMESON 1103 | SACRAMENTO | 3.6313 | 55.7827 | 92.07% | 0 | 1 | 33.3% | 0% | 0 | 0.025062 | 1 | 3.4236 | 0.085801 | Medium | Medium | High | 1869 | 2240 | 0.025062 | 56.6405
FRENCH GULCH 11011464 | FRENCH GULCH 1101 | NORTH VALLEY | 3.9608 | 72.3083 | 100% | 3 | 0 | 100% | 0% | 0 | 0.044678 | 1 | 1.9188 | 0.085727 | Medium | Medium | Low | 1870 | 1767 | 0.044678 | 56.5547
NARROWS 21052426 | NARROWS 2105 | SIERRA | 9.7882 | 10 | 86.21% | 2 | 2 | 56.57% | 0% | 0 | 0.026381 | 1 | 3.2439 | 0.085575 | Medium | Medium | High | 1871 | 2209 | 0.026381 | 56.469
PENRYN 11072708 | PENRYN 1107 | SIERRA | 8.636 | 10 | 67.69% | 3 | 4 | 79.72% | 0% | 0 | 0.026402 | 1 | 3.2393 | 0.085524 | Medium | Medium | High | 1872 | 2208 | 0.026402 | 56.3834
SISQUOC 1102M52 | SISQUOC 1102 | LOS PADRES | 31.4004 | 61.3581 | 49.81% | 0 | 2 | 87.94% | 100% | 0 | 0.18147 | 1 | 0.47061 | 0.0854 | High | High | Low | 1873 | 1089 | 0.18147 | 56.2979
GREENBRAE 1102CB | GREENBRAE 1102 | NORTH BAY | 0.15859 | 10 | 0% | 0 | 0 | 7.352% | 100% | 0 | 0.025266 | 1 | 3.3659 | 0.085044 | Medium | Medium | High | 1874 | 2234 | 0.025266 | 56.2125
TEJON 11022455 | TEJON 1102 | KERN | 6.4984 | 10 | 98.01% | 0 | 2 | 100% | 0% | 0 | 0.043014 | 1 | 1.9757 | 0.084983 | Medium | Medium | Low | 1875 | 1797 | 0.043014 | 56.1274
HIGGINS 1107 | HIGGINS 1107 | SIERRA | 0.013093 | 10 | 100% | 0 | 0 | 86.65% | 0% | 0 | 0.025031 | 1 | 3.3943 | 0.084962 | Medium | Medium | High | 1876 | 2242 | 0.025031 | 56.0424
WOODSIDE 11049116 | WOODSIDE 1104 | PENINSULA | 1.063 | 10 | 91% | 2 | 5 | 24.81% | 0% | 0 | 0.018746 | 1 | 4.5156 | 0.08465 | Low | Low | High | 1877 | 2459 | 0.018746 | 55.9575
FROGTOWN 17016807 | FROGTOWN 1701 | STOCKTON | 4.7513 | 29.5232 | 87.38% | 0 | 3 | 100% | 0% | 0 | 0.031186 | 1 | 2.7121 | 0.084578 | Medium | Medium | Medium | 1878 | 2068 | 0.031186 | 55.8728
HIGGINS 11071070 | HIGGINS 1107 | SIERRA | 7.012 | 12.4115 | 99.96% | 1 | 4 | 84.37% | 0% | 0 | 0.027337 | 1 | 3.0898 | 0.084465 | Medium | Medium | High | 1879 | 2184 | 0.027337 | 55.7882
ANTLER 11011384 | ANTLER 1101 | NORTH VALLEY | 8.8576 | 10 | 98.19% | 3 | 9 | 97.22% | 0% | 0 | 0.08259 | 1 | 1.0219 | 0.084396 | High | High | Low | 1880 | 1376 | 0.08259 | 55.7038
SOBRANTE 1101CB | SOBRANTE 1101 | DIABLO | 13.5487 | 10.8121 | 22.39% | 1 | 13 | 87.75% | 0% | 0 | 0.02661 | 1 | 3.1685 | 0.084314 | Medium | Medium | High | 1881 | 2201 | 0.02661 | 55.6194
BRENTWOOD 21056512 | BRENTWOOD 2105 | DIABLO | 0.65133 | 10 | 96.38% | 0 | 1 | 100% | 0% | 0 | 0.032177 | 1 | 2.6202 | 0.084309 | Medium | Medium | Medium | 1882 | 2039 | 0.032177 | 55.5351
HOPLAND 11014626 | HOPLAND 1101 | HUMBOLDT | 24.0779 | 57.1108 | 92.12% | 0 | 5 | 79.18% | 0% | 0 | 0.055167 | 1 | 1.524 | 0.084074 | Medium | Medium | Low | 1883 | 1624 | 0.055167 | 55.4508
DIAMOND SPRINGS 110676088 | DIAMOND SPRINGS 1106 | SIERRA | 11.0713 | 10.8319 | 90.75% | 3 | 3 | 100% | 0% | 0 | 0.038075 | 1 | 2.2072 | 0.08404 | Medium | Medium | Low | 1884 | 1896 | 0.038075 | 55.3667
POINT MORETTI 11015104 | POINT MORETTI 1101 | CENTRAL COAST | 1.8713 | 40.903 | 21.17% | 4 | 0 | 100% | 0% | 0 | 0.032915 | 1 | 2.5532 | 0.084038 | Medium | Medium | Medium | 1885 | 2013 | 0.032915 | 55.2826
MONTICELLO 11011589 | MONTICELLO 1101 | NORTH BAY | 4.3101 | 10 | 98.73% | 0 | 3 | 100% | 0% | 0 | 0.034141 | 1 | 2.4603 | 0.083998 | Medium | Medium | Medium | 1886 | 1971 | 0.034141 | 55.1986
CAMP EVERS 2106CB | CAMP EVERS 2106 | CENTRAL COAST | 0.018997 | 10 | 0% | 0 | 0 | 0.8166% | 100% | 0 | 0.023702 | 1 | 3.5428 | 0.083973 | Medium | Medium | High | 1887 | 2289 | 0.023702 | 55.1146
COTTONWOOD 1102CB | COTTONWOOD 1102 | NORTH VALLEY | 16.7139 | 23.1081 | 88.08% | 1 | 4 | 71.09% | 0% | 0 | 0.039338 | 1 | 2.1337 | 0.083935 | Medium | Medium | Low | 1888 | 1876 | 0.039338 | 55.0306
WEIMAR 1101CB | WEIMAR 1101 | SIERRA | 9.2462 | 10 | 51.97% | 4 | 11 | 100% | 0% | 0 | 0.04865 | 1 | 1.7246 | 0.083901 | Medium | Medium | Low | 1889 | 1700 | 0.04865 | 54.9467
CASTRO VALLEY 1108CB | CASTRO VALLEY 1108 | MISSION | 1.4946 | 10 | 6.175% | 3 | 1 | 53.21% | 52.04% | 0 | 0.023442 | 1 | 3.5736 | 0.083772 | Medium | Medium | High | 1890 | 2297 | 0.023442 | 54.8628
OREGON TRAIL 1104CB | OREGON TRAIL 1104 | NORTH VALLEY | 10.8574 | 25.7844 | 63.12% | 2 | 12 | 74.06% | 0% | 0 | 0.031086 | 1 | 2.6945 | 0.08376 | Medium | Medium | Medium | 1891 | 2069 | 0.031086 | 54.779
SARATOGA 1106LC22 | SARATOGA 1106 | DE ANZA | 7.1525 | 10 | 35.66% | 5 | 5 | 86.79% | 0% | 0 | 0.020092 | 1 | 4.16 | 0.083584 | Low | Low | High | 1892 | 2405 | 0.020092 | 54.6953
SO. CAL. EDISON #2 1101CB | SO. CAL. EDISON #2 1101 | YOSEMITE | 1.1766 | 10 | 100% | 0 | 0 | 100% | 37.67% | 0 | 0.051431 | 1 | 1.6243 | 0.08354 | Medium | Medium | Low | 1893 | 1669 | 0.051431 | 54.6117
EEL RIVER 11021902 | EEL RIVER 1102 | HUMBOLDT | 5.1093 | 87.5518 | 84.86% | 3 | 2 | 68.94% | 0% | 0 | 0.043714 | 1 | 1.9061 | 0.083323 | Medium | Medium | Low | 1894 | 1782 | 0.043714 | 54.5281
LAURELES 11122142 | LAURELES 1112 | CENTRAL COAST | 8.368 | 31.5595 | 39.83% | 4 | 4 | 87.21% | 0% | 0 | 0.030233 | 1 | 2.7544 | 0.083276 | Medium | Medium | Medium | 1895 | 2090 | 0.030233 | 54.4448
HIGGINS 11039753 | HIGGINS 1103 | SIERRA | 2.1041 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.918 | 0.083198 | Medium | Medium | Medium | 1896 | 2136 | 0.028512 | 54.3615
CALPELLA 1101542 | CALPELLA 1101 | HUMBOLDT | 23.4567 | 35.4534 | 89.83% | 1 | 18 | 100% | 0% | 0 | 0.058405 | 1 | 1.4223 | 0.083068 | Medium | Medium | Low | 1897 | 1588 | 0.058405 | 54.2783
DUNBAR 110179086 | DUNBAR 1101 | SONOMA | 6.3052 | 21.6901 | 56.75% | 1 | 5 | 90.82% | 0% | 0 | 0.02897 | 1 | 2.866 | 0.083029 | Medium | Medium | Medium | 1898 | 2124 | 0.02897 | 54.1953
SARATOGA 1106LC24 | SARATOGA 1106 | DE ANZA | 6.2415 | 10 | 42.44% | 3 | 7 | 55.48% | 10.64% | 0 | 0.021404 | 1 | 3.8778 | 0.083 | Low | Low | High | 1899 | 2354 | 0.021404 | 54.1122
DEL MONTE 21042762 | DEL MONTE 2104 | CENTRAL COAST | 9.4859 | 27.7626 | 17.65% | 2 | 4 | 85.79% | 0% | 0 | 0.03979 | 1 | 2.0858 | 0.082991 | Medium | Medium | Low | 1900 | 1862 | 0.03979 | 54.0292
CALAVERAS CEMENT 110136880 | CALAVERAS CEMENT 1101 | STOCKTON | 7.22 | 30.9732 | 81.65% | 0 | 2 | 83.77% | 0% | 0 | 0.037097 | 1 | 2.235 | 0.082911 | Medium | Medium | Medium | 1901 | 1915 | 0.037097 | 53.9463
MORGAN HILL 2105XR152 | MORGAN HILL 2105 | SAN JOSE | 8.3434 | 31.972 | 72.23% | 0 | 5 | 65.24% | 0% | 0 | 0.027024 | 1 | 3.0674 | 0.082892 | Medium | Medium | Medium | 1902 | 2192 | 0.027024 | 53.8633
WYANDOTTE 110738438 | WYANDOTTE 1107 | NORTH VALLEY | 16.8538 | 17.2711 | 100% | 1 | 4 | 100% | 13.33% | 1 | 0.046053 | 1 | 1.7995 | 0.082871 | Medium | Medium | Low | 1903 | 1742 | 0.046053 | 53.7804
AUBERRY 1102R1013 | AUBERRY 1102 | FRESNO | 12.3506 | 22.637 | 85.13% | 0 | 11 | 100% | 0% | 0 | 0.039152 | 1 | 2.1117 | 0.082679 | Medium | Medium | Low | 1904 | 1878 | 0.039152 | 53.6976
AUBERRY 110237466 | AUBERRY 1102 | FRESNO | 31.5797 | 23.1987 | 95.92% | 2 | 3 | 100% | 0% | 0 | 0.048258 | 1 | 1.7115 | 0.082592 | Medium | Medium | Low | 1905 | 1706 | 0.048258 | 53.6149
BANGOR 11011806 | BANGOR 1101 | NORTH VALLEY | 8.946 | 12.2309 | 77.62% | 0 | 5 | 97.6% | 0% | 0 | 0.033897 | 1 | 2.4358 | 0.082565 | Medium | Medium | Medium | 1906 | 1980 | 0.033897 | 53.5323
HALF MOON BAY 11036012 | HALF MOON BAY 1103 | PENINSULA | 5.8906 | 54.5639 | 76.22% | 11 | 4 | 61.12% | 0% | 0 | 0.039954 | 1 | 2.0637 | 0.082451 | Medium | Medium | Low | 1907 | 1857 | 0.039954 | 53.4497
RIDGE 0401CB | RIDGE 0401 | EAST BAY | 2.662 | 10 | 10.22% | 3 | 4 | 100% | 0% | 0 | 0.02026 | 1 | 4.0693 | 0.082444 | Low | Low | High | 1908 | 2397 | 0.02026 | 53.3673
STILLWATER 11021644 | STILLWATER 1102 | NORTH VALLEY | 22.854 | 11.5095 | 100% | 1 | 6 | 100% | 0% | 0 | 0.048415 | 1 | 1.7011 | 0.08236 | Medium | Medium | Low | 1909 | 1703 | 0.048415 | 53.2848
LAKEWOOD 210738404 | LAKEWOOD 2107 | DIABLO | 6.7961 | 30.5815 | 25.31% | 5 | 8 | 68.2% | 1.158% | 0 | 0.024865 | 1 | 3.312 | 0.082353 | Medium | Medium | High | 1910 | 2248 | 0.024865 | 53.2025
LUCERNE 11031663 | LUCERNE 1103 | HUMBOLDT | 1.2106 | 10 | 52.73% | 0 | 6 | 100% | 0% | 0 | 0.022038 | 1 | 3.735 | 0.082313 | Medium | Medium | High | 1911 | 2335 | 0.022038 | 53.1201
JESSUP 11019752 | JESSUP 1101 | NORTH VALLEY | 3.8979 | 33.5364 | 99.93% | 0 | 1 | 100% | 0% | 0 | 0.033991 | 1 | 2.4213 | 0.082304 | Medium | Medium | Medium | 1912 | 1976 | 0.033991 | 53.0378
MARTELL 11033152 | MARTELL 1103 | STOCKTON | 16.8696 | 31.4572 | 87.03% | 0 | 1 | 99.4% | 0% | 0 | 0.034215 | 1 | 2.4031 | 0.082223 | Medium | Medium | Medium | 1913 | 1969 | 0.034215 | 52.9555
OREGON TRAIL 110249144 | OREGON TRAIL 1102 | NORTH VALLEY | 16.2173 | 16.9745 | 93.48% | 1 | 0 | 76.03% | 0% | 0 | 0.029469 | 1 | 2.7862 | 0.082107 | Medium | Medium | Medium | 1914 | 2112 | 0.029469 | 52.8733
RINCON 1103472 | RINCON 1103 | SONOMA | 3.3276 | 10 | 93.65% | 0 | 2 | 70.54% | 3.999% | 0 | 0.025694 | 1 | 3.1877 | 0.081905 | Medium | Medium | High | 1915 | 2225 | 0.025694 | 52.7912
ANNAPOLIS 110176842 | ANNAPOLIS 1101 | HUMBOLDT | 5.647 | 81.667 | 98.52% | 2 | 3 | 100% | 0% | 0 | 0.055858 | 1 | 1.4662 | 0.0819 | Medium | Medium | Low | 1916 | 1614 | 0.055858 | 52.7093
PEORIA 170459596 | PEORIA 1704 | YOSEMITE | 19.1476 | 35.0672 | 53.97% | 0 | 6 | 53.15% | 0% | 0 | 0.024608 | 1 | 3.3279 | 0.081892 | Medium | Medium | High | 1917 | 2255 | 0.024608 | 52.6274
NAPA 11121302 | NAPA 1112 | NORTH BAY | 17.5904 | 30.9393 | 74.37% | 2 | 8 | 52.69% | 0% | 0 | 0.026355 | 1 | 3.0997 | 0.081693 | Medium | Medium | High | 1918 | 2210 | 0.026355 | 52.5455
BUELLTON 1101Y26 | BUELLTON 1101 | LOS PADRES | 14.0549 | 47.3747 | 54.06% | 1 | 8 | 88.5% | 0% | 0 | 0.039723 | 1 | 2.0524 | 0.081528 | Medium | Medium | Low | 1919 | 1864 | 0.039723 | 52.4638
RALSTON 110148936 | RALSTON 1101 | PENINSULA | 3.4057 | 10 | 32.09% | 0 | 3 | 56.99% | 0% | 0 | 0.025196 | 1 | 3.2337 | 0.081477 | Medium | Medium | High | 1920 | 2236 | 0.025196 | 52.3823
KIRKER 2104442850 | KIRKER 2104 | DIABLO | 5.4258 | 10 | 43.23% | 0 | 4 | 95.36% | 0% | 0 | 0.024306 | 1 | 3.3502 | 0.081427 | Medium | Medium | High | 1921 | 2267 | 0.024306 | 52.3008
BANGOR 1101CB | BANGOR 1101 | NORTH VALLEY | 18.8771 | 14.9118 | 68.16% | 4 | 2 | 88.52% | 0% | 0 | 0.029011 | 1 | 2.802 | 0.081291 | Medium | Medium | Medium | 1922 | 2123 | 0.029011 | 52.2194
MERCED FALLS 110222772 | MERCED FALLS 1102 | YOSEMITE | 2.2922 | 12.637 | 100% | 0 | 0 | 100% | 0% | 0 | 0.029016 | 14.9507 | 0.18721 | 0.081211 | Medium | Medium | Low | 1923 | 878 | 0.4338 | 52.1381
HIGGINS 110391052 | HIGGINS 1103 | SIERRA | 0.64834 | 10 | 100% | 0 | 0 | 84.24% | 0% | 0 | 0.024449 | 1 | 3.3175 | 0.081108 | Medium | Medium | High | 1924 | 2263 | 0.024449 | 52.0569
SAN RAFAEL 110168970 | SAN RAFAEL 1101 | NORTH BAY | 1.3404 | 10 | 17.09% | 0 | 0 | 31.9% | 46.84% | 0 | 0.018013 | 1 | 4.4995 | 0.08105 | Low | Low | High | 1925 | 2487 | 0.018013 | 51.9758
BIG MEADOWS 21012260 | BIG MEADOWS 2101 | NORTH VALLEY | 17.1948 | 71.2696 | 55.9% | 4 | 0 | 76.22% | 0% | 0 | 0.032561 | 1 | 2.4871 | 0.080983 | Medium | Medium | Medium | 1926 | 2026 | 0.032561 | 51.8947
GARBERVILLE 1102CB | GARBERVILLE 1102 | HUMBOLDT | 10.6146 | 34.8511 | 30.11% | 18 | 9 | 65.56% | 0% | 0 | 0.030692 | 1 | 2.6357 | 0.080896 | Medium | Medium | Medium | 1927 | 2077 | 0.030692 | 51.8137
HIGGINS 11094189 | HIGGINS 1109 | SIERRA | 3.326 | 25.4516 | 99.91% | 0 | 3 | 100% | 0% | 0 | 0.033551 | 1 | 2.4095 | 0.080842 | Medium | Medium | Medium | 1928 | 1991 | 0.033551 | 51.7328
OLETA 1102CB | OLETA 1102 | STOCKTON | 12.9237 | 28.5426 | 79.87% | 0 | 5 | 85.32% | 0% | 0 | 0.038817 | 1 | 2.0783 | 0.080675 | Medium | Medium | Low | 1929 | 1884 | 0.038817 | 51.652
TASSAJARA 210883368 | TASSAJARA 2108 | DIABLO | 0.069317 | 10 | 0% | 0 | 0 | 1.551% | 100% | 0 | 0.023873 | 1 | 3.3752 | 0.080577 | Medium | Medium | High | 1930 | 2281 | 0.023873 | 51.5713
MORRO BAY 110249632 | MORRO BAY 1102 | LOS PADRES | 0.66912 | 10 | 0% | 0 | 3 | 100% | 0% | 0 | 0.017573 | 1 | 4.5803 | 0.080492 | Low | Low | High | 1931 | 2506 | 0.017573 | 51.4907
TEMPLETON 2111R86 | TEMPLETON 2111 | LOS PADRES | 10.174 | 35.046 | 79.62% | 2 | 6 | 70.64% | 0% | 0 | 0.032293 | 1 | 2.4827 | 0.080172 | Medium | Medium | Medium | 1932 | 2036 | 0.032293 | 51.4102
STELLING 11109265 | STELLING 1110 | DE ANZA | 5.4699 | 10 | 92.07% | 0 | 1 | 100% | 0% | 0 | 0.027307 | 1 | 2.9335 | 0.080104 | Medium | Medium | Medium | 1933 | 2186 | 0.027307 | 51.3301
MARTELL 1102CB | MARTELL 1102 | STOCKTON | 6.4004 | 24.1429 | 66.43% | 0 | 4 | 94.03% | 0% | 0 | 0.031753 | 1 | 2.5224 | 0.080095 | Medium | Medium | Medium | 1934 | 2052 | 0.031753 | 51.25
SAN RAFAEL 1105534 | SAN RAFAEL 1105 | NORTH BAY | 1.348 | 10 | 81.92% | 3 | 4 | 85.31% | 0% | 0 | 0.024098 | 1 | 3.3132 | 0.079842 | Medium | Medium | High | 1935 | 2276 | 0.024098 | 51.1699
VIEJO 22012064 | VIEJO 2201 | CENTRAL COAST | 0.87679 | 10 | 42.79% | 0 | 3 | 100% | 0% | 0 | 0.021793 | 1 | 3.6566 | 0.079688 | Low | Low | High | 1936 | 2343 | 0.021793 | 51.09
GIRVAN 1101323094 | GIRVAN 1101 | NORTH VALLEY | 36.2683 | 55.5247 | 99.98% | 1 | 3 | 100% | 0% | 0 | 0.068706 | 1 | 1.1596 | 0.079672 | High | High | Low | 1937 | 1479 | 0.068706 | 51.0103
WOODSIDE 11049032 | WOODSIDE 1104 | PENINSULA | 2.5921 | 10 | 76.95% | 3 | 1 | 32.76% | 43.39% | 0 | 0.029563 | 1 | 2.6884 | 0.079475 | Medium | Medium | Medium | 1938 | 2109 | 0.029563 | 50.9307
TEMPLETON 2110R94 | TEMPLETON 2110 | LOS PADRES | 13.9551 | 53.972 | 81.64% | 0 | 3 | 66.74% | 0% | 0 | 0.037368 | 1 | 2.1258 | 0.079438 | Medium | Medium | Low | 1939 | 1908 | 0.037368 | 50.8512
CAYETANO 2109CB | CAYETANO 2109 | MISSION | 13.0515 | 49.7043 | 30.41% | 0 | 2 | 76.33% | 3.645% | 1 | 0.024131 | 1 | 3.2891 | 0.079369 | Medium | Medium | High | 1940 | 2275 | 0.024131 | 50.7718
BAY MEADOWS 210257886 | BAY MEADOWS 2102 | PENINSULA | 4.2245 | 10 | 28.89% | 2 | 6 | 80.67% | 0% | 0 | 0.026024 | 1 | 3.0461 | 0.079274 | Medium | Medium | Medium | 1941 | 2214 | 0.026024 | 50.6924
SAN LUIS OBISPO 1107V18 | SAN LUIS OBISPO 1107 | LOS PADRES | 3.3731 | 28.9632 | 4.194% | 1 | 0 | 84.27% | 30.63% | 0 | 0.035557 | 1 | 2.2292 | 0.079264 | Medium | Medium | Low | 1942 | 1944 | 0.035557 | 50.6131
MENLO 11038982 | MENLO 1103 | PENINSULA | 4.6231 | 36.5586 | 24.74% | 19 | 4 | 100% | 0% | 0 | 0.043182 | 1 | 1.8329 | 0.07915 | Medium | Medium | Low | 1943 | 1792 | 0.043182 | 50.5338
CLAYTON 22122944 | CLAYTON 2212 | DIABLO | 14.8336 | 10 | 45.06% | 1 | 4 | 97.25% | 6.81% | 1 | 0.024898 | 1 | 3.1713 | 0.078959 | Medium | Medium | High | 1944 | 2246 | 0.024898 | 50.4547
CLAY 11031230 | CLAY 1103 | STOCKTON | 15.7057 | 29.0509 | 99.85% | 0 | 2 | 80.49% | 0% | 0 | 0.031696 | 1 | 2.4895 | 0.078906 | Medium | Medium | Medium | 1945 | 2054 | 0.031696 | 50.3757
VIEJO 2201CB | VIEJO 2201 | CENTRAL COAST | 4.5324 | 10 | 12.86% | 16 | 6 | 89.76% | 0% | 0 | 0.020254 | 1 | 3.8798 | 0.078583 | Low | Low | High | 1946 | 2398 | 0.020254 | 50.2968
SMARTVILLE 1101CB | SMARTVILLE 1101 | SIERRA | 15.8868 | 12.1904 | 82.07% | 1 | 6 | 100% | 0% | 0 | 0.032648 | 1 | 2.4063 | 0.078562 | Medium | Medium | Medium | 1947 | 2020 | 0.032648 | 50.2182
OLEMA 1101602 | OLEMA 1101 | NORTH BAY | 15.0972 | 65.987 | 1.264% | 8 | 10 | 59.79% | 0% | 0 | 0.037469 | 1 | 2.0944 | 0.078477 | Medium | Medium | Low | 1948 | 1906 | 0.037469 | 50.1397
BIG RIVER 110169032 | BIG RIVER 1101 | HUMBOLDT | 8.4667 | 31.9768 | 17.96% | 7 | 9 | 100% | 0% | 0 | 0.033152 | 1 | 2.3622 | 0.07831 | Medium | Medium | Medium | 1949 | 2004 | 0.033152 | 50.0612
DUNBAR 1102CB | DUNBAR 1102 | SONOMA | 8.263 | 20.9256 | 44.14% | 4 | 14 | 47.06% | 0% | 0 | 0.024179 | 1 | 3.2378 | 0.078286 | Medium | Medium | High | 1950 | 2273 | 0.024179 | 49.9829
HOLLISTER 21054018 | HOLLISTER 2105 | CENTRAL COAST | 42.8602 | 78.3807 | 68.88% | 1 | 1 | 81.19% | 0% | 0 | 0.044317 | 1 | 1.765 | 0.078218 | Medium | Medium | Low | 1951 | 1771 | 0.044317 | 49.9046
IGNACIO 11011300 | IGNACIO 1101 | NORTH BAY | 2.4856 | 23.8629 | 75.16% | 0 | 4 | 40.74% | 21.73% | 0 | 0.025064 | 1 | 3.1191 | 0.078176 | Medium | Medium | High | 1952 | 2239 | 0.025064 | 49.8264
HOOPA 11013290 | HOOPA 1101 | HUMBOLDT | 13.744 | 63.8622 | 97.01% | 10 | 15 | 100% | 0% | 0 | 0.077955 | 1 | 1.0027 | 0.078163 | High | High | Low | 1953 | 1414 | 0.077955 | 49.7482
OAKLAND J 1102CR102 | OAKLAND J 1102 | EAST BAY | 0.53101 | 10 | 70.62% | 0 | 2 | 100% | 0% | 0 | 0.023454 | 1 | 3.3241 | 0.077962 | Medium | Medium | High | 1954 | 2295 | 0.023454 | 49.6701
DUNBAR 1102528 | DUNBAR 1102 | SONOMA | 3.4638 | 30.5853 | 54.13% | 1 | 3 | 85.5% | 0% | 0 | 0.021137 | 1 | 3.6876 | 0.077945 | Low | Low | High | 1955 | 2360 | 0.021137 | 49.5921
STILLWATER 110148950 | STILLWATER 1101 | NORTH VALLEY | 12.4263 | 10 | 99.94% | 1 | 4 | 100% | 0% | 0 | 0.046041 | 1 | 1.6867 | 0.077656 | Medium | Medium | Low | 1956 | 1743 | 0.046041 | 49.5142
CURTIS 170320240 | CURTIS 1703 | YOSEMITE | 0.18021 | 10 | 100% | 0 | 0 | 63.08% | 0% | 0 | 0.019869 | 1 | 3.9035 | 0.077558 | Low | Low | High | 1957 | 2415 | 0.019869 | 49.4365
OLETA 110241396 | OLETA 1102 | STOCKTON | 7.3755 | 10 | 56.8% | 3 | 3 | 100% | 0% | 0 | 0.025362 | 1 | 3.0576 | 0.077548 | Medium | Medium | Medium | 1958 | 2233 | 0.025362 | 49.3589
SILVERADO 2102714 | SILVERADO 2102 | NORTH BAY | 4.37 | 45.4785 | 19.37% | 4 | 5 | 38.82% | 6.698% | 0 | 0.022688 | 1 | 3.4176 | 0.077537 | Medium | Medium | High | 1959 | 2317 | 0.022688 | 49.2814
EMERALD LAKE 04028858 | EMERALD LAKE 0402 | PENINSULA | 1.9112 | 10 | 5.775% | 0 | 4 | 100% | 0% | 0 | 0.016487 | 1 | 4.6869 | 0.077272 | Low | Low | High | 1960 | 2553 | 0.016487 | 49.2039
CARLOTTA 11214914 | CARLOTTA 1121 | HUMBOLDT | 11.4615 | 25.5188 | 70.14% | 16 | 11 | 80.82% | 0% | 0 | 0.041044 | 1 | 1.8825 | 0.077265 | Medium | Medium | Low | 1961 | 1833 | 0.041044 | 49.1266
LUCERNE 11062327 | LUCERNE 1106 | HUMBOLDT | 0.98526 | 10 | 100% | 0 | 1 | 77.76% | 0% | 0 | 0.02342 | 1 | 3.2861 | 0.07696 | Medium | Medium | High | 1962 | 2300 | 0.02342 | 49.0493
CURTIS 1701CB | CURTIS 1701 | YOSEMITE | 8.5475 | 34.1417 | 57.96% | 1 | 9 | 68.5% | 0% | 0 | 0.024359 | 1 | 3.1577 | 0.076918 | Medium | Medium | High | 1963 | 2266 | 0.024359 | 48.9724
CLAY 11031821 | CLAY 1103 | STOCKTON | 2.0901 | 61.2881 | 100% | 0 | 0 | 55.49% | 0% | 0 | 0.029593 | 1 | 2.5933 | 0.076746 | Medium | Medium | Medium | 1964 | 2108 | 0.029593 | 48.8954
TIVY VALLEY 1107R1817 | TIVY VALLEY 1107 | FRESNO | 19.042 | 15.3654 | 99.23% | 0 | 5 | 99.01% | 0% | 0 | 0.041647 | 1 | 1.8427 | 0.076744 | Medium | Medium | Low | 1965 | 1825 | 0.041647 | 48.8187
RALSTON 11022028 | RALSTON 1102 | PENINSULA | 2.1344 | 10 | 38.62% | 0 | 5 | 92.94% | 0% | 0 | 0.020485 | 1 | 3.746 | 0.076737 | Low | Low | High | 1966 | 2387 | 0.020485 | 48.7419
BANGOR 110131502 | BANGOR 1101 | NORTH VALLEY | 11.8542 | 14.4917 | 60.88% | 1 | 3 | 100% | 0% | 0 | 0.026318 | 1 | 2.9147 | 0.076709 | Medium | Medium | Medium | 1967 | 2212 | 0.026318 | 48.6652
MOUNTAIN QUARRIES 210151584 | MOUNTAIN QUARRIES 2101 | SIERRA | 21.6351 | 34.2949 | 99.29% | 0 | 1 | 100% | 0% | 0 | 0.033987 | 1 | 2.2566 | 0.076695 | Medium | Medium | Medium | 1968 | 1977 | 0.033987 | 48.5885
HALF MOON BAY 11036065 | HALF MOON BAY 1103 | PENINSULA | 6.2488 | 59.5208 | 36.98% | 1 | 1 | 91.2% | 0% | 0 | 0.02267 | 1 | 3.3733 | 0.076472 | Medium | Medium | High | 1969 | 2318 | 0.02267 | 48.5118
RADUM 1105MR282 | RADUM 1105 | MISSION | 2.1702 | 17.1089 | 66.03% | 0 | 5 | 34.07% | 37.28% | 0 | 0.023926 | 1 | 3.184 | 0.076183 | Medium | Medium | High | 1970 | 2278 | 0.023926 | 48.4353
HIGGINS 1104CB | HIGGINS 1104 | SIERRA | 11.5789 | 10 | 38.55% | 1 | 4 | 99.62% | 0% | 0 | 0.024722 | 1 | 3.0793 | 0.076125 | Medium | Medium | High | 1971 | 2251 | 0.024722 | 48.3592
BIG RIVER 11011052 | BIG RIVER 1101 | HUMBOLDT | 2.9737 | 10 | 0% | 7 | 11 | 77.62% | 0% | 0 | 0.023654 | 1 | 3.2182 | 0.076123 | Medium | Medium | High | 1972 | 2291 | 0.023654 | 48.283
GARBERVILLE 11022010 | GARBERVILLE 1102 | HUMBOLDT | 6.6438 | 69.4132 | 9.089% | 2 | 3 | 100% | 0% | 0 | 0.042493 | 1 | 1.7903 | 0.076076 | Medium | Medium | Low | 1973 | 1806 | 0.042493 | 48.2069
SANTA YNEZ 1102Y18 | SANTA YNEZ 1102 | LOS PADRES | 4.6184 | 77.519 | 99.57% | 1 | 1 | 61.2% | 0% | 0 | 0.035874 | 1 | 2.1205 | 0.076069 | Medium | Medium | Low | 1974 | 1937 | 0.035874 | 48.1308
HIGGINS 1103995672 | HIGGINS 1103 | SIERRA | 2.7769 | 10 | 100% | 1 | 1 | 48.24% | 0% | 0 | 0.02307 | 1 | 3.2961 | 0.076042 | Medium | Medium | High | 1975 | 2307 | 0.02307 | 48.0548
CLAY 110334338 | CLAY 1103 | STOCKTON | 7.6368 | 36.5237 | 71.29% | 1 | 2 | 73.13% | 0% | 0 | 0.028445 | 1 | 2.6701 | 0.075951 | Medium | Medium | Medium | 1976 | 2156 | 0.028445 | 47.9787
HAMILTON BRANCH 11012082 | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.6281 | 32.2338 | 100% | 1 | 0 | 53.18% | 0% | 0 | 0.021199 | 1 | 3.5753 | 0.075794 | Low | Low | High | 1977 | 2358 | 0.021199 | 47.9028
WYANDOTTE 11071026 | WYANDOTTE 1107 | NORTH VALLEY | 21.2978 | 26.1479 | 94.57% | 0 | 2 | 76.21% | 0% | 0 | 0.032543 | 1 | 2.3229 | 0.075594 | Medium | Medium | Medium | 1978 | 2028 | 0.032543 | 47.827
VOLTA 110153118 | VOLTA 1101 | NORTH VALLEY | 9.6297 | 40.8133 | 100% | 0 | 1 | 100% | 0% | 0 | 0.05235 | 1 | 1.4426 | 0.075522 | Medium | Medium | Low | 1979 | 1657 | 0.05235 | 47.7514
SPRUCE 0402BR304 | SPRUCE 0402 | EAST BAY | 1.905 | 10 | 5.593% | 0 | 5 | 53.05% | 19.04% | 0 | 0.016372 | 1 | 4.6125 | 0.075515 | Low | Low | High | 1980 | 2556 | 0.016372 | 47.6759
WEIMAR 11026175 | WEIMAR 1102 | SIERRA | 2.7281 | 10 | 100% | 0 | 1 | 100% | 0% | 0 | 0.029099 | 1 | 2.5942 | 0.075486 | Medium | Medium | Medium | 1981 | 2119 | 0.029099 | 47.6003
APPLE HILL 210251792 | APPLE HILL 2102 | SIERRA | 9.3607 | 11.5456 | 100% | 6 | 2 | 100% | 0% | 0 | 0.04191 | 1 | 1.7949 | 0.075224 | Medium | Medium | Low | 1982 | 1819 | 0.04191 | 47.5249
CALPELLA 11013419 | CALPELLA 1101 | HUMBOLDT | 8.0753 | 59.7032 | 100% | 1 | 1 | 100% | 3.769% | 0 | 0.0493 | 1 | 1.5255 | 0.075207 | Medium | Medium | Low | 1983 | 1692 | 0.0493 | 47.4496
HATTON 1101CB | HATTON 1101 | CENTRAL COAST | 1.5925 | 10 | 10.22% | 4 | 0 | 100% | 0% | 0 | 0.024551 | 1 | 3.0516 | 0.074918 | Medium | Medium | Medium | 1984 | 2260 | 0.024551 | 47.3744
CLARK ROAD 11022070 | CLARK ROAD 1102 | NORTH VALLEY | 9.7077 | 20.9726 | 72.7% | 1 | 4 | 86.39% | 12.56% | 0 | 0.028935 | 1 | 2.5885 | 0.0749 | Medium | Medium | Medium | 1985 | 2127 | 0.028935 | 47.2995
PIERCY 2110XR258 | PIERCY 2110 | SAN JOSE | 14.4387 | 60.8378 | 97.27% | 4 | 1 | 54.5% | 0% | 0 | 0.026979 | 1 | 2.7761 | 0.074895 | Medium | Medium | Medium | 1986 | 2193 | 0.026979 | 47.2246
HIGHLANDS 1104CB | HIGHLANDS 1104 | HUMBOLDT | 4.6735 | 10 | 74.7% | 0 | 2 | 57.1% | 0% | 0 | 0.023554 | 1 | 3.1769 | 0.074829 | Medium | Medium | High | 1987 | 2294 | 0.023554 | 47.1497
OREGON TRAIL 1104 | OREGON TRAIL 1104 | NORTH VALLEY | 0.063815 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.6217 | 0.074749 | Medium | Medium | Medium | 1988 | 2154 | 0.028512 | 47.0749
DESCHUTES 11011380 | DESCHUTES 1101 | NORTH VALLEY | 17.936 | 29.5967 | 86.99% | 0 | 4 | 75.95% | 0% | 0 | 0.032554 | 1 | 2.2953 | 0.07472 | Medium | Medium | Medium | 1989 | 2027 | 0.032554 | 47.0001
PERRY 1101CB | PERRY 1101 | LOS PADRES | 2.5037 | 27.4854 | 19.25% | 0 | 1 | 100% | 0% | 0 | 0.025246 | 1 | 2.9519 | 0.074522 | Medium | Medium | Medium | 1990 | 2235 | 0.025246 | 46.9254
CLEAR LAKE 11011302 | CLEAR LAKE 1101 | HUMBOLDT | 6.3736 | 19.3133 | 67.28% | 0 | 7 | 36.56% | 0% | 0 | 0.024377 | 1 | 3.0552 | 0.074476 | Medium | Medium | Medium | 1991 | 2265 | 0.024377 | 46.8509
VIEJO 22029120 | VIEJO 2202 | CENTRAL COAST | 1.9636 | 10 | 20.08% | 9 | 3 | 26.52% | 0% | 0 | 0.019059 | 1 | 3.9065 | 0.074456 | Low | Low | High | 1992 | 2444 | 0.019059 | 46.7764
SAN CARLOS 11039148 | SAN CARLOS 1103 | PENINSULA | 3.9693 | 10 | 27.37% | 0 | 9 | 43.54% | 0% | 0 | 0.016236 | 1 | 4.5802 | 0.074366 | Low | Low | High | 1993 | 2563 | 0.016236 | 46.702
GUALALA 1111887180 | GUALALA 1111 | HUMBOLDT | 5.4716 | 10 | 0.3119% | 7 | 8 | 100% | 0% | 0 | 0.027751 | 1 | 2.6787 | 0.074336 | Medium | Medium | Medium | 1994 | 2169 | 0.027751 | 46.6276
CLOVERDALE 1101112 | CLOVERDALE 1101 | SONOMA | 19.0544 | 64.0868 | 84.08% | 2 | 8 | 69.85% | 0% | 0 | 0.036824 | 1 | 2.0172 | 0.074281 | Medium | Medium | Low | 1995 | 1921 | 0.036824 | 46.5533
ALLEGHANY 1101978 | ALLEGHANY 1101 | SIERRA | 13.0219 | 53.8471 | 100% | 3 | 4 | 44.63% | 0% | 0 | 0.037002 | 1 | 2.0065 | 0.074244 | Medium | Medium | Low | 1996 | 1917 | 0.037002 | 46.479
OILFIELDS 11035175 | OILFIELDS 1103 | CENTRAL COAST | 1.9738 | 10 | 100% | 0 | 3 | 89.15% | 0% | 0 | 0.027271 | 1 | 2.7162 | 0.074075 | Medium | Medium | Medium | 1997 | 2187 | 0.027271 | 46.4047
BROWNS VALLEY 110117011 | BROWNS VALLEY 1101 | SIERRA | 1.8676 | 10 | 100% | 0 | 2 | 100% | 0% | 0 | 0.029697 | 1 | 2.4913 | 0.073986 | Medium | Medium | Medium | 1998 | 2106 | 0.029697 | 46.3307
FRENCH GULCH 11021462 | FRENCH GULCH 1102 | NORTH VALLEY | 13.6588 | 44.7353 | 99.62% | 1 | 1 | 99.24% | 22.55% | 0 | 0.052153 | 1 | 1.4168 | 0.073891 | Medium | Medium | Low | 1999 | 1659 | 0.052153 | 46.2567
MARIPOSA 21018030 | MARIPOSA 2101 | YOSEMITE | 18.88 | 28.5381 | 67.58% | 1 | 11 | 100% | 1.019% | 0 | 0.032029 | 1 | 2.3021 | 0.073734 | Medium | Medium | Medium | 2000 | 2046 | 0.032029 | 46.1828
APPLE HILL 21021532 | APPLE HILL 2102 | SIERRA | 38.7437 | 26.3677 | 83.01% | 8 | 10 | 92.13% | 0.1028% | 0 | 0.045174 | 1 | 1.6238 | 0.073353 | Medium | Medium | Low | 2001 | 1761 | 0.045174 | 46.109
FORT SEWARD 1121CB | FORT SEWARD 1121 | HUMBOLDT | 7.2358 | 72.7632 | 100% | 3 | 3 | 100% | 0% | 0 | 0.047585 | 1 | 1.5395 | 0.073259 | Medium | Medium | Low | 2002 | 1715 | 0.047585 | 46.0357
HALF MOON BAY 110375550 | HALF MOON BAY 1103 | PENINSULA | 1.1869 | 54.8487 | 75.08% | 0 | 0 | 53.23% | 0% | 0 | 0.019917 | 1 | 3.6734 | 0.073163 | Low | Low | High | 2003 | 2411 | 0.019917 | 45.9624
BANGOR 110180670 | BANGOR 1101 | NORTH VALLEY | 14.7472 | 18.2405 | 76% | 0 | 1 | 89.02% | 0% | 0 | 0.02277 | 1 | 3.21 | 0.073094 | Medium | Medium | High | 2004 | 2313 | 0.02277 | 45.8893
ELK CREEK 110137334 | ELK CREEK 1101 | NORTH VALLEY | 9.7022 | 59.8583 | 100% | 0 | 0 | 100% | 0% | 0 | 0.065795 | 1 | 1.1103 | 0.073051 | High | High | Low | 2005 | 1509 | 0.065795 | 45.8162
SWIFT 2107XR526 | SWIFT 2107 | SAN JOSE | 2.6821 | 10 | 42.91% | 0 | 1 | 49.21% | 0% | 0 | 0.016512 | 1 | 4.4175 | 0.072944 | Low | Low | High | 2006 | 2550 | 0.016512 | 45.7431
KERCKHOFF 1101CB | KERCKHOFF 1101 | YOSEMITE | 16.9469 | 19.3199 | 39.66% | 0 | 15 | 100% | 0% | 0 | 0.032903 | 1 | 2.2156 | 0.072899 | Medium | Medium | Low | 2007 | 2015 | 0.032903 | 45.6702
STILLWATER 11021466 | STILLWATER 1102 | NORTH VALLEY | 19.2831 | 16.0387 | 100% | 1 | 10 | 94.09% | 0% | 0 | 0.051049 | 1 | 1.4241 | 0.0727 | Medium | Medium | Low | 2008 | 1672 | 0.051049 | 45.5973
POSO MOUNTAIN 2101CB | POSO MOUNTAIN 2101 | KERN | 4.3131 | 10 | 10.82% | 0 | 0 | 100% | 0% | 0 | 0.026686 | 1 | 2.722 | 0.072639 | Medium | Medium | Medium | 2009 | 2198 | 0.026686 | 45.5246
CABRILLO 110420711 | CABRILLO 1104 | LOS PADRES | 0.18254 | 10 | 100% | 0 | 0 | 58.32% | 0% | 0 | 0.01896 | 1 | 3.8254 | 0.072532 | Low | Low | High | 2010 | 2449 | 0.01896 | 45.4519
NORTH DUBLIN 2101CB | NORTH DUBLIN 2101 | MISSION | 3.6193 | 54.6377 | 4.667% | 0 | 3 | 91.94% | 0% | 0 | 0.019955 | 1 | 3.6341 | 0.072519 | Low | Low | High | 2011 | 2410 | 0.019955 | 45.3794
STILLWATER 1101CB | STILLWATER 1101 | NORTH VALLEY | 3.671 | 10 | 87.48% | 3 | 2 | 85.62% | 0% | 0 | 0.027635 | 1 | 2.6197 | 0.072394 | Medium | Medium | Medium | 2012 | 2173 | 0.027635 | 45.3069
OILFIELDS 11032757 | OILFIELDS 1103 | CENTRAL COAST | 2.6282 | 37.5918 | 90.66% | 0 | 3 | 100% | 0% | 0 | 0.033768 | 1 | 2.1416 | 0.072319 | Medium | Medium | Low | 2013 | 1984 | 0.033768 | 45.2345
CEDAR CREEK 1101CB | CEDAR CREEK 1101 | NORTH VALLEY | 15.4651 | 37.802 | 95.68% | 0 | 0 | 100% | 38.1% | 1 | 0.067896 | 1 | 1.0626 | 0.072148 | High | High | Low | 2014 | 1487 | 0.067896 | 45.1622
LOW GAP 110137498 | LOW GAP 1101 | HUMBOLDT | 16.1307 | 72.1022 | 98.67% | 6 | 3 | 100% | 0% | 0 | 0.062673 | 1 | 1.1505 | 0.072104 | High | High | Low | 2015 | 1535 | 0.062673 | 45.09
DUNLAP 11037040 | DUNLAP 1103 | FRESNO | 24.7254 | 12.3243 | 100% | 0 | 2 | 100% | 0% | 0 | 0.039034 | 1 | 1.8465 | 0.072078 | Medium | Medium | Low | 2016 | 1881 | 0.039034 | 45.0179
PETALUMA C 110948000 | PETALUMA C 1109 | SONOMA | 8.7103 | 40.2232 | 37.55% | 1 | 9 | 65.59% | 0% | 0 | 0.023831 | 1 | 3.0235 | 0.072053 | Medium | Medium | Medium | 2017 | 2284 | 0.023831 | 44.9458
HAMILTON BRANCH 110118205 | HAMILTON BRANCH 1101 | NORTH VALLEY | 4.0384 | 59.6103 | 100% | 0 | 1 | 100% | 0% | 0 | 0.040382 | 1 | 1.7837 | 0.072028 | Medium | Medium | Low | 2018 | 1844 | 0.040382 | 44.8738
HORSESHOE 110150140 | HORSESHOE 1101 | SIERRA | 3.7526 | 10 | 69.76% | 1 | 4 | 60.16% | 0% | 0 | 0.018953 | 1 | 3.7991 | 0.072006 | Low | Low | High | 2019 | 2450 | 0.018953 | 44.8018
ZACA 1102Y02 | ZACA 1102 | LOS PADRES | 10.6195 | 15.4408 | 92.94% | 0 | 5 | 80.71% | 0% | 0 | 0.042959 | 1 | 1.6742 | 0.071921 | Medium | Medium | Low | 2020 | 1800 | 0.042959 | 44.7298
PINE GROVE 110194936 | PINE GROVE 1101 | STOCKTON | 9.27 | 10 | 75.09% | 1 | 1 | 100% | 0% | 0 | 0.027484 | 1 | 2.6139 | 0.071841 | Medium | Medium | Medium | 2021 | 2177 | 0.027484 | 44.6578
HALSEY 1102CB | HALSEY 1102 | SIERRA | 8.0128 | 10 | 41.48% | 9 | 5 | 100% | 0% | 0 | 0.032715 | 1 | 2.1959 | 0.071838 | Medium | Medium | Low | 2022 | 2019 | 0.032715 | 44.586
TIVY VALLEY 11077380 | TIVY VALLEY 1107 | FRESNO | 12.8078 | 20.0234 | 100% | 1 | 4 | 45.52% | 0% | 0 | 0.033102 | 1 | 2.1686 | 0.071783 | Medium | Medium | Low | 2023 | 2007 | 0.033102 | 44.5142
SAND CREEK 1103CB | SAND CREEK 1103 | FRESNO | 12.8175 | 20.9724 | 70.85% | 0 | 3 | 100% | 0% | 0 | 0.033442 | 1 | 2.1429 | 0.071662 | Medium | Medium | Low | 2024 | 1997 | 0.033442 | 44.4424
AUBERRY 110137536 | AUBERRY 1101 | FRESNO | 5.4818 | 31.3295 | 100% | 3 | 2 | 100% | 20.77% | 1 | 0.055781 | 1 | 1.2846 | 0.071654 | Medium | Medium | Low | 2025 | 1615 | 0.055781 | 44.3707
AUBERRY 1102R902 | AUBERRY 1102 | FRESNO | 15.0447 | 11.5312 | 82.04% | 0 | 7 | 100% | 0% | 0 | 0.037249 | 1 | 1.9232 | 0.071637 | Medium | Medium | Low | 2026 | 1912 | 0.037249 | 44.2991
OREGON TRAIL 1103CB | OREGON TRAIL 1103 | NORTH VALLEY | 2.7772 | 25.1322 | 81.43% | 2 | 1 | 95.03% | 0% | 0 | 0.030857 | 1 | 2.3184 | 0.071539 | Medium | Medium | Medium | 2027 | 2074 | 0.030857 | 44.2274
APPLE HILL 21026552 | APPLE HILL 2102 | SIERRA | 12.3732 | 14.1708 | 74.28% | 2 | 0 | 100% | 6.545% | 1 | 0.045443 | 1 | 1.5727 | 0.07147 | Medium | Medium | Low | 2028 | 1756 | 0.045443 | 44.1559
WOODSIDE 1104CB | WOODSIDE 1104 | PENINSULA | 0.34613 | 10 | 13.48% | 0 | 0 | 4.645% | 100% | 0 | 0.027423 | 1 | 2.6038 | 0.071405 | Medium | Medium | Medium | 2029 | 2179 | 0.027423 | 44.0844
FORT SEWARD 11211602 | FORT SEWARD 1121 | HUMBOLDT | 18.3365 | 83.3472 | 100% | 8 | 9 | 80.72% | 0% | 0 | 0.074162 | 1 | 0.96205 | 0.071347 | High | High | Low | 2030 | 1444 | 0.074162 | 44.013
COTTONWOOD 11021578 | COTTONWOOD 1102 | NORTH VALLEY | 28.4377 | 38.0859 | 100% | 1 | 7 | 81.08% | 0% | 0 | 0.049028 | 1 | 1.4522 | 0.0712 | Medium | Medium | Low | 2031 | 1695 | 0.049028 | 43.9417
SUMMIT 110148632 | SUMMIT 1101 | SIERRA | 2.7291 | 10 | 63.45% | 5 | 6 | 100% | 0% | 0 | 0.037786 | 1 | 1.8801 | 0.071043 | Medium | Medium | Low | 2032 | 1901 | 0.037786 | 43.8705
COARSEGOLD 21045516 | COARSEGOLD 2104 | YOSEMITE | 18.4464 | 11.3018 | 100% | 1 | 1 | 100% | 0% | 0 | 0.043744 | 1 | 1.6156 | 0.070674 | Medium | Medium | Low | 2033 | 1781 | 0.043744 | 43.7994
VIEJO 22019490 | VIEJO 2201 | CENTRAL COAST | 2.0007 | 10 | 0.3261% | 11 | 5 | 93.15% | 0% | 0 | 0.019802 | 1 | 3.5624 | 0.070542 | Low | Low | High | 2034 | 2420 | 0.019802 | 43.7287
BUCKS CREEK 1102CB | BUCKS CREEK 1102 | NORTH VALLEY | 29.5609 | 73.8859 | 50.06% | 3 | 10 | 100% | 23.04% | 0 | 0.077422 | 1 | 0.91112 | 0.07054 | High | High | Low | 2035 | 1418 | 0.077422 | 43.6582
FULTON 1102CB | FULTON 1102 | SONOMA | 1.3424 | 10 | 29.14% | 0 | 0 | 30.03% | 82.09% | 0 | 0.02998 | 1 | 2.351 | 0.070482 | Medium | Medium | Medium | 2036 | 2099 | 0.02998 | 43.5877
OREGON TRAIL 11021382 | OREGON TRAIL 1102 | NORTH VALLEY | 5.4732 | 13.8429 | 96.06% | 0 | 1 | 100% | 0% | 0 | 0.03292 | 1 | 2.141 | 0.070481 | Medium | Medium | Low | 2037 | 2012 | 0.03292 | 43.5172
ALTO 11251256 | ALTO 1125 | NORTH BAY | 1.3805 | 10 | 15.55% | 1 | 0 | 94.69% | 19.69% | 0 | 0.018993 | 1 | 3.7099 | 0.070461 | Low | Low | High | 2038 | 2447 | 0.018993 | 43.4467
CEDAR CREEK 11011656 | CEDAR CREEK 1101 | NORTH VALLEY | 32.2585 | 60.8127 | 100% | 10 | 9 | 100% | 0% | 0 | 0.10049 | 1 | 0.70111 | 0.070453 | High | High | Low | 2039 | 1294 | 0.10049 | 43.3762
LLAGAS 21011451 | LLAGAS 2101 | SAN JOSE | 5.288 | 70.7589 | 100% | 0 | 0 | 57.46% | 0% | 0 | 0.028219 | 1 | 2.4961 | 0.070438 | Medium | Medium | Medium | 2040 | 2159 | 0.028219 | 43.3058
AUBERRY 1102R309 | AUBERRY 1102 | FRESNO | 8.5895 | 21.9499 | 78.92% | 1 | 2 | 100% | 0% | 0 | 0.04051 | 1 | 1.7362 | 0.070333 | Medium | Medium | Low | 2041 | 1841 | 0.04051 | 43.2354
RIO DELL 110275970 | RIO DELL 1102 | HUMBOLDT | 7.0738 | 89.4562 | 39.39% | 2 | 2 | 100% | 0% | 0 | 0.05303 | 1 | 1.3258 | 0.07031 | Medium | Medium | Low | 2042 | 1648 | 0.05303 | 43.165
BEAR VALLEY 21014160 | BEAR VALLEY 2101 | YOSEMITE | 22.75 | 19.66 | 91.43% | 0 | 7 | 99.99% | 0% | 0 | 0.032723 | 1 | 2.1443 | 0.070169 | Medium | Medium | Low | 2043 | 2018 | 0.032723 | 43.0947
VIEJO 22019698 | VIEJO 2201 | CENTRAL COAST | 0.90136 | 10 | 0% | 2 | 3 | 100% | 0% | 0 | 0.018036 | 1 | 3.8848 | 0.070067 | Low | Low | High | 2044 | 2486 | 0.018036 | 43.0245
TYLER 11051536 | TYLER 1105 | NORTH VALLEY | 17.0203 | 70.2834 | 100% | 0 | 5 | 94.18% | 0% | 0 | 0.044384 | 1 | 1.5772 | 0.070005 | Medium | Medium | Low | 2045 | 1770 | 0.044384 | 42.9545
COLUMBIA HILL 110190730 | COLUMBIA HILL 1101 | SIERRA | 8.3212 | 17.8031 | 100% | 1 | 4 | 100% | 5.083% | 1 | 0.040638 | 1 | 1.7208 | 0.069929 | Medium | Medium | Low | 2046 | 1838 | 0.040638 | 42.8845
HARTLEY 11011306 | HARTLEY 1101 | HUMBOLDT | 8.9139 | 32.0441 | 81.66% | 1 | 4 | 70.23% | 0% | 0 | 0.026684 | 1 | 2.6078 | 0.069587 | Medium | Medium | Medium | 2047 | 2199 | 0.026684 | 42.8145
UKIAH 11151216 | UKIAH 1115 | HUMBOLDT | 13.2203 | 25.9617 | 80.05% | 1 | 10 | 70.13% | 0% | 0 | 0.028563 | 1 | 2.4347 | 0.069541 | Medium | Medium | Medium | 2048 | 2131 | 0.028563 | 42.745
LAYTONVILLE 1101402 | LAYTONVILLE 1101 | HUMBOLDT | 22.8392 | 79.1892 | 99.99% | 6 | 8 | 96.88% | 0% | 0 | 0.070954 | 1 | 0.97747 | 0.069355 | High | High | Low | 2049 | 1466 | 0.070954 | 42.6754
WILDWOOD 11011576 | WILDWOOD 1101 | NORTH VALLEY | 8.159 | 75.9447 | 99.97% | 1 | 4 | 100% | 0% | 0 | 0.070451 | 1 | 0.98125 | 0.06913 | High | High | Low | 2050 | 1469 | 0.070451 | 42.6061
BIG RIVER 11011286 | BIG RIVER 1101 | HUMBOLDT | 4.4303 | 10 | 38.59% | 7 | 9 | 58.78% | 0% | 0 | 0.025767 | 1 | 2.6794 | 0.06904 | Medium | Medium | Medium | 2051 | 2222 | 0.025767 | 42.5369
DESCHUTES 11049718 | DESCHUTES 1104 | NORTH VALLEY | 6.0769 | 37.0786 | 75.84% | 1 | 1 | 34.09% | 0% | 0 | 0.025713 | 1 | 2.6812 | 0.068942 | Medium | Medium | Medium | 2052 | 2224 | 0.025713 | 42.4679
ATASCADERO 1103A14 | ATASCADERO 1103 | LOS PADRES | 25.1166 | 61.0387 | 72.56% | 0 | 2 | 99.83% | 36.1% | 0 | 0.058565 | 1 | 1.1767 | 0.068916 | Medium | Medium | Low | 2053 | 1586 | 0.058565 | 42.3989
PERRY 1101W12 | PERRY 1101 | LOS PADRES | 4.7971 | 10 | 2.793% | 5 | 9 | 75.15% | 0% | 0 | 0.01938 | 1 | 3.5539 | 0.068874 | Low | Low | High | 2054 | 2426 | 0.01938 | 42.33
SOLEDAD 210242506 | SOLEDAD 2102 | CENTRAL COAST | 5.4144 | 74.2068 | 100% | 0 | 1 | 19.16% | 0% | 0 | 0.029952 | 1 | 2.2961 | 0.068774 | Medium | Medium | Medium | 2055 | 2101 | 0.029952 | 42.2612
HOLLISTER 21054048 | HOLLISTER 2105 | CENTRAL COAST | 15.0102 | 85.5727 | 83.97% | 1 | 0 | 53.3% | 0% | 0 | 0.034508 | 1 | 1.9904 | 0.068686 | Medium | Medium | Low | 2056 | 1962 | 0.034508 | 42.1924
ATASCADERO 1103A16 | ATASCADERO 1103 | LOS PADRES | 18.5162 | 60.2309 | 48.27% | 0 | 1 | 91.95% | 38.05% | 0 | 0.045156 | 1 | 1.5184 | 0.068565 | Medium | Medium | Low | 2057 | 1762 | 0.045156 | 42.1237
BELL 11085703 | BELL 1108 | SIERRA | 4.5516 | 23.9501 | 96.07% | 0 | 3 | 57.44% | 0% | 0 | 0.024235 | 1 | 2.8219 | 0.068387 | Medium | Medium | Medium | 2058 | 2270 | 0.024235 | 42.0551
WYANDOTTE 11101954 | WYANDOTTE 1110 | NORTH VALLEY | 13.197 | 10 | 59.13% | 1 | 2 | 48.67% | 0% | 0 | 0.019374 | 1 | 3.5192 | 0.068181 | Low | Low | High | 2059 | 2427 | 0.019374 | 41.9867
OLETA 11014768 | OLETA 1101 | STOCKTON | 12.2184 | 44.115 | 100% | 0 | 5 | 89.74% | 0% | 0 | 0.040719 | 1 | 1.6733 | 0.068136 | Medium | Medium | Low | 2060 | 1837 | 0.040719 | 41.9186
ORINDA 04013442 | ORINDA 0401 | DIABLO | 4.9574 | 14.2459 | 5.153% | 4 | 12 | 73.89% | 0% | 0 | 0.021076 | 1 | 3.2283 | 0.068041 | Low | Low | High | 2061 | 2364 | 0.021076 | 41.8504
GARBERVILLE 11011514 | GARBERVILLE 1101 | HUMBOLDT | 14.7707 | 71.7705 | 51.17% | 15 | 7 | 100% | 0% | 0 | 0.10959 | 1 | 0.62013 | 0.067963 | High | High | Low | 2062 | 1261 | 0.10959 | 41.7824
PENRYN 1107346 | PENRYN 1107 | SIERRA | 12.7652 | 20.7142 | 69.91% | 3 | 7 | 51.25% | 0% | 0 | 0.026474 | 1 | 2.5635 | 0.067868 | Medium | Medium | Medium | 2063 | 2204 | 0.026474 | 41.7144
LAURELES 1111CB | LAURELES 1111 | CENTRAL COAST | 7.0885 | 26.8874 | 36.65% | 2 | 3 | 86.44% | 0% | 0 | 0.023775 | 1 | 2.8474 | 0.067697 | Medium | Medium | Medium | 2064 | 2285 | 0.023775 | 41.6466
MOUNTAIN QUARRIES 21012422 | MOUNTAIN QUARRIES 2101 | SIERRA | 8.6685 | 16.1435 | 71.9% | 2 | 3 | 100% | 0% | 0 | 0.029445 | 1 | 2.2909 | 0.067454 | Medium | Medium | Medium | 2065 | 2114 | 0.029445 | 41.5789
STILLWATER 110248952 | STILLWATER 1102 | NORTH VALLEY | 10.5922 | 15.961 | 100% | 1 | 3 | 100% | 0% | 0 | 0.041312 | 1 | 1.6325 | 0.067444 | Medium | Medium | Low | 2066 | 1828 | 0.041312 | 41.5114
PEORIA 170570198 | PEORIA 1705 | YOSEMITE | 1.5831 | 45.3965 | 98.01% | 1 | 0 | 49.77% | 0% | 0 | 0.025104 | 1 | 2.6852 | 0.067408 | Medium | Medium | Medium | 2067 | 2238 | 0.025104 | 41.444
BEAR VALLEY 210521160 | BEAR VALLEY 2105 | YOSEMITE | 23.7351 | 48.0267 | 99.88% | 2 | 5 | 100% | 3.193% | 0 | 0.043692 | 1 | 1.5413 | 0.067341 | Medium | Medium | Low | 2068 | 1784 | 0.043692 | 41.3766
KERCKHOFF 1101R353 | KERCKHOFF 1101 | YOSEMITE | 13.7831 | 33.1172 | 88.25% | 0 | 1 | 100% | 0% | 0 | 0.039955 | 1 | 1.6842 | 0.067293 | Medium | Medium | Low | 2069 | 1856 | 0.039955 | 41.3092
FITCH MOUNTAIN 111324550 | FITCH MOUNTAIN 1113 | SONOMA | 9.0741 | 56.5036 | 70.47% | 3 | 1 | 41.6% | 1.605% | 0 | 0.024475 | 1 | 2.7468 | 0.067228 | Medium | Medium | Medium | 2070 | 2262 | 0.024475 | 41.2419
CLARKSVILLE 2109CB | CLARKSVILLE 2109 | SIERRA | 1.031 | 10 | 7.581% | 0 | 1 | 91.6% | 7.913% | 0 | 0.018738 | 1 | 3.5876 | 0.067224 | Low | Low | High | 2071 | 2461 | 0.018738 | 41.1747
SAN CARLOS 11048942 | SAN CARLOS 1104 | PENINSULA | 1.591 | 10 | 52.6% | 0 | 5 | 59.7% | 0% | 0 | 0.016545 | 1 | 4.0626 | 0.067215 | Low | Low | High | 2072 | 2547 | 0.016545 | 41.1075
WEIMAR 1102CB | WEIMAR 1102 | SIERRA | 12.1704 | 10.9563 | 65.6% | 3 | 8 | 100% | 0% | 0 | 0.030334 | 1 | 2.2122 | 0.067104 | Medium | Medium | Low | 2073 | 2082 | 0.030334 | 41.0403
JESSUP 11012839 | JESSUP 1101 | NORTH VALLEY | 1.47 | 10 | 100% | 0 | 3 | 100% | 0% | 0 | 0.030308 | 1 | 2.2134 | 0.067083 | Medium | Medium | Low | 2074 | 2084 | 0.030308 | 40.9731
EDES 1112CR308 | EDES 1112 | EAST BAY | 3.5907 | 10 | 15.92% | 2 | 4 | 100% | 0% | 0 | 0.020943 | 1 | 3.1965 | 0.066942 | Low | Low | High | 2075 | 2369 | 0.020943 | 40.9061
CLARK ROAD 110292622 | CLARK ROAD 1102 | NORTH VALLEY | 30.8948 | 14.2994 | 87.09% | 2 | 9 | 100% | 0% | 0 | 0.032599 | 1 | 2.0512 | 0.066867 | Medium | Medium | Low | 2076 | 2024 | 0.032599 | 40.8391
CLAYTON 2215W531R | CLAYTON 2215 | DIABLO | 5.8394 | 49.6313 | 12.81% | 0 | 3 | 54.09% | 19.44% | 0 | 0.019385 | 1 | 3.4465 | 0.06681 | Low | Low | High | 2077 | 2425 | 0.019385 | 40.7723
HATTON 11012026 | HATTON 1101 | CENTRAL COAST | 6.3396 | 38.9334 | 46.88% | 0 | 2 | 62.03% | 0% | 0 | 0.021035 | 1 | 3.1737 | 0.06676 | Low | Low | High | 2078 | 2367 | 0.021035 | 40.7054
PAUL SWEET 210612828 | PAUL SWEET 2106 | CENTRAL COAST | 1.7112 | 10 | 38.85% | 0 | 0 | 34.49% | 21.63% | 0 | 0.014721 | 1 | 4.5319 | 0.066716 | Low | Low | High | 2079 | 2624 | 0.014721 | 40.6387
LAYTONVILLE 110237586 | LAYTONVILLE 1102 | HUMBOLDT | 13.9719 | 83.5514 | 97.33% | 7 | 7 | 100% | 0% | 0 | 0.064508 | 1 | 1.0342 | 0.066716 | High | High | Low | 2080 | 1520 | 0.064508 | 40.572
ELECTRA 1101L3849 | ELECTRA 1101 | STOCKTON | 5.7652 | 16.1295 | 95.19% | 1 | 1 | 100% | 0% | 0 | 0.033619 | 1 | 1.9842 | 0.066706 | Medium | Medium | Low | 2081 | 1990 | 0.033619 | 40.5053
GUALALA 1112662 | GUALALA 1112 | HUMBOLDT | 8.3014 | 33.9068 | 0.6489% | 13 | 22 | 98.43% | 0% | 0 | 0.031273 | 1 | 2.1271 | 0.06652 | Medium | Medium | Low | 2082 | 2067 | 0.031273 | 40.4385
SUNOL 1101MR650 | SUNOL 1101 | MISSION | 1.0325 | 10 | 30.92% | 0 | 2 | 64.08% | 55.43% | 0 | 0.028936 | 1 | 2.294 | 0.066379 | Medium | Medium | Medium | 2083 | 2126 | 0.028936 | 40.372
WYANDOTTE 1110 | WYANDOTTE 1110 | NORTH VALLEY | 0.049002 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.324 | 0.066261 | Medium | Medium | Medium | 2084 | 2136 | 0.028512 | 40.3056
FOOTHILL 110299432 | FOOTHILL 1102 | LOS PADRES | 0.73004 | 62.5798 | 100% | 0 | 3 | 16.66% | 0% | 0 | 0.021721 | 1 | 3.048 | 0.066206 | Low | Low | Medium | 2085 | 2345 | 0.021721 | 40.2394
VOLTA 1101CB | VOLTA 1101 | NORTH VALLEY | 9.2068 | 22.5796 | 72.56% | 6 | 5 | 100% | 27.96% | 0 | 0.059425 | 1 | 1.1139 | 0.066194 | Medium | Medium | Low | 2086 | 1573 | 0.059425 | 40.1732
SAN LUIS OBISPO 1104V14 | SAN LUIS OBISPO 1104 | LOS PADRES | 9.0673 | 22.9917 | 13.75% | 0 | 2 | 100% | 0% | 0 | 0.023923 | 1 | 2.7612 | 0.066057 | Medium | Medium | Medium | 2087 | 2279 | 0.023923 | 40.107
LUCERNE 1106526 | LUCERNE 1106 | HUMBOLDT | 9.9941 | 16.6965 | 53.92% | 1 | 9 | 92.11% | 0% | 0 | 0.026433 | 1 | 2.4967 | 0.065996 | Medium | Medium | Medium | 2088 | 2206 | 0.026433 | 40.0409
SAN LUIS OBISPO 1102597518 | SAN LUIS OBISPO 1102 | LOS PADRES | 0.61698 | 17.5901 | 98.92% | 0 | 1 | 28.41% | 0% | 0 | 0.015039 | 1 | 4.3749 | 0.065794 | Low | Low | High | 2089 | 2607 | 0.015039 | 39.9749
WILDWOOD 110185112 | WILDWOOD 1101 | NORTH VALLEY | 6.7175 | 80.7667 | 100% | 4 | 6 | 100% | 0% | 0 | 0.061113 | 1 | 1.0754 | 0.065723 | Medium | Medium | Low | 2090 | 1555 | 0.061113 | 39.9091
STAFFORD 11021019 | STAFFORD 1102 | NORTH BAY | 0.54264 | 10 | 100% | 0 | 0 | 74.36% | 0% | 0 | 0.022194 | 1 | 2.9612 | 0.065721 | Medium | Medium | Medium | 2091 | 2325 | 0.022194 | 39.8434
RED BLUFF 110585632 | RED BLUFF 1105 | NORTH VALLEY | 13.6331 | 10 | 81.59% | 1 | 4 | 91.86% | 0% | 0 | 0.032365 | 1 | 2.0302 | 0.065709 | Medium | Medium | Low | 2092 | 2032 | 0.032365 | 39.7777
AUBERRY 1101R2839 | AUBERRY 1101 | FRESNO | 12.6224 | 16.271 | 63.89% | 0 | 4 | 100% | 0% | 0 | 0.035608 | 1 | 1.8413 | 0.065564 | Medium | Medium | Low | 2093 | 1943 | 0.035608 | 39.712
CAMP EVERS 210392582 | CAMP EVERS 2103 | CENTRAL COAST | 0.22538 | 10 | 0% | 0 | 0 | 8.037% | 100% | 0 | 0.025436 | 1 | 2.5772 | 0.065553 | Medium | Medium | Medium | 2094 | 2231 | 0.025436 | 39.6464
HIGHLANDS 110275140 | HIGHLANDS 1102 | HUMBOLDT | 8.7915 | 33.3312 | 88.94% | 0 | 4 | 43.92% | 0% | 0 | 0.019109 | 1 | 3.4168 | 0.065291 | Low | Low | High | 2095 | 2438 | 0.019109 | 39.5809
DIAMOND SPRINGS 110656026 | DIAMOND SPRINGS 1106 | SIERRA | 15.0808 | 21.2538 | 81.61% | 2 | 7 | 100% | 0% | 0 | 0.031374 | 1 | 2.0796 | 0.065246 | Medium | Medium | Low | 2096 | 2064 | 0.031374 | 39.5156
INDIAN FLAT 110410270 | INDIAN FLAT 1104 | YOSEMITE | 3.8012 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.047687 | 1 | 1.3662 | 0.065148 | Medium | Medium | Low | 2097 | 1710 | 0.047687 | 39.4503
POTTER VALLEY P H 110576498 | POTTER VALLEY P H 1105 | HUMBOLDT | 14.8769 | 81.1366 | 60.61% | 2 | 8 | 100% | 0% | 0 | 0.058866 | 1 | 1.1067 | 0.065148 | Medium | Medium | Low | 2098 | 1582 | 0.058866 | 39.3852
HAMILTON BRANCH 1101CB | HAMILTON BRANCH 1101 | NORTH VALLEY | 4.2457 | 27.0953 | 61.17% | 1 | 2 | 74.22% | 0% | 0 | 0.019168 | 1 | 3.3969 | 0.065111 | Low | Low | High | 2099 | 2437 | 0.019168 | 39.32
BEAR VALLEY 210576694 | BEAR VALLEY 2105 | YOSEMITE | 4.546 | 19.6129 | 100% | 0 | 0 | 100% | 0% | 0 | 0.030391 | 1 | 2.1365 | 0.064928 | Medium | Medium | Low | 2100 | 2081 | 0.030391 | 39.2549
PEORIA 1704877670 | PEORIA 1704 | YOSEMITE | 6.3096 | 69.9259 | 47.8% | 1 | 5 | 95.84% | 0% | 0 | 0.030095 | 1 | 2.1572 | 0.064921 | Medium | Medium | Low | 2101 | 2096 | 0.030095 | 39.19
COARSEGOLD 21046210 | COARSEGOLD 2104 | YOSEMITE | 10.6712 | 44.0621 | 48.52% | 0 | 11 | 100% | 0% | 0 | 0.033703 | 1 | 1.9204 | 0.064723 | Medium | Medium | Low | 2102 | 1989 | 0.033703 | 39.1251
OAKLAND X 1104CB | OAKLAND X 1104 | EAST BAY | 1.3072 | 10 | 2.074% | 0 | 2 | 53.76% | 24.1% | 0 | 0.014319 | 1 | 4.5195 | 0.064715 | Low | Low | High | 2103 | 2639 | 0.014319 | 39.0604
CLOVERDALE 1102801904 | CLOVERDALE 1102 | SONOMA | 0.014995 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.2691 | 0.064697 | Medium | Medium | Medium | 2104 | 2136 | 0.028512 | 38.9956
BROWNS VALLEY 110197188 | BROWNS VALLEY 1101 | SIERRA | 6.5763 | 19.9978 | 93.03% | 2 | 3 | 95.83% | 0% | 0 | 0.03906 | 1 | 1.6554 | 0.064659 | Medium | Medium | Low | 2105 | 1880 | 0.03906 | 38.9309
SAND CREEK 11037070 | SAND CREEK 1103 | FRESNO | 17.8283 | 24.5064 | 100% | 1 | 3 | 100% | 0% | 0 | 0.049625 | 1 | 1.3027 | 0.064648 | Medium | Medium | Low | 2106 | 1687 | 0.049625 | 38.8663
PHILO 1102CB | PHILO 1102 | HUMBOLDT | 5.5805 | 58.9475 | 61.62% | 10 | 11 | 44.58% | 0% | 0 | 0.027409 | 1 | 2.3552 | 0.064554 | Medium | Medium | Medium | 2107 | 2180 | 0.027409 | 38.8016
GREEN VALLEY 210112106 | GREEN VALLEY 2101 | CENTRAL COAST | 6.3447 | 10 | 54.91% | 5 | 0 | 33.81% | 31.75% | 0 | 0.018337 | 1 | 3.5176 | 0.064501 | Low | Low | High | 2108 | 2473 | 0.018337 | 38.7371
STELLING 111060090 | STELLING 1110 | DE ANZA | 6.0088 | 10 | 51.27% | 4 | 1 | 91.55% | 0% | 0 | 0.019051 | 1 | 3.3845 | 0.064479 | Low | Low | High | 2109 | 2445 | 0.019051 | 38.6726
DESCHUTES 11011652 | DESCHUTES 1101 | NORTH VALLEY | 22.782 | 45.1857 | 96.26% | 0 | 4 | 93.2% | 0% | 0 | 0.035474 | 1 | 1.8172 | 0.064462 | Medium | Medium | Low | 2110 | 1946 | 0.035474 | 38.6081
JESSUP 11011496 | JESSUP 1101 | NORTH VALLEY | 14.7255 | 17.8878 | 100% | 1 | 3 | 90.72% | 1.915% | 1 | 0.030466 | 1 | 2.1149 | 0.064433 | Medium | Medium | Low | 2111 | 2078 | 0.030466 | 38.5436
SAN LEANDRO U 1114MR545 | SAN LEANDRO U 1114 | MISSION | 2.8053 | 10 | 16.34% | 0 | 2 | 62.83% | 0% | 0 | 0.01772 | 1 | 3.623 | 0.0642 | Low | Low | High | 2112 | 2501 | 0.01772 | 38.4792
COTTONWOOD 110168190 | COTTONWOOD 1101 | NORTH VALLEY | 22.7429 | 39.5713 | 100% | 3 | 4 | 90.15% | 0% | 0 | 0.045908 | 1 | 1.3967 | 0.064119 | Medium | Medium | Low | 2113 | 1746 | 0.045908 | 38.415
AUBERRY 1101R322 | AUBERRY 1101 | FRESNO | 7.483 | 34.3076 | 99.18% | 0 | 0 | 100% | 0% | 0 | 0.033278 | 1 | 1.9251 | 0.064062 | Medium | Medium | Low | 2114 | 2000 | 0.033278 | 38.3509
SAUSALITO 1102410 | SAUSALITO 1102 | NORTH BAY | 1.0698 | 10 | 84.58% | 1 | 1 | 48.49% | 0% | 0 | 0.017913 | 1 | 3.5643 | 0.063846 | Low | Low | High | 2115 | 2493 | 0.017913 | 38.2868
ROB ROY 210412596 | ROB ROY 2104 | CENTRAL COAST | 7.6393 | 10 | 59% | 3 | 3 | 72.22% | 0.5428% | 0 | 0.019837 | 1 | 3.2178 | 0.063833 | Low | Low | High | 2116 | 2418 | 0.019837 | 38.223
SAN RAFAEL 1105344 | SAN RAFAEL 1105 | NORTH BAY | 2.2778 | 10 | 70.24% | 0 | 2 | 30.4% | 0% | 0 | 0.015331 | 1 | 4.1625 | 0.063813 | Low | Low | High | 2117 | 2596 | 0.015331 | 38.1591
APPLE HILL 210212025 | APPLE HILL 2102 | SIERRA | 9.1227 | 10 | 100% | 3 | 0 | 100% | 0% | 0 | 0.033724 | 1 | 1.8915 | 0.063789 | Medium | Medium | Low | 2118 | 1985 | 0.033724 | 38.0953
CALPELLA 11011204 | CALPELLA 1101 | HUMBOLDT | 9.1784 | 21.5734 | 72.42% | 2 | 10 | 70.57% | 0% | 0 | 0.030223 | 1 | 2.1101 | 0.063774 | Medium | Medium | Low | 2119 | 2091 | 0.030223 | 38.0315
FORT SEWARD 1122CB | FORT SEWARD 1122 | HUMBOLDT | 17.3427 | 75.2963 | 100% | 3 | 11 | 79.07% | 0% | 0 | 0.067846 | 1 | 0.93948 | 0.06374 | High | High | Low | 2120 | 1488 | 0.067846 | 37.9678
CURTIS 1703CB | CURTIS 1703 | YOSEMITE | 8.4941 | 16.7987 | 53.44% | 0 | 2 | 77.88% | 0% | 0 | 0.0196 | 1 | 3.2518 | 0.063736 | Low | Low | High | 2121 | 2423 | 0.0196 | 37.904
SUNOL 1101MR387 | SUNOL 1101 | MISSION | 4.657 | 55.0854 | 92.88% | 0 | 1 | 93.35% | 0% | 0 | 0.03951 | 1 | 1.6108 | 0.063643 | Medium | Medium | Low | 2122 | 1872 | 0.03951 | 37.8403
SOBRANTE 1101L534R | SOBRANTE 1101 | DIABLO | 1.5331 | 10 | 22.75% | 1 | 1 | 80.03% | 7.584% | 0 | 0.016712 | 1 | 3.8056 | 0.0636 | Low | Low | High | 2123 | 2540 | 0.016712 | 37.7767
PHILO 11013700 | PHILO 1101 | HUMBOLDT | 18.1219 | 64.058 | 52.24% | 7 | 7 | 100% | 0% | 0 | 0.039935 | 1 | 1.5874 | 0.063395 | Medium | Medium | Low | 2124 | 1859 | 0.039935 | 37.7131
MENLO 11037902 | MENLO 1103 | PENINSULA | 11.6802 | 47.4802 | 20.98% | 8 | 4 | 71.01% | 0% | 0 | 0.022804 | 1 | 2.779 | 0.063373 | Medium | Medium | Medium | 2125 | 2311 | 0.022804 | 37.6497
OREGON TRAIL 11031448 | OREGON TRAIL 1103 | NORTH VALLEY | 30.932 | 14.1761 | 100% | 1 | 10 | 100% | 0% | 0 | 0.041357 | 1 | 1.5321 | 0.063365 | Medium | Medium | Low | 2126 | 1827 | 0.041357 | 37.5863
GOLDTREE 1108CB | GOLDTREE 1108 | LOS PADRES | 2.5563 | 36.4917 | 29.18% | 2 | 3 | 52.35% | 0% | 0 | 0.022193 | 1 | 2.85 | 0.063249 | Medium | Medium | Medium | 2127 | 2326 | 0.022193 | 37.5229
SAND CREEK 110397354 | SAND CREEK 1103 | FRESNO | 8.1104 | 10 | 100% | 0 | 1 | 80.11% | 0% | 0 | 0.035362 | 1 | 1.7829 | 0.063047 | Medium | Medium | Low | 2128 | 1950 | 0.035362 | 37.4597
CLARK ROAD 11022584 | CLARK ROAD 1102 | NORTH VALLEY | 7.9946 | 18.0642 | 99.96% | 1 | 2 | 85.31% | 0% | 0 | 0.0275 | 1 | 2.2918 | 0.063027 | Medium | Medium | Medium | 2129 | 2175 | 0.0275 | 37.3966
MONTICELLO 110193384 | MONTICELLO 1101 | NORTH BAY | 15.2847 | 55.7693 | 100% | 0 | 3 | 88.22% | 0% | 0 | 0.047273 | 1 | 1.3315 | 0.062941 | Medium | Medium | Low | 2130 | 1721 | 0.047273 | 37.3336
MOUNTAIN QUARRIES 210135466 | MOUNTAIN QUARRIES 2101 | SIERRA | 7.4036 | 10 | 90.3% | 2 | 0 | 100% | 0% | 0 | 0.030814 | 1 | 2.0397 | 0.062851 | Medium | Medium | Low | 2131 | 2075 | 0.030814 | 37.2707
CHOLAME 21025597 | CHOLAME 2102 | LOS PADRES | 5.1199 | 69.1665 | 100% | 0 | 2 | 100% | 0% | 0 | 0.049821 | 1 | 1.2615 | 0.062847 | Medium | Medium | Low | 2132 | 1684 | 0.049821 | 37.2078
DOBBINS 1101CB | DOBBINS 1101 | SIERRA | 0.67055 | 10 | 81.76% | 0 | 0 | 100% | 0% | 0 | 0.028046 | 1 | 2.2347 | 0.062675 | Medium | Medium | Medium | 2133 | 2162 | 0.028046 | 37.145
REDBUD 110191960 | REDBUD 1101 | HUMBOLDT | 7.0156 | 10 | 50% | 3 | 16 | 100% | 0% | 0 | 0.0275 | 1 | 2.2782 | 0.062653 | Medium | Medium | Medium | 2134 | 2174 | 0.0275 | 37.0823
SAND CREEK 11037823F | SAND CREEK 1103 | FRESNO | 4.6802 | 10 | 100% | 0 | 1 | 100% | 0% | 0 | 0.029099 | 1 | 2.1489 | 0.062531 | Medium | Medium | Low | 2135 | 2119 | 0.029099 | 37.0196
CALAVERAS CEMENT 110111188 | CALAVERAS CEMENT 1101 | STOCKTON | 6.2741 | 29.7373 | 82.62% | 0 | 1 | 100% | 0% | 0 | 0.032851 | 1 | 1.9023 | 0.062494 | Medium | Medium | Low | 2136 | 2016 | 0.032851 | 36.9571
NARROWS 210276952 | NARROWS 2102 | SIERRA | 3.581 | 10 | 96.43% | 1 | 1 | 31.95% | 0% | 0 | 0.016756 | 1 | 3.7233 | 0.062386 | Low | Low | High | 2137 | 2537 | 0.016756 | 36.8946
BURNEY 110145984 | BURNEY 1101 | NORTH VALLEY | 4.7181 | 10 | 42.42% | 2 | 3 | 98.54% | 0% | 0 | 0.025045 | 1 | 2.4898 | 0.062355 | Medium | Medium | Medium | 2138 | 2241 | 0.025045 | 36.8322
HALSEY 11026129 | HALSEY 1102 | SIERRA | 3.2034 | 10 | 99.84% | 0 | 1 | 100% | 0% | 0 | 0.029062 | 1 | 2.1446 | 0.062326 | Medium | Medium | Low | 2139 | 2122 | 0.029062 | 36.7699
PUEBLO 1104640 | PUEBLO 1104 | NORTH BAY | 1.0277 | 10 | 45.71% | 1 | 4 | 32.52% | 0% | 0 | 0.02008 | 1 | 3.1015 | 0.06228 | Low | Low | High | 2140 | 2407 | 0.02008 | 36.7075
LONE TREE 210521210 | LONE TREE 2105 | DIABLO | 9.5646 | 10 | 95.6% | 0 | 2 | 59.2% | 0% | 0 | 0.019234 | 1 | 3.2356 | 0.062233 | Low | Low | High | 2141 | 2434 | 0.019234 | 36.6453
HALF MOON BAY 110369412 | HALF MOON BAY 1103 | PENINSULA | 16.9285 | 23.3773 | 24.92% | 11 | 5 | 79.06% | 0% | 0 | 0.038624 | 1 | 1.6101 | 0.062188 | Medium | Medium | Low | 2142 | 1887 | 0.038624 | 36.583
FROGTOWN 17027108 | FROGTOWN 1702 | STOCKTON | 10.0437 | 39.0873 | 66.95% | 0 | 1 | 78.26% | 0% | 0 | 0.024952 | 1 | 2.4898 | 0.062125 | Medium | Medium | Medium | 2143 | 2244 | 0.024952 | 36.5208
RED BLUFF 11041302 | RED BLUFF 1104 | NORTH VALLEY | 14.0918 | 39.8066 | 84.84% | 0 | 4 | 98.04% | 0% | 0 | 0.03726 | 1 | 1.6666 | 0.062097 | Medium | Medium | Low | 2144 | 1911 | 0.03726 | 36.4587
IGNACIO 1104450582 | IGNACIO 1104 | NORTH BAY | 3.8063 | 10 | 29.85% | 0 | 4 | 90.17% | 0% | 0 | 0.020738 | 1 | 2.9935 | 0.062078 | Low | Low | Medium | 2145 | 2378 | 0.020738 | 36.3966
CAMBRIA 1102CB | CAMBRIA 1102 | LOS PADRES | 14.9946 | 41.8579 | 39.26% | 1 | 1 | 64.1% | 0% | 0 | 0.026518 | 1 | 2.3401 | 0.062055 | Medium | Medium | Medium | 2146 | 2202 | 0.026518 | 36.3345
MENLO 110212249 | MENLO 1102 | PENINSULA | 2.4062 | 33.867 | 49.86% | 2 | 1 | 100% | 0% | 0 | 0.02665 | 1 | 2.3278 | 0.062037 | Medium | Medium | Medium | 2147 | 2200 | 0.02665 | 36.2725
VALLEY VIEW 1105P190 | VALLEY VIEW 1105 | EAST BAY | 3.5037 | 10 | 43.53% | 0 | 2 | 59.31% | 0% | 0 | 0.014389 | 1 | 4.3115 | 0.062036 | Low | Low | High | 2148 | 2634 | 0.014389 | 36.2104
CASTRO VALLEY 1108MR525 | CASTRO VALLEY 1108 | MISSION | 0.061081 | 10 | 0% | 0 | 3 | 100% | 0% | 0 | 0.017573 | 1 | 3.5299 | 0.062033 | Low | Low | High | 2149 | 2506 | 0.017573 | 36.1484
WEIMAR 11022038 | WEIMAR 1102 | SIERRA | 8.1278 | 10 | 76.79% | 4 | 4 | 100% | 0% | 0 | 0.030781 | 1 | 2.0149 | 0.062021 | Medium | Medium | Low | 2150 | 2076 | 0.030781 | 36.0864
NORTH BRANCH 110111158 | NORTH BRANCH 1101 | STOCKTON | 11.9363 | 47.5829 | 78.02% | 0 | 4 | 41.95% | 0% | 0 | 0.024519 | 1 | 2.528 | 0.061986 | Medium | Medium | Medium | 2151 | 2261 | 0.024519 | 36.0244
MARIPOSA 2102CB | MARIPOSA 2102 | YOSEMITE | 6.6916 | 39.3684 | 36.18% | 1 | 6 | 63.39% | 0% | 0 | 0.024571 | 1 | 2.5225 | 0.061982 | Medium | Medium | Medium | 2152 | 2259 | 0.024571 | 35.9624
WHITMORE 110145262 | WHITMORE 1101 | NORTH VALLEY | 28.7585 | 25.719 | 87.63% | 2 | 2 | 100% | 0% | 0 | 0.03964 | 1 | 1.5616 | 0.061901 | Medium | Medium | Low | 2153 | 1867 | 0.03964 | 35.9004
MC KEE 110870535 | MC KEE 1108 | SAN JOSE | 1.0836 | 23.5844 | 100% | 0 | 0 | 32.92% | 0% | 0 | 0.016178 | 1 | 3.8247 | 0.061876 | Low | Low | High | 2154 | 2564 | 0.016178 | 35.8385
OAKLAND X 1106CB | OAKLAND X 1106 | EAST BAY | 4.876 | 10 | 15.55% | 5 | 5 | 41.41% | 19.42% | 0 | 0.014897 | 1 | 4.146 | 0.061764 | Low | Low | High | 2155 | 2611 | 0.014897 | 35.7766
HIGHLANDS 110484640 | HIGHLANDS 1104 | HUMBOLDT | 0.56405 | 10 | 72.8% | 1 | 1 | 76.24% | 0% | 0 | 0.021388 | 1 | 2.8868 | 0.061742 | Low | Low | Medium | 2156 | 2355 | 0.021388 | 35.7148
GUALALA 1111445166 | GUALALA 1111 | HUMBOLDT | 7.5421 | 19.2895 | 4.143% | 11 | 12 | 79.44% | 0% | 0 | 0.036855 | 1 | 1.6737 | 0.061683 | Medium | Medium | Low | 2157 | 1920 | 0.036855 | 35.6531
PASO ROBLES 1103N52 | PASO ROBLES 1103 | LOS PADRES | 6.5425 | 67.4375 | 22.89% | 0 | 0 | 100% | 0% | 0 | 0.025622 | 1 | 2.4074 | 0.061683 | Medium | Medium | Medium | 2158 | 2228 | 0.025622 | 35.5914
EDES 1112CR282 | EDES 1112 | EAST BAY | 3.4204 | 10 | 46.24% | 0 | 3 | 83.7% | 0% | 0 | 0.019097 | 1 | 3.2289 | 0.061662 | Low | Low | High | 2159 | 2441 | 0.019097 | 35.5297
GONZALES 11013094 | GONZALES 1101 | CENTRAL COAST | 3.5612 | 68.6689 | 100% | 1 | 1 | 39.42% | 0% | 0 | 0.027478 | 1 | 2.2388 | 0.061516 | Medium | Medium | Medium | 2160 | 2178 | 0.027478 | 35.4681
OLETA 110151740 | OLETA 1101 | STOCKTON | 9.506 | 52.4452 | 97.68% | 1 | 4 | 44.88% | 0% | 0 | 0.023833 | 1 | 2.5749 | 0.061369 | Medium | Medium | Medium | 2161 | 2283 | 0.023833 | 35.4066
SAN RAFAEL 1109418 | SAN RAFAEL 1109 | NORTH BAY | 4.3553 | 10 | 55.54% | 4 | 2 | 35.66% | 0% | 0 | 0.013234 | 1 | 4.6368 | 0.061362 | Low | Low | High | 2162 | 2702 | 0.013234 | 35.3452
HIGGINS 11097863 | HIGGINS 1109 | SIERRA | 4.2214 | 12.2843 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028948 | 1 | 2.1193 | 0.06135 | Medium | Medium | Low | 2163 | 2125 | 0.028948 | 35.2838
SAN LUIS OBISPO 1104V40 | SAN LUIS OBISPO 1104 | LOS PADRES | 11.8926 | 26.5582 | 47.13% | 0 | 7 | 51.44% | 0% | 0 | 0.028654 | 1 | 2.1403 | 0.061327 | Medium | Medium | Low | 2164 | 2129 | 0.028654 | 35.2225
BURNEY 11011358 | BURNEY 1101 | NORTH VALLEY | 7.0165 | 60.5885 | 76.98% | 1 | 3 | 74.4% | 0% | 0 | 0.0317 | 1 | 1.9333 | 0.061286 | Medium | Medium | Low | 2165 | 2053 | 0.0317 | 35.1612
NARROWS 2101CB | NARROWS 2101 | SIERRA | 15.6172 | 42.314 | 50.34% | 2 | 7 | 100% | 0% | 0 | 0.031975 | 1 | 1.9092 | 0.061047 | Medium | Medium | Low | 2166 | 2048 | 0.031975 | 35.0999
BRUNSWICK 111061602 | BRUNSWICK 1110 | SIERRA | 9.4416 | 27.4436 | 52.21% | 4 | 4 | 73.99% | 0% | 0 | 0.022016 | 1 | 2.7653 | 0.06088 | Medium | Medium | Medium | 2167 | 2336 | 0.022016 | 35.0388
KONOCTI 1102948 | KONOCTI 1102 | HUMBOLDT | 6.065 | 30.1749 | 46.64% | 1 | 1 | 78.59% | 0% | 0 | 0.02028 | 1 | 2.9925 | 0.060688 | Low | Low | Medium | 2168 | 2395 | 0.02028 | 34.9779
KONOCTI 1108CB | KONOCTI 1108 | HUMBOLDT | 6.6517 | 32.6717 | 74.99% | 0 | 6 | 75.6% | 0% | 0 | 0.024164 | 1 | 2.5096 | 0.060644 | Medium | Medium | Medium | 2169 | 2274 | 0.024164 | 34.9173
ELK CREEK 11012032 | ELK CREEK 1101 | NORTH VALLEY | 9.5675 | 53.63 | 100% | 0 | 1 | 99.9% | 0% | 0 | 0.044086 | 1 | 1.3752 | 0.060626 | Medium | Medium | Low | 2170 | 1775 | 0.044086 | 34.8566
TIVY VALLEY 11077370 | TIVY VALLEY 1107 | FRESNO | 11.4788 | 20.0364 | 68.04% | 0 | 4 | 63.49% | 0% | 0 | 0.030142 | 1 | 2.0098 | 0.060577 | Medium | Medium | Low | 2171 | 2095 | 0.030142 | 34.796
BURNEY 11011340 | BURNEY 1101 | NORTH VALLEY | 18.024 | 21.8274 | 89.51% | 4 | 2 | 100% | 0% | 0 | 0.045714 | 1 | 1.3248 | 0.060564 | Medium | Medium | Low | 2172 | 1752 | 0.045714 | 34.7354
REDBUD 1102922 | REDBUD 1102 | HUMBOLDT | 3.3 | 10 | 97% | 1 | 5 | 42.49% | 0% | 0 | 0.026319 | 1 | 2.2985 | 0.060493 | Medium | Medium | Medium | 2173 | 2211 | 0.026319 | 34.6748
CAYETANO 2109MR572 | CAYETANO 2109 | MISSION | 8.1822 | 10 | 47.67% | 0 | 2 | 66.51% | 19.49% | 0 | 0.021821 | 1 | 2.7701 | 0.060448 | Medium | Medium | Medium | 2174 | 2341 | 0.021821 | 34.6143
EL CERRITO G 1110BR236 | EL CERRITO G 1110 | EAST BAY | 0.52869 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.7576 | 0.0604 | Low | Low | High | 2175 | 2735 | 0.012695 | 34.5539
SAN RAFAEL 1104CB | SAN RAFAEL 1104 | NORTH BAY | 2.4428 | 10 | 2.078% | 0 | 0 | 23.27% | 19.55% | 0 | 0.012295 | 1 | 4.9116 | 0.060389 | Low | Low | High | 2176 | 2788 | 0.012295 | 34.4935
BELL 1109CB | BELL 1109 | SIERRA | 13.433 | 10 | 50.92% | 4 | 3 | 76.11% | 0% | 0 | 0.022099 | 1 | 2.7321 | 0.060377 | Medium | Medium | Medium | 2177 | 2331 | 0.022099 | 34.4331
MORAGA 1103E510R | MORAGA 1103 | DIABLO | 1.3196 | 10 | 100% | 0 | 1 | 21.61% | 0% | 0 | 0.013477 | 1 | 4.475 | 0.060311 | Low | Low | High | 2178 | 2684 | 0.013477 | 34.3727
LAS AROMAS 0401LA401R | LAS AROMAS 0401 | DIABLO | 3.6951 | 10 | 0.309% | 3 | 6 | 93.3% | 0% | 0 | 0.018243 | 1 | 3.3031 | 0.060258 | Low | Low | High | 2179 | 2480 | 0.018243 | 34.3124
PEORIA 170590374 | PEORIA 1705 | YOSEMITE | 3.6064 | 10 | 81.75% | 0 | 1 | 81.35% | 0% | 0 | 0.020938 | 1 | 2.8737 | 0.060168 | Low | Low | Medium | 2180 | 2370 | 0.020938 | 34.2522
PLACER 1103CB | PLACER 1103 | SIERRA | 12.2492 | 28.3994 | 44.01% | 5 | 11 | 41.67% | 0% | 0 | 0.020134 | 1 | 2.9879 | 0.060157 | Low | Low | Medium | 2181 | 2402 | 0.020134 | 34.192
SAN LUIS OBISPO 1103V82 | SAN LUIS OBISPO 1103 | LOS PADRES | 6.5219 | 24.8763 | 65.03% | 1 | 11 | 46.53% | 0% | 0 | 0.026432 | 1 | 2.2734 | 0.060091 | Medium | Medium | Medium | 2182 | 2207 | 0.026432 | 34.1318
NORTH BRANCH 1101TS1115 | NORTH BRANCH 1101 | STOCKTON | 17.6104 | 17.7152 | 77.63% | 1 | 0 | 100% | 0% | 0 | 0.025404 | 1 | 2.3625 | 0.060018 | Medium | Medium | Medium | 2183 | 2232 | 0.025404 | 34.0717
SNEATH LANE 110134438 | SNEATH LANE 1101 | PENINSULA | 1.6791 | 10 | 46% | 1 | 0 | 33.32% | 0% | 0 | 0.014366 | 1 | 4.1734 | 0.059955 | Low | Low | High | 2184 | 2636 | 0.014366 | 34.0117
SYCAMORE CREEK 1111CB | SYCAMORE CREEK 1111 | NORTH VALLEY | 8.3942 | 56.8563 | 45.31% | 1 | 3 | 47.06% | 0% | 0 | 0.020907 | 1 | 2.8652 | 0.059903 | Low | Low | Medium | 2185 | 2372 | 0.020907 | 33.9518
BOLINAS 11011236 | BOLINAS 1101 | NORTH BAY | 3.0037 | 58.0295 | 0% | 0 | 0 | 73.67% | 0% | 0 | 0.017604 | 1 | 3.3892 | 0.059663 | Low | Low | High | 2186 | 2504 | 0.017604 | 33.8919
ECHO SUMMIT 110155262 | ECHO SUMMIT 1101 | (blank) | 0.16554 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.0866 | 0.059493 | Medium | Medium | Low | 2187 | 2136 | 0.028512 | 33.8322
DIAMOND SPRINGS 110740353 | DIAMOND SPRINGS 1107 | SIERRA | 2.2415 | 10 | 74.48% | 1 | 0 | 87.31% | 0% | 0 | 0.023671 | 1 | 2.5112 | 0.059443 | Medium | Medium | Medium | 2188 | 2290 | 0.023671 | 33.7727
HARTLEY 11014710 | HARTLEY 1101 | HUMBOLDT | 1.5005 | 10 | 52.07% | 1 | 0 | 100% | 0% | 0 | 0.019631 | 1 | 3.0245 | 0.059375 | Low | Low | Medium | 2189 | 2422 | 0.019631 | 33.7133
VOLTA 11011516 | VOLTA 1101 | NORTH VALLEY | 25.7297 | 67.2634 | 100% | 4 | 8 | 100% | 0% | 0 | 0.084582 | 1 | 0.70197 | 0.059374 | High | High | Low | 2190 | 1365 | 0.084582 | 33.6539
SAN JOAQUIN #2 110310320 | SAN JOAQUIN #2 1103 | YOSEMITE | 11.8104 | 12.4719 | 98.89% | 1 | 18 | 100% | 0% | 0 | 0.047599 | 1 | 1.2459 | 0.059305 | Medium | Medium | Low | 2191 | 1714 | 0.047599 | 33.5945
OILFIELDS 110383158 | OILFIELDS 1103 | CENTRAL COAST | 18.1787 | 60.504 | 100% | 0 | 4 | 93.79% | 0% | 0 | 0.067417 | 1 | 0.87957 | 0.059298 | High | High | Low | 2192 | 1492 | 0.067417 | 33.5352
PEORIA 170567898 | PEORIA 1705 | YOSEMITE | 5.0246 | 20.73 | 47.42% | 1 | 2 | 80.37% | 0% | 0 | 0.0199 | 1 | 2.9757 | 0.059217 | Low | Low | Medium | 2193 | 2414 | 0.0199 | 33.4759
RINCON 1101CB | RINCON 1101 | SONOMA | 2.1293 | 20.6419 | 39.27% | 1 | 4 | 43.97% | 11.03% | 0 | 0.018447 | 1 | 3.2011 | 0.05905 | Low | Low | High | 2194 | 2468 | 0.018447 | 33.4167
MIRABEL 1101CB | MIRABEL 1101 | SONOMA | 2.6279 | 19.2673 | 59.3% | 0 | 2 | 31.12% | 21.2% | 0 | 0.016241 | 1 | 3.6316 | 0.058979 | Low | Low | High | 2195 | 2562 | 0.016241 | 33.3577
ANNAPOLIS 1101CB | ANNAPOLIS 1101 | HUMBOLDT | 0.65809 | 81.2301 | 84.52% | 1 | 1 | 100% | 0% | 0 | 0.041698 | 1 | 1.4144 | 0.058979 | Medium | Medium | Low | 2196 | 1822 | 0.041698 | 33.2987
PALMER 110198478 | PALMER 1101 | LOS PADRES | 4.9874 | 64.4051 | 90.52% | 0 | 0 | 100% | 0% | 0 | 0.05552 | 1 | 1.0612 | 0.058918 | Medium | Medium | Low | 2197 | 1617 | 0.05552 | 33.2397
MORGAN HILL 210940000 | MORGAN HILL 2109 | SAN JOSE | 1.7684 | 10 | 99.47% | 0 | 0 | 59.08% | 0% | 0 | 0.019023 | 1 | 3.095 | 0.058876 | Low | Low | High | 2198 | 2446 | 0.019023 | 33.1808
GEYSERVILLE 1102522 | GEYSERVILLE 1102 | SONOMA | 8.3806 | 11.5615 | 69.84% | 1 | 7 | 78.98% | 12.25% | 0 | 0.038533 | 1 | 1.5258 | 0.058796 | Medium | Medium | Low | 2199 | 1888 | 0.038533 | 33.1219
KONOCTI 11084039 | KONOCTI 1108 | HUMBOLDT | 1.6026 | 10 | 100% | 0 | 2 | 69.54% | 0% | 0 | 0.022058 | 1 | 2.6616 | 0.05871 | Medium | Medium | Medium | 2200 | 2333 | 0.022058 | 33.0631
MORAGA 11017616 | MORAGA 1101 | DIABLO | 1.1725 | 14.9864 | 34.86% | 0 | 4 | 82.16% | 0% | 0 | 0.015878 | 1 | 3.6873 | 0.058547 | Low | Low | High | 2201 | 2579 | 0.015878 | 33.0044
EL DORADO PH 210152456 | EL DORADO PH 2101 | SIERRA | 10.1963 | 62.6198 | 100% | 3 | 10 | 100% | 0% | 0 | 0.058118 | 1 | 1.007 | 0.058524 | Medium | Medium | Low | 2202 | 1593 | 0.058118 | 32.9458
JESSUP 11021550 | JESSUP 1102 | NORTH VALLEY | 17.7067 | 29.9161 | 71.58% | 1 | 0 | 80.02% | 0% | 0 | 0.024597 | 1 | 2.3755 | 0.05843 | Medium | Medium | Medium | 2203 | 2257 | 0.024597 | 32.8873
WILLOW CREEK 11033090 | WILLOW CREEK 1103 | HUMBOLDT | 10.7823 | 82.4459 | 100% | 5 | 3 | 100% | 0% | 0 | 0.058956 | 1 | 0.99063 | 0.058403 | Medium | Medium | Low | 2204 | 1581 | 0.058956 | 32.8289
STAFFORD 1102908 | STAFFORD 1102 | NORTH BAY | 0.96495 | 10 | 77.17% | 0 | 3 | 21.89% | 0% | 0 | 0.01736 | 1 | 3.3591 | 0.058315 | Low | Low | High | 2205 | 2516 | 0.01736 | 32.7705
BEAR VALLEY 21054609 | BEAR VALLEY 2105 | YOSEMITE | 4.5488 | 18.0167 | 100% | 1 | 5 | 100% | 0% | 0 | 0.033715 | 1 | 1.728 | 0.058259 | Medium | Medium | Low | 2206 | 1986 | 0.033715 | 32.7122
VIEJO 22022606 | VIEJO 2202 | CENTRAL COAST | 0.94683 | 10 | 0% | 1 | 1 | 98.67% | 0% | 0 | 0.014784 | 1 | 3.9289 | 0.058085 | Low | Low | High | 2207 | 2620 | 0.014784 | 32.6539
CORNING 110253184 | CORNING 1102 | NORTH VALLEY | 31.925 | 68.303 | 86.89% | 0 | 7 | 100% | 0% | 0 | 0.049388 | 1 | 1.1736 | 0.05796 | Medium | Medium | Low | 2208 | 1691 | 0.049388 | 32.5958
MORGAN HILL 2105XR564 | MORGAN HILL 2105 | SAN JOSE | 5.4316 | 26.8638 | 49.46% | 0 | 4 | 75.02% | 0% | 0 | 0.023443 | 1 | 2.4719 | 0.057948 | Medium | Medium | Medium | 2209 | 2296 | 0.023443 | 32.5379
CMC 1101CB | CMC 1101 | LOS PADRES | 2.0609 | 25.5297 | 52.24% | 0 | 0 | 100% | 0% | 0 | 0.021532 | 1 | 2.6866 | 0.057849 | Low | Low | Medium | 2210 | 2350 | 0.021532 | 32.4799
RIDGE 0402CB | RIDGE 0402 | EAST BAY | 1.6674 | 10 | 31.81% | 1 | 0 | 69.66% | 0% | 0 | 0.014084 | 1 | 4.0946 | 0.05767 | Low | Low | High | 2211 | 2658 | 0.014084 | 32.4221
LAS PULGAS 0401CB | LAS PULGAS 0401 | PENINSULA | 0.063561 | 10 | 100% | 0 | 1 | 1.053% | 0% | 0 | 0.012548 | 1 | 4.5955 | 0.057664 | Low | Low | High | 2212 | 2771 | 0.012548 | 32.3644
FLORENCE 0401CR220 | FLORENCE 0401 | EAST BAY | 0.0014212 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.5363 | 0.057589 | Low | Low | High | 2213 | 2735 | 0.012695 | 32.3067
LLAGAS 21011449 | LLAGAS 2101 | SAN JOSE | 7.6142 | 50.4014 | 99.39% | 2 | 1 | 54.33% | 0% | 0 | 0.024906 | 1 | 2.3109 | 0.057555 | Medium | Medium | Medium | 2214 | 2245 | 0.024906 | 32.2492
TAR FLAT 0401CB | TAR FLAT 0401 | YOSEMITE | 3.4825 | 10 | 7.176% | 1 | 2 | 94.76% | 17.84% | 1 | 0.017966 | 1 | 3.199 | 0.057473 | Low | Low | High | 2215 | 2490 | 0.017966 | 32.1916
SALMON CREEK 110137368 | SALMON CREEK 1101 | SONOMA | 7.013 | 10 | 3.2% | 1 | 7 | 100% | 0% | 0 | 0.029331 | 1 | 1.9591 | 0.057461 | Medium | Medium | Low | 2216 | 2115 | 0.029331 | 32.1341
CLOVERDALE 1102CB | CLOVERDALE 1102 | SONOMA | 0.24384 | 33.3215 | 52.03% | 0 | 0 | 8.095% | 59.2% | 0 | 0.023631 | 1 | 2.4298 | 0.05742 | Medium | Medium | Medium | 2217 | 2292 | 0.023631 | 32.0767
POINT ARENA 11012637 | POINT ARENA 1101 | HUMBOLDT | 4.0404 | 84.4232 | 59.73% | 1 | 2 | 100% | 0% | 0 | 0.046116 | 1 | 1.2415 | 0.057252 | Medium | Medium | Low | 2218 | 1739 | 0.046116 | 32.0192
VALLEY VIEW 1106P176 | VALLEY VIEW 1106 | EAST BAY | 0.884 | 14.838 | 80.1% | 1 | 0 | 21.45% | 0% | 0 | 0.013387 | 1 | 4.2737 | 0.057211 | Low | Low | High | 2219 | 2692 | 0.013387 | 31.962
ROSSMOOR 110845268 | ROSSMOOR 1108 | DIABLO | 3.7726 | 24.3862 | 31.05% | 0 | 7 | 47.92% | 0% | 0 | 0.014195 | 1 | 4.0289 | 0.057189 | Low | Low | High | 2220 | 2652 | 0.014195 | 31.9048
SAUSALITO 11021500 | SAUSALITO 1102 | NORTH BAY | 1.1513 | 69.0338 | 0% | 0 | 0 | 90.51% | 0% | 0 | 0.017208 | 1 | 3.3211 | 0.05715 | Low | Low | High | 2221 | 2522 | 0.017208 | 31.8476
SARATOGA 11076867 | SARATOGA 1107 | DE ANZA | 0.24862 | 10 | 100% | 0 | 2 | 30.1% | 0% | 0 | 0.014963 | 1 | 3.817 | 0.057115 | Low | Low | High | 2222 | 2609 | 0.014963 | 31.7904
MONTICELLO 1101654 | MONTICELLO 1101 | NORTH BAY | 8.1004 | 46.4584 | 35.79% | 0 | 2 | 92.66% | 0% | 0 | 0.031073 | 1 | 1.8356 | 0.057038 | Medium | Medium | Low | 2223 | 2070 | 0.031073 | 31.7333
PURISIMA 1101CB | PURISIMA 1101 | LOS PADRES | 3.8284 | 30.5658 | 4.848% | 1 | 0 | 83.25% | 0% | 0 | 0.014861 | 1 | 3.8367 | 0.057017 | Low | Low | High | 2224 | 2615 | 0.014861 | 31.6763
HIGGINS 1110CB | HIGGINS 1110 | SIERRA | 11.6416 | 10 | 74.55% | 3 | 1 | 64.03% | 0% | 0 | 0.01732 | 1 | 3.2906 | 0.056995 | Low | Low | High | 2225 | 2517 | 0.01732 | 31.6193
PUEBLO 21031970 | PUEBLO 2103 | NORTH BAY | 3.678 | 37.2305 | 48.19% | 3 | 0 | 44.65% | 0% | 0 | 0.017676 | 1 | 3.2222 | 0.056955 | Low | Low | High | 2226 | 2503 | 0.017676 | 31.5623
DUNLAP 11037220 | DUNLAP 1103 | FRESNO | 24.8173 | 17.858 | 99.97% | 1 | 5 | 100% | 0% | 0 | 0.0383 | 1 | 1.4867 | 0.056942 | Medium | Medium | Low | 2227 | 1891 | 0.0383 | 31.5053
PINE GROVE 110152088 | PINE GROVE 1101 | STOCKTON | 2.528 | 10 | 68.63% | 1 | 3 | 100% | 0% | 0 | 0.023865 | 1 | 2.3857 | 0.056935 | Medium | Medium | Medium | 2228 | 2282 | 0.023865 | 31.4484
REDBUD 1102510 | REDBUD 1102 | HUMBOLDT | 6.0638 | 23.833 | 59.82% | 2 | 2 | 75.22% | 0% | 0 | 0.02163 | 1 | 2.6321 | 0.056933 | Low | Low | Medium | 2229 | 2348 | 0.02163 | 31.3914
HALSEY 11012412 | HALSEY 1101 | SIERRA | 5.321 | 10 | 60.58% | 4 | 4 | 100% | 0% | 0 | 0.023732 | 1 | 2.3931 | 0.056792 | Medium | Medium | Medium | 2230 | 2287 | 0.023732 | 31.3345
MORAGA 1103CB | MORAGA 1103 | DIABLO | 1.341 | 16.5323 | 0% | 6 | 3 | 21.01% | 11.54% | 0 | 0.01426 | 1 | 3.9729 | 0.056652 | Low | Low | High | 2231 | 2643 | 0.01426 | 31.2777
COARSEGOLD 2103 | COARSEGOLD 2103 | YOSEMITE | 0.14838 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.9847 | 0.056588 | Medium | Medium | Low | 2232 | 2136 | 0.028512 | 31.2211
OAKLAND K 1103CR422 | OAKLAND K 1103 | EAST BAY | 1.8547 | 10 | 4.055% | 0 | 3 | 90.41% | 0% | 0 | 0.0127 | 1 | 4.4523 | 0.056544 | Low | Low | High | 2233 | 2731 | 0.0127 | 31.1645
POINT ARENA 11014923 | POINT ARENA 1101 | HUMBOLDT | 2.8662 | 57.1036 | 19.76% | 5 | 5 | 100% | 0% | 0 | 0.031366 | 1 | 1.8015 | 0.056505 | Medium | Medium | Low | 2234 | 2065 | 0.031366 | 31.1079
NEWBURG 1133CB | NEWBURG 1133 | HUMBOLDT | 3.7712 | 37.8079 | 38.51% | 2 | 0 | 41.21% | 0% | 0 | 0.020349 | 1 | 2.7759 | 0.056485 | Low | Low | Medium | 2235 | 2391 | 0.020349 | 31.0514
VALLEY VIEW 1106CB | VALLEY VIEW 1106 | EAST BAY | 3.4767 | 45.2583 | 0.9386% | 0 | 1 | 68.92% | 0% | 0 | 0.013903 | 1 | 4.0593 | 0.056436 | Low | Low | High | 2236 | 2667 | 0.013903 | 30.9949
FRENCH GULCH 11011892 | FRENCH GULCH 1101 | NORTH VALLEY | 2.9079 | 75.8107 | 100% | 0 | 0 | 100% | 0% | 0 | 0.044011 | 1 | 1.2823 | 0.056435 | Medium | Medium | Low | 2237 | 1778 | 0.044011 | 30.9385
SAN CARLOS 11049048 | SAN CARLOS 1104 | PENINSULA | 0.01529 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.4369 | 0.056328 | Low | Low | High | 2238 | 2735 | 0.012695 | 30.8821
HARTLEY 1101698 | HARTLEY 1101 | HUMBOLDT | 6.3129 | 57.2881 | 69.42% | 1 | 7 | 61.15% | 0% | 0 | 0.027842 | 1 | 2.0226 | 0.056312 | Medium | Medium | Low | 2239 | 2166 | 0.027842 | 30.8257
VACAVILLE 1104CB | VACAVILLE 1104 | SACRAMENTO | 0.88859 | 38.1521 | 69.79% | 0 | 1 | 28.2% | 0% | 0 | 0.017694 | 1 | 3.1813 | 0.056289 | Low | Low | High | 2240 | 2502 | 0.017694 | 30.7694
OAKLAND K 1104468 | OAKLAND K 1104 | EAST BAY | 0.0028424 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.4321 | 0.056268 | Low | Low | High | 2241 | 2735 | 0.012695 | 30.7131
FROGTOWN 170211212 | FROGTOWN 1702 | STOCKTON | 22.4074 | 27.4478 | 70.17% | 2 | 7 | 100% | 0% | 0 | 0.033949 | 1 | 1.6518 | 0.056076 | Medium | Medium | Low | 2242 | 1979 | 0.033949 | 30.6569
PIT NO 1 110170952 | PIT NO 1 1101 | NORTH VALLEY | 1.5383 | 10 | 71.41% | 1 | 1 | 89.97% | 0% | 0 | 0.024193 | 1 | 2.3158 | 0.056027 | Medium | Medium | Medium | 2243 | 2272 | 0.024193 | 30.6008
SAND CREEK 1103 | SAND CREEK 1103 | FRESNO | 0.037983 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.9649 | 0.056022 | Medium | Medium | Low | 2244 | 2136 | 0.028512 | 30.5448
UKIAH 111129452 | UKIAH 1111 | HUMBOLDT | 3.6752 | 77.2683 | 100% | 0 | 0 | 30.05% | 0% | 0 | 0.022547 | 1 | 2.4814 | 0.055947 | Medium | Medium | Medium | 2245 | 2320 | 0.022547 | 30.4888
ELK CREEK 110193504 | ELK CREEK 1101 | NORTH VALLEY | 2.2601 | 54.3949 | 100% | 0 | 0 | 90.07% | 0% | 0 | 0.034745 | 1 | 1.6101 | 0.055942 | Medium | Medium | Low | 2246 | 1956 | 0.034745 | 30.4328
SO. CAL. EDISON #3 1101CB | SO. CAL. EDISON #3 1101 | FRESNO | 6.4255 | 72.2284 | 15.88% | 0 | 1 | 100% | 34.58% | 0 | 0.038701 | 1 | 1.4452 | 0.055932 | Medium | Medium | Low | 2247 | 1886 | 0.038701 | 30.3769
FORT BRAGG A 11013100 | FORT BRAGG A 1101 | HUMBOLDT | 12.9058 | 10 | 7.343% | 8 | 11 | 88.01% | 0% | 0 | 0.021681 | 1 | 2.5776 | 0.055885 | Low | Low | Medium | 2248 | 2346 | 0.021681 | 30.3209
SAN LEANDRO U 1114MR218 | SAN LEANDRO U 1114 | MISSION | 6.9334 | 10 | 55.46% | 3 | 0 | 61.53% | 0% | 0 | 0.01617 | 1 | 3.4495 | 0.055778 | Low | Low | High | 2249 | 2565 | 0.01617 | 30.265
LUCERNE 11062355 | LUCERNE 1106 | HUMBOLDT | 0.92313 | 10 | 100% | 1 | 0 | 88.59% | 0% | 0 | 0.02584 | 1 | 2.1572 | 0.055742 | Medium | Medium | Low | 2250 | 2220 | 0.02584 | 30.2093
EL CERRITO G 1113CB | EL CERRITO G 1113 | EAST BAY | 0.20892 | 10 | 100% | 0 | 0 | 4.98% | 0% | 0 | 0.011198 | 1 | 4.968 | 0.055631 | Low | Low | High | 2251 | 2856 | 0.011198 | 30.1535
HAMILTON BRANCH 11012436 | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.2668 | 10 | 100% | 0 | 1 | 100% | 0% | 0 | 0.029099 | 1 | 1.9087 | 0.055542 | Medium | Medium | Low | 2252 | 2119 | 0.029099 | 30.0979
RESERVATION ROAD 11023030 | RESERVATION ROAD 1102 | CENTRAL COAST | 4.2831 | 56.4796 | 100% | 0 | 1 | 16.48% | 0% | 0 | 0.038229 | 1 | 1.4511 | 0.055473 | Medium | Medium | Low | 2253 | 1894 | 0.038229 | 30.0424
CORRAL 110213498 | CORRAL 1102 | STOCKTON | 0.99648 | 10 | 14.99% | 0 | 1 | 100% | 0% | 0 | 0.0167 | 1 | 3.3092 | 0.055263 | Low | Low | High | 2254 | 2541 | 0.0167 | 29.9869
OLETA 11011208 | OLETA 1101 | STOCKTON | 32.4243 | 51.211 | 80.1% | 0 | 12 | 85.11% | 0% | 0 | 0.040132 | 1 | 1.3763 | 0.055235 | Medium | Medium | Low | 2255 | 1852 | 0.040132 | 29.9316
CEDAR CREEK 11011608 | CEDAR CREEK 1101 | NORTH VALLEY | 33.3899 | 31.7775 | 100% | 3 | 12 | 100% | 36.09% | 1 | 0.10917 | 1 | 0.50558 | 0.055196 | High | High | Low | 2256 | 1263 | 0.10917 | 29.8764
SISQUOC 1103M98 | SISQUOC 1103 | LOS PADRES | 6.4595 | 29.4274 | 100% | 0 | 1 | 65.51% | 60.21% | 1 | 0.060705 | 1 | 0.90853 | 0.055153 | Medium | Medium | Low | 2257 | 1560 | 0.060705 | 29.8212
SUNOL 1101MR297 | SUNOL 1101 | MISSION | 6.0465 | 17.8817 | 28.91% | 0 | 2 | 100% | 17.46% | 0 | 0.023322 | 1 | 2.3616 | 0.055077 | Medium | Medium | Medium | 2258 | 2302 | 0.023322 | 29.766
BIG RIVER 1101CB | BIG RIVER 1101 | HUMBOLDT | 1.8594 | 10 | 0.4258% | 5 | 2 | 94.21% | 0% | 0 | 0.01527 | 1 | 3.6 | 0.054971 | Low | Low | High | 2259 | 2599 | 0.01527 | 29.711
MORRO BAY 110248384 | MORRO BAY 1102 | LOS PADRES | 0.22159 | 10 | 0% | 1 | 1 | 100% | 0% | 0 | 0.013132 | 1 | 4.1848 | 0.054953 | Low | Low | High | 2260 | 2709 | 0.013132 | 29.656
FORT BRAGG A 1102816 | FORT BRAGG A 1102 | HUMBOLDT | 2.5631 | 10 | 6.097% | 3 | 2 | 100% | 0% | 0 | 0.018806 | 1 | 2.916 | 0.054838 | Low | Low | Medium | 2261 | 2456 | 0.018806 | 29.601
MORRO BAY 110298906 | MORRO BAY 1102 | LOS PADRES | 0.034162 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.3164 | 0.054798 | Low | Low | High | 2262 | 2735 | 0.012695 | 29.5462
ARCATA 11211206 | ARCATA 1121 | HUMBOLDT | 6.629 | 50.041 | 6.756% | 12 | 6 | 42.25% | 0% | 0 | 0.022231 | 1 | 2.4644 | 0.054786 | Medium | Medium | Medium | 2263 | 2323 | 0.022231 | 29.4914
HOPLAND 110194006 | HOPLAND 1101 | HUMBOLDT | 13.3558 | 51.6995 | 99.02% | 0 | 1 | 84.05% | 0% | 0 | 0.032603 | 1 | 1.676 | 0.054643 | Medium | Medium | Low | 2264 | 2023 | 0.032603 | 29.4366
BEAR VALLEY 21059480 | BEAR VALLEY 2105 | YOSEMITE | 12.4081 | 50.2702 | 94.93% | 2 | 0 | 100% | 0% | 0 | 0.041692 | 1 | 1.3091 | 0.054581 | Medium | Medium | Low | 2265 | 1823 | 0.041692 | 29.382
PETALUMA C 1108632 | PETALUMA C 1108 | SONOMA | 14.7325 | 83.7221 | 19.94% | 0 | 2 | 100% | 0% | 0 | 0.033063 | 1 | 1.6482 | 0.054496 | Medium | Medium | Low | 2266 | 2008 | 0.033063 | 29.3274
OAKLAND J 1102CR184 | OAKLAND J 1102 | EAST BAY | 3.4622 | 10 | 2.127% | 3 | 2 | 100% | 0% | 0 | 0.01597 | 1 | 3.4089 | 0.054442 | Low | Low | High | 2267 | 2572 | 0.01597 | 29.2729
FORT SEWARD 11211663 | FORT SEWARD 1121 | HUMBOLDT | 1.9431 | 10 | 100% | 1 | 4 | 100% | 0% | 0 | 0.03133 | 1 | 1.7358 | 0.054383 | Medium | Medium | Low | 2268 | 2066 | 0.03133 | 29.2185
WISE 1101CB | WISE 1101 | SIERRA | 5.8467 | 15.7551 | 45.1% | 2 | 5 | 65.21% | 0% | 0 | 0.01999 | 1 | 2.7196 | 0.054364 | Low | Low | Medium | 2269 | 2408 | 0.01999 | 29.1641
PHILO 110137222 | PHILO 1101 | HUMBOLDT | 25.4322 | 53.3862 | 64.87% | 9 | 12 | 100% | 0% | 0 | 0.060092 | 1 | 0.9025 | 0.054233 | Medium | Medium | Low | 2270 | 1564 | 0.060092 | 29.1097
FROGTOWN 17028482 | FROGTOWN 1702 | STOCKTON | 14.6236 | 52.3445 | 57.04% | 0 | 2 | 100% | 0% | 0 | 0.027885 | 1 | 1.9388 | 0.054064 | Medium | Medium | Low | 2271 | 2165 | 0.027885 | 29.0555
SAN CARLOS 110475210 | SAN CARLOS 1104 | PENINSULA | 0.38485 | 10 | 11.56% | 0 | 1 | 100% | 0% | 0 | 0.01424 | 1 | 3.7871 | 0.053927 | Low | Low | High | 2272 | 2648 | 0.01424 | 29.0014
CRESCENT MILLS 21012562 | CRESCENT MILLS 2101 | NORTH VALLEY | 17.3839 | 76.7012 | 88.81% | 4 | 1 | 50.76% | 0% | 0 | 0.034993 | 1 | 1.5371 | 0.053789 | Medium | Medium | Low | 2273 | 1953 | 0.034993 | 28.9475
MORRO BAY 110242062 | MORRO BAY 1102 | LOS PADRES | 0.13997 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.236 | 0.053777 | Low | Low | High | 2274 | 2735 | 0.012695 | 28.8937
CASTRO VALLEY 1101MR204 | CASTRO VALLEY 1101 | MISSION | 2.1197 | 29.3697 | 13.12% | 0 | 1 | 73.48% | 0% | 0 | 0.012645 | 1 | 4.251 | 0.053753 | Low | Low | High | 2275 | 2769 | 0.012645 | 28.8399
OTTER 1101440 | OTTER 1101 | CENTRAL COAST | 8.556 | 21.3917 | 0.8557% | 24 | 4 | 77.84% | 0% | 0 | 0.021414 | 1 | 2.508 | 0.053708 | Low | Low | Medium | 2276 | 2353 | 0.021414 | 28.7862
ANTLER 1101CB | ANTLER 1101 | NORTH VALLEY | 1.601 | 30.2969 | 97.79% | 1 | 1 | 100% | 0% | 0 | 0.042837 | 1 | 1.2522 | 0.053641 | Medium | Medium | Low | 2277 | 1803 | 0.042837 | 28.7325
WEIMAR 11012764 | WEIMAR 1101 | SIERRA | 6.0658 | 10 | 51% | 1 | 6 | 100% | 0% | 0 | 0.028566 | 1 | 1.8747 | 0.053554 | Medium | Medium | Low | 2278 | 2130 | 0.028566 | 28.6788
LOS GATOS 1102CB | LOS GATOS 1102 | DE ANZA | 1.1034 | 10 | 59.61% | 1 | 4 | 18.46% | 0% | 0 | 0.013194 | 1 | 4.0562 | 0.053517 | Low | Low | High | 2279 | 2705 | 0.013194 | 28.6253
GARBERVILLE 11011604 | GARBERVILLE 1101 | HUMBOLDT | 4.3333 | 50.687 | 100% | 0 | 3 | 25.13% | 0% | 0 | 0.024833 | 1 | 2.1532 | 0.053469 | Medium | Medium | Low | 2280 | 2249 | 0.024833 | 28.5717
SARATOGA 1115LC20 | SARATOGA 1115 | DE ANZA | 2.7261 | 10 | 38.53% | 0 | 1 | 56.79% | 0% | 0 | 0.015057 | 1 | 3.5487 | 0.053432 | Low | Low | High | 2281 | 2605 | 0.015057 | 28.5183
TEMPLETON 2113A08 | TEMPLETON 2113 | LOS PADRES | 9.9198 | 65.213 | 45.79% | 1 | 2 | 40.4% | 37.28% | 0 | 0.032324 | 1 | 1.6527 | 0.053421 | Medium | Medium | Low | 2282 | 2034 | 0.032324 | 28.4648
LUCERNE 11034200 | LUCERNE 1103 | HUMBOLDT | 4.2514 | 45.4735 | 81.38% | 0 | 1 | 86.14% | 0% | 0 | 0.027721 | 1 | 1.9269 | 0.053416 | Medium | Medium | Low | 2283 | 2170 | 0.027721 | 28.4114
REDBUD 1101400 | REDBUD 1101 | HUMBOLDT | 1.0177 | 10 | 44.91% | 0 | 5 | 100% | 0% | 0 | 0.020268 | 1 | 2.632 | 0.053346 | Low | Low | Medium | 2284 | 2396 | 0.020268 | 28.358
PEORIA 170169124 | PEORIA 1701 | YOSEMITE | 2.706 | 13.7023 | 100% | 0 | 2 | 100% | 0% | 0 | 0.039389 | 1 | 1.3543 | 0.053345 | Medium | Medium | Low | 2285 | 1874 | 0.039389 | 28.3047
FORT BRAGG A 110195294 | FORT BRAGG A 1101 | HUMBOLDT | 25.9363 | 28.0829 | 8.119% | 33 | 16 | 99.05% | 0% | 0 | 0.053875 | 1 | 0.98845 | 0.053253 | Medium | Medium | Low | 2286 | 1639 | 0.053875 | 28.2513
RIO DELL 11028852 | RIO DELL 1102 | HUMBOLDT | 3.7546 | 61.6723 | 39.96% | 1 | 3 | 79.33% | 0% | 0 | 0.021849 | 1 | 2.4325 | 0.053146 | Medium | Medium | Medium | 2287 | 2339 | 0.021849 | 28.1981
NEWBURG 113190242 | NEWBURG 1131 | HUMBOLDT | 3.4074 | 35.576 | 50.59% | 5 | 2 | 78.12% | 0% | 0 | 0.020383 | 1 | 2.6054 | 0.053106 | Low | Low | Medium | 2288 | 2388 | 0.020383 | 28.1449
VOLTA 110149742 | VOLTA 1101 | NORTH VALLEY | 3.4776 | 49.9174 | 84.98% | 0 | 1 | 100% | 0% | 0 | 0.038241 | 1 | 1.3857 | 0.05299 | Medium | Medium | Low | 2289 | 1893 | 0.038241 | 28.0918
HIGGINS 111051794 | HIGGINS 1110 | SIERRA | 3.8902 | 22.6443 | 10.14% | 0 | 1 | 100% | 0% | 0 | 0.017481 | 1 | 3.0277 | 0.052927 | Low | Low | Medium | 2290 | 2513 | 0.017481 | 28.0388
HIGGINS 11041006 | HIGGINS 1104 | SIERRA | 9.9734 | 10.2486 | 72.09% | 2 | 7 | 49.68% | 0% | 0 | 0.016495 | 1 | 3.2059 | 0.052881 | Low | Low | High | 2291 | 2552 | 0.016495 | 27.9859
FORT BRAGG A 11013113 | FORT BRAGG A 1101 | HUMBOLDT | 10.0167 | 23.3659 | 35.03% | 10 | 7 | 100% | 0% | 0 | 0.031469 | 1 | 1.6795 | 0.052853 | Medium | Medium | Low | 2292 | 2062 | 0.031469 | 27.933
WEIMAR 1101 | WEIMAR 1101 | SIERRA | 0.067365 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.8525 | 0.052817 | Medium | Medium | Low | 2293 | 2136 | 0.028512 | 27.8802
PHILO 1102928 | PHILO 1102 | HUMBOLDT | 13.0575 | 61.4578 | 77.17% | 8 | 4 | 85.6% | 0% | 0 | 0.058135 | 1 | 0.90846 | 0.052813 | Medium | Medium | Low | 2294 | 1592 | 0.058135 | 27.8273
LOS GATOS 110160052 | LOS GATOS 1101 | DE ANZA | 1.8727 | 10 | 24.39% | 0 | 1 | 100% | 0% | 0 | 0.015806 | 1 | 3.3394 | 0.052781 | Low | Low | High | 2295 | 2583 | 0.015806 | 27.7745
SHINGLE SPRINGS 210819622 | SHINGLE SPRINGS 2108 | SIERRA | 4.5627 | 12.9837 | 69.35% | 2 | 3 | 39.08% | 0% | 0 | 0.015541 | 1 | 3.3954 | 0.052766 | Low | Low | High | 2296 | 2590 | 0.015541 | 27.7217
SAN RAFAEL 11042651 | SAN RAFAEL 1104 | NORTH BAY | 0.79099 | 10 | 0% | 1 | 1 | 96.62% | 0% | 0 | 0.0127 | 1 | 4.1495 | 0.0527 | Low | Low | High | 2297 | 2730 | 0.0127 | 27.669
PERRY 1101V72 | PERRY 1101 | LOS PADRES | 5.7537 | 10 | 2.358% | 4 | 2 | 65.46% | 0% | 0 | 0.013146 | 1 | 4.0035 | 0.052631 | Low | Low | High | 2298 | 2708 | 0.013146 | 27.6163
HIGHLANDS 11034630 | HIGHLANDS 1103 | HUMBOLDT | 1.4567 | 24.8899 | 80.52% | 0 | 2 | 42.07% | 0% | 0 | 0.015892 | 1 | 3.3089 | 0.052584 | Low | Low | High | 2299 | 2578 | 0.015892 | 27.5636
HOLLISTER 21044403 | HOLLISTER 2104 | CENTRAL COAST | 5.3706 | 82.3816 | 100% | 0 | 0 | 28.45% | 0% | 0 | 0.022969 | 1 | 2.2884 | 0.052563 | Medium | Medium | Medium | 2300 | 2308 | 0.022969 | 27.5111
BIG RIVER 1101954 | BIG RIVER 1101 | HUMBOLDT | 7.7476 | 11.9193 | 13.02% | 4 | 10 | 95.19% | 0% | 0 | 0.020135 | 1 | 2.6074 | 0.0525 | Low | Low | Medium | 2301 | 2401 | 0.020135 | 27.4585
EDENVALE 2107D80 | EDENVALE 2107 | SAN JOSE | 0.032033 | 71.8938 | 0% | 0 | 0 | 100% | 0% | 0 | 0.019259 | 1 | 2.7189 | 0.052363 | Low | Low | Medium | 2302 | 2431 | 0.019259 | 27.406
CLAY 11037124 | CLAY 1103 | STOCKTON | 8.9452 | 50.0578 | 97.24% | 0 | 1 | 27.91% | 0% | 0 | 0.020936 | 1 | 2.4969 | 0.052275 | Low | Low | Medium | 2303 | 2371 | 0.020936 | 27.3536
SAN JOAQUIN #2 1103157026 | SAN JOAQUIN #2 1103 | YOSEMITE | 3.2012 | 10 | 100% | 2 | 9 | 100% | 0% | 0 | 0.039941 | 1 | 1.3059 | 0.052157 | Medium | Medium | Low | 2304 | 1858 | 0.039941 | 27.3014
AUBURN 11028611 | AUBURN 1102 | SIERRA | 1.8383 | 10 | 16.6% | 1 | 2 | 100% | 0% | 0 | 0.017498 | 1 | 2.9798 | 0.05214 | Low | Low | Medium | 2305 | 2512 | 0.017498 | 27.2492
CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 1101 | STOCKTON | 0.0029886 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.8278 | 0.052113 | Medium | Medium | Low | 2306 | 2136 | 0.028512 | 27.1971
CALAVERAS CEMENT 110111236 | CALAVERAS CEMENT 1101 | STOCKTON | 20.1179 | 16.0826 | 47.9% | 0 | 4 | 100% | 0% | 0 | 0.027497 | 1 | 1.8952 | 0.052111 | Medium | Medium | Low | 2307 | 2176 | 0.027497 | 27.145
TASSAJARA 2104 | TASSAJARA 2104 | DIABLO | 0.070201 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.0947 | 0.051984 | Low | Low | High | 2308 | 2735 | 0.012695 | 27.0928
POINT ARENA 110183354 | POINT ARENA 1101 | HUMBOLDT | 5.1346 | 37.1787 | 0% | 2 | 5 | 100% | 0% | 0 | 0.025688 | 1 | 2.0227 | 0.051961 | Medium | Medium | Low | 2309 | 2227 | 0.025688 | 27.0409
DESCHUTES 11041370 | DESCHUTES 1104 | NORTH VALLEY | 12.2362 | 19.7367 | 98.52% | 1 | 1 | 55.17% | 0% | 0 | 0.022854 | 1 | 2.271 | 0.051901 | Medium | Medium | Medium | 2310 | 2310 | 0.022854 | 26.9889
POSO MOUNTAIN 21012181 | POSO MOUNTAIN 2101 | KERN | 17.1051 | 10 | 29.81% | 0 | 0 | 71.06% | 0% | 0 | 0.023433 | 1 | 2.214 | 0.051879 | Medium | Medium | Low | 2311 | 2298 | 0.023433 | 26.937
SALT SPRINGS 21011232 | SALT SPRINGS 2101 | STOCKTON | 6.1779 | 10 | 100% | 4 | 2 | 68.77% | 0% | 0 | 0.064284 | 1 | 0.80663 | 0.051853 | High | High | Low | 2312 | 1523 | 0.064284 | 26.8851
ALTO 112265474 | ALTO 1122 | NORTH BAY | 2.1481 | 10 | 21.89% | 2 | 1 | 58.84% | 6.137% | 0 | 0.013328 | 1 | 3.89 | 0.051845 | Low | Low | High | 2313 | 2697 | 0.013328 | 26.8333
PERRY 1101W52 | PERRY 1101 | LOS PADRES | 2.9028 | 10 | 12.36% | 3 | 2 | 69.83% | 0% | 0 | 0.014698 | 1 | 3.5249 | 0.051807 | Low | Low | High | 2314 | 2627 | 0.014698 | 26.7814
PENRYN 11072410 | PENRYN 1107 | SIERRA | 2.4145 | 10 | 87.13% | 0 | 1 | 32.14% | 0% | 0 | 0.015364 | 1 | 3.3713 | 0.051797 | Low | Low | High | 2315 | 2594 | 0.015364 | 26.7296
TIDEWATER 210614072 | TIDEWATER 2106 | DIABLO | 3.6661 | 10 | 16.78% | 0 | 0 | 95.56% | 0% | 0 | 0.013929 | 1 | 3.718 | 0.051789 | Low | Low | High | 2316 | 2665 | 0.013929 | 26.6778
PEORIA 170190090 | PEORIA 1701 | YOSEMITE | 29.5241 | 42.6688 | 45.08% | 1 | 8 | 98.45% | 0% | 0 | 0.050945 | 1 | 1.0149 | 0.051705 | Medium | Medium | Low | 2317 | 1673 | 0.050945 | 26.626
COARSEGOLD 2102CB | COARSEGOLD 2102 | YOSEMITE | 14.0621 | 38.5067 | 44.35% | 2 | 1 | 100% | 4.748% | 0 | 0.028352 | 1 | 1.8189 | 0.051569 | Medium | Medium | Low | 2318 | 2157 | 0.028352 | 26.5743
PERRY 110185870 | PERRY 1101 | LOS PADRES | 13.2734 | 34.8685 | 24.59% | 0 | 0 | 72.93% | 0% | 0 | 0.018257 | 1 | 2.8229 | 0.051539 | Low | Low | Medium | 2319 | 2477 | 0.018257 | 26.5228
PEORIA 170510580 | PEORIA 1705 | YOSEMITE | 6.4351 | 24.7232 | 93.54% | 1 | 4 | 54.9% | 0% | 0 | 0.021125 | 1 | 2.4388 | 0.051522 | Low | Low | Medium | 2320 | 2361 | 0.021125 | 26.4712
WALDO 0402CB | WALDO 0402 | EAST BAY | 3.0716 | 10 | 16.14% | 2 | 4 | 59.8% | 0% | 0 | 0.010847 | 1 | 4.7456 | 0.051476 | Low | Low | High | 2321 | 2878 | 0.010847 | 26.4197
PEORIA 170184318 | PEORIA 1701 | YOSEMITE | 9.9103 | 10 | 99.97% | 1 | 8 | 100% | 0% | 0 | 0.049883 | 1 | 1.0313 | 0.051441 | Medium | Medium | Low | 2322 | 1682 | 0.049883 | 26.3682
MENDOCINO 110131322 | MENDOCINO 1101 | HUMBOLDT | 4.4175 | 35.3153 | 77.6% | 2 | 7 | 15.42% | 0% | 0 | 0.01894 | 1 | 2.7133 | 0.05139 | Low | Low | Medium | 2323 | 2452 | 0.01894 | 26.3168
HOOPA 110137202 | HOOPA 1101 | HUMBOLDT | 23.7883 | 81.2571 | 100% | 8 | 3 | 82.1% | 0% | 0 | 0.045151 | 1 | 1.1358 | 0.051283 | Medium | Medium | Low | 2324 | 1763 | 0.045151 | 26.2654
HOLLISTER 21064004 | HOLLISTER 2106 | CENTRAL COAST | 7.4093 | 64.8641 | 59.97% | 2 | 1 | 36.51% | 0% | 0 | 0.019101 | 1 | 2.6827 | 0.051242 | Low | Low | Medium | 2325 | 2439 | 0.019101 | 26.2141
RACETRACK 17032553 | RACETRACK 1703 | YOSEMITE | 1.2971 | 10 | 100% | 0 | 1 | 52.29% | 0% | 0 | 0.018242 | 1 | 2.8066 | 0.051198 | Low | Low | Medium | 2326 | 2481 | 0.018242 | 26.1629
SOLEDAD 21027048 | SOLEDAD 2102 | CENTRAL COAST | 16.945 | 59.8739 | 88.98% | 0 | 0 | 48.94% | 0% | 0 | 0.022097 | 1 | 2.316 | 0.051176 | Medium | Medium | Medium | 2327 | 2332 | 0.022097 | 26.1117
UKIAH 1115CB | UKIAH 1115 | HUMBOLDT | 4.3061 | 10 | 64.92% | 0 | 1 | 67.93% | 0% | 0 | 0.018255 | 1 | 2.8014 | 0.051141 | Low | Low | Medium | 2328 | 2479 | 0.018255 | 26.0605
PIT NO 1 11013312 | PIT NO 1 1101 | NORTH VALLEY | 7.449 | 11.3541 | 100% | 0 | 1 | 82.66% | 0% | 0 | 0.032143 | 1 | 1.5906 | 0.051127 | Medium | Medium | Low | 2329 | 2041 | 0.032143 | 26.0093
CAL WATER 1102920714 | CAL WATER 1102 | KERN | 2.9688 | 76.5947 | 100% | 0 | 0 | 34.42% | 0% | 0 | 0.023426 | 1 | 2.1754 | 0.05096 | Medium | Medium | Low | 2330 | 2299 | 0.023426 | 25.9582
BIG RIVER 11012183 | BIG RIVER 1101 | HUMBOLDT | 2.6396 | 37.6233 | 33.84% | 1 | 4 | 100% | 0% | 0 | 0.022133 | 1 | 2.3018 | 0.050945 | Medium | Medium | Medium | 2331 | 2330 | 0.022133 | 25.9073
PURISIMA 1101Y80 | PURISIMA 1101 | LOS PADRES | 1.0399 | 27.8619 | 91.46% | 0 | 0 | 17.5% | 0% | 0 | 0.01334 | 1 | 3.819 | 0.050944 | Low | Low | High | 2332 | 2695 | 0.01334 | 25.8563
COTATI 110361736 | COTATI 1103 | SONOMA | 9.9372 | 78.8786 | 12.09% | 0 | 11 | 59.74% | 0% | 0 | 0.02142 | 1 | 2.3776 | 0.050928 | Low | Low | Medium | 2333 | 2352 | 0.02142 | 25.8054
MC KEE 1107XR010 | MC KEE 1107 | SAN JOSE | 2.6945 | 34.7956 | 81.62% | 0 | 0 | 19.75% | 0% | 0 | 0.013193 | 1 | 3.8599 | 0.050922 | Low | Low | High | 2334 | 2706 | 0.013193 | 25.7544
SAN JUSTO 110136902 | SAN JUSTO 1101 | CENTRAL COAST | 12.1218 | 14.481 | 44.84% | 5 | 5 | 82.09% | 0% | 0 | 0.024262 | 1 | 2.0985 | 0.050914 | Medium | Medium | Low | 2335 | 2269 | 0.024262 | 25.7035
LUCERNE 110693293 | LUCERNE 1106 | HUMBOLDT | 0.10086 | 10 | 100% | 0 | 0 | 83.34% | 0% | 0 | 0.024233 | 1 | 2.1005 | 0.050903 | Medium | Medium | Low | 2336 | 2271 | 0.024233 | 25.6526
BERKELEY F 1105BR166 | BERKELEY F 1105 | EAST BAY | 0.038193 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.0059 | 0.050857 | Low | Low | High | 2337 | 2735 | 0.012695 | 25.6017
ALTO 11201214 | ALTO 1120 | NORTH BAY | 2.1973 | 49.1379 | 3.101% | 3 | 5 | 48.69% | 0% | 0 | 0.017477 | 1 | 2.904 | 0.050753 | Low | Low | Medium | 2338 | 2514 | 0.017477 | 25.5508
HALSEY 11025739 | HALSEY 1102 | SIERRA | 6.6683 | 10 | 67.05% | 2 | 3 | 100% | 0% | 0 | 0.027187 | 1 | 1.8652 | 0.050708 | Medium | Medium | Low | 2339 | 2188 | 0.027187 | 25.5001
EL CERRITO G 1105BR164 | EL CERRITO G 1105 | EAST BAY | 0.056936 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.9936 | 0.0507 | Low | Low | High | 2340 | 2735 | 0.012695 | 25.4494
ZACA 1101Y72 | ZACA 1101 | LOS PADRES | 6.264 | 51.6717 | 31.17% | 0 | 0 | 97.2% | 23.49% | 0 | 0.039557 | 1 | 1.2802 | 0.050641 | Medium | Medium | Low | 2341 | 1869 | 0.039557 | 25.3987
FORT ROSS 1121CB | FORT ROSS 1121 | SONOMA | 13.6368 | 88.1189 | 22.5% | 13 | 2 | 100% | 0% | 0 | 0.036054 | 1 | 1.4046 | 0.050641 | Medium | Medium | Low | 2342 | 1931 | 0.036054 | 25.348
SAN RAMON 21077742 | SAN RAMON 2107 | MISSION | 0.0028424 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.9835 | 0.050572 | Low | Low | High | 2343 | 2735 | 0.012695 | 25.2974
HOLLISTER 2102855412 | HOLLISTER 2102 | CENTRAL COAST | 25.5091 | 59.8315 | 42.36% | 0 | 0 | 81.28% | 0% | 0 | 0.020819 | 1 | 2.4248 | 0.050482 | Low | Low | Medium | 2344 | 2377 | 0.020819 | 25.2468
DIAMOND SPRINGS 110699658 | DIAMOND SPRINGS 1106 | SIERRA | 5.0702 | 10 | 100% | 3 | 3 | 39.71% | 0% | 0 | 0.019909 | 1 | 2.5296 | 0.050364 | Low | Low | Medium | 2345 | 2413 | 0.019909 | 25.1963
MARTELL 110368192 | MARTELL 1103 | STOCKTON | 2.6279 | 35.8454 | 65.85% | 0 | 2 | 40.93% | 0% | 0 | 0.017124 | 1 | 2.9408 | 0.05036 | Low | Low | Medium | 2346 | 2524 | 0.017124 | 25.146
CASTRO VALLEY 1101MR359 | CASTRO VALLEY 1101 | MISSION | 0.81851 | 10 | 96.11% | 0 | 0 | 9.323% | 0% | 0 | 0.011325 | 1 | 4.4348 | 0.050223 | Low | Low | High | 2347 | 2846 | 0.011325 | 25.0956
DUNLAP 11027060 | DUNLAP 1102 | FRESNO | 17.8164 | 21.4268 | 100% | 3 | 11 | 100% | 0% | 0 | 0.045381 | 1 | 1.1057 | 0.050176 | Medium | Medium | Low | 2348 | 1757 | 0.045381 | 25.0454
JOLON 11027068 | JOLON 1102 | CENTRAL COAST | 3.8301 | 72.2303 | 100% | 0 | 0 | 100% | 0% | 0 | 0.042992 | 1 | 1.1665 | 0.05015 | Medium | Medium | Low | 2349 | 1798 | 0.042992 | 24.9952
TULUCAY 1101628 | TULUCAY 1101 | NORTH BAY | 4.4167 | 65.2777 | 26.9% | 0 | 1 | 50.38% | 0% | 0 | 0.014345 | 1 | 3.4912 | 0.050083 | Low | Low | High | 2350 | 2637 | 0.014345 | 24.9451
FROGTOWN 170232556 | FROGTOWN 1702 | STOCKTON | 4.3373 | 25.6533 | 79.39% | 0 | 0 | 69.35% | 0% | 0 | 0.025794 | 1 | 1.9369 | 0.049959 | Medium | Medium | Low | 2351 | 2221 | 0.025794 | 24.895
LAURELES 11112028 | LAURELES 1111 | CENTRAL COAST | 8.3353 | 36.2004 | 23.71% | 6 | 1 | 95.28% | 0% | 0 | 0.019345 | 1 | 2.5818 | 0.049946 | Low | Low | Medium | 2352 | 2428 | 0.019345 | 24.845
PERRY 1101W26 | PERRY 1101 | LOS PADRES | 2.7324 | 25.8267 | 23.85% | 3 | 0 | 100% | 0% | 0 | 0.017829 | 1 | 2.8 | 0.049922 | Low | Low | Medium | 2353 | 2497 | 0.017829 | 24.7951
HALF MOON BAY 11036018 | HALF MOON BAY 1103 | PENINSULA | 14.4915 | 43.0242 | 18.48% | 5 | 3 | 79.35% | 0% | 0 | 0.022185 | 1 | 2.2501 | 0.049917 | Medium | Medium | Medium | 2354 | 2328 | 0.022185 | 24.7452
PALMER 1101M84 | PALMER 1101 | LOS PADRES | 19.4244 | 65.3938 | 31.64% | 0 | 6 | 79.33% | 0% | 0 | 0.042007 | 1 | 1.1845 | 0.049756 | Medium | Medium | Low | 2355 | 1818 | 0.042007 | 24.6952
ROB ROY 21045304 | ROB ROY 2104 | CENTRAL COAST | 2.975 | 10 | 39.67% | 0 | 0 | 59.8% | 0% | 0 | 0.015337 | 1 | 3.2417 | 0.049718 | Low | Low | High | 2356 | 2595 | 0.015337 | 24.6455
MARTELL 1101CB | MARTELL 1101 | STOCKTON | 6.3498 | 10 | 65.48% | 1 | 2 | 48.33% | 0% | 0 | 0.01783 | 1 | 2.7857 | 0.049671 | Low | Low | Medium | 2357 | 2496 | 0.01783 | 24.5958
WYANDOTTE 110737472 | WYANDOTTE 1107 | NORTH VALLEY | 6.2847 | 13.7184 | 63.51% | 2 | 3 | 42.06% | 0% | 0 | 0.013447 | 1 | 3.6893 | 0.049612 | Low | Low | High | 2358 | 2687 | 0.013447 | 24.5461
LLAGAS 2101XR586 | LLAGAS 2101 | SAN JOSE | 4.744 | 52.8351 | 95.8% | 0 | 1 | 35.43% | 0% | 0 | 0.019912 | 1 | 2.4913 | 0.049608 | Low | Low | Medium | 2359 | 2412 | 0.019912 | 24.4965
ELK CREEK 11012212 | ELK CREEK 1101 | NORTH VALLEY | 10.0272 | 85.6358 | 100% | 0 | 1 | 29.79% | 0% | 0 | 0.02765 | 1 | 1.7915 | 0.049534 | Medium | Medium | Low | 2360 | 2172 | 0.02765 | 24.4469
SUNOL 110148180 | SUNOL 1101 | MISSION | 0.015663 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.7365 | 0.049509 | Medium | Medium | Low | 2361 | 2136 | 0.028512 | 24.3974
WYANDOTTE 11095607 | WYANDOTTE 1109 | NORTH VALLEY | 3.9588 | 10 | 93.75% | 0 | 0 | 59.06% | 0% | 0 | 0.018157 | 1 | 2.7246 | 0.049471 | Low | Low | Medium | 2362 | 2483 | 0.018157 | 24.3478
POSO MOUNTAIN 2103CB | POSO MOUNTAIN 2103 | KERN | 2.3192 | 10 | 26.74% | 0 | 0 | 100% | 0% | 0 | 0.017995 | 1 | 2.7452 | 0.0494 | Low | Low | Medium | 2363 | 2488 | 0.017995 | 24.2984
FRANKLIN 1104P146 | FRANKLIN 1104 | EAST BAY | 1.1753 | 10 | 98.96% | 0 | 2 | 31.88% | 0% | 0 | 0.015101 | 1 | 3.2686 | 0.049359 | Low | Low | High | 2364 | 2604 | 0.015101 | 24.249
ANDERSON 1101CB | ANDERSON 1101 | NORTH VALLEY | 1.7524 | 42.6703 | 99.35% | 0 | 2 | 19.42% | 0% | 0 | 0.016693 | 1 | 2.9503 | 0.049249 | Low | Low | Medium | 2365 | 2544 | 0.016693 | 24.1996
LINCOLN 11012310 | LINCOLN 1101 | SIERRA | 10.0776 | 10 | 72.42% | 0 | 6 | 56.39% | 0% | 0 | 0.016835 | 1 | 2.9232 | 0.049213 | Low | Low | Medium | 2366 | 2535 | 0.016835 | 24.1504
ELK CREEK 11012002 | ELK CREEK 1101 | NORTH VALLEY | 17.647 | 82.0427 | 100% | 0 | 0 | 58.67% | 0% | 0 | 0.045253 | 1 | 1.0865 | 0.049167 | Medium | Medium | Low | 2367 | 1760 | 0.045253 | 24.1012
RALSTON 1102CB | RALSTON 1102 | PENINSULA | 1.0812 | 10 | 71.25% | 0 | 0 | 25.36% | 0% | 0 | 0.014111 | 1 | 3.4704 | 0.04897 | Low | Low | High | 2368 | 2657 | 0.014111 | 24.052
CALAVERAS CEMENT 1101CB | CALAVERAS CEMENT 1101 | STOCKTON | 11.1338 | 14.2948 | 43.85% | 0 | 4 | 60.61% | 0% | 0 | 0.02038 | 1 | 2.3984 | 0.048881 | Low | Low | Medium | 2369 | 2389 | 0.02038 | 24.003
GUALALA 1111498 | GUALALA 1111 | HUMBOLDT | 2.9971 | 32.4304 | 1.089% | 0 | 12 | 100% | 0% | 0 | 0.024787 | 1 | 1.9715 | 0.048867 | Medium | Medium | Low | 2370 | 2250 | 0.024787 | 23.9541
ELECTRA 11024756 | ELECTRA 1102 | STOCKTON | 8.9008 | 26.6489 | 52.03% | 0 | 4 | 75.65% | 0% | 0 | 0.018513 | 1 | 2.637 | 0.048818 | Low | Low | Medium | 2371 | 2465 | 0.018513 | 23.9053
JESSUP 11013383 | JESSUP 1101 | NORTH VALLEY | 1.283 | 10 | 88.48% | 0 | 0 | 68.06% | 0% | 0 | 0.021667 | 1 | 2.2493 | 0.048737 | Low | Low | Medium | 2372 | 2347 | 0.021667 | 23.8564
ANTLER 11011378 | ANTLER 1101 | NORTH VALLEY | 23.3437 | 22.2502 | 87.11% | 6 | 14 | 92.94% | 12.19% | 1 | 0.058255 | 1 | 0.83529 | 0.04866 | Medium | Medium | Low | 2373 | 1591 | 0.058255 | 23.8077
CABRILLO 1104CB | CABRILLO 1104 | LOS PADRES | 4.9085 | 16.6076 | 47.38% | 0 | 1 | 28.73% | 0% | 0 | 0.012822 | 1 | 3.7934 | 0.048641 | Low | Low | High | 2374 | 2723 | 0.012822 | 23.7591
CLOVERDALE 1102262 | CLOVERDALE 1102 | SONOMA | 1.062 | 28.5735 | 25.58% | 2 | 0 | 19.75% | 47.85% | 0 | 0.020231 | 1 | 2.3861 | 0.048274 | Low | Low | Medium | 2375 | 2399 | 0.020231 | 23.7104
HOLLYWOOD 0401CB | HOLLYWOOD 0401 | EAST BAY | 2.9599 | 10 | 0% | 0 | 1 | 55.84% | 0% | 0 | 0.010899 | 1 | 4.4177 | 0.048147 | Low | Low | High | 2376 | 2875 | 0.010899 | 23.6621
DESCHUTES 11041582 | DESCHUTES 1104 | NORTH VALLEY | 6.3252 | 21.3729 | 99.66% | 0 | 1 | 41.84% | 0% | 0 | 0.020198 | 1 | 2.3806 | 0.048084 | Low | Low | Medium | 2377 | 2400 | 0.020198 | 23.614
GIRVAN 110280726 | GIRVAN 1102 | NORTH VALLEY | 5.9722 | 10 | 96.6% | 0 | 5 | 31.79% | 0% | 0 | 0.017957 | 1 | 2.6748 | 0.048032 | Low | Low | Medium | 2378 | 2491 | 0.017957 | 23.5659
PANORAMA 11021632 | PANORAMA 1102 | NORTH VALLEY | 8.5492 | 81.3182 | 43.52% | 0 | 3 | 100% | 0% | 0 | 0.040056 | 1 | 1.1987 | 0.048014 | Medium | Medium | Low | 2379 | 1855 | 0.040056 | 23.5179
SAN RAFAEL 1109CB | SAN RAFAEL 1109 | NORTH BAY | 0.026389 | 10 | 100% | 0 | 0 | 0.5374% | 0% | 0 | 0.013951 | 1 | 3.4403 | 0.047995 | Low | Low | High | 2380 | 2664 | 0.013951 | 23.4699
PEORIA 17019250 | PEORIA 1701 | YOSEMITE | 8.3271 | 28.832 | 87.97% | 0 | 3 | 100% | 0% | 0 | 0.035488 | 1 | 1.35 | 0.047908 | Medium | Medium | Low | 2381 | 1945 | 0.035488 | 23.4219
STAFFORD 1101CB | STAFFORD 1101 | NORTH BAY | 2.6576 | 10 | 64.37% | 5 | 3 | 21.89% | 0% | 0 | 0.016699 | 1 | 2.8654 | 0.047849 | Low | Low | Medium | 2382 | 2542 | 0.016699 | 23.374
HOPLAND 1101768 | HOPLAND 1101 | HUMBOLDT | 16.1128 | 49.9055 | 90.85% | 1 | 4 | 80.79% | 0% | 0 | 0.03582 | 1 | 1.3347 | 0.047808 | Medium | Medium | Low | 2383 | 1938 | 0.03582 | 23.3261
HALSEY 11015731 | HALSEY 1101 | SIERRA | 3.1252 | 10 | 52.17% | 0 | 1 | 100% | 0% | 0 | 0.019797 | 1 | 2.4133 | 0.047777 | Low | Low | Medium | 2384 | 2421 | 0.019797 | 23.2783
PEORIA 170413490 | PEORIA 1704 | YOSEMITE | 4.0441 | 23.9004 | 44.53% | 0 | 0 | 76.49% | 0% | 0 | 0.018107 | 1 | 2.6351 | 0.047714 | Low | Low | Medium | 2385 | 2484 | 0.018107 | 23.2305
OAKLAND J 1105CR256 | OAKLAND J 1105 | EAST BAY | 1.5352 | 10 | 0.8551% | 1 | 0 | 83.22% | 0% | 0 | 0.014281 | 1 | 3.3396 | 0.047692 | Low | Low | High | 2386 | 2641 | 0.014281 | 23.1828
CABRILLO 1103Y10 | CABRILLO 1103 | LOS PADRES | 4.0955 | 68.6545 | 11.89% | 0 | 1 | 43.98% | 0% | 0 | 0.012191 | 1 | 3.9107 | 0.047675 | Low | Low | High | 2387 | 2795 | 0.012191 | 23.1351
STAFFORD 11011298 | STAFFORD 1101 | NORTH BAY | 2.4249 | 10 | 52.95% | 1 | 0 | 36.21% | 0% | 0 | 0.015641 | 1 | 3.0475 | 0.047666 | Low | Low | Medium | 2388 | 2587 | 0.015641 | 23.0874
HICKS 2101XR162 | HICKS 2101 | SAN JOSE | 2.3563 | 22.9213 | 92.08% | 0 | 3 | 24.69% | 0% | 0 | 0.014813 | 1 | 3.2145 | 0.047617 | Low | Low | High | 2389 | 2616 | 0.014813 | 23.0398
TASSAJARA 2103CB | TASSAJARA 2103 | DIABLO | 1.7119 | 10 | 14.73% | 0 | 4 | 9.614% | 35.07% | 0 | 0.011177 | 1 | 4.2565 | 0.047577 | Low | Low | High | 2390 | 2857 | 0.011177 | 22.9922
REEDLEY 1104274990 | REEDLEY 1104 | FRESNO | 1.6643 | 56.3701 | 98.08% | 0 | 0 | 3.167% | 0% | 0 | 0.014809 | 1 | 3.2104 | 0.047544 | Low | Low | High | 2391 | 2617 | 0.014809 | 22.9446
MARIPOSA 210197142 | MARIPOSA 2101 | YOSEMITE | 4.6012 | 28.8872 | 53.68% | 0 | 6 | 100% | 0% | 0 | 0.025194 | 1 | 1.8808 | 0.047384 | Medium | Medium | Low | 2392 | 2237 | 0.025194 | 22.897
GARBERVILLE 1103CB | GARBERVILLE 1103 | HUMBOLDT | 1.3711 | 26.7284 | 20.19% | 10 | 1 | 61.39% | 0% | 0 | 0.017309 | 1 | 2.7282 | 0.04722 | Low | Low | Medium | 2393 | 2518 | 0.017309 | 22.8497
NOVATO 110455398 | NOVATO 1104 | NORTH BAY | 2.9149 | 74.0149 | 52.93% | 0 | 1 | 25.83% | 0% | 0 | 0.016828 | 1 | 2.8041 | 0.047187 | Low | Low | Medium | 2394 | 2536 | 0.016828 | 22.8024
GUALALA 1112CB | GUALALA 1112 | HUMBOLDT | 2.0288 | 40.2405 | 4.36% | 2 | 4 | 94.33% | 0% | 0 | 0.028665 | 1 | 1.6458 | 0.047177 | Medium | Medium | Low | 2395 | 2128 | 0.028665 | 22.7552
MONTICELLO 1101CB | MONTICELLO 1101 | NORTH BAY | 0.56293 | 10 | 41.7% | 0 | 0 | 100% | 0% | 0 | 0.020311 | 1 | 2.3219 | 0.047161 | Low | Low | Medium | 2396 | 2393 | 0.020311 | 22.7081
SNEATH LANE 110796530 | SNEATH LANE 1107 | PENINSULA | 0.71298 | 10 | 94.87% | 0 | 0 | 32.23% | 0% | 0 | 0.014063 | 1 | 3.3534 | 0.047158 | Low | Low | High | 2397 | 2663 | 0.014063 | 22.6609
OILFIELDS 1103N64 | OILFIELDS 1103 | CENTRAL COAST | 9.7922 | 31.0491 | 50.23% | 0 | 4 | 78.14% | 0% | 0 | 0.019257 | 1 | 2.4471 | 0.047124 | Low | Low | Medium | 2398 | 2432 | 0.019257 | 22.6137
LAURELES 11122768 | LAURELES 1112 | CENTRAL COAST | 6.6363 | 20.652 | 26.91% | 3 | 3 | 82.17% | 0% | 0 | 0.023337 | 1 | 2.0172 | 0.047076 | Medium | Medium | Low | 2399 | 2301 | 0.023337 | 22.5666
GREENBRAE 110388832 | GREENBRAE 1103 | NORTH BAY | 1.2167 | 10 | 6.453% | 0 | 0 | 88.72% | 0% | 0 | 0.011967 | 1 | 3.9315 | 0.047049 | Low | Low | High | 2400 | 2811 | 0.011967 | 22.5195
FLINT 1102CB | FLINT 1102 | SIERRA | 0.092844 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.014483 | 1 | 3.2339 | 0.046837 | Low | Low | High | 2401 | 2630 | 0.014483 | 22.4725
DIAMOND SPRINGS 1107CB | DIAMOND SPRINGS 1107 | SIERRA | 7.4424 | 10 | 84.55% | 2 | 3 | 62.03% | 0.42% | 0 | 0.019073 | 1 | 2.4518 | 0.046763 | Low | Low | Medium | 2402 | 2443 | 0.019073 | 22.4257
EL CERRITO G 1112BR196 | EL CERRITO G 1112 | EAST BAY | 0.02286 | 10 | 100% | 0 | 0 | 0.6321% | 0% | 0 | 0.010725 | 1 | 4.3473 | 0.046627 | Low | Low | High | 2403 | 2892 | 0.010725 | 22.3789
VIEJO 220255787 | VIEJO 2202 | CENTRAL COAST | 0.036656 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.6721 | 0.046619 | Low | Low | High | 2404 | 2735 | 0.012695 | 22.3323
SARATOGA 110413314 | SARATOGA 1104 | DE ANZA | 1.7714 | 10 | 52.47% | 2 | 5 | 15.54% | 0% | 0 | 0.010963 | 1 | 4.2395 | 0.046476 | Low | Low | High | 2405 | 2869 | 0.010963 | 22.2857
OAKLAND K 1101CR172 | OAKLAND K 1101 | EAST BAY | 0.63886 | 10 | 27.9% | 0 | 1 | 30.68% | 23.7% | 0 | 0.011998 | 1 | 3.8735 | 0.046474 | Low | Low | High | 2406 | 2808 | 0.011998 | 22.2392
PLACERVILLE 11118582 | PLACERVILLE 1111 | SIERRA | 7.7771 | 10 | 58.12% | 5 | 4 | 64.88% | 0% | 0 | 0.016693 | 1 | 2.7827 | 0.046451 | Low | Low | Medium | 2407 | 2543 | 0.016693 | 22.1927
LAURELES 1112438 | LAURELES 1112 | CENTRAL COAST | 5.2403 | 57.3236 | 0.9038% | 0 | 0 | 91.32% | 0% | 0 | 0.020992 | 1 | 2.2111 | 0.046416 | Low | Low | Low | 2408 | 2368 | 0.020992 | 22.1463
ROB ROY 210512586 | ROB ROY 2105 | CENTRAL COAST | 3.2869 | 10 | 13.9% | 3 | 2 | 50.3% | 0% | 0 | 0.015967 | 1 | 2.9067 | 0.046412 | Low | Low | Medium | 2409 | 2574 | 0.015967 | 22.0998
CLARK ROAD 110281296 | CLARK ROAD 1102 | NORTH VALLEY | 8.8512 | 53.0547 | 65.11% | 1 | 2 | 64.96% | 2.959% | 0 | 0.029241 | 1 | 1.5871 | 0.046408 | Medium | Medium | Low | 2410 | 2117 | 0.029241 | 22.0534
FAIRVIEW 220799096 | FAIRVIEW 2207 | DIABLO | 9.9116 | 14.1017 | 19.38% | 0 | 2 | 100% | 0% | 0 | 0.015926 | 1 | 2.9135 | 0.046399 | Low | Low | Medium | 2411 | 2575 | 0.015926 | 22.007
CLAY 110184572 | CLAY 1101 | STOCKTON | 1.3752 | 10 | 53.62% | 0 | 0 | 60.97% | 0% | 0 | 0.013356 | 1 | 3.473 | 0.046384 | Low | Low | High | 2412 | 2693 | 0.013356 | 21.9606
RIO DELL 11027124 | RIO DELL 1102 | HUMBOLDT | 0.67226 | 75.6649 | 100% | 0 | 0 | 100% | 0% | 0 | 0.043969 | 1 | 1.0549 | 0.046383 | Medium | Medium | Low | 2413 | 1779 | 0.043969 | 21.9142
ELK 11018779 | ELK 1101 | HUMBOLDT | 4.2672 | 21.5207 | 21.57% | 6 | 10 | 100% | 0% | 0 | 0.032081 | 1 | 1.4446 | 0.046343 | Medium | Medium | Low | 2414 | 2044 | 0.032081 | 21.8678
RALSTON 1101CB | RALSTON 1101 | PENINSULA | 5.2354 | 10 | 67.13% | 0 | 1 | 62.97% | 0% | 0 | 0.015521 | 1 | 2.985 | 0.04633 | Low | Low | Medium | 2415 | 2591 | 0.015521 | 21.8215
FORT BRAGG A 11014698 | FORT BRAGG A 1101 | HUMBOLDT | 7.9299 | 10 | 15.57% | 8 | 8 | 100% | 0% | 0 | 0.018863 | 1 | 2.4544 | 0.046298 | Low | Low | Medium | 2416 | 2454 | 0.018863 | 21.7752
CAMBRIA 1101V76 | CAMBRIA 1101 | LOS PADRES | 20.0895 | 13.7459 | 1.828% | 1 | 2 | 100% | 0% | 0 | 0.039572 | 1 | 1.1661 | 0.046144 | Medium | Medium | Low | 2417 | 1868 | 0.039572 | 21.7289
LLAGAS 2104XR294 | LLAGAS 2104 | SAN JOSE | 1.6348 | 49.1137 | 100% | 0 | 0 | 15.4% | 0% | 0 | 0.016162 | 1 | 2.8487 | 0.046041 | Low | Low | Medium | 2418 | 2566 | 0.016162 | 21.6827
KONOCTI 11081278 | KONOCTI 1108 | HUMBOLDT | 3.9864 | 24.8046 | 63% | 1 | 3 | 49.95% | 0% | 0 | 0.017559 | 1 | 2.6217 | 0.046036 | Low | Low | Medium | 2419 | 2508 | 0.017559 | 21.6367
SAN CARLOS 110479774 | SAN CARLOS 1104 | PENINSULA | 0.48017 | 10 | 65.63% | 1 | 1 | 30.37% | 0% | 0 | 0.011253 | 1 | 4.0855 | 0.045976 | Low | Low | High | 2420 | 2850 | 0.011253 | 21.5907
IGNACIO 1101CB | IGNACIO 1101 | NORTH BAY | 1.394 | 10 | 18.69% | 0 | 2 | 76.2% | 0% | 0 | 0.013891 | 1 | 3.3089 | 0.045965 | Low | Low | High | 2421 | 2668 | 0.013891 | 21.5447
OAKLAND J 1105CR150 | OAKLAND J 1105 | EAST BAY | 0.4695 | 10 | 10.02% | 0 | 1 | 100% | 0% | 0 | 0.014063 | 1 | 3.265 | 0.045915 | Low | Low | High | 2422 | 2662 | 0.014063 | 21.4987
AUBURN 1101CB | AUBURN 1101 | SIERRA | 3.1166 | 10 | 26.2% | 0 | 7 | 63.53% | 0% | 0 | 0.014449 | 1 | 3.1752 | 0.045877 | Low | Low | High | 2423 | 2632 | 0.014449 | 21.4528
FRUITLAND 114195324 | FRUITLAND 1141 | HUMBOLDT | 9.0462 | 63.96 | 12.78% | 11 | 1 | 100% | 0% | 0 | 0.027146 | 1 | 1.6852 | 0.045746 | Medium | Medium | Low | 2424 | 2189 | 0.027146 | 21.4069
FRENCH GULCH 1101CB | FRENCH GULCH 1101 | NORTH VALLEY | 2.2975 | 10 | 100% | 0 | 3 | 100% | 0% | 0 | 0.030308 | 1 | 1.5093 | 0.045746 | Medium | Medium | Low | 2425 | 2085 | 0.030308 | 21.3612
FITCH MOUNTAIN 1113583202 | FITCH MOUNTAIN 1113 | SONOMA | 3.5047 | 64.5439 | 56.95% | 1 | 2 | 36.51% | 0% | 0 | 0.018742 | 1 | 2.4393 | 0.045717 | Low | Low | Medium | 2426 | 2460 | 0.018742 | 21.3154
BIG MEADOWS 21012248 | BIG MEADOWS 2101 | NORTH VALLEY | 9.1467 | 42.3693 | 7.268% | 0 | 1 | 100% | 0% | 0 | 0.022222 | 1 | 2.056 | 0.045688 | Medium | Medium | Low | 2427 | 2324 | 0.022222 | 21.2697
UPPER LAKE 11011276 | UPPER LAKE 1101 | HUMBOLDT | 12.9332 | 76.2596 | 54.71% | 3 | 4 | 100% | 0% | 0 | 0.039478 | 1 | 1.1564 | 0.045653 | Medium | Medium | Low | 2428 | 1873 | 0.039478 | 21.224
RED BLUFF 11041566 | RED BLUFF 1104 | NORTH VALLEY | 11.3669 | 45.5787 | 76.5% | 0 | 1 | 74.23% | 0% | 0 | 0.03504 | 1 | 1.3025 | 0.045641 | Medium | Medium | Low | 2429 | 1952 | 0.03504 | 21.1784
CLARKSVILLE 210955666 | CLARKSVILLE 2109 | SIERRA | 0.61278 | 10 | 100% | 0 | 0 | 32.55% | 0% | 0 | 0.014709 | 1 | 3.1023 | 0.04563 | Low | Low | High | 2430 | 2626 | 0.014709 | 21.1327
POSO MOUNTAIN 21013990 | POSO MOUNTAIN 2101 | KERN | 4.4819 | 10 | 34.01% | 0 | 1 | 80.62% | 0% | 0 | 0.0161 | 1 | 2.8327 | 0.045606 | Low | Low | Medium | 2431 | 2568 | 0.0161 | 21.0871
CASTRO VALLEY 1106MR205 | CASTRO VALLEY 1106 | MISSION | 0.6704 | 10 | 69.55% | 0 | 0 | 12.34% | 11.35% | 0 | 0.01128 | 1 | 4.0306 | 0.045466 | Low | Low | High | 2432 | 2848 | 0.01128 | 21.0415
WYANDOTTE 110213044 | WYANDOTTE 1102 | NORTH VALLEY | 3.9523 | 10 | 53.49% | 0 | 6 | 66.87% | 0% | 0 | 0.018256 | 1 | 2.4807 | 0.045288 | Low | Low | Medium | 2433 | 2478 | 0.018256 | 20.996
LLAGAS 2107XR188 | LLAGAS 2107 | SAN JOSE | 2.7329 | 20.244 | 46.06% | 0 | 0 | 43.36% | 5.395% | 0 | 0.014067 | 1 | 3.2148 | 0.045223 | Low | Low | High | 2434 | 2660 | 0.014067 | 20.9507
UPPER LAKE 110175370 | UPPER LAKE 1101 | HUMBOLDT | 11.9492 | 35.1291 | 70.43% | 2 | 8 | 80.82% | 6.214% | 1 | 0.033449 | 1 | 1.3516 | 0.04521 | Medium | Medium | Low | 2435 | 1996 | 0.033449 | 20.9055
WOODWARD 210878448 | WOODWARD 2108 | FRESNO | 18.5469 | 31.6388 | 94.91% | 1 | 5 | 62.76% | 0% | 0 | 0.028087 | 1 | 1.6079 | 0.045161 | Medium | Medium | Low | 2436 | 2161 | 0.028087 | 20.8603
AUBERRY 1101R2579 | AUBERRY 1101 | FRESNO | 34.5067 | 14.4508 | 99.64% | 2 | 14 | 100% | 0% | 0 | 0.045338 | 1 | 0.99472 | 0.045098 | Medium | Medium | Low | 2437 | 1759 | 0.045338 | 20.8151
AUBURN 1102 | AUBURN 1102 | SIERRA | 0.025464 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.014483 | 1 | 3.1021 | 0.044929 | Low | Low | High | 2438 | 2631 | 0.014483 | 20.7701
MILPITAS 1109XR374 | MILPITAS 1109 | SAN JOSE | 0.65242 | 10 | 100% | 0 | 1 | 21.62% | 0% | 0 | 0.013479 | 1 | 3.3325 | 0.044919 | Low | Low | High | 2439 | 2683 | 0.013479 | 20.7251
RALSTON 11029126 | RALSTON 1102 | PENINSULA | 0.049841 | 10 | 100% | 0 | 1 | 2.638% | 0% | 0 | 0.012746 | 1 | 3.5205 | 0.044873 | Low | Low | High | 2440 | 2728 | 0.012746 | 20.6802
BIG MEADOWS 2101CB | BIG MEADOWS 2101 | NORTH VALLEY | 2.1059 | 66.4943 | 39.01% | 1 | 2 | 100% | 0% | 0 | 0.026855 | 1 | 1.6697 | 0.04484 | Medium | Medium | Low | 2441 | 2194 | 0.026855 | 20.6353
GARBERVILLE 110237054 | GARBERVILLE 1102 | HUMBOLDT | 8.8244 | 78.2726 | 22.8% | 0 | 2 | 95.32% | 0% | 0 | 0.04584 | 1 | 0.97592 | 0.044736 | Medium | Medium | Low | 2442 | 1750 | 0.04584 | 20.5905
MORRO BAY 110280174 | MORRO BAY 1102 | LOS PADRES | 3.4488 | 10 | 0% | 1 | 0 | 76.14% | 0% | 0 | 0.011588 | 1 | 3.8574 | 0.044702 | Low | Low | High | 2443 | 2831 | 0.011588 | 20.5458
DUNBAR 1101234 | DUNBAR 1101 | SONOMA | 3.2653 | 13.7421 | 32.63% | 2 | 8 | 50.44% | 15.33% | 0 | 0.01612 | 1 | 2.7726 | 0.044694 | Low | Low | Medium | 2444 | 2567 | 0.01612 | 20.5011
CLAY 110359714 | CLAY 1103 | STOCKTON | 4.4126 | 25.7757 | 4.31% | 0 | 1 | 95.22% | 0% | 0 | 0.014243 | 1 | 3.1342 | 0.044639 | Low | Low | High | 2445 | 2647 | 0.014243 | 20.4564
OTTER 110298036 | OTTER 1102 | CENTRAL COAST | 9.353 | 32.3159 | 7.526% | 0 | 13 | 100% | 0% | 0 | 0.034494 | 1 | 1.2921 | 0.04457 | Medium | Medium | Low | 2446 | 1963 | 0.034494 | 20.4117
VIEJO 220292792 | VIEJO 2202 | CENTRAL COAST | 0.01896 | 10 | 100% | 0 | 0 | 1.272% | 0% | 0 | 0.010794 | 1 | 4.1247 | 0.044521 | Low | Low | High | 2447 | 2883 | 0.010794 | 20.3671
CURTIS 17019230 | CURTIS 1701 | YOSEMITE | 2.2694 | 10 | 15.95% | 1 | 2 | 72.76% | 0% | 0 | 0.013303 | 1 | 3.3462 | 0.044513 | Low | Low | High | 2448 | 2699 | 0.013303 | 20.3226
MARIPOSA 2101CB | MARIPOSA 2101 | YOSEMITE | 6.8371 | 18.7213 | 60.25% | 1 | 4 | 63.95% | 0% | 0 | 0.019315 | 1 | 2.3032 | 0.044486 | Low | Low | Medium | 2449 | 2429 | 0.019315 | 20.2781
WHITMORE 1101002 | WHITMORE 1101 | NORTH VALLEY | 0.0042201 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.5578 | 0.044415 | Medium | Medium | Low | 2450 | 2136 | 0.028512 | 20.2336
COTATI 1102462 | COTATI 1102 | SONOMA | 3.3153 | 11.8938 | 22% | 1 | 2 | 84.56% | 0% | 0 | 0.015902 | 1 | 2.7902 | 0.044371 | Low | Low | Medium | 2451 | 2577 | 0.015902 | 20.1892
SAN MIGUEL 1104N60 | SAN MIGUEL 1104 | LOS PADRES | 7.3672 | 40.8154 | 100% | 0 | 1 | 83.22% | 0% | 0 | 0.030327 | 1 | 1.4627 | 0.044359 | Medium | Medium | Low | 2452 | 2083 | 0.030327 | 20.1448
HUMBOLDT BAY 11024724 | HUMBOLDT BAY 1102 | HUMBOLDT | 7.0458 | 41.454 | 0.8967% | 10 | 0 | 45.74% | 0% | 0 | 0.012021 | 1 | 3.6836 | 0.044279 | Low | Low | High | 2453 | 2807 | 0.012021 | 20.1005
ROSSMOOR 11018132 | ROSSMOOR 1101 | DIABLO | 2.3517 | 13.1594 | 38.14% | 0 | 7 | 64.04% | 0% | 0 | 0.014331 | 1 | 3.0841 | 0.044197 | Low | Low | High | 2454 | 2638 | 0.014331 | 20.0562
VINEYARD 2110CB | VINEYARD 2110 | MISSION | 5.8656 | 49.5436 | 17.49% | 1 | 0 | 52.96% | 0% | 0 | 0.013877 | 1 | 3.1806 | 0.044138 | Low | Low | High | 2455 | 2670 | 0.013877 | 20.012
BELMONT 11038958 | BELMONT 1103 | PENINSULA | 0.46477 | 10 | 49.35% | 0 | 4 | 26.9% | 0% | 0 | 0.011413 | 1 | 3.8671 | 0.044135 | Low | Low | High | 2456 | 2842 | 0.011413 | 19.9679
LAS AROMAS 04013342 | LAS AROMAS 0401 | DIABLO | 2.2911 | 10 | 3.001% | 3 | 0 | 100% | 0% | 0 | 0.013529 | 1 | 3.2617 | 0.044129 | Low | Low | High | 2457 | 2680 | 0.013529 | 19.9237
WYANDOTTE 11102590 | WYANDOTTE 1110 | NORTH VALLEY | 0.10676 | 10 | 95.21% | 0 | 0 | 17.59% | 0% | 0 | 0.012201 | 1 | 3.6162 | 0.044121 | Low | Low | High | 2458 | 2794 | 0.012201 | 19.8796
OAKLAND X 1101CR224 | OAKLAND X 1101 | EAST BAY | 0.53647 | 10 | 23.35% | 2 | 2 | 46.33% | 0% | 0 | 0.0096559 | 1 | 4.5636 | 0.044066 | Low | Low | High | 2459 | 2944 | 0.0096559 | 19.8355
SHINGLE SPRINGS 1104CB | SHINGLE SPRINGS 1104 | SIERRA | 0.43321 | 10 | 56.49% | 2 | 0 | 18.41% | 23.01% | 0 | 0.013336 | 1 | 3.3035 | 0.044055 | Low | Low | High | 2460 | 2696 | 0.013336 | 19.7914
FITCH MOUNTAIN 1113352 | FITCH MOUNTAIN 1113 | SONOMA | 7.3048 | 34.6273 | 40.22% | 1 | 0 | 61.07% | 0% | 0 | 0.016355 | 1 | 2.6925 | 0.044035 | Low | Low | Medium | 2461 | 2557 | 0.016355 | 19.7474
KERCKHOFF 1101R308 | KERCKHOFF 1101 | YOSEMITE | 3.8623 | 40.5798 | 35.11% | 0 | 3 | 100% | 0% | 0 | 0.022056 | 1 | 1.9946 | 0.043992 | Medium | Medium | Low | 2462 | 2334 | 0.022056 | 19.7033
TYLER 11051704 | TYLER 1105 | NORTH VALLEY | 12.5832 | 29.6218 | 100% | 0 | 8 | 27.35% | 0% | 0 | 0.024427 | 1 | 1.7997 | 0.043962 | Medium | Medium | Low | 2463 | 2264 | 0.024427 | 19.6593
OLETA 11021228 | OLETA 1102 | STOCKTON | 8.954 | 36.1723 | 96.93% | 0 | 0 | 20.75% | 0% | 0 | 0.019803 | 1 | 2.2184 | 0.043932 | Low | Low | Low | 2464 | 2419 | 0.019803 | 19.6154
ALHAMBRA 110581514 | ALHAMBRA 1105 | DIABLO | 2.5203 | 17.3445 | 21.67% | 2 | 3 | 52.7% | 0% | 0 | 0.014173 | 1 | 3.0995 | 0.043928 | Low | Low | High | 2465 | 2654 | 0.014173 | 19.5714
APPLE HILL 210289934 | APPLE HILL 2102 | SIERRA | 5.6225 | 10 | 91.39% | 0 | 0 | 100% | 0% | 0 | 0.030296 | 1 | 1.4475 | 0.043854 | Medium | Medium | Low | 2466 | 2087 | 0.030296 | 19.5275
EL CERRITO G 1110CB | EL CERRITO G 1110 | EAST BAY | 1.4466 | 10 | 13.89% | 0 | 3 | 52.88% | 0% | 0 | 0.0094866 | 1 | 4.6174 | 0.043803 | Low | Low | High | 2467 | 2952 | 0.0094866 | 19.4837
HIGGINS 1107CB | HIGGINS 1107 | SIERRA | 4.6439 | 10 | 81.31% | 3 | 3 | 24.48% | 0% | 0 | 0.012908 | 1 | 3.3796 | 0.043625 | Low | Low | High | 2468 | 2718 | 0.012908 | 19.4399
BASALT 11065030 | BASALT 1106 | NORTH BAY | 3.3103 | 53.7565 | 71.04% | 0 | 0 | 20.61% | 0% | 0 | 0.013874 | 1 | 3.1305 | 0.043433 | Low | Low | High | 2469 | 2671 | 0.013874 | 19.3962
DEL MONTE 21049096 | DEL MONTE 2104 | CENTRAL COAST | 2.1074 | 10 | 10.71% | 2 | 5 | 31.81% | 0% | 0 | 0.011931 | 1 | 3.6328 | 0.043344 | Low | Low | High | 2470 | 2813 | 0.011931 | 19.3528
EDES 1112CR306 | EDES 1112 | EAST BAY | 1.0069 | 10 | 0% | 3 | 0 | 100% | 0% | 0 | 0.013203 | 1 | 3.2812 | 0.043321 | Low | Low | High | 2471 | 2704 | 0.013203 | 19.3095
LOS OSITOS 21037468 | LOS OSITOS 2103 | CENTRAL COAST | 1.0746 | 71.3986 | 100% | 0 | 0 | 13.23% | 0% | 0 | 0.018377 | 1 | 2.3508 | 0.043201 | Low | Low | Medium | 2472 | 2472 | 0.018377 | 19.2661
CALPELLA 1101CB | CALPELLA 1101 | HUMBOLDT | 10.9748 | 13.9128 | 62.49% | 0 | 11 | 53.93% | 0% | 0 | 0.025545 | 1 | 1.6899 | 0.043167 | Medium | Medium | Low | 2473 | 2229 | 0.025545 | 19.2229
SAN LEANDRO U 1109CR284 | SAN LEANDRO U 1109 | MISSION | 0.93355 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.3989 | 0.043151 | Low | Low | High | 2474 | 2735 | 0.012695 | 19.1798
VALLEY VIEW 1105CB | VALLEY VIEW 1105 | EAST BAY | 0.87089 | 10 | 56.45% | 0 | 0 | 18.73% | 0% | 0 | 0.0089925 | 1 | 4.7951 | 0.04312 | Low | Low | High | 2475 | 2976 | 0.0089925 | 19.1366
BIG MEADOWS 21012016 | BIG MEADOWS 2101 | NORTH VALLEY | 0.0028416 | 10 | 100% | 0 | 0 | 0.06646% | 0% | 0 | 0.010666 | 1 | 4.0333 | 0.043017 | Low | Low | High | 2476 | 2897 | 0.010666 | 19.0935
FROGTOWN 1701CB | FROGTOWN 1701 | STOCKTON | 9.8066 | 35.2796 | 29.68% | 0 | 4 | 86.99% | 0% | 0 | 0.018301 | 1 | 2.3489 | 0.042988 | Low | Low | Medium | 2477 | 2475 | 0.018301 | 19.0505
CAROLANDS 0404 | CAROLANDS 0404 | PENINSULA | 0.066741 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.3793 | 0.042901 | Low | Low | High | 2478 | 2732 | 0.012695 | 19.0075
FRUITLAND 114137410 | FRUITLAND 1141 | HUMBOLDT | 3.8197 | 75.1023 | 57.88% | 10 | 0 | 69.23% | 0% | 0 | 0.034236 | 1 | 1.2527 | 0.042886 | Medium | Medium | Low | 2479 | 1967 | 0.034236 | 18.9646
SNEATH LANE 11071277 | SNEATH LANE 1107 | PENINSULA | 0.25243 | 10 | 100% | 0 | 1 | 11.7% | 0% | 0 | 0.012219 | 1 | 3.504 | 0.042815 | Low | Low | High | 2480 | 2792 | 0.012219 | 18.9217
PEORIA 1704CB | PEORIA 1704 | YOSEMITE | 8.3627 | 39.95 | 39.21% | 0 | 3 | 93.61% | 0% | 0 | 0.021324 | 1 | 2.0061 | 0.042779 | Low | Low | Low | 2481 | 2356 | 0.021324 | 18.8789
BELL 1108CB | BELL 1108 | SIERRA | 4.1507 | 10 | 64.56% | 0 | 6 | 33.13% | 0% | 0 | 0.016334 | 1 | 2.6182 | 0.042766 | Low | Low | Medium | 2482 | 2558 | 0.016334 | 18.8361
WHITMORE 1101CB | WHITMORE 1101 | NORTH VALLEY | 5.8976 | 20.259 | 68.5% | 1 | 0 | 100% | 0% | 0 | 0.027347 | 1 | 1.5637 | 0.042762 | Medium | Medium | Low | 2483 | 2183 | 0.027347 | 18.7933
UKIAH 1114822 | UKIAH 1114 | HUMBOLDT | 1.3145 | 67.0871 | 100% | 0 | 3 | 9.397% | 0% | 0 | 0.018289 | 1 | 2.3374 | 0.042749 | Low | Low | Medium | 2484 | 2476 | 0.018289 | 18.7506
WILLITS 110434006 | WILLITS 1104 | HUMBOLDT | 3.7731 | 21.9583 | 31.14% | 0 | 7 | 66.96% | 0% | 0 | 0.016864 | 1 | 2.5304 | 0.042672 | Low | Low | Medium | 2485 | 2533 | 0.016864 | 18.7078
CASTRO VALLEY 1108MR341 | CASTRO VALLEY 1108 | MISSION | 2.4534 | 10 | 13.13% | 0 | 1 | 77.41% | 2.031% | 0 | 0.011918 | 1 | 3.5792 | 0.042656 | Low | Low | High | 2486 | 2814 | 0.011918 | 18.6652
WYANDOTTE 110313018 | WYANDOTTE 1103 | NORTH VALLEY | 0.12548 | 10 | 100% | 0 | 0 | 7.599% | 0% | 0 | 0.011492 | 1 | 3.697 | 0.042487 | Low | Low | High | 2487 | 2835 | 0.011492 | 18.6225
SWIFT 2109XR300 | SWIFT 2109 | SAN JOSE | 0.30955 | 10 | 37.52% | 0 | 0 | 37.32% | 0% | 0 | 0.0092647 | 1 | 4.5685 | 0.042326 | Low | Low | High | 2488 | 2967 | 0.0092647 | 18.58
HARRIS 11082062 | HARRIS 1108 | HUMBOLDT | 2.3961 | 14.4145 | 20.24% | 1 | 5 | 45.88% | 0% | 0 | 0.010144 | 1 | 4.1719 | 0.042318 | Low | Low | High | 2489 | 2922 | 0.010144 | 18.5377
VIEJO 2204CB | VIEJO 2204 | CENTRAL COAST | 2.2166 | 10 | 31.01% | 10 | 1 | 54.6% | 0% | 0 | 0.013845 | 1 | 3.0559 | 0.04231 | Low | Low | Medium | 2490 | 2673 | 0.013845 | 18.4954
PANOCHE 11034008 | PANOCHE 1103 | YOSEMITE | 35.3708 | 69.547 | 99.82% | 0 | 2 | 100% | 0% | 0 | 0.064167 | 1 | 0.65772 | 0.042204 | High | High | Low | 2491 | 1524 | 0.064167 | 18.4531
JAMESON 11059472 | JAMESON 1105 | SACRAMENTO | 2.8377 | 36.7552 | 61.91% | 0 | 2 | 38.64% | 0% | 0 | 0.016315 | 1 | 2.585 | 0.042175 | Low | Low | Medium | 2492 | 2559 | 0.016315 | 18.4109
HATTON 1102CB | HATTON 1102 | CENTRAL COAST | 2.1206 | 10 | 0.1341% | 1 | 3 | 45.47% | 0% | 0 | 0.013538 | 1 | 3.1114 | 0.042121 | Low | Low | High | 2493 | 2679 | 0.013538 | 18.3687
MESA 1103M68 | MESA 1103 | LOS PADRES | 0.22844 | 10 | 100% | 0 | 0 | 7.509% | 0% | 0 | 0.013101 | 1 | 3.2134 | 0.042099 | Low | Low | High | 2494 | 2712 | 0.013101 | 18.3266
CURTIS 170349746 | CURTIS 1703 | YOSEMITE | 0.37395 | 10 | 15.4% | 0 | 1 | 100% | 0% | 0 | 0.014691 | 1 | 2.8626 | 0.042055 | Low | Low | Medium | 2495 | 2628 | 0.014691 | 18.2845
FRENCH GULCH 11012905 | FRENCH GULCH 1101 | NORTH VALLEY | 9.7071 | 49.4271 | 100% | 1 | 0 | 100% | 0% | 0 | 0.037487 | 1 | 1.1218 | 0.042053 | Medium | Medium | Low | 2496 | 1905 | 0.037487 | 18.2424
BELL 110880680 | BELL 1108 | SIERRA | 1.2687 | 10 | 46.62% | 0 | 0 | 71.23% | 0% | 0 | 0.015926 | 1 | 2.6403 | 0.042048 | Low | Low | Medium | 2497 | 2576 | 0.015926 | 18.2004
MARTELL 110299214 | MARTELL 1102 | STOCKTON | 0.5909 | 10 | 69.1% | 1 | 4 | 29.13% | 0% | 0 | 0.013885 | 1 | 3.016 | 0.041876 | Low | Low | Medium | 2498 | 2669 | 0.013885 | 18.1583
WYANDOTTE 1105CB | WYANDOTTE 1105 | NORTH VALLEY | 12.987 | 37.2024 | 0% | 0 | 0 | 96.35% | 0.5289% | 1 | 0.016922 | 1 | 2.4689 | 0.041778 | Low | Low | Medium | 2499 | 2531 | 0.016922 | 18.1164
FRENCH GULCH 11022902 | FRENCH GULCH 1102 | NORTH VALLEY | 6.9875 | 84.5854 | 100% | 0 | 4 | 100% | 0% | 0 | 0.057283 | 1 | 0.72881 | 0.041748 | Medium | Medium | Low | 2500 | 1602 | 0.057283 | 18.0747
PERRY 1101W10 | PERRY 1101 | LOS PADRES | 1.7167 | 22.2223 | 1.272% | 0 | 2 | 91.87% | 0% | 0 | 0.013398 | 1 | 3.1157 | 0.041744 | Low | Low | High | 2501 | 2690 | 0.013398 | 18.0329
FORT ROSS 112137326 | FORT ROSS 1121 | SONOMA | 5.1708 | 13.0882 | 4.203% | 4 | 1 | 100% | 0% | 0 | 0.031597 | 1 | 1.3203 | 0.04172 | Medium | Medium | Low | 2502 | 2058 | 0.031597 | 17.9912
MORRO BAY 1101 | MORRO BAY 1101 | LOS PADRES | 0.0056924 | 70 | 100% | 0 | 0 | 9.555% | 0% | 0 | 0.017559 | 1 | 2.3749 | 0.041701 | Low | Low | Medium | 2503 | 2509 | 0.017559 | 17.9494
CAYETANO 2111CB | CAYETANO 2111 | MISSION | 5.2576 | 70.3707 | 27.25% | 0 | 1 | 45% | 0% | 0 | 0.014119 | 1 | 2.9536 | 0.041701 | Low | Low | Medium | 2504 | 2656 | 0.014119 | 17.9077
EDES 1112CR100 | EDES 1112 | EAST BAY | 3.3566 | 10 | 0% | 1 | 0 | 100% | 0% | 0 | 0.012862 | 1 | 3.2337 | 0.041593 | Low | Low | High | 2505 | 2721 | 0.012862 | 17.866
HALF MOON BAY 11039112 | HALF MOON BAY 1103 | PENINSULA | 3.4704 | 36.5949 | 39.16% | 3 | 0 | 43.21% | 0% | 0 | 0.012394 | 1 | 3.3557 | 0.041589 | Low | Low | High | 2506 | 2777 | 0.012394 | 17.8244
DOLAN ROAD 11013012 | DOLAN ROAD 1101 | CENTRAL COAST | 2.5496 | 10 | 65.12% | 1 | 1 | 12.08% | 0% | 0 | 0.010669 | 1 | 3.8845 | 0.041444 | Low | Low | High | 2507 | 2896 | 0.010669 | 17.7829
LAYTONVILLE 11022502 | LAYTONVILLE 1102 | HUMBOLDT | 17.8026 | 72.9803 | 99.59% | 0 | 9 | 100% | 0% | 0 | 0.051556 | 1 | 0.80349 | 0.041424 | Medium | Medium | Low | 2508 | 1666 | 0.051556 | 17.7414
PUTAH CREEK 11028352 | PUTAH CREEK 1102 | SACRAMENTO | 4.7179 | 43.9192 | 97.12% | 0 | 4 | 40.06% | 0% | 0 | 0.021102 | 1 | 1.961 | 0.041381 | Low | Low | Low | 2509 | 2363 | 0.021102 | 17.7
OTTER 110263868 | OTTER 1102 | CENTRAL COAST | 15.8742 | 30.1739 | 15.67% | 12 | 5 | 100% | 0% | 0 | 0.031617 | 1 | 1.3086 | 0.041374 | Medium | Medium | Low | 2510 | 2057 | 0.031617 | 17.6586
OLEMA 110175686 | OLEMA 1101 | NORTH BAY | 3.5949 | 80.3245 | 25.14% | 0 | 0 | 69.82% | 0% | 0 | 0.021165 | 1 | 1.9507 | 0.041286 | Low | Low | Low | 2511 | 2359 | 0.021165 | 17.6172
KONOCTI 1102CB | KONOCTI 1102 | HUMBOLDT | 6.3926 | 38.5127 | 58.33% | 0 | 0 | 42.97% | 1.842% | 0 | 0.01654 | 1 | 2.4961 | 0.041284 | Low | Low | Medium | 2512 | 2548 | 0.01654 | 17.5759
RACETRACK 170310850 | RACETRACK 1703 | YOSEMITE | 0.060314 | 10 | 0% | 0 | 0 | 95.5% | 0% | 0 | 0.012143 | 1 | 3.3993 | 0.041276 | Low | Low | High | 2513 | 2798 | 0.012143 | 17.5347
POINT ARENA 1101CB | POINT ARENA 1101 | HUMBOLDT | 2.4683 | 40.0153 | 0% | 3 | 1 | 100% | 0% | 0 | 0.016501 | 1 | 2.4898 | 0.041084 | Low | Low | Medium | 2514 | 2551 | 0.016501 | 17.4934
LAS GALLINAS A 1105904 | LAS GALLINAS A 1105 | NORTH BAY | 2.5108 | 10 | 36.59% | 0 | 1 | 34.95% | 0% | 0 | 0.010466 | 1 | 3.9244 | 0.041073 | Low | Low | High | 2515 | 2906 | 0.010466 | 17.4523
LUCERNE 110647198 | LUCERNE 1106 | HUMBOLDT | 3.6836 | 20.6629 | 59.47% | 1 | 7 | 65.28% | 0% | 0 | 0.018382 | 1 | 2.2339 | 0.041063 | Low | Low | Medium | 2516 | 2471 | 0.018382 | 17.4112
SAN RAFAEL 1106910 | SAN RAFAEL 1106 | NORTH BAY | 1.5306 | 10 | 41.18% | 0 | 1 | 20.8% | 0% | 0 | 0.010777 | 1 | 3.8096 | 0.041054 | Low | Low | High | 2517 | 2885 | 0.010777 | 17.3702
MESA 1101M86 | MESA 1101 | LOS PADRES | 10.0922 | 14.4649 | 78% | 0 | 7 | 48.4% | 0% | 0 | 0.019529 | 1 | 2.0981 | 0.040973 | Low | Low | Low | 2518 | 2424 | 0.019529 | 17.3291
CALPELLA 1101 | CALPELLA 1101 | HUMBOLDT | 0.0052324 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.4352 | 0.040921 | Medium | Medium | Low | 2519 | 2136 | 0.028512 | 17.2881
HATTON 110137088 | HATTON 1101 | CENTRAL COAST | 4.1243 | 13.8122 | 55.58% | 4 | 4 | 48.38% | 0% | 0 | 0.014072 | 1 | 2.9011 | 0.040823 | Low | Low | Medium | 2520 | 2659 | 0.014072 | 17.2472
TOCALOMA 0241CB | TOCALOMA 0241 | NORTH BAY | 0.031239 | 60 | 0% | 0 | 0 | 100% | 0% | 0 | 0.017781 | 1 | 2.2908 | 0.040732 | Low | Low | Medium | 2521 | 2499 | 0.017781 | 17.2064
POINT MORETTI 1101CB | POINT MORETTI 1101 | CENTRAL COAST | 0.028582 | 13.6525 | 6.641% | 0 | 0 | 100% | 6.641% | 0 | 0.015281 | 1 | 2.6605 | 0.040655 | Low | Low | Medium | 2522 | 2598 | 0.015281 | 17.1657
ROB ROY 210512474 | ROB ROY 2105 | CENTRAL COAST | 2.374 | 10 | 59.61% | 0 | 1 | 28.06% | 0% | 0 | 0.013458 | 1 | 3.02 | 0.040644 | Low | Low | Medium | 2523 | 2685 | 0.013458 | 17.125
PEORIA 17046090 | PEORIA 1704 | YOSEMITE | 0.79834 | 10 | 4.922% | 0 | 1 | 100% | 0% | 0 | 0.01755 | 1 | 2.3134 | 0.0406 | Low | Low | Medium | 2524 | 2510 | 0.01755 | 17.0844
SAN LEANDRO U 1107MR560 | SAN LEANDRO U 1107 | MISSION | 0.061986 | 10 | 100% | 0 | 0 | 0.7828% | 0% | 0 | 0.010742 | 1 | 3.7725 | 0.040522 | Low | Low | High | 2525 | 2888 | 0.010742 | 17.0438
HIGGINS 1108CB | HIGGINS 1108 | SIERRA | 0.020411 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.189 | 0.040485 | Low | Low | High | 2526 | 2766 | 0.012695 | 17.0032
REDBUD 110244119 | REDBUD 1102 | HUMBOLDT | 0.66752 | 10 | 86.82% | 0 | 0 | 23.81% | 0% | 0 | 0.012119 | 1 | 3.3402 | 0.040479 | Low | Low | High | 2527 | 2801 | 0.012119 | 16.9628
SPENCE 11223078 | SPENCE 1122 | CENTRAL COAST | 9.9861 | 56.9194 | 40.99% | 1 | 2 | 62.29% | 0% | 0 | 0.0298 | 1 | 1.3582 | 0.040476 | Medium | Medium | Low | 2528 | 2104 | 0.0298 | 16.9223
BAY MEADOWS 2102 | BAY MEADOWS 2102 | PENINSULA | 0.027395 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.1881 | 0.040474 | Low | Low | High | 2529 | 2735 | 0.012695 | 16.8818
CAMPHORA 110177978 | CAMPHORA 1101 | CENTRAL COAST | 1.4665 | 83.8291 | 100% | 0 | 0 | 5.721% | 0% | 0 | 0.018555 | 1 | 2.1797 | 0.040444 | Low | Low | Low | 2530 | 2463 | 0.018555 | 16.8413
CABRILLO 1104Y22 | CABRILLO 1104 | LOS PADRES | 7.1091 | 12.8346 | 36.03% | 1 | 10 | 27.87% | 0% | 0 | 0.012091 | 1 | 3.3316 | 0.040283 | Low | Low | High | 2531 | 2803 | 0.012091 | 16.8009
PANORAMA 11021342 | PANORAMA 1102 | NORTH VALLEY | 11.6409 | 39.043 | 100% | 0 | 1 | 45.41% | 0% | 0 | 0.020716 | 1 | 1.9444 | 0.04028 | Low | Low | Low | 2532 | 2379 | 0.020716 | 16.7606
UPPER LAKE 1101412 | UPPER LAKE 1101 | HUMBOLDT | 11.536 | 63.7276 | 55.28% | 0 | 4 | 61.85% | 0% | 0 | 0.031441 | 1 | 1.2806 | 0.040263 | Medium | Medium | Low | 2533 | 2063 | 0.031441 | 16.7203
WOODWARD 2108R2860 | WOODWARD 2108 | FRESNO | 11.5924 | 40.5433 | 94.73% | 0 | 1 | 52.86% | 0% | 0 | 0.024579 | 1 | 1.6377 | 0.040253 | Medium | Medium | Low | 2534 | 2258 | 0.024579 | 16.6801
COTATI 1102CB | COTATI 1102 | SONOMA | 1.3007 | 52.8482 | 0.4591% | 0 | 0 | 64.8% | 0% | 0 | 0.013707 | 1 | 2.9311 | 0.040175 | Low | Low | Medium | 2535 | 2677 | 0.013707 | 16.6398
WILDWOOD 110198896 | WILDWOOD 1101 | NORTH VALLEY | 9.9251 | 71.2641 | 100% | 1 | 1 | 100% | 0% | 0 | 0.044142 | 1 | 0.90896 | 0.040124 | Medium | Medium | Low | 2536 | 1774 | 0.044142 | 16.5996
FLORENCE 0401CB | FLORENCE 0401 | EAST BAY | 1.7144 | 10 | 2.295% | 5 | 1 | 39.92% | 0% | 0 | 0.00887 | 1 | 4.5207 | 0.040099 | Low | Low | High | 2537 | 2983 | 0.00887 | 16.5595
MADISON 21017702 | MADISON 2101 | SACRAMENTO | 2.3216 | 70.1745 | 98.98% | 0 | 0 | 10.42% | 0% | 0 | 0.017585 | 1 | 2.2784 | 0.040066 | Low | Low | Medium | 2538 | 2505 | 0.017585 | 16.5194
OAKLAND K 1101CB | OAKLAND K 1101 | EAST BAY | 0.35314 | 10 | 0% | 1 | 1 | 14.81% | 24.18% | 0 | 0.0095124 | 1 | 4.2078 | 0.040027 | Low | Low | High | 2539 | 2950 | 0.0095124 | 16.4793
LLAGAS 2106XR146 | LLAGAS 2106 | SAN JOSE | 1.5959 | 59.0705 | 100% | 0 | 0 | 7.634% | 0% | 0 | 0.016009 | 1 | 2.4996 | 0.040015 | Low | Low | Medium | 2540 | 2569 | 0.016009 | 16.4393
HOPLAND 1101960 | HOPLAND 1101 | HUMBOLDT | 16.1295 | 41.2103 | 77.4% | 2 | 9 | 74.6% | 0% | 0 | 0.028177 | 1 | 1.4185 | 0.039967 | Medium | Medium | Low | 2541 | 2160 | 0.028177 | 16.3993
PACIFICA 110266732 | PACIFICA 1102 | PENINSULA | 1.1315 | 10 | 0% | 1 | 0 | 38.02% | 24.53% | 0 | 0.010334 | 1 | 3.8564 | 0.039854 | Low | Low | High | 2542 | 2913 | 0.010334 | 16.3593
HATTON 1102648928 | HATTON 1102 | CENTRAL COAST | 2.8842 | 29.9397 | 0% | 2 | 4 | 59.99% | 0% | 0 | 0.014193 | 1 | 2.8013 | 0.039758 | Low | Low | Medium | 2543 | 2653 | 0.014193 | 16.3195
FRANKLIN 1101P138 | FRANKLIN 1101 | EAST BAY | 1.4993 | 10 | 0% | 0 | 0 | 97.65% | 0% | 0 | 0.012403 | 1 | 3.2 | 0.03969 | Low | Low | High | 2544 | 2776 | 0.012403 | 16.2797
SOLEDAD 21017056 | SOLEDAD 2101 | CENTRAL COAST | 1.1515 | 59.0572 | 100% | 0 | 0 | 11.67% | 0% | 0 | 0.016656 | 1 | 2.3825 | 0.039684 | Low | Low | Medium | 2545 | 2545 | 0.016656 | 16.24
MORGAN HILL 2105XR494 | MORGAN HILL 2105 | SAN JOSE | 0.23352 | 25.7168 | 100% | 0 | 0 | 3.179% | 0% | 0 | 0.012233 | 1 | 3.2406 | 0.039642 | Low | Low | High | 2546 | 2791 | 0.012233 | 16.2004
COTATI 1104426 | COTATI 1104 | SONOMA | 2.1239 | 10 | 43.82% | 0 | 2 | 54.27% | 0% | 0 | 0.012029 | 1 | 3.2883 | 0.039554 | Low | Low | High | 2547 | 2806 | 0.012029 | 16.1607
GARBERVILLE 110256048 | GARBERVILLE 1102 | HUMBOLDT | 4.9695 | 84.598 | 7.194% | 2 | 1 | 100% | 0% | 0 | 0.030194 | 1 | 1.3096 | 0.039543 | Medium | Medium | Low | 2548 | 2092 | 0.030194 | 16.1212
KONOCTI 11084041 | KONOCTI 1108 | HUMBOLDT | 1.9081 | 10 | 99.47% | 0 | 0 | 40.69% | 0% | 0 | 0.015871 | 1 | 2.4887 | 0.039499 | Low | Low | Medium | 2549 | 2580 | 0.015871 | 16.0816
ROSSMOOR 1101L501R | ROSSMOOR 1101 | DIABLO | 0.055455 | 10 | 100% | 0 | 0 | 2.751% | 0% | 0 | 0.010953 | 1 | 3.5964 | 0.039392 | Low | Low | High | 2550 | 2871 | 0.010953 | 16.0421
SONOMA 1104914376 | SONOMA 1104 | SONOMA | 0.42319 | 32.6662 | 64.75% | 0 | 0 | 6.07% | 0% | 0 | 0.0098958 | 1 | 3.98 | 0.039385 | Low | Low | High | 2551 | 2934 | 0.0098958 | 16.0027
ANTLER 11011520 | ANTLER 1101 | NORTH VALLEY | 8.8735 | 30.8958 | 71.85% | 2 | 4 | 100% | 0% | 0 | 0.033121 | 1 | 1.188 | 0.039347 | Medium | Medium | Low | 2552 | 2006 | 0.033121 | 15.9633
MENDOCINO 1101450 | MENDOCINO 1101 | HUMBOLDT | 5.6815 | 36.3951 | 100% | 0 | 2 | 30.28% | 3.061% | 1 | 0.021431 | 1 | 1.8346 | 0.039318 | Low | Low | Low | 2553 | 2351 | 0.021431 | 15.924
SAN LUIS OBISPO 110742048 | SAN LUIS OBISPO 1107 | LOS PADRES | 0.025219 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0883 | 0.039207 | Low | Low | High | 2554 | 2735 | 0.012695 | 15.8847
DOLAN ROAD 110122158 | DOLAN ROAD 1101 | CENTRAL COAST | 1.2712 | 10 | 84.22% | 0 | 1 | 10.85% | 0% | 0 | 0.010653 | 1 | 3.6785 | 0.039186 | Low | Low | High | 2555 | 2899 | 0.010653 | 15.8455
SAN LUIS OBISPO 1107V08 | SAN LUIS OBISPO 1107 | LOS PADRES | 0.024874 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0856 | 0.039173 | Low | Low | High | 2556 | 2735 | 0.012695 | 15.8063
SAN LEANDRO U 11149838 | SAN LEANDRO U 1114 | MISSION | 1.9933 | 10 | 1.408% | 0 | 0 | 80.56% | 0% | 0 | 0.010593 | 1 | 3.6901 | 0.039087 | Low | Low | High | 2557 | 2902 | 0.010593 | 15.7671
NEWBURG 1131CB | NEWBURG 1131 | HUMBOLDT | 3.0239 | 26.9176 | 14.49% | 0 | 2 | 24.41% | 0% | 0 | 0.013392 | 1 | 2.916 | 0.03905 | Low | Low | Medium | 2558 | 2691 | 0.013392 | 15.728
PALMER 1101M82 | PALMER 1101 | LOS PADRES | 10.3483 | 48.0186 | 61.68% | 0 | 5 | 69.3% | 0% | 0 | 0.022153 | 1 | 1.7614 | 0.03902 | Medium | Medium | Low | 2559 | 2329 | 0.022153 | 15.689
DEL MONTE 21032204 | DEL MONTE 2103 | CENTRAL COAST | 0.36868 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0732 | 0.039015 | Low | Low | Medium | 2560 | 2735 | 0.012695 | 15.65
LOS OSITOS 21037082 | LOS OSITOS 2103 | CENTRAL COAST | 0.3792 | 71.4337 | 96.62% | 0 | 0 | 1.843% | 0% | 0 | 0.015988 | 1 | 2.4399 | 0.03901 | Low | Low | Medium | 2561 | 2571 | 0.015988 | 15.6109
FAIRMOUNT 0401CB | FAIRMOUNT 0401 | EAST BAY | 1.4849 | 10 | 0% | 0 | 2 | 25.81% | 0% | 0 | 0.0082593 | 1 | 4.7218 | 0.038999 | Low | Low | High | 2562 | 3005 | 0.0082593 | 15.5719
JESSUP 11031540 | JESSUP 1103 | NORTH VALLEY | 2.7435 | 22.0778 | 100% | 1 | 1 | 18.03% | 0% | 0 | 0.01631 | 1 | 2.3847 | 0.038895 | Low | Low | Medium | 2563 | 2560 | 0.01631 | 15.5329
ROB ROY 2105CB | ROB ROY 2105 | CENTRAL COAST | 0.78923 | 10 | 41.07% | 2 | 0 | 55.78% | 0% | 0 | 0.013414 | 1 | 2.895 | 0.038833 | Low | Low | Medium | 2564 | 2689 | 0.013414 | 15.494
PEABODY 210818182 | PEABODY 2108 | SACRAMENTO | 0.013085 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0555 | 0.03879 | Low | Low | Medium | 2565 | 2735 | 0.012695 | 15.4552
PUEBLO 2103694 | PUEBLO 2103 | NORTH BAY | 0.4502 | 10 | 100% | 0 | 0 | 9.445% | 0% | 0 | 0.011704 | 1 | 3.3141 | 0.038789 | Low | Low | High | 2566 | 2822 | 0.011704 | 15.4164
SAN LUIS OBISPO 1105CB | SAN LUIS OBISPO 1105 | LOS PADRES | 1.9887 | 39.9951 | 43.06% | 3 | 3 | 16.92% | 0% | 0 | 0.012254 | 1 | 3.1619 | 0.038746 | Low | Low | High | 2567 | 2790 | 0.012254 | 15.3776
POINT MORETTI 11015076 | POINT MORETTI 1101 | CENTRAL COAST | 7.1634 | 15.8606 | 16.59% | 11 | 1 | 79.19% | 0% | 0 | 0.018862 | 1 | 2.0481 | 0.03863 | Low | Low | Low | 2568 | 2455 | 0.018862 | 15.3389
NORTH BRANCH 110113496 | NORTH BRANCH 1101 | STOCKTON | 2.2189 | 10 | 62.08% | 0 | 0 | 44.24% | 0% | 0 | 0.012126 | 1 | 3.1825 | 0.03859 | Low | Low | High | 2569 | 2799 | 0.012126 | 15.3002
SOLEDAD 21013720 | SOLEDAD 2101 | CENTRAL COAST | 2.3505 | 51.9589 | 88.77% | 0 | 0 | 12.85% | 0% | 0 | 0.016725 | 1 | 2.3054 | 0.038559 | Low | Low | Medium | 2570 | 2539 | 0.016725 | 15.2617
BURNEY 11012402 | BURNEY 1101 | NORTH VALLEY | 1.4308 | 10 | 91.1% | 2 | 2 | 38.13% | 0% | 0 | 0.020105 | 1 | 1.914 | 0.038481 | Low | Low | Low | 2571 | 2404 | 0.020105 | 15.2231
BEAR VALLEY 2101CB | BEAR VALLEY 2101 | YOSEMITE | 18.7199 | 23.9906 | 55.73% | 0 | 6 | 100% | 0% | 0 | 0.047229 | 1 | 0.81463 | 0.038474 | Medium | Medium | Low | 2572 | 1722 | 0.047229 | 15.1846
DUNLAP 11027849F | DUNLAP 1102 | FRESNO | 8.6653 | 17.4771 | 100% | 3 | 9 | 100% | 0% | 0 | 0.037371 | 1 | 1.0288 | 0.038447 | Medium | Medium | Low | 2573 | 1907 | 0.037371 | 15.1461
SAN LEANDRO U 1114MR544 | SAN LEANDRO U 1114 | MISSION | 2.1618 | 10 | 45.25% | 0 | 0 | 34.37% | 0% | 0 | 0.010938 | 1 | 3.5146 | 0.038442 | Low | Low | High | 2574 | 2874 | 0.010938 | 15.1077
CAYUCOS 1102W18 | CAYUCOS 1102 | LOS PADRES | 1.9754 | 67.8899 | 46.98% | 0 | 0 | 8.859% | 14.04% | 0 | 0.015968 | 1 | 2.4056 | 0.038413 | Low | Low | Medium | 2575 | 2573 | 0.015968 | 15.0693
HIGGINS 1110 | HIGGINS 1110 | SIERRA | 0.035539 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0246 | 0.038398 | Low | Low | Medium | 2576 | 2735 | 0.012695 | 15.0308
PETALUMA C 1109270 | PETALUMA C 1109 | SONOMA | 1.61 | 25.9839 | 62.25% | 0 | 3 | 21.02% | 0% | 0 | 0.011438 | 1 | 3.35 | 0.038318 | Low | Low | High | 2577 | 2840 | 0.011438 | 14.9924
WILLOW CREEK 110191926 | WILLOW CREEK 1101 | HUMBOLDT | 5.6211 | 81.2548 | 100% | 2 | 0 | 52.92% | 0% | 0 | 0.033802 | 1 | 1.1327 | 0.038287 | Medium | Medium | Low | 2578 | 1981 | 0.033802 | 14.9541
TEMPLETON 2112R98 | TEMPLETON 2112 | LOS PADRES | 2.5848 | 57.8675 | 88.32% | 0 | 0 | 11.06% | 0% | 0 | 0.017037 | 1 | 2.2449 | 0.038247 | Low | Low | Medium | 2579 | 2527 | 0.017037 | 14.9158
WYANDOTTE 11091520 | WYANDOTTE 1109 | NORTH VALLEY | 4.1645 | 10 | 80.53% | 0 | 0 | 21.24% | 0% | 0 | 0.011222 | 1 | 3.4039 | 0.038199 | Low | Low | High | 2580 | 2852 | 0.011222 | 14.8776
ANDERSON 11011752 | ANDERSON 1101 | NORTH VALLEY | 3.4624 | 22.5175 | 29.42% | 0 | 0 | 74.73% | 0% | 0 | 0.015595 | 1 | 2.4433 | 0.038104 | Low | Low | Medium | 2581 | 2589 | 0.015595 | 14.8394
SUNOL 110111587 | SUNOL 1101 | MISSION | 0.25848 | 10 | 100% | 0 | 1 | 24.35% | 0% | 0 | 0.013849 | 1 | 2.7479 | 0.038054 | Low | Low | Medium | 2582 | 2672 | 0.013849 | 14.8013
LAYTONVILLE 1102220946 | LAYTONVILLE 1102 | HUMBOLDT | 0.040461 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.3334 | 0.038016 | Medium | Medium | Low | 2583 | 2136 | 0.028512 | 14.7632
SUNOL 11018721 | SUNOL 1101 | MISSION | 2.3818 | 51.7237 | 49.03% | 0 | 1 | 76.51% | 0% | 0 | 0.0231 | 1 | 1.6423 | 0.037937 | Medium | Medium | Low | 2584 | 2306 | 0.0231 | 14.7252
JESSUP 11019002 | JESSUP 1101 | NORTH VALLEY | 6.7893 | 16.4426 | 68.96% | 0 | 5 | 44.76% | 0% | 0 | 0.017028 | 1 | 2.2277 | 0.037935 | Low | Low | Low | 2585 | 2528 | 0.017028 | 14.6873
SOLEDAD 21027562 | SOLEDAD 2102 | CENTRAL COAST | 1.9641 | 22.7828 | 92.71% | 0 | 0 | 25.93% | 0% | 0 | 0.014154 | 1 | 2.6794 | 0.037924 | Low | Low | Medium | 2586 | 2655 | 0.014154 | 14.6493
FROGTOWN 170236870 | FROGTOWN 1702 | STOCKTON | 2.2467 | 10 | 88.34% | 0 | 2 | 72.13% | 0% | 0 | 0.020592 | 1 | 1.8354 | 0.037794 | Low | Low | Low | 2587 | 2383 | 0.020592 | 14.6114
SAN LUIS OBISPO 110788962 | SAN LUIS OBISPO 1107 | LOS PADRES | 1.6209 | 48.7477 | 22.43% | 0 | 1 | 40.61% | 0% | 0 | 0.012815 | 1 | 2.9485 | 0.037786 | Low | Low | Medium | 2588 | 2724 | 0.012815 | 14.5736
WOOD 0401CB | WOOD 0401 | EAST BAY | 0.4018 | 10 | 54.38% | 0 | 0 | 12.06% | 0% | 0 | 0.0082741 | 1 | 4.5612 | 0.037739 | Low | Low | High | 2589 | 3004 | 0.0082741 | 14.5358
RED BLUFF 1101 | RED BLUFF 1101 | NORTH VALLEY | 0.18711 | 22.4749 | 100% | 0 | 0 | 61.69% | 0% | 0 | 0.021308 | 1 | 1.7689 | 0.037691 | Low | Low | Low | 2590 | 2357 | 0.021308 | 14.4981
WYANDOTTE 110942650 | WYANDOTTE 1109 | NORTH VALLEY | 0.71686 | 10 | 44.77% | 0 | 0 | 27.21% | 0% | 0 | 0.0088907 | 1 | 4.2335 | 0.037638 | Low | Low | High | 2591 | 2982 | 0.0088907 | 14.4604
CARLOTTA 112142896 | CARLOTTA 1121 | HUMBOLDT | 2.183 | 31.2732 | 37.15% | 2 | 2 | 39.92% | 0% | 0 | 0.015245 | 1 | 2.4688 | 0.037636 | Low | Low | Medium | 2592 | 2601 | 0.015245 | 14.4228
CORONA 11034446 | CORONA 1103 | SONOMA | 0.968 | 50.7747 | 83.54% | 0 | 0 | 7.888% | 0% | 0 | 0.013274 | 1 | 2.8291 | 0.037555 | Low | Low | Medium | 2593 | 2700 | 0.013274 | 14.3851
CLOVERDALE 1102429006 | CLOVERDALE 1102 | SONOMA | 2.0089 | 22.4739 | 19.1% | 0 | 1 | 100% | 0% | 0 | 0.016467 | 1 | 2.2766 | 0.037488 | Low | Low | Medium | 2594 | 2554 | 0.016467 | 14.3476
MILPITAS 110962157 | MILPITAS 1109 | SAN JOSE | 0.044828 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.9508 | 0.037462 | Low | Low | Medium | 2595 | 2735 | 0.012695 | 14.3101
NARROWS 21022718 | NARROWS 2102 | SIERRA | 0.45209 | 10 | 82.65% | 0 | 1 | 6.234% | 0% | 0 | 0.010047 | 1 | 3.7245 | 0.037421 | Low | Low | High | 2596 | 2926 | 0.010047 | 14.2726
ANDERSON 11031600 | ANDERSON 1103 | NORTH VALLEY | 2.5631 | 13.0676 | 100% | 0 | 0 | 23.83% | 0% | 0 | 0.015715 | 1 | 2.3807 | 0.037413 | Low | Low | Medium | 2597 | 2585 | 0.015715 | 14.2352
OTTER 11022166 | OTTER 1102 | CENTRAL COAST | 4.0812 | 30.3358 | 3.172% | 4 | 2 | 100% | 0% | 0 | 0.027673 | 1 | 1.3506 | 0.037374 | Medium | Medium | Low | 2598 | 2171 | 0.027673 | 14.1978
GRASS VALLEY 1103 | GRASS VALLEY 1103 | SIERRA | 0.021115 | 10 | 19.87% | 0 | 0 | 100% | 0% | 0 | 0.014923 | 1 | 2.5027 | 0.037349 | Low | Low | Medium | 2599 | 2610 | 0.014923 | 14.1604
SAUSALITO 11011270 | SAUSALITO 1101 | NORTH BAY | 0.49678 | 64.5423 | 0% | 0 | 0 | 50.41% | 0% | 0 | 0.011233 | 1 | 3.3242 | 0.037341 | Low | Low | High | 2600 | 2851 | 0.011233 | 14.1231
MENLO 11029110 | MENLO 1102 | PENINSULA | 0.16148 | 10 | 87.04% | 1 | 0 | 1.751% | 0% | 0 | 0.0098849 | 1 | 3.7774 | 0.037339 | Low | Low | High | 2601 | 2935 | 0.0098849 | 14.0857
HICKS 2101XR548 | HICKS 2101 | SAN JOSE | 1.763 | 53.1133 | 61.37% | 0 | 0 | 20.35% | 0% | 0 | 0.012735 | 1 | 2.9304 | 0.037318 | Low | Low | Medium | 2602 | 2729 | 0.012735 | 14.0484
CORRAL 110214028 | CORRAL 1102 | STOCKTON | 3.2845 | 10 | 84.85% | 0 | 2 | 41.18% | 0% | 0 | 0.01476 | 1 | 2.5258 | 0.03728 | Low | Low | Medium | 2603 | 2621 | 0.01476 | 14.0111
WILLOW PASS 1101CB | WILLOW PASS 1101 | DIABLO | 0.46926 | 10 | 100% | 0 | 1 | 6.681% | 0% | 0 | 0.011627 | 1 | 3.2051 | 0.037265 | Low | Low | High | 2604 | 2828 | 0.011627 | 13.9738
NARROWS 210551582 | NARROWS 2105 | SIERRA | 9.5263 | 10 | 48.26% | 0 | 1 | 100% | 0% | 0 | 0.019181 | 1 | 1.9413 | 0.037237 | Low | Low | Low | 2605 | 2436 | 0.019181 | 13.9365
COTTONWOOD 11029026 | COTTONWOOD 1102 | NORTH VALLEY | 14.1835 | 17.7686 | 84.41% | 1 | 2 | 58.01% | 0% | 0 | 0.021122 | 1 | 1.7609 | 0.037192 | Low | Low | Low | 2606 | 2362 | 0.021122 | 13.8993
FORT ROSS 1121134 | FORT ROSS 1121 | SONOMA | 7.7066 | 23.2401 | 8.01% | 16 | 1 | 95.15% | 0% | 0 | 0.029926 | 1 | 1.2427 | 0.037189 | Medium | Medium | Low | 2607 | 2102 | 0.029926 | 13.8621
KONOCTI 11022293 | KONOCTI 1102 | HUMBOLDT | 0.16556 | 10 | 100% | 0 | 0 | 9.444% | 0% | 0 | 0.011704 | 1 | 3.1767 | 0.03718 | Low | Low | High | 2608 | 2823 | 0.011704 | 13.8249
JESSUP 1101CB | JESSUP 1101 | NORTH VALLEY | 1.1327 | 30.8343 | 100% | 0 | 0 | 19.43% | 0% | 0 | 0.01487 | 1 | 2.5003 | 0.037179 | Low | Low | Medium | 2609 | 2614 | 0.01487 | 13.7877
POSO MOUNTAIN 2104CB | POSO MOUNTAIN 2104 | KERN | 5.3916 | 10 | 6.227% | 0 | 6 | 72.59% | 0% | 0 | 0.013157 | 1 | 2.8181 | 0.037076 | Low | Low | Medium | 2610 | 2707 | 0.013157 | 13.7506
LUCERNE 110676850 | LUCERNE 1106 | HUMBOLDT | 2.0465 | 10 | 61.3% | 0 | 3 | 55.89% | 0% | 0 | 0.014386 | 1 | 2.5722 | 0.037005 | Low | Low | Medium | 2611 | 2635 | 0.014386 | 13.7135
COTATI 1102464 | COTATI 1102 | SONOMA | 1.2747 | 26.0788 | 66.97% | 0 | 1 | 15.73% | 0% | 0 | 0.012358 | 1 | 2.9928 | 0.036986 | Low | Low | Medium | 2612 | 2780 | 0.012358 | 13.6765
SYCAMORE CREEK 1109CB | SYCAMORE CREEK 1109 | NORTH VALLEY | 0.58228 | 10 | 100% | 0 | 0 | 6.6% | 0% | 0 | 0.011379 | 1 | 3.2447 | 0.036922 | Low | Low | High | 2613 | 2843 | 0.011379 | 13.6395
MORRO BAY 1102CB | MORRO BAY 1102 | LOS PADRES | 3.3958 | 10 | 1.002% | 0 | 0 | 71.82% | 0% | 0 | 0.011049 | 1 | 3.3405 | 0.036911 | Low | Low | High | 2614 | 2861 | 0.011049 | 13.6026
PEABODY 2106CB | PEABODY 2106 | SACRAMENTO | 0.58049 | 10 | 53.14% | 0 | 0 | 53.74% | 0% | 0 | 0.012385 | 1 | 2.9801 | 0.036907 | Low | Low | Medium | 2615 | 2778 | 0.012385 | 13.5657
NORTH BRANCH 1101CB | NORTH BRANCH 1101 | STOCKTON | 10.7662 | 27.7002 | 39.92% | 0 | 5 | 56% | 0% | 0 | 0.014214 | 1 | 2.5951 | 0.036887 | Low | Low | Medium | 2616 | 2650 | 0.014214 | 13.5287
JARVIS 1108MR368 | JARVIS 1108 | MISSION | 0.80128 | 10 | 39.98% | 0 | 0 | 23.87% | 0% | 0 | 0.0094416 | 1 | 3.9056 | 0.036875 | Low | Low | High | 2617 | 2958 | 0.0094416 | 13.4919
COARSEGOLD 210410030 | COARSEGOLD 2104 | YOSEMITE | 15.7445 | 10.7109 | 33.01% | 0 | 3 | 88.51% | 0% | 0 | 0.020603 | 1 | 1.786 | 0.036797 | Low | Low | Low | 2618 | 2382 | 0.020603 | 13.455
RIO DEL MAR 0401CB | RIO DEL MAR 0401 | CENTRAL COAST | 1.702 | 10 | 16.67% | 5 | 1 | 48.18% | 0% | 0 | 0.010828 | 1 | 3.3814 | 0.036613 | Low | Low | High | 2619 | 2882 | 0.010828 | 13.4182
HATTON 11029642 | HATTON 1102 | CENTRAL COAST | 1.1982 | 10 | 4.477% | 2 | 1 | 100% | 0% | 0 | 0.013798 | 1 | 2.6508 | 0.036576 | Low | Low | Medium | 2620 | 2674 | 0.013798 | 13.3816
RACETRACK 170310870 | RACETRACK 1703 | YOSEMITE | 1.0803 | 10 | 45.22% | 0 | 3 | 41.49% | 0% | 0 | 0.010943 | 1 | 3.3367 | 0.036514 | Low | Low | High | 2621 | 2873 | 0.010943 | 13.345
FITCH MOUNTAIN 11115060 | FITCH MOUNTAIN 1111 | SONOMA | 2.1624 | 43.6089 | 39.41% | 0 | 3 | 35.19% | 0% | 0 | 0.012308 | 1 | 2.9515 | 0.036326 | Low | Low | Medium | 2622 | 2784 | 0.012308 | 13.3085
KONOCTI 11084037 | KONOCTI 1108 | HUMBOLDT | 0.3878 | 10 | 100% | 0 | 0 | 22.52% | 0% | 0 | 0.013321 | 1 | 2.7262 | 0.036316 | Low | Low | Medium | 2623 | 2698 | 0.013321 | 13.2722
ELK 110191336 | ELK 1101 | HUMBOLDT | 7.8266 | 12.5917 | 0% | 14 | 5 | 92.25% | 0% | 0 | 0.020708 | 1 | 1.7508 | 0.036255 | Low | Low | Low | 2624 | 2380 | 0.020708 | 13.2358
OAKHURST 110311900 | OAKHURST 1103 | YOSEMITE | 0.064919 | 10 | 100% | 0 | 0 | 7.722% | 0% | 0 | 0.011506 | 1 | 3.147 | 0.03621 | Low | Low | High | 2625 | 2834 | 0.011506 | 13.1996
WISE 110163199 | WISE 1101 | SIERRA | 0.5708 | 42.4087 | 13.05% | 0 | 0 | 61.18% | 0% | 0 | 0.01197 | 1 | 3.0242 | 0.036199 | Low | Low | Medium | 2626 | 2810 | 0.01197 | 13.1634
WILLITS 1103696 | WILLITS 1103 | HUMBOLDT | 6.5774 | 41.2479 | 62.23% | 0 | 3 | 69.69% | 0% | 0 | 0.020487 | 1 | 1.7628 | 0.036115 | Low | Low | Low | 2627 | 2386 | 0.020487 | 13.1272
CHESTER 1102CB | CHESTER 1102 | NORTH VALLEY | 0.32002 | 10 | 100% | 0 | 0 | 10.17% | 0% | 0 | 0.01345 | 1 | 2.6792 | 0.036036 | Low | Low | Medium | 2628 | 2686 | 0.01345 | 13.0911
OILFIELDS 1103 | OILFIELDS 1103 | CENTRAL COAST | 0.020981 | 19.5696 | 17.4% | 0 | 0 | 100% | 0% | 0 | 0.015601 | 1 | 2.3018 | 0.035911 | Low | Low | Medium | 2629 | 2588 | 0.015601 | 13.055
EDENVALE 2107CB | EDENVALE 2107 | SAN JOSE | 0.73661 | 33.423 | 98.26% | 0 | 0 | 2.254% | 0% | 0 | 0.01259 | 1 | 2.8521 | 0.035908 | Low | Low | Medium | 2630 | 2770 | 0.01259 | 13.0191
SAN CARLOS 11048846 | SAN CARLOS 1104 | PENINSULA | 1.1188 | 10 | 42.43% | 0 | 1 | 25.48% | 0% | 0 | 0.0087545 | 1 | 4.0972 | 0.035869 | Low | Low | High | 2631 | 2986 | 0.0087545 | 12.9832
HALSEY 11022514 | HALSEY 1102 | SIERRA | 9.2843 | 10 | 42.43% | 1 | 2 | 47.49% | 0% | 0 | 0.012855 | 1 | 2.7818 | 0.035761 | Low | Low | Medium | 2632 | 2722 | 0.012855 | 12.9473
CLAY 1102CB | CLAY 1102 | STOCKTON | 1.1664 | 10 | 0% | 0 | 0 | 60.02% | 0% | 0 | 0.011126 | 1 | 3.2104 | 0.035721 | Low | Low | High | 2633 | 2860 | 0.011126 | 12.9116
MENDOCINO 110137462 | MENDOCINO 1101 | HUMBOLDT | 2.449 | 10 | 46.73% | 0 | 2 | 50.22% | 0% | 0 | 0.0135 | 1 | 2.6397 | 0.035636 | Low | Low | Medium | 2634 | 2682 | 0.0135 | 12.8759
HICKS 1116CB | HICKS 1116 | SAN JOSE | 1.3112 | 10 | 43.95% | 1 | 3 | 7.743% | 0% | 0 | 0.0089608 | 1 | 3.9753 | 0.035622 | Low | Low | High | 2635 | 2979 | 0.0089608 | 12.8402
CURTIS 170190120 | CURTIS 1701 | YOSEMITE | 2.5983 | 10 | 28.78% | 0 | 1 | 50.57% | 0% | 0 | 0.010044 | 1 | 3.5453 | 0.035611 | Low | Low | High | 2636 | 2927 | 0.010044 | 12.8046
DESCHUTES 1101CB | DESCHUTES 1101 | NORTH VALLEY | 4.1985 | 15.36 | 72.74% | 0 | 0 | 36.89% | 0% | 0 | 0.012752 | 1 | 2.792 | 0.035602 | Low | Low | Medium | 2637 | 2727 | 0.012752 | 12.769
TIDEWATER 210665866 | TIDEWATER 2106 | DIABLO | 4.2405 | 36.2821 | 12.3% | 0 | 0 | 47.54% | 0% | 0 | 0.0099699 | 1 | 3.5683 | 0.035576 | Low | Low | High | 2638 | 2929 | 0.0099699 | 12.7334
MORGAN HILL 2110XR326 | MORGAN HILL 2110 | SAN JOSE | 2.054 | 29.8956 | 63.47% | 0 | 2 | 9.633% | 0% | 0 | 0.013515 | 1 | 2.63 | 0.035544 | Low | Low | Medium | 2639 | 2681 | 0.013515 | 12.6978
BANGOR 110155206 | BANGOR 1101 | NORTH VALLEY | 2.9326 | 34.2156 | 61.32% | 1 | 0 | 28.49% | 0% | 0 | 0.012304 | 1 | 2.8829 | 0.03547 | Low | Low | Medium | 2640 | 2785 | 0.012304 | 12.6623
CEDAR CREEK 11011362 | CEDAR CREEK 1101 | NORTH VALLEY | 0.015515 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.2439 | 0.035466 | Medium | Medium | Low | 2641 | 2136 | 0.028512 | 12.6268
DUNBAR 1101160 | DUNBAR 1101 | SONOMA | 4.1387 | 21.8951 | 29.76% | 0 | 0 | 62.23% | 10.35% | 0 | 0.01425 | 1 | 2.486 | 0.035427 | Low | Low | Medium | 2642 | 2644 | 0.01425 | 12.5913
PEORIA 17013186 | PEORIA 1701 | YOSEMITE | 10.0751 | 10 | 99.94% | 1 | 2 | 100% | 0% | 0 | 0.030068 | 1 | 1.1773 | 0.035399 | Medium | Medium | Low | 2643 | 2098 | 0.030068 | 12.5559
FORT ORD 21069658 | FORT ORD 2106 | CENTRAL COAST | 0.097044 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.7847 | 0.035353 | Low | Low | Medium | 2644 | 2735 | 0.012695 | 12.5205
CHESTER 1101CB | CHESTER 1101 | NORTH VALLEY | 2.5695 | 10 | 96.88% | 0 | 0 | 31.91% | 0% | 0 | 0.01425 | 1 | 2.4772 | 0.035299 | Low | Low | Medium | 2645 | 2645 | 0.01425 | 12.4852
HATTON 11022070 | HATTON 1102 | CENTRAL COAST | 0.49418 | 10 | 29.42% | 0 | 3 | 25.81% | 0% | 0 | 0.010726 | 1 | 3.2805 | 0.035187 | Low | Low | High | 2646 | 2891 | 0.010726 | 12.4499
LUCERNE 1106CB | LUCERNE 1106 | HUMBOLDT | 2.483 | 10 | 34.76% | 1 | 7 | 68.8% | 0% | 0 | 0.01653 | 1 | 2.1266 | 0.035153 | Low | Low | Low | 2647 | 2549 | 0.01653 | 12.4147
CURTIS 170356972 | CURTIS 1703 | YOSEMITE | 8.4449 | 49.5291 | 11.99% | 0 | 2 | 100% | 0.5389% | 1 | 0.02188 | 1 | 1.6045 | 0.035106 | Medium | Medium | Low | 2648 | 2338 | 0.02188 | 12.3795
ELK 11011260 | ELK 1101 | HUMBOLDT | 15.6745 | 74.4455 | 25.71% | 10 | 4 | 100% | 0% | 0 | 0.043784 | 1 | 0.80153 | 0.035094 | Medium | Medium | Low | 2649 | 1780 | 0.043784 | 12.3444
PLACERVILLE 1109CB | PLACERVILLE 1109 | SIERRA | 0.020146 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.012961 | 1 | 2.6978 | 0.034966 | Low | Low | Medium | 2650 | 2716 | 0.012961 | 12.3093
ROSSMOOR 110192164 | ROSSMOOR 1101 | DIABLO | 0.25455 | 10 | 51.39% | 0 | 0 | 26.2% | 0% | 0 | 0.0092923 | 1 | 3.7629 | 0.034966 | Low | Low | High | 2651 | 2963 | 0.0092923 | 12.2743
ROSSMOOR 110676468 | ROSSMOOR 1106 | DIABLO | 1.5034 | 10 | 14.83% | 1 | 2 | 51.08% | 0% | 0 | 0.0093177 | 1 | 3.7505 | 0.034946 | Low | Low | High | 2652 | 2962 | 0.0093177 | 12.2394
FAIRVIEW 2207P150 | FAIRVIEW 2207 | DIABLO | 1.7182 | 19.1624 | 0% | 0 | 0 | 75.67% | 0% | 0 | 0.010614 | 1 | 3.2893 | 0.034913 | Low | Low | High | 2653 | 2900 | 0.010614 | 12.2044
GEYSERVILLE 110135492 | GEYSERVILLE 1101 | SONOMA | 8.4529 | 69.0353 | 85.9% | 0 | 0 | 39.22% | 0% | 0 | 0.020833 | 1 | 1.6734 | 0.034862 | Low | Low | Low | 2654 | 2376 | 0.020833 | 12.1695
WILLOW PASS 2107P500R | WILLOW PASS 2107 | DIABLO | 0.15832 | 10 | 100% | 0 | 0 | 4.986% | 0% | 0 | 0.011198 | 1 | 3.1106 | 0.034834 | Low | Low | High | 2655 | 2855 | 0.011198 | 12.1347
BERKELEY F 0402CB | BERKELEY F 0402 | EAST BAY | 0.47631 | 10 | 26.87% | 0 | 0 | 22.4% | 0% | 0 | 0.0083588 | 1 | 4.1661 | 0.034823 | Low | Low | High | 2656 | 3002 | 0.0083588 | 12.0998
SAND CREEK 11037110 | SAND CREEK 1103 | FRESNO | 19.4155 | 27.8259 | 94.86% | 5 | 7 | 100% | 0% | 0 | 0.080582 | 1 | 0.43197 | 0.034809 | High | High | Low | 2657 | 1393 | 0.080582 | 12.065
POSO MOUNTAIN 210448268 | POSO MOUNTAIN 2104 | KERN | 4.774 | 10 | 10.21% | 0 | 0 | 90.31% | 0% | 0 | 0.012535 | 1 | 2.7681 | 0.034699 | Low | Low | Medium | 2658 | 2772 | 0.012535 | 12.0302
BELMONT 1103415994 | BELMONT 1103 | PENINSULA | 1.0684 | 10 | 38.18% | 0 | 2 | 26.01% | 0% | 0 | 0.0086782 | 1 | 3.9933 | 0.034655 | Low | Low | High | 2659 | 2991 | 0.0086782 | 11.9955
BUTTE 11052410 | BUTTE 1105 | NORTH VALLEY | 1.8432 | 10 | 92.92% | 0 | 0 | 16.76% | 0% | 0 | 0.011878 | 1 | 2.9154 | 0.034628 | Low | Low | Medium | 2660 | 2815 | 0.011878 | 11.9608
VALLEY VIEW 1105P126 | VALLEY VIEW 1105 | EAST BAY | 0.94179 | 10 | 5.099% | 0 | 0 | 45.94% | 0% | 0 | 0.008838 | 1 | 3.9116 | 0.034571 | Low | Low | High | 2661 | 2984 | 0.008838 | 11.9262
TEJON 11023751 | TEJON 1102 | KERN | 20.1546 | 14.4086 | 57.09% | 0 | 4 | 78.15% | 0% | 0 | 0.034903 | 1 | 0.99037 | 0.034567 | Medium | Medium | Low | 2662 | 1954 | 0.034903 | 11.8916
MESA 1101CB | MESA 1101 | LOS PADRES | 13.1474 | 48.8211 | 12.29% | 0 | 3 | 51.32% | 0% | 0 | 0.013679 | 1 | 2.5227 | 0.034509 | Low | Low | Medium | 2663 | 2678 | 0.013679 | 11.8571
CMC 1102CB | CMC 1102 | LOS PADRES | 0.46264 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.714 | 0.034455 | Low | Low | Medium | 2664 | 2766 | 0.012695 | 11.8226
SNEATH LANE 1106CB | SNEATH LANE 1106 | PENINSULA | 1.101 | 10 | 47.15% | 3 | 3 | 17.83% | 0% | 0 | 0.0091441 | 1 | 3.7667 | 0.034443 | Low | Low | High | 2665 | 2973 | 0.0091441 | 11.7881
HARTLEY 110194178 | HARTLEY 1101 | HUMBOLDT | 1.6171 | 10 | 47.04% | 0 | 1 | 41.48% | 0% | 0 | 0.012159 | 1 | 2.8315 | 0.034428 | Low | Low | Medium | 2666 | 2797 | 0.012159 | 11.7537
KERN OIL 11063301 | KERN OIL 1106 | KERN | 0.36257 | 10 | 100% | 0 | 0 | 1.116% | 0% | 0 | 0.012298 | 1 | 2.7994 | 0.034427 | Low | Low | Medium | 2667 | 2786 | 0.012298 | 11.7192
SAN LUIS OBISPO 1103CB | SAN LUIS OBISPO 1103 | LOS PADRES | 2.8352 | 59.393 | 72.07% | 0 | 1 | 20.37% | 0% | 0 | 0.014802 | 1 | 2.3239 | 0.034398 | Low | Low | Medium | 2668 | 2618 | 0.014802 | 11.6848
LOS MOLINOS 11011308 | LOS MOLINOS 1101 | NORTH VALLEY | 0.1275 | 79.8468 | 100% | 0 | 0 | 1.055% | 0% | 0 | 0.017254 | 1 | 1.9923 | 0.034377 | Low | Low | Low | 2669 | 2519 | 0.017254 | 11.6504
CLAY 1103CB | CLAY 1103 | STOCKTON | 5.7506 | 36.571 | 11.82% | 0 | 1 | 42.68% | 0% | 0 | 0.011049 | 1 | 3.1111 | 0.034376 | Low | Low | High | 2670 | 2862 | 0.011049 | 11.616
CABRILLO 11031437 | CABRILLO 1103 | LOS PADRES | 3.2446 | 37.9706 | 72.77% | 0 | 0 | 66.31% | 0% | 0 | 0.019849 | 1 | 1.7318 | 0.034374 | Low | Low | Low | 2671 | 2417 | 0.019849 | 11.5817
SONOMA 11054456 | SONOMA 1105 | SONOMA | 1.6486 | 23.1811 | 52.93% | 0 | 1 | 22.31% | 0% | 0 | 0.010106 | 1 | 3.401 | 0.034372 | Low | Low | High | 2672 | 2923 | 0.010106 | 11.5473
STELLING 110913228 | STELLING 1109 | DE ANZA | 0.52786 | 10 | 79.39% | 0 | 0 | 6.214% | 0% | 0 | 0.0095798 | 1 | 3.5877 | 0.034369 | Low | Low | High | 2673 | 2947 | 0.0095798 | 11.5129
TEJON 11023760 | TEJON 1102 | KERN | 5.5529 | 84.6891 | 100% | 0 | 0 | 84.6% | 0% | 0 | 0.040235 | 1 | 0.85149 | 0.03426 | Medium | Medium | Low | 2674 | 1850 | 0.040235 | 11.4785
WILLITS 11044650 | WILLITS 1104 | HUMBOLDT | 2.8566 | 16.3398 | 61.51% | 0 | 4 | 48.68% | 0% | 0 | 0.014299 | 1 | 2.3934 | 0.034224 | Low | Low | Medium | 2675 | 2640 | 0.014299 | 11.4443
MORGAN HILL 2105XR602 | MORGAN HILL 2105 | SAN JOSE | 0.59187 | 10 | 11.22% | 0 | 0 | 69.56% | 0% | 0 | 0.010291 | 1 | 3.3208 | 0.034174 | Low | Low | High | 2676 | 2916 | 0.010291 | 11.4101
BURNEY 1101CB | BURNEY 1101 | NORTH VALLEY | 0.91927 | 10 | 59.07% | 1 | 0 | 46.14% | 0% | 0 | 0.012215 | 1 | 2.7975 | 0.034171 | Low | Low | Medium | 2677 | 2793 | 0.012215 | 11.3759
BURNEY 110297318 | BURNEY 1102 | NORTH VALLEY | 0.71383 | 14.6507 | 68.47% | 0 | 0 | 50.51% | 0% | 0 | 0.015997 | 1 | 2.1361 | 0.034171 | Low | Low | Low | 2678 | 2570 | 0.015997 | 11.3417
TEMPLETON 2108A40 | TEMPLETON 2108 | LOS PADRES | 1.2118 | 10 | 85.64% | 0 | 0 | 9.425% | 0% | 0 | 0.010408 | 1 | 3.2792 | 0.03413 | Low | Low | High | 2679 | 2909 | 0.010408 | 11.3075
PIT NO 1 1101CB | PIT NO 1 1101 | NORTH VALLEY | 6.4361 | 10 | 29.8% | 1 | 2 | 98.02% | 0% | 0 | 0.019097 | 1 | 1.7847 | 0.034083 | Low | Low | Low | 2680 | 2440 | 0.019097 | 11.2734
OREGON TRAIL 110346860 | OREGON TRAIL 1103 | NORTH VALLEY | 0.53541 | 10 | 100% | 0 | 0 | 16.12% | 0% | 0 | 0.012504 | 1 | 2.7222 | 0.034039 | Low | Low | Medium | 2681 | 2774 | 0.012504 | 11.2393
HIGHLANDS 1101CB | HIGHLANDS 1101 | HUMBOLDT | 0.026418 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.6761 | 0.033974 | Low | Low | Medium | 2682 | 2766 | 0.012695 | 11.2053
LAS GALLINAS A 11051218 | LAS GALLINAS A 1105 | NORTH BAY | 0.13008 | 10 | 100% | 0 | 0 | 5.571% | 0% | 0 | 0.011264 | 1 | 3.0158 | 0.033969 | Low | Low | Medium | 2683 | 2849 | 0.011264 | 11.1713
WISE 11011404 | WISE 1101 | SIERRA | 2.2264 | 13.0264 | 54.75% | 0 | 1 | 62.41% | 0% | 0 | 0.014247 | 1 | 2.3816 | 0.03393 | Low | Low | Medium | 2684 | 2646 | 0.014247 | 11.1374
RACETRACK 1703332820 | RACETRACK 1703 | YOSEMITE | 1.3085 | 10 | 3.686% | 0 | 0 | 71.54% | 0% | 0 | 0.0098677 | 1 | 3.4356 | 0.033901 | Low | Low | High | 2685 | 2936 | 0.0098677 | 11.1034
GONZALES 110422420 | GONZALES 1104 | CENTRAL COAST | 0.060363 | 60 | 100% | 0 | 0 | 0.7167% | 0% | 0 | 0.015047 | 1 | 2.2459 | 0.033793 | Low | Low | Medium | 2686 | 2606 | 0.015047 | 11.0695
SANTA YNEZ 1104CB | SANTA YNEZ 1104 | LOS PADRES | 0.81728 | 10 | 74.93% | 2 | 0 | 9.437% | 0% | 0 | 0.00979 | 1 | 3.444 | 0.033717 | Low | Low | High | 2687 | 2941 | 0.00979 | 11.0357
GEYSERVILLE 1101166 | GEYSERVILLE 1101 | SONOMA | 11.044 | 32.5571 | 62.6% | 3 | 3 | 68.81% | 0% | 0 | 0.022773 | 1 | 1.478 | 0.033658 | Medium | Medium | Low | 2688 | 2312 | 0.022773 | 11.002
WYANDOTTE 1105329930 | WYANDOTTE 1105 | NORTH VALLEY | 7.9312 | 11.1268 | 28.89% | 0 | 1 | 75.51% | 0% | 0 | 0.01297 | 1 | 2.5915 | 0.033613 | Low | Low | Medium | 2689 | 2715 | 0.01297 | 10.9684
MONTEREY 04022644 | MONTEREY 0402 | CENTRAL COAST | 0.7655 | 10 | 0% | 1 | 1 | 53.52% | 0% | 0 | 0.010791 | 1 | 3.0937 | 0.033385 | Low | Low | High | 2690 | 2884 | 0.010791 | 10.9347
PIT NO 3 2101CB | PIT NO 3 2101 | NORTH VALLEY | 4.5423 | 34.7965 | 2.145% | 10 | 3 | 100% | 0% | 0 | 0.027375 | 1 | 1.2188 | 0.033365 | Medium | Medium | Low | 2691 | 2181 | 0.027375 | 10.9014
ZACA 1102Y48 | ZACA 1102 | LOS PADRES | 4.0585 | 10 | 41.4% | 0 | 6 | 34.23% | 0% | 0 | 0.011989 | 1 | 2.7812 | 0.033343 | Low | Low | Medium | 2692 | 2809 | 0.011989 | 10.868
BEAR VALLEY 21014500 | BEAR VALLEY 2101 | YOSEMITE | 27.333 | 23.9548 | 99.26% | 0 | 3 | 33.35% | 0% | 0 | 0.017222 | 1 | 1.9324 | 0.03328 | Low | Low | Low | 2693 | 2521 | 0.017222 | 10.8346
SAN BERNARD 1101CB | SAN BERNARD 1101 | KERN | 0.91753 | 10 | 100% | 0 | 0 | 2.928% | 0% | 0 | 0.010972 | 1 | 3.031 | 0.033257 | Low | Low | Medium | 2694 | 2867 | 0.010972 | 10.8014
GEYSERVILLE 110137454 | GEYSERVILLE 1101 | SONOMA | 7.5123 | 58.2774 | 62.29% | 0 | 0 | 62.62% | 0% | 0 | 0.022967 | 1 | 1.4474 | 0.033242 | Medium | Medium | Low | 2695 | 2309 | 0.022967 | 10.7681
JESSUP 1102CB | JESSUP 1102 | NORTH VALLEY | 0.20781 | 10 | 69.42% | 4 | 1 | 3.869% | 0% | 0 | 0.01209 | 1 | 2.7419 | 0.033151 | Low | Low | Medium | 2696 | 2804 | 0.01209 | 10.7349
LLAGAS 2105XR234 | LLAGAS 2105 | SAN JOSE | 0.40589 | 10 | 70.52% | 0 | 1 | 18.63% | 0% | 0 | 0.01029 | 1 | 3.2175 | 0.033108 | Low | Low | High | 2697 | 2917 | 0.01029 | 10.7017
COVELO 110196896 | COVELO 1101 | HUMBOLDT | 3.6958 | 52.7111 | 100% | 5 | 0 | 24.03% | 0% | 0 | 0.024981 | 1 | 1.3246 | 0.033091 | Medium | Medium | Low | 2698 | 2243 | 0.024981 | 10.6686
SILVERADO 21023010 | SILVERADO 2102 | NORTH BAY | 3.5284 | 66.7535 | 84.82% | 0 | 1 | 27.23% | 0% | 0 | 0.018454 | 1 | 1.79 | 0.033032 | Low | Low | Low | 2699 | 2467 | 0.018454 | 10.6355
STONE CORRAL 11107784F | STONE CORRAL 1110 | FRESNO | 0.37155 | 63.2273 | 64.55% | 0 | 0 | 7.804% | 0% | 0 | 0.012359 | 1 | 2.6713 | 0.033015 | Low | Low | Medium | 2700 | 2779 | 0.012359 | 10.6025
LAS POSITAS 2108MR190 | LAS POSITAS 2108 | MISSION | 1.1924 | 39.2847 | 52.56% | 0 | 0 | 10.54% | 0% | 0 | 0.011177 | 1 | 2.9514 | 0.032988 | Low | Low | Medium | 2701 | 2858 | 0.011177 | 10.5695
EDES 1112CB | EDES 1112 | EAST BAY | 0.77646 | 10 | 11.31% | 0 | 0 | 52.35% | 0% | 0 | 0.0099087 | 1 | 3.3253 | 0.032949 | Low | Low | High | 2702 | 2933 | 0.0099087 | 10.5365
SAN MIGUEL 1106CB | SAN MIGUEL 1106 | LOS PADRES | 36.8861 | 40.1614 | 99.45% | 1 | 6 | 63.1% | 0% | 0 | 0.035909 | 1 | 0.91469 | 0.032845 | Medium | Medium | Low | 2703 | 1935 | 0.035909 | 10.5035
WALDO 0401CB | WALDO 0401 | EAST BAY | 1.6612 | 10 | 12.79% | 0 | 1 | 29.42% | 0% | 0 | 0.0071421 | 1 | 4.5981 | 0.03284 | Low | Low | High | 2704 | 3050 | 0.0071421 | 10.4707
BURNEY 11011322 | BURNEY 1101 | NORTH VALLEY | 16.3381 | 29.8396 | 61.19% | 0 | 0 | 87.48% | 0% | 0 | 0.021071 | 1 | 1.5564 | 0.032794 | Low | Low | Low | 2705 | 2365 | 0.021071 | 10.4379
BIG MEADOWS 21012476 | BIG MEADOWS 2101 | NORTH VALLEY | 4.675 | 24.1427 | 65.6% | 4 | 4 | 53.74% | 0% | 0 | 0.017254 | 1 | 1.8966 | 0.032724 | Low | Low | Low | 2706 | 2520 | 0.017254 | 10.4051
POINT MORETTI 110112122 | POINT MORETTI 1101 | CENTRAL COAST | 6.8941 | 11.1834 | 26.23% | 14 | 1 | 86.19% | 0% | 0 | 0.019307 | 1 | 1.689 | 0.03261 | Low | Low | Low | 2707 | 2430 | 0.019307 | 10.3723
SAN RAFAEL 11042235 | SAN RAFAEL 1104 | NORTH BAY | 0.29854 | 10 | 0% | 0 | 1 | 34.56% | 0% | 0 | 0.0067695 | 1 | 4.8094 | 0.032557 | Low | Low | High | 2708 | 3065 | 0.0067695 | 10.3397
LINCOLN 11042072 | LINCOLN 1104 | SIERRA | 0.13391 | 10 | 100% | 0 | 0 | 0.7885% | 0% | 0 | 0.010742 | 1 | 3.0303 | 0.032552 | Low | Low | Medium | 2709 | 2887 | 0.010742 | 10.3072
TASSAJARA 2109CB | TASSAJARA 2109 | DIABLO | 0.80761 | 10 | 0% | 0 | 4 | 46.43% | 0% | 0 | 0.0081085 | 1 | 4.0127 | 0.032537 | Low | Low | High | 2710 | 3009 | 0.0081085 | 10.2746
OCEANO 1105V44 | OCEANO 1105 | LOS PADRES | 0.92167 | 10 | 6.253% | 0 | 2 | 80.43% | 0% | 0 | 0.011472 | 1 | 2.8318 | 0.032488 | Low | Low | Medium | 2711 | 2837 | 0.011472 | 10.2421
POINT ARENA 11013702 | POINT ARENA 1101 | HUMBOLDT | 4.3225 | 19.0711 | 4.681% | 4 | 1 | 86.66% | 0% | 0 | 0.013218 | 1 | 2.4572 | 0.03248 | Low | Low | Medium | 2712 | 2703 | 0.013218 | 10.2096
PURISIMA 110149394 | PURISIMA 1101 | LOS PADRES | 0.38618 | 10 | 25.81% | 1 | 0 | 4.395% | 0% | 0 | 0.0070193 | 1 | 4.6217 | 0.032441 | Low | Low | High | 2713 | 3054 | 0.0070193 | 10.1771
LAKEVILLE 1102530 | LAKEVILLE 1102 | SONOMA | 0.62549 | 57.7371 | 40.72% | 0 | 0 | 12.01% | 0% | 0 | 0.010222 | 1 | 3.1695 | 0.032397 | Low | Low | High | 2714 | 2919 | 0.010222 | 10.1447
BALCH NO 1 1101CB | BALCH NO 1 1101 | FRESNO | 8.601 | 30.315 | 65.14% | 0 | 10 | 100% | 0% | 0 | 0.030256 | 1 | 1.07 | 0.032375 | Medium | Medium | Low | 2715 | 2089 | 0.030256 | 10.1123
MC KEE 1103XR028 | MC KEE 1103 | SAN JOSE | 2.8083 | 15.9921 | 15.4% | 0 | 2 | 26.81% | 0% | 0 | 0.007561 | 1 | 4.2746 | 0.032321 | Low | Low | High | 2716 | 3027 | 0.007561 | 10.0799
ELK CREEK 11012228 | ELK CREEK 1101 | NORTH VALLEY | 3.1012 | 51.6707 | 100% | 0 | 0 | 29.46% | 0% | 0 | 0.018884 | 1 | 1.7101 | 0.032292 | Low | Low | Low | 2717 | 2453 | 0.018884 | 10.0476
BERKELEY F 1105CB | BERKELEY F 1105 | EAST BAY | 1.3653 | 10 | 33.54% | 1 | 1 | 21.32% | 0% | 0 | 0.0079134 | 1 | 4.0804 | 0.03229 | Low | Low | High | 2718 | 3014 | 0.0079134 | 10.0153
FRENCH GULCH 1102CB | FRENCH GULCH 1102 | NORTH VALLEY | 1.6951 | 33.4949 | 100% | 0 | 1 | 100% | 0% | 0 | 0.034 | 1 | 0.94898 | 0.032265 | Medium | Medium | Low | 2719 | 1975 | 0.034 | 9.983
DUNBAR 110113481 | DUNBAR 1101 | SONOMA | 0.13904 | 10 | 89.93% | 1 | 0 | 12.88% | 0% | 0 | 0.011301 | 1 | 2.8533 | 0.032246 | Low | Low | Medium | 2720 | 2847 | 0.011301 | 9.9507
UKIAH 1114528 | UKIAH 1114 | HUMBOLDT | 2.0763 | 22.6279 | 79.13% | 0 | 2 | 16.87% | 0% | 0 | 0.013763 | 1 | 2.3375 | 0.032173 | Low | Low | Medium | 2721 | 2676 | 0.013763 | 9.9185
VOLTA 110165764 | VOLTA 1101 | NORTH VALLEY | 10.3627 | 58.9136 | 100% | 1 | 0 | 100% | 0% | 0 | 0.0399 | 1 | 0.80592 | 0.032156 | Medium | Medium | Low | 2722 | 1861 | 0.0399 | 9.8863
CLEAR LAKE 11024708 | CLEAR LAKE 1102 | HUMBOLDT | 0.26472 | 10 | 85.61% | 0 | 0 | 9.354% | 0% | 0 | 0.010398 | 1 | 3.0898 | 0.032127 | Low | Low | High | 2723 | 2911 | 0.010398 | 9.8542
SNEATH LANE 11015311 | SNEATH LANE 1101 | PENINSULA | 0.49818 | 10 | 0% | 0 | 0 | 44.61% | 0% | 0 | 0.0073269 | 1 | 4.3756 | 0.032059 | Low | Low | High | 2724 | 3039 | 0.0073269 | 9.822
RISING RIVER 1101CB | RISING RIVER 1101 | NORTH VALLEY | 9.43 | 10 | 88.75% | 1 | 2 | 70.58% | 0% | 0 | 0.020612 | 1 | 1.5535 | 0.03202 | Low | Low | Low | 2725 | 2381 | 0.020612 | 9.79
GRASS VALLEY 1103CB | GRASS VALLEY 1103 | SIERRA | 0.095866 | 10 | 0% | 0 | 0 | 80.7% | 0% | 0 | 0.010486 | 1 | 3.0497 | 0.03198 | Low | Low | Medium | 2726 | 2904 | 0.010486 | 9.7579
OAKLAND J 1102CR254 | OAKLAND J 1102 | EAST BAY | 1.0198 | 10 | 0% | 1 | 0 | 66.21% | 0% | 0 | 0.0092017 | 1 | 3.4742 | 0.031969 | Low | Low | High | 2727 | 2968 | 0.0092017 | 9.726
OTTER 11022002 | OTTER 1102 | CENTRAL COAST | 8.6285 | 34.3246 | 5.086% | 6 | 1 | 100% | 0% | 0 | 0.025475 | 1 | 1.2546 | 0.03196 | Medium | Medium | Low | 2728 | 2230 | 0.025475 | 9.694
JOLON 11027040 | JOLON 1102 | CENTRAL COAST | 20.3578 | 63.5106 | 29.02% | 0 | 1 | 88.79% | 0% | 0 | 0.02105 | 1 | 1.5142 | 0.031874 | Low | Low | Low | 2729 | 2366 | 0.02105 | 9.662
CAMBRIA 1102W50 | CAMBRIA 1102 | LOS PADRES | 2.1309 | 10 | 10.45% | 0 | 0 | 58.83% | 0% | 0 | 0.010493 | 1 | 3.0352 | 0.031848 | Low | Low | Medium | 2730 | 2903 | 0.010493 | 9.6302
PUEBLO 2102CB | PUEBLO 2102 | NORTH BAY | 0.216 | 10 | 100% | 0 | 1 | 1.423% | 0% | 0 | 0.011037 | 1 | 2.8708 | 0.031684 | Low | Low | Medium | 2731 | 2864 | 0.011037 | 9.5983
JESSUP 110338864 | JESSUP 1103 | NORTH VALLEY | 0.59204 | 10 | 100% | 1 | 3 | 7.85% | 0% | 0 | 0.012422 | 1 | 2.5473 | 0.031642 | Low | Low | Medium | 2732 | 2775 | 0.012422 | 9.5666
GIRVAN 1102CB | GIRVAN 1102 | NORTH VALLEY | 4.7326 | 13.9144 | 68.55% | 4 | 1 | 22.51% | 1.048% | 1 | 0.01158 | 1 | 2.7229 | 0.031532 | Low | Low | Medium | 2733 | 2832 | 0.01158 | 9.535
RESERVATION ROAD 1102CB | RESERVATION ROAD 1102 | CENTRAL COAST | 6.8792 | 54.6073 | 43.73% | 1 | 5 | 38.43% | 0% | 0 | 0.017073 | 1 | 1.8467 | 0.031528 | Low | Low | Low | 2734 | 2525 | 0.017073 | 9.5035
SAN RAFAEL 110969860 | SAN RAFAEL 1109 | NORTH BAY | 0.67004 | 10 | 27.57% | 0 | 0 | 26.27% | 0% | 0 | 0.0076522 | 1 | 4.1175 | 0.031508 | Low | Low | High | 2735 | 3024 | 0.0076522 | 9.4719
PANORAMA 11021526 | PANORAMA 1102 | NORTH VALLEY | 11.8848 | 23.1923 | 53.04% | 0 | 7 | 67.25% | 0% | 0 | 0.020361 | 1 | 1.5446 | 0.03145 | Low | Low | Low | 2736 | 2390 | 0.020361 | 9.4404
FLINT 110140666 | FLINT 1101 | SIERRA | 0.79305 | 10 | 48.92% | 0 | 1 | 27.77% | 0% | 0 | 0.009443 | 1 | 3.3257 | 0.031404 | Low | Low | High | 2737 | 2957 | 0.009443 | 9.409
OLETA 11022642 | OLETA 1102 | STOCKTON | 4.6588 | 10 | 54.08% | 0 | 0 | 100% | 0.8976% | 1 | 0.01998 | 1 | 1.5701 | 0.031371 | Low | Low | Low | 2738 | 2409 | 0.01998 | 9.3776
CLAY 11037142 | CLAY 1103 | STOCKTON | 4.4879 | 10 | 67.68% | 2 | 0 | 29.1% | 0% | 0 | 0.012796 | 1 | 2.4498 | 0.031348 | Low | Low | Medium | 2739 | 2726 | 0.012796 | 9.3462
FRANKLIN 1104P136 | FRANKLIN 1104 | EAST BAY | 3.8457 | 10 | 0% | 0 | 1 | 65.24% | 0% | 0 | 0.009184 | 1 | 3.4131 | 0.031346 | Low | Low | High | 2740 | 2969 | 0.009184 | 9.3149
DIVIDE 110348160 | DIVIDE 1103 | LOS PADRES | 2.2423 | 10 | 32.11% | 0 | 0 | 17.66% | 0% | 0 | 0.010844 | 1 | 2.8904 | 0.031344 | Low | Low | Medium | 2741 | 2879 | 0.010844 | 9.2835
JOLON 11027070 | JOLON 1102 | CENTRAL COAST | 4.9443 | 33.893 | 99.18% | 0 | 3 | 30.01% | 0% | 0 | 0.023132 | 1 | 1.3548 | 0.031339 | Medium | Medium | Low | 2742 | 2305 | 0.023132 | 9.2522
SANTA YNEZ 1102320270 | SANTA YNEZ 1102 | LOS PADRES | 0.55315 | 10 | 90.55% | 0 | 2 | 19.74% | 0% | 0 | 0.012507 | 1 | 2.5016 | 0.031288 | Low | Low | Medium | 2743 | 2773 | 0.012507 | 9.2208
OLEMA 110137074 | OLEMA 1101 | NORTH BAY | 0.013643 | 10 | 100% | 0 | 0 | 4.337% | 0% | 0 | 0.011127 | 1 | 2.8085 | 0.03125 | Low | Low | Medium | 2744 | 2859 | 0.011127 | 9.1895
PUTAH CREEK 11058812 | PUTAH CREEK 1105 | SACRAMENTO | 0.75773 | 78.0828 | 100% | 0 | 0 | 1.163% | 0% | 0 | 0.017069 | 1 | 1.8258 | 0.031165 | Low | Low | Low | 2745 | 2526 | 0.017069 | 9.1583
PACIFIC GROVE 04222614 | PACIFIC GROVE 0422 | CENTRAL COAST | 0.61996 | 10 | 0% | 1 | 0 | 28.91% | 0% | 0 | 0.007251 | 1 | 4.276 | 0.031005 | Low | Low | High | 2746 | 3044 | 0.007251 | 9.1271
WILLITS 1102CB | WILLITS 1102 | HUMBOLDT | 5.2584 | 15.1568 | 26.36% | 0 | 4 | 54.45% | 0% | 0 | 0.01287 | 1 | 2.3959 | 0.030834 | Low | Low | Medium | 2747 | 2719 | 0.01287 | 9.0961
SOBRANTE 110142914 | SOBRANTE 1101 | DIABLO | 0.83179 | 10 | 55.86% | 0 | 1 | 20.13% | 0% | 0 | 0.0092648 | 1 | 3.3242 | 0.030798 | Low | Low | High | 2748 | 2966 | 0.0092648 | 9.0653
OAKLAND X 1105CB | OAKLAND X 1105 | EAST BAY | 3.475 | 10 | 21.39% | 0 | 3 | 23.79% | 0% | 0 | 0.0086247 | 1 | 3.5708 | 0.030797 | Low | Low | High | 2749 | 2993 | 0.0086247 | 9.0345
SAN CARLOS 110436864 | SAN CARLOS 1104 | PENINSULA | 0.3154 | 10 | 0% | 0 | 1 | 37.17% | 0% | 0 | 0.0069476 | 1 | 4.4226 | 0.030727 | Low | Low | High | 2750 | 3056 | 0.0069476 | 9.0037
POINT MORETTI 110135874 | POINT MORETTI 1101 | CENTRAL COAST | 0.27376 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.4196 | 0.030718 | Low | Low | Medium | 2751 | 2735 | 0.012695 | 8.973
ROB ROY 210512584 | ROB ROY 2105 | CENTRAL COAST | 3.0913 | 10 | 22.02% | 2 | 1 | 25.72% | 0% | 0 | 0.011337 | 1 | 2.7064 | 0.030682 | Low | Low | Medium | 2752 | 2845 | 0.011337 | 8.9422
CHOLAME 2102X06 | CHOLAME 2102 | LOS PADRES | 33.5233 | 47.8201 | 99.99% | 1 | 7 | 63.4% | 0% | 0 | 0.034127 | 1 | 0.89797 | 0.030645 | Medium | Medium | Low | 2753 | 1972 | 0.034127 | 8.9116
ZACA 1101CB | ZACA 1101 | LOS PADRES | 7.3177 | 63.5153 | 26.01% | 0 | 1 | 67.25% | 0% | 0 | 0.024613 | 1 | 1.2436 | 0.030608 | Medium | Medium | Low | 2754 | 2254 | 0.024613 | 8.8809
BEAR VALLEY 21059570 | BEAR VALLEY 2105 | YOSEMITE | 8.0469 | 57.8177 | 84.85% | 0 | 1 | 100% | 0% | 0 | 0.035385 | 1 | 0.86453 | 0.030591 | Medium | Medium | Low | 2755 | 1949 | 0.035385 | 8.8503
VIEJO 220146068 | VIEJO 2201 | CENTRAL COAST | 0.073762 | 10 | 0% | 0 | 0 | 53.15% | 0% | 0 | 0.0079762 | 1 | 3.8343 | 0.030583 | Low | Low | High | 2756 | 3011 | 0.0079762 | 8.8197
UPPER LAKE 1101472084 | UPPER LAKE 1101 | HUMBOLDT | 4.5266 | 10 | 55.47% | 0 | 3 | 61.59% | 0% | 0 | 0.016554 | 1 | 1.8437 | 0.030521 | Low | Low | Low | 2757 | 2546 | 0.016554 | 8.7891
LOS OSITOS 21027470 | LOS OSITOS 2102 | CENTRAL COAST | 2.5834 | 65.4453 | 76.6% | 0 | 0 | 9.453% | 0% | 0 | 0.014067 | 1 | 2.1688 | 0.030509 | Low | Low | Low | 2758 | 2661 | 0.014067 | 8.7586
SANTA YNEZ 1102CB | SANTA YNEZ 1102 | LOS PADRES | 1.3864 | 10 | 42.97% | 0 | 2 | 15.51% | 0% | 0 | 0.010594 | 1 | 2.8741 | 0.030449 | Low | Low | Medium | 2759 | 2901 | 0.010594 | 8.7281
BERESFORD 04039154 | BERESFORD 0403 | PENINSULA | 3.1988 | 10 | 17.34% | 4 | 1 | 48.83% | 0% | 0 | 0.0094751 | 1 | 3.2128 | 0.030442 | Low | Low | High | 2760 | 2953 | 0.0094751 | 8.6977
SAN BENITO 2104CB | SAN BENITO 2104 | CENTRAL COAST | 4.8064 | 10 | 7.992% | 0 | 0 | 52.81% | 0% | 0 | 0.014395 | 1 | 2.1147 | 0.030441 | Low | Low | Low | 2761 | 2633 | 0.014395 | 8.6672
ELECTRA 1102CB | ELECTRA 1102 | STOCKTON | 2.62 | 68.1508 | 1.119% | 0 | 0 | 100% | 0% | 0 | 0.018952 | 1 | 1.606 | 0.030437 | Low | Low | Low | 2762 | 2451 | 0.018952 | 8.6368
CARLOTTA 11214045 | CARLOTTA 1121 | HUMBOLDT | 0.14338 | 10 | 100% | 0 | 0 | 7.252% | 0% | 0 | 0.011453 | 1 | 2.6575 | 0.030436 | Low | Low | Medium | 2763 | 2839 | 0.011453 | 8.6063
HOPLAND 11011100 | HOPLAND 1101 | HUMBOLDT | 2.6093 | 13.3851 | 100% | 0 | 1 | 39.2% | 0% | 0 | 0.016404 | 1 | 1.8539 | 0.030412 | Low | Low | Low | 2764 | 2555 | 0.016404 | 8.5759
REDBUD 1102432 | REDBUD 1102 | HUMBOLDT | 1.3051 | 10 | 69.46% | 0 | 1 | 11.62% | 0% | 0 | 0.0095157 | 1 | 3.1897 | 0.030352 | Low | Low | High | 2765 | 2949 | 0.0095157 | 8.5455
WILLITS 1103CB | WILLITS 1103 | HUMBOLDT | 1.4734 | 28.6497 | 64.03% | 0 | 1 | 37.49% | 0% | 0 | 0.015222 | 1 | 1.9923 | 0.030328 | Low | Low | Low | 2766 | 2602 | 0.015222 | 8.5151
JOLON 11027002 | JOLON 1102 | CENTRAL COAST | 7.9112 | 56.9708 | 100% | 0 | 0 | 43.93% | 0% | 0 | 0.025691 | 1 | 1.1804 | 0.030327 | Medium | Medium | Low | 2767 | 2226 | 0.025691 | 8.4848
CLARK ROAD 11022044 | CLARK ROAD 1102 | NORTH VALLEY | 5.5376 | 29.0224 | 29.16% | 0 | 3 | 44.24% | 0% | 0 | 0.018991 | 1 | 1.5914 | 0.030222 | Low | Low | Low | 2768 | 2448 | 0.018991 | 8.4545
PEORIA 1704 | PEORIA 1704 | YOSEMITE | 0.12912 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.3748 | 0.030148 | Low | Low | Medium | 2769 | 2735 | 0.012695 | 8.4243
OAKLAND J 1102CR252 | OAKLAND J 1102 | EAST BAY | 1.1914 | 10 | 48.94% | 0 | 1 | 19.56% | 0% | 0 | 0.0087055 | 1 | 3.4603 | 0.030124 | Low | Low | High | 2770 | 2990 | 0.0087055 | 8.3941
RIO DEL MAR 0402CB | RIO DEL MAR 0402 | CENTRAL COAST | 1.6949 | 10 | 6.344% | 2 | 0 | 47.04% | 0% | 0 | 0.0081166 | 1 | 3.7099 | 0.030112 | Low | Low | High | 2771 | 3008 | 0.0081166 | 8.364
HARTLEY 1101738 | HARTLEY 1101 | HUMBOLDT | 3.053 | 10 | 42.13% | 1 | 2 | 37.87% | 0% | 0 | 0.011659 | 1 | 2.581 | 0.030092 | Low | Low | Medium | 2772 | 2824 | 0.011659 | 8.3339
ANTLER 11011612 | ANTLER 1101 | NORTH VALLEY | 8.3928 | 10 | 100% | 2 | 6 | 90.86% | 15.08% | 1 | 0.043586 | 1 | 0.69008 | 0.030078 | Medium | Medium | Low | 2773 | 1786 | 0.043586 | 8.3038
VALLEY VIEW 1106P128 | VALLEY VIEW 1106 | EAST BAY | 0.72514 | 10 | 44.15% | 0 | 0 | 28.68% | 0% | 0 | 0.0089763 | 1 | 3.3463 | 0.030037 | Low | Low | High | 2774 | 2978 | 0.0089763 | 8.2737
FORT ORD 210637286 | FORT ORD 2106 | CENTRAL COAST | 1.5847 | 10 | 0% | 0 | 4 | 43% | 0% | 0 | 0.010213 | 1 | 2.936 | 0.029984 | Low | Low | Medium | 2775 | 2920 | 0.010213 | 8.2437
SAN MIGUEL 1104R58 | SAN MIGUEL 1104 | LOS PADRES | 9.7655 | 26.7568 | 99.18% | 0 | 1 | 40.61% | 0% | 0 | 0.018077 | 1 | 1.6551 | 0.029918 | Low | Low | Low | 2776 | 2485 | 0.018077 | 8.2137
MORAGA 110381146 | MORAGA 1103 | DIABLO | 0.81099 | 10 | 24.05% | 0 | 0 | 14.46% | 0% | 0 | 0.00661 | 1 | 4.5238 | 0.029902 | Low | Low | High | 2777 | 3072 | 0.00661 | 8.1838
UKIAH 111472990 | UKIAH 1114 | HUMBOLDT | 0.7336 | 10 | 33.42% | 1 | 5 | 22.74% | 0% | 0 | 0.0099473 | 1 | 3.0013 | 0.029855 | Low | Low | Medium | 2778 | 2930 | 0.0099473 | 8.1539
MORRO BAY 1101V66 | MORRO BAY 1101 | LOS PADRES | 3.6398 | 32.9293 | 34.81% | 0 | 0 | 22.6% | 18.48% | 0 | 0.01232 | 1 | 2.4197 | 0.029811 | Low | Low | Medium | 2779 | 2783 | 0.01232 | 8.124
SAN CARLOS 1103 | SAN CARLOS 1103 | PENINSULA | 0.013694 | 10 | 0% | 0 | 0 | 32.32% | 0% | 0 | 0.0064833 | 1 | 4.5959 | 0.029797 | Low | Low | High | 2780 | 3080 | 0.0064833 | 8.0942
FORT ORD 210736596 | FORT ORD 2107 | CENTRAL COAST | 2.9621 | 10 | 1.434% | 0 | 3 | 23.77% | 0% | 0 | 0.0095449 | 1 | 3.1211 | 0.029791 | Low | Low | High | 2781 | 2948 | 0.0095449 | 8.0644
LAS GALLINAS A 11041220 | LAS GALLINAS A 1104 | NORTH BAY | 1.0215 | 10 | 17.87% | 0 | 0 | 20.99% | 0% | 0 | 0.0076561 | 1 | 3.869 | 0.029621 | Low | Low | High | 2782 | 3023 | 0.0076561 | 8.0346
CALAVERAS CEMENT 110113424 | CALAVERAS CEMENT 1101 | STOCKTON | 1.1628 | 27.7873 | 54.51% | 0 | 1 | 32.26% | 0% | 0 | 0.011657 | 1 | 2.5395 | 0.029604 | Low | Low | Medium | 2783 | 2825 | 0.011657 | 8.005
LOYOLA 1102LL12 | LOYOLA 1102 | DE ANZA | 0.10967 | 10 | 100% | 0 | 0 | 1.811% | 0% | 0 | 0.010852 | 1 | 2.7206 | 0.029523 | Low | Low | Medium | 2784 | 2877 | 0.010852 | 7.9754
VIEJO 220285904 | VIEJO 2202 | CENTRAL COAST | 0.44182 | 10 | 5.103% | 1 | 0 | 22.34% | 0% | 0 | 0.007082 | 1 | 4.1688 | 0.029523 | Low | Low | High | 2785 | 3051 | 0.007082 | 7.9459
ANDERSON 1103CB | ANDERSON 1103 | NORTH VALLEY | 3.2551 | 15.9196 | 80.29% | 1 | 2 | 15.59% | 0% | 0 | 0.011642 | 1 | 2.5308 | 0.029465 | Low | Low | Medium | 2786 | 2826 | 0.011642 | 7.9163
MIRABEL 1102206 | MIRABEL 1102 | SONOMA | 1.6804 | 10 | 37.83% | 0 | 1 | 13.09% | 0% | 0 | 0.0097141 | 1 | 3.0324 | 0.029457 | Low | Low | Medium | 2787 | 2943 | 0.0097141 | 7.8869
PASO ROBLES 110355374 | PASO ROBLES 1103 | LOS PADRES | 2.104 | 28.3586 | 87.29% | 0 | 2 | 19.75% | 0% | 0 | 0.013788 | 1 | 2.1323 | 0.0294 | Low | Low | Low | 2788 | 2675 | 0.013788 | 7.8574
ECHO SUMMIT 1101344250 | ECHO SUMMIT 1101 | (blank) | 0.80694 | 10 | 100% | 1 | 0 | 14.32% | 0% | 0 | 0.014197 | 1 | 2.0707 | 0.029398 | Low | Low | Low | 2789 | 2651 | 0.014197 | 7.828
DEL MONTE 210332886 | DEL MONTE 2103 | CENTRAL COAST | 1.2598 | 10 | 0% | 5 | 1 | 31.74% | 0% | 0 | 0.0091616 | 1 | 3.2009 | 0.029325 | Low | Low | High | 2790 | 2970 | 0.0091616 | 7.7986
BIG RIVER 11012989 | BIG RIVER 1101 | HUMBOLDT | 0.072968 | 10 | 100% | 0 | 0 | 6.918% | 0% | 0 | 0.011415 | 1 | 2.5683 | 0.029316 | Low | Low | Medium | 2791 | 2841 | 0.011415 | 7.7693
PETALUMA C 1108630 | PETALUMA C 1108 | SONOMA | 1.2522 | 54.3048 | 11.61% | 0 | 2 | 29.56% | 0% | 0 | 0.0097687 | 1 | 3 | 0.029306 | Low | Low | Medium | 2792 | 2942 | 0.0097687 | 7.74
WILLITS 1104CB | WILLITS 1104 | HUMBOLDT | 2.2442 | 16.2086 | 22.49% | 1 | 7 | 29.86% | 0% | 0 | 0.012113 | 1 | 2.4118 | 0.029214 | Low | Low | Medium | 2793 | 2802 | 0.012113 | 7.7107
SOLEDAD 2101CB | SOLEDAD 2101 | CENTRAL COAST | 1.1091 | 10 | 100% | 0 | 0 | 7.451% | 0% | 0 | 0.011475 | 1 | 2.5437 | 0.02919 | Low | Low | Medium | 2794 | 2836 | 0.011475 | 7.6815
OAKLAND J 1106CR330 | OAKLAND J 1106 | EAST BAY | 0.49535 | 10 | 40.09% | 0 | 0 | 20.57% | 0% | 0 | 0.0091449 | 1 | 3.1852 | 0.029128 | Low | Low | High | 2795 | 2972 | 0.0091449 | 7.6523
POINT MORETTI 11015074 | POINT MORETTI 1101 | CENTRAL COAST | 1.726 | 19.9026 | 1.553% | 2 | 1 | 56.7% | 0% | 0 | 0.009381 | 1 | 3.1003 | 0.029084 | Low | Low | High | 2796 | 2961 | 0.009381 | 7.6231
BUELLTON 1101753644 | BUELLTON 1101 | LOS PADRES | 0.0028488 | 10 | 100% | 0 | 0 | 0.4009% | 0% | 0 | 0.010701 | 1 | 2.7101 | 0.029001 | Low | Low | Medium | 2797 | 2894 | 0.010701 | 7.5941
SAN LUIS OBISPO 1107CB | SAN LUIS OBISPO 1107 | LOS PADRES | 0.84728 | 10 | 25.92% | 0 | 0 | 48.86% | 0% | 0 | 0.0094493 | 1 | 3.0675 | 0.028986 | Low | Low | Medium | 2798 | 2955 | 0.0094493 | 7.5651
OAKLAND J 1106CR164 | OAKLAND J 1106 | EAST BAY | 1.4865 | 10 | 46.08% | 2 | 1 | 22.66% | 0% | 0 | 0.0090035 | 1 | 3.2151 | 0.028947 | Low | Low | High | 2799 | 2975 | 0.0090035 | 7.5361
WILDWOOD 11011454 | WILDWOOD 1101 | NORTH VALLEY | 7.7462 | 36.802 | 100% | 0 | 1 | 100% | 0% | 0 | 0.034751 | 1 | 0.83154 | 0.028897 | Medium | Medium | Low | 2800 | 1955 | 0.034751 | 7.5071
GARBERVILLE 11024744 | GARBERVILLE 1102 | HUMBOLDT | 16.8626 | 50.888 | 35.22% | 7 | 3 | 83.26% | 0% | 0 | 0.047692 | 1 | 0.60586 | 0.028895 | Medium | Medium | Low | 2801 | 1709 | 0.047692 | 7.4782
ATASCADERO 1101CB | ATASCADERO 1101 | LOS PADRES | 0.44126 | 10 | 57.34% | 0 | 0 | 21.26% | 0% | 0 | 0.0092885 | 1 | 3.1059 | 0.028849 | Low | Low | High | 2802 | 2964 | 0.0092885 | 7.4493
LAS GALLINAS A 1104304 | LAS GALLINAS A 1104 | NORTH BAY | 0.14237 | 10 | 35.52% | 0 | 1 | 5.697% | 0% | 0 | 0.0067954 | 1 | 4.2336 | 0.028769 | Low | Low | High | 2803 | 3062 | 0.0067954 | 7.4205
HOLLISTER 210441808 | HOLLISTER 2104 | CENTRAL COAST | 0.1888 | 10 | 100% | 0 | 0 | 1.735% | 0% | 0 | 0.010843 | 1 | 2.6518 | 0.028755 | Low | Low | Medium | 2804 | 2880 | 0.010843 | 7.3917
RAWSON 110385334 | RAWSON 1103 | NORTH VALLEY | 2.3781 | 53.7562 | 78.76% | 0 | 1 | 24.97% | 0% | 0 | 0.017954 | 1 | 1.5952 | 0.028642 | Low | Low | Low | 2805 | 2492 | 0.017954 | 7.363
WYANDOTTE 11101952 | WYANDOTTE 1110 | NORTH VALLEY | 0.44853 | 10 | 100% | 0 | 0 | 5.144% | 0% | 0 | 0.011216 | 1 | 2.5511 | 0.028613 | Low | Low | Medium | 2806 | 2853 | 0.011216 | 7.3343
HOLLISTER 21024780 | HOLLISTER 2102 | CENTRAL COAST | 2.8684 | 10 | 66.05% | 0 | 1 | 19.03% | 0% | 0 | 0.011367 | 1 | 2.5162 | 0.028602 | Low | Low | Medium | 2807 | 2844 | 0.011367 | 7.3057
VIEJO 22029089 | VIEJO 2202 | CENTRAL COAST | 0.44699 | 10 | 0% | 1 | 3 | 26.75% | 0% | 0 | 0.0075545 | 1 | 3.7807 | 0.028562 | Low | Low | High | 2808 | 3028 | 0.0075545 | 7.2771
HOOPA 110193038 | HOOPA 1101 | HUMBOLDT | 0.1684 | 40.7085 | 100% | 0 | 1 | 6.029% | 0% | 0 | 0.014214 | 1 | 2.0078 | 0.028539 | Low | Low | Low | 2809 | 2649 | 0.014214 | 7.2485
ATASCADERO 1101A22 | ATASCADERO 1101 | LOS PADRES | 0.48233 | 10 | 88.74% | 0 | 1 | 3.681% | 0% | 0 | 0.010296 | 1 | 2.761 | 0.028426 | Low | Low | Medium | 2810 | 2915 | 0.010296 | 7.22
VIEJO 22049110 | VIEJO 2204 | CENTRAL COAST | 0.89252 | 10 | 16.91% | 0 | 0 | 20.66% | 0% | 0 | 0.0066316 | 1 | 4.2831 | 0.028404 | Low | Low | High | 2811 | 3071 | 0.0066316 | 7.1916
ROB ROY 210410930 | ROB ROY 2104 | CENTRAL COAST | 1.4484 | 10 | 54.81% | 0 | 0 | 12.82% | 0% | 0 | 0.0083664 | 1 | 3.3859 | 0.028328 | Low | Low | High | 2812 | 3000 | 0.0083664 | 7.1632
GREEN VALLEY 210112130 | GREEN VALLEY 2101 | CENTRAL COAST | 1.2937 | 17.054 | 59.16% | 0 | 0 | 7.411% | 0% | 0 | 0.0086186 | 1 | 3.2862 | 0.028323 | Low | Low | High | 2813 | 2995 | 0.0086186 | 7.1348
HARTLEY 110186876 | HARTLEY 1101 | HUMBOLDT | 2.3866 | 10 | 49.85% | 0 | 0 | 28.66% | 0% | 0 | 0.0094023 | 1 | 2.9982 | 0.02819 | Low | Low | Medium | 2814 | 2960 | 0.0094023 | 7.1065
EL CERRITO G 1111CB | EL CERRITO G 1111 | EAST BAY | 0.94606 | 10 | 6.246% | 0 | 0 | 7.497% | 0% | 0 | 0.0053291 | 1 | 5.2654 | 0.028059 | Low | Low | High | 2815 | 3131 | 0.0053291 | 7.0783
VINEYARD 2107CB | VINEYARD 2107 | MISSION | 1.6942 | 13.0214 | 48.11% | 0 | 2 | 16.67% | 0% | 0 | 0.0087566 | 1 | 3.1976 | 0.028 | Low | Low | High | 2816 | 2985 | 0.0087566 | 7.0503
TEMPLETON 2113R82 | TEMPLETON 2113 | LOS PADRES | 34.6176 | 62.3861 | 93.76% | 0 | 4 | 50.19% | 6.458% | 0 | 0.03681 | 1 | 0.75794 | 0.0279 | Medium | Medium | Low | 2817 | 1922 | 0.03681 | 7.0223
MERCED FALLS 110287352 | MERCED FALLS 1102 | YOSEMITE | 26.2614 | 32.8974 | 99.99% | 0 | 0 | 98.93% | 0% | 0 | 0.054765 | 1 | 0.50877 | 0.027863 | Medium | Medium | Low | 2818 | 1628 | 0.054765 | 6.9944
GUALALA 1111CB | GUALALA 1111 | HUMBOLDT | 3.8671 | 10 | 20.51% | 4 | 5 | 100% | 0% | 0 | 0.017522 | 1 | 1.59 | 0.02786 | Low | Low | Low | 2819 | 2511 | 0.017522 | 6.9665
BRENTWOOD 2105502672 | BRENTWOOD 2105 | DIABLO | 1.383 | 10 | 100% | 0 | 0 | 7.371% | 0% | 0 | 0.011466 | 1 | 2.4116 | 0.027652 | Low | Low | Medium | 2820 | 2838 | 0.011466 | 6.9386
PEORIA 17019811 | PEORIA 1701 | YOSEMITE | 5.5301 | 39.6322 | 92.09% | 0 | 0 | 62.43% | 0% | 0 | 0.022586 | 1 | 1.223 | 0.027623 | Medium | Medium | Low | 2821 | 2319 | 0.022586 | 6.911
MESA 1103M92 | MESA 1103 | LOS PADRES | 1.0274 | 49.2008 | 44.21% | 0 | 0 | 12.96% | 0% | 0 | 0.010021 | 1 | 2.7565 | 0.027622 | Low | Low | Medium | 2822 | 2928 | 0.010021 | 6.8834
STAFFORD 110242542 | STAFFORD 1102 | NORTH BAY | 0.92749 | 10 | 53.57% | 0 | 0 | 26.56% | 0% | 0 | 0.0094932 | 1 | 2.9041 | 0.027569 | Low | Low | Medium | 2823 | 2951 | 0.0094932 | 6.8557
PURISIMA 1101Y42 | PURISIMA 1101 | LOS PADRES | 0.33998 | 72.2951 | 27.05% | 0 | 0 | 2.02% | 0% | 0 | 0.010429 | 1 | 2.6418 | 0.02755 | Low | Low | Medium | 2824 | 2908 | 0.010429 | 6.8282
FLINT 1101CB | FLINT 1101 | SIERRA | 0.81732 | 10 | 11.07% | 0 | 2 | 31.46% | 0% | 0 | 0.008378 | 1 | 3.2795 | 0.027475 | Low | Low | High | 2825 | 2998 | 0.008378 | 6.8006
GRASS VALLEY 110358498 | GRASS VALLEY 1103 | SIERRA | 0.54343 | 10 | 37.4% | 0 | 2 | 23.91% | 0% | 0 | 0.0096407 | 1 | 2.8446 | 0.027424 | Low | Low | Medium | 2826 | 2945 | 0.0096407 | 6.7732
CAYUCOS 11014701 | CAYUCOS 1101 | LOS PADRES | 2.0826 | 72.227 | 28.46% | 1 | 0 | 23.77% | 0% | 0 | 0.011613 | 1 | 2.3562 | 0.027363 | Low | Low | Medium | 2827 | 2829 | 0.011613 | 6.7457
ELK CREEK 11012106 | ELK CREEK 1101 | NORTH VALLEY | 13.2055 | 80.5547 | 100% | 0 | 1 | 100% | 0% | 0 | 0.052586 | 1 | 0.52019 | 0.027355 | Medium | Medium | Low | 2828 | 1655 | 0.052586 | 6.7184
LUCERNE 11031280 | LUCERNE 1103 | HUMBOLDT | 8.886 | 18.4647 | 53.77% | 0 | 7 | 37.48% | 0% | 0 | 0.012974 | 1 | 2.1053 | 0.027314 | Low | Low | Low | 2829 | 2714 | 0.012974 | 6.691
SAN RAFAEL 1106837 | SAN RAFAEL 1106 | NORTH BAY | 0.43527 | 10 | 0% | 0 | 2 | 28.12% | 0% | 0 | 0.0074019 | 1 | 3.69 | 0.027313 | Low | Low | High | 2830 | 3035 | 0.0074019 | 6.6637
RESERVATION ROAD 11023032 | RESERVATION ROAD 1102 | CENTRAL COAST | 1.7351 | 10 | 40.39% | 0 | 1 | 17.91% | 0% | 0 | 0.010406 | 1 | 2.6242 | 0.027307 | Low | Low | Medium | 2831 | 2910 | 0.010406 | 6.6364
CORNING 110135974 | CORNING 1101 | NORTH VALLEY | 0.83179 | 10 | 47.68% | 0 | 0 | 100% | 0% | 0 | 0.02429 | 1 | 1.1214 | 0.027239 | Medium | Medium | Low | 2832 | 2268 | 0.02429 | 6.6091
GEYSERVILLE 1101122 | GEYSERVILLE 1101 | SONOMA | 3.5712 | 48.4332 | 60.55% | 0 | 3 | 18.96% | 0% | 0 | 0.012864 | 1 | 2.1153 | 0.027211 | Low | Low | Low | 2833 | 2720 | 0.012864 | 6.5818
SOLEDAD 21027008 | SOLEDAD 2102 | CENTRAL COAST | 1.2631 | 69.0048 | 38.01% | 0 | 0 | 6.974% | 0% | 0 | 0.011715 | 1 | 2.322 | 0.027202 | Low | Low | Medium | 2834 | 2820 | 0.011715 | 6.5546
COARSEGOLD 21036110 | COARSEGOLD 2103 | YOSEMITE | 9.9772 | 20.6713 | 95.13% | 0 | 5 | 33.47% | 0% | 0 | 0.016997 | 1 | 1.5993 | 0.027183 | Low | Low | Low | 2835 | 2529 | 0.016997 | 6.5274
FRUITLAND 11418860 | FRUITLAND 1141 | HUMBOLDT | 2.4992 | 72.7282 | 25.93% | 4 | 0 | 65.81% | 0% | 0 | 0.01798 | 1 | 1.5096 | 0.027143 | Low | Low | Low | 2836 | 2489 | 0.01798 | 6.5002
JOLON 1102CB | JOLON 1102 | CENTRAL COAST | 23.7338 | 63.1412 | 51.5% | 0 | 1 | 99.01% | 0% | 0 | 0.02781 | 1 | 0.97488 | 0.027111 | Medium | Medium | Low | 2837 | 2168 | 0.02781 | 6.4731
SUMMIT 1101CB | SUMMIT 1101 | SIERRA | 0.12475 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.016863 | 1 | 1.5975 | 0.026939 | Low | Low | Low | 2838 | 2534 | 0.016863 | 6.446
CAROLANDS 04049026 | CAROLANDS 0404 | PENINSULA | 0.27754 | 10 | 28.62% | 0 | 0 | 5.507% | 0% | 0 | 0.0071679 | 1 | 3.7571 | 0.026931 | Low | Low | High | 2839 | 3049 | 0.0071679 | 6.419
SUMMIT 11016627 | SUMMIT 1101 | SIERRA | 0.56142 | 10 | 45.61% | 0 | 0 | 100% | 0% | 0 | 0.01839 | 1 | 1.4632 | 0.026909 | Low | Low | Low | 2840 | 2470 | 0.01839 | 6.3921
MARIPOSA 210210250 | MARIPOSA 2102 | YOSEMITE | 0.04003 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.119 | 0.026901 | Low | Low | Low | 2841 | 2735 | 0.012695 | 6.3652
FRANKLIN 1104CB | FRANKLIN 1104 | EAST BAY | 0.64777 | 10 | 0% | 0 | 2 | 12.31% | 0% | 0 | 0.0072216 | 1 | 3.7113 | 0.026802 | Low | Low | High | 2842 | 3046 | 0.0072216 | 6.3383
PRUNEDALE 11103716 | PRUNEDALE 1110 | CENTRAL COAST | 0.046537 | 10 | 100% | 0 | 0 | 0.3534% | 0% | 0 | 0.010696 | 1 | 2.4997 | 0.026736 | Low | Low | Medium | 2843 | 2895 | 0.010696 | 6.3115
TEMPLETON 2113A32 | TEMPLETON 2113 | LOS PADRES | 0.77097 | 10 | 66.93% | 0 | 0 | 13.18% | 0% | 0 | 0.0092713 | 1 | 2.8821 | 0.026721 | Low | Low | Medium | 2844 | 2965 | 0.0092713 | 6.2848
SNEATH LANE 1107CB | SNEATH LANE 1107 | PENINSULA | 0.3748 | 10 | 41.65% | 0 | 1 | 9.682% | 0% | 0 | 0.0074343 | 1 | 3.594 | 0.026719 | Low | Low | High | 2845 | 3034 | 0.0074343 | 6.258
WYANDOTTE 1107CB | WYANDOTTE 1107 | NORTH VALLEY | 1.0691 | 10 | 31.7% | 0 | 1 | 7.068% | 0% | 0 | 0.0066762 | 1 | 3.9827 | 0.026589 | Low | Low | High | 2846 | 3067 | 0.0066762 | 6.2313
BEAR VALLEY 21054170 | BEAR VALLEY 2105 | YOSEMITE | 9.5178 | 57.2029 | 100% | 3 | 1 | 100% | 0% | 0 | 0.041292 | 1 | 0.64305 | 0.026553 | Medium | Medium | Low | 2847 | 1830 | 0.041292 | 6.2047
PEORIA 170488630 | PEORIA 1704 | YOSEMITE | 0.77831 | 38.0661 | 100% | 0 | 0 | 100% | 0% | 0 | 0.050412 | 1 | 0.52663 | 0.026548 | Medium | Medium | Low | 2848 | 1678 | 0.050412 | 6.1782
TRES PINOS 11114032 | TRES PINOS 1111 | CENTRAL COAST | 0.10269 | 70 | 100% | 0 | 0 | 0.5446% | 0% | 0 | 0.018321 | 1 | 1.4487 | 0.026542 | Low | Low | Low | 2849 | 2474 | 0.018321 | 6.1516
BRENTWOOD 210596324 | BRENTWOOD 2105 | DIABLO | 0.37122 | 10 | 0% | 0 | 0 | 76.98% | 0% | 0 | 0.010106 | 1 | 2.6232 | 0.02651 | Low | Low | Medium | 2850 | 2924 | 0.010106 | 6.1251
PEORIA 1701CB | PEORIA 1701 | YOSEMITE | 8.8374 | 31.1758 | 54.24% | 0 | 6 | 100% | 0% | 0 | 0.037882 | 1 | 0.69967 | 0.026505 | Medium | Medium | Low | 2851 | 1900 | 0.037882 | 6.0986
SONOMA 1107126 | SONOMA 1107 | SONOMA | 2.2583 | 59.5559 | 29.29% | 0 | 1 | 10.13% | 0% | 0 | 0.009446 | 1 | 2.8041 | 0.026487 | Low | Low | Medium | 2852 | 2956 | 0.009446 | 6.0721
JOLON 11027004 | JOLON 1102 | CENTRAL COAST | 5.4816 | 47.887 | 100% | 0 | 0 | 27.2% | 0% | 0 | 0.020525 | 1 | 1.2884 | 0.026445 | Low | Low | Low | 2853 | 2385 | 0.020525 | 6.0456
ELK 11014628 | ELK 1101 | HUMBOLDT | 2.8486 | 10 | 0% | 0 | 7 | 69.22% | 0% | 0 | 0.012349 | 1 | 2.1397 | 0.026424 | Low | Low | Low | 2854 | 2781 | 0.012349 | 6.0191
CLOVERDALE 1102670 | CLOVERDALE 1102 | SONOMA | 0.27521 | 10 | 95.35% | 0 | 0 | 6.733% | 0% | 0 | 0.01097 | 1 | 2.3989 | 0.026316 | Low | Low | Medium | 2855 | 2868 | 0.01097 | 5.9927
NOVATO 11041282 | NOVATO 1104 | NORTH BAY | 1.3064 | 10 | 9.821% | 0 | 6 | 28.52% | 0% | 0 | 0.008753 | 1 | 3.0035 | 0.026289 | Low | Low | Medium | 2856 | 2987 | 0.008753 | 5.9664
HICKS 1116LB16 | HICKS 1116 | SAN JOSE | 1.4512 | 10 | 12.53% | 1 | 1 | 15.83% | 0% | 0 | 0.0072028 | 1 | 3.6384 | 0.026207 | Low | Low | High | 2857 | 3048 | 0.0072028 | 5.9401
LOS GATOS 1101CB | LOS GATOS 1101 | DE ANZA | 0.83125 | 10 | 32.44% | 0 | 1 | 21.19% | 0% | 0 | 0.0077301 | 1 | 3.3892 | 0.026199 | Low | Low | High | 2858 | 3020 | 0.0077301 | 5.9139
POTTER VALLEY P H 110537476 | POTTER VALLEY P H 1105 | HUMBOLDT | 0.5064 | 62.972 | 86.61% | 0 | 3 | 5.941% | 0% | 0 | 0.015424 | 1 | 1.6964 | 0.026166 | Low | Low | Low | 2859 | 2592 | 0.015424 | 5.8877
LINCOLN 110195756 | LINCOLN 1101 | SIERRA | 3.5302 | 10.7023 | 65.54% | 2 | 0 | 19.54% | 0% | 0 | 0.010072 | 1 | 2.5936 | 0.026122 | Low | Low | Medium | 2860 | 2925 | 0.010072 | 5.8615
FAIRVIEW 2207M501R | FAIRVIEW 2207 | DIABLO | 1.376 | 10 | 11.91% | 1 | 2 | 29.22% | 0% | 0 | 0.0083598 | 1 | 3.1246 | 0.026121 | Low | Low | High | 2861 | 3001 | 0.0083598 | 5.8354
COAST RD 0401CB | COAST RD 0401 | CENTRAL COAST | 0.04709 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.0553 | 0.026093 | Low | Low | Low | 2862 | 2735 | 0.012695 | 5.8093
GONZALES 11033096 | GONZALES 1103 | CENTRAL COAST | 1.0413 | 57.173 | 49.23% | 0 | 0 | 5.766% | 0% | 0 | 0.011709 | 1 | 2.2241 | 0.026042 | Low | Low | Low | 2863 | 2821 | 0.011709 | 5.7832
CASTRO VALLEY 1106MR233 | CASTRO VALLEY 1106 | MISSION | 0.14387 | 10 | 11.99% | 0 | 0 | 22.61% | 0% | 0 | 0.0064943 | 1 | 3.9938 | 0.025937 | Low | Low | High | 2864 | 3079 | 0.0064943 | 5.7572
CARLOTTA 1121CB | CARLOTTA 1121 | HUMBOLDT | 3.8375 | 25.0692 | 63.58% | 0 | 0 | 16.59% | 0% | 0 | 0.010334 | 1 | 2.4931 | 0.025765 | Low | Low | Medium | 2865 | 2914 | 0.010334 | 5.7312
PETALUMA C 1109CB | PETALUMA C 1109 | SONOMA | 0.77473 | 10 | 39.24% | 0 | 1 | 15.77% | 0% | 0 | 0.007744 | 1 | 3.3257 | 0.025754 | Low | Low | High | 2866 | 3019 | 0.007744 | 5.7055
PAUL SWEET 210510290 | PAUL SWEET 2105 | CENTRAL COAST | 0.48079 | 10 | 22.97% | 0 | 0 | 8.329% | 0% | 0 | 0.0061637 | 1 | 4.1772 | 0.025747 | Low | Low | High | 2867 | 3097 | 0.0061637 | 5.6797
FORT BRAGG A 1102CB | FORT BRAGG A 1102 | HUMBOLDT | 1.663 | 13.8095 | 19.07% | 2 | 1 | 29% | 0% | 0 | 0.0078888 | 1 | 3.2475 | 0.025619 | Low | Low | High | 2868 | 3015 | 0.0078888 | 5.654
SNEATH LANE 110748338 | SNEATH LANE 1107 | PENINSULA | 0.48719 | 10 | 2.1% | 0 | 0 | 45.41% | 0% | 0 | 0.0075134 | 1 | 3.4081 | 0.025607 | Low | Low | High | 2869 | 3030 | 0.0075134 | 5.6284
PANORAMA 1102CB | PANORAMA 1102 | NORTH VALLEY | 0.071747 | 10 | 100% | 0 | 0 | 0.6421% | 0% | 0 | 0.010727 | 1 | 2.3856 | 0.025589 | Low | Low | Medium | 2870 | 2890 | 0.010727 | 5.6027
STONE CORRAL 11107320 | STONE CORRAL 1110 | FRESNO | 1.9474 | 22.4898 | 48.09% | 0 | 0 | 8.248% | 0% | 0 | 0.010731 | 1 | 2.3816 | 0.025558 | Low | Low | Medium | 2871 | 2889 | 0.010731 | 5.5772
ALTO 1123CB | ALTO 1123 | NORTH BAY | 2.3955 | 10 | 3.352% | 0 | 0 | 39.61% | 4.121% | 0 | 0.0076595 | 1 | 3.3336 | 0.025533 | Low | Low | High | 2872 | 3022 | 0.0076595 | 5.5516
ELK 11011298 | ELK 1101 | HUMBOLDT | 13.5042 | 33.0971 | 18.55% | 6 | 11 | 83.72% | 0% | 0 | 0.022711 | 1 | 1.1193 | 0.025419 | Medium | Medium | Low | 2873 | 2316 | 0.022711 | 5.5261
TRIDAM POWERHOUSE 2101CB | TRIDAM POWERHOUSE 2101 | YOSEMITE | 0.050313 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.89044 | 0.025388 | Medium | Medium | Low | 2874 | 2132 | 0.028512 | 5.5006
OTTER 11022012 | OTTER 1102 | CENTRAL COAST | 9.1781 | 41.691 | 0% | 3 | 4 | 91.18% | 0% | 0 | 0.018558 | 1 | 1.3664 | 0.025359 | Low | Low | Low | 2875 | 2462 | 0.018558 | 5.4753
ARLINGTON 0401CB | ARLINGTON 0401 | EAST BAY | 0.76473 | 10 | 0% | 0 | 1 | 19.15% | 0% | 0 | 0.005806 | 1 | 4.3631 | 0.025332 | Low | Low | High | 2876 | 3112 | 0.005806 | 5.4499
FITCH MOUNTAIN 1113154 | FITCH MOUNTAIN 1113 | SONOMA | 2.1793 | 18.0666 | 70.63% | 0 | 0 | 11.51% | 0% | 0 | 0.0099274 | 1 | 2.5363 | 0.025179 | Low | Low | Medium | 2877 | 2931 | 0.0099274 | 5.4246
OCEANO 1106V28 | OCEANO 1106 | LOS PADRES | 1.0201 | 10 | 22.73% | 0 | 0 | 11.28% | 0% | 0 | 0.006335 | 1 | 3.973 | 0.025169 | Low | Low | High | 2878 | 3087 | 0.006335 | 5.3994
FAIRVIEW 2207CB | FAIRVIEW 2207 | DIABLO | 0.060291 | 10 | 69.19% | 0 | 0 | 1.178% | 0% | 0 | 0.0083828 | 1 | 2.9891 | 0.025057 | Low | Low | Medium | 2879 | 2997 | 0.0083828 | 5.3742
RESERVATION ROAD 1101CB | RESERVATION ROAD 1101 | CENTRAL COAST | 3.6814 | 10 | 45.32% | 0 | 3 | 39.08% | 0% | 0 | 0.013924 | 1 | 1.799 | 0.025049 | Low | Low | Low | 2880 | 2666 | 0.013924 | 5.3492
COVELO 110137328 | COVELO 1101 | HUMBOLDT | 3.9213 | 85.1621 | 100% | 0 | 0 | 16.63% | 0% | 0 | 0.020839 | 1 | 1.2015 | 0.025038 | Low | Low | Low | 2881 | 2374 | 0.020839 | 5.3241
IGNACIO 1104316 | IGNACIO 1104 | NORTH BAY | 0.5655 | 10 | 40.98% | 0 | 2 | 6.524% | 0% | 0 | 0.0073158 | 1 | 3.4198 | 0.025018 | Low | Low | High | 2882 | 3040 | 0.0073158 | 5.2991
GARBERVILLE 110139524 | GARBERVILLE 1101 | HUMBOLDT | 5.5428 | 59.5329 | 86.83% | 1 | 2 | 35.93% | 0% | 0 | 0.020129 | 1 | 1.2425 | 0.02501 | Low | Low | Low | 2883 | 2403 | 0.020129 | 5.2741
OLEMA 1101320 | OLEMA 1101 | NORTH BAY | 0.033859 | 54.8898 | 25.18% | 0 | 1 | 0.2531% | 0% | 0 | 0.0091583 | 1 | 2.7217 | 0.024926 | Low | Low | Medium | 2884 | 2971 | 0.0091583 | 5.249
OAKLAND J 1118CR198 | OAKLAND J 1118 | EAST BAY | 0.38627 | 10 | 34.69% | 0 | 0 | 7.348% | 0% | 0 | 0.0076722 | 1 | 3.2489 | 0.024926 | Low | Low | High | 2885 | 3021 | 0.0076722 | 5.2241
UKIAH 1114CB | UKIAH 1114 | HUMBOLDT | 1.2249 | 10 | 45.97% | 1 | 2 | 14.08% | 0% | 0 | 0.0083238 | 1 | 2.9939 | 0.024921 | Low | Low | Medium | 2886 | 3003 | 0.0083238 | 5.1992
UPPER LAKE 1101660 | UPPER LAKE 1101 | HUMBOLDT | 7.1376 | 10 | 50.04% | 0 | 2 | 74.17% | 0% | 0 | 0.015402 | 1 | 1.6171 | 0.024907 | Low | Low | Low | 2887 | 2593 | 0.015402 | 5.1743
CASTRO VALLEY 1104MR201 | CASTRO VALLEY 1104 | MISSION | 1.8766 | 10 | 10.28% | 0 | 1 | 19.54% | 0% | 0 | 0.007241 | 1 | 3.4354 | 0.024876 | Low | Low | High | 2888 | 3045 | 0.007241 | 5.1494
HOPLAND 1101770 | HOPLAND 1101 | HUMBOLDT | 8.7193 | 58.1602 | 26.75% | 1 | 4 | 57.45% | 0% | 0 | 0.015784 | 1 | 1.5698 | 0.024778 | Low | Low | Low | 2889 | 2584 | 0.015784 | 5.1245
POTTER VALLEY P H 110495878 | POTTER VALLEY P H 1104 | HUMBOLDT | 6.3973 | 36.9398 | 60.01% | 0 | 4 | 34.83% | 8.674% | 0 | 0.01627 | 1 | 1.5212 | 0.024749 | Low | Low | Low | 2890 | 2561 | 0.01627 | 5.0997
WILLITS 110337504 | WILLITS 1103 | HUMBOLDT | 0.81372 | 28.0694 | 47.51% | 0 | 2 | 22.82% | 0% | 0 | 0.010255 | 1 | 2.412 | 0.024736 | Low | Low | Medium | 2891 | 2918 | 0.010255 | 5.075
SPENCE 1123CB | SPENCE 1123 | CENTRAL COAST | 2.0801 | 71.6022 | 100% | 0 | 0 | 6.177% | 0% | 0 | 0.017169 | 1 | 1.4373 | 0.024677 | Low | Low | Low | 2892 | 2523 | 0.017169 | 5.0502
BOLINAS 11011064 | BOLINAS 1101 | NORTH BAY | 0.79432 | 10 | 14.47% | 2 | 1 | 17.88% | 0% | 0 | 0.0075676 | 1 | 3.2571 | 0.024648 | Low | Low | High | 2893 | 3026 | 0.0075676 | 5.0255
HARTLEY 1101CB | HARTLEY 1101 | HUMBOLDT | 1.2777 | 10 | 19.8% | 0 | 1 | 42.25% | 0% | 0 | 0.0098099 | 1 | 2.5013 | 0.024537 | Low | Low | Medium | 2894 | 2939 | 0.0098099 | 5.0009
HALF MOON BAY 110265568 | HALF MOON BAY 1102 | PENINSULA | 0.079124 | 10 | 0% | 0 | 0 | 2.534% | 0% | 0 | 0.0062845 | 1 | 3.8984 | 0.0245 | Low | Low | High | 2895 | 3089 | 0.0062845 | 4.9764
OAKLAND K 1103CB | OAKLAND K 1103 | EAST BAY | 0.65834 | 10 | 0% | 1 | 2 | 13.28% | 0% | 0 | 0.0056661 | 1 | 4.3233 | 0.024496 | Low | Low | High | 2896 | 3120 | 0.0056661 | 4.9519
OCEANO 110376678 | OCEANO 1103 | LOS PADRES | 0.055262 | 10 | 22.91% | 0 | 2 | 14.84% | 0% | 0 | 0.0068538 | 1 | 3.5692 | 0.024463 | Low | Low | High | 2897 | 3061 | 0.0068538 | 4.9274
COTTONWOOD 110131500 | COTTONWOOD 1101 | NORTH VALLEY | 3.2216 | 22.5046 | 96% | 0 | 0 | 27.31% | 0% | 0 | 0.01471 | 1 | 1.6607 | 0.024428 | Low | Low | Low | 2898 | 2625 | 0.01471 | 4.9029
WYANDOTTE 110213914 | WYANDOTTE 1102 | NORTH VALLEY | 0.60739 | 10 | 33.65% | 0 | 0 | 34.43% | 0% | 0 | 0.0087222 | 1 | 2.7969 | 0.024396 | Low | Low | Medium | 2899 | 2989 | 0.0087222 | 4.8785
ALHAMBRA 1105CB | ALHAMBRA 1105 | DIABLO | 0.38371 | 10 | 15.25% | 0 | 0 | 20.22% | 0% | 0 | 0.0074366 | 1 | 3.2796 | 0.02439 | Low | Low | High | 2900 | 3033 | 0.0074366 | 4.8541
HARRIS 11084674 | HARRIS 1108 | HUMBOLDT | 0.15936 | 10 | 0% | 0 | 0 | 1.98% | 0% | 0 | 0.0047917 | 1 | 5.073 | 0.024308 | Low | Low | High | 2901 | 3164 | 0.0047917 | 4.8297
POTTER VALLEY P H 110564118 | POTTER VALLEY P H 1105 | HUMBOLDT | 1.7203 | 30.1363 | 62.86% | 2 | 1 | 18.17% | 0% | 0 | 0.014734 | 1 | 1.6469 | 0.024265 | Low | Low | Low | 2902 | 2623 | 0.014734 | 4.8054
KONOCTI 110264464 | KONOCTI 1102 | HUMBOLDT | 0.53615 | 10 | 9.05% | 1 | 0 | 19.93% | 0% | 0 | 0.0081536 | 1 | 2.9706 | 0.024221 | Low | Low | Medium | 2903 | 3007 | 0.0081536 | 4.7811
MORRO BAY 1101W20 | MORRO BAY 1101 | LOS PADRES | 1.8981 | 10 | 0% | 0 | 1 | 48.29% | 0% | 0 | 0.0077601 | 1 | 3.1154 | 0.024176 | Low | Low | High | 2904 | 3018 | 0.0077601 | 4.7569
EEL RIVER 110249130 | EEL RIVER 1102 | HUMBOLDT | 1.458 | 43.0989 | 47.28% | 0 | 1 | 10.5% | 0% | 0 | 0.0098241 | 1 | 2.4567 | 0.024135 | Low | Low | Medium | 2905 | 2937 | 0.0098241 | 4.7327
PEORIA 170176030 | PEORIA 1701 | YOSEMITE | 5.4729 | 32.855 | 62.69% | 0 | 1 | 88.26% | 0% | 0 | 0.022385 | 1 | 1.0774 | 0.024117 | Medium | Medium | Low | 2906 | 2321 | 0.022385 | 4.7086
PAUL SWEET 210212850 | PAUL SWEET 2102 | CENTRAL COAST | 0.99852 | 10 | 0% | 0 | 0 | 24.38% | 0% | 0 | 0.0059903 | 1 | 4.0239 | 0.024104 | Low | Low | High | 2907 | 3108 | 0.0059903 | 4.6845
KERN OIL 110646960 | KERN OIL 1106 | KERN | 1.1498 | 10 | 1.744% | 0 | 0 | 59.65% | 0% | 0 | 0.0086311 | 1 | 2.7916 | 0.024095 | Low | Low | Medium | 2908 | 2992 | 0.0086311 | 4.6604
PANORAMA 1101CB | PANORAMA 1101 | NORTH VALLEY | 1.9355 | 10 | 100% | 0 | 2 | 10.24% | 0% | 0 | 0.012297 | 1 | 1.9576 | 0.024072 | Low | Low | Low | 2909 | 2787 | 0.012297 | 4.6363
SILVERADO 210298998 | SILVERADO 2102 | NORTH BAY | 4.5559 | 48.6012 | 79.99% | 0 | 0 | 16.02% | 0% | 0 | 0.015709 | 1 | 1.5297 | 0.024031 | Low | Low | Low | 2910 | 2586 | 0.015709 | 4.6122
TEMPLETON 2113A30 | TEMPLETON 2113 | LOS PADRES | 0.53596 | 10 | 10.42% | 0 | 0 | 34.36% | 0% | 0 | 0.0082271 | 1 | 2.9117 | 0.023955 | Low | Low | Medium | 2911 | 3006 | 0.0082271 | 4.5882
ALHAMBRA 110213333 | ALHAMBRA 1102 | DIABLO | 0.074793 | 10 | 23.29% | 0 | 0 | 25.18% | 0% | 0 | 0.007309 | 1 | 3.2612 | 0.023836 | Low | Low | High | 2912 | 3041 | 0.007309 | 4.5642
IONE 1101CB | IONE 1101 | STOCKTON | 1.9633 | 49.7739 | 2.974% | 1 | 0 | 13.95% | 0% | 0 | 0.007346 | 1 | 3.2391 | 0.023794 | Low | Low | High | 2913 | 3038 | 0.007346 | 4.5404
TEJON 11032280 | TEJON 1103 | KERN | 2.7582 | 10 | 100% | 0 | 0 | 9.965% | 0% | 0 | 0.011765 | 1 | 2.0211 | 0.023777 | Low | Low | Low | 2914 | 2817 | 0.011765 | 4.5166
EL CERRITO G 1108CB | EL CERRITO G 1108 | EAST BAY | 0.47538 | 10 | 0% | 0 | 0 | 6.483% | 0% | 0 | 0.0050118 | 1 | 4.7287 | 0.023699 | Low | Low | High | 2915 | 3145 | 0.0050118 | 4.4928
EAST MARYSVILLE 11081706 | EAST MARYSVILLE 1108 | SIERRA | 0.35809 | 10 | 100% | 0 | 0 | 0.5923% | 0% | 0 | 0.010721 | 1 | 2.2096 | 0.02369 | Low | Low | Low | 2916 | 2893 | 0.010721 | 4.4691
MADISON 21011943 | MADISON 2101 | SACRAMENTO | 0.028904 | 10 | 100% | 0 | 0 | 0.9967% | 0% | 0 | 0.010764 | 1 | 2.1991 | 0.023671 | Low | Low | Low | 2917 | 2886 | 0.010764 | 4.4454
LAKEWOOD 210769586 | LAKEWOOD 2107 | DIABLO | 0.5706 | 16.4781 | 12.07% | 0 | 2 | 6.994% | 0% | 0 | 0.0069201 | 1 | 3.4182 | 0.023654 | Low | Low | High | 2918 | 3057 | 0.0069201 | 4.4217
GARBERVILLE 11011770 | GARBERVILLE 1101 | HUMBOLDT | 8.6092 | 87.0246 | 95.86% | 7 | 3 | 100% | 0% | 0 | 0.087398 | 1 | 0.26991 | 0.02359 | High | High | Low | 2919 | 1347 | 0.087398 | 4.3981
MORGAN HILL 2105XR578 | MORGAN HILL 2105 | SAN JOSE | 0.218 | 10 | 8.67% | 0 | 0 | 31.62% | 0% | 0 | 0.0069127 | 1 | 3.4108 | 0.023578 | Low | Low | High | 2920 | 3058 | 0.0069127 | 4.3745
MC ARTHUR 11011546 | MC ARTHUR 1101 | NORTH VALLEY | 13.3497 | 54.7981 | 96.53% | 1 | 1 | 58.43% | 0% | 0 | 0.025754 | 1 | 0.91531 | 0.023572 | Medium | Medium | Low | 2921 | 2223 | 0.025754 | 4.3509
HOLLISTER 210491424 | HOLLISTER 2104 | CENTRAL COAST | 0.19482 | 10 | 75.59% | 0 | 0 | 2.224% | 0% | 0 | 0.0089256 | 1 | 2.6389 | 0.023554 | Low | Low | Medium | 2922 | 2981 | 0.0089256 | 4.3274
COTATI 1105893 | COTATI 1105 | SONOMA | 0.50896 | 59.1092 | 51.41% | 0 | 0 | 4.828% | 0% | 0 | 0.010484 | 1 | 2.2464 | 0.023552 | Low | Low | Medium | 2923 | 2905 | 0.010484 | 4.3038
HALF MOON BAY 1102CB | HALF MOON BAY 1102 | PENINSULA | 0.43987 | 10 | 9.941% | 0 | 1 | 10.85% | 0% | 0 | 0.0057997 | 1 | 4.0421 | 0.023443 | Low | Low | High | 2924 | 3114 | 0.0057997 | 4.2802
DEL MAR 2109CB | DEL MAR 2109 | SIERRA | 1.7939 | 12.1972 | 19.79% | 0 | 1 | 27.43% | 0% | 0 | 0.0075272 | 1 | 3.1113 | 0.023419 | Low | Low | High | 2925 | 3029 | 0.0075272 | 4.2568
ESTUDILLO 0401CB | ESTUDILLO 0401 | MISSION | 0.69789 | 10 | 26.72% | 0 | 0 | 14.78% | 0% | 0 | 0.0067781 | 1 | 3.4546 | 0.023416 | Low | Low | High | 2926 | 3064 | 0.0067781 | 4.2334
TAR FLAT 0402CB | TAR FLAT 0402 | YOSEMITE | 0.52249 | 10 | 7.104% | 0 | 0 | 35.32% | 0% | 0 | 0.0070807 | 1 | 3.3002 | 0.023368 | Low | Low | High | 2927 | 3052 | 0.0070807 | 4.21
ELK CREEK 11012004 | ELK CREEK 1101 | NORTH VALLEY | 14.9707 | 82.0149 | 100% | 0 | 1 | 27.7% | 0% | 0 | 0.034268 | 1 | 0.68104 | 0.023338 | Medium | Medium | Low | 2928 | 1966 | 0.034268 | 4.1866
PIT NO 1 11011552 | PIT NO 1 1101 | NORTH VALLEY | 9.8425 | 12.4749 | 95.95% | 1 | 1 | 37.18% | 0% | 0 | 0.023212 | 1 | 1.0048 | 0.023324 | Medium | Medium | Low | 2929 | 2303 | 0.023212 | 4.1633
AUBURN 1102CB | AUBURN 1102 | SIERRA | 0.41789 | 10 | 46.75% | 0 | 2 | 6.005% | 0% | 0 | 0.0076302 | 1 | 3.055 | 0.02331 | Low | Low | Medium | 2930 | 3025 | 0.0076302 | 4.1399
EEL RIVER 1102530 | EEL RIVER 1102 | HUMBOLDT | 5.0874 | 49.3959 | 37.23% | 9 | 0 | 15.69% | 0% | 0 | 0.010956 | 1 | 2.1273 | 0.023307 | Low | Low | Low | 2931 | 2870 | 0.010956 | 4.1166
TULE POWER HOUSE 1101CB | TULE POWER HOUSE 1101 | FRESNO | 4.0927 | 57.029 | 3.215% | 0 | 0 | 100% | 0% | 0 | 0.01789 | 1 | 1.3019 | 0.023291 | Low | Low | Low | 2932 | 2494 | 0.01789 | 4.0933
EL CERRITO G 1108BR346 | EL CERRITO G 1108 | EAST BAY | 0.1038 | 10 | 0% | 0 | 0 | 1.483% | 0% | 0 | 0.004768 | 1 | 4.878 | 0.023259 | Low | Low | High | 2933 | 3168 | 0.004768 | 4.07
OCEANO 1105V16 | OCEANO 1105 | LOS PADRES | 1.6064 | 10 | 0% | 0 | 0 | 44.18% | 0% | 0 | 0.0072956 | 1 | 3.1854 | 0.023239 | Low | Low | High | 2934 | 3042 | 0.0072956 | 4.0468
ALHAMBRA 110595016 | ALHAMBRA 1105 | DIABLO | 0.37201 | 51.8878 | 0% | 0 | 0 | 9.208% | 0% | 0 | 0.0078178 | 1 | 2.9552 | 0.023103 | Low | Low | Medium | 2935 | 3017 | 0.0078178 | 4.0235
BEAR VALLEY 210110000 | BEAR VALLEY 2101 | YOSEMITE | 29.476 | 56.7898 | 61.86% | 4 | 0 | 88.5% | 0% | 0 | 0.039743 | 1 | 0.58061 | 0.023075 | Medium | Medium | Low | 2936 | 1863 | 0.039743 | 4.0004
IGNACIO 11041290 | IGNACIO 1104 | NORTH BAY | 1.6542 | 10 | 24.98% | 1 | 1 | 15.64% | 0% | 0 | 0.0079604 | 1 | 2.8977 | 0.023067 | Low | Low | Medium | 2937 | 3013 | 0.0079604 | 3.9774
TIDEWATER 210695842 | TIDEWATER 2106 | DIABLO | 0.21866 | 10 | 7.343% | 0 | 0 | 20.55% | 0% | 0 | 0.0061241 | 1 | 3.7665 | 0.023066 | Low | Low | High | 2938 | 3100 | 0.0061241 | 3.9543
GEYSERVILLE 110289714 | GEYSERVILLE 1102 | SONOMA | 1.4773 | 46.3035 | 100% | 0 | 0 | 11.51% | 0% | 0 | 0.015262 | 1 | 1.5055 | 0.022977 | Low | Low | Low | 2939 | 2600 | 0.015262 | 3.9312
SNEATH LANE 1101CB | SNEATH LANE 1101 | PENINSULA | 0.21236 | 10 | 2.867% | 0 | 1 | 21.58% | 0% | 0 | 0.0060901 | 1 | 3.7657 | 0.022933 | Low | Low | High | 2940 | 3102 | 0.0060901 | 3.9082
HARTLEY 1102CB | HARTLEY 1102 | HUMBOLDT | 2.7707 | 10 | 40.84% | 0 | 2 | 23.94% | 0% | 0 | 0.0099181 | 1 | 2.3095 | 0.022906 | Low | Low | Medium | 2941 | 2932 | 0.0099181 | 3.8853
OROSI 11027948F | OROSI 1102 | FRESNO | 0.26307 | 10 | 100% | 0 | 0 | 3.077% | 0% | 0 | 0.010989 | 1 | 2.0809 | 0.022866 | Low | Low | Low | 2942 | 2865 | 0.010989 | 3.8624
POINT MORETTI 110183716 | POINT MORETTI 1101 | CENTRAL COAST | 2.5672 | 18.0705 | 6.579% | 5 | 0 | 94.36% | 0% | 0 | 0.014279 | 1 | 1.6002 | 0.022849 | Low | Low | Low | 2943 | 2642 | 0.014279 | 3.8395
SARATOGA 1105CB | SARATOGA 1105 | DE ANZA | 0.26967 | 10 | 28.45% | 0 | 0 | 4.984% | 0% | 0 | 0.0062358 | 1 | 3.6613 | 0.022831 | Low | Low | High | 2944 | 3094 | 0.0062358 | 3.8167
PACIFICA 1104CB | PACIFICA 1104 | PENINSULA | 0.50255 | 42.4378 | 0% | 0 | 0 | 11.92% | 0% | 0 | 0.006597 | 1 | 3.4551 | 0.022793 | Low | Low | High | 2945 | 3073 | 0.006597 | 3.7939
CASTRO VALLEY 1104MR236 | CASTRO VALLEY 1104 | MISSION | 1.7251 | 10 | 10.02% | 0 | 1 | 20.44% | 0% | 0 | 0.0063847 | 1 | 3.5607 | 0.022734 | Low | Low | High | 2946 | 3086 | 0.0063847 | 3.7711
PENRYN 11051378 | PENRYN 1105 | SIERRA | 0.3076 | 10 | 15.69% | 2 | 1 | 16.27% | 0% | 0 | 0.0065875 | 1 | 3.4493 | 0.022722 | Low | Low | High | 2947 | 3076 | 0.0065875 | 3.7483
MORRO BAY 1101CB | MORRO BAY 1101 | LOS PADRES | 0.64776 | 10 | 6.384% | 0 | 0 | 29.39% | 0% | 0 | 0.0066355 | 1 | 3.4209 | 0.0227 | Low | Low | High | 2948 | 3070 | 0.0066355 | 3.7256
COTTONWOOD 1103CB | COTTONWOOD 1103 | NORTH VALLEY | 0.091321 | 14.0615 | 100% | 0 | 0 | 0.8116% | 0% | 0 | 0.011044 | 1 | 2.0553 | 0.022699 | Low | Low | Low | 2949 | 2863 | 0.011044 | 3.7029
BAYWOOD 1101CB | BAYWOOD 1101 | LOS PADRES | 1.4233 | 43.3041 | 38.16% | 0 | 0 | 4.9% | 0% | 0 | 0.008459 | 1 | 2.6765 | 0.022641 | Low | Low | Medium | 2950 | 2996 | 0.008459 | 3.6802
SAN LUIS OBISPO 1104645976 | SAN LUIS OBISPO 1104 | LOS PADRES | 2.1274 | 42.6681 | 27.62% | 0 | 0 | 32.32% | 0% | 0 | 0.010145 | 1 | 2.231 | 0.022633 | Low | Low | Medium | 2951 | 2921 | 0.010145 | 3.6576
SISQUOC 1102M54 | SISQUOC 1102 | LOS PADRES | 17.0931 | 11.3388 | 62.6% | 1 | 3 | 56.95% | 1.375% | 0 | 0.022753 | 1 | 0.99426 | 0.022622 | Medium | Medium | Low | 2952 | 2315 | 0.022753 | 3.6349
SUNOL 1101MR169 | SUNOL 1101 | MISSION | 3.8873 | 57.3439 | 37.68% | 0 | 0 | 41.76% | 0% | 0 | 0.013353 | 1 | 1.6919 | 0.022592 | Low | Low | Low | 2953 | 2694 | 0.013353 | 3.6123
TASSAJARA 211238868 | TASSAJARA 2112 | DIABLO | 0.17353 | 10 | 11.26% | 2 | 2 | 4.039% | 0% | 0 | 0.0057426 | 1 | 3.9277 | 0.022555 | Low | Low | High | 2954 | 3117 | 0.0057426 | 3.5897
COARSEGOLD 210490356 | COARSEGOLD 2104 | YOSEMITE | 4.6415 | 10 | 96.81% | 0 | 4 | 27.05% | 0% | 0 | 0.014744 | 1 | 1.5262 | 0.022503 | Low | Low | Low | 2955 | 2622 | 0.014744 | 3.5672
VIEJO 22049540 | VIEJO 2204 | CENTRAL COAST | 0.84933 | 10 | 0% | 3 | 2 | 38.01% | 0% | 0 | 0.0074407 | 1 | 3.0127 | 0.022417 | Low | Low | Medium | 2956 | 3032 | 0.0074407 | 3.5447
SUMMIT 110158642 | SUMMIT 1101 | SIERRA | 1.9126 | 10 | 32.51% | 0 | 1 | 100% | 0% | 0 | 0.019248 | 1 | 1.1597 | 0.022322 | Low | Low | Low | 2957 | 2433 | 0.019248 | 3.5222
RED BLUFF 11041630 | RED BLUFF 1104 | NORTH VALLEY | 2.5495 | 10 | 100% | 0 | 1 | 18.04% | 0% | 0 | 0.01301 | 1 | 1.715 | 0.022313 | Low | Low | Low | 2958 | 2713 | 0.01301 | 3.4999
VASONA 1102CB | VASONA 1102 | DE ANZA | 0.06716 | 10 | 0% | 0 | 0 | 0.4408% | 0% | 0 | 0.0047187 | 1 | 4.7083 | 0.022217 | Low | Low | High | 2959 | 3176 | 0.0047187 | 3.4776
FORT BRAGG A 1102 | FORT BRAGG A 1102 | HUMBOLDT | 0.10961 | 10 | 0% | 0 | 0 | 85.38% | 0% | 0 | 0.010984 | 1 | 2.0184 | 0.02217 | Low | Low | Low | 2960 | 2866 | 0.010984 | 3.4554
FAIRVIEW 2207P142 | FAIRVIEW 2207 | DIABLO | 0.64407 | 10 | 4.931% | 0 | 0 | 20.76% | 0% | 0 | 0.0060169 | 1 | 3.6784 | 0.022132 | Low | Low | High | 2961 | 3107 | 0.0060169 | 3.4332
SAN MIGUEL 1104R66 | SAN MIGUEL 1104 | LOS PADRES | 8.3967 | 54.4532 | 99.05% | 0 | 3 | 18.97% | 0% | 0 | 0.020883 | 1 | 1.0549 | 0.02203 | Low | Low | Low | 2962 | 2373 | 0.020883 | 3.4111
COTATI 1105616 | COTATI 1105 | SONOMA | 0.88156 | 51.5142 | 16.32% | 0 | 0 | 2.877% | 0% | 0 | 0.0083693 | 1 | 2.6305 | 0.022015 | Low | Low | Medium | 2963 | 2999 | 0.0083693 | 3.3891
SUNOL 1101CB | SUNOL 1101 | MISSION | 3.3865 | 29.3526 | 12.99% | 0 | 0 | 58.39% | 0% | 0 | 0.010654 | 1 | 2.0615 | 0.021963 | Low | Low | Low | 2964 | 2898 | 0.010654 | 3.367
BEAR VALLEY 210511210 | BEAR VALLEY 2105 | YOSEMITE | 17.0195 | 54.7309 | 100% | 0 | 6 | 100% | 0% | 0 | 0.049124 | 1 | 0.44607 | 0.021913 | Medium | Medium | Low | 2965 | 1693 | 0.049124 | 3.3451
OCEANO 1106CB | OCEANO 1106 | LOS PADRES | 0.86306 | 10 | 5.571% | 1 | 4 | 19.68% | 0% | 0 | 0.0065904 | 1 | 3.3208 | 0.021885 | Low | Low | High | 2966 | 3075 | 0.0065904 | 3.3232
CLARKSVILLE 2106CB | CLARKSVILLE 2106 | SIERRA | 0.13957 | 10 | 0% | 0 | 0 | 27.21% | 0% | 0 | 0.0061619 | 1 | 3.5511 | 0.021882 | Low | Low | High | 2967 | 3098 | 0.0061619 | 3.3013
SAN RAFAEL 110648752 | SAN RAFAEL 1106 | NORTH BAY | 0.61983 | 10 | 0% | 0 | 1 | 26.76% | 0% | 0 | 0.0062637 | 1 | 3.4892 | 0.021855 | Low | Low | High | 2968 | 3090 | 0.0062637 | 3.2794
OAKLAND J 1105CR132 | OAKLAND J 1105 | EAST BAY | 0.28914 | 10 | 34.84% | 0 | 0 | 6.37% | 0% | 0 | 0.0066625 | 1 | 3.2608 | 0.021725 | Low | Low | High | 2969 | 3068 | 0.0066625 | 3.2575
ATASCADERO 1103A46 | ATASCADERO 1103 | LOS PADRES | 0.63104 | 65.2454 | 33.62% | 0 | 0 | 6.794% | 0% | 0 | 0.0096376 | 1 | 2.251 | 0.021694 | Low | Low | Medium | 2970 | 2946 | 0.0096376 | 3.2358
PACIFICA 1103CB | PACIFICA 1103 | PENINSULA | 0.044512 | 50.42 | 0% | 0 | 0 | 0.9046% | 0% | 0 | 0.0062412 | 1 | 3.4634 | 0.021616 | Low | Low | High | 2971 | 3093 | 0.0062412 | 3.2141
SAN RAFAEL 11092213 | SAN RAFAEL 1109 | NORTH BAY | 0.014561 | 10 | 0% | 0 | 0 | 3.395% | 0% | 0 | 0.0048598 | 1 | 4.438 | 0.021568 | Low | Low | High | 2972 | 3156 | 0.0048598 | 3.1925
VIEJO 22029488 | VIEJO 2202 | CENTRAL COAST | 0.18548 | 10 | 0% | 0 | 0 | 14.19% | 0% | 0 | 0.0054123 | 1 | 3.9833 | 0.021559 | Low | Low | High | 2973 | 3128 | 0.0054123 | 3.1709
BERESFORD 0403CB | BERESFORD 0403 | PENINSULA | 0.94707 | 10 | 19.89% | 1 | 1 | 17.08% | 0% | 0 | 0.0067843 | 1 | 3.1734 | 0.02153 | Low | Low | High | 2974 | 3063 | 0.0067843 | 3.1494
WOODSIDE 11028862 | WOODSIDE 1102 | PENINSULA | 0.10582 | 10 | 0% | 0 | 0 | 2.762% | 0% | 0 | 0.0048292 | 1 | 4.4266 | 0.021377 | Low | Low | High | 2975 | 3161 | 0.0048292 | 3.1279
MORRO BAY 1101V70 | MORRO BAY 1101 | LOS PADRES | 0.13653 | 10 | 0% | 0 | 0 | 22.43% | 0% | 0 | 0.0058754 | 1 | 3.6321 | 0.02134 | Low | Low | High | 2976 | 3111 | 0.0058754 | 3.1065
LAS GALLINAS A 1105CB | LAS GALLINAS A 1105 | NORTH BAY | 0.31033 | 10 | 12.89% | 0 | 0 | 14.92% | 0% | 0 | 0.0060597 | 1 | 3.5062 | 0.021246 | Low | Low | High | 2977 | 3104 | 0.0060597 | 3.0851
SALT SPRINGS 21014913 | SALT SPRINGS 2101 | STOCKTON | 3.8651 | 10 | 100% | 0 | 2 | 100% | 0% | 0 | 0.029697 | 1 | 0.71504 | 0.021235 | Medium | Medium | Low | 2978 | 2107 | 0.029697 | 3.0639
COTTONWOOD 1101CB | COTTONWOOD 1101 | NORTH VALLEY | 5.2937 | 10 | 60.95% | 2 | 2 | 23.27% | 0% | 0 | 0.010444 | 1 | 2.0305 | 0.021206 | Low | Low | Low | 2979 | 2907 | 0.010444 | 3.0427
OCEANO 1104Q04 | OCEANO 1104 | LOS PADRES | 0.015582 | 10 | 0% | 0 | 0 | 0.5987% | 0% | 0 | 0.0047262 | 1 | 4.4629 | 0.021092 | Low | Low | High | 2980 | 3175 | 0.0047262 | 3.0215
SAUSALITO 11021224 | SAUSALITO 1102 | NORTH BAY | 0.046722 | 10 | 29.73% | 0 | 0 | 1.494% | 0% | 0 | 0.0060863 | 1 | 3.4619 | 0.02107 | Low | Low | High | 2981 | 3103 | 0.0060863 | 3.0004
NARROWS 2104CB | NARROWS 2104 | SIERRA | 0.002841 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.6515 | 0.020967 | Low | Low | Low | 2982 | 2735 | 0.012695 | 2.9793
ZACA 1101Y70 | ZACA 1101 | LOS PADRES | 5.1032 | 39.0808 | 69.39% | 0 | 1 | 58.75% | 0% | 0 | 0.018441 | 1 | 1.1363 | 0.020954 | Low | Low | Low | 2983 | 2469 | 0.018441 | 2.9583
FRUITLAND 11413902 | FRUITLAND 1141 | HUMBOLDT | 5.0988 | 85.765 | 7.833% | 1 | 0 | 99.69% | 0% | 0 | 0.025906 | 1 | 0.80512 | 0.020857 | Medium | Medium | Low | 2984 | 2216 | 0.025906 | 2.9374
SUMMIT 110186658 | SUMMIT 1101 | SIERRA | 0.66943 | 10 | 1.926% | 3 | 0 | 100% | 0% | 0 | 0.015299 | 1 | 1.3569 | 0.020759 | Low | Low | Low | 2985 | 2597 | 0.015299 | 2.9165
MARIPOSA 210190180 | MARIPOSA 2101 | YOSEMITE | 4.7841 | 52.2474 | 63.07% | 0 | 2 | 100% | 0% | 0 | 0.033288 | 1 | 0.62236 | 0.020717 | Medium | Medium | Low | 2986 | 1999 | 0.033288 | 2.8958
CALPELLA 1102496 | CALPELLA 1102 | HUMBOLDT | 4.1652 | 16.4846 | 91.99% | 0 | 2 | 24.91% | 0% | 0 | 0.015871 | 1 | 1.3046 | 0.020706 | Low | Low | Low | 2987 | 2581 | 0.015871 | 2.875
BANCROFT 0402CB | BANCROFT 0402 | EAST BAY | 1.0716 | 10 | 1.687% | 0 | 0 | 23.45% | 0% | 0 | 0.0060178 | 1 | 3.4396 | 0.020699 | Low | Low | High | 2988 | 3106 | 0.0060178 | 2.8543
OAKLAND J 1105CR130 | OAKLAND J 1105 | EAST BAY | 0.95094 | 10 | 5.238% | 0 | 0 | 19.42% | 0% | 0 | 0.0059522 | 1 | 3.464 | 0.020619 | Low | Low | High | 2989 | 3110 | 0.0059522 | 2.8336
MADISON 210137082 | MADISON 2101 | SACRAMENTO | 0.85819 | 87.1383 | 100% | 0 | 0 | 4.662% | 0% | 0 | 0.018775 | 1 | 1.0976 | 0.020608 | Low | Low | Low | 2990 | 2457 | 0.018775 | 2.813
CLEAR LAKE 1102CB | CLEAR LAKE 1102 | HUMBOLDT | 0.13095 | 10 | 54.49% | 0 | 0 | 0.5805% | 0% | 0 | 0.0073882 | 1 | 2.7821 | 0.020555 | Low | Low | Medium | 2991 | 3036 | 0.0073882 | 2.7924
GARBERVILLE 11028189 | GARBERVILLE 1102 | HUMBOLDT | 1.0385 | 78.4457 | 65.35% | 2 | 1 | 100% | 0% | 0 | 0.035613 | 1 | 0.5748 | 0.02047 | Medium | Medium | Low | 2992 | 1942 | 0.035613 | 2.7719
GUALALA 1111402866 | GUALALA 1111 | HUMBOLDT | 1.5915 | 10 | 0% | 1 | 1 | 100% | 0% | 0 | 0.013132 | 1 | 1.557 | 0.020445 | Low | Low | Low | 2993 | 2709 | 0.013132 | 2.7514
SUMMIT 1102CB | SUMMIT 1102 | SIERRA | 1.0104 | 10 | 73.24% | 1 | 3 | 100% | 0% | 0 | 0.032108 | 1 | 0.63651 | 0.020437 | Medium | Medium | Low | 2994 | 2042 | 0.032108 | 2.7309
SNEATH LANE 110168070 | SNEATH LANE 1101 | PENINSULA | 0.099639 | 10 | 0% | 0 | 2 | 4.651% | 0% | 0 | 0.0051309 | 1 | 3.9783 | 0.020412 | Low | Low | High | 2995 | 3138 | 0.0051309 | 2.7105
BUELLTON 11016621 | BUELLTON 1101 | LOS PADRES | 1.6446 | 36.7928 | 44.49% | 0 | 1 | 16.9% | 0% | 0 | 0.0098043 | 1 | 2.0776 | 0.020369 | Low | Low | Low | 2996 | 2940 | 0.0098043 | 2.6901
COPPERMINE 1104R755 | COPPERMINE 1104 | FRESNO | 8.1519 | 17.5841 | 96.77% | 0 | 3 | 13.19% | 0% | 0 | 0.013252 | 1 | 1.537 | 0.020367 | Low | Low | Low | 2997 | 2701 | 0.013252 | 2.6697
PLACER 110451732 | PLACER 1104 | SIERRA | 1.3434 | 10 | 21.69% | 0 | 0 | 16.14% | 0% | 0 | 0.0065925 | 1 | 3.0863 | 0.020346 | Low | Low | High | 2998 | 3074 | 0.0065925 | 2.6494
PLACER 1101CB | PLACER 1101 | SIERRA | 0.77573 | 10 | 3.906% | 0 | 0 | 10.24% | 0% | 0 | 0.0061355 | 1 | 3.3142 | 0.020334 | Low | Low | High | 2999 | 3099 | 0.0061355 | 2.629
GABILAN 11013034 | GABILAN 1101 | CENTRAL COAST | 0.41092 | 10 | 76.33% | 0 | 0 | 1.978% | 0% | 0 | 0.0089581 | 1 | 2.2622 | 0.020265 | Low | Low | Medium | 3000 | 2980 | 0.0089581 | 2.6087
OCEANO 1105V48 | OCEANO 1105 | LOS PADRES | 0.76105 | 10 | 0% | 0 | 1 | 30.2% | 0% | 0 | 0.0064819 | 1 | 3.124 | 0.020249 | Low | Low | High | 3001 | 3081 | 0.0064819 | 2.5884
BRUNSWICK 111094368 | BRUNSWICK 1110 | SIERRA | 0.16855 | 10 | 0% | 0 | 0 | 35.28% | 0% | 0 | 0.0066771 | 1 | 3.0325 | 0.020249 | Low | Low | Medium | 3002 | 3066 | 0.0066771 | 2.5682
PIT NO 7 1101CB | PIT NO 7 1101 | NORTH VALLEY | 2.7098 | 77.1247 | 100% | 0 | 2 | 100% | 0% | 0 | 0.046206 | 1 | 0.4374 | 0.02021 | Medium | Medium | Low | 3003 | 1737 | 0.046206 | 2.5479
MADISON 21011606 | MADISON 2101 | SACRAMENTO | 0.66018 | 28.3427 | 86.09% | 0 | 0 | 3.933% | 0% | 0 | 0.0112 | 1 | 1.8042 | 0.020206 | Low | Low | Low | 3004 | 2854 | 0.0112 | 2.5277
LOS COCHES 1101CB | LOS COCHES 1101 | CENTRAL COAST | 2.6219 | 75.2391 | 12.86% | 0 | 1 | 13.12% | 0% | 0 | 0.009461 | 1 | 2.1351 | 0.020201 | Low | Low | Low | 3005 | 2954 | 0.009461 | 2.5075
CALPELLA 1102CB | CALPELLA 1102 | HUMBOLDT | 1.6769 | 10 | 88.62% | 0 | 2 | 18.53% | 0% | 0 | 0.012165 | 1 | 1.6553 | 0.020137 | Low | Low | Low | 3006 | 2796 | 0.012165 | 2.4873
VIEJO 22022014 | VIEJO 2202 | CENTRAL COAST | 0.34884 | 10 | 0% | 0 | 0 | 8.641% | 0% | 0 | 0.0051208 | 1 | 3.9267 | 0.020108 | Low | Low | High | 3007 | 3139 | 0.0051208 | 2.4672
MARTELL 110198374 | MARTELL 1101 | STOCKTON | 0.48931 | 10 | 16.23% | 0 | 0 | 12.89% | 0% | 0 | 0.0061034 | 1 | 3.2848 | 0.020049 | Low | Low | High | 3008 | 3101 | 0.0061034 | 2.447
BOSTON 0401CR242 | BOSTON 0401 | EAST BAY | 0.44969 | 10 | 0% | 0 | 0 | 9.847% | 0% | 0 | 0.0051828 | 1 | 3.8356 | 0.019879 | Low | Low | High | 3009 | 3135 | 0.0051828 | 2.427
SAN RAFAEL 1105CB | SAN RAFAEL 1105 | NORTH BAY | 0.49095 | 10 | 6.778% | 3 | 1 | 5.07% | 0% | 0 | 0.0055495 | 1 | 3.5772 | 0.019852 | Low | Low | High | 3010 | 3122 | 0.0055495 | 2.4071
VIEJO 22032634 | VIEJO 2203 | CENTRAL COAST | 0.37273 | 10 | 10.45% | 0 | 0 | 22.39% | 0% | 0 | 0.0063984 | 1 | 3.0948 | 0.019802 | Low | Low | High | 3011 | 3083 | 0.0063984 | 2.3873
SAN LUIS OBISPO 1104CB | SAN LUIS OBISPO 1104 | LOS PADRES | 0.36018 | 63.441 | 2.835% | 0 | 0 | 5.218% | 0% | 0 | 0.007285 | 1 | 2.718 | 0.019801 | Low | Low | Medium | 3012 | 3043 | 0.007285 | 2.3675
SARATOGA 1103LC40 | SARATOGA 1103 | DE ANZA | 0.12637 | 10 | 0% | 0 | 0 | 6.576% | 0% | 0 | 0.0050164 | 1 | 3.9395 | 0.019762 | Low | Low | High | 3013 | 3144 | 0.0050164 | 2.3477
POTTER VALLEY P H 1105CB | POTTER VALLEY P H 1105 | HUMBOLDT | 0.024417 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.014786 | 1 | 1.3325 | 0.019702 | Low | Low | Low | 3014 | 2619 | 0.014786 | 2.3279
CASTRO VALLEY 1101MR518 | CASTRO VALLEY 1101 | MISSION | 0.037775 | 10 | 0% | 0 | 0 | 1.912% | 0% | 0 | 0.0047885 | 1 | 4.111 | 0.019686 | Low | Low | High | 3015 | 3165 | 0.0047885 | 2.3082
SNEATH LANE 1102CB | SNEATH LANE 1102 | PENINSULA | 0.28247 | 10 | 3.955% | 0 | 1 | 11.21% | 0% | 0 | 0.0055412 | 1 | 3.5434 | 0.019634 | Low | Low | High | 3016 | 3123 | 0.0055412 | 2.2885
HORSESHOE 1104CB | HORSESHOE 1104 | SIERRA | 0.063337 | 10 | 0% | 0 | 0 | 2.137% | 0% | 0 | 0.0047992 | 1 | 4.0681 | 0.019524 | Low | Low | High | 3017 | 3163 | 0.0047992 | 2.2689
VOLTA 110185234 | VOLTA 1101 | NORTH VALLEY | 7.9136 | 44.4652 | 95.46% | 10 | 12 | 100% | 0% | 0 | 0.11805 | 1 | 0.16495 | 0.019472 | High | High | Low | 3018 | 1229 | 0.11805 | 2.2494
CARMEL 0402CB | CARMEL 0402 | CENTRAL COAST | 0.30828 | 10 | 0% | 0 | 0 | 21.19% | 0% | 0 | 0.0058032 | 1 | 3.3503 | 0.019442 | Low | Low | High | 3019 | 3113 | 0.0058032 | 2.2299
HOLLISTER 2104855412 | HOLLISTER 2104 | CENTRAL COAST | 0.30314 | 60 | 0% | 1 | 0 | 11.12% | 0% | 0 | 0.007471 | 1 | 2.599 | 0.019417 | Low | Low | Medium | 3020 | 3031 | 0.007471 | 2.2104
PUEBLO 11053022 | PUEBLO 1105 | NORTH BAY | 0.42768 | 10 | 42.51% | 0 | 0 | 4.687% | 0% | 0 | 0.0069771 | 1 | 2.7525 | 0.019205 | Low | Low | Medium | 3021 | 3055 | 0.0069771 | 2.191
HALF MOON BAY 11019014 | HALF MOON BAY 1101 | PENINSULA | 0.031423 | 10 | 0% | 0 | 0 | 1.737% | 0% | 0 | 0.0047801 | 1 | 4.0077 | 0.019157 | Low | Low | High | 3022 | 3166 | 0.0047801 | 2.1718
POINT ARENA 11011296 | POINT ARENA 1101 | HUMBOLDT | 2.101 | 59.6296 | 9.522% | 3 | 3 | 37.92% | 0% | 0 | 0.013105 | 1 | 1.4612 | 0.019149 | Low | Low | Low | 3023 | 2711 | 0.013105 | 2.1527
PIT NO 5 11011658 | PIT NO 5 1101 | NORTH VALLEY | 4.5542 | 60.6461 | 59.05% | 1 | 2 | 100% | 0% | 0 | 0.039255 | 1 | 0.48755 | 0.019139 | Medium | Medium | Low | 3024 | 1877 | 0.039255 | 2.1335
WILLOW PASS 210821196 | WILLOW PASS 2108 | DIABLO | 0.047227 | 10 | 0% | 0 | 0 | 23.89% | 0% | 0 | 0.005961 | 1 | 3.2102 | 0.019136 | Low | Low | High | 3025 | 3109 | 0.005961 | 2.1144
HOOPA 1101 | HOOPA 1101 | HUMBOLDT | 0.098699 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.5065 | 0.019125 | Low | Low | Low | 3026 | 2735 | 0.012695 | 2.0952
COAST RD 04015134 | COAST RD 0401 | CENTRAL COAST | 1.6146 | 10 | 0% | 0 | 0 | 53.13% | 0% | 0 | 0.007975 | 1 | 2.3974 | 0.019119 | Low | Low | Medium | 3027 | 3012 | 0.007975 | 2.0761
SAN RAFAEL 11061230 | SAN RAFAEL 1106 | NORTH BAY | 0.27095 | 10 | 0% | 0 | 1 | 5.214% | 0% | 0 | 0.0050532 | 1 | 3.7783 | 0.019092 | Low | Low | High | 3028 | 3142 | 0.0050532 | 2.057
ANTLER 11011376 | ANTLER 1101 | NORTH VALLEY | 9.003 | 26.8195 | 100% | 0 | 3 | 100% | 0% | 0 | 0.049747 | 1 | 0.38247 | 0.019027 | Medium | Medium | Low | 3029 | 1685 | 0.049747 | 2.0379
FORT BRAGG A 1103588 | FORT BRAGG A 1103 | HUMBOLDT | 0.37656 | 10 | 0% | 0 | 0 | 20.3% | 0% | 0 | 0.0057518 | 1 | 3.299 | 0.018975 | Low | Low | High | 3030 | 3116 | 0.0057518 | 2.0189
LAKEWOOD 1102CB | LAKEWOOD 1102 | DIABLO | 0.47236 | 10 | 18.19% | 0 | 0 | 4.922% | 0% | 0 | 0.0057291 | 1 | 3.3099 | 0.018962 | Low | Low | High | 3031 | 3119 | 0.0057291 | 1.9999
SARATOGA 1107CB | SARATOGA 1107 | DE ANZA | 0.16938 | 10 | 0% | 0 | 1 | 1.739% | 0% | 0 | 0.0048811 | 1 | 3.8453 | 0.018769 | Low | Low | High | 3032 | 3155 | 0.0048811 | 1.9809
CAMBRIA 1101CB | CAMBRIA 1101 | LOS PADRES | 7.5504 | 30.2261 | 1.521% | 0 | 1 | 62.43% | 0% | 0 | 0.010371 | 1 | 1.7969 | 0.018636 | Low | Low | Low | 3033 | 2912 | 0.010371 | 1.9622
CARMEL 0405CB | CARMEL 0405 | CENTRAL COAST | 0.33684 | 10 | 0% | 0 | 1 | 10.77% | 0% | 0 | 0.0053408 | 1 | 3.4633 | 0.018497 | Low | Low | High | 3034 | 3130 | 0.0053408 | 1.9435
ROSSMOOR 110479146 | ROSSMOOR 1104 | DIABLO | 0.24893 | 10 | 0% | 0 | 0 | 11.42% | 0% | 0 | 0.0052646 | 1 | 3.5101 | 0.018479 | Low | Low | High | 3035 | 3133 | 0.0052646 | 1.925
WYANDOTTE 1103CB | WYANDOTTE 1103 | NORTH VALLEY | 0.060864 | 10 | 0% | 0 | 0 | 0.8345% | 0% | 0 | 0.0047373 | 1 | 3.8992 | 0.018471 | Low | Low | High | 3036 | 3172 | 0.0047373 | 1.9066
FORT BRAGG A 110436526 | FORT BRAGG A 1104 | HUMBOLDT | 0.39885 | 10 | 0% | 0 | 0 | 6.124% | 0% | 0 | 0.0049939 | 1 | 3.6762 | 0.018359 | Low | Low | High | 3037 | 3146 | 0.0049939 | 1.8881
DEL MONTE 210386496 | DEL MONTE 2103 | CENTRAL COAST | 0.39145 | 10 | 0% | 3 | 0 | 5.331% | 0% | 0 | 0.0051542 | 1 | 3.545 | 0.018272 | Low | Low | High | 3038 | 3136 | 0.0051542 | 1.8697
LAMONT 11024222 | LAMONT 1102 | KERN | 0.50063 | 85 | 100% | 0 | 0 | 3.081% | 0% | 0 | 0.018222 | 1 | 1.0005 | 0.01823 | Low | Low | Low | 3039 | 2482 | 0.018222 | 1.8515
SOLEDAD 111435306 | SOLEDAD 1114 | CENTRAL COAST | 0.90872 | 10 | 9.031% | 0 | 0 | 12.56% | 0% | 0 | 0.0065483 | 1 | 2.7745 | 0.018169 | Low | Low | Medium | 3040 | 3077 | 0.0065483 | 1.8332
CAYETANO 2109MR186 | CAYETANO 2109 | MISSION | 0.10978 | 10 | 0% | 0 | 0 | 4.27% | 0% | 0 | 0.0063941 | 1 | 2.8337 | 0.018119 | Low | Low | Medium | 3041 | 3084 | 0.0063941 | 1.8151
VALLEY VIEW 1105P124 | VALLEY VIEW 1105 | EAST BAY | 0.092976 | 10 | 0% | 0 | 0 | 2.939% | 0% | 0 | 0.0048377 | 1 | 3.7353 | 0.01807 | Low | Low | High | 3042 | 3160 | 0.0048377 | 1.7969
SUMMIT 110249484 | SUMMIT 1102 | SIERRA | 2.6877 | 10 | 54.68% | 1 | 0 | 100% | 0% | 0 | 0.026029 | 1 | 0.69298 | 0.018038 | Medium | Medium | Low | 3043 | 2213 | 0.026029 | 1.7789
EEL RIVER 11033820 | EEL RIVER 1103 | HUMBOLDT | 2.3658 | 10 | 0% | 0 | 1 | 11.93% | 0% | 0 | 0.0080448 | 1 | 2.2417 | 0.018034 | Low | Low | Medium | 3044 | 3010 | 0.0080448 | 1.7608
OAKLAND J 1105153228 | OAKLAND J 1105 | EAST BAY | 0.47385 | 10 | 4.597% | 0 | 0 | 11.41% | 0% | 0 | 0.0054665 | 1 | 3.2905 | 0.017988 | Low | Low | High | 3045 | 3125 | 0.0054665 | 1.7428
CLARKSVILLE 2103CB | CLARKSVILLE 2103 | SIERRA | 0.11367 | 10 | 0% | 0 | 0 | 7.91% | 0% | 0 | 0.0050836 | 1 | 3.5358 | 0.017975 | Low | Low | High | 3046 | 3140 | 0.0050836 | 1.7248
FLINT 110138570 | FLINT 1101 | SIERRA | 0.12622 | 10 | 17.37% | 0 | 0 | 3.673% | 0% | 0 | 0.0056203 | 1 | 3.1886 | 0.017921 | Low | Low | High | 3047 | 3121 | 0.0056203 | 1.7068
HALF MOON BAY 11036014 | HALF MOON BAY 1103 | PENINSULA | 5.273 | 14.6725 | 1.871% | 0 | 0 | 42.92% | 0% | 0 | 0.0086216 | 1 | 2.0756 | 0.017895 | Low | Low | Low | 3048 | 2994 | 0.0086216 | 1.6889
RISING RIVER 11019032 | RISING RIVER 1101 | NORTH VALLEY | 23.4901 | 16.8815 | 99.94% | 5 | 2 | 100% | 0% | 0 | 0.033124 | 1 | 0.53301 | 0.017655 | Medium | Medium | Low | 3049 | 2005 | 0.033124 | 1.671
GREENBRAE 1104751 | GREENBRAE 1104 | NORTH BAY | 0.079918 | 10 | 0% | 0 | 1 | 2.532% | 0% | 0 | 0.0049198 | 1 | 3.5848 | 0.017636 | Low | Low | High | 3050 | 3151 | 0.0049198 | 1.6534
PIT NO 3 21011480 | PIT NO 3 2101 | NORTH VALLEY | 2.2265 | 10 | 27.11% | 1 | 1 | 90.29% | 0% | 0 | 0.016964 | 1 | 1.0365 | 0.017582 | Low | Low | Low | 3051 | 2530 | 0.016964 | 1.6357
FROGTOWN 1702CB | FROGTOWN 1702 | STOCKTON | 2.2987 | 10 | 21.1% | 0 | 2 | 44.33% | 0% | 0 | 0.0090529 | 1 | 1.9418 | 0.017579 | Low | Low | Low | 3052 | 2974 | 0.0090529 | 1.6181
BIG RIVER 110155402 | BIG RIVER 1101 | HUMBOLDT | 2.6094 | 10 | 0.156% | 5 | 5 | 28.18% | 0% | 0 | 0.0073839 | 1 | 2.3739 | 0.017528 | Low | Low | Medium | 3053 | 3037 | 0.0073839 | 1.6006
LUCERNE 11034624 | LUCERNE 1103 | HUMBOLDT | 0.73972 | 10 | 26.07% | 0 | 0 | 19.5% | 0% | 0 | 0.0070666 | 1 | 2.4759 | 0.017496 | Low | Low | Medium | 3054 | 3053 | 0.0070666 | 1.583
GEYSERVILLE 1101CB | GEYSERVILLE 1101 | SONOMA | 0.2847 | 40.3314 | 82.04% | 0 | 1 | 3.457% | 0% | 0 | 0.011941 | 1 | 1.4595 | 0.017428 | Low | Low | Low | 3055 | 2812 | 0.011941 | 1.5655
FORT BRAGG A 1104CB | FORT BRAGG A 1104 | HUMBOLDT | 0.049503 | 10 | 0% | 1 | 0 | 1.775% | 0% | 0 | 0.0048453 | 1 | 3.575 | 0.017322 | Low | Low | High | 3056 | 3157 | 0.0048453 | 1.5481
OROVILLE 11042588 | OROVILLE 1104 | NORTH VALLEY | 0.2392 | 13.5731 | 31.06% | 1 | 0 | 2.673% | 0% | 0 | 0.0064634 | 1 | 2.6797 | 0.01732 | Low | Low | Medium | 3057 | 3082 | 0.0064634 | 1.5308
SALT SPRINGS 21011216 | SALT SPRINGS 2101 | STOCKTON | 5.4385 | 73.7435 | 99.91% | 0 | 1 | 98.38% | 0% | 0 | 0.056184 | 1 | 0.30767 | 0.017286 | Medium | Medium | Low | 3058 | 1612 | 0.056184 | 1.5135
HOLLISTER 21054724 | HOLLISTER 2105 | CENTRAL COAST | 3.4016 | 78.2881 | 100% | 0 | 0 | 12.91% | 0% | 0 | 0.019187 | 1 | 0.89991 | 0.017267 | Low | Low | Low | 3059 | 2435 | 0.019187 | 1.4962
FORT BRAGG A 1101CB | FORT BRAGG A 1101 | HUMBOLDT | 0.22122 | 10 | 0% | 0 | 1 | 2.86% | 0% | 0 | 0.0049359 | 1 | 3.4946 | 0.017249 | Low | Low | High | 3060 | 3148 | 0.0049359 | 1.4789
COVELO 1101562360 | COVELO 1101 | HUMBOLDT | 2.2904 | 16.1283 | 100% | 0 | 1 | 6.052% | 0% | 0 | 0.012043 | 1 | 1.4309 | 0.017233 | Low | Low | Low | 3061 | 2805 | 0.012043 | 1.4617
BEAR VALLEY 210190550 | BEAR VALLEY 2101 | YOSEMITE | 8.0073 | 10 | 99.83% | 0 | 6 | 100% | 0% | 0 | 0.032169 | 1 | 0.53108 | 0.017084 | Medium | Medium | Low | 3062 | 2040 | 0.032169 | 1.4444
POINT ARENA 1101476 | POINT ARENA 1101 | HUMBOLDT | 2.7213 | 21.4527 | 0% | 6 | 2 | 18.23% | 0% | 0 | 0.0068718 | 1 | 2.4696 | 0.01697 | Low | Low | Medium | 3063 | 3060 | 0.0068718 | 1.4273
IGNACIO 1104 | IGNACIO 1104 | NORTH BAY | 0.012266 | 10 | 0% | 0 | 0 | 20.53% | 0% | 0 | 0.005765 | 1 | 2.9425 | 0.016964 | Low | Low | Medium | 3064 | 3115 | 0.005765 | 1.4104
POTTER VALLEY P H 1105990354 | POTTER VALLEY P H 1105 | HUMBOLDT | 0.0040482 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.331 | 0.016897 | Low | Low | Low | 3065 | 2732 | 0.012695 | 1.3934
PIT NO 5 11011660 | PIT NO 5 1101 | NORTH VALLEY | 4.8851 | 10 | 71.19% | 4 | 4 | 100% | 0% | 0 | 0.033496 | 1 | 0.50439 | 0.016895 | Medium | Medium | Low | 3066 | 1995 | 0.033496 | 1.3765
POTTER VALLEY PH 11054634 | POTTER VALLEY PH 1105 | HUMBOLDT | 0.0052407 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.3294 | 0.016878 | Low | Low | Low | 3067 | 2732 | 0.012695 | 1.3596
POTTER VALLEY P H 1104CB | POTTER VALLEY P H 1104 | HUMBOLDT | 0.077279 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.3279 | 0.016858 | Low | Low | Low | 3068 | 2735 | 0.012695 | 1.3427
POTTER VALLEY P H 11054634 | POTTER VALLEY P H 1105 | HUMBOLDT | 0.13813 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.3268 | 0.016844 | Low | Low | Low | 3069 | 2735 | 0.012695 | 1.3259
SAN LEANDRO U 1109CR344 | SAN LEANDRO U 1109 | MISSION | 0.097411 | 10 | 0% | 0 | 0 | 3.929% | 0% | 0 | 0.0048858 | 1 | 3.393 | 0.016577 | Low | Low | High | 3070 | 3154 | 0.0048858 | 1.309
OAKLAND J 1116CR420 | OAKLAND J 1116 | EAST BAY | 0.031861 | 10 | 0% | 0 | 0 | 0.2787% | 0% | 0 | 0.0047111 | 1 | 3.508 | 0.016527 | Low | Low | High | 3071 | 3177 | 0.0047111 | 1.2925
PANOCHE 11034036 | PANOCHE 1103 | YOSEMITE | 8.0979 | 77.6294 | 100% | 0 | 1 | 32.26% | 0% | 0 | 0.023574 | 1 | 0.7002 | 0.016507 | Medium | Medium | Low | 3072 | 2293 | 0.023574 | 1.2759
TEMPLETON 2108A64 | TEMPLETON 2108 | LOS PADRES | 1.3676 | 10 | 21.6% | 0 | 0 | 11.56% | 0% | 0 | 0.0062941 | 1 | 2.6112 | 0.016435 | Low | Low | Medium | 3073 | 3088 | 0.0062941 | 1.2594
DEL MAR 210938684 | DEL MAR 2109 | SIERRA | 0.062211 | 10 | 0% | 0 | 0 | 6.669% | 0% | 0 | 0.0050211 | 1 | 3.2725 | 0.016432 | Low | Low | High | 3074 | 3143 | 0.0050211 | 1.243
JOLON 1103CB | JOLON 1103 | CENTRAL COAST | 14.8367 | 53.4685 | 41.31% | 0 | 2 | 82.37% | 0% | 0 | 0.020833 | 1 | 0.78084 | 0.016268 | Low | Low | Low | 3075 | 2375 | 0.020833 | 1.2266
SHINGLE SPRINGS 210851474 | SHINGLE SPRINGS 2108 | SIERRA | 0.24496 | 10 | 0% | 0 | 0 | 5.255% | 0% | 0 | 0.0049508 | 1 | 3.2752 | 0.016215 | Low | Low | High | 3076 | 3147 | 0.0049508 | 1.2103
SUMMIT 1101742 | SUMMIT 1101 | SIERRA | 0.86692 | 10 | 60.19% | 0 | 1 | 66.72% | 0% | 0 | 0.017361 | 1 | 0.93316 | 0.016201 | Low | Low | Low | 3077 | 2515 | 0.017361 | 1.1941
GEYSERVILLE 1102756 | GEYSERVILLE 1102 | SONOMA | 0.58953 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.012961 | 1 | 1.2459 | 0.016148 | Low | Low | Low | 3078 | 2716 | 0.012961 | 1.1779
SNEATH LANE 110275844 | SNEATH LANE 1102 | PENINSULA | 0.025403 | 10 | 0% | 0 | 0 | 4.723% | 0% | 0 | 0.0049246 | 1 | 3.2777 | 0.016141 | Low | Low | High | 3079 | 3150 | 0.0049246 | 1.1617
MC ARTHUR 11021324 | MC ARTHUR 1102 | NORTH VALLEY | 0.91154 | 54.3228 | 100% | 0 | 0 | 3.568% | 0% | 0 | 0.014895 | 1 | 1.0821 | 0.016117 | Low | Low | Low | 3080 | 2612 | 0.014895 | 1.1456
FORT ROSS 1121560 | FORT ROSS 1121 | SONOMA | 5.3342 | 23.1043 | 0.06425% | 1 | 0 | 90.51% | 0% | 0 | 0.0128 | 1 | 1.2567 | 0.016087 | Low | Low | Low | 3081 | 2725 | 0.0128 | 1.1295
SALT SPRINGS 210110416 | SALT SPRINGS 2101 | STOCKTON | 0.57657 | 81.6052 | 94.63% | 2 | 1 | 100% | 0% | 0 | 0.045848 | 1 | 0.35085 | 0.016086 | Medium | Medium | Low | 3082 | 1749 | 0.045848 | 1.1134
GARBERVILLE 1102 | GARBERVILLE 1102 | HUMBOLDT | 0.096479 | 11.5575 | 97.17% | 0 | 0 | 86.15% | 0% | 0 | 0.024601 | 1 | 0.65244 | 0.016051 | Medium | Medium | Low | 3083 | 2256 | 0.024601 | 1.0973
MILPITAS 1109XR044 | MILPITAS 1109 | SAN JOSE | 0.07893 | 10 | 0% | 0 | 0 | 4.212% | 0% | 0 | 0.0048996 | 1 | 3.2735 | 0.016039 | Low | Low | High | 3084 | 3153 | 0.0048996 | 1.0813
MONTEREY 04012642 | MONTEREY 0401 | CENTRAL COAST | 0.26645 | 10 | 0% | 0 | 0 | 10.11% | 0% | 0 | 0.0051963 | 1 | 3.0669 | 0.015936 | Low | Low | Medium | 3085 | 3134 | 0.0051963 | 1.0652
ALHAMBRA 1102CB | ALHAMBRA 1102 | DIABLO | 0.16935 | 10 | 0% | 0 | 0 | 2.96% | 0% | 0 | 0.0048388 | 1 | 3.2866 | 0.015903 | Low | Low | High | 3086 | 3159 | 0.0048388 | 1.0493
VIEJO 22039094 | VIEJO 2203 | CENTRAL COAST | 0.038317 | 10 | 0% | 0 | 0 | 1.572% | 0% | 0 | 0.0047723 | 1 | 3.3195 | 0.015842 | Low | Low | High | 3087 | 3167 | 0.0047723 | 1.0334
RIO DELL 11024230 | RIO DELL 1102 | HUMBOLDT | 22.9435 | 79.495 | 27.47% | 20 | 5 | 99.94% | 0% | 0 | 0.05306 | 1 | 0.29839 | 0.015832 | Medium | Medium | Low | 3088 | 1647 | 0.05306 | 1.0175
COVELO 1101536 | COVELO 1101 | HUMBOLDT | 0.011418 | 10 | 100% | 1 | 0 | 0.05103% | 0% | 0 | 0.012329 | 1 | 1.2835 | 0.015825 | Low | Low | Low | 3089 | 2782 | 0.012329 | 1.0017
FRANKLIN 1101P132 | FRANKLIN 1101 | EAST BAY | 0.033203 | 10 | 0% | 0 | 0 | 2.185% | 0% | 0 | 0.0048015 | 1 | 3.2929 | 0.015811 | Low | Low | High | 3090 | 3162 | 0.0048015 | 0.98587
RINCON 1102640 | RINCON 1102 | SONOMA | 0.04813 | 10 | 0% | 0 | 0 | 1.143% | 0% | 0 | 0.0047519 | 1 | 3.3054 | 0.015707 | Low | Low | High | 3091 | 3170 | 0.0047519 | 0.97006
SALT SPRINGS 21023118 | SALT SPRINGS 2102 | STOCKTON | 0.07196 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.54869 | 0.015644 | Medium | Medium | Low | 3092 | 2154 | 0.028512 | 0.95436
VACAVILLE 110847860 | VACAVILLE 1108 | SACRAMENTO | 0.28908 | 10 | 0% | 0 | 0 | 7.334% | 0% | 0 | 0.0050545 | 1 | 3.0859 | 0.015598 | Low | Low | High | 3093 | 3141 | 0.0050545 | 0.93871
CAROLANDS 040484797 | CAROLANDS 0404 | PENINSULA | 0.013784 | 10 | 0% | 0 | 0 | 1.034% | 0% | 0 | 0.0047467 | 1 | 3.2801 | 0.01557 | Low | Low | High | 3094 | 3171 | 0.0047467 | 0.92311
GARBERVILLE 11022540 | GARBERVILLE 1102 | HUMBOLDT | 15.3454 | 59.7556 | 6.792% | 13 | 5 | 85.73% | 0% | 0 | 0.046446 | 1 | 0.33411 | 0.015518 | Medium | Medium | Low | 3095 | 1732 | 0.046446 | 0.90754
ARCATA 112233060 | ARCATA 1122 | HUMBOLDT | 0.34235 | 10 | 0% | 0 | 1 | 7.017% | 0% | 0 | 0.0051448 | 1 | 3.0094 | 0.015483 | Low | Low | Medium | 3096 | 3137 | 0.0051448 | 0.89203
HOPLAND 1101CB | HOPLAND 1101 | HUMBOLDT | 0.39955 | 10 | 100% | 0 | 1 | 6.5% | 0% | 0 | 0.011606 | 1 | 1.3337 | 0.015479 | Low | Low | Low | 3097 | 2830 | 0.011606 | 0.87654
BIG MEADOWS 21012510 | BIG MEADOWS 2101 | NORTH VALLEY | 5.0492 | 32.6868 | 6.505% | 7 | 2 | 57.3% | 0% | 0 | 0.015201 | 1 | 1.0173 | 0.015464 | Low | Low | Low | 3098 | 2603 | 0.015201 | 0.86106
RED BLUFF 1105161818 | RED BLUFF 1105 | NORTH VALLEY | 0.38337 | 10 | 100% | 0 | 0 | 8.045% | 0% | 0 | 0.011543 | 1 | 1.3232 | 0.015274 | Low | Low | Low | 3099 | 2833 | 0.011543 | 0.8456
BRUNSWICK 111095576 | BRUNSWICK 1110 | SIERRA | 0.15603 | 10 | 0% | 0 | 0 | 4.385% | 0% | 0 | 0.004908 | 1 | 3.0967 | 0.015199 | Low | Low | High | 3100 | 3152 | 0.004908 | 0.83033
REEDLEY 11127240 | REEDLEY 1112 | FRESNO | 0.0028032 | 10 | 0% | 0 | 0 | 0.01029% | 0% | 0 | 0.0046985 | 1 | 3.2223 | 0.01514 | Low | Low | High | 3101 | 3181 | 0.0046985 | 0.81513
MAXWELL 11053008 | MAXWELL 1105 | SACRAMENTO | 1.6684 | 73.9154 | 100% | 0 | 0 | 12.26% | 0% | 0 | 0.018513 | 1 | 0.80874 | 0.014972 | Low | Low | Low | 3102 | 2464 | 0.018513 | 0.79999
POSO MOUNTAIN 21011703 | POSO MOUNTAIN 2101 | KERN | 0.0074631 | 10 | 0% | 0 | 0 | 0.304% | 0% | 0 | 0.0053821 | 1 | 2.7786 | 0.014955 | Low | Low | Medium | 3103 | 3129 | 0.0053821 | 0.78501
RISING RIVER 11011532 | RISING RIVER 1101 | NORTH VALLEY | 3.0653 | 21.21 | 32.28% | 0 | 0 | 62.2% | 0% | 0 | 0.012255 | 1 | 1.2187 | 0.014936 | Low | Low | Low | 3104 | 2789 | 0.012255 | 0.77006
CORRAL 110175204 | CORRAL 1101 | STOCKTON | 1.1128 | 10 | 10.09% | 0 | 0 | 5.993% | 0% | 0 | 0.0054182 | 1 | 2.7419 | 0.014856 | Low | Low | Medium | 3105 | 3127 | 0.0054182 | 0.75512
ALTO 1121CB | ALTO 1121 | NORTH BAY | 0.013093 | 10 | 0% | 0 | 0 | 0.2456% | 0% | 0 | 0.0047095 | 1 | 3.1177 | 0.014683 | Low | Low | High | 3106 | 3178 | 0.0047095 | 0.74027
ALTO 112088190 | ALTO 1120 | NORTH BAY | 0.01959 | 10 | 0% | 0 | 0 | 0.6244% | 0% | 0 | 0.0047274 | 1 | 3.0907 | 0.014611 | Low | Low | High | 3107 | 3174 | 0.0047274 | 0.72558
WESTLEY 11039010 | WESTLEY 1103 | YOSEMITE | 0.92376 | 10 | 100% | 0 | 0 | 2.686% | 0% | 0 | 0.010946 | 1 | 1.3317 | 0.014577 | Low | Low | Low | 3108 | 2872 | 0.010946 | 0.71097
BEAR VALLEY 210110019 | BEAR VALLEY 2101 | YOSEMITE | 1.9804 | 23.7531 | 100% | 0 | 6 | 100% | 0% | 0 | 0.04012 | 1 | 0.35957 | 0.014426 | Medium | Medium | Low | 3109 | 1853 | 0.04012 | 0.6964
FORT BRAGG A 11021226 | FORT BRAGG A 1102 | HUMBOLDT | 1.1335 | 10 | 21.46% | 0 | 3 | 14.45% | 0% | 0 | 0.0068882 | 1 | 2.0906 | 0.0144 | Low | Low | Low | 3110 | 3059 | 0.0068882 | 0.68197
GEYSERVILLE 1101480 | GEYSERVILLE 1101 | SONOMA | 1.4699 | 10 | 99.61% | 0 | 0 | 9.197% | 0% | 0 | 0.011639 | 1 | 1.237 | 0.014397 | Low | Low | Low | 3111 | 2827 | 0.011639 | 0.66757
RISING RIVER 11011530 | RISING RIVER 1101 | NORTH VALLEY | 10.3786 | 10.5372 | 70.85% | 4 | 0 | 58.6% | 0% | 0 | 0.01587 | 1 | 0.8986 | 0.014261 | Low | Low | Low | 3112 | 2582 | 0.01587 | 0.65317
BRUNSWICK 110765574 | BRUNSWICK 1107 | SIERRA | 0.053599 | 10 | 0% | 0 | 0 | 3.058% | 0% | 0 | 0.0048435 | 1 | 2.9407 | 0.014243 | Low | Low | Medium | 3113 | 3158 | 0.0048435 | 0.63891
OCEANO 1105V42 | OCEANO 1105 | LOS PADRES | 0.34173 | 10 | 0% | 0 | 0 | 14.57% | 0% | 0 | 0.0054323 | 1 | 2.6024 | 0.014137 | Low | Low | Medium | 3114 | 3126 | 0.0054323 | 0.62467
BRUNSWICK 1110CB | BRUNSWICK 1110 | SIERRA | 0.0037878 | 10 | 0% | 0 | 0 | 0.2212% | 0% | 0 | 0.0047084 | 1 | 2.9563 | 0.01392 | Low | Low | Medium | 3115 | 3179 | 0.0047084 | 0.61053
CLARK ROAD 11022094 | CLARK ROAD 1102 | NORTH VALLEY | 0.57902 | 10 | 17.05% | 0 | 0 | 16.85% | 0% | 0 | 0.0063918 | 1 | 2.1553 | 0.013776 | Low | Low | Low | 3116 | 3085 | 0.0063918 | 0.59661
PALMER 1101M88 | PALMER 1101 | LOS PADRES | 2.2617 | 68.2305 | 27.53% | 0 | 1 | 14.75% | 0% | 0 | 0.011798 | 1 | 1.1586 | 0.013669 | Low | Low | Low | 3117 | 2816 | 0.011798 | 0.58284
RESERVATION ROAD 110222136 | RESERVATION ROAD 1102 | CENTRAL COAST | 1.1023 | 40.7641 | 13.41% | 0 | 0 | 19.9% | 0% | 0 | 0.0078815 | 1 | 1.7282 | 0.013621 | Low | Low | Low | 3118 | 3016 | 0.0078815 | 0.56917
ELK 1101900 | ELK 1101 | HUMBOLDT | 6.0335 | 22.7757 | 2.097% | 2 | 3 | 29.53% | 0% | 0 | 0.0087294 | 1 | 1.5553 | 0.013577 | Low | Low | Low | 3119 | 2988 | 0.0087294 | 0.55555
VOLTA 11011596 | VOLTA 1101 | NORTH VALLEY | 21.7972 | 45.4978 | 99.98% | 1 | 12 | 100% | 0% | 0 | 0.052789 | 1 | 0.25608 | 0.013518 | Medium | Medium | Low | 3120 | 1651 | 0.052789 | 0.54197
SUMMIT 11022302 | SUMMIT 1102 | SIERRA | 1.4575 | 10 | 25.54% | 1 | 4 | 100% | 0% | 0 | 0.022343 | 1 | 0.59618 | 0.01332 | Medium | Medium | Low | 3121 | 2322 | 0.022343 | 0.52845
PEORIA 17048040 | PEORIA 1704 | YOSEMITE | 8.9787 | 41.627 | 97.88% | 2 | 3 | 34.87% | 0% | 0 | 0.02277 | 1 | 0.58079 | 0.013225 | Medium | Medium | Low | 3122 | 2314 | 0.02277 | 0.51513
GIRVAN 1101CB | GIRVAN 1101 | NORTH VALLEY | 0.35544 | 10 | 1.64% | 0 | 0 | 10.78% | 0% | 0 | 0.0053021 | 1 | 2.487 | 0.013186 | Low | Low | Medium | 3123 | 3132 | 0.0053021 | 0.50191
CORNING 110193362 | CORNING 1101 | NORTH VALLEY | 0.36788 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.0353 | 0.013144 | Low | Low | Low | 3124 | 2735 | 0.012695 | 0.48872
MERCED FALLS 1102CB | MERCED FALLS 1102 | YOSEMITE | 8.7968 | 48.2872 | 48.16% | 0 | 1 | 34.84% | 0% | 0 | 0.014879 | 1 | 0.87183 | 0.012972 | Low | Low | Low | 3125 | 2613 | 0.014879 | 0.47558
RIO DELL 11021504 | RIO DELL 1102 | HUMBOLDT | 8.4162 | 77.8437 | 6.428% | 4 | 1 | 69.81% | 0% | 0 | 0.016871 | 1 | 0.76309 | 0.012874 | Low | Low | Low | 3126 | 2532 | 0.016871 | 0.4626
CAYUCOS 1101W14 | CAYUCOS 1101 | LOS PADRES | 0.012808 | 10 | 0% | 0 | 0 | 0.1056% | 0% | 0 | 0.004703 | 1 | 2.7337 | 0.012857 | Low | Low | Medium | 3127 | 3180 | 0.004703 | 0.44973
HOPLAND 1101558 | HOPLAND 1101 | HUMBOLDT | 0.37929 | 10 | 97.04% | 0 | 0 | 4.114% | 0% | 0 | 0.010837 | 1 | 1.1824 | 0.012815 | Low | Low | Low | 3128 | 2881 | 0.010837 | 0.43687
BROWNS VALLEY 110136622 | BROWNS VALLEY 1101 | SIERRA | 2.3766 | 10 | 8.927% | 0 | 1 | 25.35% | 0% | 0 | 0.0066455 | 1 | 1.9026 | 0.012644 | Low | Low | Low | 3129 | 3069 | 0.0066455 | 0.42406
PIT NO 1 11019702 | PIT NO 1 1101 | NORTH VALLEY | 0.44484 | 10 | 24.55% | 0 | 0 | 4.849% | 0% | 0 | 0.0060315 | 1 | 2.0734 | 0.012506 | Low | Low | Low | 3130 | 3105 | 0.0060315 | 0.41142
MC ARTHUR 11011492 | MC ARTHUR 1101 | NORTH VALLEY | 9.6647 | 34.9258 | 100% | 1 | 0 | 31.38% | 0% | 0 | 0.019862 | 1 | 0.62862 | 0.012486 | Low | Low | Low | 3131 | 2416 | 0.019862 | 0.39891
MC ARTHUR 110138998 | MC ARTHUR 1101 | NORTH VALLEY | 11.0305 | 56.1464 | 63.76% | 0 | 2 | 67.61% | 0% | 0 | 0.021999 | 1 | 0.56625 | 0.012457 | Medium | Medium | Low | 3132 | 2337 | 0.021999 | 0.38642
PIT NO 5 11011606 | PIT NO 5 1101 | NORTH VALLEY | 5.5302 | 10 | 89.8% | 1 | 2 | 100% | 0% | 0 | 0.031556 | 1 | 0.39242 | 0.012383 | Medium | Medium | Low | 3133 | 2059 | 0.031556 | 0.37397
SUMMIT 110147786 | SUMMIT 1101 | SIERRA | 1.7732 | 10 | 6.416% | 0 | 1 | 100% | 0% | 0 | 0.017764 | 1 | 0.69667 | 0.012376 | Low | Low | Low | 3134 | 2500 | 0.017764 | 0.36158
SALT SPRINGS 21013116 | SALT SPRINGS 2101 | STOCKTON | 0.70592 | 10 | 100% | 0 | 1 | 70.33% | 0% | 0 | 0.021776 | 1 | 0.56292 | 0.012258 | Low | Low | Low | 3135 | 2344 | 0.021776 | 0.34921
SUMMIT 110148636 | SUMMIT 1101 | SIERRA | 0.057422 | 10 | 100% | 0 | 0 | 2.116% | 0% | 0 | 0.010884 | 1 | 1.1135 | 0.01212 | Low | Low | Low | 3136 | 2876 | 0.010884 | 0.33695
LAURELES 1112CB | LAURELES 1112 | CENTRAL COAST | 0.015644 | 10 | 0% | 0 | 0 | 0.6574% | 0% | 0 | 0.0047289 | 1 | 2.5304 | 0.011966 | Low | Low | Medium | 3137 | 3173 | 0.0047289 | 0.32483
MARTELL 1103CB | MARTELL 1103 | STOCKTON | 0.8745 | 10 | 17.84% | 0 | 0 | 13.95% | 0% | 0 | 0.0062499 | 1 | 1.9128 | 0.011955 | Low | Low | Low | 3138 | 3091 | 0.0062499 | 0.31286
MC ARTHUR 11011490 | MC ARTHUR 1101 | NORTH VALLEY | 9.1248 | 10 | 79.7% | 0 | 4 | 60.48% | 0% | 0 | 0.02318 | 1 | 0.49873 | 0.01156 | Medium | Medium | Low | 3139 | 2304 | 0.02318 | 0.30091
GLENN 11012012 | GLENN 1101 | NORTH VALLEY | 2.3498 | 85 | 100% | 0 | 0 | 7.814% | 0% | 0 | 0.01909 | 1 | 0.59338 | 0.011328 | Low | Low | Low | 3140 | 2442 | 0.01909 | 0.28935
OLEMA 110149756 | OLEMA 1101 | NORTH BAY | 0.14983 | 10 | 0% | 0 | 2 | 2.553% | 0% | 0 | 0.0057386 | 1 | 1.9687 | 0.011298 | Low | Low | Low | 3141 | 3118 | 0.0057386 | 0.27802
ANTELOPE 11011631 | ANTELOPE 1101 | KERN | 0.75322 | 47.1276 | 100% | 0 | 0 | 6.682% | 0% | 0 | 0.014633 | 1 | 0.73269 | 0.010722 | Low | Low | Low | 3142 | 2629 | 0.014633 | 0.26672
MC ARTHUR 110137344 | MC ARTHUR 1101 | NORTH VALLEY | 0.26567 | 10 | 48.66% | 0 | 0 | 2.972% | 0% | 0 | 0.0072135 | 1 | 1.4849 | 0.010712 | Low | Low | Low | 3143 | 3047 | 0.0072135 | 0.256
STONE CORRAL 11087100 | STONE CORRAL 1108 | FRESNO | 2.9159 | 10 | 14.41% | 0 | 0 | 15.91% | 0% | 0 | 0.0061962 | 1 | 1.7025 | 0.010549 | Low | Low | Low | 3144 | 3095 | 0.0061962 | 0.24529
FREMONT 1104MR707 | FREMONT 1104 | MISSION | 1.4479 | 10 | 0% | 0 | 0 | 16.1% | 0% | 0 | 0.0055159 | 1 | 1.8893 | 0.010421 | Low | Low | Low | 3145 | 3124 | 0.0055159 | 0.23474
CUYAMA 1103622728 | CUYAMA 1103 | KERN | 2.3769 | 95 | 100% | 0 | 0 | 6.184% | 0% | 0 | 0.02009 | 1 | 0.49944 | 0.010034 | Low | Low | Low | 3146 | 2406 | 0.02009 | 0.22432
MERCED FALLS 11029460 | MERCED FALLS 1102 | YOSEMITE | 8.5158 | 30.9683 | 53.31% | 0 | 0 | 95.4% | 0% | 0 | 0.031807 | 1 | 0.30868 | 0.009818 | Medium | Medium | Low | 3147 | 2050 | 0.031807 | 0.21429
ELK 1101CB | ELK 1101 | HUMBOLDT | 0.88673 | 10 | 0% | 1 | 0 | 90.98% | 0% | 0 | 0.011764 | 1 | 0.82427 | 0.0096969 | Low | Low | Low | 3148 | 2818 | 0.011764 | 0.20447
PANOCHE 11034016 | PANOCHE 1103 | YOSEMITE | 2.3488 | 61.1971 | 100% | 0 | 0 | 18.31% | 0% | 0 | 0.020566 | 1 | 0.46613 | 0.0095864 | Low | Low | Low | 3149 | 2384 | 0.020566 | 0.19477
RIO DELL 11028768 | RIO DELL 1102 | HUMBOLDT | 0.28084 | 10 | 0% | 0 | 0 | 4.757% | 0% | 0 | 0.0049263 | 1 | 1.9394 | 0.0095539 | Low | Low | Low | 3150 | 3149 | 0.0049263 | 0.18518
MERCED FALLS 11029470 | MERCED FALLS 1102 | YOSEMITE | 22.9864 | 12.6287 | 82.62% | 0 | 4 | 100% | 0% | 0 | 0.040338 | 1 | 0.22626 | 0.0091268 | Medium | Medium | Low | 3151 | 1845 | 0.040338 | 0.17563
JOLON 110268034 | JOLON 1102 | CENTRAL COAST | 0.019914 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.71712 | 0.0091041 | Low | Low | Low | 3152 | 2735 | 0.012695 | 0.1665
BEAR VALLEY 2105CB | BEAR VALLEY 2105 | YOSEMITE | 3.852 | 80.717 | 62.63% | 2 | 1 | 100% | 0% | 0 | 0.040229 | 1 | 0.22311 | 0.0089755 | Medium | Medium | Low | 3153 | 1851 | 0.040229 | 0.1574
PIT NO 5 110190846 | PIT NO 5 1101 | NORTH VALLEY | 0.092785 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.31428 | 0.0089606 | Medium | Medium | Low | 3154 | 2136 | 0.028512 | 0.14842
PEORIA 170492888 | PEORIA 1704 | YOSEMITE | 0.24891 | 10 | 100% | 0 | 0 | 52.34% | 0% | 0 | 0.017878 | 1 | 0.4954 | 0.0088569 | Low | Low | Low | 3155 | 2495 | 0.017878 | 0.13946
PEORIA 1701 | PEORIA 1701 | YOSEMITE | 0.00281 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.6973 | 0.0088524 | Low | Low | Low | 3156 | 2735 | 0.012695 | 0.13061
CLARK ROAD 1102CB | CLARK ROAD 1102 | NORTH VALLEY | 0.16153 | 10 | 1.759% | 0 | 1 | 10.59% | 0% | 0 | 0.006177 | 1 | 1.3847 | 0.0085535 | Low | Low | Low | 3157 | 3096 | 0.006177 | 0.12175
PIT NO 3 21011360 | PIT NO 3 2101 | NORTH VALLEY | 21.8208 | 46.6037 | 72.84% | 2 | 7 | 96.78% | 0% | 0 | 0.033534 | 1 | 0.24766 | 0.0083049 | Medium | Medium | Low | 3158 | 1994 | 0.033534 | 0.1132
PIT NO 5 11011614 | PIT NO 5 1101 | NORTH VALLEY | 1.8659 | 92.5056 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049074 | 1 | 0.16422 | 0.0080592 | Medium | Medium | Low | 3159 | 1694 | 0.049074 | 0.1049
SAN ARDO 11017094 | SAN ARDO 1101 | CENTRAL COAST | 1.1437 | 50.6148 | 100% | 0 | 0 | 6.71% | 0% | 0 | 0.014985 | 1 | 0.52695 | 0.0078965 | Low | Low | Low | 3160 | 2608 | 0.014985 | 0.096837
ELK 11011300 | ELK 1101 | HUMBOLDT | 3.0348 | 10 | 21.85% | 10 | 1 | 31.85% | 0% | 0 | 0.0089861 | 1 | 0.83981 | 0.0075467 | Low | Low | Low | 3161 | 2977 | 0.0089861 | 0.08894
PIT NO 3 21011386 | PIT NO 3 2101 | NORTH VALLEY | 5.8084 | 10 | 93.45% | 4 | 0 | 84.51% | 0% | 0 | 0.027889 | 1 | 0.24957 | 0.0069602 | Medium | Medium | Low | 3162 | 2164 | 0.027889 | 0.081394
VOLTA 11011640 | VOLTA 1101 | NORTH VALLEY | 10.4338 | 80.2423 | 83.4% | 1 | 4 | 100% | 0% | 0 | 0.072189 | 1 | 0.092106 | 0.006649 | High | High | Low | 3163 | 1459 | 0.072189 | 0.074434
MERCED FALLS 110238748 | MERCED FALLS 1102 | YOSEMITE | 15.288 | 16.9529 | 100% | 0 | 0 | 100% | 0% | 0 | 0.033981 | 1 | 0.19224 | 0.0065325 | Medium | Medium | Low | 3164 | 1978 | 0.033981 | 0.067785
MC ARTHUR 11011488 | MC ARTHUR 1101 | NORTH VALLEY | 2.4985 | 10 | 70.57% | 0 | 2 | 7.462% | 0% | 0 | 0.0094078 | 1 | 0.63499 | 0.0059739 | Low | Low | Low | 3165 | 2959 | 0.0094078 | 0.061252
MERCED FALLS 110222774 | MERCED FALLS 1102 | YOSEMITE | 1.0091 | 37.0223 | 100% | 0 | 0 | 27.2% | 0% | 0 | 0.016738 | 1 | 0.33771 | 0.0056526 | Low | Low | Low | 3166 | 2538 | 0.016738 | 0.055278
SAN ARDO 11017632 | SAN ARDO 1101 | CENTRAL COAST | 0.79963 | 10 | 100% | 0 | 0 | 9.729% | 0% | 0 | 0.011737 | 1 | 0.481 | 0.0056455 | Low | Low | Low | 3167 | 2819 | 0.011737 | 0.049625
CORNING 110187304 | CORNING 1101 | NORTH VALLEY | 1.5372 | 10 | 14.41% | 0 | 3 | 10.47% | 0% | 0 | 0.0062491 | 1 | 0.88021 | 0.0055005 | Low | Low | Low | 3168 | 3092 | 0.0062491 | 0.04398
SAN ARDO 110193072 | SAN ARDO 1101 | CENTRAL COAST | 0.72134 | 10 | 63.38% | 0 | 0 | 8.566% | 0% | 0 | 0.0098197 | 1 | 0.54117 | 0.0053141 | Low | Low | Low | 3169 | 2938 | 0.0098197 | 0.038479
LOGAN CREEK 21022226 | LOGAN CREEK 2102 | NORTH VALLEY | 3.7103 | 86.8404 | 100% | 0 | 1 | 10.78% | 0% | 0 | 0.020313 | 1 | 0.2575 | 0.0052305 | Low | Low | Low | 3170 | 2392 | 0.020313 | 0.033165
PIT NO 5 1101CB | PIT NO 5 1101 | NORTH VALLEY | 0.72275 | 65.782 | 100% | 4 | 2 | 100% | 0% | 0 | 0.045131 | 1 | 0.11458 | 0.0051713 | Medium | Medium | Low | 3171 | 1764 | 0.045131 | 0.027935
PIT NO 3 21011482 | PIT NO 3 2101 | NORTH VALLEY | 12.042 | 25.2752 | 56.98% | 0 | 2 | 100% | 0% | 0 | 0.026507 | 1 | 0.19495 | 0.0051676 | Medium | Medium | Low | 3172 | 2203 | 0.026507 | 0.022764
SUMMIT 110168706 | SUMMIT 1101 | SIERRA | 0.058904 | 10 | 0% | 0 | 0 | 1.149% | 0% | 0 | 0.0047522 | 1 | 1.0375 | 0.0049304 | Low | Low | Low | 3173 | 3169 | 0.0047522 | 0.017596
DUNLAP 11027360 | DUNLAP 1102 | FRESNO | 8.5319 | 14.1381 | 99.93% | 0 | 0 | 100% | 0% | 0 | 0.048964 | 1 | 0.093748 | 0.0045903 | Medium | Medium | Low | 3174 | 1696 | 0.048964 | 0.012666
MC ARTHUR 11011544 | MC ARTHUR 1101 | NORTH VALLEY | 14.33 | 61.0373 | 66.86% | 0 | 1 | 51.35% | 0% | 0 | 0.022186 | 1 | 0.18317 | 0.0040638 | Medium | Medium | Low | 3175 | 2327 | 0.022186 | 0.0080753
RIO DELL 110270960 | RIO DELL 1102 | HUMBOLDT | 3.7354 | 51.8564 | 33.96% | 2 | 2 | 31.94% | 0% | 0 | 0.012119 | 1 | 0.29794 | 0.0036108 | Low | Low | Low | 3176 | 2800 | 0.012119 | 0.0040114
SPAULDING 1101578852 | SPAULDING 1101 | SIERRA | 20.1063 | 56.8104 | 73.09% | 2 | 12 | 82.23% | 8.84% | 1 | 0.13582 | 1 | 0.021523 | 0.0029234 | High | High | Low | 3177 | 1181 | 0.13582 | 0.00040061
GARBERVILLE 110197300 | GARBERVILLE 1101 | HUMBOLDT | 14.1538 | 63.6884 | 85.32% | 13 | 2 | 100% | 0% | 0 | 0.1059 | 1 | 0.026166 | 0.0027709 | High | High | Low | 3178 | 1270 | 0.1059 | -0.0025228
PIT NO 5 11011618 | PIT NO 5 1101 | NORTH VALLEY | 6.0991 | 69.0036 | 93.71% | 0 | 2 | 100% | 0% | 0 | 0.047368 | 1 | 0.028548 | 0.0013523 | Medium | Medium | Low | 3179 | 1719 | 0.047368 | -0.0052937
OILFIELDS 1103N42 | OILFIELDS 1103 | CENTRAL COAST | 2.2461 | 52.6729 | 47.6% | 0 | 0 | 37.49% | 0% | 0 | 0.013447 | 1 | 0.061363 | 0.00082516 | Low | Low | Low | 3180 | 2688 | 0.013447 | -0.006646
SAN MIGUEL 1106N34 | SAN MIGUEL 1106 | LOS PADRES | 0.29269 | 10 | 21.51% | 0 | 0 | 2.142% | 0% | 0 | 0.0065395 | 1 | 0.080486 | 0.00052634 | Low | Low | Low | 3181 | 3078 | 0.0065395 | -0.0074711
OCEANO 1105V20 | OCEANO 1105 | LOS PADRES | 0.031809 | 10 | 0% | 0 | 0 | 0.5465% | 0% | 0 | 0.0047237 | 0 | 0 | 0 | Low | Low | Low | 3182 | 3182 | 0 | -0.0079975
ECHO SUMMIT 1101CB | ECHO SUMMIT 1101 | (blank) | 0.03514 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 0 | 0 | 0 | Medium | Medium | Low | 3182 | 3182 | 0 | -0.0079975
MC ARTHUR 110137388 | MC ARTHUR 1101 | NORTH VALLEY | 8.6734 | 54.6058 | 74.62% | 0 | 2 | 69.39% | 0% | 0 | 0.024182 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0079975
CHOLAME 2102X10 | CHOLAME 2102 | LOS PADRES | 19.7574 | 72.3337 | 100% | 0 | 0 | 44.78% | 0% | 0 | 0.028694 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.007634
DUNLAP 110239190 | DUNLAP 1102 | FRESNO | 1.8032 | 10 | 99.73% | 0 | 0 | 100% | 0% | 0 | 0.02845 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0072704
LAYTONVILLE 11011760 | LAYTONVILLE 1101 | HUMBOLDT | 8.2141 | 83.102 | 88.6% | 5 | 4 | 64.9% | 0% | 0 | 0.039524 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0069069
OILFIELDS 11037006 | OILFIELDS 1103 | CENTRAL COAST | 2.4385 | 10 | 100% | 0 | 0 | 16.07% | 0% | 0 | 0.016263 | 0 | 0 | -0.00036352 | Low | Low | Low | 3184 | 3182 | 0 | -0.0065434
CARLOTTA 112144150 | CARLOTTA 1121 | HUMBOLDT | 3.5728 | 56.6428 | 100% | 0 | 1 | 100% | 0% | 0 | 0.039603 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0061799
DUNLAP 11027050 | DUNLAP 1102 | FRESNO | 9.1044 | 57.339 | 92.11% | 4 | 10 | 100% | 0% | 0 | 0.15825 | 0 | 0 | -0.00036352 | High | High | Low | 3184 | 3182 | 0 | -0.0058164
PIT NO 5 11013308 | PIT NO 5 1101 | NORTH VALLEY | 0.044135 | 85 | 100% | 0 | 0 | 100% | 0% | 0 | 0.046733 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0054528
EL DORADO PH 210113532 | EL DORADO PH 2101 | SIERRA | 5.3271 | 64.1847 | 100% | 5 | 1 | 100% | 0% | 0 | 0.082958 | 0 | 0 | -0.00036352 | High | High | Low | 3184 | 3182 | 0 | -0.0050893
BRIDGEVILLE 1102 | BRIDGEVILLE 1102 | HUMBOLDT | 0.0078479 | 90 | 100% | 0 | 0 | 100% | 0% | 0 | 0.048281 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0047258
BRIDGEVILLE 110237486 | BRIDGEVILLE 1102 | HUMBOLDT | 10.3672 | 71.0468 | 99.35% | 4 | 7 | 92.24% | 0% | 0 | 0.054132 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0043623
DUNLAP 11037170 | DUNLAP 1103 | FRESNO | 5.3633 | 51.4528 | 91.12% | 7 | 8 | 100% | 0% | 0 | 0.057836 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0039987
DUNLAP 1102778286 | DUNLAP 1102 | FRESNO | 2.6016 | 93.4441 | 63.93% | 0 | 0 | 100% | 0% | 0 | 0.042218 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0036352
DUNLAP 1102CB | DUNLAP 1102 | FRESNO | 6.506 | 11.6092 | 99.83% | 1 | 2 | 100% | 0% | 0 | 0.034553 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0032717
BOGARD 1101CB | BOGARD 1101 | NORTH VALLEY | 0.51623 | 20.4818 | 100% | 1 | 0 | 100% | 0% | 0 | 0.03523 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0029082
DUNLAP 11037080 | DUNLAP 1103 | FRESNO | 7.9166 | 53.1398 | 56.92% | 4 | 5 | 100% | 0% | 0 | 0.052315 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0025447
DUNLAP 11027290 | DUNLAP 1102 | FRESNO | 0.73169 | 39.1465 | 99.26% | 0 | 9 | 100% | 0% | 0 | 0.04685 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0021811
DUNLAP 1103CB | DUNLAP 1103 | FRESNO | 5.3266 | 46.6515 | 99.77% | 2 | 1 | 100% | 0% | 0 | 0.043161 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0018176
BALCH NO 1 1101R372 | BALCH NO 1 1101 | FRESNO | 6.0973 | 42.1008 | 100% | 0 | 0 | 100% | 0% | 0 | 0.035267 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.0014541
EL DORADO PH 210136764 | EL DORADO PH 2101 | SIERRA | 3.1646 | 79.8685 | 100% | 3 | 0 | 72.39% | 0% | 0 | 0.12435 | 0 | 0 | -0.00036352 | High | High | Low | 3184 | 3182 | 0 | -0.0010906
BRIDGEVILLE 1102CB | BRIDGEVILLE 1102 | HUMBOLDT | 0.72529 | 72.3371 | 88.58% | 0 | 0 | 5.257% | 0% | 0 | 0.020259 | 0 | 0 | -0.00036352 | Low | Low | Low | 3184 | 3182 | 0 | -0.00072704
DUNLAP 11037991F | DUNLAP 1103 | FRESNO | 2.6521 | 79.9208 | 100% | 1 | 4 | 100% | 0% | 0 | 0.056283 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0 | -0.00036352

## Dx - Inspection
Dx Prioritization Output - Inspection
Circuit Information |  |  |  |  | Independent Variables | [29 empty] | Dependent Variable | Risk Scoring |  |  |  | Risk Tiers
Feeder Name | Circuit ID | Region Name | Division Name | Tier 2/3 OH Miles | 3-year Average Summer Load | Average Pole Height | Loading Percent - Mile-weighted Average | Conductor Size 2 - % of Miles | Conductor Size 4 - % of Miles | Conductor Size 6 - % of Miles | Conductor_Broken_Damaged | Conductor_Clearance_Impaired | Total Fuses | Material AR - % of Miles | Material C - % of Miles | Pole Species - % Western Red Cedar | Pole Height >45 | Poles Original Treatment: Cellon_Gas | Poles Original Treatment: Copper_Napthenate__CNI_ | Poles Original Treatment: Methane_Propane | Poles Original Treatment: Penta | Poles Original Treatment: Penta_in_Petroleum | Total Splice Count | Switch Type: 14 | Total Switches | Total Poles | Transformers: Avg SummerPCT | Transformers: RatedKVA - 15 | Transformers: RatedKVA - 25 | Transformers: RatedKVA - 50 | Total Transformers | Transformers Version: A3P7 | VoltageRegulators Version: M2C9 | Number of Fuses Per Phase: 1 | Above Average Outage Indicator | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Consolidated Risk Score | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Consolidated Risk Score | Rank Cons Risk | Rank P*C | P*C
MEADOW LANE 2106 | 014302106 | BAY AREA | DIABLO | 0.84595 | 1211425.3333 | 41.6667 | 0% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 16.67% | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6 | 46.6667 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.12434 | 85.4511 | 6.3861 | 67.8537 | Low | High | High | Top | 63 | 1 | 545.7029
DOWNIEVILLE DIESEL 1101 | 158001101 | NORTHERN | SIERRA | 0.032712 | 0 | 45 | 0% | 100% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.51842 | 102.1389 | 5.2688 | 278.9877 | Medium | High | Medium | Top | 2 | 2 | 538.1461
ORO FINO 1102 | 103031102 | NORTHERN | NORTH VALLEY | 109.5969 | 444513.6667 | 41.5442 | 15.84% | 67.73% | 17.24% | 3.447% | 14 | 3 | 125 | 92.19% | 3.587% | 5.444% | 143 | 1245 | 41 | 0 | 643 | 97 | 1 | 37 | 57 | 2700 | 45.6659 | 376 | 190 | 26 | 881 | 0 | 4 | 122 | 0 | 0.12196 | 76.0455 | 5.7587 | 53.4088 | Low | High | High | Top | 93 | 3 | 437.9241
ORO FINO 1101 | 103031101 | NORTHERN | NORTH VALLEY | 46.3606 | 646807.6667 | 42.8923 | 21.1% | 79.62% | 2.308% | 0% | 13 | 3 | 150 | 90.41% | 2.501% | 5.505% | 173 | 1023 | 9 | 0 | 184 | 68 | 10 | 26 | 59 | 1544 | 68.3964 | 344 | 321 | 145 | 967 | 0 | 4 | 149 | 0 | 0.19375 | 60.5421 | 6.6109 | 77.546 | Low | High | High | Top | 51 | 4 | 400.238
MIWUK 1701 | 163661701 | CENTRAL VALLEY | YOSEMITE | 77.1453 | 519456 | 43.0016 | 35.1% | 79.89% | 1.633% | 2.682% | 18 | 1 | 135 | 86.77% | 6.286% | 5.964% | 330 | 999 | 1 | 0 | 852 | 155 | 57 | 10 | 39 | 2448 | 17.2147 | 478 | 310 | 48 | 1179 | 0 | 0 | 135 | 0 | 0.2456 | 58.7054 | 6.395 | 92.2031 | Low | High | High | Top | 35 | 5 | 375.4194
WOODACRE 1101 | 043021101 | BAY AREA | NORTH BAY | 37.9171 | 273416.3333 | 43.81 | 20.15% | 5.073% | 33.09% | 36.66% | 32 | 6 | 79 | 29.85% | 45.04% | 9.908% | 250 | 387 | 11 | 7 | 313 | 262 | 0 | 20 | 36 | 1090 | 35.8159 | 113 | 108 | 20 | 359 | 0 | 0 | 79 | 1 | 0.86687 | 49.5253 | 7.3343 | 314.8735 | High | High | High | Top | 1 | 6 | 363.2322
PARADISE 1106 | 102831106 | NORTHERN | NORTH VALLEY | 24.5474 | 711555.3333 | 45.3904 | 76.96% | 59.18% | 0.2597% | 0% | 2 | 4 | 29 | 82.84% | 0% | 4.075% | 234 | 638 | 0 | 0 | 10 | 69 | 0 | 3 | 14 | 859 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 29 | 0 | 0.24182 | 43.2819 | 7.4641 | 78.1235 | Low | High | High | Top | 49 | 7 | 323.059
TIGER CREEK 0201 | 161380201 | CENTRAL VALLEY | STOCKTON | 3.8998 | 887 | 40.0543 | 0% | 22.85% | 77.15% | 0% | 0 | 0 | 2 | 100% | 0% | 4.348% | 8 | 69 | 0 | 0 | 10 | 3 | 0 | 0 | 1 | 92 | 16.1667 | 1 | 4 | 1 | 10 | 0 | 0 | 1 | 0 | 0.22906 | 71.5175 | 4.4647 | 73.1388 | Low | High | Medium | Top | 52 | 8 | 319.3026
MORAGA 1105 | 013801105 | BAY AREA | DIABLO | 9.5389 | 587971.3333 | 45.9444 | 37.45% | 0% | 29.87% | 23.07% | 3 | 2 | 13 | 24.38% | 66.25% | 21.95% | 49 | 69 | 0 | 0 | 20 | 13 | 3 | 5 | 6 | 164 | 24.8462 | 19 | 17 | 5 | 54 | 0 | 0 | 12 | 1 | 0.76456 | 47.5187 | 6.7041 | 243.5644 | High | High | High | Top | 4 | 9 | 318.568
BIG BEND 1102 | 103751102 | NORTHERN | NORTH VALLEY | 38.1787 | 0 | 41.5415 | 0% | 26.13% | 69.74% | 2.151% | 2 | 0 | 23 | 97.83% | 2.151% | 11.87% | 42 | 414 | 24 | 0 | 139 | 82 | 0 | 9 | 12 | 893 | 39.7652 | 113 | 28 | 0 | 258 | 0 | 4 | 23 | 0 | 0.21549 | 67.4098 | 4.7008 | 68.2843 | Low | High | Medium | Top | 61 | 10 | 316.8776
SIERRA CITY GEN 1101 | 158011101 | NORTHERN | SIERRA | 0.018511 | 0 | 40 | 0% | 100% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.46796 | 85.4511 | 3.6603 | 146.3655 | Medium | High | Low | Top | 13 | 11 | 312.7725
MIWUK 1702 | 163661702 | CENTRAL VALLEY | YOSEMITE | 75.7688 | 700089.6667 | 43.5587 | 51.21% | 80.48% | 8.501% | 3.03% | 14 | 1 | 124 | 83.29% | 8.9% | 5.685% | 437 | 1281 | 0 | 0 | 549 | 187 | 15 | 14 | 36 | 2410 | 20.1794 | 574 | 370 | 29 | 1281 | 0 | 0 | 123 | 0 | 0.17901 | 42.6734 | 7.0209 | 53.6334 | Low | High | High | Top | 92 | 12 | 299.604
BRUNSWICK 1105 | 152481105 | NORTHERN | SIERRA | 121.439 | 1156546 | 41.8642 | 38.42% | 92.06% | 2.166% | 0.7665% | 19 | 5 | 296 | 93.3% | 2.918% | 12.71% | 219 | 1949 | 11 | 0 | 579 | 305 | 1 | 59 | 101 | 3375 | 40.1125 | 591 | 409 | 47 | 1422 | 0 | 7 | 296 | 1 | 0.30112 | 82.3318 | 3.5748 | 88.6249 | Low | High | Low | Top | 38 | 13 | 294.3166
MONTE RIO 1113 | 042811113 | NORTHERN | SONOMA | 61.2941 | 888801.3333 | 42.5277 | 24.79% | 5.339% | 50.76% | 32.68% | 51 | 13 | 90 | 47.74% | 42.26% | 11.85% | 299 | 593 | 1 | 9 | 644 | 305 | 101 | 24 | 48 | 1806 | 39.267 | 208 | 169 | 92 | 702 | 0 | 0 | 90 | 1 | 0.89768 | 48.4702 | 5.9889 | 260.5828 | High | High | High | Top | 3 | 14 | 290.2846
WEST POINT 1101 | 163201101 | CENTRAL VALLEY | STOCKTON | 63.0247 | 313435.6667 | 41.0194 | 44.91% | 89.98% | 0% | 0% | 1 | 3 | 72 | 90.89% | 5.997% | 1.771% | 148 | 1043 | 4 | 0 | 568 | 68 | 0 | 10 | 38 | 1863 | 32.8842 | 447 | 207 | 5 | 863 | 0 | 3 | 70 | 0 | 0.073726 | 60.3254 | 4.7757 | 21.2403 | Low | High | Medium | Top | 223 | 15 | 288.0982
SPANISH CREEK 4401 | 103104401 | NORTHERN | NORTH VALLEY | 7.9163 | 4545.3333 | 47.0543 | 179% | 96.68% | 0% | 3.324% | 1 | 0 | 2 | 10.89% | 89.11% | 37.21% | 54 | 33 | 0 | 0 | 59 | 14 | 0 | 0 | 2 | 129 | 16 | 5 | 5 | 1 | 14 | 0 | 1 | 2 | 1 | 0.56086 | 69.1856 | 4.1141 | 159.6402 | Medium | High | Medium | Top | 11 | 16 | 284.6368
PIKE CITY 1101 | 152201101 | NORTHERN | SIERRA | 34.5379 | 89793.3333 | 40.9752 | 25.31% | 99.84% | 0% | 0% | 6 | 2 | 37 | 99.84% | 0.1367% | 13.65% | 54 | 324 | 9 | 0 | 87 | 95 | 10 | 4 | 10 | 806 | 38.1636 | 69 | 25 | 6 | 226 | 0 | 0 | 37 | 1 | 0.62309 | 85.7553 | 3.2113 | 171.5898 | Medium | High | Low | Top | 8 | 17 | 275.3846
STANISLAUS 1702 | 162821702 | CENTRAL VALLEY | YOSEMITE | 85.5755 | 713366.3333 | 43.3785 | 19.57% | 89.52% | 1.995% | 1.119% | 7 | 2 | 187 | 89.99% | 3.239% | 2.18% | 651 | 1571 | 1 | 1 | 834 | 112 | 58 | 33 | 71 | 2936 | 26.0683 | 879 | 402 | 13 | 1757 | 0 | 0 | 187 | 1 | 0.18553 | 45.2841 | 5.7429 | 48.2501 | Low | High | High | Top | 102 | 18 | 260.062
SILVERADO 2103 | 043432103 | BAY AREA | NORTH BAY | 11.51 | 1588607 | 42.7387 | 6.913% | 3.441% | 86.31% | 10.2% | 2 | 0 | 9 | 88.77% | 11.18% | 12.06% | 27 | 50 | 0 | 1 | 47 | 41 | 0 | 5 | 5 | 199 | 47.7167 | 10 | 13 | 3 | 61 | 0 | 0 | 9 | 0 | 0.28458 | 52.7974 | 4.7886 | 71.95 | Low | High | Medium | Top | 55 | 19 | 252.8263
TASSAJARA 2108 | 014662108 | BAY AREA | DIABLO | 1.5457 | 1333879 | 44.4186 | 18.89% | 0% | 33.34% | 66.66% | 0 | 0 | 3 | 33.34% | 66.66% | 18.6% | 10 | 13 | 0 | 0 | 15 | 4 | 0 | 1 | 1 | 43 | 54.96 | 9 | 10 | 0 | 25 | 0 | 0 | 3 | 1 | 0.66045 | 41.5134 | 6.0558 | 166.0359 | High | High | High | Top | 10 | 20 | 251.3971
HALF MOON BAY 1101 | 024101101 | CENTRAL COAST | PENINSULA | 32.9103 | 1062793.6667 | 41.5213 | 27.97% | 0.2214% | 40.67% | 32.07% | 12 | 4 | 45 | 44.44% | 48.11% | 6.897% | 38 | 186 | 0 | 2 | 229 | 27 | 38 | 4 | 8 | 493 | 30.4785 | 57 | 33 | 5 | 169 | 1 | 0 | 45 | 1 | 0.80716 | 36.9629 | 6.6522 | 198.469 | High | High | High | Top | 6 | 21 | 245.8857
FORESTHILL 1101 | 152181101 | NORTHERN | SIERRA | 65.2463 | 717203.6667 | 39.6521 | 32.8% | 90.26% | 3.167% | 0.1137% | 6 | 7 | 140 | 93.37% | 0.5195% | 5.618% | 57 | 963 | 8 | 0 | 365 | 128 | 0 | 31 | 46 | 1780 | 42.6561 | 326 | 226 | 26 | 744 | 0 | 0 | 140 | 0 | 0.13101 | 62.8764 | 3.8926 | 32.0653 | Low | High | Medium | Top | 165 | 22 | 244.7513
SYCAMORE CREEK 1111 | 102971111 | NORTHERN | NORTH VALLEY | 54.4191 | 856377.3333 | 41.5149 | 121.2% | 57.08% | 32.93% | 6.766% | 4 | 2 | 61 | 90.01% | 6.766% | 7.16% | 74 | 483 | 30 | 0 | 187 | 46 | 0 | 9 | 11 | 1243 | 38.4848 | 153 | 80 | 5 | 382 | 0 | 6 | 61 | 0 | 0.078038 | 49.371 | 4.9398 | 19.0319 | Low | High | Medium | Top | 239 | 23 | 243.8816
BRUNSWICK 1103 | 152481103 | NORTHERN | SIERRA | 56.4048 | 1067549.3333 | 41.3644 | 13.51% | 62.41% | 31.22% | 5.069% | 4 | 1 | 169 | 81.85% | 16.84% | 11.68% | 126 | 1045 | 10 | 0 | 335 | 138 | 3 | 26 | 46 | 1849 | 37.0174 | 279 | 171 | 27 | 704 | 0 | 2 | 169 | 1 | 0.14531 | 56.0528 | 4.315 | 35.1465 | Low | High | Medium | Top | 145 | 24 | 241.8683
MONTE RIO 1112 | 042811112 | NORTHERN | SONOMA | 20.2317 | 364345.6667 | 42.1563 | 33.13% | 13.3% | 28.64% | 27.75% | 26 | 9 | 48 | 43.13% | 41.53% | 7.236% | 112 | 226 | 0 | 12 | 256 | 126 | 11 | 11 | 20 | 691 | 41.4675 | 76 | 53 | 27 | 240 | 0 | 2 | 48 | 1 | 0.82845 | 41.2665 | 5.8415 | 199.7026 | High | High | High | Top | 5 | 25 | 241.057
EL DORADO PH 2102 | 152762102 | NORTHERN | SIERRA | 34.253 | 447460.6667 | 42.0764 | 22.92% | 82.78% | 4.398% | 0% | 13 | 2 | 59 | 88.76% | 11.02% | 0.9658% | 146 | 609 | 16 | 0 | 268 | 70 | 12 | 13 | 22 | 1139 | 45.3724 | 279 | 123 | 24 | 527 | 0 | 1 | 59 | 0 | 0.22067 | 63.9055 | 3.7472 | 52.8413 | Low | High | Medium | Top | 94 | 26 | 239.4637
KANAKA 1101 | 103221101 | NORTHERN | NORTH VALLEY | 93.2538 | 157764.3333 | 41.4647 | 24.57% | 19.68% | 69.64% | 3.536% | 17 | 4 | 56 | 81.77% | 13.86% | 5.938% | 101 | 1074 | 43 | 0 | 326 | 111 | 4 | 29 | 39 | 2004 | 42.3043 | 217 | 44 | 1 | 551 | 0 | 2 | 56 | 0 | 0.1712 | 50.17 | 4.744 | 40.7468 | Low | High | Medium | Top | 125 | 27 | 238.0071
WYANDOTTE 1103 | 102911103 | NORTHERN | NORTH VALLEY | 85.3328 | 1309730 | 41.7952 | 68.67% | 12.09% | 73.24% | 3.693% | 6 | 1 | 67 | 91.02% | 3.693% | 4.266% | 114 | 1321 | 29 | 0 | 252 | 128 | 0 | 23 | 38 | 2063 | 43.7528 | 326 | 93 | 5 | 740 | 0 | 4 | 67 | 0 | 0.04014 | 39.8104 | 5.8477 | 9.3445 | Low | High | High | Mid | 340 | 28 | 232.7993
CHALLENGE 1101 | 103201101 | NORTHERN | NORTH VALLEY | 48.4283 | 111396.6667 | 41.2851 | 70.45% | 93.19% | 6.727% | 0% | 21 | 0 | 53 | 99.91% | 0.09182% | 5.085% | 47 | 581 | 13 | 0 | 189 | 74 | 7 | 19 | 27 | 1180 | 40.4863 | 131 | 29 | 5 | 345 | 0 | 6 | 53 | 0 | 0.29117 | 73.9452 | 3.1368 | 67.5371 | Low | High | Low | Top | 65 | 29 | 231.9531
SILVERADO 2105 | 043432105 | BAY AREA | NORTH BAY | 39.6838 | 1206104.6667 | 42.9808 | 18.97% | 0.5537% | 84.96% | 11.55% | 11 | 5 | 61 | 78.81% | 21.17% | 8.075% | 129 | 311 | 0 | 3 | 114 | 140 | 12 | 24 | 26 | 743 | 53.0083 | 59 | 53 | 20 | 246 | 0 | 0 | 60 | 1 | 0.61045 | 41.9515 | 5.4951 | 140.7273 | Medium | High | High | Top | 14 | 30 | 230.5296
CHALLENGE 1102 | 103201102 | NORTHERN | NORTH VALLEY | 63.9131 | 200478.6667 | 40.6424 | 26.02% | 28.96% | 67.3% | 0% | 21 | 5 | 54 | 97.76% | 0.003964% | 3.731% | 51 | 848 | 23 | 0 | 214 | 52 | 0 | 14 | 21 | 1474 | 45.2548 | 211 | 53 | 4 | 551 | 0 | 4 | 53 | 0 | 0.1784 | 54.9878 | 4.1301 | 40.5158 | Low | High | Medium | Top | 126 | 31 | 227.1058
PUEBLO 2102 | 043292102 | BAY AREA | NORTH BAY | 24.0288 | 2021001 | 42.1375 | 22.76% | 0% | 93.89% | 6.111% | 4 | 2 | 18 | 93.79% | 6.207% | 5% | 46 | 83 | 1 | 2 | 107 | 108 | 0 | 7 | 8 | 400 | 38.5968 | 45 | 28 | 6 | 131 | 0 | 0 | 18 | 1 | 0.43521 | 49.0597 | 4.583 | 97.8539 | Medium | High | Medium | Top | 31 | 32 | 224.8421
BELL 1110 | 152701110 | NORTHERN | SIERRA | 0.36763 | 1090418.3333 | 41.875 | 14.41% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 33.2 | 1 | 3 | 0 | 5 | 0 | 0 | 0 | 0 | 0.21636 | 47.6367 | 4.7034 | 48.4765 | Low | High | Medium | Top | 101 | 33 | 224.0565
ALLEGHANY 1101 | 152101101 | NORTHERN | SIERRA | 63.6568 | 172093.6667 | 38.5274 | 61.05% | 85.42% | 1.736% | 1.002% | 9 | 3 | 93 | 85.96% | 2.267% | 14.33% | 106 | 759 | 9 | 58 | 427 | 166 | 0 | 20 | 69 | 2156 | 37.914 | 96 | 59 | 11 | 301 | 0 | 6 | 93 | 0 | 0.22658 | 65.1726 | 3.4063 | 50.3011 | Low | High | Low | Top | 99 | 34 | 222.0006
BRUNSWICK 1102 | 152481102 | NORTHERN | SIERRA | 51.0819 | 584357.6667 | 42.8594 | 18.57% | 88.64% | 6.798% | 0% | 7 | 1 | 80 | 81.29% | 14.15% | 15.25% | 93 | 743 | 3 | 0 | 204 | 184 | 1 | 17 | 27 | 1298 | 36.6673 | 238 | 106 | 7 | 500 | 0 | 2 | 80 | 0 | 0.11075 | 58.9898 | 3.7495 | 24.4963 | Low | High | Medium | Top | 196 | 35 | 221.181
GARCIA 0401 | 043040401 | NORTHERN | HUMBOLDT | 2.4735 | 4533.6667 | 39.7059 | 0% | 75.56% | 24.44% | 0% | 1 | 1 | 1 | 100% | 0% | 0% | 2 | 19 | 0 | 0 | 9 | 0 | 0 | 1 | 2 | 34 | 57.5714 | 3 | 2 | 0 | 8 | 0 | 0 | 1 | 0 | 0.33591 | 93.5007 | 2.3124 | 72.6268 | Medium | High | Low | Top | 54 | 36 | 216.2094
WOODSIDE 1101 | 024251101 | CENTRAL COAST | PENINSULA | 42.3143 | 731429.6667 | 42.484 | 26.09% | 0.1141% | 34.56% | 43.73% | 70 | 2 | 106 | 47.82% | 48.88% | 12.26% | 139 | 482 | 0 | 6 | 559 | 67 | 1 | 12 | 22 | 1248 | 20.9813 | 135 | 157 | 23 | 443 | 4 | 1 | 105 | 1 | 0.80161 | 32.5504 | 6.6282 | 172.9485 | High | High | High | Top | 7 | 37 | 215.7519
BONNIE NOOK 1102 | 152301102 | NORTHERN | SIERRA | 34.3352 | 96245 | 42.2368 | 13.33% | 82.61% | 12.88% | 4.503% | 4 | 7 | 51 | 85.18% | 14.81% | 14.47% | 86 | 399 | 7 | 0 | 125 | 106 | 3 | 17 | 17 | 919 | 34.8528 | 121 | 44 | 2 | 279 | 0 | 0 | 51 | 1 | 0.51672 | 79.0787 | 2.6595 | 108.6697 | Medium | High | Low | Top | 25 | 38 | 210.3079
MIRABEL 1101 | 042091101 | NORTHERN | SONOMA | 30.224 | 547280.3333 | 43.036 | 23.83% | 19.53% | 54.19% | 20.9% | 27 | 2 | 49 | 55.16% | 39.46% | 7.376% | 106 | 313 | 0 | 2 | 142 | 58 | 0 | 7 | 11 | 583 | 28.2218 | 87 | 42 | 11 | 252 | 0 | 0 | 49 | 1 | 0.72695 | 39.009 | 5.3754 | 152.4327 | High | High | Medium | Top | 12 | 39 | 209.6888
VINEYARD 2108 | 014502108 | CENTRAL COAST | MISSION | 4.6061 | 1483072.6667 | 43.2524 | 10.74% | 0% | 71.39% | 28.55% | 0 | 0 | 15 | 37.6% | 62.34% | 17.31% | 20 | 33 | 0 | 3 | 22 | 11 | 0 | 1 | 3 | 104 | 40.3103 | 11 | 14 | 0 | 33 | 0 | 0 | 15 | 1 | 0.66651 | 35.5506 | 5.877 | 139.2542 | High | High | High | Top | 15 | 40 | 208.9307
LAS GALLINAS A 1105 | 042991105 | BAY AREA | NORTH BAY | 13.3067 | 815852.6667 | 47.0429 | 54.58% | 4.201% | 51.94% | 3.297% | 0 | 0 | 17 | 52.88% | 6.559% | 1.709% | 114 | 135 | 0 | 1 | 46 | 38 | 0 | 6 | 13 | 234 | 33.3333 | 15 | 20 | 3 | 58 | 0 | 2 | 17 | 0 | 0.25962 | 27.6546 | 7.5185 | 53.9799 | Low | High | High | Top | 91 | 41 | 207.9219
BOLINAS 1101 | 042261101 | BAY AREA | NORTH BAY | 36.998 | 354120 | 45.8392 | 71.21% | 6.313% | 30.38% | 16.61% | 5 | 1 | 43 | 15.42% | 45.77% | 10.19% | 169 | 183 | 8 | 10 | 199 | 89 | 9 | 13 | 35 | 569 | 23.6196 | 28 | 27 | 10 | 95 | 0 | 5 | 43 | 0 | 0.48819 | 29.7958 | 6.927 | 100.7604 | Medium | High | High | Top | 26 | 42 | 206.3957
EL DORADO PH 2101 | 152762101 | NORTHERN | SIERRA | 156.326 | 892577.3333 | 42.4752 | 40.66% | 91.79% | 3.443% | 0.1415% | 20 | 6 | 210 | 93.29% | 3.482% | 2.047% | 428 | 2233 | 36 | 0 | 801 | 247 | 55 | 45 | 77 | 4347 | 47.9521 | 858 | 340 | 34 | 1844 | 0 | 5 | 209 | 0 | 0.25422 | 60.6839 | 3.3481 | 51.6505 | Low | High | Low | Top | 96 | 43 | 203.1751
PIKE CITY 1102 | 152201102 | NORTHERN | SIERRA | 9.4149 | 3190 | 40.4831 | 16.19% | 62.21% | 37.34% | 0% | 2 | 0 | 8 | 75.24% | 24.76% | 35.27% | 7 | 31 | 1 | 1 | 80 | 72 | 0 | 0 | 3 | 207 | 27.4706 | 7 | 1 | 0 | 17 | 0 | 0 | 8 | 0 | 0.30098 | 90.6538 | 2.225 | 60.7099 | Low | High | Low | Top | 79 | 44 | 201.7078
PINE GROVE 1102 | 163751102 | CENTRAL VALLEY | STOCKTON | 177.6802 | 1059080.6667 | 41.5789 | 39.49% | 69.29% | 21.95% | 0.3204% | 17 | 4 | 227 | 90.53% | 2.333% | 4.474% | 473 | 2499 | 7 | 0 | 1385 | 286 | 5 | 44 | 72 | 4806 | 34.2066 | 889 | 448 | 29 | 1913 | 0 | 3 | 224 | 0 | 0.18246 | 35.5813 | 5.6368 | 36.5942 | Low | High | High | Top | 141 | 45 | 200.5632
BONNIE NOOK 1101 | 152301101 | NORTHERN | SIERRA | 24.4427 | 118202 | 43.2057 | 19.81% | 63.3% | 32.61% | 0.4943% | 0 | 0 | 52 | 58.93% | 41.04% | 13.11% | 138 | 239 | 6 | 0 | 177 | 73 | 0 | 8 | 14 | 671 | 40.1806 | 91 | 46 | 4 | 225 | 0 | 2 | 52 | 0 | 0.33611 | 71.1778 | 2.8122 | 67.2784 | Medium | High | Low | Top | 67 | 46 | 200.1696
MONTE RIO 1111 | 042811111 | NORTHERN | SONOMA | 59.7678 | 340795 | 41.9722 | 32.33% | 1.776% | 42.07% | 47.48% | 42 | 28 | 95 | 32.57% | 59.3% | 12.46% | 158 | 426 | 1 | 5 | 563 | 164 | 40 | 24 | 47 | 1372 | 33.6364 | 181 | 77 | 33 | 524 | 0 | 5 | 95 | 1 | 0.84976 | 36.3844 | 5.4039 | 167.0779 | High | High | High | Top | 9 | 47 | 196.6188
SILVERADO 2104 | 043432104 | BAY AREA | NORTH BAY | 126.0115 | 1582484 | 42.671 | 56.62% | 2.81% | 70.69% | 16.2% | 28 | 8 | 181 | 69.19% | 21.13% | 8.469% | 307 | 997 | 3 | 35 | 670 | 483 | 5 | 39 | 69 | 2633 | 51.0611 | 248 | 201 | 42 | 889 | 0 | 6 | 180 | 1 | 0.64794 | 31.2142 | 6.206 | 125.5164 | Medium | High | High | Top | 17 | 48 | 193.7149
CALPINE 1146 | 048011146 | NORTHERN | SONOMA | 7.0108 | 0 | 54.5 | 0% | 12.38% | 29.09% | 11.85% | 0 | 0 | 12 | 72.04% | 11.85% | 0% | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 13 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 12 | 0 | 0.33574 | 49.4557 | 3.8156 | 63.3541 | Medium | High | Medium | Top | 73 | 49 | 188.7025
MIDDLETOWN 1101 | 043141101 | NORTHERN | HUMBOLDT | 96.9667 | 760831.3333 | 42.8966 | 35.12% | 25.16% | 58.37% | 9% | 21 | 9 | 122 | 80.4% | 14.96% | 9.066% | 388 | 870 | 1 | 18 | 694 | 173 | 14 | 18 | 31 | 2217 | 38.0723 | 307 | 142 | 32 | 732 | 0 | 2 | 122 | 0 | 0.28996 | 42.6631 | 4.373 | 54.0978 | Low | High | Medium | Top | 90 | 50 | 186.5677
ALLEGHANY 1102 | 152101102 | NORTHERN | SIERRA | 18.0939 | 31926.6667 | 45 | 47.86% | 91.29% | 8.479% | 0% | 1 | 1 | 21 | 39.16% | 60.61% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 5 | 15 | 1 | 38.7324 | 22 | 14 | 3 | 75 | 0 | 0 | 21 | 0 | 0.43406 | 85.5381 | 2.1807 | 80.9689 | Medium | High | Low | Top | 43 | 51 | 186.5369
FITCH MOUNTAIN 1113 | 042751113 | NORTHERN | SONOMA | 76.7611 | 881431 | 42.8272 | 26.89% | 3.271% | 63.28% | 31.49% | 33 | 1 | 77 | 63.56% | 35.4% | 8.406% | 201 | 488 | 0 | 25 | 273 | 195 | 10 | 16 | 21 | 1154 | 29.4603 | 160 | 80 | 8 | 435 | 0 | 1 | 77 | 0 | 0.6378 | 44.6104 | 4.1614 | 118.4028 | Medium | High | Medium | Top | 20 | 52 | 185.6419
SALT SPRINGS 2102 | 163692102 | CENTRAL VALLEY | STOCKTON | 52.0669 | 174733.6667 | 45.2358 | 15.15% | 63.02% | 1.348% | 0% | 4 | 0 | 49 | 97.67% | 2.329% | 4.379% | 625 | 933 | 0 | 0 | 268 | 88 | 45 | 16 | 32 | 1553 | 26.9377 | 413 | 125 | 6 | 766 | 0 | 2 | 48 | 1 | 0.155 | 45.6414 | 4.0669 | 28.7703 | Low | High | Medium | Top | 174 | 53 | 185.6202
SPRING GAP 1702 | 162831702 | CENTRAL VALLEY | YOSEMITE | 41.0705 | 0 | 42.5719 | 143.6% | 84.92% | 3.058% | 0% | 9 | 1 | 53 | 83.26% | 4.717% | 8.784% | 171 | 335 | 0 | 0 | 526 | 59 | 0 | 11 | 29 | 1184 | 25.0833 | 160 | 108 | 8 | 449 | 0 | 0 | 52 | 0 | 0.23994 | 50.1342 | 3.6805 | 44.2745 | Low | High | Low | Top | 110 | 54 | 184.5213
HICKS 2103 | 083432103 | CENTRAL COAST | SAN JOSE | 12.878 | 1050230 | 45.2812 | 32.31% | 0% | 80.23% | 19.77% | 1 | 2 | 12 | 80.23% | 19.77% | 17.5% | 40 | 83 | 0 | 3 | 33 | 2 | 0 | 3 | 3 | 160 | 46.1071 | 8 | 10 | 0 | 33 | 0 | 0 | 12 | 0 | 0.36574 | 36.537 | 4.9968 | 66.7726 | Medium | High | Medium | Top | 69 | 55 | 182.5692
FORT ROSS 1121 | 042851121 | NORTHERN | SONOMA | 94.05 | 141625.6667 | 41.9432 | 26.12% | 13.3% | 55.06% | 26.25% | 25 | 3 | 96 | 60.65% | 37.35% | 4.676% | 121 | 275 | 0 | 7 | 510 | 240 | 2 | 24 | 40 | 1326 | 27.0773 | 158 | 43 | 10 | 396 | 0 | 2 | 96 | 0 | 0.55429 | 46.7686 | 3.8784 | 100.5414 | Medium | High | Medium | Top | 27 | 56 | 181.3878
MOLINO 1102 | 042571102 | NORTHERN | SONOMA | 113.1393 | 1494417.6667 | 43.6669 | 26.83% | 0.09873% | 58.93% | 35.46% | 38 | 12 | 205 | 55.31% | 39.9% | 7.03% | 582 | 1241 | 3 | 40 | 684 | 353 | 48 | 45 | 59 | 2717 | 31.1546 | 428 | 183 | 42 | 1093 | 0 | 3 | 205 | 1 | 0.71054 | 36.3102 | 4.8722 | 125.7032 | High | High | Medium | Top | 16 | 57 | 176.912
SAN RAMON 2108 | 014232108 | CENTRAL COAST | MISSION | 16.6213 | 1249108 | 44.2447 | 49.12% | 10.21% | 65.3% | 24.46% | 1 | 3 | 44 | 50.08% | 49.89% | 7.463% | 52 | 146 | 2 | 3 | 113 | 10 | 0 | 7 | 10 | 335 | 46.7524 | 31 | 30 | 5 | 112 | 1 | 0 | 43 | 0 | 0.45199 | 27.2942 | 6.4811 | 79.9552 | Medium | High | High | Top | 46 | 58 | 176.8971
BRUNSWICK 1104 | 152481104 | NORTHERN | SIERRA | 56.8876 | 1004879.3333 | 41.5361 | 23.73% | 63.18% | 27.21% | 2.673% | 6 | 2 | 99 | 83.29% | 9.921% | 11.92% | 122 | 845 | 9 | 1 | 364 | 179 | 19 | 10 | 31 | 1636 | 38.3063 | 248 | 169 | 19 | 632 | 0 | 3 | 99 | 0 | 0.11063 | 38.5596 | 4.5752 | 19.5179 | Low | High | Medium | Top | 235 | 59 | 176.4199
CRESCENT MILLS 2101 | 103132101 | NORTHERN | NORTH VALLEY | 49.7398 | 187120.6667 | 42.6676 | 11.47% | 88.75% | 1.613% | 3.972% | 1 | 1 | 46 | 89.85% | 6.575% | 19.91% | 144 | 469 | 12 | 0 | 251 | 123 | 0 | 10 | 14 | 1105 | 42.9088 | 95 | 29 | 2 | 279 | 0 | 1 | 46 | 0 | 0.23089 | 48.487 | 3.5488 | 39.7293 | Low | High | Low | Top | 131 | 60 | 172.07
MIDDLETOWN 1103 | 043141103 | NORTHERN | HUMBOLDT | 27.8272 | 89806 | 43.6236 | 68.25% | 9.431% | 76.29% | 0.7473% | 0 | 0 | 12 | 85.72% | 0.7473% | 17.22% | 90 | 130 | 0 | 3 | 94 | 70 | 2 | 4 | 6 | 360 | 37.5278 | 34 | 13 | 3 | 78 | 0 | 0 | 12 | 0 | 0.23524 | 39.0448 | 4.3749 | 40.1831 | Low | High | Medium | Top | 129 | 61 | 170.8184
ROSSMOOR 1108 | 014161108 | BAY AREA | DIABLO | 13.4853 | 1018341.3333 | 44.9576 | 79.53% | 1.278% | 20.16% | 50.27% | 4 | 0 | 34 | 21.2% | 50.57% | 8.017% | 47 | 87 | 0 | 0 | 68 | 13 | 0 | 6 | 11 | 237 | 20.6591 | 26 | 37 | 4 | 93 | 0 | 0 | 34 | 1 | 0.69505 | 24.5636 | 6.9013 | 117.8266 | High | High | High | Top | 21 | 62 | 169.5214
WEST POINT 1102 | 163201102 | CENTRAL VALLEY | STOCKTON | 230.9017 | 563721.6667 | 41.661 | 28.27% | 88% | 7.589% | 0% | 20 | 9 | 289 | 93.01% | 3.954% | 3.801% | 434 | 2599 | 5 | 1 | 1348 | 396 | 13 | 36 | 71 | 5340 | 28.6072 | 923 | 305 | 7 | 2081 | 0 | 6 | 289 | 0 | 0.20713 | 35.6819 | 4.7401 | 35.0326 | Low | High | Medium | Top | 147 | 63 | 169.1346
APPLE HILL 1104 | 153661104 | NORTHERN | SIERRA | 93.3232 | 721905.3333 | 41.8187 | 25.47% | 84.35% | 7.756% | 0.5476% | 11 | 3 | 170 | 90.26% | 3.94% | 0.9738% | 169 | 1508 | 26 | 0 | 526 | 149 | 18 | 19 | 32 | 2670 | 42.4293 | 552 | 282 | 23 | 1142 | 0 | 3 | 170 | 0 | 0.11727 | 51.8866 | 3.2527 | 19.7917 | Low | High | Low | Top | 233 | 64 | 168.7734
CALPINE 1144 | 048011144 | NORTHERN | SONOMA | 30.4155 | 14794.6667 | 0 | 0% | 17.18% | 39.68% | 6.755% | 0 | 0 | 35 | 56.23% | 9.093% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 19 | 0 | 5 | 2 | 5 | 2 | 44 | 0 | 0 | 35 | 0 | 0.33222 | 44.753 | 3.7313 | 55.4765 | Medium | High | Low | Top | 87 | 65 | 166.9886
PUEBLO 2103 | 043292103 | BAY AREA | NORTH BAY | 47.7491 | 1373463.3333 | 42.5493 | 34.46% | 1.582% | 78.95% | 19.46% | 25 | 1 | 61 | 56.76% | 43.24% | 6.771% | 131 | 363 | 0 | 11 | 284 | 170 | 6 | 12 | 18 | 1019 | 40.3447 | 130 | 48 | 7 | 331 | 0 | 0 | 61 | 1 | 0.52269 | 33.3329 | 4.8731 | 84.9015 | Medium | High | Medium | Top | 40 | 66 | 162.4333
PURISIMA 1101 | 182971101 | CENTRAL COAST | LOS PADRES | 19.2204 | 1576262.6667 | 41.0931 | 135.2% | 0% | 36.93% | 11.68% | 2 | 0 | 7 | 36.93% | 11.68% | 0.8032% | 13 | 11 | 0 | 23 | 124 | 30 | 0 | 10 | 18 | 249 | 25.1875 | 4 | 7 | 1 | 36 | 0 | 0 | 7 | 0 | 0.29858 | 23.0277 | 6.8643 | 47.1964 | Low | High | High | Top | 105 | 67 | 158.0695
JARVIS 1111 | 013501111 | CENTRAL COAST | MISSION | 1.7872 | 1285978.3333 | 46.875 | 10.08% | 0% | 3.913% | 96.09% | 1 | 2 | 2 | 3.913% | 96.09% | 0% | 10 | 18 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 24 | 0.8 | 1 | 3 | 0 | 9 | 0 | 0 | 1 | 0 | 0.2221 | 27.9901 | 5.6278 | 34.9862 | Low | High | High | Top | 149 | 68 | 157.5226
DUNBAR 1103 | 043071103 | NORTHERN | SONOMA | 32.1454 | 645561.3333 | 44.5221 | 56.3% | 0% | 88.63% | 8.735% | 1 | 2 | 24 | 87.06% | 10.31% | 7.875% | 113 | 251 | 2 | 5 | 98 | 102 | 0 | 6 | 7 | 546 | 39.7349 | 89 | 42 | 10 | 222 | 0 | 0 | 24 | 0 | 0.13363 | 27.724 | 5.6755 | 21.0257 | Low | High | High | Top | 225 | 69 | 157.3488
GRAYS FLAT 0401 | 102530401 | NORTHERN | NORTH VALLEY | 10.7057 | 15420.6667 | 44.4889 | 76.07% | 74.47% | 0.1799% | 21.84% | 1 | 0 | 13 | 68.42% | 28.08% | 21.68% | 76 | 87 | 3 | 0 | 48 | 27 | 0 | 0 | 0 | 226 | 16.1429 | 13 | 22 | 1 | 53 | 0 | 0 | 13 | 0 | 0.45263 | 54.5771 | 2.8156 | 69.5542 | Medium | High | Low | Top | 58 | 70 | 153.6677
PARADISE 1105 | 102831105 | NORTHERN | NORTH VALLEY | 14.2966 | 586838.6667 | 42.7788 | 31.82% | 35.13% | 6.272% | 28.06% | 10 | 0 | 20 | 43.08% | 30.07% | 4.031% | 95 | 220 | 3 | 0 | 151 | 33 | 0 | 4 | 17 | 521 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 20 | 1 | 0.5487 | 22.8948 | 6.6999 | 84.1666 | Medium | High | High | Top | 42 | 71 | 153.3931
SHADY GLEN 1102 | 152431102 | NORTHERN | SIERRA | 39.9524 | 232070.3333 | 43.3918 | 21.35% | 56.21% | 23.77% | 0.9866% | 1 | 2 | 73 | 85.12% | 7.619% | 7.763% | 157 | 469 | 6 | 0 | 166 | 82 | 0 | 9 | 17 | 979 | 33.3199 | 162 | 92 | 9 | 377 | 0 | 0 | 73 | 0 | 0.095149 | 42.5798 | 3.5604 | 14.4247 | Low | High | Low | Top | 272 | 72 | 151.6013
SANTA ROSA A 1111 | 042151111 | NORTHERN | SONOMA | 5.9664 | 1044190.3333 | 43.6641 | 10.27% | 0% | 60.18% | 39.82% | 1 | 0 | 14 | 60.18% | 39.82% | 12.21% | 32 | 62 | 0 | 0 | 37 | 24 | 0 | 1 | 1 | 131 | 38.7321 | 23 | 9 | 1 | 59 | 0 | 0 | 14 | 1 | 0.6526 | 40.33 | 3.7553 | 98.8371 | Medium | High | Medium | Top | 28 | 73 | 151.4506
REDBUD 1101 | 043191101 | NORTHERN | HUMBOLDT | 50.857 | 569887.6667 | 43.4176 | 20.08% | 15.05% | 67.27% | 3.547% | 4 | 2 | 74 | 81.76% | 4.11% | 8.186% | 266 | 406 | 1 | 5 | 307 | 93 | 3 | 10 | 22 | 1075 | 30.2011 | 158 | 77 | 26 | 369 | 0 | 3 | 74 | 0 | 0.16109 | 32.1788 | 4.6637 | 24.1748 | Low | High | Medium | Top | 200 | 74 | 150.0715
OLEMA 1101 | 042291101 | BAY AREA | NORTH BAY | 66.1086 | 448317.6667 | 44.1264 | 25.78% | 7.557% | 31.32% | 49.59% | 53 | 7 | 85 | 12.34% | 76.2% | 6.101% | 360 | 527 | 7 | 16 | 499 | 201 | 37 | 19 | 28 | 1557 | 29.0694 | 157 | 117 | 14 | 457 | 0 | 4 | 84 | 1 | 0.77859 | 27.9587 | 5.3446 | 116.3441 | High | High | Medium | Top | 22 | 75 | 149.4287
FORESTHILL 1102 | 152181102 | NORTHERN | SIERRA | 29.7452 | 122980.6667 | 40.8218 | 78.51% | 55.95% | 43.8% | 0% | 2 | 0 | 38 | 99.72% | 0.01595% | 10.24% | 60 | 290 | 1 | 0 | 130 | 45 | 0 | 9 | 11 | 586 | 36.7281 | 104 | 55 | 4 | 223 | 0 | 0 | 38 | 0 | 0.25527 | 39.6063 | 3.7424 | 37.8357 | Low | High | Medium | Top | 138 | 76 | 148.2206
COLUMBIA HILL 1101 | 152471101 | NORTHERN | SIERRA | 90.9452 | 320210 | 41.9552 | 37.57% | 51.19% | 48.58% | 0% | 16 | 3 | 99 | 99.88% | 0% | 12.86% | 188 | 1157 | 18 | 0 | 199 | 251 | 2 | 15 | 28 | 2076 | 40.6647 | 245 | 102 | 15 | 706 | 0 | 3 | 99 | 1 | 0.19573 | 39.5629 | 3.742 | 28.9769 | Low | High | Medium | Top | 171 | 77 | 148.0432
GANSNER 1101 | 103021101 | NORTHERN | NORTH VALLEY | 39.2147 | 433695 | 43.3222 | 18.21% | 82.72% | 7.229% | 9.981% | 3 | 1 | 40 | 88.36% | 11.57% | 10.64% | 208 | 544 | 9 | 0 | 272 | 112 | 2 | 10 | 12 | 1081 | 37.7562 | 129 | 62 | 6 | 292 | 0 | 2 | 39 | 0 | 0.14642 | 35.2913 | 4.1621 | 21.5069 | Low | High | Medium | Top | 219 | 78 | 146.8844
ALHAMBRA 1105 | 014101105 | BAY AREA | DIABLO | 37.7253 | 497618.3333 | 44.5342 | 7.539% | 3.137% | 77.85% | 12.85% | 7 | 3 | 75 | 43.84% | 49.99% | 12.42% | 123 | 355 | 1 | 0 | 202 | 50 | 8 | 21 | 30 | 805 | 26.3074 | 110 | 119 | 14 | 340 | 0 | 1 | 75 | 0 | 0.40998 | 24.356 | 5.9383 | 59.2964 | Medium | High | High | Top | 83 | 79 | 144.6337
CASTRO VALLEY 1108 | 014091108 | CENTRAL COAST | MISSION | 23.8731 | 633879.3333 | 43.8625 | 25.09% | 1.618% | 53.21% | 31.18% | 14 | 5 | 49 | 18.59% | 68.72% | 12.72% | 93 | 216 | 0 | 9 | 237 | 33 | 0 | 10 | 21 | 613 | 8.2542 | 75 | 76 | 17 | 247 | 1 | 0 | 49 | 1 | 0.82415 | 22.6481 | 6.3834 | 119.1487 | High | High | High | Top | 19 | 80 | 144.572
MORAGA 1101 | 013801101 | BAY AREA | DIABLO | 19.0142 | 238194.3333 | 45.5655 | 51.54% | 0.2943% | 28.08% | 26.07% | 12 | 7 | 26 | 11.36% | 48.52% | 15.48% | 136 | 93 | 0 | 0 | 200 | 34 | 22 | 11 | 30 | 504 | 23.5492 | 62 | 69 | 17 | 198 | 0 | 0 | 26 | 1 | 0.77846 | 20.5225 | 6.8809 | 109.9299 | High | High | High | Top | 24 | 81 | 141.2139
DUNBAR 1102 | 043071102 | NORTHERN | SONOMA | 49.625 | 1055070 | 44.5079 | 35.25% | 1.251% | 57.69% | 35.79% | 9 | 8 | 92 | 56.29% | 38.6% | 7.402% | 343 | 548 | 2 | 13 | 290 | 153 | 25 | 22 | 31 | 1270 | 40.5804 | 172 | 107 | 24 | 483 | 0 | 0 | 92 | 1 | 0.6997 | 26.194 | 5.3908 | 98.8029 | High | High | High | Top | 29 | 82 | 141.2073
STAFFORD 1102 | 043201102 | BAY AREA | NORTH BAY | 23.9883 | 1147106 | 44.7403 | 41.86% | 2.538% | 46.07% | 47.89% | 10 | 1 | 36 | 45.01% | 51.48% | 5.34% | 159 | 309 | 2 | 3 | 183 | 63 | 0 | 16 | 26 | 618 | 28.0064 | 53 | 40 | 4 | 161 | 0 | 0 | 36 | 1 | 0.68685 | 24.2775 | 5.8053 | 96.8023 | High | High | High | Top | 33 | 83 | 140.9373
CASTRO VALLEY 1106 | 014091106 | CENTRAL COAST | MISSION | 20.1929 | 1020298.3333 | 43.1944 | 30.74% | 0% | 51.18% | 46.16% | 2 | 0 | 29 | 48.72% | 48.62% | 5.627% | 20 | 192 | 1 | 0 | 111 | 7 | 6 | 0 | 1 | 391 | 12.0248 | 27 | 34 | 18 | 126 | 0 | 1 | 29 | 0 | 0.47754 | 22.5872 | 6.233 | 67.2308 | Medium | High | High | Top | 68 | 84 | 140.7869
SAN RAFAEL 1108 | 042011108 | BAY AREA | NORTH BAY | 38.5753 | 1208223.3333 | 44.7083 | 17.5% | 3.798% | 18.92% | 56.56% | 59 | 2 | 96 | 19.21% | 63.02% | 10.94% | 519 | 550 | 22 | 13 | 637 | 437 | 46 | 22 | 39 | 1856 | 39.1417 | 150 | 195 | 89 | 616 | 0 | 0 | 96 | 1 | 0.85709 | 15.8796 | 8.7878 | 119.6041 | High | High | High | Top | 18 | 85 | 139.5474
SILVERADO 2102 | 043432102 | BAY AREA | NORTH BAY | 61.4862 | 1297278.3333 | 43.148 | 89.13% | 0.5129% | 89.11% | 3.798% | 17 | 1 | 75 | 88.65% | 5.534% | 9.625% | 167 | 315 | 1 | 17 | 258 | 241 | 0 | 33 | 47 | 987 | 45.3902 | 60 | 57 | 11 | 282 | 0 | 1 | 75 | 0 | 0.30025 | 27.6603 | 5.016 | 41.6584 | Low | High | Medium | Top | 122 | 86 | 138.7436
BIG BEND 1101 | 103751101 | NORTHERN | NORTH VALLEY | 57.4664 | 0 | 42.1363 | 0% | 38.12% | 57.61% | 1.166% | 22 | 1 | 49 | 87.75% | 9.141% | 12.87% | 63 | 585 | 27 | 0 | 203 | 174 | 9 | 11 | 19 | 1375 | 41.0997 | 175 | 38 | 1 | 355 | 0 | 2 | 49 | 0 | 0.31114 | 24.5458 | 5.5674 | 42.5183 | Low | High | High | Top | 120 | 87 | 136.6551
TASSAJARA 2113 | 014662113 | BAY AREA | DIABLO | 3.7253 | 1442201.6667 | 47 | 34.59% | 2.73% | 47.87% | 28.5% | 0 | 0 | 11 | 33.02% | 49.38% | 17.57% | 34 | 24 | 0 | 0 | 22 | 5 | 0 | 5 | 5 | 74 | 31.75 | 7 | 3 | 1 | 18 | 0 | 0 | 11 | 1 | 0.68513 | 19.1639 | 7.1048 | 93.2843 | High | High | High | Top | 34 | 88 | 136.1559
SOBRANTE 1103 | 014671103 | BAY AREA | DIABLO | 3.9569 | 359945 | 44.5755 | 23.68% | 0% | 17.29% | 17.27% | 2 | 1 | 9 | 24.4% | 30.11% | 31.13% | 17 | 41 | 0 | 0 | 24 | 12 | 0 | 5 | 15 | 106 | 23.0811 | 13 | 13 | 2 | 39 | 0 | 0 | 9 | 1 | 0.66178 | 19.8226 | 6.8661 | 90.0701 | High | High | High | Top | 36 | 89 | 136.1034
PARADISE 1102 | 102831102 | NORTHERN | NORTH VALLEY | 15.5735 | 1127377 | 42.2321 | 18.64% | 19.44% | 26.09% | 38.88% | 1 | 3 | 0 | 45.45% | 39.14% | 5.179% | 76 | 226 | 3 | 0 | 183 | 25 | 71 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38818 | 19.4771 | 6.9671 | 52.6759 | Medium | High | High | Top | 95 | 90 | 135.6986
LOS GATOS 1107 | 082021107 | CENTRAL COAST | DE ANZA | 94.6764 | 820307 | 43.3633 | 45.31% | 7.429% | 67.97% | 9.819% | 45 | 8 | 175 | 76.39% | 10.72% | 10.78% | 351 | 1073 | 1 | 10 | 674 | 173 | 12 | 29 | 51 | 2282 | 3.4667 | 320 | 211 | 40 | 911 | 0 | 0 | 172 | 1 | 0.35698 | 24.1189 | 5.5723 | 47.9779 | Medium | High | High | Top | 103 | 91 | 134.3986
HIGHLANDS 1102 | 043361102 | NORTHERN | HUMBOLDT | 37.0971 | 1292006.6667 | 44.2937 | 50.91% | 1.527% | 69.43% | 1.902% | 1 | 0 | 33 | 58.28% | 14.94% | 7.011% | 167 | 317 | 2 | 13 | 283 | 74 | 0 | 4 | 13 | 813 | 40.3849 | 78 | 76 | 33 | 250 | 0 | 0 | 33 | 0 | 0.17838 | 24.8843 | 5.3908 | 23.9291 | Low | High | High | Top | 203 | 92 | 134.1456
RINCON 1103 | 043321103 | NORTHERN | SONOMA | 45.8675 | 513395 | 42.8019 | 90.78% | 0% | 74.98% | 18.96% | 22 | 0 | 53 | 75.63% | 18.96% | 11.4% | 90 | 271 | 0 | 10 | 247 | 129 | 9 | 10 | 19 | 737 | 33.9135 | 117 | 55 | 16 | 319 | 0 | 5 | 53 | 1 | 0.60151 | 33.225 | 4.0312 | 80.5653 | Medium | High | Medium | Top | 44 | 93 | 133.9381
VALLEY VIEW 1106 | 014341106 | BAY AREA | EAST BAY | 9.8122 | 799970.6667 | 44.5192 | 0% | 0.5291% | 19.36% | 13.87% | 1 | 0 | 8 | 14.66% | 21.58% | 7.051% | 35 | 39 | 0 | 1 | 89 | 17 | 0 | 5 | 7 | 156 | 11.2121 | 8 | 8 | 5 | 38 | 0 | 0 | 8 | 0 | 0.51791 | 17.9636 | 7.3446 | 68.3312 | Medium | High | High | Top | 60 | 94 | 131.9359
MENLO 1102 | 024131102 | CENTRAL COAST | PENINSULA | 28.7936 | 829244.3333 | 42.4303 | 41.92% | 13.21% | 64.33% | 7.693% | 10 | 0 | 50 | 62.16% | 37.46% | 11.65% | 59 | 241 | 2 | 11 | 200 | 31 | 10 | 8 | 12 | 575 | 23.0058 | 61 | 50 | 9 | 177 | 1 | 0 | 50 | 1 | 0.64574 | 23.9405 | 5.4737 | 84.6193 | Medium | High | High | Top | 41 | 95 | 131.0429
ALTO 1124 | 042031124 | BAY AREA | NORTH BAY | 30.9272 | 748572.6667 | 44.3557 | 10.74% | 11.84% | 15.43% | 64.15% | 24 | 4 | 70 | 20.63% | 72.31% | 9.419% | 309 | 427 | 12 | 6 | 460 | 168 | 29 | 9 | 18 | 1274 | 36.3527 | 130 | 115 | 43 | 460 | 0 | 0 | 70 | 1 | 0.88167 | 16.3831 | 7.9503 | 114.8378 | High | High | High | Top | 23 | 96 | 130.2498
STELLING 1110 | 083481110 | CENTRAL COAST | DE ANZA | 37.1918 | 1044813.3333 | 45.1508 | 117.2% | 0.01493% | 67.34% | 16.04% | 16 | 0 | 42 | 65.01% | 21.39% | 7.899% | 180 | 294 | 0 | 6 | 132 | 72 | 0 | 12 | 21 | 633 | 3.3481 | 50 | 36 | 9 | 166 | 0 | 0 | 42 | 1 | 0.6158 | 26.0714 | 4.98 | 79.9516 | Medium | High | Medium | Top | 47 | 97 | 129.8347
STANISLAUS 1701 | 162821701 | CENTRAL VALLEY | YOSEMITE | 45.3745 | 376817.6667 | 43.848 | 19.74% | 69.23% | 1.57% | 0.6919% | 1 | 2 | 72 | 63.97% | 7.656% | 4.91% | 284 | 589 | 0 | 0 | 406 | 54 | 0 | 8 | 34 | 1283 | 23.438 | 218 | 123 | 11 | 531 | 0 | 0 | 72 | 0 | 0.15783 | 21.9018 | 5.9241 | 20.4777 | Low | High | High | Top | 228 | 98 | 129.7481
FRUITLAND 1142 | 192311142 | NORTHERN | HUMBOLDT | 59.9112 | 294852.3333 | 40.6435 | 45.61% | 3.332% | 77.32% | 5.909% | 31 | 0 | 56 | 75.23% | 11.94% | 39.01% | 96 | 72 | 0 | 0 | 690 | 57 | 5 | 13 | 24 | 1156 | 30.0948 | 96 | 41 | 18 | 321 | 0 | 2 | 56 | 1 | 0.52745 | 46.1007 | 2.797 | 68.0119 | Medium | High | Low | Top | 62 | 99 | 128.9442
EAST QUINCY 1101 | 102551101 | NORTHERN | NORTH VALLEY | 3.9217 | 430641 | 42.5194 | 20.26% | 70.89% | 0.07478% | 2.009% | 0 | 0 | 2 | 85.68% | 7.367% | 7.752% | 18 | 88 | 2 | 0 | 11 | 6 | 0 | 1 | 2 | 129 | 37.5532 | 20 | 12 | 2 | 48 | 0 | 0 | 2 | 0 | 0.31432 | 25.4904 | 4.9573 | 39.7179 | Low | High | Medium | Top | 132 | 100 | 126.3633
BUCKS CREEK 1101 | 102211101 | NORTHERN | NORTH VALLEY | 20.005 | 4541.3333 | 43.9709 | 29.47% | 86.51% | 3.485% | 7.184% | 2 | 1 | 11 | 6.119% | 91.51% | 33.06% | 80 | 115 | 2 | 0 | 154 | 38 | 0 | 1 | 11 | 484 | 32.1765 | 9 | 2 | 0 | 23 | 0 | 0 | 11 | 0 | 0.47328 | 26.2124 | 4.8176 | 59.7668 | Medium | High | Medium | Top | 82 | 101 | 126.2809
BERKELEY F 1103 | 012061103 | BAY AREA | EAST BAY | 2.1377 | 1054702.3333 | 44.1026 | 3.803% | 24.57% | 59.11% | 16.33% | 1 | 0 | 5 | 44.5% | 55.5% | 26.92% | 10 | 15 | 0 | 6 | 31 | 5 | 0 | 1 | 2 | 78 | 22.1429 | 8 | 6 | 7 | 28 | 0 | 0 | 5 | 0 | 0.48197 | 17.5559 | 7.1543 | 60.5365 | Medium | High | High | Top | 81 | 102 | 125.6011
WASHINGTON CITY GEN. 1101 | 158041101 | NORTHERN | SIERRA | 0.016194 | 0 | 45 | 0% | 100% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0.51587 | 65.3912 | 1.8983 | 64.0372 | Medium | High | Low | Top | 71 | 103 | 124.1349
BRUNSWICK 1106 | 152481106 | NORTHERN | SIERRA | 174.0097 | 1283831.3333 | 42.2812 | 29.73% | 59.28% | 30.38% | 0.9753% | 19 | 11 | 272 | 78.86% | 12.16% | 11.24% | 375 | 2818 | 19 | 0 | 831 | 434 | 7 | 36 | 61 | 4820 | 39.1351 | 961 | 501 | 36 | 2088 | 0 | 5 | 272 | 0 | 0.26639 | 29.8946 | 4.1467 | 33.0222 | Low | High | Medium | Top | 164 | 104 | 123.9631
SAN RAMON 2107 | 014232107 | CENTRAL COAST | MISSION | 13.9149 | 1508724.3333 | 45.4089 | 13.88% | 0.5199% | 72.21% | 25.32% | 1 | 0 | 34 | 72.18% | 25.87% | 7.011% | 87 | 130 | 1 | 0 | 60 | 14 | 0 | 10 | 12 | 271 | 28.7 | 21 | 19 | 5 | 78 | 0 | 0 | 33 | 0 | 0.38737 | 18.9553 | 6.5285 | 47.9372 | Medium | High | High | Top | 104 | 105 | 123.7494
WOODACRE 1102 | 043021102 | BAY AREA | NORTH BAY | 32.9746 | 735161.3333 | 44.5506 | 29.78% | 3.241% | 26.83% | 45.01% | 20 | 8 | 71 | 24.33% | 50.83% | 6.682% | 321 | 307 | 7 | 22 | 501 | 294 | 8 | 12 | 23 | 1317 | 37.9609 | 115 | 124 | 55 | 413 | 0 | 0 | 71 | 1 | 0.79914 | 13.9926 | 8.807 | 98.4806 | High | High | High | Top | 30 | 106 | 123.2328
PARADISE 1101 | 102831101 | NORTHERN | NORTH VALLEY | 24.3296 | 775325.6667 | 41.9196 | 10.24% | 20.18% | 20.33% | 39.86% | 41 | 1 | 0 | 34.11% | 47.09% | 6.853% | 156 | 411 | 4 | 0 | 387 | 42 | 116 | 0 | 0 | 1109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.65652 | 18.0935 | 6.7536 | 80.2249 | Medium | High | High | Top | 45 | 107 | 122.1965
CAMP EVERS 2106 | 083622106 | CENTRAL COAST | CENTRAL COAST | 130.0354 | 1461187.3333 | 44.2214 | 0% | 0.3016% | 58.29% | 19.37% | 95 | 21 | 247 | 63.6% | 21.78% | 9.994% | 729 | 1439 | 2 | 25 | 884 | 315 | 109 | 62 | 91 | 3292 | 32.3605 | 505 | 316 | 41 | 1321 | 7 | 0 | 245 | 1 | 0.8005 | 17.3477 | 6.977 | 96.8882 | High | High | High | Top | 32 | 108 | 121.0343
LAKEVILLE 1102 | 043371102 | NORTHERN | SONOMA | 22.8278 | 324491 | 44.2947 | 40.97% | 7.7% | 54.72% | 36.61% | 1 | 1 | 10 | 52.92% | 46.12% | 9.091% | 75 | 125 | 0 | 14 | 80 | 59 | 0 | 5 | 5 | 319 | 35.662 | 22 | 15 | 2 | 72 | 0 | 0 | 10 | 0 | 0.41298 | 30.9464 | 3.8583 | 49.3101 | Medium | High | Medium | Top | 100 | 109 | 119.401
CURTIS 1704 | 163351704 | CENTRAL VALLEY | YOSEMITE | 75.7369 | 1032983.3333 | 42.7292 | 0% | 21.67% | 51.52% | 12.63% | 12 | 1 | 89 | 71.24% | 21.97% | 4.389% | 317 | 1069 | 2 | 0 | 384 | 138 | 0 | 17 | 37 | 1914 | 21.6413 | 285 | 172 | 18 | 787 | 0 | 0 | 88 | 0 | 0.29832 | 20.5941 | 5.6887 | 34.9487 | Low | High | High | Top | 150 | 110 | 117.1534
MAPLE CREEK 1101 | 192101101 | NORTHERN | HUMBOLDT | 10.4152 | 110830.6667 | 43.2515 | 127.8% | 20.72% | 61.54% | 11.06% | 6 | 0 | 7 | 74.63% | 18.69% | 44.71% | 44 | 2 | 0 | 2 | 108 | 9 | 16 | 2 | 3 | 170 | 23 | 7 | 3 | 0 | 18 | 0 | 0 | 7 | 1 | 0.59034 | 25.9034 | 4.5175 | 69.0803 | Medium | High | Medium | Top | 59 | 111 | 117.0176
BIG MEADOWS 2101 | 102812101 | NORTHERN | NORTH VALLEY | 63.4393 | 493664.3333 | 43.7034 | 52.57% | 88.47% | 0.6282% | 3.3% | 12 | 0 | 69 | 54.98% | 40.51% | 14.39% | 299 | 560 | 4 | 0 | 423 | 89 | 0 | 14 | 34 | 1724 | 41.9714 | 126 | 72 | 11 | 329 | 0 | 2 | 69 | 0 | 0.3795 | 26.4346 | 4.3997 | 44.1376 | Medium | High | Medium | Top | 113 | 112 | 116.3033
KONOCTI 1102 | 043311102 | NORTHERN | HUMBOLDT | 125.5875 | 939842 | 43.4403 | 68.51% | 28.03% | 51.57% | 14.79% | 47 | 10 | 156 | 65.6% | 30.38% | 11.08% | 490 | 1204 | 0 | 30 | 736 | 313 | 0 | 26 | 59 | 2806 | 38.5626 | 417 | 199 | 44 | 966 | 0 | 7 | 143 | 0 | 0.53781 | 22.8305 | 5.0794 | 62.3678 | Medium | High | Medium | Top | 74 | 113 | 115.9654
HIGHLANDS 1103 | 043361103 | NORTHERN | HUMBOLDT | 114.7409 | 801003 | 44.9955 | 67.57% | 12.43% | 65.75% | 1.789% | 8 | 8 | 115 | 86.52% | 2.564% | 12.58% | 642 | 1074 | 22 | 9 | 354 | 453 | 0 | 15 | 29 | 2249 | 41.8491 | 376 | 182 | 56 | 856 | 0 | 5 | 115 | 0 | 0.11397 | 22.9843 | 5.0074 | 13.1168 | Low | High | Medium | Mid | 289 | 114 | 115.0924
WILLITS 1104 | 042661104 | NORTHERN | HUMBOLDT | 86.9073 | 978692.3333 | 45.1893 | 29.96% | 52.92% | 34.17% | 6.231% | 9 | 1 | 119 | 86.82% | 6.51% | 6.631% | 812 | 1269 | 13 | 10 | 260 | 288 | 15 | 11 | 20 | 2247 | 42.7252 | 287 | 105 | 39 | 881 | 0 | 2 | 118 | 1 | 0.3021 | 37.5818 | 3.0623 | 34.7685 | Low | High | Low | Top | 152 | 115 | 115.0884
HAMILTON BRANCH 1101 | 102361101 | NORTHERN | NORTH VALLEY | 27.1542 | 424216.3333 | 43.8696 | 38.36% | 81.53% | 0% | 3.465% | 8 | 3 | 51 | 76.62% | 16.34% | 3.586% | 196 | 307 | 3 | 0 | 233 | 45 | 0 | 20 | 30 | 725 | 38.2857 | 87 | 66 | 13 | 207 | 0 | 0 | 50 | 0 | 0.35316 | 19.9897 | 5.6969 | 40.217 | Medium | High | High | Top | 128 | 116 | 113.8792
BUCKS CREEK 1103 | 102211103 | NORTHERN | NORTH VALLEY | 10.5199 | 37208 | 42.0381 | 44.83% | 82.75% | 2.62% | 0% | 10 | 0 | 18 | 99.97% | 0% | 10.82% | 12 | 115 | 0 | 0 | 84 | 33 | 41 | 12 | 15 | 342 | 43.6 | 59 | 13 | 3 | 119 | 0 | 1 | 18 | 1 | 0.68568 | 65.0189 | 1.7474 | 77.9036 | High | High | Low | Top | 50 | 117 | 113.6148
CALISTOGA 1101 | 042711101 | BAY AREA | NORTH BAY | 95.7332 | 589307.3333 | 42.0721 | 42.65% | 7.025% | 68.84% | 23.35% | 20 | 8 | 139 | 64.3% | 34.95% | 10.92% | 184 | 690 | 3 | 12 | 541 | 301 | 16 | 36 | 50 | 1895 | 35.0987 | 205 | 115 | 12 | 655 | 0 | 3 | 139 | 1 | 0.70389 | 26.144 | 4.3442 | 79.9442 | High | High | Medium | Top | 48 | 118 | 113.5747
SAN LUIS OBISPO 1101 | 182631101 | CENTRAL COAST | LOS PADRES | 28.243 | 691252 | 41.6046 | 120.7% | 8.695% | 44.57% | 21.48% | 2 | 0 | 24 | 42.08% | 43.85% | 3.893% | 58 | 16 | 2 | 35 | 208 | 82 | 0 | 4 | 8 | 488 | 31.4885 | 43 | 32 | 5 | 138 | 0 | 0 | 24 | 0 | 0.29372 | 25.4113 | 4.4635 | 33.3146 | Low | High | Medium | Top | 158 | 119 | 113.4241
SONOMA 1104 | 042721104 | NORTHERN | SONOMA | 20.5139 | 741589.3333 | 44.6264 | 41.13% | 4.224% | 69.12% | 26.66% | 7 | 0 | 33 | 71.34% | 28.66% | 7.473% | 134 | 208 | 0 | 4 | 94 | 81 | 2 | 9 | 9 | 455 | 35.7857 | 73 | 46 | 8 | 186 | 0 | 1 | 33 | 0 | 0.39279 | 21.5406 | 5.0643 | 42.8485 | Medium | High | Medium | Top | 119 | 120 | 109.0873
PUTAH CREEK 1103 | 063681103 | NORTHERN | SACRAMENTO | 4.0778 | 820485.3333 | 42.8431 | 6.4% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 11.76% | 9 | 17 | 6 | 0 | 9 | 15 | 0 | 0 | 0 | 51 | 34.2727 | 6 | 2 | 0 | 13 | 0 | 0 | 0 | 0 | 0.20705 | 33.5773 | 3.2063 | 22.2902 | Low | High | Low | Top | 211 | 121 | 107.658
GARBERVILLE 1102 | 192221102 | NORTHERN | HUMBOLDT | 127.6889 | 692058.6667 | 40.5965 | 87.09% | 13.66% | 30.68% | 20.71% | 65 | 5 | 140 | 42.93% | 22.78% | 39.63% | 172 | 103 | 0 | 5 | 1525 | 152 | 2 | 28 | 51 | 2339 | 33.5908 | 170 | 82 | 45 | 648 | 0 | 11 | 140 | 1 | 0.66354 | 37.7728 | 2.8479 | 71.3775 | High | High | Low | Top | 56 | 122 | 107.5715
ANITA 1106 | 102841106 | NORTHERN | NORTH VALLEY | 1.7851 | 678856 | 41.5 | 2.269% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 10% | 0 | 4 | 0 | 0 | 3 | 2 | 5 | 0 | 0 | 10 | 33 | 2 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.22299 | 36.1193 | 2.9673 | 23.8997 | Low | High | Low | Top | 204 | 123 | 107.1758
CASTRO VALLEY 1109 | 014091109 | CENTRAL COAST | MISSION | 5.9691 | 477156 | 43.1818 | 28.05% | 0.1603% | 26.28% | 36.61% | 2 | 2 | 14 | 23.73% | 39.29% | 3.788% | 20 | 33 | 0 | 0 | 68 | 7 | 0 | 2 | 4 | 132 | 20.1571 | 17 | 20 | 13 | 75 | 0 | 1 | 14 | 0 | 0.63046 | 16.8148 | 6.3721 | 67.5504 | Medium | High | High | Top | 64 | 124 | 107.1452
CLEAR LAKE 1101 | 042141101 | NORTHERN | HUMBOLDT | 20.6199 | 835264 | 44.0314 | 33.73% | 1.064% | 84.1% | 14.84% | 5 | 0 | 20 | 85.16% | 14.84% | 6.545% | 84 | 127 | 0 | 4 | 134 | 44 | 10 | 1 | 2 | 382 | 38.3719 | 41 | 35 | 5 | 128 | 0 | 0 | 20 | 0 | 0.31052 | 21.5331 | 4.9446 | 33.0616 | Low | High | Medium | Top | 162 | 125 | 106.4727
GARBERVILLE 1101 | 192221101 | NORTHERN | HUMBOLDT | 86.6908 | 480627.3333 | 41.7085 | 34.66% | 19.32% | 55.03% | 0.6503% | 36 | 3 | 108 | 83.68% | 0.7413% | 35.26% | 213 | 106 | 0 | 1 | 810 | 69 | 21 | 25 | 40 | 1520 | 29.0128 | 122 | 65 | 23 | 421 | 0 | 0 | 107 | 1 | 0.5911 | 38.006 | 2.7692 | 62.2114 | Medium | High | Low | Top | 75 | 126 | 105.2467
ANNAPOLIS 1101 | 042861101 | NORTHERN | HUMBOLDT | 51.2424 | 73654.6667 | 43.1562 | 22.7% | 10.09% | 71.98% | 1.626% | 15 | 0 | 49 | 97.83% | 2.115% | 3.201% | 150 | 188 | 0 | 4 | 446 | 34 | 2 | 10 | 16 | 781 | 36.44 | 38 | 11 | 2 | 161 | 0 | 0 | 48 | 1 | 0.55712 | 44.643 | 2.3285 | 57.9138 | Medium | High | Low | Top | 84 | 127 | 103.9519
SANTA ROSA A 1108 | 042151108 | NORTHERN | SONOMA | 0.13621 | 1285152.6667 | 42.5 | 21.79% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 228 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.13174 | 26.5534 | 3.9118 | 13.6844 | Low | High | Medium | Mid | 281 | 128 | 103.8719
SARATOGA 1107 | 083371107 | CENTRAL COAST | DE ANZA | 33.4836 | 875523.3333 | 43.8562 | 23.19% | 1.918% | 71.25% | 22.52% | 28 | 7 | 85 | 70.63% | 25.15% | 7.91% | 173 | 280 | 2 | 10 | 361 | 68 | 5 | 30 | 40 | 885 | 4.1008 | 104 | 117 | 41 | 373 | 0 | 1 | 85 | 1 | 0.71571 | 16.8903 | 6.0226 | 72.8047 | High | High | High | Top | 53 | 129 | 101.7235
ALTO 1125 | 042031125 | BAY AREA | NORTH BAY | 37.5324 | 671150 | 43.3888 | 20.73% | 17.34% | 22% | 51.19% | 47 | 13 | 90 | 18.53% | 72.43% | 7.861% | 237 | 417 | 15 | 9 | 435 | 245 | 65 | 16 | 40 | 1323 | 29.7205 | 127 | 139 | 48 | 438 | 0 | 2 | 90 | 1 | 0.84635 | 13.5659 | 7.4405 | 85.4285 | High | High | High | Top | 39 | 130 | 100.9377
MIRABEL 1102 | 042091102 | NORTHERN | SONOMA | 37.7507 | 657529.3333 | 43.2312 | 21.57% | 4.553% | 39.93% | 39.36% | 28 | 17 | 70 | 39.85% | 45.53% | 6.683% | 252 | 413 | 1 | 6 | 399 | 179 | 51 | 17 | 26 | 1212 | 36.788 | 120 | 90 | 37 | 374 | 0 | 0 | 70 | 1 | 0.90476 | 19.1361 | 5.195 | 89.9435 | High | High | Medium | Top | 37 | 131 | 99.4115
FORT SEWARD 1121 | 192321121 | NORTHERN | HUMBOLDT | 39.059 | 73000 | 39.7697 | 75.37% | 49.12% | 29.4% | 0% | 6 | 3 | 20 | 100% | 0% | 34.85% | 35 | 12 | 0 | 0 | 287 | 53 | 0 | 8 | 13 | 614 | 35.6535 | 34 | 11 | 4 | 134 | 0 | 1 | 20 | 0 | 0.43329 | 38.5389 | 2.5731 | 42.9664 | Medium | High | Low | Top | 117 | 132 | 99.1637
KING CITY 1103 | 182031103 | CENTRAL COAST | CENTRAL COAST | 17.6652 | 567182 | 40.3876 | 20.41% | 0.04509% | 99.95% | 0% | 0 | 0 | 21 | 99.95% | 0% | 6.95% | 12 | 105 | 0 | 2 | 76 | 19 | 0 | 3 | 3 | 259 | 14.3854 | 44 | 8 | 0 | 105 | 0 | 0 | 21 | 0 | 0.12954 | 25.8045 | 3.8377 | 12.8287 | Low | High | Medium | Mid | 293 | 133 | 99.0299
GOLDTREE 1105 | 182581105 | CENTRAL COAST | LOS PADRES | 7.1045 | 856916.3333 | 42.3504 | 118% | 0% | 33.32% | 40.83% | 0 | 0 | 8 | 33.32% | 40.83% | 2.564% | 8 | 1 | 0 | 15 | 55 | 12 | 0 | 2 | 5 | 117 | 19.4286 | 5 | 2 | 0 | 18 | 0 | 0 | 8 | 0 | 0.45177 | 20.1837 | 4.9002 | 44.6824 | Medium | High | Medium | Top | 109 | 134 | 98.9051
PETALUMA C 1108 | 042631108 | NORTHERN | SONOMA | 74.2809 | 1293574.3333 | 42.6589 | 32.65% | 0.1844% | 49.58% | 46.86% | 21 | 3 | 121 | 29.01% | 68.63% | 5.274% | 290 | 785 | 0 | 4 | 529 | 214 | 34 | 21 | 37 | 1858 | 26.6996 | 194 | 63 | 6 | 495 | 0 | 0 | 121 | 0 | 0.6193 | 33.2388 | 2.9732 | 61.2016 | Medium | High | Low | Top | 78 | 135 | 98.8243
SCE TEHACHAPI 1101 | 258131101 | CENTRAL VALLEY | KERN | 1.4276 | 3303.3333 | 0 | 0% | 0% | 56.93% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.26781 | 26.8233 | 3.6719 | 26.3773 | Low | High | Low | Top | 182 | 136 | 98.4917
PLACERVILLE 2106 | 153082106 | NORTHERN | SIERRA | 276.5055 | 1392202.6667 | 42.4766 | 31.57% | 50.23% | 36.82% | 4.119% | 37 | 4 | 406 | 79.07% | 12.22% | 4.603% | 563 | 3741 | 123 | 4 | 940 | 630 | 19 | 55 | 104 | 6822 | 40.202 | 1185 | 542 | 59 | 2553 | 0 | 9 | 406 | 0 | 0.25289 | 25.2136 | 3.8202 | 24.358 | Low | High | Medium | Top | 198 | 137 | 96.3205
CAYUCOS 1102 | 182551102 | CENTRAL COAST | LOS PADRES | 14.9742 | 532008.6667 | 41.8956 | 10.74% | 13.99% | 50.24% | 23.97% | 3 | 0 | 6 | 76.03% | 23.97% | 10.38% | 24 | 2 | 0 | 8 | 85 | 29 | 0 | 3 | 3 | 183 | 32.4231 | 20 | 2 | 1 | 54 | 0 | 0 | 6 | 0 | 0.43451 | 22.5077 | 4.2742 | 41.8006 | Medium | High | Medium | Top | 121 | 138 | 96.2022
SCE REFUGIO 1101 | 188071101 | CENTRAL COAST | LOS PADRES | 0.29161 | 0 | 0 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0.23266 | 47.7737 | 1.9745 | 21.9458 | Low | High | Low | Top | 216 | 139 | 94.3271
WYANDOTTE 1106 | 102911106 | NORTHERN | NORTH VALLEY | 2.1424 | 1331297.3333 | 45.8333 | 3.022% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 2 | 3 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 18 | 47.5 | 5 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 0.24462 | 18.9456 | 4.9601 | 22.9876 | Low | High | Medium | Top | 207 | 140 | 93.9729
TASSAJARA 2112 | 014662112 | BAY AREA | DIABLO | 10.8205 | 1218166.3333 | 44.3694 | 34.53% | 38.7% | 14.54% | 23.77% | 1 | 0 | 28 | 14.54% | 62.47% | 14.35% | 64 | 84 | 0 | 0 | 63 | 18 | 0 | 18 | 26 | 223 | 51.5753 | 17 | 29 | 15 | 81 | 0 | 0 | 28 | 1 | 0.71198 | 14.5909 | 6.4193 | 66.687 | High | High | High | Top | 70 | 141 | 93.6636
CALISTOGA 1102 | 042711102 | BAY AREA | NORTH BAY | 25.8439 | 1209225.6667 | 42.9894 | 78.86% | 1.451% | 64.1% | 21.01% | 9 | 0 | 33 | 64.28% | 31.22% | 7.544% | 94 | 224 | 3 | 5 | 127 | 122 | 0 | 17 | 21 | 570 | 37.8608 | 50 | 46 | 11 | 207 | 0 | 0 | 33 | 1 | 0.54883 | 17.2654 | 5.3093 | 50.3095 | Medium | High | Medium | Top | 98 | 142 | 91.6664
PUEBLO 1104 | 043291104 | BAY AREA | NORTH BAY | 31.2032 | 723874 | 41.893 | 33.25% | 1.253% | 57.25% | 39.6% | 5 | 0 | 36 | 46.1% | 52% | 8.453% | 44 | 266 | 0 | 15 | 157 | 97 | 8 | 11 | 13 | 627 | 42.2246 | 78 | 41 | 5 | 190 | 0 | 1 | 36 | 0 | 0.48292 | 18.8717 | 4.8451 | 44.1556 | Medium | High | Medium | Top | 112 | 143 | 91.4353
CAMP EVERS 2104 | 083622104 | CENTRAL COAST | CENTRAL COAST | 28.9403 | 1715943.6667 | 44.8958 | 16.2% | 1.513% | 64.32% | 25.03% | 20 | 9 | 33 | 59.21% | 31.79% | 6.935% | 202 | 337 | 0 | 16 | 172 | 58 | 11 | 14 | 22 | 721 | 46.0478 | 111 | 64 | 9 | 302 | 2 | 0 | 33 | 1 | 0.74064 | 12.2665 | 7.4164 | 67.3779 | High | High | High | Top | 66 | 144 | 90.9728
GLENN 1101 | 102601101 | NORTHERN | NORTH VALLEY | 2.3498 | 784294 | 37 | 7.384% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 1 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 5 | 11.5 | 2 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0.16613 | 47.6367 | 1.9073 | 15.0944 | Low | High | Low | Top | 268 | 145 | 90.8597
FRUITLAND 1141 | 192311141 | NORTHERN | HUMBOLDT | 25.2358 | 143637.6667 | 40.4961 | 69.09% | 1.516% | 24.99% | 17.04% | 13 | 0 | 30 | 25.8% | 17.75% | 31.09% | 35 | 19 | 0 | 0 | 377 | 15 | 15 | 7 | 19 | 521 | 20.6947 | 27 | 15 | 12 | 102 | 0 | 1 | 30 | 1 | 0.71072 | 43.5287 | 2.057 | 63.6351 | High | High | Low | Top | 72 | 146 | 89.5367
CAYETANO 2111 | 014422111 | CENTRAL COAST | MISSION | 5.6926 | 1694873 | 42.1084 | 18.37% | 1.868% | 58.97% | 39.17% | 0 | 0 | 1 | 27.84% | 72.16% | 9.639% | 0 | 20 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 83 | 24.1481 | 15 | 2 | 0 | 31 | 0 | 0 | 1 | 0 | 0.32508 | 16.3151 | 5.4631 | 28.9751 | Low | High | High | Top | 172 | 147 | 89.1313
CABRILLO 1103 | 183101103 | CENTRAL COAST | LOS PADRES | 61.5614 | 439667.3333 | 41.4516 | 44.87% | 9.704% | 52.79% | 21.84% | 1 | 1 | 50 | 56.48% | 31.3% | 2.335% | 55 | 87 | 2 | 184 | 307 | 160 | 0 | 4 | 7 | 1028 | 24.3281 | 66 | 34 | 4 | 275 | 0 | 0 | 49 | 0 | 0.19035 | 15.1342 | 5.7894 | 16.6782 | Low | High | High | Top | 251 | 148 | 87.6175
MILPITAS 1108 | 082831108 | CENTRAL COAST | SAN JOSE | 0.28331 | 934813.6667 | 40 | 0% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 44 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.13615 | 26.5534 | 3.2974 | 11.9212 | Low | High | Low | Mid | 303 | 149 | 87.557
WOODSIDE 1104 | 024251104 | CENTRAL COAST | PENINSULA | 14.8672 | 883355.3333 | 42.9964 | 25.38% | 1.23% | 67.34% | 22.58% | 9 | 4 | 39 | 69.83% | 23.26% | 8.587% | 60 | 189 | 0 | 1 | 294 | 20 | 0 | 7 | 11 | 559 | 17.3192 | 65 | 71 | 25 | 217 | 0 | 0 | 39 | 1 | 0.65918 | 9.7107 | 8.9719 | 57.4295 | Medium | Medium | High | Top | 85 | 150 | 87.1233
PENNGROVE 1101 | 043471101 | NORTHERN | SONOMA | 20.4175 | 939644.6667 | 44.6137 | 21.7% | 1.682% | 78.69% | 19.63% | 5 | 3 | 26 | 80.37% | 19.63% | 4.846% | 136 | 247 | 0 | 7 | 71 | 66 | 0 | 8 | 8 | 454 | 27.598 | 80 | 33 | 4 | 204 | 0 | 2 | 26 | 0 | 0.30952 | 23.2872 | 3.7267 | 26.8613 | Low | High | Low | Top | 180 | 151 | 86.7834
VOLTA 1102 | 102541102 | NORTHERN | NORTH VALLEY | 128.9875 | 581294.6667 | 39.3776 | 0% | 95.94% | 1.1% | 0.03167% | 13 | 2 | 187 | 97.04% | 0.03167% | 6.354% | 66 | 1996 | 69 | 0 | 514 | 202 | 41 | 34 | 66 | 3352 | 39.5782 | 438 | 168 | 8 | 1116 | 0 | 10 | 187 | 0 | 0.15947 | 30.8605 | 2.8037 | 13.7976 | Low | High | Low | Mid | 280 | 152 | 86.5226
MENLO 1103 | 024131103 | CENTRAL COAST | PENINSULA | 40.483 | 542020.6667 | 41.4118 | 30.72% | 0.6489% | 60.17% | 13.68% | 34 | 3 | 58 | 52.2% | 47.8% | 7.451% | 56 | 378 | 1 | 9 | 267 | 34 | 20 | 11 | 21 | 765 | 20.4041 | 79 | 30 | 2 | 200 | 0 | 0 | 58 | 0 | 0.59311 | 18.4464 | 4.6883 | 51.2938 | Medium | High | Medium | Top | 97 | 153 | 86.4832
BELLEVUE 2103 | 043182103 | NORTHERN | SONOMA | 32.2764 | 1226044.6667 | 44.2334 | 22.47% | 0.4413% | 81.51% | 6.989% | 2 | 2 | 54 | 80.16% | 8.974% | 7.491% | 157 | 397 | 0 | 15 | 67 | 70 | 7 | 10 | 12 | 574 | 36.5889 | 112 | 78 | 9 | 272 | 0 | 0 | 54 | 0 | 0.17484 | 23.3201 | 3.7084 | 15.1202 | Low | High | Low | Top | 267 | 154 | 86.4804
OAKLAND K 1102 | 012101102 | BAY AREA | EAST BAY | 15.6371 | 511025 | 46.4153 | 34.6% | 0% | 37.32% | 19.08% | 13 | 1 | 40 | 18.81% | 47.36% | 23.61% | 159 | 113 | 0 | 1 | 191 | 52 | 36 | 26 | 45 | 487 | 18.3043 | 31 | 80 | 28 | 170 | 0 | 0 | 39 | 0 | 0.64899 | 13.1282 | 6.5755 | 56.0234 | Medium | High | High | Top | 86 | 155 | 86.3243
FOOTHILL 1101 | 182951101 | CENTRAL COAST | LOS PADRES | 19.8573 | 161535.3333 | 41.6914 | 10.46% | 0% | 50.37% | 40.15% | 4 | 0 | 12 | 50.37% | 40.15% | 7.09% | 36 | 27 | 0 | 106 | 141 | 35 | 0 | 2 | 4 | 409 | 28.3333 | 40 | 9 | 4 | 103 | 0 | 0 | 12 | 1 | 0.64347 | 14.7358 | 5.7639 | 54.6534 | Medium | High | High | Top | 89 | 156 | 84.935
HALF MOON BAY 1103 | 024101103 | CENTRAL COAST | PENINSULA | 144.5672 | 1311801 | 41.2361 | 45.7% | 2.707% | 43.84% | 28.56% | 62 | 6 | 181 | 35.72% | 60.32% | 5.516% | 117 | 1383 | 1 | 10 | 1225 | 127 | 30 | 29 | 58 | 2973 | 24.4918 | 228 | 144 | 26 | 780 | 1 | 0 | 181 | 1 | 0.82543 | 15.2282 | 5.5362 | 69.5888 | High | High | High | Top | 57 | 157 | 84.3065
SANTA YNEZ 1101 | 182721101 | CENTRAL COAST | LOS PADRES | 34.6124 | 1199568 | 41.3793 | 113.2% | 4.532% | 74.18% | 5.897% | 1 | 0 | 27 | 78.16% | 11.69% | 3.058% | 56 | 43 | 0 | 46 | 204 | 77 | 0 | 14 | 18 | 556 | 22.3465 | 18 | 14 | 4 | 109 | 0 | 1 | 27 | 0 | 0.14889 | 33.8357 | 2.4884 | 12.5359 | Low | High | Low | Mid | 297 | 158 | 84.196
CLARKSVILLE 2104 | 153612104 | NORTHERN | SIERRA | 68.1625 | 1494335.3333 | 44.0434 | 54.18% | 0.3882% | 90.3% | 0% | 3 | 4 | 74 | 90.79% | 0% | 0.7107% | 248 | 843 | 29 | 0 | 134 | 90 | 0 | 13 | 25 | 1407 | 48.5196 | 223 | 237 | 19 | 557 | 0 | 0 | 74 | 0 | 0.052517 | 15.9304 | 5.2704 | 4.4093 | Low | High | Medium | Mid | 458 | 159 | 83.9591
RINCON 1101 | 043321101 | NORTHERN | SONOMA | 22.5067 | 856789 | 43.9057 | 46.18% | 0% | 89.1% | 5.069% | 0 | 1 | 27 | 89.1% | 5.069% | 6.767% | 59 | 138 | 0 | 0 | 69 | 32 | 0 | 7 | 9 | 266 | 33.1448 | 64 | 31 | 10 | 151 | 0 | 0 | 27 | 1 | 0.20622 | 20.328 | 4.0865 | 17.1307 | Low | High | Medium | Top | 247 | 160 | 83.07
OAKHURST 1103 | 254421103 | CENTRAL VALLEY | YOSEMITE | 129.2156 | 1392881.3333 | 40.0855 | 0% | 65.77% | 17.19% | 0.3504% | 32 | 2 | 190 | 75.05% | 11.4% | 23.1% | 122 | 546 | 0 | 0 | 1391 | 265 | 17 | 39 | 67 | 3299 | 26.6074 | 469 | 314 | 46 | 1404 | 0 | 3 | 186 | 0 | 0.27031 | 21.771 | 3.734 | 21.9744 | Low | High | Low | Top | 215 | 161 | 81.2928
VACA DIXON 1101 | 063591101 | NORTHERN | SACRAMENTO | 0.95938 | 1369157.6667 | 44.7222 | 0.7454% | 40.21% | 59.79% | 0% | 0 | 0 | 3 | 100% | 0% | 5.556% | 5 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 18 | 17.2 | 4 | 1 | 0 | 7 | 0 | 0 | 3 | 0 | 0.23531 | 20.3765 | 3.9802 | 19.084 | Low | High | Medium | Top | 238 | 162 | 81.1016
NORTH DUBLIN 2103 | 014052103 | CENTRAL COAST | MISSION | 19.5175 | 1418542.3333 | 43.3628 | 87.41% | 1.211% | 48.44% | 39.07% | 0 | 1 | 28 | 40% | 50.81% | 7.375% | 16 | 198 | 0 | 4 | 69 | 11 | 0 | 13 | 15 | 339 | 46.9619 | 23 | 46 | 10 | 114 | 0 | 0 | 28 | 0 | 0.50016 | 12.8108 | 6.3181 | 40.4827 | Medium | High | High | Top | 127 | 163 | 80.9395
SANTA MARIA 1108 | 182671108 | CENTRAL COAST | LOS PADRES | 73.6335 | 1175161.3333 | 40.9195 | 35.85% | 2.43% | 93.3% | 0.2728% | 5 | 0 | 53 | 97.28% | 1.23% | 11.01% | 64 | 139 | 0 | 125 | 483 | 97 | 0 | 8 | 13 | 1054 | 27.4301 | 96 | 32 | 8 | 307 | 0 | 0 | 53 | 0 | 0.15542 | 30.8224 | 2.6213 | 12.5573 | Low | High | Low | Mid | 296 | 164 | 80.7943
FOOTHILL 1102 | 182951102 | CENTRAL COAST | LOS PADRES | 11.5966 | 1015329 | 42.2917 | 51.79% | 0% | 53.14% | 5.519% | 4 | 0 | 16 | 53.14% | 14.94% | 17.13% | 22 | 12 | 0 | 11 | 122 | 23 | 0 | 3 | 9 | 216 | 33.3898 | 23 | 4 | 2 | 62 | 0 | 0 | 16 | 0 | 0.41901 | 14.7557 | 5.3882 | 33.314 | Medium | High | High | Top | 159 | 165 | 79.507
LAYTONVILLE 1102 | 042681102 | NORTHERN | HUMBOLDT | 114.8069 | 241083.3333 | 41.8251 | 15.8% | 43.57% | 44.21% | 0.2741% | 11 | 3 | 101 | 95.61% | 0.4488% | 7.915% | 202 | 449 | 1 | 12 | 564 | 267 | 0 | 20 | 33 | 1794 | 33.0655 | 129 | 41 | 15 | 463 | 0 | 1 | 101 | 0 | 0.27405 | 46.6879 | 1.6916 | 21.6439 | Low | High | Low | Top | 218 | 166 | 78.9784
PHILO 1102 | 042601102 | NORTHERN | HUMBOLDT | 91.607 | 267821 | 42.0276 | 52.79% | 3.105% | 86.33% | 8.621% | 26 | 2 | 82 | 81.49% | 18.04% | 8.598% | 158 | 498 | 0 | 28 | 330 | 112 | 0 | 11 | 15 | 1419 | 38.444 | 190 | 54 | 13 | 533 | 0 | 5 | 81 | 0 | 0.27998 | 31.5923 | 2.4968 | 22.0846 | Low | High | Low | Top | 213 | 167 | 78.8787
WILLITS 1103 | 042661103 | NORTHERN | HUMBOLDT | 145.158 | 627725.6667 | 43.3384 | 22.62% | 33.33% | 60.18% | 4.309% | 22 | 1 | 155 | 88.19% | 9.633% | 10.87% | 563 | 1124 | 4 | 39 | 761 | 357 | 21 | 36 | 52 | 2961 | 38.7011 | 389 | 132 | 33 | 1035 | 0 | 7 | 154 | 0 | 0.23888 | 34.3856 | 2.2905 | 18.8143 | Low | High | Low | Top | 241 | 168 | 78.7604
MOLINO 1101 | 042571101 | NORTHERN | SONOMA | 34.3752 | 1326137.6667 | 43.9088 | 17.04% | 0.03488% | 68.7% | 29.48% | 6 | 0 | 88 | 64% | 34.21% | 6.519% | 190 | 472 | 0 | 13 | 198 | 64 | 13 | 6 | 9 | 813 | 35.8114 | 172 | 78 | 20 | 391 | 0 | 0 | 88 | 1 | 0.4493 | 19.5174 | 4.0205 | 35.257 | Medium | High | Medium | Top | 144 | 169 | 78.4703
MORGAN HILL 2111 | 083242111 | CENTRAL COAST | SAN JOSE | 51.8726 | 1641880 | 42.2732 | 50.3% | 7.74% | 72.11% | 10.01% | 11 | 0 | 88 | 79.43% | 13.6% | 7.361% | 143 | 415 | 1 | 23 | 325 | 54 | 0 | 6 | 16 | 951 | 17.2821 | 89 | 63 | 7 | 323 | 0 | 0 | 86 | 0 | 0.20331 | 18.1806 | 4.2576 | 15.7369 | Low | High | Medium | Top | 260 | 170 | 77.4054
FULTON 1107 | 042561107 | NORTHERN | SONOMA | 38.1815 | 1355819.3333 | 43.9477 | 44.27% | 0.1011% | 63.83% | 27.3% | 6 | 3 | 51 | 66.33% | 27.73% | 8.235% | 186 | 378 | 0 | 6 | 209 | 95 | 15 | 8 | 18 | 765 | 34.733 | 140 | 74 | 14 | 373 | 0 | 2 | 49 | 1 | 0.45784 | 16.6839 | 4.5961 | 35.1072 | Medium | High | Medium | Top | 146 | 171 | 76.6806
PETALUMA C 1109 | 042631109 | NORTHERN | SONOMA | 50.3206 | 989739.3333 | 44.5784 | 45.21% | 0.3492% | 59.26% | 26.88% | 6 | 0 | 75 | 49.58% | 37.91% | 3.507% | 211 | 458 | 0 | 1 | 207 | 113 | 0 | 11 | 19 | 941 | 22.7729 | 75 | 36 | 5 | 241 | 0 | 1 | 74 | 0 | 0.34315 | 21.485 | 3.5633 | 26.2708 | Medium | High | Low | Top | 183 | 172 | 76.5572
PUEBLO 1105 | 043291105 | BAY AREA | NORTH BAY | 26.5646 | 658552.3333 | 43.1205 | 54% | 0% | 82.91% | 17.08% | 4 | 0 | 25 | 76.18% | 23.81% | 16.87% | 53 | 145 | 0 | 5 | 91 | 129 | 0 | 11 | 14 | 415 | 34.4031 | 38 | 24 | 10 | 133 | 0 | 0 | 25 | 1 | 0.51355 | 17.3535 | 4.39 | 39.1225 | Medium | High | Medium | Top | 135 | 173 | 76.1812
CLAYTON 2215 | 012022215 | BAY AREA | DIABLO | 8.9607 | 1585359 | 44.6471 | 0% | 2.854% | 11.4% | 24.63% | 3 | 0 | 7 | 11.4% | 30.35% | 14.71% | 33 | 86 | 0 | 0 | 21 | 6 | 0 | 3 | 5 | 170 | 48.475 | 10 | 16 | 4 | 46 | 0 | 0 | 7 | 0 | 0.62031 | 11.0942 | 6.8386 | 47.0622 | Medium | Medium | High | Top | 106 | 174 | 75.869
PASO ROBLES 1107 | 182611107 | CENTRAL COAST | LOS PADRES | 0.27858 | 948215.3333 | 38.3333 | 9.404% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 16.67% | 0 | 0 | 0 | 2 | 2 | 2 | 0 | 0 | 0 | 6 | 34.5 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.16605 | 24.9252 | 3.038 | 12.5737 | Low | High | Low | Mid | 295 | 175 | 75.7226
LOW GAP 1101 | 192411101 | NORTHERN | HUMBOLDT | 71.107 | 138249.3333 | 39.9325 | 36.89% | 72.24% | 13.89% | 0% | 12 | 0 | 87 | 99.7% | 0% | 32.86% | 76 | 192 | 0 | 8 | 1002 | 111 | 0 | 15 | 27 | 1564 | 21.3201 | 112 | 28 | 14 | 423 | 0 | 0 | 87 | 0 | 0.31922 | 37.7486 | 1.9831 | 23.8968 | Low | High | Low | Top | 205 | 176 | 74.8605
COTATI 1103 | 042271103 | NORTHERN | SONOMA | 85.8821 | 571225.3333 | 42.0299 | 100.3% | 0.8466% | 42.44% | 45.86% | 21 | 2 | 107 | 22.08% | 72.47% | 4.327% | 212 | 753 | 0 | 5 | 507 | 201 | 35 | 18 | 39 | 1710 | 31.7867 | 138 | 60 | 9 | 384 | 0 | 1 | 107 | 0 | 0.59061 | 24.6428 | 3.0163 | 43.8998 | Medium | High | Low | Top | 115 | 177 | 74.3298
CAYUCOS 1101 | 182551101 | CENTRAL COAST | LOS PADRES | 2.5426 | 221217 | 38.9655 | 9.713% | 0% | 26.38% | 68.26% | 0 | 0 | 1 | 26.38% | 71.91% | 3.448% | 0 | 14 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 29 | 116.6 | 4 | 2 | 0 | 10 | 0 | 0 | 1 | 1 | 0.38046 | 22.1068 | 3.317 | 27.8987 | Medium | High | Low | Top | 177 | 178 | 73.3284
MENDOCINO 1101 | 042951101 | NORTHERN | HUMBOLDT | 44.2375 | 553806.6667 | 42.8664 | 30.44% | 22.23% | 66.86% | 7.339% | 5 | 1 | 41 | 89.5% | 7.339% | 8.363% | 116 | 381 | 0 | 8 | 181 | 140 | 0 | 5 | 10 | 849 | 38.7038 | 147 | 41 | 8 | 374 | 0 | 0 | 41 | 0 | 0.1357 | 26.2844 | 2.7636 | 9.8572 | Low | High | Low | Mid | 333 | 179 | 72.6401
BURNS 2101 | 183582101 | CENTRAL COAST | CENTRAL COAST | 1.6694 | 0 | 43.8662 | 34.99% | 1.805% | 42.28% | 25.56% | 35 | 3 | 104 | 37.72% | 51.73% | 9.719% | 239 | 376 | 0 | 9 | 458 | 156 | 46 | 34 | 52 | 1317 | 32.416 | 188 | 99 | 14 | 522 | 4 | 0 | 103 | 1 | 0.854 | 10.0722 | 7.1684 | 61.6602 | High | Medium | High | Top | 77 | 180 | 72.2019
BURNS 2101 | 183582101 | CENTRAL COAST | CENTRAL COAST | 1.6694 | 0 | 43.5294 | 0% | 0% | 8.944% | 22.02% | 2 | 0 | 3 | 25.87% | 24.07% | 5.556% | 8 | 8 | 0 | 0 | 19 | 3 | 0 | 3 | 4 | 36 | 32.0714 | 6 | 2 | 0 | 14 | 1 | 0 | 3 | 1 | 0.60685 | 10.0722 | 7.1684 | 43.8155 | Medium | Medium | High | Top | 116 | 180 | 72.2019
CAMP EVERS 2105 | 083622105 | CENTRAL COAST | CENTRAL COAST | 89.301 | 917398.3333 | 44.0145 | 0% | 0.564% | 53.59% | 22.8% | 92 | 33 | 210 | 54.81% | 27.43% | 7.444% | 490 | 816 | 0 | 26 | 1049 | 203 | 115 | 65 | 95 | 2633 | 36.9282 | 333 | 262 | 50 | 990 | 14 | 0 | 209 | 1 | 0.84514 | 8.9754 | 8.0024 | 60.7015 | High | Medium | High | Top | 80 | 182 | 71.8241
BRUNSWICK 1107 | 152481107 | NORTHERN | SIERRA | 8.871 | 757448.3333 | 41.9088 | 11.04% | 38.53% | 51.17% | 2.63% | 2 | 0 | 31 | 46.46% | 46.65% | 12.82% | 34 | 171 | 3 | 0 | 88 | 26 | 11 | 7 | 10 | 351 | 38.2028 | 35 | 50 | 12 | 147 | 0 | 0 | 31 | 1 | 0.63707 | 14.2839 | 5.0141 | 45.6282 | Medium | High | Medium | Top | 107 | 183 | 71.6216
WILLOW CREEK 1102 | 192171102 | NORTHERN | HUMBOLDT | 9.6275 | 37994.3333 | 44.2767 | 16.2% | 8.232% | 31.81% | 0.04622% | 2 | 0 | 21 | 99.31% | 0.1192% | 57.14% | 41 | 6 | 0 | 0 | 105 | 6 | 0 | 3 | 6 | 161 | 33.76 | 16 | 14 | 2 | 51 | 0 | 0 | 21 | 1 | 0.53644 | 41.1814 | 1.7321 | 38.2656 | Medium | High | Low | Top | 136 | 184 | 71.3323
GEYSERVILLE 1101 | 042891101 | NORTHERN | SONOMA | 76.3146 | 772005 | 43.9944 | 16.55% | 1.539% | 82.14% | 13.09% | 6 | 1 | 50 | 84.22% | 13.09% | 11.53% | 185 | 498 | 0 | 19 | 90 | 179 | 35 | 15 | 19 | 902 | 29.6115 | 104 | 43 | 10 | 289 | 0 | 0 | 50 | 0 | 0.28882 | 21.875 | 3.2553 | 20.5671 | Low | High | Low | Top | 226 | 185 | 71.2095
TULUCAY 1101 | 042301101 | BAY AREA | NORTH BAY | 5.2142 | 1477437 | 42.2222 | 8.963% | 0% | 30.47% | 69.45% | 0 | 1 | 3 | 30.47% | 69.45% | 8.333% | 4 | 12 | 0 | 0 | 9 | 5 | 12 | 1 | 3 | 36 | 4.5556 | 2 | 2 | 0 | 10 | 0 | 0 | 3 | 0 | 0.47375 | 16.6451 | 4.2652 | 33.6344 | Medium | High | Medium | Top | 157 | 186 | 70.9956
SAN LUIS OBISPO 1104 | 182631104 | CENTRAL COAST | LOS PADRES | 55.0451 | 846517.6667 | 42.6227 | 45.22% | 5.14% | 64.99% | 25.28% | 14 | 0 | 78 | 58.52% | 37.71% | 3.181% | 111 | 193 | 1 | 79 | 245 | 56 | 0 | 13 | 21 | 943 | 31.6207 | 62 | 33 | 10 | 248 | 0 | 1 | 78 | 0 | 0.46928 | 15.2773 | 4.6252 | 33.1594 | Medium | High | Medium | Top | 161 | 187 | 70.6602
SUNOL 1101 | 014241101 | CENTRAL COAST | MISSION | 38.3328 | 675538 | 44.5115 | 69.23% | 3.622% | 60.17% | 13.02% | 11 | 4 | 44 | 41.1% | 39.98% | 9.909% | 133 | 283 | 7 | 7 | 178 | 41 | 0 | 9 | 16 | 656 | 10.6432 | 59 | 56 | 5 | 199 | 0 | 2 | 44 | 0 | 0.48925 | 13.785 | 5.0808 | 34.2669 | Medium | High | Medium | Top | 154 | 188 | 70.0393
RACETRACK 1704 | 163761704 | CENTRAL VALLEY | YOSEMITE | 45.5677 | 180126 | 43.3317 | 45.93% | 2.308% | 56.44% | 28.44% | 3 | 3 | 43 | 38.93% | 50.17% | 3.149% | 164 | 521 | 0 | 0 | 225 | 97 | 6 | 7 | 12 | 1048 | 27.5783 | 152 | 67 | 6 | 376 | 0 | 0 | 43 | 0 | 0.30415 | 14.732 | 4.7463 | 21.2671 | Low | High | Medium | Top | 222 | 189 | 69.9224
LAURELES 1111 | 182371111 | CENTRAL COAST | CENTRAL COAST | 105.5941 | 313728.3333 | 40.507 | 34.76% | 21.84% | 71.69% | 2.14% | 20 | 2 | 111 | 80.39% | 18.12% | 12.52% | 153 | 729 | 0 | 88 | 537 | 150 | 0 | 15 | 20 | 1789 | 14.9403 | 171 | 83 | 18 | 617 | 0 | 0 | 111 | 0 | 0.23895 | 22.8849 | 3.0551 | 16.7061 | Low | High | Low | Top | 250 | 190 | 69.9159
CABRILLO 1104 | 183101104 | CENTRAL COAST | LOS PADRES | 34.4425 | 615165 | 41.762 | 48.45% | 9.532% | 25.85% | 30.82% | 9 | 2 | 21 | 30.75% | 45% | 2.762% | 65 | 34 | 0 | 69 | 236 | 59 | 20 | 2 | 8 | 543 | 23.41 | 36 | 8 | 1 | 113 | 0 | 0 | 20 | 0 | 0.59436 | 11.348 | 6.1259 | 41.3185 | Medium | Medium | High | Top | 124 | 191 | 69.517
BIG BASIN 1101 | 082841101 | CENTRAL COAST | CENTRAL COAST | 56.1051 | 568121.3333 | 43.4029 | 18.97% | 0.5049% | 47.45% | 28.29% | 74 | 13 | 128 | 51.44% | 33.93% | 9.023% | 226 | 384 | 0 | 18 | 730 | 186 | 94 | 25 | 42 | 1751 | 24.8837 | 217 | 183 | 38 | 667 | 3 | 0 | 128 | 1 | 0.89531 | 9.9669 | 6.9512 | 62.0292 | High | Medium | High | Top | 76 | 192 | 69.282
NORTH DUBLIN 2101 | 014052101 | CENTRAL COAST | MISSION | 3.8203 | 1705733.6667 | 54.8485 | 111.3% | 0.4186% | 4.003% | 0.4585% | 0 | 0 | 2 | 4.422% | 0.4585% | 34.34% | 93 | 4 | 0 | 0 | 16 | 4 | 0 | 3 | 5 | 99 | 75.2 | 3 | 1 | 1 | 5 | 0 | 0 | 2 | 1 | 0.50495 | 10.8414 | 6.3623 | 34.8295 | Medium | Medium | High | Top | 151 | 193 | 68.9766
RESEARCH 2102 | 014692102 | BAY AREA | DIABLO | 1.8257 | 1648770 | 44.918 | 11.42% | 0% | 24.38% | 75.46% | 1 | 0 | 9 | 24.38% | 75.46% | 11.29% | 18 | 15 | 0 | 0 | 25 | 1 | 0 | 3 | 3 | 62 | 50.0303 | 9 | 17 | 2 | 33 | 0 | 0 | 9 | 0 | 0.57996 | 11.4244 | 5.9634 | 39.5118 | Medium | Medium | High | Top | 133 | 194 | 68.1286
LUCERNE 1106 | 043351106 | NORTHERN | HUMBOLDT | 37.8799 | 845747.6667 | 45.3434 | 57.6% | 2.469% | 62.94% | 12.15% | 11 | 1 | 51 | 65.41% | 12.15% | 8.037% | 453 | 493 | 1 | 4 | 207 | 175 | 7 | 7 | 16 | 1095 | 41.5934 | 214 | 173 | 44 | 524 | 0 | 3 | 51 | 0 | 0.31024 | 12.0284 | 5.6516 | 21.09 | Low | Medium | High | Top | 224 | 195 | 67.9795
REDBUD 1102 | 043191102 | NORTHERN | HUMBOLDT | 29.3262 | 893934.6667 | 44.7823 | 73.97% | 3.45% | 68.7% | 8.426% | 4 | 1 | 17 | 72.15% | 8.426% | 8.484% | 216 | 285 | 3 | 10 | 176 | 83 | 0 | 6 | 9 | 719 | 35.119 | 91 | 80 | 14 | 259 | 0 | 0 | 17 | 0 | 0.19155 | 12.7704 | 5.2758 | 12.9055 | Low | High | Medium | Mid | 291 | 196 | 67.3739
SANTA YNEZ 1104 | 182721104 | CENTRAL COAST | LOS PADRES | 46.9293 | 971931.6667 | 41.9828 | 80.97% | 1.287% | 78.43% | 17.04% | 1 | 0 | 74 | 78.06% | 19.19% | 5.665% | 48 | 55 | 0 | 78 | 211 | 163 | 0 | 7 | 9 | 812 | 30.0575 | 50 | 40 | 3 | 234 | 0 | 0 | 73 | 0 | 0.15411 | 25.263 | 2.6431 | 10.2901 | Low | High | Low | Mid | 327 | 197 | 66.7727
SAN LUIS OBISPO 1103 | 182631103 | CENTRAL COAST | LOS PADRES | 19.9224 | 1227529 | 42.4841 | 18.95% | 0% | 66.14% | 25.17% | 6 | 0 | 34 | 66.14% | 25.19% | 7.789% | 63 | 60 | 0 | 66 | 178 | 33 | 0 | 5 | 7 | 475 | 26.0335 | 54 | 32 | 3 | 184 | 0 | 0 | 34 | 0 | 0.36473 | 11.7829 | 5.6258 | 24.1772 | Medium | Medium | High | Top | 199 | 198 | 66.2882
NOVATO 1104 | 042211104 | BAY AREA | NORTH BAY | 4.7025 | 1065059 | 51.5714 | 22.56% | 15.79% | 37.33% | 29.34% | 0 | 0 | 5 | 35.54% | 46.92% | 3.077% | 35 | 10 | 0 | 0 | 25 | 8 | 0 | 2 | 4 | 65 | 12.3 | 5 | 2 | 0 | 13 | 0 | 0 | 5 | 0 | 0.47286 | 11.8674 | 5.5799 | 31.3125 | Medium | Medium | High | Top | 166 | 199 | 66.2189
TASSAJARA 2109 | 014662109 | BAY AREA | DIABLO | 1.2042 | 719239 | 0 | 62.8% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.34331 | 9.4155 | 6.9926 | 22.6033 | Medium | Medium | High | Top | 210 | 200 | 65.8392
UKIAH 1111 | 042771111 | NORTHERN | HUMBOLDT | 22.9697 | 692428 | 41.4815 | 64.46% | 18.2% | 81.8% | 0% | 0 | 0 | 8 | 99.86% | 0.1414% | 16% | 20 | 46 | 0 | 1 | 153 | 96 | 0 | 0 | 0 | 325 | 43.5 | 29 | 11 | 4 | 75 | 0 | 0 | 8 | 0 | 0.16351 | 28.8186 | 2.2781 | 10.7352 | Low | High | Low | Mid | 320 | 201 | 65.6529
CORNING 1102 | 103331102 | NORTHERN | NORTH VALLEY | 81.2965 | 1289581.3333 | 39.9017 | 95.68% | 11.15% | 84.86% | 0.07427% | 4 | 0 | 36 | 90.2% | 6.193% | 3.328% | 86 | 786 | 12 | 0 | 148 | 77 | 0 | 10 | 18 | 1322 | 40.104 | 89 | 32 | 3 | 208 | 0 | 2 | 36 | 0 | 0.11127 | 25.5568 | 2.5613 | 7.2837 | Low | High | Low | Mid | 372 | 202 | 65.4598
NOTRE DAME 1104 | 102041104 | NORTHERN | NORTH VALLEY | 28.6184 | 1065755.6667 | 43.1707 | 38.88% | 7.59% | 62.48% | 0% | 0 | 1 | 10 | 70.07% | 0% | 7.266% | 71 | 178 | 4 | 0 | 59 | 9 | 0 | 5 | 9 | 578 | 39.5289 | 67 | 23 | 2 | 126 | 0 | 3 | 10 | 0 | 0.28459 | 11.1999 | 5.831 | 18.5858 | Low | Medium | High | Top | 243 | 203 | 65.307
GRASS VALLEY 1101 | 152031101 | NORTHERN | SIERRA | 17.4986 | 470903 | 42.0538 | 20.32% | 47.37% | 21.93% | 1.034% | 1 | 0 | 43 | 63.29% | 7.041% | 7.312% | 48 | 268 | 2 | 0 | 81 | 29 | 0 | 3 | 14 | 465 | 33.0793 | 82 | 30 | 3 | 166 | 0 | 1 | 43 | 0 | 0.26083 | 14.2287 | 4.5855 | 17.0183 | Low | High | Medium | Top | 248 | 204 | 65.2463
VACA DIXON 1105 | 063591105 | NORTHERN | SACRAMENTO | 29.0754 | 747516 | 42.2837 | 22.35% | 0.1419% | 90.86% | 0.8615% | 3 | 0 | 19 | 91% | 0.8615% | 2.2% | 56 | 230 | 3 | 0 | 71 | 17 | 1 | 6 | 7 | 500 | 35.7798 | 74 | 57 | 12 | 191 | 0 | 0 | 19 | 0 | 0.20292 | 18.0837 | 3.6007 | 13.2127 | Low | High | Low | Mid | 288 | 205 | 65.1137
BIG BASIN 1102 | 082841102 | CENTRAL COAST | CENTRAL COAST | 73.4523 | 445922 | 44.4454 | 19.22% | 2.324% | 57.19% | 16.45% | 83 | 15 | 125 | 55.68% | 24.43% | 11.65% | 349 | 696 | 0 | 17 | 524 | 228 | 58 | 21 | 44 | 1777 | 24.2091 | 213 | 117 | 29 | 619 | 2 | 0 | 123 | 1 | 0.85269 | 10.5824 | 6.1282 | 55.2976 | High | Medium | High | Top | 88 | 206 | 64.8512
GUALALA 1112 | 042841112 | NORTHERN | HUMBOLDT | 46.2448 | 283978.6667 | 42.2627 | 37.35% | 0.2584% | 28.02% | 67.98% | 35 | 2 | 96 | 10.58% | 86.13% | 3.661% | 106 | 308 | 0 | 3 | 307 | 49 | 44 | 13 | 20 | 956 | 36.3333 | 120 | 35 | 10 | 427 | 0 | 1 | 96 | 1 | 0.69981 | 19.1758 | 3.3433 | 44.8652 | High | High | Low | Top | 108 | 207 | 64.1103
TOCALOMA 0241 | 043150241 | BAY AREA | NORTH BAY | 0.031239 | 140551.6667 | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2517 | 11.2183 | 5.7098 | 16.1223 | Low | Medium | High | Top | 258 | 208 | 64.0548
OAKLAND X 1106 | 012541106 | BAY AREA | EAST BAY | 16.5816 | 765290.3333 | 44.2004 | 34.31% | 4.536% | 56% | 18.4% | 18 | 1 | 52 | 24.92% | 54.1% | 18.45% | 107 | 111 | 0 | 6 | 346 | 19 | 5 | 21 | 36 | 569 | 19.8299 | 38 | 64 | 20 | 149 | 0 | 0 | 52 | 0 | 0.62186 | 9.9434 | 6.4265 | 39.7379 | Medium | Medium | High | Top | 130 | 209 | 63.9013
FREMONT 1104 | 014351104 | CENTRAL COAST | MISSION | 7.4071 | 841311 | 41.4706 | 8.998% | 0% | 3.264% | 19.86% | 0 | 0 | 2 | 3.264% | 96.74% | 5.882% | 1 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 3 | 1 | 1 | 5 | 0 | 0 | 2 | 0 | 0.21027 | 12.4551 | 5.1163 | 13.3992 | Low | High | Medium | Mid | 283 | 210 | 63.7244
VINEYARD 2110 | 014502110 | CENTRAL COAST | MISSION | 6.8528 | 1350053.6667 | 42.7679 | 128.2% | 0% | 15.62% | 56.42% | 2 | 0 | 5 | 15.62% | 56.42% | 8.85% | 14 | 36 | 0 | 0 | 45 | 2 | 0 | 2 | 3 | 113 | 44.08 | 10 | 4 | 1 | 27 | 0 | 0 | 5 | 0 | 0.53485 | 11.3495 | 5.5876 | 33.9185 | Medium | Medium | High | Top | 155 | 211 | 63.4164
BAYWOOD 1101 | 182801101 | CENTRAL COAST | LOS PADRES | 4.2971 | 403333.6667 | 41.1628 | 3.693% | 0% | 74.94% | 25.06% | 0 | 0 | 1 | 74.94% | 25.06% | 4.651% | 4 | 1 | 2 | 2 | 17 | 0 | 0 | 2 | 3 | 43 | 20.1667 | 6 | 1 | 0 | 15 | 0 | 0 | 1 | 0 | 0.24583 | 12.3111 | 5.1411 | 15.5592 | Low | High | Medium | Top | 262 | 212 | 63.292
DRUM 1101 | 152321101 | NORTHERN | SIERRA | 18.8373 | 38852.3333 | 40.9494 | 12.54% | 91.97% | 8.034% | 0% | 3 | 1 | 18 | 98.7% | 1.3% | 18.88% | 29 | 168 | 9 | 0 | 180 | 49 | 0 | 9 | 17 | 482 | 35.4483 | 32 | 16 | 3 | 104 | 0 | 0 | 18 | 1 | 0.5977 | 59.9623 | 1.0505 | 37.6487 | Medium | High | Low | Top | 140 | 213 | 62.9897
APPLE HILL 2102 | 153662102 | NORTHERN | SIERRA | 340.2385 | 1278042.6667 | 42.6618 | 39.25% | 67.52% | 27.16% | 0.0005566% | 25 | 5 | 457 | 95.5% | 0.0005566% | 1.824% | 682 | 4238 | 270 | 0 | 1183 | 707 | 25 | 44 | 74 | 8167 | 42.6252 | 1351 | 653 | 40 | 2988 | 0 | 7 | 457 | 0 | 0.24544 | 18.073 | 3.4818 | 15.4449 | Low | High | Low | Top | 263 | 214 | 62.9265
JARVIS 1101 | 013501101 | CENTRAL COAST | MISSION | 0.92149 | 1462003 | 42.7778 | 3.281% | 0% | 93.6% | 0% | 0 | 0 | 1 | 37.36% | 56.23% | 0% | 1 | 6 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 9 | 1.5 | 2 | 1 | 0 | 4 | 0 | 0 | 1 | 0 | 0.18332 | 9.8889 | 6.3467 | 11.5054 | Low | Medium | High | Mid | 310 | 215 | 62.7618
LLAGAS 2107 | 083182107 | CENTRAL COAST | SAN JOSE | 9.1355 | 1392960.3333 | 41.7939 | 40.48% | 0% | 71.27% | 18.13% | 0 | 0 | 15 | 63.4% | 28.54% | 4.58% | 24 | 83 | 0 | 1 | 25 | 3 | 0 | 1 | 1 | 131 | 16.7636 | 21 | 15 | 2 | 59 | 0 | 0 | 15 | 0 | 0.35821 | 16.1281 | 3.8499 | 22.2414 | Medium | High | Medium | Top | 212 | 216 | 62.0911
CAYETANO 2109 | 014422109 | CENTRAL COAST | MISSION | 37.0707 | 935025 | 42.8694 | 40.93% | 0% | 59.19% | 25.44% | 0 | 0 | 46 | 59.33% | 35.19% | 19.55% | 32 | 266 | 0 | 0 | 160 | 17 | 0 | 7 | 9 | 583 | 43.6142 | 42 | 30 | 6 | 137 | 0 | 0 | 46 | 0 | 0.42316 | 11.2808 | 5.4929 | 26.221 | Medium | Medium | High | Top | 186 | 217 | 61.9645
ELECTRA 1102 | 162161102 | CENTRAL VALLEY | STOCKTON | 83.9986 | 567923.3333 | 43.1537 | 52.38% | 44.29% | 34.7% | 4.547% | 4 | 1 | 16 | 85.67% | 8.854% | 3.815% | 283 | 813 | 0 | 0 | 504 | 134 | 24 | 5 | 11 | 1835 | 41.9552 | 26 | 12 | 0 | 69 | 0 | 2 | 16 | 0 | 0.23094 | 13.9932 | 4.4144 | 14.2655 | Low | High | Medium | Top | 274 | 218 | 61.7712
SAN LUIS OBISPO 1105 | 182631105 | CENTRAL COAST | LOS PADRES | 2.3718 | 922696.6667 | 41.0484 | 35.1% | 1.227% | 36.65% | 38.53% | 0 | 0 | 6 | 37.87% | 38.53% | 3.226% | 4 | 1 | 0 | 1 | 35 | 4 | 0 | 1 | 2 | 62 | 15.3571 | 3 | 5 | 1 | 14 | 0 | 0 | 6 | 1 | 0.53568 | 12.2002 | 5.0535 | 33.0265 | Medium | Medium | Medium | Top | 163 | 219 | 61.6537
PASO ROBLES 1104 | 182611104 | CENTRAL COAST | LOS PADRES | 42.6155 | 983878.3333 | 42.6529 | 71.31% | 13.13% | 75.36% | 3.966% | 0 | 0 | 42 | 81.22% | 11.95% | 3.22% | 72 | 13 | 1 | 92 | 191 | 95 | 0 | 5 | 10 | 559 | 41.4633 | 70 | 31 | 6 | 194 | 0 | 0 | 42 | 0 | 0.10492 | 16.4912 | 3.6294 | 6.2801 | Low | High | Low | Mid | 395 | 220 | 59.8537
LAKEWOOD 2107 | 013532107 | BAY AREA | DIABLO | 9.3294 | 1395105 | 45 | 0% | 0% | 22.34% | 41.19% | 2 | 0 | 31 | 19.17% | 78.97% | 13.58% | 71 | 73 | 0 | 0 | 94 | 14 | 9 | 6 | 8 | 243 | 49.6636 | 27 | 45 | 12 | 108 | 0 | 0 | 31 | 1 | 0.74167 | 8.9554 | 6.6182 | 43.958 | High | Medium | High | Top | 114 | 221 | 59.2689
OTTER 1101 | 182941101 | CENTRAL COAST | CENTRAL COAST | 25.0962 | 123757 | 40.0704 | 32.22% | 4.226% | 24.73% | 37.01% | 16 | 4 | 31 | 17.53% | 62.62% | 13.25% | 20 | 188 | 0 | 9 | 190 | 42 | 2 | 10 | 16 | 498 | 13.2086 | 50 | 36 | 4 | 169 | 0 | 0 | 31 | 1 | 0.74861 | 13.9573 | 4.2298 | 44.195 | High | High | Medium | Top | 111 | 222 | 59.0362
BASALT 1106 | 042461106 | BAY AREA | NORTH BAY | 6.2402 | 1007250 | 42.7586 | 30.81% | 7.111% | 80.61% | 0.7277% | 0 | 0 | 4 | 70.63% | 20.15% | 6.897% | 4 | 15 | 0 | 0 | 6 | 1 | 0 | 0 | 0 | 29 | 36 | 1 | 0 | 0 | 5 | 0 | 0 | 4 | 0 | 0.18266 | 17.6161 | 3.3495 | 10.7778 | Low | High | Low | Mid | 319 | 223 | 59.0053
SANTA YNEZ 1102 | 182721102 | CENTRAL COAST | LOS PADRES | 7.2642 | 780186.3333 | 43.866 | 97.1% | 0.2586% | 86.15% | 1.148% | 0 | 1 | 11 | 85.39% | 2.167% | 5.102% | 17 | 4 | 0 | 11 | 35 | 10 | 0 | 3 | 3 | 98 | 34.3478 | 5 | 6 | 1 | 24 | 0 | 0 | 11 | 0 | 0.19826 | 19.492 | 3.0213 | 11.6756 | Low | High | Low | Mid | 309 | 224 | 58.8911
UKIAH 1113 | 042771113 | NORTHERN | HUMBOLDT | 7.0118 | 342503.6667 | 44.0107 | 0% | 32.53% | 55.33% | 12.06% | 0 | 0 | 8 | 86.76% | 13.16% | 8.021% | 42 | 65 | 0 | 0 | 64 | 15 | 0 | 2 | 2 | 187 | 28.8605 | 33 | 18 | 4 | 88 | 0 | 0 | 8 | 0 | 0.22946 | 19.4946 | 2.9987 | 13.4136 | Low | High | Low | Mid | 282 | 225 | 58.4583
DOBBINS 1101 | 153741101 | NORTHERN | SIERRA | 80.9568 | 273408.3333 | 41.9471 | 29.91% | 12.82% | 76.24% | 2.657% | 7 | 0 | 82 | 93.55% | 2.657% | 6.025% | 170 | 1122 | 58 | 0 | 211 | 148 | 10 | 13 | 25 | 1892 | 39.7418 | 277 | 73 | 9 | 638 | 0 | 6 | 82 | 0 | 0.072378 | 14.2415 | 4.1027 | 4.229 | Low | High | Medium | Mid | 468 | 226 | 58.4285
BRIDGEVILLE 1101 | 192461101 | NORTHERN | HUMBOLDT | 22.6718 | 41572 | 41.2399 | 18.92% | 28.24% | 12.88% | 0% | 10 | 3 | 28 | 99.69% | 0% | 28.3% | 35 | 7 | 0 | 1 | 221 | 24 | 3 | 6 | 13 | 371 | 31.6471 | 22 | 8 | 3 | 70 | 0 | 0 | 28 | 1 | 0.67759 | 74.0616 | 0.78727 | 39.5078 | High | High | Low | Top | 134 | 227 | 58.3068
MOLINO 1104 | 042571104 | NORTHERN | SONOMA | 2.6049 | 1197726 | 43.5 | 13.33% | 0% | 36.75% | 63.25% | 1 | 0 | 1 | 36.75% | 63.25% | 0% | 11 | 27 | 0 | 0 | 12 | 6 | 0 | 1 | 1 | 50 | 36.5833 | 11 | 4 | 1 | 24 | 0 | 0 | 1 | 0 | 0.41317 | 16.3193 | 3.5606 | 24.008 | Medium | High | Low | Top | 202 | 228 | 58.1064
COTATI 1105 | 042271105 | NORTHERN | SONOMA | 39.2511 | 853816.3333 | 43.1749 | 51.84% | 7.026% | 56.51% | 22.56% | 7 | 1 | 72 | 51.92% | 34.18% | 3.934% | 170 | 524 | 0 | 4 | 200 | 119 | 8 | 22 | 34 | 915 | 37.1816 | 140 | 68 | 16 | 374 | 0 | 4 | 72 | 0 | 0.32337 | 19.3531 | 2.9919 | 18.7239 | Low | High | Low | Top | 242 | 229 | 57.9026
PEABODY 2113 | 063642113 | NORTHERN | SACRAMENTO | 1.6686 | 1469742 | 41.0417 | 8.551% | 2.441% | 77.59% | 19.96% | 0 | 0 | 2 | 80.04% | 19.96% | 0% | 2 | 0 | 0 | 0 | 10 | 1 | 0 | 0 | 0 | 24 | 12.6667 | 3 | 0 | 1 | 7 | 0 | 0 | 2 | 0 | 0.16237 | 13.8657 | 4.1688 | 9.3853 | Low | High | Medium | Mid | 339 | 230 | 57.8035
FLINT 1101 | 152531101 | NORTHERN | SIERRA | 6.2972 | 697988.3333 | 44.3262 | 44.08% | 6.072% | 61.82% | 20.02% | 1 | 0 | 10 | 64.72% | 23.21% | 8.451% | 29 | 81 | 0 | 0 | 27 | 8 | 0 | 3 | 9 | 142 | 29.0364 | 23 | 22 | 0 | 55 | 0 | 0 | 10 | 0 | 0.45312 | 11.8876 | 4.8331 | 26.0333 | Medium | Medium | Medium | Top | 188 | 231 | 57.454
SWIFT 2110 | 083392110 | CENTRAL COAST | SAN JOSE | 83.7273 | 1271083.6667 | 40.976 | 49.02% | 11.88% | 65.4% | 22.33% | 3 | 0 | 73 | 73.06% | 26.93% | 6.649% | 67 | 548 | 0 | 8 | 275 | 81 | 0 | 3 | 12 | 1128 | 9.4839 | 78 | 49 | 5 | 250 | 0 | 1 | 72 | 0 | 0.22472 | 21.4706 | 2.6679 | 12.8723 | Low | High | Low | Mid | 292 | 232 | 57.2813
BUELLTON 1101 | 183041101 | CENTRAL COAST | LOS PADRES | 83.6196 | 1244816.3333 | 41.788 | 38.57% | 8.091% | 58.81% | 17.29% | 6 | 2 | 68 | 62.04% | 23.75% | 2.684% | 105 | 110 | 2 | 246 | 351 | 182 | 0 | 11 | 17 | 1267 | 20.1398 | 74 | 30 | 14 | 352 | 0 | 0 | 67 | 0 | 0.2908 | 15.5306 | 3.6659 | 16.5566 | Low | High | Low | Top | 253 | 233 | 56.9339
TEMPLETON 2113 | 183052113 | CENTRAL COAST | LOS PADRES | 199.0069 | 2234642 | 40.4477 | 73.34% | 5.894% | 77.49% | 11.62% | 7 | 1 | 131 | 76.11% | 20.08% | 9.025% | 175 | 184 | 3 | 593 | 1360 | 292 | 0 | 30 | 42 | 3191 | 37.3539 | 401 | 140 | 16 | 1120 | 0 | 1 | 131 | 0 | 0.13377 | 21.458 | 2.6495 | 7.6055 | Low | High | Low | Mid | 365 | 234 | 56.8533
TASSAJARA 2104 | 014662104 | BAY AREA | DIABLO | 7.4925 | 934894.3333 | 45.6034 | 42.88% | 0% | 60.47% | 26.97% | 2 | 0 | 10 | 57.62% | 31.83% | 17.09% | 33 | 51 | 0 | 0 | 19 | 9 | 0 | 4 | 5 | 117 | 45.7381 | 15 | 17 | 3 | 42 | 0 | 0 | 10 | 1 | 0.67001 | 8.4601 | 6.6681 | 37.7974 | High | Medium | High | Top | 139 | 235 | 56.4128
DUNBAR 1101 | 043071101 | NORTHERN | SONOMA | 43.5849 | 843643 | 43.9917 | 24.41% | 1.622% | 60.47% | 30.58% | 14 | 1 | 65 | 60.85% | 32.35% | 8.245% | 210 | 418 | 1 | 12 | 211 | 124 | 20 | 22 | 26 | 849 | 37.2642 | 120 | 91 | 17 | 359 | 0 | 0 | 65 | 1 | 0.76795 | 11.9565 | 4.6754 | 42.9292 | High | Medium | Medium | Top | 118 | 236 | 55.9009
SHINGLE SPRINGS 2105 | 153652105 | NORTHERN | SIERRA | 32.0602 | 1266119 | 43.0414 | 43.26% | 0.0146% | 83.23% | 0.1687% | 4 | 4 | 60 | 83.25% | 0.1687% | 0.7084% | 107 | 584 | 3 | 0 | 116 | 47 | 12 | 6 | 16 | 847 | 56.5618 | 230 | 149 | 15 | 435 | 0 | 0 | 60 | 0 | 0.12831 | 10.4629 | 5.2798 | 7.0883 | Low | Medium | Medium | Mid | 379 | 237 | 55.2424
PACIFICA 1103 | 022811103 | CENTRAL COAST | PENINSULA | 5.1834 | 366741 | 44.5775 | 3.111% | 1.604% | 13.5% | 7.182% | 2 | 0 | 4 | 3.981% | 18.3% | 5.556% | 14 | 19 | 0 | 0 | 36 | 6 | 1 | 2 | 7 | 72 | 14.5263 | 3 | 5 | 3 | 20 | 1 | 0 | 4 | 0 | 0.46166 | 8.529 | 6.4696 | 25.4741 | Medium | Medium | High | Top | 192 | 238 | 55.1792
HUMBOLDT BAY 1102 | 192341102 | NORTHERN | HUMBOLDT | 7.6153 | 641347 | 39.3706 | 20.18% | 0% | 3.741% | 96.26% | 3 | 0 | 9 | 0.8297% | 99.17% | 39.86% | 3 | 7 | 0 | 0 | 115 | 1 | 0 | 0 | 0 | 143 | 21.7619 | 15 | 7 | 2 | 45 | 0 | 0 | 9 | 0 | 0.44021 | 7.9626 | 6.8887 | 24.1463 | Medium | Medium | High | Top | 201 | 239 | 54.8519
WHITMORE 1101 | 103601101 | NORTHERN | NORTH VALLEY | 92.5696 | 144177 | 40.5451 | 32.28% | 71.28% | 21.05% | 1.318% | 6 | 0 | 84 | 83.16% | 10.49% | 8.126% | 178 | 999 | 54 | 0 | 485 | 144 | 0 | 13 | 26 | 2006 | 37.5782 | 191 | 65 | 5 | 451 | 0 | 2 | 83 | 0 | 0.064368 | 25.3433 | 2.1627 | 3.528 | Low | High | Low | Mid | 500 | 240 | 54.8096
ATASCADERO 1103 | 182541103 | CENTRAL COAST | LOS PADRES | 96.6947 | 871402 | 41.4933 | 70.47% | 3.698% | 79.43% | 12.11% | 2 | 3 | 89 | 73.22% | 24.88% | 6.851% | 176 | 76 | 1 | 272 | 663 | 179 | 6 | 20 | 31 | 1664 | 33.3787 | 245 | 128 | 4 | 602 | 0 | 0 | 88 | 0 | 0.11207 | 16.1071 | 3.3745 | 6.0916 | Low | High | Low | Mid | 404 | 241 | 54.3537
MONTICELLO 1101 | 043051101 | BAY AREA | NORTH BAY | 114.3461 | 412528 | 43.6848 | 85.14% | 3.791% | 87.7% | 7.604% | 14 | 7 | 98 | 64.78% | 34.32% | 6.723% | 277 | 694 | 3 | 14 | 575 | 384 | 10 | 24 | 41 | 1904 | 31 | 207 | 106 | 11 | 546 | 0 | 4 | 98 | 0 | 0.39577 | 13.3474 | 4.0532 | 21.411 | Medium | High | Medium | Top | 220 | 242 | 54.1003
CLOVERDALE 1101 | 042821101 | NORTHERN | SONOMA | 24.6061 | 702582.6667 | 43.4877 | 46.47% | 7.145% | 75.67% | 12.85% | 1 | 0 | 15 | 82.63% | 13.03% | 16.92% | 62 | 129 | 0 | 3 | 64 | 74 | 0 | 4 | 5 | 325 | 35.5678 | 54 | 17 | 5 | 122 | 0 | 0 | 15 | 0 | 0.19234 | 24.723 | 2.1882 | 10.4056 | Low | High | Low | Mid | 324 | 243 | 54.0995
WILLOW CREEK 1103 | 192171103 | NORTHERN | HUMBOLDT | 84.8219 | 402608 | 41.3286 | 24.87% | 20.3% | 58.13% | 0.366% | 46 | 3 | 96 | 79.72% | 0.4735% | 48.48% | 103 | 55 | 0 | 0 | 1004 | 89 | 30 | 16 | 27 | 1706 | 33.2074 | 225 | 98 | 20 | 646 | 1 | 2 | 96 | 1 | 0.4792 | 25.4354 | 2.1189 | 25.8269 | Medium | High | Low | Top | 191 | 244 | 53.8957
SAN LUIS OBISPO 1107 | 182631107 | CENTRAL COAST | LOS PADRES | 48.8854 | 1313335.6667 | 41.8043 | 63.41% | 3.533% | 48.4% | 29.04% | 12 | 0 | 82 | 47.4% | 40.63% | 7.056% | 94 | 74 | 1 | 134 | 432 | 130 | 0 | 25 | 35 | 992 | 32.1584 | 103 | 34 | 3 | 323 | 0 | 0 | 81 | 1 | 0.52312 | 10.881 | 4.9523 | 28.1892 | Medium | Medium | Medium | Top | 176 | 245 | 53.8862
VASCO 1102 | 013751102 | CENTRAL COAST | MISSION | 43.1032 | 566741 | 42.0938 | 99.26% | 0.3618% | 97.47% | 2.164% | 0 | 0 | 41 | 86.37% | 13.63% | 11.73% | 49 | 193 | 0 | 10 | 263 | 40 | 0 | 7 | 8 | 597 | 6.6599 | 51 | 46 | 8 | 164 | 0 | 1 | 40 | 0 | 0.13324 | 20.2954 | 2.6442 | 7.1504 | Low | High | Low | Mid | 376 | 246 | 53.6659
WILLOW CREEK 1101 | 192171101 | NORTHERN | HUMBOLDT | 48.6376 | 236976.6667 | 42.5683 | 41.37% | 27.06% | 48.46% | 0.005846% | 21 | 0 | 51 | 97.41% | 0.005846% | 50.27% | 152 | 43 | 0 | 0 | 524 | 73 | 27 | 15 | 21 | 923 | 34.2955 | 90 | 36 | 12 | 274 | 0 | 0 | 51 | 1 | 0.64034 | 35.5089 | 1.5081 | 34.2916 | Medium | High | Low | Top | 153 | 247 | 53.5525
JAMESON 1105 | 063801105 | NORTHERN | SACRAMENTO | 22.537 | 1153872.3333 | 43.1313 | 13.93% | 0% | 79.81% | 13.73% | 2 | 3 | 15 | 73.95% | 19.58% | 3.023% | 72 | 264 | 5 | 0 | 44 | 28 | 0 | 1 | 1 | 397 | 29.7642 | 44 | 33 | 5 | 118 | 0 | 0 | 15 | 0 | 0.2476 | 11.0603 | 4.8249 | 13.2129 | Low | Medium | Medium | Mid | 287 | 248 | 53.3644
UKIAH 1114 | 042771114 | NORTHERN | HUMBOLDT | 56.1108 | 603713.3333 | 42.2371 | 0% | 46.79% | 43.87% | 4.081% | 4 | 0 | 34 | 72.94% | 21.81% | 6.452% | 101 | 344 | 0 | 9 | 282 | 54 | 0 | 1 | 2 | 899 | 32.2492 | 130 | 42 | 9 | 306 | 0 | 0 | 34 | 0 | 0.23571 | 22.8555 | 2.3246 | 12.5234 | Low | High | Low | Mid | 298 | 249 | 53.1296
PUTAH CREEK 1102 | 063681102 | NORTHERN | SACRAMENTO | 28.6295 | 404010 | 43.8606 | 44.46% | 0% | 90.58% | 9.42% | 0 | 0 | 16 | 90.58% | 9.42% | 4.307% | 99 | 294 | 8 | 0 | 82 | 19 | 0 | 3 | 6 | 534 | 22.3988 | 66 | 38 | 4 | 182 | 0 | 1 | 16 | 0 | 0.089636 | 19.4519 | 2.7226 | 4.7471 | Low | High | Low | Mid | 442 | 250 | 52.9594
BEAR VALLEY 2105 | 252192105 | CENTRAL VALLEY | YOSEMITE | 133.2806 | 221278.6667 | 40.9388 | 0% | 66.83% | 31.03% | 0.5335% | 4 | 1 | 101 | 97.5% | 2.486% | 26.73% | 107 | 260 | 3 | 10 | 1208 | 140 | 0 | 36 | 59 | 2507 | 17.8247 | 288 | 94 | 15 | 786 | 0 | 4 | 101 | 0 | 0.16978 | 16.9472 | 3.1109 | 8.9509 | Low | High | Low | Mid | 345 | 251 | 52.721
CORONA 1103 | 043491103 | NORTHERN | SONOMA | 1.2055 | 996177.6667 | 40.2778 | 6.019% | 0% | 76.96% | 23.04% | 0 | 0 | 0 | 76.96% | 23.04% | 0% | 1 | 5 | 0 | 0 | 10 | 2 | 0 | 0 | 0 | 18 | 34.5 | 0 | 2 | 0 | 6 | 0 | 0 | 0 | 0 | 0.1333 | 13.3391 | 3.9397 | 7.0052 | Low | High | Medium | Mid | 381 | 252 | 52.5523
SHINGLE SPRINGS 1104 | 153651104 | NORTHERN | SIERRA | 44.414 | 484282.3333 | 43.6518 | 33.15% | 1.429% | 96.25% | 0% | 2 | 2 | 36 | 98.43% | 0% | 1.228% | 116 | 539 | 17 | 0 | 183 | 41 | 4 | 6 | 8 | 1059 | 46.4609 | 160 | 204 | 21 | 456 | 0 | 0 | 36 | 0 | 0.069469 | 11.3519 | 4.6197 | 3.6432 | Low | Medium | Medium | Mid | 495 | 253 | 52.443
TEMPLETON 2112 | 183052112 | CENTRAL COAST | LOS PADRES | 3.3396 | 1058186 | 42.4194 | 22.73% | 0% | 82.75% | 17.25% | 0 | 0 | 2 | 82.75% | 17.25% | 3.226% | 9 | 0 | 0 | 3 | 11 | 2 | 0 | 0 | 0 | 31 | 25.1667 | 3 | 4 | 0 | 13 | 0 | 0 | 2 | 0 | 0.22631 | 15.8309 | 3.3114 | 11.8637 | Low | High | Low | Mid | 305 | 254 | 52.4217
HOOPA 1101 | 192401101 | NORTHERN | HUMBOLDT | 109.0104 | 374716 | 42.2778 | 76.54% | 36.54% | 52.94% | 1.34% | 66 | 4 | 109 | 97.73% | 1.856% | 38.68% | 244 | 47 | 0 | 0 | 1037 | 217 | 11 | 35 | 43 | 1988 | 29.7526 | 260 | 72 | 11 | 643 | 2 | 3 | 107 | 1 | 0.54358 | 28.7619 | 1.8223 | 28.4902 | Medium | High | Low | Top | 175 | 255 | 52.4119
BEN LOMOND 0401 | 083040401 | CENTRAL COAST | CENTRAL COAST | 21.1277 | 173524.6667 | 44.4801 | 0% | 1.251% | 40.32% | 34.47% | 26 | 1 | 36 | 41.81% | 41.66% | 7.107% | 122 | 165 | 0 | 1 | 221 | 66 | 28 | 17 | 23 | 605 | 20.2422 | 57 | 88 | 15 | 231 | 1 | 0 | 36 | 0 | 0.78936 | 6.6101 | 7.9288 | 41.3705 | High | Medium | High | Top | 123 | 256 | 52.4105
LOS GATOS 1106 | 082021106 | CENTRAL COAST | DE ANZA | 70.8424 | 529466.6667 | 44.0876 | 26.26% | 1.726% | 66.18% | 15.87% | 51 | 6 | 143 | 67.75% | 17.31% | 10.52% | 398 | 841 | 1 | 15 | 556 | 175 | 23 | 25 | 51 | 1930 | 3.4031 | 248 | 173 | 32 | 693 | 0 | 0 | 142 | 1 | 0.72921 | 8.9217 | 5.867 | 38.1692 | High | Medium | High | Top | 137 | 257 | 52.3432
LAYTONVILLE 1101 | 042681101 | NORTHERN | HUMBOLDT | 53.8079 | 227276.3333 | 42.2127 | 36% | 30.05% | 40.22% | 0.07462% | 7 | 7 | 52 | 97.69% | 0.07462% | 10.48% | 102 | 326 | 0 | 3 | 191 | 54 | 16 | 6 | 11 | 935 | 36.2151 | 105 | 28 | 13 | 288 | 0 | 0 | 52 | 0 | 0.38664 | 36.3313 | 1.4317 | 20.1108 | Medium | High | Low | Top | 230 | 258 | 52.0143
MC KEE 1111 | 083531111 | CENTRAL COAST | SAN JOSE | 8.9106 | 1066791.3333 | 44.0446 | 42.57% | 0% | 67.12% | 32.88% | 0 | 0 | 13 | 67.12% | 32.88% | 10.83% | 23 | 73 | 0 | 1 | 50 | 9 | 0 | 4 | 5 | 157 | 12.5556 | 21 | 12 | 2 | 54 | 0 | 0 | 13 | 1 | 0.53022 | 17.8967 | 2.8981 | 27.5012 | Medium | High | Low | Top | 178 | 259 | 51.8673
VACAVILLE 1108 | 063601108 | NORTHERN | SACRAMENTO | 30.2656 | 956164.3333 | 42.1267 | 27.73% | 17.16% | 78.83% | 1.73% | 3 | 0 | 19 | 88.9% | 9.616% | 4.673% | 62 | 198 | 4 | 1 | 126 | 20 | 13 | 3 | 5 | 535 | 25.5682 | 59 | 59 | 9 | 201 | 0 | 0 | 19 | 0 | 0.22624 | 14.4907 | 3.5756 | 11.7221 | Low | High | Low | Mid | 308 | 260 | 51.8124
BEN LOMOND 1101 | 083041101 | CENTRAL COAST | CENTRAL COAST | 15.4019 | 131737.3333 | 43.9722 | 0% | 0% | 55.72% | 26.65% | 25 | 4 | 26 | 56.43% | 43.22% | 9.392% | 118 | 134 | 0 | 5 | 189 | 57 | 28 | 8 | 13 | 543 | 21.4279 | 78 | 47 | 7 | 205 | 0 | 0 | 26 | 0 | 0.7062 | 6.4203 | 8.0629 | 36.5574 | High | Medium | High | Top | 142 | 261 | 51.7663
SALMON CREEK 1101 | 043161101 | NORTHERN | SONOMA | 29.8535 | 493241 | 43.3764 | 38.45% | 0.007616% | 17.98% | 73.9% | 20 | 0 | 36 | 12.08% | 79.81% | 4.31% | 50 | 174 | 0 | 1 | 97 | 34 | 6 | 10 | 13 | 348 | 24.8256 | 33 | 21 | 8 | 88 | 0 | 3 | 36 | 0 | 0.60581 | 12.2083 | 4.2284 | 31.273 | Medium | Medium | Medium | Top | 167 | 262 | 51.6218
GEYSERVILLE 1102 | 042891102 | NORTHERN | SONOMA | 59.7619 | 896499.3333 | 43.4738 | 43.68% | 6.622% | 73.37% | 14.71% | 2 | 2 | 39 | 76.77% | 18.23% | 6.831% | 159 | 308 | 0 | 2 | 141 | 134 | 0 | 15 | 16 | 688 | 29.5061 | 113 | 33 | 5 | 255 | 0 | 2 | 39 | 0 | 0.19288 | 20.7752 | 2.4522 | 9.826 | Low | High | Low | Mid | 335 | 263 | 50.9445
BRIDGEVILLE 1102 | 192461102 | NORTHERN | HUMBOLDT | 35.2561 | 71499 | 45.2783 | 34.27% | 16.97% | 70.78% | 0% | 5 | 0 | 33 | 99.57% | 0% | 34.54% | 178 | 13 | 0 | 1 | 366 | 24 | 0 | 7 | 11 | 524 | 32.9725 | 31 | 14 | 7 | 114 | 0 | 2 | 33 | 0 | 0.45248 | 49.2394 | 1.0316 | 22.9841 | Medium | High | Low | Top | 208 | 264 | 50.7954
CURTIS 1703 | 163351703 | CENTRAL VALLEY | YOSEMITE | 195.9575 | 1283179.6667 | 43.1818 | 0% | 53.14% | 37.62% | 0.8058% | 19 | 1 | 202 | 90.47% | 1.158% | 3.02% | 712 | 2036 | 5 | 0 | 858 | 408 | 15 | 44 | 82 | 4205 | 25.3661 | 570 | 384 | 63 | 1540 | 0 | 1 | 202 | 0 | 0.26317 | 10.7025 | 4.7409 | 13.3531 | Low | Medium | Medium | Mid | 284 | 265 | 50.7395
OLETA 1101 | 163541101 | CENTRAL VALLEY | STOCKTON | 91.7582 | 636401.6667 | 43.7272 | 66.43% | 3.039% | 81.21% | 9.707% | 4 | 2 | 49 | 79.19% | 15.36% | 3.26% | 294 | 946 | 0 | 0 | 430 | 145 | 0 | 7 | 23 | 1810 | 37.0636 | 252 | 118 | 10 | 522 | 0 | 6 | 48 | 0 | 0.061666 | 9.7544 | 5.1735 | 3.1119 | Low | Medium | Medium | Mid | 520 | 266 | 50.4642
EL CERRITO G 1105 | 012501105 | BAY AREA | EAST BAY | 19.526 | 595064.3333 | 44.101 | 29.33% | 3.688% | 60.19% | 15.46% | 7 | 2 | 52 | 25.97% | 64.12% | 28.91% | 107 | 166 | 0 | 4 | 289 | 17 | 34 | 6 | 26 | 768 | 19.7189 | 46 | 115 | 24 | 234 | 0 | 0 | 52 | 0 | 0.52174 | 6.0467 | 8.3184 | 26.2432 | Medium | Medium | High | Top | 185 | 267 | 50.2994
HATTON 1101 | 182291101 | CENTRAL COAST | CENTRAL COAST | 16.0491 | 831835.3333 | 39.942 | 18.08% | 1.257% | 60.03% | 22.96% | 2 | 3 | 24 | 37.58% | 48.7% | 8.357% | 25 | 84 | 0 | 4 | 148 | 24 | 0 | 8 | 12 | 347 | 15.0168 | 39 | 25 | 6 | 121 | 0 | 0 | 23 | 0 | 0.46974 | 11.2329 | 4.47 | 23.5863 | Medium | Medium | Medium | Top | 206 | 268 | 50.2114
LOS OSITOS 2103 | 182082103 | CENTRAL COAST | CENTRAL COAST | 45.0959 | 716742.3333 | 39.2462 | 71.04% | 1.849% | 90.35% | 7.449% | 4 | 0 | 20 | 90.93% | 8.504% | 15.18% | 22 | 121 | 1 | 14 | 294 | 74 | 7 | 9 | 14 | 652 | 12.5521 | 67 | 14 | 6 | 208 | 0 | 0 | 20 | 0 | 0.19223 | 30.202 | 1.6624 | 9.6512 | Low | High | Low | Mid | 336 | 269 | 50.2066
HALF MOON BAY 1102 | 024101102 | CENTRAL COAST | PENINSULA | 9.0112 | 1004665.6667 | 42.2449 | 20.25% | 0% | 32.97% | 57.61% | 3 | 0 | 10 | 28.62% | 61.96% | 5.442% | 1 | 93 | 0 | 0 | 40 | 10 | 0 | 1 | 1 | 147 | 26.2885 | 14 | 11 | 3 | 52 | 4 | 0 | 10 | 0 | 0.60755 | 6.693 | 7.4146 | 30.1504 | Medium | Medium | High | Top | 169 | 270 | 49.626
CORRAL 1101 | 162991101 | CENTRAL VALLEY | STOCKTON | 122.4932 | 1121144 | 42.3663 | 74.89% | 0.1268% | 82.86% | 8.016% | 3 | 2 | 135 | 82.83% | 8.175% | 11.06% | 287 | 1036 | 10 | 0 | 585 | 129 | 11 | 9 | 22 | 2433 | 9.0406 | 414 | 269 | 23 | 974 | 0 | 0 | 135 | 0 | 0.089599 | 9.7556 | 5.0466 | 4.4112 | Low | Medium | Medium | Mid | 457 | 271 | 49.2325
PHILO 1101 | 042601101 | NORTHERN | HUMBOLDT | 78.3323 | 289113.3333 | 42.4822 | 35.62% | 7.394% | 80.96% | 7.054% | 20 | 0 | 57 | 66.43% | 28.97% | 5.924% | 142 | 457 | 0 | 5 | 317 | 79 | 0 | 8 | 13 | 1131 | 32.6424 | 130 | 26 | 8 | 366 | 0 | 3 | 57 | 0 | 0.28284 | 19.2782 | 2.544 | 13.8714 | Low | High | Low | Mid | 278 | 272 | 49.0438
MOUNTAIN QUARRIES 2101 | 152282101 | NORTHERN | SIERRA | 224.836 | 1285830 | 43.5164 | 33.38% | 13.47% | 75.99% | 1.38% | 16 | 3 | 322 | 85.21% | 9.612% | 7.27% | 564 | 3178 | 32 | 3 | 342 | 415 | 14 | 37 | 76 | 4952 | 46.5909 | 1051 | 564 | 31 | 2166 | 0 | 6 | 322 | 0 | 0.16423 | 10.9288 | 4.4155 | 7.9252 | Low | Medium | Medium | Mid | 362 | 273 | 48.2566
POINT ARENA 1101 | 043381101 | NORTHERN | HUMBOLDT | 44.7075 | 253041 | 41.7775 | 32.83% | 7.617% | 22.77% | 69.01% | 28 | 1 | 59 | 17.1% | 82.26% | 4.4% | 69 | 185 | 0 | 5 | 254 | 33 | 2 | 10 | 15 | 750 | 37.9359 | 64 | 21 | 11 | 240 | 0 | 0 | 59 | 1 | 0.73932 | 19.1632 | 2.5157 | 35.6415 | High | High | Low | Top | 143 | 274 | 48.2086
NORTH BRANCH 1101 | 163231101 | CENTRAL VALLEY | STOCKTON | 67.6297 | 539394.6667 | 43.3792 | 76.35% | 5.477% | 72.6% | 10.14% | 3 | 0 | 41 | 71% | 18.81% | 7.439% | 246 | 609 | 0 | 0 | 298 | 94 | 0 | 10 | 21 | 1277 | 27.9283 | 129 | 61 | 4 | 336 | 0 | 0 | 41 | 0 | 0.11885 | 8.9501 | 5.3505 | 5.6916 | Low | Medium | Medium | Mid | 415 | 275 | 47.8872
MILPITAS 1109 | 082831109 | CENTRAL COAST | SAN JOSE | 31.7351 | 944263.6667 | 42.297 | 46.2% | 10.39% | 84% | 0.9638% | 9 | 0 | 19 | 94.39% | 0.9638% | 5.051% | 42 | 151 | 0 | 1 | 117 | 5 | 0 | 11 | 16 | 396 | 9.042 | 36 | 24 | 6 | 129 | 0 | 0 | 18 | 0 | 0.39836 | 16.4592 | 2.901 | 19.0211 | Medium | High | Low | Top | 240 | 276 | 47.7484
RIO DELL 1102 | 192251102 | NORTHERN | HUMBOLDT | 54.1452 | 399090 | 40.5793 | 47.48% | 29.91% | 33.88% | 13.64% | 15 | 1 | 27 | 27.95% | 50.61% | 42.76% | 60 | 27 | 0 | 0 | 656 | 33 | 0 | 16 | 28 | 898 | 27.6838 | 36 | 16 | 4 | 123 | 0 | 1 | 24 | 0 | 0.53344 | 31.657 | 1.5043 | 25.4034 | Medium | High | Low | Top | 193 | 277 | 47.6217
DIAMOND SPRINGS 1107 | 152261107 | NORTHERN | SIERRA | 54.1952 | 1206886.3333 | 43.6342 | 17.79% | 13.78% | 72.19% | 2.187% | 3 | 0 | 81 | 85.78% | 2.386% | 0.3187% | 185 | 765 | 40 | 0 | 121 | 82 | 5 | 7 | 9 | 1255 | 46.2512 | 246 | 268 | 15 | 605 | 0 | 2 | 81 | 0 | 0.050584 | 11.5356 | 4.1074 | 2.3967 | Low | Medium | Medium | Bottom | 571 | 278 | 47.3811
CURTIS 1702 | 163351702 | CENTRAL VALLEY | YOSEMITE | 112.3028 | 1209566.6667 | 42.8858 | 0% | 24.78% | 60.65% | 5.201% | 8 | 1 | 138 | 87.58% | 8.982% | 3.342% | 442 | 1710 | 0 | 0 | 568 | 239 | 5 | 30 | 62 | 3022 | 24.3476 | 598 | 377 | 42 | 1424 | 0 | 0 | 136 | 0 | 0.15508 | 7.1779 | 6.5779 | 7.3224 | Low | Medium | High | Mid | 369 | 279 | 47.2154
SHADY GLEN 1101 | 152431101 | NORTHERN | SIERRA | 42.3648 | 695856.6667 | 42.1893 | 17.57% | 59.28% | 27.98% | 3.447% | 5 | 1 | 66 | 85.01% | 11.4% | 8.072% | 86 | 620 | 2 | 0 | 133 | 89 | 15 | 16 | 22 | 1053 | 36.5293 | 194 | 103 | 15 | 471 | 0 | 0 | 66 | 0 | 0.17219 | 11.439 | 4.1118 | 8.0989 | Low | Medium | Medium | Mid | 357 | 280 | 47.0346
ROB ROY 2105 | 083692105 | CENTRAL COAST | CENTRAL COAST | 43.7417 | 1421678 | 44.4507 | 8.058% | 0.4349% | 68.03% | 18.71% | 30 | 7 | 94 | 65.28% | 22.25% | 6.667% | 139 | 493 | 0 | 12 | 288 | 91 | 17 | 38 | 48 | 1065 | 47.523 | 118 | 94 | 12 | 486 | 0 | 0 | 94 | 1 | 0.72299 | 7.8598 | 5.9669 | 33.9072 | High | Medium | High | Top | 156 | 281 | 46.8986
OCEANO 1103 | 182601103 | CENTRAL COAST | LOS PADRES | 1.2899 | 1402991.3333 | 42.3333 | 10.74% | 0% | 88.78% | 11.22% | 0 | 0 | 4 | 88.78% | 11.22% | 0% | 0 | 0 | 0 | 1 | 3 | 11 | 0 | 2 | 2 | 15 | 58.25 | 0 | 1 | 0 | 7 | 0 | 0 | 4 | 1 | 0.23181 | 9.651 | 4.8193 | 10.7817 | Low | Medium | Medium | Mid | 318 | 282 | 46.511
TASSAJARA 2106 | 014662106 | BAY AREA | DIABLO | 0.35035 | 830488.3333 | 43.75 | 3.084% | 0% | 11.98% | 88.02% | 0 | 0 | 1 | 11.98% | 88.02% | 0% | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 38.6667 | 2 | 1 | 0 | 3 | 0 | 0 | 1 | 0 | 0.14591 | 6.1501 | 7.5502 | 6.7755 | Low | Medium | High | Mid | 385 | 283 | 46.4347
PIERCY 2110 | 083912110 | CENTRAL COAST | SAN JOSE | 21.9492 | 830413 | 40.7759 | 18.46% | 0% | 91.1% | 0% | 5 | 0 | 9 | 89% | 2.102% | 5.603% | 12 | 9 | 0 | 1 | 194 | 14 | 0 | 3 | 3 | 232 | 20.6364 | 11 | 3 | 3 | 44 | 0 | 0 | 8 | 0 | 0.23788 | 15.0285 | 3.0676 | 10.9666 | Low | High | Low | Mid | 315 | 284 | 46.1014
SAUSALITO 1101 | 042491101 | BAY AREA | NORTH BAY | 0.75125 | 757959.6667 | 44.359 | 11.8% | 0% | 18.96% | 9.827% | 3 | 0 | 3 | 12.91% | 75.95% | 2.564% | 8 | 12 | 0 | 0 | 17 | 5 | 0 | 1 | 2 | 39 | 12.8667 | 0 | 7 | 1 | 15 | 0 | 0 | 3 | 1 | 0.56512 | 7.7572 | 5.9244 | 25.971 | Medium | Medium | High | Top | 189 | 285 | 45.9569
PAUL SWEET 2104 | 083252104 | CENTRAL COAST | CENTRAL COAST | 17.7398 | 1907378 | 45.2185 | 8.745% | 0% | 76.87% | 11.53% | 3 | 0 | 52 | 76.1% | 12.43% | 4.37% | 91 | 203 | 0 | 5 | 108 | 27 | 0 | 10 | 10 | 389 | 57.9791 | 42 | 39 | 8 | 192 | 4 | 0 | 52 | 0 | 0.35781 | 7.4358 | 6.1387 | 16.3329 | Medium | Medium | High | Top | 256 | 286 | 45.6462
BRUNSWICK 1110 | 152481110 | NORTHERN | SIERRA | 24.9441 | 1326975 | 41.5924 | 18.5% | 43.86% | 34% | 0% | 3 | 0 | 40 | 56.96% | 20.9% | 9.772% | 58 | 432 | 6 | 0 | 127 | 53 | 11 | 12 | 21 | 788 | 35.9049 | 106 | 75 | 19 | 287 | 0 | 0 | 40 | 1 | 0.57292 | 9.2457 | 4.8758 | 25.8271 | Medium | Medium | Medium | Top | 190 | 287 | 45.0801
LOS COCHES 1101 | 182151101 | CENTRAL COAST | CENTRAL COAST | 2.6219 | 393335.3333 | 39.8649 | 6.6% | 0% | 100% | 0% | 0 | 0 | 0 | 12.86% | 87.14% | 5.405% | 1 | 14 | 0 | 0 | 12 | 3 | 0 | 0 | 0 | 37 | 10.8 | 4 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0.15319 | 29.4995 | 1.5275 | 6.9025 | Low | High | Low | Mid | 383 | 288 | 45.0597
FRENCH GULCH 1102 | 103381102 | NORTHERN | NORTH VALLEY | 22.423 | 40453.6667 | 40.4175 | 76.3% | 62.99% | 30.28% | 0% | 1 | 0 | 7 | 99.77% | 0% | 4.277% | 78 | 184 | 7 | 0 | 216 | 32 | 0 | 4 | 7 | 491 | 30.8 | 13 | 3 | 0 | 30 | 0 | 0 | 6 | 0 | 0.26809 | 11.8873 | 3.7098 | 11.8226 | Low | Medium | Low | Mid | 306 | 289 | 44.0996
EEL RIVER 1102 | 192381102 | NORTHERN | HUMBOLDT | 40.3143 | 853283.3333 | 41.3694 | 27.77% | 39.69% | 30.43% | 29.88% | 18 | 0 | 15 | 61.68% | 38.32% | 44.69% | 57 | 11 | 0 | 0 | 321 | 73 | 33 | 9 | 11 | 631 | 22.6667 | 29 | 9 | 3 | 99 | 1 | 0 | 15 | 0 | 0.67847 | 26.3681 | 1.6609 | 29.713 | High | High | Low | Top | 170 | 290 | 43.7943
OAKHURST 1101 | 254421101 | CENTRAL VALLEY | YOSEMITE | 92.9272 | 802392 | 39.9706 | 63.81% | 51.99% | 38.39% | 3.996% | 2 | 1 | 71 | 86.64% | 7.922% | 24.32% | 57 | 394 | 1 | 2 | 873 | 142 | 0 | 24 | 32 | 2052 | 27.984 | 300 | 172 | 16 | 820 | 0 | 1 | 71 | 0 | 0.092651 | 11.2547 | 3.8539 | 4.0187 | Low | Medium | Medium | Mid | 476 | 291 | 43.3744
TEMPLETON 2110 | 183052110 | CENTRAL COAST | LOS PADRES | 136.5197 | 1004387.3333 | 41.6003 | 57.59% | 13.55% | 78.42% | 4.468% | 13 | 2 | 112 | 81.92% | 18.04% | 8.597% | 217 | 141 | 0 | 350 | 748 | 191 | 0 | 33 | 44 | 1896 | 38.1793 | 224 | 118 | 6 | 622 | 0 | 0 | 111 | 0 | 0.18446 | 12.0159 | 3.6039 | 7.988 | Low | Medium | Low | Mid | 360 | 292 | 43.3044
FORT SEWARD 1122 | 192321122 | NORTHERN | HUMBOLDT | 17.6582 | 29145 | 38.3943 | 42.47% | 10.48% | 67.82% | 0% | 2 | 0 | 10 | 100% | 0% | 21.77% | 13 | 4 | 0 | 0 | 158 | 8 | 0 | 1 | 2 | 248 | 36.7347 | 14 | 8 | 5 | 50 | 0 | 0 | 10 | 0 | 0.30678 | 25.8623 | 1.6724 | 13.2692 | Low | High | Low | Mid | 286 | 293 | 43.2527
CLAYTON 2212 | 012022212 | BAY AREA | DIABLO | 48.6411 | 1195201.6667 | 44.6242 | 0% | 14.48% | 64.81% | 12.94% | 9 | 3 | 76 | 52.57% | 40.75% | 13.93% | 175 | 495 | 1 | 1 | 169 | 42 | 0 | 17 | 18 | 919 | 45.8519 | 118 | 104 | 14 | 351 | 0 | 0 | 76 | 1 | 0.61951 | 7.6487 | 5.6075 | 26.5708 | Medium | Medium | High | Top | 181 | 294 | 42.8903
VACAVILLE 1104 | 063601104 | NORTHERN | SACRAMENTO | 15.7436 | 991004.3333 | 43.3104 | 143.9% | 1.618% | 39.26% | 27.79% | 2 | 0 | 20 | 39.57% | 33.35% | 6.831% | 60 | 116 | 1 | 0 | 109 | 20 | 0 | 3 | 11 | 366 | 33.0805 | 33 | 21 | 2 | 102 | 0 | 5 | 20 | 0 | 0.35647 | 10.7723 | 3.9792 | 15.28 | Medium | Medium | Medium | Top | 265 | 295 | 42.8647
OILFIELDS 1103 | 182391103 | CENTRAL COAST | CENTRAL COAST | 117.8387 | 676842 | 41.8217 | 59.82% | 7.064% | 80.84% | 0.0615% | 2 | 0 | 99 | 90.89% | 0.3467% | 8.601% | 74 | 195 | 1 | 319 | 370 | 80 | 0 | 24 | 37 | 1151 | 33.2937 | 112 | 68 | 8 | 446 | 0 | 0 | 99 | 0 | 0.078838 | 11.8293 | 3.6117 | 3.3683 | Low | Medium | Low | Mid | 510 | 296 | 42.7243
PASO ROBLES 1103 | 182611103 | CENTRAL COAST | LOS PADRES | 40.9142 | 920890.6667 | 44.0492 | 98.09% | 0.966% | 50.6% | 15.19% | 4 | 0 | 51 | 50.48% | 16.9% | 6.831% | 177 | 84 | 0 | 88 | 149 | 66 | 0 | 16 | 30 | 732 | 37.9921 | 147 | 33 | 2 | 260 | 0 | 0 | 51 | 0 | 0.28115 | 10.6388 | 3.9743 | 11.8876 | Low | Medium | Medium | Mid | 304 | 297 | 42.2821
JAMESON 1103 | 063801103 | NORTHERN | SACRAMENTO | 3.8489 | 503860 | 44.1489 | 8.384% | 0% | 91.62% | 8.383% | 0 | 0 | 0 | 91.62% | 8.383% | 2.083% | 5 | 37 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 48 | 26.2353 | 7 | 4 | 0 | 18 | 0 | 0 | 0 | 0 | 0.15795 | 9.962 | 4.1924 | 6.597 | Low | Medium | Medium | Mid | 391 | 298 | 41.7652
RESERVATION ROAD 1101 | 182731101 | CENTRAL COAST | CENTRAL COAST | 26.4979 | 367194 | 42.1029 | 27.19% | 11.7% | 54.62% | 26.37% | 4 | 1 | 64 | 38.81% | 53.79% | 9.892% | 68 | 162 | 1 | 9 | 226 | 30 | 2 | 13 | 22 | 556 | 14.1441 | 74 | 50 | 5 | 244 | 0 | 0 | 64 | 1 | 0.63189 | 11.6366 | 3.5694 | 26.2459 | Medium | Medium | Low | Top | 184 | 299 | 41.5356
FITCH MOUNTAIN 1111 | 042751111 | NORTHERN | SONOMA | 3.8443 | 985909.6667 | 43.4211 | 30.64% | 8.052% | 44.36% | 47.25% | 0 | 0 | 0 | 52.42% | 47.25% | 10.53% | 20 | 23 | 1 | 2 | 20 | 8 | 0 | 0 | 0 | 57 | 30.8 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0.48412 | 11.4461 | 3.6063 | 19.9835 | Medium | Medium | Low | Top | 232 | 300 | 41.2776
CLAYTON 2213 | 012022213 | BAY AREA | DIABLO | 3.8789 | 1024410 | 42.1698 | 0% | 0% | 100% | 0% | 0 | 0 | 2 | 100% | 0% | 0% | 14 | 10 | 0 | 0 | 40 | 0 | 0 | 1 | 1 | 53 | 21 | 1 | 0 | 2 | 4 | 0 | 0 | 2 | 1 | 0.39159 | 6.6722 | 6.1598 | 16.094 | Medium | Medium | High | Top | 259 | 301 | 41.0996
BIG TREES 0402 | 083050402 | CENTRAL COAST | CENTRAL COAST | 16.2451 | 179748.6667 | 42.7589 | 0% | 0.849% | 40.88% | 45.19% | 30 | 1 | 28 | 37.02% | 49.89% | 8.659% | 86 | 131 | 0 | 6 | 256 | 66 | 56 | 8 | 11 | 589 | 33.5945 | 60 | 66 | 13 | 221 | 3 | 0 | 28 | 1 | 0.8653 | 5.1328 | 7.8809 | 35.0022 | High | Medium | High | Top | 148 | 302 | 40.4508
CLOVERDALE 1102 | 042821102 | NORTHERN | SONOMA | 83.3346 | 1190946 | 42.7159 | 42.23% | 4.676% | 76.45% | 13.66% | 10 | 0 | 69 | 75.96% | 20.78% | 9.05% | 147 | 365 | 0 | 6 | 223 | 164 | 6 | 20 | 26 | 884 | 34.094 | 131 | 60 | 9 | 330 | 0 | 2 | 69 | 0 | 0.3486 | 16.796 | 2.4032 | 14.071 | Medium | High | Low | Mid | 277 | 303 | 40.3646
RESERVATION ROAD 1102 | 182731102 | CENTRAL COAST | CENTRAL COAST | 17.671 | 873814.3333 | 40.3351 | 7.497% | 0.4033% | 64.91% | 33.98% | 2 | 0 | 26 | 58.49% | 40.8% | 9.043% | 17 | 105 | 0 | 1 | 140 | 25 | 0 | 4 | 5 | 376 | 15.2941 | 49 | 29 | 3 | 147 | 0 | 0 | 26 | 0 | 0.3525 | 14.7217 | 2.7418 | 14.2282 | Medium | High | Low | Top | 275 | 304 | 40.3641
MESA 1101 | 182821101 | CENTRAL COAST | LOS PADRES | 51.3797 | 610527 | 42.1948 | 32.34% | 0.08203% | 61.62% | 22.63% | 7 | 0 | 55 | 64.34% | 22.8% | 5.841% | 93 | 74 | 0 | 210 | 216 | 85 | 0 | 3 | 8 | 856 | 30.3484 | 95 | 41 | 4 | 311 | 0 | 0 | 55 | 0 | 0.27505 | 11.6851 | 3.4196 | 10.9904 | Low | Medium | Low | Mid | 314 | 305 | 39.9579
LAS POSITAS 2108 | 014402108 | CENTRAL COAST | MISSION | 8.2317 | 1375733.6667 | 43.6667 | 67.99% | 11.23% | 50.94% | 32.08% | 0 | 0 | 15 | 34.49% | 65.23% | 14.07% | 16 | 82 | 0 | 1 | 21 | 8 | 0 | 2 | 2 | 135 | 28.2692 | 3 | 7 | 4 | 32 | 0 | 0 | 15 | 0 | 0.61383 | 8.5365 | 4.6617 | 24.4271 | Medium | Medium | Medium | Top | 197 | 306 | 39.7948
HICKS 2101 | 083432101 | CENTRAL COAST | SAN JOSE | 17.3217 | 1240974.3333 | 44.1935 | 67.8% | 0.4407% | 47.47% | 20.94% | 5 | 0 | 17 | 41.44% | 27.41% | 9.545% | 51 | 97 | 0 | 5 | 62 | 14 | 7 | 3 | 3 | 220 | 32.973 | 26 | 15 | 3 | 82 | 0 | 0 | 17 | 0 | 0.54487 | 10.2974 | 3.8628 | 21.6733 | Medium | Medium | Medium | Top | 217 | 307 | 39.7772
LLAGAS 2106 | 083182106 | CENTRAL COAST | SAN JOSE | 2.0521 | 1901998 | 47.5 | 0.7117% | 0% | 100% | 0% | 0 | 0 | 2 | 100% | 0% | 83.33% | 12 | 2 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 18 | 0 | 1 | 3 | 0 | 5 | 0 | 0 | 2 | 0 | 0.29163 | 13.8356 | 2.8315 | 11.4249 | Low | High | Low | Mid | 312 | 308 | 39.1756
POTTER VALLEY P H 1105 | 042281105 | NORTHERN | HUMBOLDT | 49.5502 | 211374 | 42.6262 | 33.12% | 10.21% | 72.73% | 10.72% | 2 | 1 | 28 | 80.59% | 13.06% | 5.156% | 101 | 325 | 2 | 24 | 231 | 67 | 0 | 10 | 15 | 834 | 37.7011 | 87 | 30 | 8 | 273 | 0 | 1 | 28 | 0 | 0.10901 | 24.9211 | 1.5637 | 4.2481 | Low | High | Low | Mid | 465 | 309 | 38.9688
PERRY 1101 | 183071101 | CENTRAL COAST | LOS PADRES | 70.1245 | 547419 | 41.3534 | 16.81% | 3.192% | 45.63% | 40.66% | 13 | 1 | 103 | 34.54% | 57.69% | 3.878% | 104 | 138 | 0 | 159 | 693 | 125 | 0 | 19 | 39 | 1470 | 25.5915 | 174 | 87 | 7 | 462 | 0 | 0 | 103 | 0 | 0.54895 | 7.3713 | 5.2829 | 21.3772 | Medium | Medium | Medium | Top | 221 | 310 | 38.9417
GUALALA 1111 | 042841111 | NORTHERN | HUMBOLDT | 37.4475 | 390200 | 43.257 | 39.15% | 0.4% | 15.42% | 58.55% | 19 | 4 | 73 | 10.49% | 73.81% | 0.9646% | 120 | 178 | 0 | 5 | 296 | 9 | 10 | 27 | 44 | 622 | 33.2212 | 74 | 26 | 9 | 235 | 0 | 0 | 72 | 1 | 0.74923 | 11.7966 | 3.2724 | 28.9232 | High | Medium | Low | Top | 173 | 311 | 38.6037
FRENCH GULCH 1101 | 103381101 | NORTHERN | NORTH VALLEY | 18.8732 | 81398 | 41.7304 | 57.91% | 30.8% | 64.98% | 0% | 3 | 0 | 7 | 100% | 0% | 7.219% | 49 | 205 | 14 | 1 | 97 | 57 | 0 | 4 | 11 | 471 | 37.3176 | 36 | 13 | 0 | 90 | 0 | 1 | 7 | 0 | 0.26417 | 10.7915 | 3.5769 | 10.1971 | Low | Medium | Low | Mid | 328 | 312 | 38.6003
PLACER 1103 | 152461103 | NORTHERN | SIERRA | 14.4144 | 655934 | 43.4528 | 37.12% | 0.03919% | 44.06% | 24.96% | 1 | 0 | 21 | 40.47% | 28.89% | 5.212% | 48 | 220 | 1 | 0 | 41 | 11 | 0 | 2 | 4 | 307 | 33.2034 | 49 | 36 | 0 | 120 | 0 | 0 | 21 | 0 | 0.34787 | 7.7884 | 4.9258 | 13.3454 | Medium | Medium | Medium | Mid | 285 | 313 | 38.3637
SAN BENITO 2101 | 182742101 | CENTRAL COAST | CENTRAL COAST | 3.8338 | 1306436.3333 | 39.1538 | 71.09% | 0% | 61.18% | 38.82% | 0 | 0 | 3 | 61.18% | 38.82% | 0% | 1 | 21 | 0 | 1 | 39 | 0 | 0 | 0 | 0 | 65 | 35.087 | 12 | 2 | 0 | 25 | 0 | 0 | 3 | 0 | 0.27258 | 12.0304 | 3.1507 | 10.3316 | Low | Medium | Low | Mid | 326 | 314 | 37.9037
APPLE HILL 1103 | 153661103 | NORTHERN | SIERRA | 61.6574 | 603883 | 41.8106 | 19.54% | 49.2% | 27.98% | 7.434% | 10 | 2 | 109 | 75.99% | 13.71% | 2.511% | 146 | 783 | 12 | 0 | 356 | 196 | 6 | 8 | 14 | 1752 | 46.4663 | 296 | 169 | 23 | 675 | 0 | 0 | 109 | 0 | 0.14332 | 10.7653 | 3.4967 | 5.3949 | Low | Medium | Low | Mid | 422 | 315 | 37.6429
ZACA 1102 | 182681102 | CENTRAL COAST | LOS PADRES | 66.1296 | 626381.6667 | 42.3989 | 27.47% | 4.279% | 75.51% | 12.04% | 3 | 0 | 133 | 79.4% | 12.67% | 3.33% | 92 | 63 | 0 | 274 | 296 | 300 | 24 | 13 | 17 | 1141 | 28.724 | 82 | 82 | 3 | 357 | 0 | 0 | 131 | 0 | 0.15579 | 14.0871 | 2.6654 | 5.8494 | Low | High | Low | Mid | 410 | 316 | 37.5477
SONOMA 1107 | 042721107 | NORTHERN | SONOMA | 3.8318 | 610322.6667 | 44.7887 | 31.83% | 0% | 22.48% | 51.09% | 0 | 0 | 5 | 22.48% | 73.69% | 8.333% | 26 | 25 | 0 | 0 | 4 | 13 | 0 | 0 | 0 | 72 | 25.8571 | 3 | 1 | 0 | 9 | 0 | 0 | 5 | 0 | 0.40148 | 9.6896 | 3.8449 | 14.9574 | Medium | Medium | Medium | Top | 269 | 317 | 37.2559
PALMER 1101 | 183031101 | CENTRAL COAST | LOS PADRES | 39.5446 | 932357 | 45.1737 | 131.3% | 5.813% | 57.29% | 12.2% | 1 | 0 | 44 | 46.65% | 30.11% | 1.625% | 115 | 56 | 1 | 93 | 144 | 110 | 5 | 11 | 20 | 554 | 26.48 | 30 | 11 | 1 | 113 | 0 | 0 | 44 | 0 | 0.19953 | 12.9258 | 2.8668 | 7.3937 | Low | High | Low | Mid | 368 | 318 | 37.0557
COTTONWOOD 1103 | 102931103 | NORTHERN | NORTH VALLEY | 129.5388 | 1086587.3333 | 42.5679 | 51.9% | 49.26% | 45.06% | 4.398% | 5 | 0 | 88 | 94.32% | 4.398% | 9.656% | 293 | 1624 | 109 | 0 | 547 | 468 | 0 | 21 | 30 | 3252 | 52.9558 | 472 | 306 | 36 | 1127 | 0 | 5 | 88 | 0 | 0.082078 | 10.5165 | 3.5227 | 3.0407 | Low | Medium | Low | Mid | 523 | 319 | 37.0465
ROB ROY 2104 | 083692104 | CENTRAL COAST | CENTRAL COAST | 106.0267 | 906993 | 43.4998 | 15.78% | 0.734% | 72.55% | 14.36% | 63 | 13 | 211 | 71.7% | 20.47% | 7.288% | 334 | 1233 | 1 | 14 | 626 | 211 | 78 | 47 | 59 | 2415 | 45.1421 | 279 | 118 | 20 | 987 | 8 | 0 | 211 | 1 | 0.70868 | 6.8211 | 5.4061 | 26.133 | High | Medium | High | Top | 187 | 320 | 36.8758
SAN RAFAEL 1107 | 042011107 | BAY AREA | NORTH BAY | 21.024 | 904257 | 44.2947 | 29.24% | 2.146% | 28.21% | 65.05% | 18 | 4 | 54 | 27.54% | 69.51% | 6.667% | 222 | 230 | 8 | 5 | 271 | 244 | 18 | 22 | 30 | 885 | 41.8753 | 105 | 134 | 45 | 367 | 0 | 0 | 54 | 1 | 0.84623 | 4.2874 | 8.5737 | 31.1065 | High | Medium | High | Top | 168 | 321 | 36.7589
GIRVAN 1101 | 103401101 | NORTHERN | NORTH VALLEY | 107.3683 | 551410 | 41.9268 | 66.67% | 38.45% | 50.68% | 0.1729% | 2 | 0 | 88 | 92.96% | 0.3634% | 9.752% | 251 | 1261 | 70 | 3 | 450 | 209 | 17 | 19 | 30 | 2461 | 47.2913 | 314 | 242 | 19 | 761 | 0 | 4 | 88 | 0 | 0.065167 | 9.7381 | 3.7654 | 2.3895 | Low | Medium | Medium | Bottom | 576 | 322 | 36.6676
SEACLIFF 0401 | 083500401 | CENTRAL COAST | CENTRAL COAST | 8.831 | 68383.6667 | 44.7143 | 89.29% | 0% | 69.59% | 23.45% | 3 | 0 | 11 | 69.59% | 23.45% | 6.667% | 43 | 91 | 0 | 3 | 67 | 17 | 23 | 4 | 6 | 210 | 27.716 | 17 | 25 | 2 | 84 | 0 | 0 | 11 | 0 | 0.52438 | 5.9604 | 6.131 | 19.1625 | Medium | Medium | High | Top | 237 | 323 | 36.5429
CAMP EVERS 2103 | 083622103 | CENTRAL COAST | CENTRAL COAST | 48.9903 | 837752 | 43.9178 | 13.65% | 0.3207% | 42.76% | 25.74% | 49 | 18 | 117 | 51.78% | 36.46% | 8.049% | 222 | 411 | 0 | 6 | 420 | 98 | 36 | 25 | 36 | 1230 | 50.4239 | 170 | 115 | 24 | 531 | 5 | 0 | 117 | 1 | 0.90961 | 5.454 | 6.6958 | 33.218 | High | Medium | High | Top | 160 | 324 | 36.5191
MORGAN HILL 2105 | 083242105 | CENTRAL COAST | SAN JOSE | 53.819 | 1235253.3333 | 42.623 | 31.12% | 0.5059% | 67.87% | 17.27% | 7 | 0 | 123 | 64.03% | 22.35% | 7.328% | 168 | 591 | 1 | 10 | 269 | 54 | 0 | 23 | 35 | 1078 | 24.7897 | 131 | 103 | 19 | 426 | 0 | 0 | 122 | 0 | 0.31888 | 8.7824 | 4.0834 | 11.4356 | Low | Medium | Medium | Mid | 311 | 325 | 35.8618
PANORAMA 1102 | 103461102 | NORTHERN | NORTH VALLEY | 34.2527 | 976523.6667 | 43.0259 | 52.24% | 24.89% | 45.15% | 15.66% | 1 | 0 | 12 | 66.55% | 33.45% | 7.246% | 126 | 246 | 10 | 0 | 114 | 71 | 0 | 5 | 7 | 621 | 35.5055 | 31 | 19 | 1 | 106 | 0 | 0 | 12 | 0 | 0.29312 | 9.8211 | 3.6499 | 10.5071 | Low | Medium | Low | Mid | 323 | 326 | 35.8457
ARCATA 1122 | 192021122 | NORTHERN | HUMBOLDT | 20.6796 | 707240 | 41.8762 | 45.78% | 0.3739% | 44.86% | 53.1% | 12 | 0 | 31 | 45.78% | 54.22% | 56.01% | 58 | 21 | 0 | 1 | 362 | 34 | 3 | 5 | 10 | 516 | 27.8462 | 62 | 17 | 19 | 188 | 0 | 2 | 31 | 1 | 0.77057 | 6.9454 | 5.1355 | 27.4847 | High | Medium | Medium | Top | 179 | 327 | 35.6681
WILDWOOD 1101 | 103611101 | NORTHERN | NORTH VALLEY | 32.6037 | 57735.6667 | 38.9234 | 116.9% | 81.49% | 18.51% | 0% | 0 | 0 | 11 | 99.99% | 0% | 1.59% | 12 | 257 | 7 | 0 | 254 | 18 | 0 | 9 | 19 | 629 | 43.3605 | 36 | 9 | 2 | 96 | 0 | 2 | 11 | 0 | 0.27865 | 24.5337 | 1.4501 | 9.9136 | Low | High | Low | Mid | 331 | 328 | 35.5774
GOLDTREE 1108 | 182581108 | CENTRAL COAST | LOS PADRES | 2.8394 | 635317 | 44.3333 | 127% | 1.891% | 25.37% | 6.778% | 1 | 0 | 3 | 27.26% | 6.778% | 4.444% | 11 | 0 | 0 | 4 | 18 | 16 | 0 | 1 | 1 | 45 | 58.1818 | 3 | 2 | 0 | 12 | 0 | 0 | 3 | 0 | 0.36451 | 7.1986 | 4.9397 | 12.9614 | Medium | Medium | Medium | Mid | 290 | 329 | 35.5587
FORT BRAGG A 1102 | 042761102 | NORTHERN | HUMBOLDT | 65.6344 | 694872 | 43.2274 | 26.5% | 4.471% | 24.95% | 67.01% | 78 | 3 | 111 | 24.79% | 71.64% | 4.627% | 334 | 581 | 0 | 9 | 367 | 134 | 55 | 16 | 25 | 1621 | 35.5671 | 214 | 87 | 31 | 667 | 0 | 3 | 111 | 0 | 0.69983 | 9.8268 | 3.6102 | 24.8273 | High | Medium | Low | Top | 195 | 330 | 35.4763
UPPER LAKE 1101 | 042871101 | NORTHERN | HUMBOLDT | 57.6996 | 410579 | 44.0754 | 58.66% | 9.214% | 53.33% | 32.16% | 4 | 1 | 25 | 61.24% | 33.46% | 7.415% | 244 | 444 | 0 | 17 | 234 | 147 | 24 | 8 | 16 | 998 | 36.4437 | 128 | 51 | 11 | 325 | 0 | 1 | 25 | 0 | 0.47303 | 13.3397 | 2.6416 | 16.6684 | Medium | High | Low | Top | 252 | 331 | 35.2378
CLARKSVILLE 2103 | 153612103 | NORTHERN | SIERRA | 34.4179 | 1667164.6667 | 43.3111 | 70.71% | 0.1511% | 99.61% | 0% | 2 | 0 | 15 | 99.74% | 0% | 0.8292% | 51 | 364 | 3 | 0 | 119 | 12 | 5 | 3 | 6 | 603 | 49.5714 | 78 | 82 | 9 | 210 | 0 | 0 | 15 | 0 | 0.16045 | 8.0221 | 4.3638 | 5.6169 | Low | Medium | Medium | Mid | 417 | 332 | 35.0065
JAMESON 1102 | 063801102 | NORTHERN | SACRAMENTO | 8.9423 | 874727 | 42.0833 | 31.17% | 0.5673% | 59.84% | 37.25% | 1 | 0 | 10 | 60.41% | 37.25% | 3.226% | 31 | 94 | 4 | 0 | 59 | 10 | 0 | 5 | 5 | 217 | 33.9159 | 29 | 50 | 8 | 113 | 0 | 0 | 10 | 0 | 0.43725 | 5.3375 | 6.5491 | 15.2846 | Medium | Medium | High | Top | 264 | 333 | 34.9562
PINECREST 0401 | 163160401 | CENTRAL VALLEY | YOSEMITE | 2.308 | 17353 | 40.7692 | 123.7% | 100% | 0% | 0% | 1 | 0 | 2 | 100% | 0% | 16.92% | 1 | 7 | 0 | 0 | 70 | 2 | 0 | 1 | 2 | 130 | 8.7308 | 6 | 16 | 0 | 26 | 0 | 0 | 2 | 1 | 0.55994 | 10.7721 | 3.2114 | 19.3702 | Medium | Medium | Low | Top | 236 | 334 | 34.5934
BUCKS CREEK 1102 | 102211102 | NORTHERN | NORTH VALLEY | 29.5609 | 24064 | 45.1628 | 29.42% | 95.12% | 2.32% | 1.332% | 0 | 0 | 20 | 50.06% | 49.94% | 25.17% | 238 | 195 | 1 | 0 | 227 | 74 | 0 | 6 | 19 | 743 | 30.913 | 11 | 11 | 7 | 65 | 0 | 0 | 19 | 0 | 0.42203 | 30.0939 | 1.1382 | 14.4563 | Medium | High | Low | Top | 271 | 335 | 34.254
LINCOLN 1104 | 153701104 | NORTHERN | SIERRA | 41.2963 | 492281.3333 | 41.7903 | 30.03% | 0.6821% | 66.55% | 31.26% | 1 | 0 | 46 | 64.23% | 34.26% | 5.136% | 59 | 400 | 2 | 0 | 64 | 24 | 5 | 8 | 8 | 623 | 30.6027 | 100 | 62 | 1 | 232 | 0 | 0 | 46 | 0 | 0.27935 | 11.8636 | 2.8558 | 9.4642 | Low | Medium | Low | Mid | 338 | 336 | 33.8796
FULTON 1102 | 042561102 | NORTHERN | SONOMA | 32.1618 | 1112538.6667 | 44.0832 | 35.57% | 0.1938% | 71.61% | 16.81% | 0 | 0 | 44 | 72.74% | 16.88% | 9.808% | 116 | 240 | 0 | 6 | 77 | 99 | 0 | 14 | 14 | 469 | 34.1714 | 69 | 28 | 4 | 179 | 0 | 0 | 44 | 0 | 0.25329 | 9.2752 | 3.6516 | 8.5787 | Low | Medium | Low | Mid | 347 | 337 | 33.869
GARBERVILLE 1103 | 192221103 | NORTHERN | HUMBOLDT | 1.5013 | 204302 | 42.7083 | 10.26% | 0% | 22.25% | 56.82% | 0 | 0 | 2 | 18.44% | 72.86% | 25% | 4 | 4 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 24 | 30.2222 | 3 | 3 | 1 | 9 | 0 | 0 | 2 | 1 | 0.51486 | 7.0838 | 4.657 | 16.985 | Medium | Medium | Medium | Top | 249 | 338 | 32.9893
SHINGLE SPRINGS 2109 | 153652109 | NORTHERN | SIERRA | 214.6135 | 1317493.6667 | 43.0853 | 33.47% | 1.045% | 89.27% | 1.473% | 23 | 2 | 292 | 87.98% | 4.051% | 1.234% | 633 | 3363 | 51 | 0 | 597 | 353 | 22 | 31 | 54 | 5269 | 47.94 | 1002 | 638 | 70 | 2194 | 0 | 5 | 292 | 0 | 0.20119 | 7.6038 | 4.3282 | 6.6214 | Low | Medium | Medium | Mid | 389 | 339 | 32.911
ELK 1101 | 042981101 | NORTHERN | HUMBOLDT | 79.6211 | 489185 | 41.2989 | 60.79% | 6.005% | 33.57% | 54.94% | 53 | 1 | 121 | 15.74% | 82.42% | 9.971% | 139 | 456 | 0 | 12 | 372 | 130 | 10 | 13 | 23 | 1364 | 37.1869 | 180 | 35 | 16 | 498 | 0 | 2 | 120 | 1 | 0.76642 | 10.6701 | 3.0792 | 25.1809 | High | Medium | Low | Top | 194 | 340 | 32.8554
GREEN VALLEY 2101 | 083192101 | CENTRAL COAST | CENTRAL COAST | 45.9799 | 1544278.6667 | 43.1863 | 11.38% | 0.1774% | 62.85% | 31.7% | 18 | 0 | 47 | 61.69% | 34.45% | 4.878% | 100 | 383 | 0 | 3 | 245 | 45 | 0 | 11 | 12 | 820 | 47.3034 | 65 | 27 | 9 | 285 | 4 | 0 | 47 | 1 | 0.62633 | 7.1918 | 4.5628 | 20.5529 | Medium | Medium | Medium | Top | 227 | 341 | 32.8148
CAMBRIA 1102 | 182771102 | CENTRAL COAST | LOS PADRES | 19.7066 | 241500.3333 | 42.5837 | 17.92% | 0.2957% | 51.45% | 43.75% | 1 | 0 | 12 | 31.12% | 67.03% | 7.177% | 27 | 4 | 0 | 14 | 108 | 29 | 0 | 3 | 4 | 209 | 32.7 | 20 | 11 | 6 | 62 | 0 | 0 | 11 | 0 | 0.50187 | 7.6706 | 4.246 | 16.3457 | Medium | Medium | Medium | Top | 255 | 342 | 32.5697
LOS OSITOS 2102 | 182082102 | CENTRAL COAST | CENTRAL COAST | 2.7527 | 758740.6667 | 39.7959 | 2.354% | 0% | 71.89% | 19.77% | 0 | 0 | 0 | 71.89% | 19.77% | 10.2% | 0 | 34 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 49 | 1.7778 | 3 | 2 | 0 | 11 | 0 | 0 | 0 | 0 | 0.14359 | 12.2495 | 2.6437 | 4.6502 | Low | Medium | Low | Mid | 445 | 343 | 32.3842
KESWICK 1101 | 103451101 | NORTHERN | NORTH VALLEY | 52.2738 | 367563.6667 | 41.7379 | 46.35% | 52.86% | 31.75% | 1.08% | 4 | 1 | 55 | 82.79% | 13.43% | 8.664% | 177 | 666 | 75 | 0 | 249 | 131 | 0 | 18 | 36 | 1385 | 39.9348 | 136 | 92 | 10 | 367 | 0 | 2 | 54 | 0 | 0.076647 | 6.1074 | 5.2822 | 2.4727 | Low | Medium | Medium | Bottom | 559 | 344 | 32.2605
SHINGLE SPRINGS 2108 | 153652108 | NORTHERN | SIERRA | 15.2009 | 1326514.3333 | 44.2614 | 78.45% | 7.544% | 60.05% | 0% | 1 | 0 | 33 | 67.6% | 0% | 1.989% | 46 | 207 | 0 | 0 | 78 | 27 | 8 | 10 | 20 | 352 | 52.0895 | 76 | 95 | 10 | 195 | 0 | 0 | 33 | 0 | 0.24584 | 5.9973 | 5.3365 | 7.8681 | Low | Medium | Medium | Mid | 363 | 345 | 32.0045
LLAGAS 2104 | 083182104 | CENTRAL COAST | SAN JOSE | 2.9141 | 524502.3333 | 37.2222 | 0% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 0% | 0 | 5 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 27 | 1.4444 | 2 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 0.14492 | 9.7685 | 3.2688 | 4.6274 | Low | Medium | Low | Mid | 446 | 346 | 31.9315
BUELLTON 1102 | 183041102 | CENTRAL COAST | LOS PADRES | 16.9572 | 665292.3333 | 42.7893 | 47.68% | 3.595% | 53.83% | 12.51% | 0 | 0 | 33 | 57.71% | 13.56% | 1.471% | 33 | 33 | 1 | 120 | 98 | 33 | 0 | 8 | 9 | 340 | 25.0917 | 31 | 26 | 3 | 117 | 0 | 0 | 33 | 0 | 0.19293 | 10.1629 | 3.1254 | 6.1282 | Low | Medium | Low | Mid | 401 | 347 | 31.7635
FORT BRAGG A 1104 | 042761104 | NORTHERN | HUMBOLDT | 26.426 | 480870.6667 | 40.9883 | 15% | 1.766% | 23.28% | 69.39% | 11 | 0 | 69 | 22.94% | 76.2% | 7.299% | 45 | 205 | 1 | 2 | 233 | 64 | 28 | 4 | 4 | 685 | 33.2632 | 111 | 50 | 14 | 309 | 0 | 0 | 67 | 0 | 0.69322 | 8.8034 | 3.6033 | 21.9897 | High | Medium | Low | Top | 214 | 348 | 31.7212
JOLON 1102 | 182981102 | CENTRAL COAST | CENTRAL COAST | 69.9647 | 275593 | 42.1747 | 38.06% | 7.302% | 53.86% | 0.2338% | 1 | 0 | 45 | 61.35% | 0.2094% | 15.99% | 79 | 217 | 3 | 16 | 290 | 107 | 16 | 7 | 21 | 807 | 16.48 | 95 | 17 | 1 | 242 | 0 | 0 | 43 | 0 | 0.31963 | 14.6619 | 2.1624 | 10.134 | Low | High | Low | Mid | 329 | 349 | 31.7049
BELL 1107 | 152701107 | NORTHERN | SIERRA | 43.5817 | 1149493 | 42.7907 | 21.07% | 4.099% | 59.89% | 27.58% | 3 | 1 | 32 | 62.47% | 29.1% | 4.949% | 98 | 767 | 2 | 0 | 72 | 54 | 15 | 6 | 9 | 990 | 35.4893 | 196 | 137 | 4 | 433 | 0 | 5 | 32 | 0 | 0.28902 | 7.4759 | 4.2173 | 9.1125 | Low | Medium | Medium | Mid | 342 | 350 | 31.5285
WEIMAR 1101 | 152491101 | NORTHERN | SIERRA | 74.3116 | 525083.6667 | 42.7381 | 26.56% | 51.77% | 33.33% | 7.885% | 9 | 2 | 165 | 76.71% | 19.3% | 9.082% | 218 | 1115 | 16 | 1 | 329 | 188 | 9 | 26 | 37 | 1938 | 35.6812 | 389 | 212 | 19 | 878 | 0 | 2 | 165 | 0 | 0.19673 | 8.2398 | 3.8132 | 6.1813 | Low | Medium | Medium | Mid | 398 | 351 | 31.4198
MONROE 2103 | 043302103 | NORTHERN | SONOMA | 1.5309 | 1768564.3333 | 46.1111 | 4.176% | 0% | 87.86% | 0.1856% | 0 | 0 | 1 | 87.86% | 0.1856% | 11.11% | 2 | 3 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 9 | 24.6667 | 1 | 0 | 0 | 5 | 0 | 0 | 1 | 1 | 0.27354 | 7.2428 | 4.3373 | 8.5931 | Low | Medium | Medium | Mid | 346 | 352 | 31.414
COTTONWOOD 1101 | 102931101 | NORTHERN | NORTH VALLEY | 71.9061 | 576424 | 42.1748 | 0% | 56.03% | 37.89% | 0.2479% | 4 | 0 | 35 | 96.19% | 0.2479% | 5.753% | 89 | 836 | 77 | 0 | 262 | 167 | 0 | 8 | 17 | 1634 | 45.5487 | 178 | 94 | 8 | 435 | 0 | 4 | 35 | 0 | 0.062505 | 11.3331 | 2.7676 | 1.9605 | Low | Medium | Low | Bottom | 607 | 353 | 31.366
PINE GROVE 1101 | 163751101 | CENTRAL VALLEY | STOCKTON | 73.0596 | 1107892.3333 | 41.9271 | 39.09% | 18.75% | 70.66% | 0.8748% | 5 | 4 | 115 | 82.66% | 7.703% | 4.255% | 195 | 996 | 0 | 0 | 410 | 152 | 6 | 11 | 24 | 1833 | 38.345 | 352 | 201 | 11 | 785 | 0 | 1 | 114 | 0 | 0.071362 | 6.2186 | 5.0282 | 2.2314 | Low | Medium | Medium | Bottom | 584 | 354 | 31.2684
FROGTOWN 1702 | 163451702 | CENTRAL VALLEY | STOCKTON | 241.6432 | 1521660.3333 | 42.5691 | 36.1% | 2.94% | 84.05% | 3.711% | 7 | 1 | 127 | 77.02% | 15.61% | 4.634% | 533 | 2297 | 3 | 0 | 982 | 258 | 0 | 22 | 44 | 4618 | 28.5008 | 568 | 205 | 5 | 1292 | 0 | 1 | 127 | 0 | 0.08854 | 6.9375 | 4.5015 | 2.765 | Low | Medium | Medium | Mid | 541 | 355 | 31.2292
SAN JUSTO 1101 | 183181101 | CENTRAL COAST | CENTRAL COAST | 39.4357 | 320395.3333 | 40.7899 | 54.3% | 14.62% | 66.44% | 18.94% | 2 | 0 | 34 | 68.3% | 31.7% | 8.589% | 37 | 192 | 0 | 14 | 245 | 51 | 0 | 7 | 8 | 652 | 15.0843 | 95 | 34 | 2 | 269 | 0 | 0 | 34 | 0 | 0.22829 | 11.5172 | 2.7089 | 7.1225 | Low | Medium | Low | Mid | 378 | 356 | 31.1992
MIDDLETOWN 1102 | 043141102 | NORTHERN | HUMBOLDT | 42.3893 | 840964 | 46.2448 | 73.79% | 20.19% | 67.42% | 0.2889% | 18 | 2 | 19 | 91.88% | 0.2889% | 13.08% | 424 | 602 | 0 | 2 | 97 | 131 | 17 | 15 | 23 | 963 | 52.5093 | 140 | 155 | 64 | 439 | 0 | 0 | 19 | 0 | 0.27312 | 5.8176 | 5.3484 | 8.4981 | Low | Medium | Medium | Mid | 349 | 357 | 31.1148
PENRYN 1103 | 152561103 | NORTHERN | SIERRA | 68.3912 | 559268 | 42.2959 | 34.43% | 1.345% | 64.14% | 23.75% | 9 | 0 | 139 | 65.33% | 24.08% | 5.737% | 137 | 983 | 9 | 4 | 202 | 72 | 0 | 13 | 28 | 1499 | 33.0661 | 294 | 203 | 17 | 639 | 0 | 2 | 139 | 0 | 0.34554 | 6.5132 | 4.7384 | 10.664 | Medium | Medium | Medium | Mid | 321 | 358 | 30.8624
ARCATA 1121 | 192021121 | NORTHERN | HUMBOLDT | 6.8402 | 810260 | 40.963 | 75.92% | 2.883% | 3.664% | 93.45% | 7 | 0 | 10 | 6.547% | 93.45% | 40.74% | 0 | 4 | 0 | 0 | 92 | 7 | 0 | 2 | 2 | 135 | 15.4375 | 9 | 2 | 3 | 33 | 0 | 0 | 10 | 1 | 0.5651 | 7.3201 | 4.2129 | 17.4269 | Medium | Medium | Medium | Top | 245 | 359 | 30.8384
ROSSMOOR 1101 | 014161101 | BAY AREA | DIABLO | 13.7756 | 880452.6667 | 43.5049 | 35.63% | 0% | 32.74% | 48.49% | 26 | 2 | 40 | 24.8% | 56.42% | 11.17% | 73 | 90 | 0 | 0 | 193 | 19 | 9 | 5 | 12 | 412 | 17.5174 | 34 | 103 | 33 | 208 | 0 | 0 | 40 | 0 | 0.74002 | 5.1737 | 5.9514 | 22.786 | High | Medium | High | Top | 209 | 360 | 30.7909
LLAGAS 2101 | 083182101 | CENTRAL COAST | SAN JOSE | 23.8607 | 1657473.3333 | 42.5 | 7.639% | 1.247% | 96.57% | 2.004% | 0 | 0 | 23 | 95.36% | 4.461% | 6.984% | 44 | 131 | 0 | 14 | 97 | 14 | 0 | 4 | 4 | 315 | 24.1212 | 14 | 14 | 1 | 83 | 0 | 0 | 22 | 0 | 0.19551 | 9.3367 | 3.2614 | 5.9535 | Low | Medium | Low | Mid | 407 | 361 | 30.4511
TYLER 1105 | 103571105 | NORTHERN | NORTH VALLEY | 62.3352 | 607112 | 41.0656 | 34.33% | 0.1812% | 99.82% | 0% | 3 | 0 | 26 | 100% | 0% | 6.205% | 53 | 627 | 28 | 2 | 222 | 94 | 0 | 7 | 8 | 1241 | 43.4947 | 118 | 44 | 3 | 295 | 0 | 0 | 26 | 0 | 0.096827 | 14.6898 | 2.0602 | 2.9304 | Low | High | Low | Mid | 531 | 362 | 30.2643
HOPLAND 1101 | 042251101 | NORTHERN | HUMBOLDT | 91.6366 | 662550 | 44.0373 | 35.32% | 10.05% | 75.48% | 12.02% | 2 | 0 | 44 | 80.88% | 16.66% | 13.03% | 257 | 408 | 1 | 4 | 291 | 150 | 0 | 5 | 7 | 1305 | 42.4963 | 142 | 55 | 15 | 433 | 0 | 0 | 44 | 0 | 0.08993 | 13.7277 | 2.1763 | 2.6867 | Low | High | Low | Bottom | 547 | 363 | 29.8751
CURTIS 1705 | 163351705 | CENTRAL VALLEY | YOSEMITE | 84.8308 | 1039972 | 42.2644 | 0% | 22.69% | 56.89% | 4.67% | 6 | 1 | 144 | 78.75% | 14.77% | 3.447% | 333 | 1290 | 3 | 0 | 509 | 164 | 1 | 21 | 38 | 2321 | 22.3541 | 465 | 262 | 30 | 1105 | 0 | 0 | 142 | 0 | 0.12924 | 4.6492 | 6.3526 | 3.8172 | Low | Medium | High | Mid | 483 | 364 | 29.5347
FELTON 0401 | 083140401 | CENTRAL COAST | CENTRAL COAST | 2.536 | 8693 | 50 | 0% | 0% | 4.149% | 13.64% | 3 | 0 | 3 | 4.149% | 95.85% | 27.12% | 41 | 12 | 0 | 1 | 23 | 15 | 3 | 2 | 4 | 59 | 22 | 5 | 4 | 2 | 13 | 0 | 0 | 3 | 1 | 0.68495 | 3.6103 | 8.0992 | 20.0282 | High | Medium | High | Top | 231 | 365 | 29.2403
GABILAN 1101 | 182331101 | CENTRAL COAST | CENTRAL COAST | 7.2565 | 1406118.6667 | 39.9038 | 10.48% | 0% | 59.09% | 36.3% | 1 | 0 | 2 | 57.88% | 42.12% | 5.769% | 1 | 14 | 0 | 0 | 22 | 1 | 0 | 0 | 0 | 52 | 5.6316 | 5 | 3 | 0 | 22 | 0 | 0 | 2 | 0 | 0.28754 | 9.9013 | 2.9325 | 8.3491 | Low | Medium | Low | Mid | 353 | 366 | 29.0357
EMERALD LAKE 0401 | 024080401 | CENTRAL COAST | PENINSULA | 16.2767 | 245797.3333 | 43.1377 | 58.16% | 0% | 36.54% | 38.06% | 9 | 0 | 30 | 30.34% | 69.37% | 12.19% | 40 | 187 | 0 | 2 | 178 | 21 | 17 | 1 | 10 | 443 | 41.52 | 30 | 86 | 25 | 177 | 3 | 0 | 29 | 0 | 0.71426 | 3.2162 | 8.9033 | 20.4527 | High | Medium | High | Top | 229 | 367 | 28.6349
VOLTA 1101 | 102541101 | NORTHERN | NORTH VALLEY | 153.1533 | 261975 | 40.4718 | 0% | 46.76% | 42.24% | 1.944% | 41 | 5 | 114 | 89.01% | 4.004% | 12% | 220 | 1320 | 54 | 1 | 1004 | 244 | 32 | 34 | 59 | 3375 | 42.5214 | 244 | 96 | 23 | 635 | 0 | 9 | 113 | 0 | 0.28746 | 11.8539 | 2.3935 | 8.1561 | Low | Medium | Low | Mid | 354 | 368 | 28.3727
CURTIS 1701 | 163351701 | CENTRAL VALLEY | YOSEMITE | 14.8035 | 1423665 | 43.9225 | 0% | 0% | 42.83% | 18.88% | 1 | 1 | 10 | 42.78% | 22.21% | 6.731% | 109 | 165 | 0 | 0 | 118 | 44 | 1 | 4 | 13 | 416 | 29.8258 | 47 | 51 | 10 | 168 | 0 | 0 | 10 | 0 | 0.41835 | 4.74 | 5.9345 | 11.7678 | Medium | Medium | High | Mid | 307 | 369 | 28.1292
MARIPOSA 2101 | 254452101 | CENTRAL VALLEY | YOSEMITE | 261.3822 | 909338.6667 | 40.3495 | 0% | 86.47% | 8.223% | 0.9472% | 8 | 3 | 223 | 84.61% | 12.03% | 23.6% | 172 | 1687 | 14 | 1 | 1903 | 292 | 5 | 33 | 54 | 5687 | 38.1209 | 914 | 417 | 33 | 2249 | 0 | 4 | 215 | 0 | 0.13837 | 9.8502 | 2.8455 | 3.8783 | Low | Medium | Low | Mid | 482 | 370 | 28.029
VALLEY VIEW 1103 | 014341103 | BAY AREA | EAST BAY | 0.6427 | 857099 | 46.3636 | 0% | 86.99% | 0% | 4.309% | 0 | 0 | 0 | 0% | 91.3% | 0% | 4 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 11 | 0 | 1 | 3 | 0 | 4 | 0 | 0 | 0 | 0 | 0.18394 | 3.6934 | 7.5586 | 5.135 | Low | Medium | High | Mid | 429 | 371 | 27.917
TEJON 1102 | 252931102 | CENTRAL VALLEY | KERN | 34.9658 | 1275225.3333 | 42.4099 | 62.49% | 81.27% | 8.228% | 1.952% | 0 | 0 | 41 | 69.41% | 30.2% | 26.76% | 44 | 41 | 0 | 38 | 314 | 55 | 0 | 2 | 10 | 751 | 9.85 | 83 | 57 | 12 | 241 | 0 | 0 | 41 | 0 | 0.27617 | 6.3453 | 4.3844 | 7.6832 | Low | Medium | Medium | Mid | 364 | 372 | 27.8208
SAN RAMON 2102 | 014232102 | CENTRAL COAST | MISSION | 1.7607 | 1716244.3333 | 52.1053 | 451.9% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 10.53% | 17 | 10 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25132 | 4.0028 | 6.8359 | 6.8768 | Low | Medium | High | Mid | 384 | 373 | 27.3627
OROVILLE 1104 | 102521104 | NORTHERN | NORTH VALLEY | 0.28474 | 627607.3333 | 0 | 4.031% | 0% | 65.82% | 34.18% | 0 | 0 | 0 | 65.82% | 34.18% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17896 | 4.4448 | 6.1103 | 4.8605 | Low | Medium | High | Mid | 439 | 374 | 27.1591
IGNACIO 1101 | 042481101 | BAY AREA | NORTH BAY | 6.5242 | 913608.6667 | 45.6085 | 64.41% | 0% | 54.92% | 0% | 3 | 0 | 19 | 54.92% | 0% | 2.105% | 46 | 29 | 0 | 1 | 98 | 31 | 0 | 8 | 13 | 190 | 27.4898 | 6 | 21 | 14 | 53 | 0 | 0 | 19 | 0 | 0.40325 | 3.9009 | 6.9266 | 10.8959 | Medium | Medium | High | Mid | 317 | 375 | 27.0201
DIAMOND SPRINGS 1105 | 152261105 | NORTHERN | SIERRA | 128.5585 | 751877.6667 | 42.8131 | 36.02% | 7.677% | 75.25% | 4.002% | 11 | 3 | 137 | 81.54% | 5.39% | 2.246% | 384 | 1714 | 55 | 0 | 378 | 184 | 1 | 15 | 25 | 2939 | 42.0833 | 562 | 322 | 27 | 1100 | 0 | 3 | 137 | 0 | 0.089201 | 6.585 | 4.0987 | 2.4075 | Low | Medium | Medium | Bottom | 568 | 376 | 26.9898
CASTRO VALLEY 1101 | 014091101 | CENTRAL COAST | MISSION | 3.4212 | 992296.6667 | 43.9216 | 25.37% | 0% | 45.71% | 10.04% | 8 | 4 | 0 | 36.26% | 19.49% | 3.922% | 4 | 9 | 0 | 0 | 40 | 1 | 0 | 1 | 2 | 51 | 5.6667 | 0 | 6 | 0 | 12 | 0 | 0 | 0 | 0 | 0.45379 | 4.2248 | 6.38 | 12.2315 | Medium | Medium | High | Mid | 300 | 377 | 26.9542
CLAY 1103 | 163341103 | CENTRAL VALLEY | STOCKTON | 56.3815 | 626730 | 44.3689 | 132.9% | 4.832% | 80.45% | 0.3339% | 2 | 3 | 25 | 73.75% | 13.44% | 7.906% | 199 | 436 | 0 | 0 | 264 | 92 | 0 | 8 | 23 | 936 | 32.4372 | 69 | 37 | 3 | 193 | 0 | 1 | 25 | 0 | 0.145 | 5.6318 | 4.7711 | 3.8961 | Low | Medium | Medium | Mid | 481 | 378 | 26.8697
SHINGLE SPRINGS 1103 | 153651103 | NORTHERN | SIERRA | 9.0287 | 773103 | 45.0222 | 26.7% | 0% | 80.57% | 0.4649% | 2 | 0 | 9 | 80.57% | 0.4649% | 0.8889% | 60 | 117 | 1 | 0 | 68 | 26 | 0 | 5 | 11 | 225 | 55.6071 | 32 | 63 | 6 | 112 | 0 | 0 | 9 | 0 | 0.21868 | 5.1181 | 5.2475 | 5.873 | Low | Medium | Medium | Mid | 409 | 379 | 26.8572
SAN JOAQUIN #3 1101 | 252531101 | CENTRAL VALLEY | YOSEMITE | 24.668 | 0 | 39.9922 | 292.2% | 69.68% | 6.734% | 0.7802% | 2 | 1 | 22 | 82.86% | 15.1% | 21.01% | 46 | 50 | 0 | 0 | 297 | 71 | 4 | 19 | 25 | 652 | 32.3179 | 35 | 44 | 18 | 160 | 0 | 0 | 22 | 0 | 0.36647 | 8.251 | 3.1698 | 9.5846 | Medium | Medium | Low | Mid | 337 | 380 | 26.1541
OCEANO 1104 | 182601104 | CENTRAL COAST | LOS PADRES | 93.0178 | 1243391 | 41.8747 | 18.26% | 2.748% | 57.26% | 30.7% | 15 | 0 | 170 | 56.75% | 38.65% | 7.593% | 210 | 193 | 0 | 329 | 915 | 166 | 3 | 32 | 45 | 2173 | 27.9753 | 351 | 139 | 19 | 934 | 0 | 2 | 169 | 0 | 0.58112 | 5.4309 | 4.7955 | 15.1348 | Medium | Medium | Medium | Top | 266 | 381 | 26.0441
CENTERVILLE 1101 | 102021101 | NORTHERN | NORTH VALLEY | 36.3928 | 119772.6667 | 44.4126 | 21.95% | 6.43% | 65.78% | 18.73% | 13 | 1 | 0 | 65.79% | 25.15% | 6.933% | 159 | 312 | 1 | 0 | 100 | 67 | 2 | 0 | 0 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44045 | 4.0581 | 6.3214 | 11.2989 | Medium | Medium | High | Mid | 313 | 382 | 25.6533
SALT SPRINGS 2101 | 163692101 | CENTRAL VALLEY | STOCKTON | 16.0684 | 59288.6667 | 46.2035 | 33.03% | 44.28% | 3.125% | 0% | 1 | 1 | 16 | 99.78% | 0.1926% | 3.462% | 268 | 290 | 0 | 0 | 109 | 22 | 0 | 4 | 14 | 520 | 28.3106 | 68 | 15 | 2 | 137 | 0 | 2 | 16 | 1 | 0.4829 | 15.8942 | 1.5862 | 12.1744 | Medium | High | Low | Mid | 301 | 383 | 25.2111
ALTO 1122 | 042031122 | BAY AREA | NORTH BAY | 9.2369 | 541722.3333 | 43.7024 | 21.44% | 0% | 26.32% | 46.46% | 6 | 2 | 17 | 26.28% | 58.56% | 9.176% | 75 | 80 | 9 | 4 | 167 | 97 | 23 | 2 | 8 | 425 | 30.0855 | 42 | 45 | 17 | 155 | 0 | 0 | 17 | 1 | 0.78086 | 3.4502 | 7.3044 | 19.6788 | High | Medium | High | Top | 234 | 384 | 25.2014
SANTA ROSA A 1104 | 042151104 | NORTHERN | SONOMA | 44.9934 | 1003317.3333 | 44.2131 | 27.46% | 0.08983% | 67.49% | 14.7% | 3 | 2 | 120 | 69.48% | 14.7% | 6.934% | 264 | 505 | 0 | 9 | 283 | 151 | 2 | 31 | 43 | 1024 | 35.1076 | 213 | 127 | 23 | 511 | 0 | 3 | 120 | 1 | 0.28997 | 5.9898 | 4.1716 | 7.2455 | Low | Medium | Medium | Mid | 373 | 385 | 24.9871
SAUSALITO 1102 | 042491102 | BAY AREA | NORTH BAY | 8.7614 | 820352.6667 | 43.0369 | 19.47% | 4.189% | 12.46% | 42.41% | 4 | 1 | 17 | 11.63% | 73.47% | 4.362% | 40 | 44 | 0 | 1 | 202 | 22 | 0 | 10 | 15 | 298 | 35.0161 | 24 | 14 | 5 | 63 | 0 | 0 | 17 | 1 | 0.73232 | 4.1671 | 5.9676 | 18.2113 | High | Medium | High | Top | 244 | 386 | 24.8678
WHEATLAND 1105 | 152811105 | NORTHERN | SIERRA | 11.3149 | 387985.6667 | 45.3867 | 35.01% | 0% | 100% | 0% | 0 | 0 | 2 | 100% | 0% | 4.972% | 46 | 95 | 2 | 0 | 15 | 14 | 0 | 2 | 2 | 181 | 33.1633 | 31 | 6 | 0 | 53 | 0 | 0 | 2 | 0 | 0.18863 | 9.212 | 2.6356 | 4.5799 | Low | Medium | Low | Mid | 447 | 387 | 24.2792
OAKLAND D 1112 | 012041112 | BAY AREA | EAST BAY | 2.7059 | 1308951.6667 | 45.1087 | 8.874% | 25.7% | 11.84% | 33.9% | 2 | 0 | 8 | 29.52% | 62.52% | 36.96% | 30 | 14 | 0 | 0 | 43 | 16 | 6 | 6 | 9 | 92 | 11.6923 | 8 | 7 | 5 | 29 | 0 | 0 | 8 | 0 | 0.66632 | 3.5155 | 6.8847 | 16.1272 | High | Medium | High | Top | 257 | 388 | 24.2033
RED BLUFF 1104 | 103541104 | NORTHERN | NORTH VALLEY | 71.2322 | 647331.3333 | 41.8722 | 81.92% | 12.93% | 72.82% | 6.502% | 2 | 4 | 34 | 89.91% | 6.617% | 6.063% | 115 | 516 | 48 | 0 | 265 | 136 | 0 | 12 | 19 | 1336 | 44.7473 | 168 | 110 | 10 | 386 | 0 | 4 | 34 | 0 | 0.041784 | 7.4316 | 3.1769 | 0.98649 | Low | Medium | Low | Bottom | 712 | 389 | 23.6094
PEORIA 1704 | 163781704 | CENTRAL VALLEY | YOSEMITE | 69.8555 | 1152041.6667 | 42.2251 | 0% | 1.12% | 67.14% | 0.2721% | 2 | 1 | 42 | 66.78% | 16.39% | 5.376% | 215 | 651 | 0 | 0 | 269 | 197 | 0 | 14 | 36 | 1358 | 44.3532 | 198 | 105 | 11 | 425 | 0 | 0 | 41 | 0 | 0.15653 | 5.0902 | 4.6091 | 3.6724 | Low | Medium | Medium | Mid | 492 | 390 | 23.4613
ALTO 1120 | 042031120 | BAY AREA | NORTH BAY | 2.732 | 1013554.6667 | 43.4375 | 5.513% | 0% | 65.93% | 34.07% | 2 | 0 | 11 | 2.494% | 97.51% | 7.692% | 24 | 34 | 2 | 1 | 49 | 18 | 0 | 2 | 7 | 130 | 31.3889 | 8 | 16 | 0 | 37 | 0 | 0 | 11 | 1 | 0.65076 | 3.266 | 7.0337 | 14.9492 | Medium | Medium | High | Top | 270 | 391 | 22.9719
SPRUCE 0401 | 013340401 | BAY AREA | EAST BAY | 4.123 | 83704.6667 | 44.7953 | 34.2% | 0% | 40.19% | 28.52% | 3 | 0 | 12 | 7.456% | 66% | 65.7% | 22 | 15 | 0 | 0 | 35 | 4 | 2 | 3 | 8 | 172 | 45.7818 | 6 | 24 | 14 | 55 | 0 | 0 | 12 | 1 | 0.7654 | 2.5009 | 9.038 | 17.3002 | High | Medium | High | Top | 246 | 392 | 22.6029
CLARK ROAD 1102 | 103091102 | NORTHERN | NORTH VALLEY | 126.4512 | 506713.6667 | 42.3085 | 57.53% | 1.404% | 83.59% | 7.319% | 3 | 1 | 107 | 80.81% | 13.46% | 6.255% | 237 | 1205 | 59 | 0 | 355 | 171 | 4 | 28 | 42 | 2510 | 42.8078 | 336 | 133 | 7 | 730 | 0 | 13 | 104 | 0 | 0.047318 | 4.2677 | 5.2944 | 1.0692 | Low | Medium | Medium | Bottom | 700 | 393 | 22.5952
PEABODY 2108 | 063642108 | NORTHERN | SACRAMENTO | 0.94269 | 1304830.6667 | 41.4286 | 296.8% | 0% | 50.32% | 1.388% | 0 | 0 | 0 | 50.32% | 1.388% | 0% | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 56.6667 | 1 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.21045 | 5.4692 | 4.1289 | 4.7523 | Low | Medium | Medium | Mid | 441 | 394 | 22.5819
CALAVERAS CEMENT 1101 | 162211101 | CENTRAL VALLEY | STOCKTON | 192.3056 | 882692.6667 | 43.0491 | 42.52% | 48.89% | 42.65% | 1.271% | 10 | 1 | 229 | 86.35% | 7.593% | 6.122% | 504 | 1805 | 8 | 0 | 1129 | 294 | 0 | 32 | 66 | 3822 | 26.369 | 644 | 228 | 15 | 1430 | 0 | 8 | 227 | 0 | 0.12984 | 5.1692 | 4.3663 | 2.9306 | Low | Medium | Medium | Mid | 530 | 395 | 22.5704
JOLON 1103 | 182981103 | CENTRAL COAST | CENTRAL COAST | 15.4705 | 0 | 44.0179 | 220.2% | 7.902% | 35.28% | 0.9642% | 0 | 0 | 3 | 43.18% | 0.9642% | 23.21% | 11 | 16 | 0 | 0 | 20 | 10 | 0 | 2 | 4 | 56 | 16.1667 | 2 | 0 | 0 | 8 | 0 | 0 | 3 | 0 | 0.43911 | 14.1831 | 1.5867 | 9.882 | Medium | High | Low | Mid | 332 | 396 | 22.5043
PEORIA 1705 | 163781705 | CENTRAL VALLEY | YOSEMITE | 61.6661 | 839391 | 43.4978 | 0% | 0.3851% | 69.22% | 7.749% | 2 | 1 | 58 | 68.93% | 10.16% | 3.057% | 243 | 767 | 1 | 0 | 254 | 114 | 4 | 10 | 24 | 1374 | 25.0452 | 203 | 90 | 10 | 516 | 0 | 0 | 58 | 0 | 0.12715 | 4.6382 | 4.8512 | 2.861 | Low | Medium | Medium | Mid | 534 | 397 | 22.5006
LAURELES 1112 | 182371112 | CENTRAL COAST | CENTRAL COAST | 29.5797 | 437175.6667 | 40.7037 | 11.39% | 0.561% | 42.14% | 30.11% | 8 | 3 | 43 | 23.27% | 67.16% | 6.657% | 38 | 169 | 0 | 20 | 340 | 30 | 0 | 7 | 10 | 676 | 15.813 | 83 | 73 | 12 | 265 | 4 | 0 | 43 | 1 | 0.71132 | 5.2747 | 4.1937 | 15.7349 | High | Medium | Medium | Top | 261 | 398 | 22.1207
SAN MIGUEL 1104 | 182661104 | CENTRAL COAST | LOS PADRES | 26.5441 | 1053624 | 41.345 | 83.2% | 0.2016% | 98.92% | 0.3796% | 0 | 1 | 12 | 99.4% | 0.5812% | 1.754% | 15 | 76 | 0 | 67 | 100 | 34 | 0 | 8 | 11 | 342 | 46.8646 | 41 | 19 | 2 | 100 | 0 | 1 | 11 | 0 | 0.19154 | 7.5083 | 2.911 | 4.1865 | Low | Medium | Low | Mid | 470 | 399 | 21.857
PAUL SWEET 2107 | 083252107 | CENTRAL COAST | CENTRAL COAST | 11.6036 | 2229446.6667 | 42.5758 | 6.567% | 0.3399% | 48.7% | 19.85% | 0 | 1 | 9 | 48.7% | 43.43% | 8.333% | 20 | 32 | 0 | 3 | 53 | 8 | 0 | 5 | 5 | 132 | 26.3478 | 15 | 4 | 1 | 52 | 0 | 0 | 9 | 1 | 0.65913 | 3.567 | 6.0734 | 14.279 | Medium | Medium | High | Top | 273 | 400 | 21.6634
SOBRANTE 1102 | 014671102 | BAY AREA | DIABLO | 27.4867 | 665912.3333 | 44.9287 | 44.98% | 1.018% | 33.4% | 36.09% | 6 | 2 | 107 | 30.18% | 40.33% | 15.56% | 198 | 196 | 1 | 1 | 310 | 33 | 0 | 11 | 20 | 771 | 25.2005 | 84 | 205 | 53 | 411 | 0 | 0 | 107 | 1 | 0.57577 | 3.4775 | 6.2088 | 12.4314 | Medium | Medium | High | Mid | 299 | 401 | 21.5911
SAN LUIS OBISPO 1108 | 182631108 | CENTRAL COAST | LOS PADRES | 2.4048 | 1467656 | 43.3696 | 112.3% | 0% | 23.43% | 14.17% | 0 | 0 | 2 | 23.43% | 14.17% | 0% | 3 | 2 | 0 | 3 | 10 | 1 | 0 | 1 | 1 | 47 | 28.8889 | 2 | 3 | 1 | 11 | 0 | 0 | 2 | 0 | 0.31519 | 3.9129 | 5.4833 | 6.7626 | Low | Medium | High | Mid | 386 | 402 | 21.4555
CLAY 1101 | 163341101 | CENTRAL VALLEY | STOCKTON | 27.9248 | 622525 | 43.6759 | 32.66% | 0.6155% | 97.09% | 2.108% | 3 | 0 | 16 | 94.58% | 5.239% | 7.011% | 95 | 282 | 1 | 0 | 100 | 62 | 0 | 1 | 6 | 542 | 31.2308 | 71 | 41 | 1 | 162 | 0 | 1 | 16 | 0 | 0.13945 | 4.2814 | 4.9572 | 2.9597 | Low | Medium | Medium | Mid | 529 | 403 | 21.2237
IONE 1101 | 163881101 | CENTRAL VALLEY | STOCKTON | 16.9978 | 1124748.3333 | 42.5714 | 71.69% | 0% | 94.02% | 0% | 0 | 0 | 7 | 87.97% | 6.052% | 4.082% | 21 | 100 | 0 | 0 | 65 | 44 | 0 | 1 | 3 | 245 | 36.0345 | 26 | 12 | 2 | 61 | 0 | 0 | 7 | 0 | 0.17819 | 4.7899 | 4.4058 | 3.7604 | Low | Medium | Medium | Mid | 486 | 404 | 21.1036
DESCHUTES 1104 | 103351104 | NORTHERN | NORTH VALLEY | 84.9328 | 1165655 | 42.729 | 16.73% | 67.16% | 28.77% | 0% | 9 | 0 | 72 | 95.93% | 0% | 5.745% | 202 | 1450 | 45 | 1 | 180 | 201 | 0 | 6 | 12 | 2141 | 42.7229 | 367 | 252 | 14 | 810 | 0 | 1 | 72 | 0 | 0.12323 | 4.8181 | 4.3552 | 2.5858 | Low | Medium | Medium | Bottom | 554 | 405 | 20.9837
GONZALES 1103 | 182131103 | CENTRAL COAST | CENTRAL COAST | 1.7723 | 932805 | 41.4286 | 3.265% | 0% | 39.15% | 60.85% | 0 | 0 | 3 | 39.15% | 60.85% | 23.81% | 1 | 7 | 0 | 0 | 4 | 7 | 0 | 1 | 1 | 21 | 30.8 | 5 | 0 | 0 | 11 | 0 | 0 | 3 | 0 | 0.4298 | 16.4522 | 1.2676 | 8.9637 | Medium | High | Low | Mid | 344 | 406 | 20.8553
CORRAL 1102 | 162991102 | CENTRAL VALLEY | STOCKTON | 51.2858 | 770762.3333 | 43.7391 | 73.37% | 0.5883% | 75.4% | 11.43% | 1 | 0 | 44 | 75.99% | 11.43% | 10.18% | 304 | 620 | 6 | 0 | 249 | 103 | 0 | 3 | 11 | 1267 | 32.2722 | 252 | 174 | 9 | 533 | 0 | 0 | 44 | 0 | 0.050231 | 3.8123 | 5.4683 | 1.0472 | Low | Medium | High | Bottom | 705 | 407 | 20.8467
ELECTRA 1101 | 162161101 | CENTRAL VALLEY | STOCKTON | 83.4541 | 732194.6667 | 42.3763 | 57.61% | 18.69% | 62.3% | 5.245% | 4 | 4 | 67 | 75.96% | 16.77% | 4.972% | 287 | 1122 | 1 | 0 | 569 | 155 | 7 | 15 | 40 | 2112 | 34.6052 | 346 | 188 | 13 | 750 | 0 | 1 | 67 | 0 | 0.099441 | 4.1963 | 4.9111 | 2.0493 | Low | Medium | Medium | Bottom | 600 | 408 | 20.6084
OTTER 1102 | 182941102 | CENTRAL COAST | CENTRAL COAST | 54.0889 | 233793.3333 | 39.8005 | 123.4% | 8.731% | 59.84% | 22.32% | 11 | 5 | 91 | 6.951% | 86.82% | 6.049% | 36 | 192 | 0 | 9 | 272 | 25 | 2 | 30 | 44 | 777 | 27.0575 | 88 | 39 | 11 | 241 | 0 | 1 | 90 | 1 | 0.67709 | 6.6789 | 3.0669 | 13.8692 | High | Medium | Low | Mid | 279 | 409 | 20.4837
CALPELLA 1101 | 043411101 | NORTHERN | HUMBOLDT | 75.2133 | 522431.6667 | 44.3029 | 62.5% | 17.24% | 64.05% | 5.835% | 5 | 4 | 59 | 85.31% | 6.852% | 7.756% | 310 | 466 | 0 | 3 | 307 | 149 | 0 | 10 | 16 | 1212 | 42.6318 | 187 | 82 | 11 | 459 | 0 | 0 | 59 | 0 | 0.11846 | 8.5089 | 2.3965 | 2.4155 | Low | Medium | Low | Bottom | 567 | 410 | 20.3913
ELK CREEK 1101 | 102781101 | NORTHERN | NORTH VALLEY | 97.876 | 245296.6667 | 39.9527 | 127.2% | 13.18% | 86.8% | 0% | 2 | 0 | 36 | 99.97% | 0% | 7.708% | 28 | 792 | 4 | 0 | 246 | 95 | 0 | 14 | 21 | 1479 | 40.4424 | 87 | 36 | 5 | 233 | 0 | 3 | 36 | 0 | 0.10469 | 25.9335 | 0.78561 | 2.1329 | Low | High | Low | Bottom | 591 | 411 | 20.3736
CORRAL 1103 | 162991103 | CENTRAL VALLEY | STOCKTON | 25.6729 | 706934 | 42.1524 | 46.13% | 0.08536% | 87.47% | 0% | 5 | 0 | 8 | 87.55% | 0% | 9.715% | 96 | 357 | 0 | 0 | 128 | 45 | 0 | 1 | 3 | 597 | 47.5245 | 156 | 93 | 2 | 288 | 0 | 0 | 8 | 0 | 0.1131 | 3.2436 | 6.2602 | 2.2966 | Low | Medium | High | Bottom | 583 | 412 | 20.3056
NEWBURG 1133 | 192151133 | NORTHERN | HUMBOLDT | 4.5902 | 104146 | 41.5217 | 18.35% | 0% | 39.51% | 25.94% | 0 | 0 | 3 | 39.51% | 48.81% | 63.04% | 7 | 0 | 0 | 0 | 36 | 4 | 0 | 1 | 1 | 46 | 12 | 6 | 0 | 0 | 16 | 0 | 0 | 3 | 1 | 0.62446 | 7.44 | 2.7149 | 12.6134 | Medium | Medium | Low | Mid | 294 | 413 | 20.1989
SONOMA 1103 | 042721103 | NORTHERN | SONOMA | 14.1173 | 720886.6667 | 44.0377 | 30.67% | 0% | 95.21% | 4.746% | 1 | 3 | 9 | 90.87% | 9.088% | 5.021% | 47 | 166 | 0 | 0 | 29 | 10 | 1 | 5 | 5 | 239 | 47.1702 | 32 | 22 | 3 | 97 | 0 | 0 | 8 | 0 | 0.22636 | 3.9482 | 5.1063 | 4.5635 | Low | Medium | Medium | Mid | 448 | 414 | 20.1607
ZACA 1101 | 182681101 | CENTRAL COAST | LOS PADRES | 20.191 | 337919.3333 | 44.3945 | 56.26% | 29.52% | 40.55% | 20% | 1 | 0 | 18 | 41.83% | 48.93% | 9.966% | 62 | 17 | 1 | 56 | 100 | 47 | 0 | 6 | 8 | 291 | 31.8769 | 11 | 8 | 3 | 69 | 0 | 0 | 18 | 0 | 0.36334 | 9.9161 | 2.025 | 7.2959 | Medium | Medium | Low | Mid | 371 | 415 | 20.0798
PEORIA 1701 | 163781701 | CENTRAL VALLEY | YOSEMITE | 80.9793 | 522460 | 43.7626 | 0% | 41.46% | 28.14% | 2.464% | 6 | 3 | 94 | 70.58% | 3.53% | 4.754% | 408 | 811 | 3 | 0 | 296 | 287 | 10 | 9 | 35 | 1704 | 28.1064 | 256 | 177 | 21 | 684 | 0 | 0 | 93 | 0 | 0.18788 | 4.3409 | 4.6157 | 3.7645 | Low | Medium | Medium | Mid | 485 | 416 | 20.0363
HIGGINS 1109 | 152691109 | NORTHERN | SIERRA | 140.9716 | 609072.3333 | 43.312 | 37.7% | 4.367% | 88.44% | 1.787% | 5 | 0 | 164 | 92.68% | 1.939% | 15.2% | 162 | 1680 | 11 | 0 | 219 | 382 | 10 | 17 | 27 | 2894 | 37.946 | 519 | 279 | 22 | 1112 | 0 | 4 | 164 | 0 | 0.071544 | 5.1067 | 3.9221 | 1.433 | Low | Medium | Medium | Bottom | 666 | 417 | 20.0289
GREENBRAE 1103 | 043091103 | BAY AREA | NORTH BAY | 5.5389 | 1089266 | 43.1922 | 9.46% | 0% | 32.68% | 65.01% | 10 | 1 | 8 | 32.68% | 66.45% | 9.091% | 43 | 79 | 5 | 1 | 113 | 79 | 9 | 1 | 1 | 308 | 26.4937 | 21 | 29 | 16 | 83 | 0 | 0 | 8 | 1 | 0.83128 | 2.375 | 8.3516 | 16.4882 | High | Low | High | Top | 254 | 418 | 19.8346
HARRIS 1108 | 192431108 | NORTHERN | HUMBOLDT | 3.1677 | 1162559 | 42.2794 | 22.21% | 0% | 19.91% | 79.84% | 0 | 0 | 7 | 20.16% | 79.84% | 26.47% | 5 | 6 | 0 | 1 | 49 | 3 | 0 | 1 | 2 | 68 | 23.3846 | 8 | 7 | 0 | 26 | 0 | 0 | 7 | 0 | 0.55493 | 2.6375 | 7.4912 | 10.9641 | Medium | Medium | High | Mid | 316 | 419 | 19.7578
CORNING 1101 | 103331101 | NORTHERN | NORTH VALLEY | 51.4057 | 1242662 | 40.5836 | 65.5% | 83.56% | 2.678% | 0% | 1 | 2 | 36 | 94.64% | 0% | 4.807% | 42 | 760 | 57 | 0 | 81 | 72 | 18 | 11 | 14 | 1269 | 52.7519 | 233 | 88 | 8 | 543 | 0 | 1 | 36 | 0 | 0.118 | 4.8595 | 4.0295 | 2.3106 | Low | Medium | Medium | Bottom | 581 | 420 | 19.5816
STAFFORD 1101 | 043201101 | BAY AREA | NORTH BAY | 8.5838 | 1056111 | 43.9262 | 27.29% | 0% | 66.95% | 10.79% | 1 | 0 | 13 | 66.95% | 10.79% | 4.878% | 38 | 49 | 3 | 0 | 46 | 23 | 0 | 5 | 9 | 123 | 28.2273 | 15 | 16 | 5 | 45 | 0 | 0 | 13 | 1 | 0.41419 | 3.3148 | 5.8841 | 8.0787 | Medium | Medium | High | Mid | 358 | 421 | 19.5047
SHINGLE SPRINGS 2110 | 153652110 | NORTHERN | SIERRA | 63.9953 | 1226260.6667 | 42.4151 | 45.26% | 0.2067% | 83.25% | 5.136% | 7 | 0 | 83 | 83.46% | 5.097% | 2.134% | 173 | 1013 | 12 | 0 | 308 | 69 | 13 | 15 | 27 | 1593 | 42.395 | 338 | 181 | 15 | 644 | 0 | 6 | 83 | 0 | 0.050897 | 4.0293 | 4.7906 | 0.98245 | Low | Medium | Medium | Bottom | 715 | 422 | 19.3026
OREGON TRAIL 1104 | 103521104 | NORTHERN | NORTH VALLEY | 46.6336 | 454202.6667 | 42.6543 | 48.06% | 45.35% | 41.08% | 0.05981% | 0 | 0 | 64 | 86.28% | 0.2109% | 7.73% | 129 | 714 | 12 | 0 | 194 | 96 | 0 | 5 | 9 | 1216 | 42.5193 | 178 | 122 | 9 | 458 | 0 | 2 | 64 | 0 | 0.032789 | 4.4935 | 4.2518 | 0.62645 | Low | Medium | Medium | Bottom | 752 | 423 | 19.1052
ATASCADERO 1101 | 182541101 | CENTRAL COAST | LOS PADRES | 48.5498 | 1006188.3333 | 41.4182 | 24.47% | 0% | 78.63% | 16.95% | 10 | 5 | 40 | 78.81% | 19.87% | 8.61% | 90 | 59 | 0 | 393 | 391 | 110 | 10 | 9 | 13 | 1173 | 52.4545 | 280 | 145 | 15 | 577 | 0 | 0 | 40 | 0 | 0.36204 | 3.9898 | 4.7787 | 6.9028 | Medium | Medium | Medium | Mid | 382 | 424 | 19.0664
OLETA 1102 | 163541102 | CENTRAL VALLEY | STOCKTON | 65.7192 | 435994 | 43.7225 | 32.18% | 2.003% | 83.86% | 9.889% | 2 | 0 | 45 | 83.64% | 12.11% | 3.201% | 224 | 697 | 4 | 1 | 223 | 95 | 0 | 5 | 9 | 1281 | 34.8693 | 145 | 64 | 9 | 350 | 0 | 0 | 43 | 0 | 0.040535 | 3.9755 | 4.7775 | 0.76989 | Low | Medium | Medium | Bottom | 740 | 425 | 18.993
BIG RIVER 1101 | 043081101 | NORTHERN | HUMBOLDT | 73.6464 | 656342 | 42.0514 | 21.84% | 2.061% | 18.35% | 70.42% | 71 | 0 | 148 | 17.45% | 79.11% | 3.96% | 194 | 693 | 0 | 11 | 435 | 71 | 53 | 17 | 27 | 1717 | 36.2511 | 228 | 94 | 17 | 705 | 0 | 1 | 148 | 1 | 0.74751 | 4.0922 | 4.6289 | 14.1595 | High | Medium | Medium | Mid | 276 | 426 | 18.9422
JESSUP 1102 | 103441102 | NORTHERN | NORTH VALLEY | 55.2091 | 877468 | 40.9455 | 0% | 67.4% | 22.82% | 0.03146% | 3 | 3 | 65 | 90.16% | 0.08954% | 6.697% | 54 | 1031 | 45 | 0 | 125 | 91 | 2 | 7 | 12 | 1523 | 42.5389 | 281 | 108 | 3 | 578 | 0 | 6 | 65 | 0 | 0.056661 | 5.3608 | 3.5021 | 1.0638 | Low | Medium | Low | Bottom | 701 | 427 | 18.7745
NARROWS 2101 | 153132101 | NORTHERN | SIERRA | 61.1189 | 168654 | 45.2804 | 72.81% | 0.5616% | 92.09% | 3.646% | 3 | 1 | 49 | 83.47% | 12.83% | 7.893% | 247 | 431 | 45 | 0 | 158 | 189 | 0 | 11 | 24 | 1267 | 41.9685 | 222 | 73 | 7 | 401 | 0 | 4 | 49 | 0 | 0.075116 | 4.1813 | 4.4896 | 1.4101 | Low | Medium | Medium | Bottom | 669 | 428 | 18.7726
CAMPHORA 1101 | 182071101 | CENTRAL COAST | CENTRAL COAST | 2.177 | 949679.6667 | 39.0909 | 9.398% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 4.545% | 0 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 22 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 1 | 0 | 0.10721 | 15.7705 | 1.1803 | 1.9957 | Low | High | Low | Bottom | 603 | 429 | 18.6144
WYANDOTTE 1107 | 102911107 | NORTHERN | NORTH VALLEY | 106.7969 | 810745 | 41.8392 | 36.08% | 1.122% | 84.3% | 8.984% | 8 | 3 | 72 | 83.97% | 10.45% | 4.967% | 191 | 1673 | 36 | 2 | 203 | 123 | 2 | 9 | 17 | 2577 | 40.75 | 437 | 146 | 5 | 952 | 0 | 2 | 72 | 0 | 0.041139 | 2.9393 | 6.2964 | 0.76135 | Low | Medium | High | Bottom | 742 | 430 | 18.5071
COARSEGOLD 2104 | 254432104 | CENTRAL VALLEY | YOSEMITE | 249.6433 | 1435361.3333 | 40.5176 | 78.07% | 8.356% | 78.34% | 4.366% | 6 | 0 | 156 | 87.23% | 7.592% | 30.19% | 204 | 744 | 0 | 1 | 2019 | 429 | 11 | 25 | 39 | 4995 | 28.9785 | 762 | 876 | 95 | 2380 | 0 | 0 | 155 | 0 | 0.14241 | 4.7699 | 3.8787 | 2.6346 | Low | Medium | Medium | Bottom | 549 | 431 | 18.5007
JARVIS 1110 | 013501110 | CENTRAL COAST | MISSION | 0.83431 | 874083.6667 | 0 | 3.699% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13589 | 2.5792 | 7.1237 | 2.4967 | Low | Medium | High | Bottom | 558 | 432 | 18.3733
DEL MONTE 2104 | 182222104 | CENTRAL COAST | CENTRAL COAST | 61.8446 | 2135572 | 43.948 | 25.97% | 0.06563% | 58.88% | 15.23% | 4 | 2 | 123 | 38.09% | 39.91% | 9.39% | 264 | 503 | 0 | 16 | 380 | 85 | 8 | 66 | 84 | 1214 | 17.1443 | 148 | 77 | 6 | 429 | 0 | 0 | 123 | 0 | 0.39261 | 4.4291 | 4.1273 | 7.1771 | Medium | Medium | Medium | Mid | 375 | 433 | 18.2804
MARTELL 1103 | 163011103 | CENTRAL VALLEY | STOCKTON | 20.9115 | 861488.3333 | 45.9909 | 28.77% | 4.141% | 64.78% | 4.509% | 0 | 0 | 17 | 79.74% | 8.434% | 4.989% | 104 | 172 | 1 | 0 | 124 | 76 | 0 | 4 | 5 | 441 | 35.2474 | 52 | 20 | 1 | 105 | 0 | 0 | 17 | 0 | 0.14531 | 3.6373 | 5.0111 | 2.6486 | Low | Medium | Medium | Bottom | 548 | 434 | 18.2269
DUNLAP 1102 | 254061102 | CENTRAL VALLEY | FRESNO | 55.7604 | 130517 | 40.8203 | 38.2% | 75.31% | 23.26% | 0% | 12 | 5 | 63 | 96.98% | 0% | 29.35% | 68 | 56 | 1 | 85 | 404 | 98 | 0 | 11 | 24 | 1097 | 11.9612 | 122 | 45 | 5 | 341 | 0 | 0 | 62 | 0 | 0.30752 | 8.8689 | 2.0526 | 5.5982 | Low | Medium | Low | Mid | 418 | 435 | 18.2043
MORAGA 1102 | 013801102 | BAY AREA | DIABLO | 4.3902 | 485517.3333 | 44.8457 | 104.1% | 0% | 27.11% | 30.91% | 0 | 0 | 11 | 13.13% | 74.88% | 20.25% | 43 | 41 | 0 | 0 | 84 | 7 | 0 | 0 | 4 | 163 | 20.55 | 12 | 32 | 7 | 60 | 0 | 0 | 11 | 0 | 0.58353 | 2.6954 | 6.6962 | 10.5322 | Medium | Medium | High | Mid | 322 | 436 | 18.049
SONOMA 1106 | 042721106 | NORTHERN | SONOMA | 1.2651 | 969903.6667 | 42.8125 | 19.52% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 0% | 1 | 0 | 0 | 0 | 8 | 5 | 0 | 0 | 0 | 16 | 22.4 | 2 | 1 | 0 | 5 | 0 | 0 | 1 | 0 | 0.20325 | 3.2426 | 5.5195 | 3.6377 | Low | Medium | High | Mid | 497 | 437 | 17.8977
GIRVAN 1102 | 103401102 | NORTHERN | NORTH VALLEY | 46.0035 | 665380.3333 | 43.1333 | 37.64% | 36.8% | 43.85% | 0% | 4 | 1 | 62 | 93.18% | 1.609% | 10.01% | 199 | 698 | 20 | 1 | 176 | 143 | 0 | 14 | 33 | 1289 | 42.3467 | 186 | 137 | 5 | 465 | 0 | 2 | 62 | 0 | 0.065579 | 3.8498 | 4.6134 | 1.1647 | Low | Medium | Medium | Bottom | 691 | 438 | 17.7608
VACAVILLE 1109 | 063601109 | NORTHERN | SACRAMENTO | 0.50066 | 930867.3333 | 46.1111 | 51.41% | 0% | 12.32% | 87.68% | 0 | 0 | 0 | 12.32% | 87.68% | 10% | 5 | 0 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 10 | 37.3333 | 1 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0.15986 | 4.149 | 4.2802 | 2.8388 | Low | Medium | Medium | Mid | 538 | 439 | 17.7584
KONOCTI 1108 | 043311108 | NORTHERN | HUMBOLDT | 23.2432 | 650308.6667 | 45.7309 | 56.47% | 0% | 77.17% | 0.5813% | 4 | 1 | 15 | 77.17% | 0.5813% | 14.62% | 243 | 320 | 0 | 2 | 115 | 86 | 6 | 4 | 11 | 602 | 48.3822 | 107 | 96 | 34 | 261 | 0 | 0 | 15 | 0 | 0.23488 | 2.8782 | 6.0774 | 4.1084 | Low | Medium | High | Mid | 472 | 440 | 17.4919
CMC 1101 | 183111101 | CENTRAL COAST | LOS PADRES | 2.0609 | 0 | 44.7222 | 0% | 0% | 52.24% | 0% | 0 | 0 | 1 | 52.24% | 0% | 0% | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.36307 | 3.4262 | 5.0135 | 6.2367 | Medium | Medium | Medium | Mid | 396 | 441 | 17.1774
SAN MIGUEL 1105 | 182661105 | CENTRAL COAST | LOS PADRES | 1.3942 | 377495 | 43.6111 | 17.58% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 5.556% | 1 | 13 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 18 | 62.8571 | 5 | 1 | 0 | 7 | 0 | 0 | 1 | 0 | 0.22921 | 5.3197 | 3.2213 | 3.9278 | Low | Medium | Low | Mid | 479 | 442 | 17.1363
BEAR VALLEY 2101 | 252192101 | CENTRAL VALLEY | YOSEMITE | 109.9397 | 330590 | 40.2159 | 0% | 22.27% | 68.68% | 0.7968% | 2 | 0 | 67 | 80.27% | 13.19% | 20.67% | 42 | 279 | 2 | 0 | 598 | 182 | 0 | 15 | 25 | 1630 | 30.9944 | 226 | 87 | 9 | 567 | 0 | 1 | 66 | 0 | 0.11438 | 6.4533 | 2.6256 | 1.938 | Low | Medium | Low | Bottom | 610 | 443 | 16.9437
AUBERRY 1101 | 254151101 | CENTRAL VALLEY | FRESNO | 243.6273 | 954361.6667 | 40.614 | 47% | 27.66% | 65.22% | 2.352% | 27 | 2 | 260 | 92.44% | 2.791% | 25.83% | 179 | 468 | 3 | 533 | 1555 | 514 | 3 | 43 | 76 | 4583 | 14.7982 | 938 | 344 | 27 | 2021 | 0 | 6 | 260 | 0 | 0.21545 | 7.1086 | 2.3763 | 3.6394 | Low | Medium | Low | Mid | 496 | 444 | 16.8922
COTATI 1102 | 042271102 | NORTHERN | SONOMA | 17.1258 | 1012833.6667 | 45.663 | 37.38% | 7.087% | 36.6% | 28.56% | 5 | 0 | 22 | 35.04% | 39.34% | 3.315% | 109 | 176 | 0 | 2 | 107 | 27 | 4 | 8 | 11 | 362 | 25.929 | 52 | 32 | 4 | 158 | 0 | 0 | 22 | 0 | 0.50342 | 4.551 | 3.6744 | 8.4182 | Medium | Medium | Low | Mid | 351 | 445 | 16.722
CEDAR CREEK 1101 | 103321101 | NORTHERN | NORTH VALLEY | 110.9 | 178675 | 41.2931 | 29.15% | 83.75% | 15.51% | 0% | 9 | 0 | 76 | 99.07% | 0.9185% | 15.51% | 78 | 1036 | 205 | 1 | 384 | 354 | 3 | 13 | 23 | 2527 | 36.609 | 236 | 81 | 5 | 596 | 0 | 2 | 76 | 0 | 0.17084 | 10.4136 | 1.5854 | 2.8205 | Low | Medium | Low | Mid | 539 | 446 | 16.5097
SOLEDAD 2102 | 182052102 | CENTRAL COAST | CENTRAL COAST | 31.2821 | 1529844.6667 | 39.7018 | 81.38% | 0% | 83.82% | 14.88% | 3 | 1 | 7 | 83.17% | 15.53% | 6.818% | 9 | 56 | 0 | 2 | 60 | 15 | 0 | 4 | 5 | 220 | 27.9425 | 19 | 7 | 1 | 97 | 0 | 0 | 7 | 0 | 0.2142 | 18.3454 | 0.8933 | 3.5103 | Low | High | Low | Mid | 503 | 447 | 16.3879
PARADISE 1104 | 102831104 | NORTHERN | NORTH VALLEY | 38.9544 | 1065050.6667 | 42.4077 | 14.54% | 3.104% | 56.28% | 32.08% | 21 | 5 | 82 | 56.48% | 35.62% | 4.57% | 172 | 664 | 27 | 0 | 323 | 80 | 76 | 10 | 28 | 1466 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 81 | 1 | 0.73559 | 2.41 | 6.7957 | 12.047 | High | Medium | High | Mid | 302 | 448 | 16.3773
WISE 1102 | 152271102 | NORTHERN | SIERRA | 115.3011 | 586467.6667 | 42.7308 | 42.3% | 1.815% | 67.61% | 21.91% | 8 | 0 | 130 | 63.37% | 28% | 7.857% | 197 | 1584 | 10 | 0 | 316 | 146 | 58 | 19 | 39 | 2482 | 32.1484 | 452 | 309 | 10 | 1032 | 0 | 1 | 130 | 0 | 0.33606 | 3.9368 | 4.1412 | 5.4788 | Medium | Medium | Medium | Mid | 420 | 449 | 16.3028
MORRO BAY 1101 | 183011101 | CENTRAL COAST | LOS PADRES | 7.6115 | 1054437 | 42.193 | 16.43% | 12.48% | 15.44% | 64.32% | 0 | 0 | 5 | 17.26% | 74.97% | 0% | 25 | 1 | 11 | 25 | 36 | 6 | 1 | 3 | 3 | 115 | 36.8462 | 6 | 6 | 0 | 27 | 0 | 0 | 5 | 0 | 0.41487 | 3.0723 | 5.2632 | 6.7086 | Medium | Medium | Medium | Mid | 387 | 450 | 16.1703
MARIPOSA 2102 | 254452102 | CENTRAL VALLEY | YOSEMITE | 248.8941 | 1035525 | 40.3388 | 57.51% | 50.91% | 44.57% | 0.08718% | 9 | 0 | 173 | 93.58% | 2.121% | 24.56% | 125 | 1484 | 0 | 4 | 1647 | 269 | 9 | 19 | 31 | 4739 | 43.5371 | 767 | 331 | 30 | 1884 | 0 | 2 | 171 | 0 | 0.1473 | 5.7432 | 2.8035 | 2.3716 | Low | Medium | Low | Bottom | 577 | 451 | 16.1011
RACETRACK 1703 | 163761703 | CENTRAL VALLEY | YOSEMITE | 57.8457 | 1049270.3333 | 42.5404 | 112.5% | 6.292% | 65.59% | 17.44% | 8 | 0 | 126 | 50.66% | 39.55% | 5.133% | 291 | 706 | 1 | 0 | 434 | 169 | 10 | 25 | 46 | 1617 | 25.2642 | 201 | 181 | 30 | 645 | 0 | 0 | 126 | 0 | 0.41672 | 2.981 | 5.3557 | 6.653 | Medium | Medium | Medium | Mid | 388 | 452 | 15.9651
DUNLAP 1103 | 254061103 | CENTRAL VALLEY | FRESNO | 70.8013 | 317583.3333 | 41.437 | 95.18% | 51.79% | 42.82% | 0.09684% | 19 | 2 | 59 | 94.48% | 0.7698% | 23.66% | 80 | 70 | 0 | 45 | 502 | 136 | 3 | 22 | 36 | 1196 | 12.7956 | 156 | 76 | 7 | 421 | 0 | 0 | 59 | 0 | 0.29453 | 6.9649 | 2.2879 | 4.6932 | Low | Medium | Low | Mid | 443 | 453 | 15.9347
NAPA 1112 | 042021112 | BAY AREA | NORTH BAY | 19.8336 | 624532.6667 | 42.9805 | 14.88% | 0% | 75% | 8.553% | 3 | 1 | 13 | 72.43% | 27.57% | 16.61% | 44 | 120 | 0 | 0 | 49 | 58 | 0 | 3 | 4 | 307 | 31.4458 | 19 | 21 | 2 | 89 | 0 | 0 | 13 | 0 | 0.318 | 3.4143 | 4.6347 | 5.0322 | Low | Medium | Medium | Mid | 433 | 454 | 15.8244
RINCON 1102 | 043321102 | NORTHERN | SONOMA | 3.7815 | 795269.6667 | 45.1587 | 51.96% | 0% | 31.56% | 28.58% | 2 | 0 | 10 | 30.29% | 29.85% | 0% | 18 | 20 | 0 | 3 | 24 | 8 | 0 | 2 | 2 | 63 | 40.3478 | 19 | 10 | 4 | 47 | 0 | 0 | 10 | 1 | 0.51752 | 3.9597 | 3.9716 | 8.1388 | Medium | Medium | Medium | Mid | 355 | 455 | 15.7264
SONOMA 1105 | 042721105 | NORTHERN | SONOMA | 16.7065 | 977537 | 43.7416 | 30.56% | 0% | 53.56% | 45.41% | 2 | 2 | 14 | 53.56% | 45.41% | 8.638% | 46 | 143 | 0 | 0 | 59 | 43 | 14 | 6 | 6 | 301 | 34.7438 | 52 | 22 | 3 | 123 | 0 | 1 | 14 | 0 | 0.58215 | 3.4113 | 4.6018 | 9.1387 | Medium | Medium | Medium | Mid | 341 | 456 | 15.6982
JESSUP 1101 | 103441101 | NORTHERN | NORTH VALLEY | 66.1287 | 798939 | 41.3006 | 0% | 57.53% | 38.98% | 0% | 5 | 0 | 58 | 96.41% | 0.4507% | 7.582% | 163 | 1135 | 44 | 0 | 201 | 135 | 0 | 12 | 23 | 1807 | 39.5921 | 288 | 144 | 12 | 687 | 0 | 7 | 58 | 0 | 0.042059 | 4.3919 | 3.5388 | 0.65369 | Low | Medium | Low | Bottom | 750 | 457 | 15.5421
GRASS VALLEY 1103 | 152031103 | NORTHERN | SIERRA | 86.458 | 534422 | 42.7367 | 43.7% | 41.13% | 51.11% | 1.285% | 9 | 2 | 125 | 90.34% | 3.412% | 12.68% | 112 | 1291 | 3 | 0 | 272 | 207 | 3 | 20 | 34 | 2035 | 38.7995 | 405 | 175 | 16 | 830 | 0 | 2 | 125 | 0 | 0.1218 | 3.2523 | 4.7244 | 1.8714 | Low | Medium | Medium | Bottom | 619 | 458 | 15.3651
OAKHURST 1102 | 254421102 | CENTRAL VALLEY | YOSEMITE | 11.4965 | 459199.6667 | 40.0723 | 39.62% | 48.97% | 42.86% | 0% | 1 | 0 | 25 | 94.71% | 0.9497% | 23.71% | 18 | 59 | 0 | 0 | 168 | 27 | 0 | 6 | 11 | 350 | 38.9931 | 51 | 50 | 5 | 152 | 0 | 0 | 25 | 0 | 0.25737 | 3.9396 | 3.8815 | 3.9356 | Low | Medium | Medium | Mid | 478 | 459 | 15.2916
FROGTOWN 1701 | 163451701 | CENTRAL VALLEY | STOCKTON | 70.7853 | 668544.6667 | 43.2019 | 45.77% | 44.34% | 42.74% | 1.166% | 4 | 1 | 86 | 81.99% | 6.255% | 7.251% | 302 | 744 | 0 | 0 | 482 | 100 | 0 | 10 | 26 | 1710 | 24.0812 | 237 | 136 | 17 | 570 | 0 | 1 | 86 | 0 | 0.066096 | 2.7561 | 5.5434 | 1.0098 | Low | Medium | High | Bottom | 710 | 460 | 15.2784
HARTLEY 1101 | 043211101 | NORTHERN | HUMBOLDT | 31.2788 | 1012195.3333 | 44.292 | 49.86% | 2.894% | 62.58% | 18.56% | 3 | 0 | 38 | 66.25% | 19.74% | 8.496% | 153 | 263 | 0 | 2 | 161 | 60 | 8 | 4 | 14 | 565 | 31.0041 | 114 | 47 | 4 | 244 | 0 | 0 | 38 | 0 | 0.29774 | 4.231 | 3.5693 | 4.4964 | Low | Medium | Low | Mid | 451 | 461 | 15.1018
DESCHUTES 1101 | 103351101 | NORTHERN | NORTH VALLEY | 114.8711 | 486589.3333 | 41.1437 | 66.27% | 61.81% | 33.84% | 1.545% | 6 | 1 | 79 | 95.65% | 1.545% | 9.249% | 183 | 1490 | 93 | 1 | 308 | 255 | 0 | 11 | 23 | 2584 | 47.1203 | 288 | 163 | 14 | 677 | 0 | 12 | 79 | 0 | 0.044915 | 4.2763 | 3.5025 | 0.67273 | Low | Medium | Low | Bottom | 748 | 462 | 14.9779
OAKLAND K 1104 | 012101104 | BAY AREA | EAST BAY | 15.128 | 643588 | 45.8829 | 19.27% | 0% | 47.07% | 23.19% | 11 | 2 | 43 | 26.48% | 51% | 31.59% | 172 | 118 | 1 | 13 | 243 | 61 | 46 | 27 | 48 | 573 | 16.262 | 41 | 92 | 32 | 198 | 0 | 0 | 43 | 0 | 0.65953 | 2.2398 | 6.6719 | 9.8558 | Medium | Low | High | Mid | 334 | 463 | 14.9438
RADUM 1105 | 013151105 | CENTRAL COAST | MISSION | 2.3633 | 898321.6667 | 46.828 | 13.05% | 0% | 71.01% | 13.68% | 2 | 3 | 7 | 67.75% | 16.94% | 21.51% | 37 | 29 | 0 | 0 | 43 | 3 | 0 | 6 | 10 | 93 | 10.5116 | 9 | 18 | 6 | 46 | 0 | 0 | 7 | 1 | 0.5345 | 2.7701 | 5.3598 | 7.9357 | Medium | Medium | Medium | Mid | 361 | 464 | 14.8471
SAN MIGUEL 1106 | 182661106 | CENTRAL COAST | LOS PADRES | 39.7691 | 362299 | 41.392 | 58.88% | 3.399% | 94.25% | 0.3695% | 0 | 0 | 10 | 96.61% | 3.388% | 5.666% | 42 | 9 | 0 | 48 | 178 | 40 | 0 | 0 | 0 | 353 | 24.5357 | 40 | 12 | 1 | 95 | 0 | 0 | 10 | 0 | 0.083464 | 5.814 | 2.5469 | 1.2359 | Low | Medium | Low | Bottom | 683 | 465 | 14.8075
CARLOTTA 1121 | 192291121 | NORTHERN | HUMBOLDT | 23.6581 | 315621 | 44.1397 | 25.44% | 20.75% | 46.03% | 11.31% | 8 | 0 | 17 | 68.48% | 25.21% | 33.42% | 95 | 19 | 0 | 0 | 239 | 24 | 8 | 2 | 5 | 404 | 28.6829 | 43 | 20 | 12 | 130 | 0 | 2 | 17 | 0 | 0.55115 | 5.1578 | 2.8531 | 8.1105 | Medium | Medium | Low | Mid | 356 | 466 | 14.7154
MC KEE 1107 | 083531107 | CENTRAL COAST | SAN JOSE | 2.8856 | 977403 | 43.5849 | 9.903% | 0% | 82.84% | 11.1% | 1 | 0 | 6 | 82.84% | 14.34% | 9.434% | 8 | 22 | 0 | 0 | 17 | 3 | 0 | 0 | 1 | 53 | 0 | 6 | 6 | 0 | 24 | 0 | 0 | 6 | 0 | 0.20895 | 4.9293 | 2.9617 | 3.0505 | Low | Medium | Low | Mid | 522 | 467 | 14.5991
OREGON TRAIL 1103 | 103521103 | NORTHERN | NORTH VALLEY | 118.6709 | 743676.6667 | 42.5605 | 47.64% | 60.02% | 31.71% | 0.2304% | 2 | 0 | 117 | 95.36% | 0.3707% | 8.405% | 379 | 1728 | 86 | 3 | 437 | 244 | 3 | 22 | 38 | 3141 | 44.1023 | 472 | 252 | 12 | 1023 | 0 | 8 | 117 | 0 | 0.062522 | 3.3776 | 4.3191 | 0.91208 | Low | Medium | Medium | Bottom | 721 | 468 | 14.5882
MARTELL 1102 | 163011102 | CENTRAL VALLEY | STOCKTON | 9.84 | 363802.3333 | 43.0645 | 67.6% | 0% | 60.56% | 7.422% | 3 | 0 | 8 | 53.89% | 34.16% | 1.29% | 21 | 73 | 0 | 0 | 45 | 21 | 0 | 4 | 7 | 155 | 29 | 16 | 5 | 3 | 41 | 0 | 0 | 8 | 0 | 0.37154 | 2.6842 | 5.3749 | 5.3603 | Medium | Medium | Medium | Mid | 423 | 469 | 14.4271
MORAGA 1103 | 013801103 | BAY AREA | DIABLO | 4.0164 | 626060.6667 | 43.8889 | 34.64% | 0% | 48.32% | 34.84% | 3 | 0 | 6 | 45.28% | 40.44% | 9.524% | 7 | 10 | 0 | 0 | 37 | 2 | 0 | 0 | 2 | 63 | 23.3103 | 7 | 12 | 7 | 31 | 0 | 0 | 6 | 1 | 0.70234 | 1.9231 | 7.4024 | 9.9984 | High | Low | High | Mid | 330 | 470 | 14.2358
SAN ARDO 1101 | 182191101 | CENTRAL COAST | CENTRAL COAST | 2.7868 | 271781.3333 | 39.359 | 8.763% | 0% | 88.24% | 11.76% | 0 | 0 | 0 | 88.24% | 11.76% | 17.5% | 1 | 9 | 0 | 0 | 12 | 1 | 0 | 0 | 0 | 40 | 19.1538 | 7 | 1 | 0 | 13 | 0 | 0 | 0 | 0 | 0.11775 | 7.1101 | 1.9981 | 1.6728 | Low | Medium | Low | Bottom | 638 | 471 | 14.2067
COARSEGOLD 2103 | 254432103 | CENTRAL VALLEY | YOSEMITE | 94.1821 | 1349627.3333 | 40.6886 | 85.78% | 0.6152% | 82.94% | 0.4203% | 4 | 0 | 59 | 85.6% | 0.4203% | 29.52% | 130 | 305 | 1 | 0 | 677 | 228 | 0 | 14 | 23 | 1992 | 34.5554 | 293 | 421 | 41 | 1031 | 0 | 0 | 59 | 0 | 0.13752 | 3.7859 | 3.7343 | 1.9442 | Low | Medium | Low | Bottom | 609 | 472 | 14.1375
VACAVILLE 1111 | 063601111 | NORTHERN | SACRAMENTO | 12.1732 | 730974 | 42.4232 | 68.03% | 10.69% | 44.05% | 28.98% | 1 | 0 | 13 | 44.9% | 38.83% | 4.437% | 49 | 139 | 6 | 0 | 65 | 14 | 0 | 5 | 8 | 293 | 30.0167 | 49 | 59 | 3 | 139 | 0 | 0 | 13 | 1 | 0.43303 | 3.2456 | 4.3457 | 6.1076 | Medium | Medium | Medium | Mid | 403 | 473 | 14.1045
PLACERVILLE 1110 | 153081110 | NORTHERN | SIERRA | 34.3842 | 527171.3333 | 42.7593 | 19.84% | 23.11% | 46.88% | 17.8% | 6 | 0 | 77 | 54.68% | 33.1% | 0.201% | 153 | 498 | 15 | 0 | 190 | 41 | 0 | 10 | 29 | 995 | 48.9063 | 166 | 116 | 20 | 404 | 0 | 2 | 77 | 0 | 0.28065 | 3.5354 | 3.9518 | 3.9211 | Low | Medium | Medium | Mid | 480 | 474 | 13.9714
SONOMA 1102 | 042721102 | NORTHERN | SONOMA | 6.154 | 984388.6667 | 44.031 | 43.3% | 0% | 80.66% | 19.34% | 3 | 1 | 6 | 80.66% | 19.34% | 6.977% | 28 | 49 | 0 | 1 | 43 | 18 | 0 | 2 | 2 | 129 | 42.2778 | 13 | 22 | 2 | 54 | 0 | 0 | 6 | 1 | 0.37399 | 2.4554 | 5.6694 | 5.2062 | Medium | Medium | High | Mid | 425 | 475 | 13.9205
BROWNS VALLEY 1101 | 152921101 | NORTHERN | SIERRA | 41.7706 | 201976 | 42.608 | 31.69% | 0% | 89.81% | 7.84% | 4 | 0 | 37 | 82.72% | 17.28% | 4.742% | 84 | 489 | 27 | 0 | 107 | 59 | 0 | 10 | 19 | 949 | 40.0779 | 150 | 69 | 1 | 334 | 0 | 3 | 37 | 0 | 0.083871 | 3.0913 | 4.4402 | 1.1512 | Low | Medium | Medium | Bottom | 692 | 476 | 13.726
NEWBURG 1131 | 192151131 | NORTHERN | HUMBOLDT | 8.326 | 589860.3333 | 43.0065 | 17.28% | 0% | 35.74% | 62.59% | 2 | 0 | 5 | 34.38% | 63.96% | 43.14% | 19 | 28 | 0 | 0 | 85 | 17 | 0 | 0 | 0 | 153 | 25.9474 | 14 | 7 | 4 | 58 | 0 | 0 | 5 | 1 | 0.63324 | 4.1728 | 3.2415 | 8.5651 | Medium | Medium | Low | Mid | 348 | 477 | 13.5259
HARRIS 1109 | 192431109 | NORTHERN | HUMBOLDT | 13.4593 | 1050995 | 41.8673 | 6.082% | 3.296% | 43.05% | 53.66% | 5 | 0 | 21 | 29.16% | 70.84% | 41.91% | 28 | 23 | 0 | 1 | 306 | 28 | 22 | 1 | 1 | 408 | 26.7095 | 54 | 27 | 9 | 183 | 0 | 0 | 20 | 1 | 0.76709 | 2.1669 | 6.2272 | 10.3507 | High | Low | High | Mid | 325 | 478 | 13.4935
COTTONWOOD 1102 | 102931102 | NORTHERN | NORTH VALLEY | 62.6112 | 771151.6667 | 41.6414 | 0% | 42.26% | 50.57% | 0.4287% | 2 | 0 | 57 | 92.83% | 0.4287% | 8.442% | 114 | 733 | 45 | 0 | 293 | 134 | 27 | 5 | 12 | 1386 | 49.295 | 206 | 118 | 2 | 455 | 0 | 1 | 57 | 0 | 0.08656 | 4.0518 | 3.3252 | 1.1662 | Low | Medium | Low | Bottom | 690 | 479 | 13.473
NARROWS 2102 | 153132102 | NORTHERN | SIERRA | 96.3992 | 1160087.6667 | 42.8608 | 41.46% | 4.305% | 80.42% | 2.279% | 3 | 0 | 154 | 84.91% | 2.279% | 9.627% | 117 | 1399 | 5 | 0 | 136 | 217 | 0 | 8 | 27 | 2171 | 52.4735 | 369 | 185 | 8 | 819 | 0 | 1 | 154 | 0 | 0.043566 | 2.6317 | 5.0863 | 0.58317 | Low | Medium | Medium | Bottom | 759 | 480 | 13.3857
OREGON TRAIL 1102 | 103521102 | NORTHERN | NORTH VALLEY | 46.8334 | 435781.3333 | 43.1527 | 54.14% | 40.11% | 44.99% | 0% | 2 | 0 | 32 | 85.51% | 0.0627% | 6.973% | 175 | 688 | 25 | 0 | 200 | 94 | 2 | 12 | 29 | 1176 | 43.0439 | 169 | 99 | 6 | 402 | 0 | 5 | 32 | 0 | 0.046428 | 2.7529 | 4.8585 | 0.62096 | Low | Medium | Medium | Bottom | 753 | 481 | 13.3748
HOLLISTER 2102 | 182492102 | CENTRAL COAST | CENTRAL COAST | 31.7344 | 522197.3333 | 50.8373 | 18.19% | 0.7013% | 42.11% | 6.044% | 0 | 0 | 11 | 42.46% | 57.54% | 10.95% | 115 | 107 | 8 | 4 | 36 | 20 | 0 | 4 | 4 | 210 | 16.5778 | 16 | 12 | 1 | 47 | 0 | 0 | 11 | 0 | 0.46472 | 10.11 | 1.3052 | 6.1323 | Medium | Medium | Low | Mid | 400 | 482 | 13.1959
HOLLISTER 2102 | 182492102 | CENTRAL COAST | CENTRAL COAST | 31.7344 | 522197.3333 | 38.3333 | 25.09% | 15.35% | 77.48% | 1.755% | 0 | 0 | 4 | 92.84% | 1.755% | 2.778% | 2 | 13 | 0 | 0 | 51 | 1 | 0 | 0 | 0 | 72 | 1.6667 | 2 | 3 | 1 | 10 | 0 | 0 | 4 | 0 | 0.11331 | 10.11 | 1.3052 | 1.4952 | Low | Medium | Low | Bottom | 657 | 482 | 13.1959
PUTAH CREEK 1105 | 063681105 | NORTHERN | SACRAMENTO | 1.9567 | 900677 | 42.6562 | 13.07% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 3.03% | 9 | 23 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 33 | 69.8 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0.20027 | 42.6644 | 0.30666 | 2.6203 | Low | High | Low | Bottom | 551 | 484 | 13.0834
PACIFICA 1102 | 022811102 | CENTRAL COAST | PENINSULA | 6.4541 | 946069 | 43.4375 | 9.475% | 10.53% | 13.09% | 57.4% | 0 | 0 | 3 | 0% | 98.05% | 3.125% | 25 | 19 | 0 | 0 | 50 | 2 | 0 | 1 | 1 | 96 | 14.4211 | 6 | 4 | 5 | 22 | 1 | 0 | 3 | 0 | 0.48867 | 2.0338 | 6.3815 | 6.3422 | Medium | Low | High | Mid | 393 | 485 | 12.9785
BURNEY 1101 | 103311101 | NORTHERN | NORTH VALLEY | 52.0491 | 536787 | 42.1151 | 32.24% | 82.94% | 2.126% | 0.1522% | 6 | 0 | 66 | 73.8% | 11.42% | 17.76% | 143 | 556 | 6 | 0 | 305 | 140 | 0 | 22 | 42 | 1470 | 26.4424 | 119 | 94 | 13 | 384 | 0 | 4 | 66 | 0 | 0.19288 | 4.8346 | 2.5914 | 2.4166 | Low | Medium | Low | Bottom | 566 | 486 | 12.5285
HARTLEY 1102 | 043211102 | NORTHERN | HUMBOLDT | 5.905 | 539118.3333 | 45.7386 | 83.43% | 20.96% | 51.04% | 11.35% | 0 | 0 | 7 | 51.04% | 32.31% | 18.18% | 28 | 44 | 0 | 0 | 18 | 17 | 0 | 0 | 1 | 88 | 29.4054 | 11 | 12 | 0 | 38 | 0 | 0 | 7 | 0 | 0.46974 | 3.6499 | 3.4317 | 5.8836 | Medium | Medium | Low | Mid | 408 | 487 | 12.5252
UKIAH 1115 | 042771115 | NORTHERN | HUMBOLDT | 18.3 | 313014.3333 | 44.1337 | 0% | 3.584% | 71.18% | 13.35% | 2 | 0 | 18 | 74.77% | 17.33% | 5.185% | 96 | 150 | 0 | 1 | 124 | 65 | 0 | 10 | 11 | 405 | 37.3867 | 57 | 65 | 5 | 184 | 0 | 0 | 18 | 0 | 0.27079 | 4.5889 | 2.7266 | 3.3882 | Low | Medium | Low | Mid | 509 | 488 | 12.5122
NARROWS 2105 | 153132105 | NORTHERN | SIERRA | 179.3789 | 1278710 | 42.6748 | 33% | 1.996% | 83.86% | 2.835% | 7 | 6 | 207 | 85.79% | 2.997% | 13.3% | 337 | 2666 | 22 | 0 | 303 | 459 | 20 | 24 | 43 | 4227 | 50.4105 | 855 | 356 | 18 | 1719 | 0 | 5 | 207 | 0 | 0.1137 | 2.325 | 5.3456 | 1.4131 | Low | Low | Medium | Bottom | 668 | 489 | 12.4285
SAN BENITO 2104 | 182742104 | CENTRAL COAST | CENTRAL COAST | 30.1443 | 253743.6667 | 43.8982 | 22.3% | 0.2078% | 46.34% | 21.02% | 14 | 1 | 53 | 46.36% | 46.11% | 4.863% | 130 | 337 | 0 | 4 | 161 | 56 | 0 | 5 | 12 | 658 | 46.9528 | 90 | 26 | 2 | 265 | 2 | 0 | 53 | 0 | 0.61226 | 2.9223 | 4.2369 | 7.5805 | Medium | Medium | Medium | Mid | 366 | 490 | 12.3813
MC KEE 1108 | 083531108 | CENTRAL COAST | SAN JOSE | 1.0836 | 1053694.6667 | 44.6154 | 3.935% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 3 | 8 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 13 | 12.5 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0.23714 | 3.7762 | 3.1908 | 2.8573 | Low | Medium | Low | Mid | 535 | 491 | 12.0489
HATTON 1102 | 182291102 | CENTRAL COAST | CENTRAL COAST | 11.2788 | 817731.6667 | 40.4734 | 31.82% | 6.678% | 31.11% | 31.08% | 12 | 1 | 30 | 15.54% | 72.72% | 15.63% | 11 | 101 | 0 | 2 | 136 | 23 | 3 | 23 | 27 | 339 | 15.2936 | 43 | 28 | 6 | 116 | 0 | 0 | 29 | 1 | 0.70058 | 2.3868 | 5.0435 | 8.4333 | High | Low | Medium | Mid | 350 | 492 | 12.0376
FORT BRAGG A 1101 | 042761101 | NORTHERN | HUMBOLDT | 71.2927 | 664677.3333 | 41.3017 | 37.32% | 1.35% | 21.27% | 71.76% | 44 | 8 | 128 | 11.84% | 87.73% | 4.19% | 147 | 514 | 0 | 17 | 468 | 58 | 49 | 19 | 26 | 1456 | 37.1306 | 177 | 75 | 20 | 500 | 0 | 4 | 127 | 0 | 0.69501 | 3.574 | 3.3624 | 8.3519 | High | Medium | Low | Mid | 352 | 493 | 12.0171
MERCED FALLS 1102 | 252811102 | CENTRAL VALLEY | YOSEMITE | 121.7278 | 1387449.6667 | 43.8872 | 0% | 1.165% | 74.99% | 0% | 2 | 0 | 103 | 88.44% | 0.08232% | 39.16% | 339 | 369 | 3 | 6 | 1235 | 219 | 0 | 11 | 26 | 2689 | 28.1762 | 492 | 290 | 17 | 1062 | 0 | 2 | 103 | 0 | 0.10838 | 3.5035 | 3.4266 | 1.3011 | Low | Medium | Low | Bottom | 678 | 494 | 12.0052
WYANDOTTE 1109 | 102911109 | NORTHERN | NORTH VALLEY | 56.7801 | 1419512 | 42.1136 | 31.89% | 0.2035% | 79.09% | 14.66% | 2 | 0 | 42 | 74% | 19.88% | 3.313% | 133 | 704 | 28 | 0 | 163 | 24 | 0 | 7 | 11 | 1298 | 41.1795 | 231 | 83 | 2 | 498 | 0 | 0 | 42 | 0 | 0.085646 | 2.0554 | 5.745 | 1.0114 | Low | Low | High | Bottom | 709 | 495 | 11.8085
REEDLEY 1104 | 252341104 | CENTRAL VALLEY | FRESNO | 2.6606 | 1032168.6667 | 38.913 | 12.44% | 8.961% | 65.68% | 25.36% | 0 | 0 | 1 | 74.64% | 25.36% | 4.348% | 0 | 20 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 1 | 0 | 4 | 0 | 0 | 1 | 0 | 0.12433 | 4.6705 | 2.501 | 1.4523 | Low | Medium | Low | Bottom | 665 | 496 | 11.6811
RED BLUFF 1101 | 103541101 | NORTHERN | NORTH VALLEY | 48.8637 | 558800.6667 | 40.8648 | 19.94% | 7.923% | 92.07% | 0% | 3 | 0 | 25 | 99.99% | 0% | 10.26% | 22 | 669 | 40 | 0 | 148 | 126 | 0 | 3 | 3 | 1140 | 50.2513 | 216 | 64 | 6 | 387 | 0 | 2 | 25 | 0 | 0.067369 | 4.7159 | 2.4645 | 0.783 | Low | Medium | Low | Bottom | 738 | 497 | 11.6225
PAUL SWEET 2106 | 083252106 | CENTRAL COAST | CENTRAL COAST | 39.4262 | 710856.6667 | 43.9967 | 17.4% | 0.2284% | 57.77% | 26.71% | 19 | 3 | 78 | 51.57% | 34.93% | 7.9% | 173 | 307 | 1 | 12 | 313 | 92 | 7 | 12 | 18 | 924 | 38.9403 | 131 | 72 | 14 | 404 | 8 | 0 | 76 | 1 | 0.79157 | 1.7883 | 6.3865 | 9.0408 | High | Low | High | Mid | 343 | 498 | 11.4213
SAN JOAQUIN #3 1103 | 252531103 | CENTRAL VALLEY | YOSEMITE | 54.5173 | 0 | 40.4287 | 67.87% | 75.5% | 18.68% | 0.2307% | 3 | 4 | 33 | 85.23% | 9.182% | 23.94% | 37 | 214 | 0 | 1 | 491 | 56 | 14 | 5 | 8 | 1207 | 22.7551 | 195 | 69 | 12 | 526 | 0 | 0 | 32 | 0 | 0.26462 | 4.374 | 2.5612 | 2.9644 | Low | Medium | Low | Mid | 528 | 499 | 11.2024
SO. CAL. EDISON #3 1101 | 258861101 | CENTRAL VALLEY | FRESNO | 6.4255 | 1140.3333 | 42.5 | 0% | 0% | 15.88% | 0% | 0 | 0 | 4 | 15.88% | 84.12% | 10% | 0 | 0 | 0 | 0 | 11 | 4 | 0 | 0 | 0 | 20 | 15.0769 | 10 | 3 | 0 | 17 | 0 | 0 | 4 | 0 | 0.37251 | 4.6056 | 2.4212 | 4.1539 | Medium | Medium | Low | Mid | 471 | 500 | 11.151
HIGGINS 1103 | 152691103 | NORTHERN | SIERRA | 75.7487 | 680134.6667 | 42.9244 | 42.22% | 6.927% | 75.99% | 0.3822% | 6 | 4 | 107 | 83.25% | 0.3822% | 11.41% | 176 | 1365 | 6 | 0 | 249 | 131 | 0 | 6 | 26 | 2007 | 41.9881 | 432 | 162 | 15 | 859 | 0 | 4 | 106 | 0 | 0.056665 | 2.4937 | 4.465 | 0.63094 | Low | Medium | Medium | Bottom | 751 | 501 | 11.1346
POSO MOUNTAIN 2101 | 253642101 | CENTRAL VALLEY | KERN | 50.7844 | 413243 | 42.8582 | 78.01% | 40.17% | 40.79% | 8.342% | 30 | 0 | 16 | 57.21% | 32.19% | 11.77% | 86 | 29 | 0 | 98 | 158 | 77 | 0 | 8 | 21 | 705 | 6.6789 | 35 | 10 | 3 | 117 | 0 | 1 | 15 | 0 | 0.46369 | 7.8088 | 1.4221 | 5.149 | Medium | Medium | Low | Mid | 427 | 502 | 11.1046
TAMARACK 1101 | 152291101 | NORTHERN | SIERRA | 17.6532 | 57018.3333 | 43.6402 | 11.63% | 71.08% | 8.336% | 2.557% | 13 | 1 | 26 | 69.68% | 12.29% | 23.19% | 87 | 108 | 2 | 0 | 129 | 22 | 14 | 7 | 11 | 483 | 36.1429 | 52 | 30 | 6 | 142 | 0 | 0 | 26 | 1 | 0.73405 | 5.1641 | 2.1191 | 8.0327 | High | Medium | Low | Mid | 359 | 503 | 10.943
TEMPLETON 2111 | 183052111 | CENTRAL COAST | LOS PADRES | 46.5161 | 707863.3333 | 43.1801 | 13.41% | 0.03222% | 76.19% | 14.78% | 10 | 1 | 87 | 76.19% | 19.38% | 7.533% | 134 | 67 | 2 | 202 | 359 | 201 | 0 | 14 | 19 | 1062 | 52.0586 | 242 | 184 | 19 | 547 | 0 | 1 | 87 | 0 | 0.29919 | 2.8834 | 3.7852 | 3.2654 | Low | Medium | Medium | Mid | 513 | 504 | 10.9143
MORGAN HILL 2104 | 083242104 | CENTRAL COAST | SAN JOSE | 6.2528 | 979082.6667 | 43 | 23.93% | 1.22% | 98.69% | 0% | 2 | 0 | 11 | 100% | 0% | 5.333% | 17 | 32 | 0 | 0 | 28 | 4 | 0 | 6 | 7 | 75 | 36.2683 | 6 | 17 | 38 | 85 | 9 | 0 | 11 | 1 | 0.54864 | 2.6192 | 4.0646 | 5.8409 | Medium | Medium | Medium | Mid | 411 | 505 | 10.646
EDES 1112 | 013681112 | BAY AREA | EAST BAY | 16.0717 | 698923.6667 | 45.2051 | 22.63% | 0% | 45.38% | 10.27% | 4 | 2 | 40 | 19.69% | 42.92% | 30.09% | 120 | 80 | 0 | 1 | 356 | 20 | 19 | 25 | 42 | 585 | 22.5211 | 24 | 58 | 29 | 148 | 0 | 0 | 40 | 1 | 0.68701 | 1.9154 | 5.5547 | 7.3095 | High | Low | High | Mid | 370 | 506 | 10.6396
INDIAN FLAT 1104 | 252691104 | CENTRAL VALLEY | YOSEMITE | 16.7358 | 311983 | 42.409 | 0% | 58.08% | 14.74% | 2.828% | 2 | 0 | 21 | 76.62% | 11.94% | 11.51% | 37 | 11 | 5 | 0 | 183 | 53 | 9 | 8 | 15 | 365 | 69.881 | 29 | 16 | 4 | 98 | 0 | 0 | 21 | 0 | 0.38718 | 3.3705 | 3.132 | 4.0872 | Medium | Medium | Low | Mid | 473 | 507 | 10.5564
IGNACIO 1104 | 042481104 | BAY AREA | NORTH BAY | 7.7928 | 917913.6667 | 44.0407 | 32.42% | 12.03% | 36.09% | 15.62% | 4 | 2 | 12 | 33.32% | 46.51% | 10.57% | 65 | 96 | 1 | 2 | 69 | 54 | 0 | 3 | 4 | 246 | 26.4321 | 28 | 19 | 1 | 82 | 0 | 0 | 12 | 1 | 0.69028 | 1.5732 | 6.6586 | 7.231 | High | Low | High | Mid | 374 | 508 | 10.4755
EMERALD LAKE 0402 | 024080402 | CENTRAL COAST | PENINSULA | 8.0268 | 214527.6667 | 45.6734 | 70.51% | 1.854% | 14.23% | 40.68% | 8 | 1 | 17 | 14.77% | 80.23% | 10.77% | 63 | 150 | 1 | 1 | 96 | 18 | 8 | 2 | 9 | 297 | 45.4621 | 22 | 71 | 18 | 151 | 0 | 0 | 17 | 0 | 0.6989 | 1 | 10.2221 | 7.1442 | High | Low | High | Mid | 377 | 509 | 10.2221
ANDERSON 1103 | 103261103 | NORTHERN | NORTH VALLEY | 8.2733 | 374128.6667 | 42.6316 | 29.15% | 32.81% | 53.1% | 0% | 0 | 0 | 4 | 85.91% | 0% | 8.571% | 34 | 96 | 6 | 0 | 56 | 18 | 0 | 2 | 2 | 210 | 43.92 | 38 | 18 | 1 | 77 | 0 | 0 | 4 | 0 | 0.2342 | 2.6804 | 3.8114 | 2.3926 | Low | Medium | Medium | Bottom | 572 | 510 | 10.216
ANDERSON 1101 | 103261101 | NORTHERN | NORTH VALLEY | 10.7872 | 729481.3333 | 43.7986 | 50.24% | 33.96% | 39.57% | 0.4306% | 0 | 0 | 16 | 76.02% | 17.28% | 2.817% | 76 | 127 | 5 | 0 | 78 | 24 | 0 | 5 | 7 | 284 | 41.7361 | 19 | 16 | 4 | 77 | 0 | 0 | 16 | 0 | 0.24362 | 2.5234 | 4.0188 | 2.4705 | Low | Medium | Medium | Bottom | 561 | 511 | 10.141
CLARKSVILLE 2105 | 153612105 | NORTHERN | SIERRA | 11.2819 | 1512786 | 46.0406 | 96.87% | 0.3472% | 67.33% | 0.4438% | 0 | 0 | 8 | 67.68% | 0.4438% | 0.5% | 50 | 127 | 0 | 0 | 4 | 12 | 0 | 3 | 8 | 200 | 57.2407 | 22 | 20 | 5 | 54 | 0 | 0 | 8 | 0 | 0.25384 | 1.8669 | 5.3527 | 2.5366 | Low | Low | Medium | Bottom | 556 | 512 | 9.9932
PENRYN 1107 | 152561107 | NORTHERN | SIERRA | 43.5049 | 1131270 | 42.5192 | 47.95% | 1.169% | 68.49% | 12.43% | 2 | 0 | 101 | 65.57% | 16.68% | 7.843% | 83 | 611 | 2 | 0 | 143 | 54 | 5 | 17 | 22 | 918 | 28.8128 | 147 | 152 | 11 | 402 | 0 | 0 | 101 | 0 | 0.15717 | 1.8038 | 5.3775 | 1.5245 | Low | Low | High | Bottom | 650 | 513 | 9.6998
BELL 1108 | 152701108 | NORTHERN | SIERRA | 68.8953 | 1348734 | 43.0846 | 32.43% | 2.226% | 73.48% | 8.798% | 6 | 0 | 76 | 77.62% | 9.142% | 5.112% | 224 | 1117 | 6 | 0 | 123 | 83 | 25 | 16 | 24 | 1565 | 36.5314 | 292 | 257 | 39 | 715 | 0 | 3 | 75 | 0 | 0.11856 | 2.3851 | 4.0188 | 1.1365 | Low | Low | Medium | Bottom | 693 | 514 | 9.5852
MORGAN HILL 2110 | 083242110 | CENTRAL COAST | SAN JOSE | 2.1851 | 1472058.6667 | 44.7 | 7.402% | 0% | 79.23% | 15.35% | 0 | 0 | 7 | 56.73% | 37.85% | 12% | 20 | 34 | 0 | 0 | 8 | 2 | 0 | 2 | 2 | 50 | 11.2857 | 6 | 10 | 2 | 23 | 0 | 0 | 7 | 1 | 0.5356 | 2.3084 | 4.1363 | 5.114 | Medium | Low | Medium | Mid | 430 | 515 | 9.548
OAKLAND X 1104 | 012541104 | BAY AREA | EAST BAY | 13.0513 | 312078.6667 | 45.438 | 49.79% | 4.765% | 61.12% | 19.37% | 12 | 4 | 43 | 35.41% | 57.39% | 20% | 127 | 120 | 0 | 1 | 316 | 13 | 52 | 19 | 31 | 550 | 19.375 | 24 | 66 | 34 | 157 | 0 | 0 | 43 | 0 | 0.64178 | 1.4326 | 6.6605 | 6.1236 | Medium | Low | High | Mid | 402 | 516 | 9.5416
OAK 0401 | 012600401 | BAY AREA | EAST BAY | 4.4257 | 107039 | 44.6053 | 45.28% | 6.689% | 37.47% | 25.47% | 0 | 0 | 5 | 1.207% | 89.88% | 47.37% | 12 | 31 | 0 | 2 | 25 | 3 | 2 | 6 | 13 | 152 | 55.7391 | 6 | 25 | 10 | 46 | 0 | 0 | 5 | 0 | 0.64455 | 1 | 9.5343 | 6.1453 | Medium | Low | High | Mid | 399 | 517 | 9.5343
PAUL SWEET 2105 | 083252105 | CENTRAL COAST | CENTRAL COAST | 9.836 | 1033592.6667 | 46.3946 | 61.57% | 0.5614% | 33.7% | 17.58% | 10 | 0 | 13 | 31.27% | 25.61% | 6.803% | 53 | 68 | 0 | 0 | 41 | 4 | 10 | 6 | 6 | 147 | 46.9787 | 16 | 8 | 0 | 49 | 0 | 0 | 13 | 1 | 0.74116 | 1.5428 | 6.1566 | 7.0398 | High | Low | High | Mid | 380 | 518 | 9.4984
ORINDA 0401 | 012350401 | BAY AREA | DIABLO | 9.525 | 214002.6667 | 44.5238 | 0% | 8.848% | 49.67% | 30.24% | 11 | 2 | 27 | 7.449% | 90.73% | 27.09% | 82 | 106 | 1 | 1 | 102 | 27 | 11 | 8 | 16 | 358 | 46.0258 | 24 | 97 | 13 | 157 | 0 | 0 | 27 | 1 | 0.79195 | 1.3734 | 6.8908 | 7.4951 | High | Low | High | Mid | 367 | 519 | 9.4641
DIAMOND SPRINGS 1106 | 152261106 | NORTHERN | SIERRA | 111.1641 | 910047.3333 | 42.3542 | 21.14% | 50.87% | 39.12% | 2.759% | 6 | 6 | 145 | 90.16% | 2.867% | 1.338% | 225 | 1554 | 44 | 0 | 468 | 170 | 6 | 13 | 21 | 2840 | 40.1305 | 599 | 221 | 12 | 1114 | 0 | 3 | 145 | 0 | 0.087538 | 2.5895 | 3.6341 | 0.82376 | Low | Medium | Low | Bottom | 734 | 520 | 9.4103
LUCERNE 1103 | 043351103 | NORTHERN | HUMBOLDT | 33.4045 | 868095 | 44.6968 | 52.31% | 2.663% | 59.12% | 13.46% | 7 | 5 | 17 | 70.8% | 15.45% | 6.564% | 216 | 385 | 0 | 14 | 185 | 103 | 8 | 7 | 13 | 777 | 33.2283 | 133 | 72 | 18 | 317 | 0 | 0 | 17 | 0 | 0.28111 | 1.9423 | 4.8221 | 2.6329 | Low | Low | Medium | Bottom | 550 | 521 | 9.3662
COARSEGOLD 2102 | 254432102 | CENTRAL VALLEY | YOSEMITE | 69.5656 | 333162 | 41.1098 | 105% | 50.59% | 24.23% | 0.6864% | 2 | 0 | 72 | 81.55% | 17.93% | 26.38% | 129 | 250 | 0 | 1 | 713 | 131 | 0 | 23 | 41 | 1664 | 30.7496 | 254 | 171 | 15 | 664 | 0 | 0 | 71 | 0 | 0.15087 | 2.686 | 3.4666 | 1.4048 | Low | Medium | Low | Bottom | 670 | 522 | 9.3112
FULTON 1104 | 042561104 | NORTHERN | SONOMA | 0.58254 | 862530 | 48.3333 | 5.146% | 0% | 77.78% | 22.22% | 0 | 0 | 1 | 77.78% | 22.22% | 16.67% | 5 | 3 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 6 | 41.6 | 3 | 1 | 0 | 5 | 0 | 0 | 1 | 1 | 0.36699 | 2.2972 | 3.9527 | 3.3323 | Medium | Low | Medium | Mid | 511 | 523 | 9.0801
EL CERRITO G 1111 | 012501111 | BAY AREA | EAST BAY | 0.97377 | 404613.3333 | 43.3333 | 1.769% | 0% | 15.73% | 83.98% | 0 | 0 | 1 | 6.068% | 93.64% | 0% | 2 | 4 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 15 | 44.5 | 0 | 2 | 0 | 4 | 0 | 0 | 1 | 0 | 0.16872 | 1 | 8.9706 | 1.5136 | Low | Low | High | Bottom | 651 | 524 | 8.9706
LAS PULGAS 0401 | 024120401 | CENTRAL COAST | PENINSULA | 0.12527 | 193094.3333 | 43.3333 | 39.18% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 6.667% | 1 | 2 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 15 | 87.7143 | 0 | 4 | 1 | 7 | 0 | 0 | 0 | 1 | 0.33866 | 1 | 8.9603 | 3.0345 | Medium | Low | High | Mid | 524 | 525 | 8.9603
SAN CARLOS 1103 | 024181103 | CENTRAL COAST | PENINSULA | 4.0359 | 1078094 | 43.125 | 24.85% | 0% | 31.87% | 31.47% | 1 | 1 | 11 | 28.23% | 38.59% | 13.82% | 35 | 46 | 0 | 0 | 76 | 18 | 0 | 1 | 4 | 152 | 14.2429 | 24 | 13 | 8 | 71 | 0 | 0 | 11 | 1 | 0.73959 | 1 | 8.9438 | 6.6147 | High | Low | High | Mid | 390 | 526 | 8.9438
SHEPHERD 2111 | 252062111 | CENTRAL VALLEY | FRESNO | 20.5291 | 0 | 43.4091 | 33.12% | 0% | 100% | 0% | 0 | 0 | 10 | 100% | 0% | 36.77% | 54 | 13 | 0 | 18 | 162 | 36 | 0 | 4 | 6 | 310 | 46.6993 | 76 | 57 | 1 | 173 | 0 | 0 | 10 | 0 | 0.21054 | 7.2895 | 1.2264 | 1.8822 | Low | Medium | Low | Bottom | 616 | 527 | 8.9398
WOODWARD 2108 | 255292108 | CENTRAL VALLEY | FRESNO | 32.5265 | 1243541.3333 | 41.8898 | 15.92% | 0.1617% | 83.65% | 0.009516% | 1 | 1 | 19 | 93.94% | 1.985% | 26.6% | 25 | 54 | 0 | 12 | 228 | 44 | 0 | 5 | 7 | 470 | 30.9934 | 55 | 53 | 6 | 171 | 0 | 0 | 19 | 0 | 0.20324 | 4.6388 | 1.9232 | 1.8131 | Low | Medium | Low | Bottom | 623 | 528 | 8.9211
POTTER VALLEY P H 1104 | 042281104 | NORTHERN | HUMBOLDT | 7.7001 | 0 | 42.5714 | 22.89% | 0% | 51.2% | 47.83% | 0 | 0 | 3 | 51.2% | 47.83% | 9.434% | 16 | 47 | 0 | 1 | 24 | 11 | 0 | 4 | 7 | 106 | 27.0256 | 17 | 1 | 3 | 40 | 0 | 0 | 3 | 0 | 0.5682 | 5.2347 | 1.6975 | 5.049 | Medium | Medium | Low | Mid | 431 | 529 | 8.8859
WALDO 0402 | 013350402 | BAY AREA | EAST BAY | 3.133 | 123975.6667 | 43.156 | 40.99% | 41.27% | 45.39% | 5.478% | 4 | 2 | 4 | 15.83% | 79.77% | 41.13% | 11 | 12 | 0 | 0 | 63 | 4 | 0 | 4 | 4 | 141 | 45.2857 | 8 | 26 | 5 | 43 | 0 | 0 | 4 | 1 | 0.71881 | 1 | 8.8774 | 6.3812 | High | Low | High | Mid | 392 | 530 | 8.8774
ANTLER 1101 | 103271101 | NORTHERN | NORTH VALLEY | 61.4203 | 341088.3333 | 41.8627 | 43.84% | 84.36% | 4.793% | 1.216% | 12 | 2 | 46 | 90.43% | 1.339% | 7.462% | 180 | 737 | 45 | 0 | 408 | 178 | 0 | 27 | 36 | 1635 | 43.2549 | 199 | 125 | 18 | 476 | 0 | 4 | 45 | 0 | 0.12287 | 2.813 | 3.1543 | 1.0903 | Low | Medium | Low | Bottom | 696 | 531 | 8.873
EL CERRITO G 1108 | 012501108 | BAY AREA | EAST BAY | 0.774 | 593206 | 0 | 2.573% | 0% | 43.34% | 44.78% | 0 | 1 | 0 | 0% | 98.55% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1974 | 1 | 8.776 | 1.7324 | Low | Low | High | Bottom | 633 | 532 | 8.776
FAIRMOUNT 0401 | 012650401 | BAY AREA | EAST BAY | 1.5131 | 126678 | 44.8611 | 31.51% | 0% | 89.61% | 3.405% | 2 | 0 | 3 | 0% | 100% | 51.39% | 2 | 7 | 0 | 0 | 7 | 1 | 0 | 1 | 2 | 72 | 37.9 | 2 | 11 | 4 | 21 | 0 | 0 | 3 | 0 | 0.34629 | 1 | 8.7552 | 3.0318 | Medium | Low | High | Mid | 525 | 533 | 8.7552
PIT NO 3 2101 | 103732101 | NORTHERN | NORTH VALLEY | 47.9266 | 228818 | 40.3882 | 81.88% | 48.93% | 15.56% | 0.328% | 2 | 1 | 18 | 63.08% | 27.99% | 28.61% | 49 | 420 | 6 | 0 | 206 | 61 | 5 | 17 | 36 | 1185 | 23.4096 | 26 | 18 | 2 | 95 | 0 | 2 | 18 | 0 | 0.27482 | 9.5194 | 0.91411 | 2.3914 | Low | Medium | Low | Bottom | 573 | 534 | 8.7018
SAN RAFAEL 1104 | 042011104 | BAY AREA | NORTH BAY | 12.8595 | 894448.6667 | 43.7289 | 9.62% | 1.035% | 17.71% | 75.04% | 13 | 2 | 31 | 13.96% | 80.31% | 4.762% | 88 | 121 | 4 | 1 | 164 | 109 | 0 | 9 | 17 | 462 | 35.7865 | 50 | 66 | 26 | 198 | 0 | 0 | 31 | 0 | 0.7301 | 1 | 8.682 | 6.3388 | High | Low | High | Mid | 394 | 535 | 8.682
EL CERRITO G 1110 | 012501110 | BAY AREA | EAST BAY | 2.1358 | 453257.6667 | 47.3438 | 70.74% | 0.1331% | 23.71% | 1.212% | 2 | 1 | 2 | 9.408% | 41.43% | 46.88% | 14 | 6 | 0 | 1 | 13 | 0 | 2 | 1 | 2 | 32 | 11 | 0 | 1 | 0 | 3 | 0 | 0 | 2 | 0 | 0.4024 | 1 | 8.6693 | 3.4885 | Medium | Low | High | Mid | 504 | 536 | 8.6693
EL CERRITO G 1113 | 012501113 | BAY AREA | EAST BAY | 0.24171 | 889579.6667 | 42.5 | 7.767% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6 | 24 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0.23041 | 1 | 8.6451 | 1.9919 | Low | Low | High | Bottom | 605 | 537 | 8.6451
WOODSIDE 1102 | 024251102 | CENTRAL COAST | PENINSULA | 0.12901 | 537438 | 40 | 0.2934% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 1 | 1 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 8 | 19.6667 | 0 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 0.27865 | 1 | 8.576 | 2.3897 | Low | Low | High | Bottom | 575 | 538 | 8.576
BALCH NO 1 1101 | 252501101 | CENTRAL VALLEY | FRESNO | 14.6983 | 2345.3333 | 47.069 | 38.08% | 78.09% | 10.35% | 3.548% | 0 | 0 | 5 | 79.6% | 20.4% | 5.83% | 135 | 8 | 0 | 2 | 144 | 12 | 0 | 3 | 6 | 223 | 7.4444 | 5 | 1 | 2 | 21 | 0 | 0 | 5 | 0 | 0.31373 | 5.294 | 1.6177 | 2.6869 | Low | Medium | Low | Bottom | 546 | 539 | 8.5641
SAN CARLOS 1104 | 024181104 | CENTRAL COAST | PENINSULA | 8.7241 | 1170594 | 43.2872 | 36.63% | 0.4447% | 39.83% | 28.96% | 6 | 0 | 24 | 37.62% | 41.59% | 11.08% | 45 | 83 | 0 | 2 | 230 | 26 | 0 | 4 | 12 | 397 | 29.3106 | 30 | 68 | 16 | 161 | 0 | 0 | 24 | 0 | 0.67498 | 1 | 8.55 | 5.7711 | High | Low | High | Mid | 413 | 540 | 8.55
EL CERRITO G 1112 | 012501112 | BAY AREA | EAST BAY | 5.0582 | 676843.6667 | 43.3333 | 9.659% | 0% | 64% | 27.08% | 2 | 0 | 2 | 24.47% | 68.63% | 30.68% | 4 | 14 | 0 | 1 | 59 | 1 | 0 | 1 | 1 | 88 | 6.3448 | 7 | 12 | 0 | 29 | 0 | 0 | 2 | 0 | 0.46574 | 1 | 8.5484 | 3.9813 | Medium | Low | High | Mid | 477 | 541 | 8.5484
PENRYN 1105 | 152561105 | NORTHERN | SIERRA | 43.6524 | 716362.3333 | 42.7881 | 33.94% | 1.216% | 59.25% | 20.65% | 7 | 0 | 74 | 57.51% | 24.36% | 9.292% | 86 | 501 | 2 | 1 | 109 | 67 | 0 | 5 | 11 | 861 | 30.2798 | 165 | 112 | 9 | 375 | 0 | 0 | 74 | 0 | 0.34134 | 2.0241 | 4.2125 | 2.9105 | Medium | Low | Medium | Mid | 532 | 542 | 8.5266
SPRUCE 0402 | 013340402 | BAY AREA | EAST BAY | 2.1044 | 0 | 43.9091 | 21.02% | 0% | 40.64% | 23.67% | 1 | 0 | 5 | 5.063% | 66.79% | 45.45% | 5 | 8 | 0 | 0 | 20 | 4 | 2 | 2 | 6 | 55 | 29.05 | 3 | 9 | 7 | 22 | 0 | 0 | 5 | 1 | 0.71004 | 1 | 8.4618 | 6.0082 | High | Low | High | Mid | 406 | 543 | 8.4618
WALDO 0401 | 013350401 | BAY AREA | EAST BAY | 1.7206 | 147915.3333 | 43.012 | 40.55% | 26.03% | 12.34% | 39.32% | 0 | 0 | 1 | 12.34% | 77.91% | 26.51% | 3 | 13 | 0 | 0 | 56 | 2 | 4 | 0 | 2 | 83 | 46.5455 | 5 | 11 | 7 | 24 | 0 | 0 | 1 | 0 | 0.50388 | 1 | 8.4574 | 4.2615 | Medium | Low | High | Mid | 463 | 544 | 8.4574
VASONA 1102 | 083771102 | CENTRAL COAST | DE ANZA | 0.075415 | 960837.3333 | 38 | 2.142% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 5 | 0 | 2 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.10648 | 1 | 8.4479 | 0.8995 | Low | Low | High | Bottom | 723 | 545 | 8.4479
PIT NO 5 1101 | 101321101 | NORTHERN | NORTH VALLEY | 23.7942 | 22337.3333 | 43.757 | 97.46% | 51.05% | 3.644% | 0% | 4 | 1 | 18 | 82.26% | 13.75% | 12.38% | 138 | 153 | 4 | 1 | 200 | 74 | 4 | 13 | 26 | 541 | 25.9595 | 24 | 12 | 2 | 86 | 0 | 3 | 18 | 0 | 0.41374 | 10.1216 | 0.82163 | 3.4407 | Medium | Medium | Low | Mid | 506 | 546 | 8.3162
MIRA VISTA 0403 | 012330403 | BAY AREA | EAST BAY | 0.1074 | 159961.3333 | 0 | 19.33% | 0% | 100% | 0% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16858 | 1 | 8.3009 | 1.3994 | Low | Low | High | Bottom | 672 | 547 | 8.3009
AUBERRY 1102 | 254151102 | CENTRAL VALLEY | FRESNO | 127.9128 | 604229.6667 | 41.5586 | 28.6% | 6.247% | 83.97% | 0.2351% | 0 | 5 | 129 | 89.34% | 1.146% | 30.21% | 106 | 167 | 0 | 253 | 780 | 244 | 0 | 15 | 29 | 2208 | 17.2949 | 512 | 211 | 22 | 1137 | 0 | 0 | 129 | 0 | 0.098189 | 3.2245 | 2.5632 | 0.81154 | Low | Medium | Low | Bottom | 735 | 548 | 8.265
BANGOR 1101 | 103191101 | NORTHERN | NORTH VALLEY | 198.8492 | 791087 | 42.4606 | 48.55% | 0.5655% | 84.37% | 6.825% | 16 | 17 | 173 | 83.4% | 8.32% | 4.776% | 421 | 2528 | 124 | 0 | 321 | 309 | 7 | 35 | 57 | 4439 | 41.3142 | 717 | 219 | 6 | 1540 | 0 | 8 | 172 | 0 | 0.1452 | 1.5986 | 5.1617 | 1.1981 | Low | Low | Medium | Bottom | 687 | 549 | 8.2517
SAN RAFAEL 1109 | 042011109 | BAY AREA | NORTH BAY | 11.6485 | 967675 | 43.8345 | 74.16% | 1.921% | 42.39% | 20.6% | 8 | 1 | 9 | 59.73% | 22.52% | 7.718% | 49 | 57 | 2 | 4 | 141 | 57 | 4 | 7 | 9 | 298 | 30.4255 | 26 | 24 | 15 | 95 | 0 | 1 | 9 | 1 | 0.6749 | 1 | 8.2237 | 5.5502 | High | Low | High | Mid | 419 | 550 | 8.2237
STILLWATER 1101 | 103561101 | NORTHERN | NORTH VALLEY | 36.1073 | 327931.3333 | 42.6121 | 40.19% | 54.86% | 25% | 2.059% | 3 | 0 | 46 | 87.51% | 2.675% | 10.53% | 149 | 577 | 31 | 0 | 154 | 107 | 0 | 6 | 14 | 1073 | 34.6416 | 131 | 82 | 7 | 365 | 0 | 2 | 46 | 0 | 0.073854 | 1.8134 | 4.5151 | 0.60469 | Low | Low | Medium | Bottom | 755 | 551 | 8.1877
GOLDTREE 1107 | 182581107 | CENTRAL COAST | LOS PADRES | 1.1277 | 95289 | 43.3333 | 58.4% | 0% | 5.234% | 7.596% | 0 | 0 | 0 | 5.234% | 7.596% | 0% | 5 | 0 | 0 | 6 | 5 | 1 | 0 | 0 | 2 | 16 | 34.25 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0.26296 | 1.5852 | 5.1526 | 2.1478 | Low | Low | Medium | Bottom | 590 | 552 | 8.168
SAN RAFAEL 1106 | 042011106 | BAY AREA | NORTH BAY | 3.8001 | 931321 | 42.9082 | 24.99% | 11.6% | 22.06% | 23.41% | 5 | 0 | 3 | 22.06% | 35.01% | 1.02% | 12 | 25 | 0 | 0 | 47 | 12 | 0 | 2 | 3 | 98 | 36.125 | 14 | 7 | 3 | 48 | 0 | 0 | 3 | 0 | 0.52609 | 1 | 8.0737 | 4.2475 | Medium | Low | High | Mid | 466 | 553 | 8.0737
DIAMOND SPRINGS 1103 | 152261103 | NORTHERN | SIERRA | 35.304 | 845974.3333 | 42.1526 | 20.18% | 37.61% | 37.93% | 10.24% | 4 | 6 | 53 | 75.54% | 11.02% | 1.149% | 110 | 513 | 9 | 0 | 236 | 47 | 0 | 4 | 12 | 957 | 43.9837 | 200 | 146 | 9 | 433 | 0 | 0 | 53 | 0 | 0.11388 | 1.9067 | 4.2233 | 0.91703 | Low | Low | Medium | Bottom | 719 | 554 | 8.0525
DEL MONTE 1101 | 182221101 | CENTRAL COAST | CENTRAL COAST | 0.22068 | 517133.6667 | 58.8462 | 97.1% | 0% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 13 | 25 | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.30013 | 1 | 7.9973 | 2.4002 | Low | Low | High | Bottom | 570 | 555 | 7.9973
BELMONT 1103 | 024031103 | CENTRAL COAST | PENINSULA | 2.1749 | 1009738.6667 | 42.8873 | 3.119% | 0% | 46.55% | 53.45% | 1 | 0 | 12 | 46.55% | 53.45% | 7.042% | 17 | 48 | 0 | 0 | 78 | 8 | 0 | 5 | 6 | 142 | 11.0702 | 9 | 24 | 12 | 57 | 0 | 0 | 12 | 1 | 0.7262 | 1 | 7.9875 | 5.8005 | High | Low | High | Mid | 412 | 556 | 7.9875
SISQUOC 1102 | 182811102 | CENTRAL COAST | LOS PADRES | 52.3119 | 1118488.3333 | 42.2034 | 91.72% | 0% | 51.74% | 13.78% | 0 | 2 | 22 | 51% | 32.39% | 2.316% | 39 | 17 | 0 | 82 | 137 | 77 | 0 | 2 | 2 | 475 | 18.4194 | 25 | 4 | 2 | 95 | 0 | 0 | 22 | 0 | 0.24085 | 13.2082 | 0.60004 | 1.9089 | Low | High | Low | Bottom | 615 | 557 | 7.9255
MORAGA 1104 | 013801104 | BAY AREA | DIABLO | 17.5873 | 532398.6667 | 44.5925 | 29.46% | 0% | 56.63% | 13.78% | 14 | 4 | 35 | 53.75% | 19.15% | 14.14% | 120 | 133 | 0 | 0 | 223 | 28 | 21 | 9 | 13 | 481 | 19.1368 | 42 | 104 | 33 | 219 | 0 | 0 | 35 | 1 | 0.71511 | 1.2163 | 6.4929 | 5.6473 | High | Low | High | Mid | 416 | 558 | 7.8972
LAS GALLINAS A 1104 | 042991104 | BAY AREA | NORTH BAY | 1.251 | 1034461.3333 | 46 | 6.426% | 0% | 29.11% | 67.07% | 0 | 0 | 1 | 29.11% | 67.07% | 10% | 2 | 1 | 0 | 0 | 7 | 1 | 0 | 0 | 0 | 10 | 45.6667 | 1 | 1 | 1 | 3 | 0 | 0 | 1 | 0 | 0.22128 | 1 | 7.8951 | 1.747 | Low | Low | High | Bottom | 631 | 559 | 7.8951
ARLINGTON 0401 | 013700401 | BAY AREA | EAST BAY | 0.87294 | 79259.3333 | 45.2174 | 14.3% | 0% | 10.82% | 10.92% | 0 | 0 | 1 | 0% | 100% | 65.22% | 1 | 1 | 0 | 0 | 18 | 1 | 8 | 0 | 1 | 23 | 35.1818 | 2 | 4 | 2 | 11 | 0 | 0 | 1 | 0 | 0.41135 | 1 | 7.8902 | 3.2456 | Medium | Low | High | Mid | 515 | 560 | 7.8902
SAN RAFAEL 1101 | 042011101 | BAY AREA | NORTH BAY | 9.7957 | 1072501.6667 | 44.4457 | 8.888% | 2.542% | 18.89% | 70% | 7 | 0 | 20 | 18.46% | 72.98% | 10.16% | 120 | 99 | 6 | 1 | 142 | 137 | 12 | 8 | 11 | 443 | 30.6879 | 48 | 55 | 15 | 159 | 0 | 0 | 20 | 1 | 0.78794 | 1 | 7.8684 | 6.1998 | High | Low | High | Mid | 397 | 561 | 7.8684
SAND CREEK 1103 | 254601103 | CENTRAL VALLEY | FRESNO | 149.7701 | 442223.3333 | 42.4289 | 59.2% | 16.96% | 68.29% | 0.003395% | 7 | 6 | 102 | 95.28% | 0.003395% | 29.38% | 279 | 462 | 0 | 262 | 1101 | 213 | 0 | 9 | 23 | 2999 | 16.3756 | 520 | 171 | 6 | 1198 | 0 | 0 | 102 | 0 | 0.10796 | 2.3955 | 3.2681 | 0.8452 | Low | Medium | Low | Bottom | 732 | 562 | 7.8287
WILLITS 1102 | 042661102 | NORTHERN | HUMBOLDT | 6.3612 | 451490 | 43.1897 | 26.26% | 3.841% | 23.89% | 49.54% | 0 | 0 | 11 | 23.89% | 56.8% | 9.195% | 28 | 60 | 0 | 1 | 65 | 7 | 0 | 3 | 5 | 174 | 28.8636 | 15 | 20 | 10 | 66 | 0 | 0 | 11 | 0 | 0.60528 | 2.4994 | 3.0894 | 4.6739 | Medium | Medium | Low | Mid | 444 | 563 | 7.7218
RALSTON 1102 | 024141102 | CENTRAL COAST | PENINSULA | 3.4743 | 495767.6667 | 44.4444 | 15.12% | 0% | 50.03% | 1.248% | 2 | 0 | 11 | 50.03% | 1.248% | 4.444% | 4 | 5 | 0 | 0 | 81 | 2 | 0 | 6 | 8 | 90 | 28.4423 | 2 | 10 | 33 | 52 | 1 | 0 | 11 | 1 | 0.63487 | 1 | 7.6717 | 4.8705 | Medium | Low | High | Mid | 438 | 564 | 7.6717
LAKEWOOD 2109 | 013532109 | BAY AREA | DIABLO | 0.27299 | 1133254.6667 | 40.4167 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 8.333% | 0 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 12 | 57.8571 | 3 | 1 | 1 | 7 | 0 | 0 | 0 | 0 | 0.21104 | 1 | 7.6658 | 1.6177 | Low | Low | High | Bottom | 644 | 565 | 7.6658
DEL MONTE 2102 | 182222102 | CENTRAL COAST | CENTRAL COAST | 0.13454 | 1559551.3333 | 50 | 14.28% | 0% | 0% | 0% | 0 | 0 | 1 | 0% | 0% | 0% | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.27121 | 1 | 7.6365 | 2.0711 | Low | Low | High | Bottom | 595 | 566 | 7.6365
SAN RAFAEL 1105 | 042011105 | BAY AREA | NORTH BAY | 5.2298 | 1166879 | 43.9333 | 3.422% | 0% | 61.54% | 24.22% | 2 | 0 | 10 | 61.49% | 24.28% | 5.333% | 10 | 21 | 0 | 1 | 36 | 6 | 0 | 2 | 3 | 75 | 22.1 | 6 | 10 | 3 | 30 | 0 | 0 | 10 | 0 | 0.47677 | 1 | 7.6239 | 3.6348 | Medium | Low | High | Mid | 498 | 567 | 7.6239
GREENBRAE 1102 | 043091102 | BAY AREA | NORTH BAY | 7.6047 | 1050311.6667 | 43.3746 | 18.35% | 0.2032% | 39.71% | 58.87% | 20 | 1 | 7 | 35.26% | 63.87% | 3.976% | 58 | 43 | 3 | 2 | 140 | 63 | 18 | 0 | 0 | 327 | 44.2289 | 26 | 30 | 14 | 85 | 0 | 0 | 7 | 1 | 0.79759 | 1 | 7.5934 | 6.0564 | High | Low | High | Mid | 405 | 568 | 7.5934
RIDGE 0401 | 012840401 | BAY AREA | EAST BAY | 2.662 | 47847 | 44.2308 | 44.35% | 4.035% | 33.08% | 33.93% | 1 | 0 | 6 | 10.22% | 87.78% | 29.91% | 9 | 21 | 0 | 0 | 72 | 7 | 6 | 6 | 9 | 117 | 43.9 | 7 | 25 | 6 | 43 | 0 | 0 | 6 | 1 | 0.71977 | 1 | 7.5885 | 5.462 | High | Low | High | Mid | 421 | 569 | 7.5885
BERKELEY F 1105 | 012061105 | BAY AREA | EAST BAY | 1.9192 | 695082.3333 | 46.131 | 4.802% | 0% | 60.21% | 19.91% | 2 | 0 | 9 | 29.09% | 70.02% | 35.71% | 20 | 25 | 0 | 0 | 32 | 3 | 7 | 8 | 11 | 84 | 25.6364 | 6 | 9 | 2 | 23 | 0 | 0 | 9 | 0 | 0.58515 | 1 | 7.5238 | 4.4025 | Medium | Low | High | Mid | 459 | 570 | 7.5238
LAS GALLINAS A 1106 | 042991106 | BAY AREA | NORTH BAY | 6.4929 | 743147.3333 | 44.3443 | 29.21% | 0.2812% | 77.31% | 4.193% | 0 | 0 | 4 | 77.31% | 8.339% | 3.226% | 13 | 9 | 0 | 0 | 43 | 6 | 0 | 0 | 0 | 62 | 15.8235 | 3 | 3 | 4 | 17 | 0 | 0 | 4 | 0 | 0.20631 | 1 | 7.5211 | 1.5517 | Low | Low | High | Bottom | 648 | 571 | 7.5211
RIDGE 0402 | 012840402 | BAY AREA | EAST BAY | 1.857 | 62430.6667 | 43.3951 | 69.08% | 0% | 44.06% | 36.54% | 0 | 0 | 2 | 30.41% | 69.44% | 23.46% | 7 | 21 | 0 | 0 | 33 | 1 | 2 | 3 | 5 | 81 | 44.4167 | 4 | 9 | 5 | 24 | 0 | 0 | 2 | 0 | 0.56589 | 1 | 7.47 | 4.2271 | Medium | Low | High | Mid | 469 | 572 | 7.47
DIAMOND SPRINGS 1104 | 152261104 | NORTHERN | SIERRA | 15.1099 | 379179.6667 | 42.0509 | 34.6% | 39.88% | 33.95% | 17.87% | 4 | 0 | 24 | 63.86% | 27.84% | 0.2681% | 31 | 232 | 2 | 0 | 57 | 25 | 0 | 0 | 0 | 373 | 40.9058 | 65 | 43 | 2 | 141 | 0 | 0 | 24 | 0 | 0.33256 | 1.604 | 4.635 | 2.4724 | Medium | Low | Medium | Bottom | 560 | 573 | 7.4345
SARATOGA 1104 | 083371104 | CENTRAL COAST | DE ANZA | 1.8773 | 667755 | 41.3265 | 5.481% | 0% | 51.56% | 10.6% | 5 | 0 | 14 | 51.56% | 10.6% | 12.12% | 18 | 12 | 0 | 0 | 68 | 9 | 0 | 5 | 7 | 99 | 1.451 | 11 | 20 | 5 | 52 | 0 | 0 | 14 | 1 | 0.66903 | 1 | 7.4301 | 4.9709 | High | Low | High | Mid | 435 | 574 | 7.4301
BERKELEY F 0402 | 012060402 | BAY AREA | EAST BAY | 0.58346 | 175201 | 43.3333 | 30.72% | 0% | 85.64% | 13.87% | 5 | 0 | 1 | 34.97% | 64.79% | 16.67% | 1 | 1 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 6 | 42.25 | 0 | 0 | 1 | 4 | 0 | 0 | 1 | 0 | 0.29506 | 1 | 7.3537 | 2.1697 | Low | Low | High | Bottom | 588 | 575 | 7.3537
WISE 1101 | 152271101 | NORTHERN | SIERRA | 9.297 | 455854.6667 | 41.6791 | 51.02% | 0.3197% | 43.48% | 23.38% | 1 | 0 | 11 | 43.8% | 23.38% | 7.353% | 14 | 76 | 0 | 0 | 25 | 5 | 0 | 3 | 8 | 136 | 28.6667 | 22 | 12 | 1 | 55 | 0 | 0 | 11 | 0 | 0.50555 | 1.5447 | 4.7524 | 3.7113 | Medium | Low | Medium | Mid | 488 | 576 | 7.3411
SAN LUIS OBISPO 1102 | 182631102 | CENTRAL COAST | LOS PADRES | 0.68163 | 1030598 | 38.6667 | 11.17% | 0% | 99.44% | 0% | 0 | 0 | 2 | 99.03% | 0.4172% | 0% | 0 | 3 | 0 | 0 | 11 | 0 | 0 | 2 | 2 | 15 | 16.2 | 2 | 0 | 0 | 5 | 0 | 0 | 2 | 0 | 0.20447 | 1 | 7.3203 | 1.4968 | Low | Low | High | Bottom | 655 | 577 | 7.3203
SOBRANTE 1101 | 014671101 | BAY AREA | DIABLO | 16.0465 | 881948 | 45.22 | 69.58% | 1.748% | 33.94% | 22.64% | 7 | 0 | 34 | 24.53% | 33.92% | 34.66% | 179 | 102 | 0 | 0 | 235 | 16 | 0 | 6 | 21 | 502 | 27.0992 | 80 | 107 | 25 | 261 | 0 | 0 | 34 | 0 | 0.50746 | 1.13 | 6.3636 | 3.6492 | Medium | Low | High | Mid | 494 | 578 | 7.1911
PACIFICA 1104 | 022811104 | CENTRAL COAST | PENINSULA | 0.58219 | 361086.3333 | 46.4706 | 2.809% | 14.66% | 0% | 75.59% | 0 | 0 | 4 | 0% | 90.25% | 11.76% | 6 | 3 | 0 | 0 | 12 | 1 | 0 | 1 | 1 | 17 | 4.5 | 1 | 2 | 0 | 6 | 0 | 0 | 4 | 0 | 0.30434 | 1.1676 | 6.1375 | 2.1809 | Low | Low | High | Bottom | 586 | 579 | 7.1662
TASSAJARA 2103 | 014662103 | BAY AREA | DIABLO | 1.9027 | 1249838.6667 | 41.7647 | 38.85% | 0% | 16.52% | 63.81% | 0 | 0 | 2 | 16.52% | 63.81% | 0% | 0 | 1 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 17 | 42.8571 | 0 | 3 | 2 | 8 | 0 | 0 | 1 | 0 | 0.27399 | 1 | 7.1533 | 1.9599 | Low | Low | High | Bottom | 608 | 580 | 7.1533
LAKEWOOD 2110 | 013532110 | BAY AREA | DIABLO | 0.50309 | 1187370 | 0 | 9.113% | 0% | 73.94% | 10.16% | 0 | 0 | 0 | 31.68% | 52.42% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15113 | 1 | 7.1259 | 1.0769 | Low | Low | High | Bottom | 698 | 581 | 7.1259
PACIFICA 1101 | 022811101 | CENTRAL COAST | PENINSULA | 3.269 | 247844 | 42.5 | 32.81% | 0% | 49.98% | 0.5257% | 0 | 0 | 1 | 45.54% | 5.147% | 0% | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 52.4211 | 4 | 10 | 3 | 19 | 0 | 0 | 1 | 0 | 0.34121 | 1.1629 | 6.0989 | 2.42 | Medium | Low | High | Bottom | 565 | 582 | 7.0923
MORRO BAY 1102 | 183011102 | CENTRAL COAST | LOS PADRES | 22.9719 | 1059852 | 40.6152 | 47.97% | 1.978% | 7.314% | 71.06% | 2 | 0 | 42 | 9.464% | 79.15% | 7.58% | 30 | 25 | 0 | 36 | 189 | 27 | 8 | 8 | 10 | 343 | 24.2749 | 67 | 24 | 19 | 178 | 0 | 0 | 42 | 0 | 0.48819 | 1.0414 | 6.7615 | 3.4375 | Medium | Low | High | Mid | 507 | 583 | 7.0412
LOS GATOS 1102 | 082021102 | CENTRAL COAST | DE ANZA | 1.2351 | 613031.3333 | 42.3276 | 8.803% | 0% | 53.25% | 36.39% | 2 | 0 | 4 | 53.25% | 46.75% | 18.97% | 3 | 20 | 0 | 2 | 23 | 8 | 0 | 2 | 2 | 58 | 0 | 7 | 7 | 7 | 22 | 0 | 0 | 4 | 1 | 0.63391 | 1 | 7.0409 | 4.4633 | Medium | Low | High | Mid | 453 | 584 | 7.0409
SARATOGA 1106 | 083371106 | CENTRAL COAST | DE ANZA | 13.828 | 910023.6667 | 44.5 | 22.41% | 7.284% | 44.05% | 36.05% | 8 | 0 | 47 | 38.59% | 57.45% | 11.41% | 126 | 142 | 0 | 5 | 232 | 41 | 20 | 14 | 23 | 491 | 2.0973 | 57 | 82 | 31 | 237 | 0 | 0 | 47 | 0 | 0.62822 | 1 | 7.0258 | 4.4137 | Medium | Low | High | Mid | 456 | 585 | 7.0258
ALTO 1123 | 042031123 | BAY AREA | NORTH BAY | 2.6839 | 971672 | 44 | 94.03% | 0% | 2.992% | 46.14% | 0 | 0 | 1 | 2.992% | 46.14% | 15% | 3 | 3 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 20 | 56 | 1 | 1 | 2 | 4 | 0 | 0 | 1 | 0 | 0.33055 | 1 | 6.9911 | 2.3109 | Medium | Low | High | Bottom | 580 | 586 | 6.9911
IGNACIO 1103 | 042481103 | BAY AREA | NORTH BAY | 0.10132 | 793294.3333 | 47.1429 | 27.36% | 0% | 0% | 100% | 0 | 0 | 2 | 0% | 100% | 21.43% | 5 | 3 | 0 | 0 | 3 | 7 | 0 | 0 | 1 | 14 | 31.1429 | 2 | 2 | 1 | 7 | 0 | 0 | 2 | 1 | 0.29363 | 1 | 6.9815 | 2.05 | Low | Low | High | Bottom | 599 | 587 | 6.9815
KERCKHOFF 1101 | 252561101 | CENTRAL VALLEY | YOSEMITE | 34.5924 | 62243 | 40.0179 | 33.34% | 4.787% | 62.85% | 7.22% | 1 | 1 | 27 | 58.51% | 16.85% | 24.91% | 30 | 41 | 0 | 24 | 284 | 29 | 0 | 6 | 16 | 570 | 16.9306 | 55 | 29 | 3 | 165 | 0 | 0 | 27 | 0 | 0.29197 | 2.3844 | 2.9222 | 2.0344 | Low | Low | Low | Bottom | 601 | 588 | 6.9676
VALLEY VIEW 1105 | 014341105 | BAY AREA | EAST BAY | 5.9477 | 821930 | 43.2258 | 0% | 0% | 55.14% | 25.83% | 5 | 0 | 7 | 39.76% | 41.21% | 15.48% | 12 | 23 | 0 | 1 | 87 | 2 | 0 | 1 | 1 | 155 | 16.8333 | 17 | 18 | 1 | 49 | 0 | 0 | 7 | 0 | 0.62058 | 1 | 6.9552 | 4.3163 | Medium | Low | High | Mid | 461 | 589 | 6.9552
WYANDOTTE 1110 | 102911110 | NORTHERN | NORTH VALLEY | 15.7768 | 980007.6667 | 42.2344 | 73.74% | 0.1738% | 61.82% | 17.2% | 2 | 0 | 13 | 62% | 17.2% | 3.125% | 24 | 189 | 1 | 0 | 43 | 39 | 0 | 1 | 3 | 320 | 52.8548 | 59 | 30 | 3 | 133 | 0 | 2 | 13 | 0 | 0.2573 | 1 | 6.8825 | 1.7709 | Low | Low | High | Bottom | 628 | 590 | 6.8825
OAKLAND X 1101 | 012541101 | BAY AREA | EAST BAY | 0.53647 | 356371.6667 | 46.3462 | 2.387% | 0% | 23.35% | 23.76% | 0 | 0 | 0 | 23.35% | 67.92% | 19.23% | 11 | 2 | 0 | 1 | 14 | 3 | 0 | 2 | 4 | 26 | 26.875 | 2 | 4 | 1 | 8 | 0 | 0 | 0 | 0 | 0.39383 | 1 | 6.8698 | 2.7056 | Medium | Low | High | Bottom | 545 | 591 | 6.8698
ALTO 1121 | 042031121 | BAY AREA | NORTH BAY | 0.066131 | 581015 | 0 | 1.842% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15069 | 1 | 6.8577 | 1.0334 | Low | Low | High | Bottom | 707 | 592 | 6.8577
WOOD 0401 | 013380401 | BAY AREA | EAST BAY | 0.4661 | 127718.3333 | 45 | 0% | 0% | 99.35% | 0% | 1 | 0 | 0 | 46.88% | 52.82% | 42.86% | 2 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 7 | 70 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0.2397 | 1 | 6.8397 | 1.6395 | Low | Low | High | Bottom | 640 | 593 | 6.8397
ROSSMOOR 1102 | 014161102 | BAY AREA | DIABLO | 0.23759 | 508088.6667 | 55 | 490.6% | 0% | 0% | 0% | 0 | 0 | 1 | 0% | 0% | 16.67% | 6 | 5 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.31985 | 1 | 6.8316 | 2.1851 | Low | Low | High | Bottom | 585 | 594 | 6.8316
SAN RAMON 2117 | 014232117 | CENTRAL COAST | MISSION | 0.67335 | 1594385.6667 | 55 | 450.4% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 100% | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31589 | 1 | 6.8118 | 2.1518 | Low | Low | High | Bottom | 589 | 595 | 6.8118
SAN RAMON 2119 | 014232119 | CENTRAL COAST | MISSION | 0.72877 | 1190973.3333 | 0 | 366.8% | 0% | 0% | 0% | 0 | 0 | 1 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.28888 | 1 | 6.8115 | 1.9677 | Low | Low | High | Bottom | 606 | 596 | 6.8115
SAN RAMON 2101 | 014232101 | CENTRAL COAST | MISSION | 0.78266 | 1284209.3333 | 56 | 353.9% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 13.33% | 14 | 3 | 0 | 0 | 1 | 2 | 0 | 0 | 1 | 15 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.25765 | 1 | 6.8071 | 1.7539 | Low | Low | High | Bottom | 630 | 597 | 6.8071
ROSSMOOR 1106 | 014161106 | BAY AREA | DIABLO | 4.9819 | 896923 | 44.3871 | 65.85% | 0% | 48.66% | 32.51% | 3 | 0 | 8 | 38.49% | 42.67% | 11.54% | 31 | 45 | 0 | 0 | 65 | 3 | 0 | 1 | 3 | 156 | 21.7564 | 16 | 37 | 10 | 79 | 0 | 0 | 8 | 1 | 0.72089 | 1 | 6.7743 | 4.8836 | High | Low | High | Mid | 436 | 598 | 6.7743
LAKEWOOD 2224 | 013532224 | BAY AREA | DIABLO | 1.1155 | 828489.6667 | 44.6 | 15.02% | 0% | 86.93% | 13.07% | 1 | 0 | 1 | 28.76% | 71.24% | 8% | 8 | 8 | 0 | 0 | 11 | 1 | 0 | 0 | 0 | 25 | 53.3636 | 3 | 7 | 0 | 11 | 0 | 0 | 1 | 0 | 0.27727 | 1 | 6.7667 | 1.8762 | Low | Low | High | Bottom | 618 | 599 | 6.7667
FLORENCE 0401 | 012690401 | BAY AREA | EAST BAY | 1.7951 | 74733 | 44.0323 | 0% | 0% | 13.98% | 22.65% | 5 | 0 | 3 | 2.192% | 89.6% | 37.5% | 5 | 3 | 0 | 0 | 14 | 1 | 10 | 0 | 3 | 32 | 44.8 | 6 | 4 | 0 | 10 | 0 | 0 | 3 | 1 | 0.72014 | 1 | 6.7634 | 4.8706 | High | Low | High | Mid | 437 | 600 | 6.7634
PALO SECO 0401 | 013180401 | BAY AREA | EAST BAY | 4.7078 | 111604.3333 | 45.0439 | 0% | 13.34% | 29.12% | 13.74% | 0 | 0 | 12 | 0% | 81.88% | 55.26% | 21 | 7 | 0 | 0 | 52 | 12 | 4 | 0 | 7 | 114 | 55.5227 | 9 | 24 | 7 | 46 | 0 | 0 | 12 | 1 | 0.62874 | 1 | 6.7383 | 4.2367 | Medium | Low | High | Mid | 467 | 601 | 6.7383
SMARTVILLE 1101 | 153791101 | NORTHERN | SIERRA | 15.8868 | 96105 | 43.9017 | 44.78% | 0.3694% | 81.7% | 10.89% | 0 | 0 | 17 | 82.07% | 10.89% | 2.586% | 50 | 90 | 43 | 0 | 55 | 13 | 0 | 4 | 6 | 348 | 35.8868 | 50 | 28 | 2 | 115 | 0 | 1 | 17 | 0 | 0.16709 | 1.4125 | 4.7638 | 1.1243 | Low | Low | Medium | Bottom | 694 | 602 | 6.7286
BRYANT 0402 | 013090402 | BAY AREA | DIABLO | 1.5416 | 135820.3333 | 44.8026 | 0% | 38.71% | 10.43% | 50.86% | 2 | 0 | 2 | 3.005% | 96.99% | 23.68% | 31 | 17 | 0 | 0 | 29 | 1 | 0 | 0 | 0 | 76 | 42.2727 | 7 | 19 | 4 | 33 | 0 | 0 | 2 | 0 | 0.56816 | 1 | 6.7117 | 3.8133 | Medium | Low | High | Mid | 484 | 603 | 6.7117
LOS GATOS 1108 | 082021108 | CENTRAL COAST | DE ANZA | 4.3173 | 505778.6667 | 44.1867 | 16.21% | 3.661% | 40.4% | 44.3% | 7 | 0 | 17 | 37.17% | 62.08% | 5.422% | 43 | 69 | 0 | 7 | 66 | 8 | 0 | 7 | 10 | 166 | 1.1447 | 15 | 23 | 15 | 78 | 0 | 0 | 17 | 1 | 0.77051 | 1 | 6.6966 | 5.1598 | High | Low | High | Mid | 426 | 604 | 6.6966
STILLWATER 1102 | 103561102 | NORTHERN | NORTH VALLEY | 78.3748 | 518238.3333 | 42.6453 | 42.29% | 77.66% | 16.93% | 0% | 8 | 5 | 63 | 94.68% | 0% | 11.96% | 241 | 1330 | 52 | 2 | 272 | 284 | 0 | 18 | 25 | 2299 | 46.4434 | 381 | 218 | 12 | 843 | 0 | 7 | 63 | 0 | 0.079759 | 1.606 | 4.1614 | 0.53305 | Low | Low | Medium | Bottom | 763 | 605 | 6.6833
PAUL SWEET 2102 | 083252102 | CENTRAL COAST | CENTRAL COAST | 5.5176 | 1317659.6667 | 45.1149 | 107.4% | 0.05154% | 26.6% | 40.14% | 9 | 2 | 13 | 25.82% | 42.53% | 4.598% | 17 | 29 | 0 | 3 | 36 | 5 | 5 | 5 | 10 | 87 | 63 | 5 | 3 | 0 | 31 | 0 | 0 | 13 | 1 | 0.76947 | 1 | 6.6814 | 5.1412 | High | Low | High | Mid | 428 | 606 | 6.6814
GREENBRAE 1104 | 043091104 | BAY AREA | NORTH BAY | 0.37143 | 843442.6667 | 44.5455 | 40.95% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 10 | 1 | 0 | 0 | 0 | 11 | 10.3333 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0.11506 | 1 | 6.6496 | 0.76508 | Low | Low | High | Bottom | 741 | 607 | 6.6496
HOLLYWOOD 0401 | 013170401 | BAY AREA | EAST BAY | 3.0693 | 172815 | 47.0073 | 0% | 5.048% | 50.61% | 12.22% | 0 | 0 | 8 | 0% | 100% | 62.77% | 57 | 17 | 0 | 0 | 63 | 2 | 6 | 3 | 7 | 137 | 42.7857 | 4 | 15 | 10 | 42 | 0 | 0 | 8 | 0 | 0.51878 | 1 | 6.6406 | 3.445 | Medium | Low | High | Mid | 505 | 608 | 6.6406
PAUL SWEET 2109 | 083252109 | CENTRAL COAST | CENTRAL COAST | 4.8379 | 921379.3333 | 44.5181 | 6.578% | 0.1206% | 62.21% | 29.35% | 0 | 1 | 8 | 63.94% | 30.95% | 9.639% | 12 | 40 | 0 | 1 | 27 | 8 | 0 | 2 | 2 | 83 | 39.5957 | 16 | 10 | 3 | 47 | 1 | 0 | 8 | 1 | 0.55732 | 1 | 6.6296 | 3.6948 | Medium | Low | High | Mid | 490 | 609 | 6.6296
JARVIS 1108 | 013501108 | CENTRAL COAST | MISSION | 2.883 | 835206 | 41.2963 | 15.24% | 0.1315% | 50.79% | 48.89% | 0 | 0 | 6 | 34.3% | 65.38% | 7.407% | 2 | 5 | 0 | 0 | 18 | 0 | 0 | 1 | 1 | 27 | 14.1667 | 0 | 4 | 2 | 8 | 0 | 0 | 6 | 0 | 0.38853 | 1 | 6.6173 | 2.571 | Medium | Low | High | Bottom | 555 | 610 | 6.6173
BOSTON 0401 | 013320401 | BAY AREA | EAST BAY | 0.68358 | 0 | 45 | 63.38% | 0% | 19.82% | 0% | 0 | 0 | 0 | 0% | 100% | 88.89% | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 9 | 25 | 0 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 0.21197 | 1 | 6.6079 | 1.4007 | Low | Low | High | Bottom | 671 | 611 | 6.6079
OAKLAND K 1103 | 012101103 | BAY AREA | EAST BAY | 6.1448 | 472078.6667 | 45.4792 | 27.36% | 5.229% | 42.94% | 15.12% | 10 | 2 | 23 | 29.51% | 44.46% | 25% | 57 | 57 | 1 | 3 | 97 | 24 | 15 | 8 | 19 | 240 | 30.7857 | 19 | 34 | 8 | 72 | 0 | 0 | 22 | 0 | 0.76445 | 1 | 6.5519 | 5.0086 | High | Low | High | Mid | 434 | 612 | 6.5519
VIEJO 2201 | 182852201 | CENTRAL COAST | CENTRAL COAST | 16.3884 | 946231 | 42.2955 | 14.97% | 2.949% | 36.71% | 23.86% | 23 | 5 | 55 | 17.52% | 59.59% | 15.56% | 60 | 143 | 0 | 9 | 246 | 32 | 37 | 17 | 28 | 540 | 36.5947 | 46 | 66 | 13 | 200 | 3 | 0 | 55 | 1 | 0.8768 | 1 | 6.5488 | 5.742 | High | Low | High | Mid | 414 | 613 | 6.5488
OAKLAND X 1105 | 012541105 | BAY AREA | EAST BAY | 4.3515 | 707029.6667 | 44.5041 | 18.3% | 0% | 68.95% | 30.73% | 1 | 1 | 2 | 20.97% | 79.03% | 36.59% | 26 | 17 | 0 | 2 | 77 | 17 | 16 | 1 | 1 | 123 | 15.6053 | 5 | 18 | 6 | 38 | 0 | 0 | 2 | 0 | 0.53834 | 1 | 6.5414 | 3.5215 | Medium | Low | High | Mid | 501 | 614 | 6.5414
LAS AROMAS 0401 | 013600401 | BAY AREA | DIABLO | 5.9862 | 115734 | 44.5026 | 0% | 0.1907% | 68.28% | 16.32% | 8 | 2 | 14 | 1.339% | 87.73% | 31.09% | 41 | 59 | 0 | 6 | 68 | 9 | 8 | 2 | 6 | 193 | 44.6915 | 12 | 54 | 15 | 94 | 0 | 0 | 14 | 0 | 0.65372 | 1 | 6.5306 | 4.2692 | Medium | Low | High | Mid | 462 | 615 | 6.5306
OAKLAND J 1116 | 012091116 | BAY AREA | EAST BAY | 0.10355 | 1036186 | 40.7143 | 7.798% | 0% | 100% | 0% | 0 | 0 | 0 | 0% | 100% | 42.86% | 0 | 1 | 0 | 0 | 4 | 2 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13957 | 1 | 6.4353 | 0.89816 | Low | Low | High | Bottom | 724 | 616 | 6.4353
PARADISE 1103 | 102831103 | NORTHERN | NORTH VALLEY | 41.5864 | 1124803.6667 | 43.0094 | 10.11% | 2.857% | 56.83% | 26.25% | 25 | 6 | 65 | 61.46% | 28.58% | 6.832% | 206 | 569 | 65 | 1 | 406 | 109 | 41 | 23 | 35 | 1493 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 65 | 1 | 0.74929 | 1.0005 | 6.4304 | 4.8204 | High | Low | High | Mid | 440 | 617 | 6.4334
HORSESHOE 1104 | 152571104 | NORTHERN | SIERRA | 1.2893 | 585906.6667 | 44.8571 | 33.6% | 0% | 91.7% | 0% | 0 | 0 | 5 | 91.7% | 0% | 0% | 3 | 29 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 35 | 41.963 | 7 | 17 | 2 | 29 | 0 | 0 | 5 | 0 | 0.264 | 1 | 6.3837 | 1.6853 | Low | Low | High | Bottom | 636 | 618 | 6.3837
SARATOGA 1103 | 083371103 | CENTRAL COAST | DE ANZA | 4.5983 | 534592 | 42.6816 | 20.02% | 8.864% | 37.78% | 34.42% | 5 | 1 | 19 | 46.64% | 34.42% | 10.61% | 27 | 30 | 0 | 0 | 120 | 10 | 0 | 5 | 9 | 179 | 8.0513 | 16 | 31 | 12 | 78 | 0 | 0 | 19 | 1 | 0.796 | 1 | 6.3393 | 5.0461 | High | Low | High | Mid | 432 | 619 | 6.3393
PACIFIC GROVE 0422 | 182440422 | CENTRAL COAST | CENTRAL COAST | 0.65447 | 111011.6667 | 48.9286 | 104.5% | 0% | 0% | 0% | 0 | 0 | 1 | 0% | 100% | 0% | 13 | 11 | 0 | 0 | 1 | 2 | 2 | 2 | 3 | 14 | 5.3333 | 0 | 2 | 0 | 3 | 0 | 0 | 1 | 0 | 0.2389 | 1 | 6.3303 | 1.5123 | Low | Low | High | Bottom | 652 | 620 | 6.3303
ROSSMOOR 1104 | 014161104 | BAY AREA | DIABLO | 0.29689 | 875410 | 42.7778 | 3.845% | 0% | 100% | 0% | 0 | 0 | 1 | 16.15% | 83.85% | 55.56% | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 9 | 5.5 | 3 | 2 | 0 | 6 | 0 | 0 | 1 | 0 | 0.21373 | 1 | 6.3299 | 1.3529 | Low | Low | High | Bottom | 675 | 621 | 6.3299
WISHON 1101 | 251511101 | CENTRAL VALLEY | YOSEMITE | 7.7822 | 4220 | 42.7477 | 0% | 27.36% | 72.21% | 0.4235% | 0 | 0 | 2 | 78.45% | 21.55% | 12.7% | 24 | 8 | 0 | 1 | 40 | 3 | 0 | 0 | 4 | 126 | 14.7692 | 6 | 5 | 1 | 19 | 0 | 0 | 2 | 0 | 0.30598 | 2.4093 | 2.6231 | 1.9338 | Low | Medium | Low | Bottom | 611 | 622 | 6.3199
OAKLAND J 1102 | 012091102 | BAY AREA | EAST BAY | 6.3189 | 965953.6667 | 45.3663 | 11.05% | 2.379% | 37.3% | 29.17% | 5 | 1 | 22 | 16.33% | 55.88% | 17.88% | 66 | 47 | 1 | 0 | 190 | 5 | 0 | 9 | 15 | 274 | 20.1216 | 17 | 29 | 12 | 78 | 0 | 0 | 22 | 0 | 0.7059 | 1 | 6.3192 | 4.4607 | High | Low | High | Mid | 454 | 623 | 6.3192
HORSESHOE 1101 | 152571101 | NORTHERN | SIERRA | 7.1108 | 675190 | 44.3243 | 32.3% | 0% | 61.55% | 2.707% | 0 | 0 | 11 | 61.55% | 2.707% | 2.703% | 13 | 79 | 0 | 0 | 8 | 3 | 0 | 2 | 8 | 111 | 44.2979 | 20 | 19 | 2 | 48 | 0 | 0 | 11 | 1 | 0.48077 | 1 | 6.2542 | 3.0068 | Medium | Low | High | Mid | 526 | 624 | 6.2542
VIEJO 2202 | 182852202 | CENTRAL COAST | CENTRAL COAST | 14.9046 | 1361490 | 42.5173 | 30.45% | 2.66% | 35.44% | 27.21% | 20 | 5 | 47 | 9.565% | 64.62% | 10.2% | 74 | 91 | 0 | 10 | 244 | 15 | 8 | 20 | 36 | 549 | 40.142 | 55 | 54 | 11 | 174 | 0 | 0 | 47 | 1 | 0.85804 | 1 | 6.2054 | 5.3245 | High | Low | High | Mid | 424 | 625 | 6.2054
WYANDOTTE 1105 | 102911105 | NORTHERN | NORTH VALLEY | 21.9604 | 306464.3333 | 41.028 | 95.88% | 0.04982% | 14.35% | 22.69% | 1 | 2 | 5 | 14.65% | 72.03% | 7.009% | 10 | 85 | 6 | 0 | 42 | 12 | 0 | 1 | 1 | 214 | 47.7627 | 30 | 8 | 0 | 64 | 0 | 1 | 5 | 1 | 0.59769 | 1.054 | 5.8853 | 3.7074 | Medium | Low | High | Mid | 489 | 626 | 6.2028
LOS GATOS 1101 | 082021101 | CENTRAL COAST | DE ANZA | 10.2975 | 1000993 | 42.8101 | 22.58% | 2.826% | 54.09% | 41.84% | 13 | 0 | 46 | 54.67% | 44.09% | 4.545% | 80 | 146 | 0 | 0 | 197 | 11 | 0 | 18 | 23 | 396 | 6.3576 | 40 | 67 | 31 | 171 | 0 | 0 | 46 | 1 | 0.72044 | 1 | 6.1605 | 4.4382 | High | Low | High | Mid | 455 | 627 | 6.1605
OAKLAND J 1105 | 012091105 | BAY AREA | EAST BAY | 4.233 | 793234 | 44.6842 | 11.74% | 0% | 44.34% | 17.04% | 1 | 2 | 2 | 6.234% | 55.15% | 21.05% | 17 | 10 | 0 | 0 | 59 | 7 | 0 | 3 | 4 | 95 | 27.4615 | 6 | 12 | 7 | 27 | 0 | 0 | 2 | 0 | 0.61111 | 1 | 6.1504 | 3.7586 | Medium | Low | High | Mid | 487 | 628 | 6.1504
TAR FLAT 0402 | 163240402 | CENTRAL VALLEY | YOSEMITE | 5.7251 | 92911.3333 | 42.6374 | 0% | 0% | 24.67% | 60.03% | 0 | 0 | 4 | 24.18% | 71.75% | 5.464% | 26 | 85 | 0 | 0 | 53 | 22 | 0 | 0 | 0 | 183 | 37.6418 | 16 | 30 | 8 | 73 | 0 | 0 | 4 | 0 | 0.51697 | 1.162 | 5.2879 | 3.1764 | Medium | Low | Medium | Mid | 518 | 629 | 6.1443
OAKLAND K 1101 | 012101101 | BAY AREA | EAST BAY | 2.9361 | 516942 | 45.087 | 22.59% | 12.38% | 15.6% | 21.08% | 3 | 0 | 10 | 13.33% | 55.83% | 51.3% | 49 | 12 | 0 | 0 | 81 | 7 | 8 | 10 | 17 | 115 | 17.4643 | 6 | 10 | 8 | 30 | 0 | 0 | 10 | 0 | 0.65841 | 1 | 6.1353 | 4.0395 | Medium | Low | High | Mid | 475 | 630 | 6.1353
TIDEWATER 2106 | 014652106 | BAY AREA | DIABLO | 9.2683 | 1632499.3333 | 44.5088 | 0% | 0% | 11.65% | 21.24% | 1 | 0 | 4 | 14.27% | 21.24% | 39.47% | 15 | 25 | 0 | 0 | 25 | 10 | 0 | 0 | 0 | 114 | 46.9231 | 5 | 7 | 5 | 30 | 0 | 0 | 4 | 0 | 0.5414 | 1.1373 | 5.3892 | 3.3182 | Medium | Low | High | Mid | 512 | 631 | 6.129
CLAYTON 2217 | 012022217 | BAY AREA | DIABLO | 0.67567 | 1167387 | 0 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14964 | 1 | 6.1247 | 0.9165 | Low | Low | High | Bottom | 720 | 632 | 6.1247
TIVY VALLEY 1107 | 252941107 | CENTRAL VALLEY | FRESNO | 122.1496 | 758900.6667 | 41.6268 | 53.64% | 15.55% | 80.65% | 0.7768% | 9 | 3 | 84 | 95.12% | 3.052% | 28.24% | 106 | 204 | 0 | 190 | 680 | 182 | 0 | 12 | 26 | 2015 | 18.0469 | 337 | 162 | 16 | 823 | 0 | 1 | 82 | 0 | 0.1277 | 2.3799 | 2.5509 | 0.77522 | Low | Low | Low | Bottom | 739 | 633 | 6.0709
FRANKLIN 1104 | 013921104 | BAY AREA | EAST BAY | 7.4881 | 983534.6667 | 48.2593 | 0% | 33.02% | 23.93% | 13.79% | 0 | 0 | 9 | 23.93% | 58.85% | 17.99% | 81 | 36 | 0 | 9 | 30 | 5 | 0 | 2 | 6 | 139 | 16.2917 | 10 | 6 | 1 | 29 | 0 | 0 | 9 | 0 | 0.47096 | 1 | 6.0394 | 2.8443 | Medium | Low | High | Mid | 537 | 634 | 6.0394
SEACLIFF 0402 | 083500402 | CENTRAL COAST | CENTRAL COAST | 1.0712 | 24358 | 40 | 86.6% | 0% | 21.9% | 76.41% | 1 | 0 | 0 | 21.9% | 76.41% | 0% | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.17641 | 1 | 5.9918 | 1.057 | Low | Low | High | Bottom | 702 | 635 | 5.9918
SARATOGA 1105 | 083371105 | CENTRAL COAST | DE ANZA | 9.944 | 515332 | 44.3932 | 22.52% | 0.1397% | 67.73% | 19.61% | 1 | 0 | 36 | 68.56% | 19.61% | 10.68% | 52 | 50 | 0 | 1 | 101 | 12 | 0 | 10 | 16 | 206 | 4.8586 | 28 | 23 | 13 | 103 | 0 | 0 | 35 | 1 | 0.61503 | 1 | 5.9343 | 3.6498 | Medium | Low | High | Mid | 493 | 636 | 5.9343
VIEJO 2204 | 182852204 | CENTRAL COAST | CENTRAL COAST | 4.1676 | 1493490.3333 | 42.637 | 35.66% | 11.26% | 51.09% | 16.76% | 4 | 0 | 10 | 18.87% | 58.93% | 10.27% | 14 | 43 | 0 | 0 | 35 | 9 | 0 | 2 | 4 | 146 | 41.2093 | 13 | 19 | 0 | 44 | 2 | 0 | 10 | 1 | 0.76053 | 1 | 5.9272 | 4.5078 | High | Low | High | Mid | 450 | 637 | 5.9272
HICKS 1116 | 083431116 | CENTRAL COAST | SAN JOSE | 11.3852 | 890645.3333 | 43.0429 | 1.727% | 1.957% | 55.88% | 39.91% | 5 | 0 | 50 | 57.84% | 39.91% | 10.13% | 79 | 100 | 0 | 1 | 184 | 20 | 0 | 6 | 11 | 375 | 3.5269 | 49 | 80 | 15 | 190 | 0 | 0 | 50 | 0 | 0.54573 | 1 | 5.923 | 3.2323 | Medium | Low | High | Mid | 516 | 638 | 5.923
MONTEREY 0401 | 182090401 | CENTRAL COAST | CENTRAL COAST | 0.30119 | 192386.6667 | 42.7273 | 79.84% | 0% | 69.45% | 19.02% | 0 | 0 | 0 | 0% | 88.47% | 18.18% | 0 | 2 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 11 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.16998 | 1 | 5.9171 | 1.0058 | Low | Low | High | Bottom | 711 | 639 | 5.9171
RIO DEL MAR 0402 | 083260402 | CENTRAL COAST | CENTRAL COAST | 2.2696 | 70566 | 44.4444 | 36.28% | 0% | 12.34% | 59.43% | 1 | 0 | 0 | 12.34% | 83.34% | 7.937% | 15 | 17 | 0 | 1 | 23 | 6 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34848 | 1 | 5.8894 | 2.0523 | Medium | Low | High | Bottom | 597 | 640 | 5.8894
RALSTON 1101 | 024141101 | CENTRAL COAST | PENINSULA | 9.8432 | 1073316 | 44.1255 | 43.03% | 0% | 58.71% | 8.348% | 2 | 0 | 19 | 50.06% | 17.08% | 4.943% | 23 | 25 | 0 | 0 | 220 | 7 | 0 | 7 | 15 | 263 | 18.449 | 14 | 43 | 19 | 102 | 0 | 0 | 18 | 0 | 0.4125 | 1 | 5.8789 | 2.425 | Medium | Low | High | Bottom | 564 | 641 | 5.8789
MONTEREY 0402 | 182090402 | CENTRAL COAST | CENTRAL COAST | 0.9685 | 192008.6667 | 43.6842 | 38.49% | 29.84% | 0% | 41.97% | 0 | 0 | 1 | 0% | 75.46% | 42.11% | 0 | 4 | 0 | 0 | 17 | 1 | 0 | 0 | 0 | 38 | 69.5 | 2 | 4 | 1 | 10 | 0 | 0 | 1 | 1 | 0.50618 | 1 | 5.8785 | 2.9756 | Medium | Low | High | Mid | 527 | 642 | 5.8785
LAKEWOOD 1102 | 013531102 | BAY AREA | DIABLO | 0.5008 | 379090.6667 | 38.3333 | 6.308% | 0% | 17.16% | 1.022% | 0 | 0 | 0 | 17.16% | 1.022% | 0% | 1 | 2 | 0 | 0 | 3 | 0 | 0 | 1 | 1 | 6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.40858 | 1 | 5.8765 | 2.401 | Medium | Low | High | Bottom | 569 | 643 | 5.8765
RIO DEL MAR 0401 | 083260401 | CENTRAL COAST | CENTRAL COAST | 1.8233 | 68016.3333 | 53.75 | 36.6% | 0% | 18.3% | 26.83% | 0 | 0 | 0 | 18.3% | 28.42% | 25% | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25383 | 1 | 5.8637 | 1.4884 | Low | Low | High | Bottom | 659 | 644 | 5.8637
WYANDOTTE 1102 | 102911102 | NORTHERN | NORTH VALLEY | 5.4206 | 1395187 | 43.9773 | 194% | 1.413% | 56.1% | 42.49% | 1 | 0 | 1 | 57.51% | 42.49% | 13.64% | 16 | 28 | 0 | 0 | 18 | 7 | 0 | 1 | 1 | 88 | 36.1875 | 6 | 4 | 1 | 19 | 0 | 0 | 1 | 0 | 0.46516 | 1 | 5.8389 | 2.716 | Medium | Low | High | Bottom | 544 | 645 | 5.8389
VIEJO 2203 | 182852203 | CENTRAL COAST | CENTRAL COAST | 3.9689 | 655455 | 47.4405 | 29.55% | 20.94% | 33.14% | 15.69% | 11 | 0 | 10 | 19.76% | 54.06% | 4.762% | 29 | 35 | 0 | 0 | 23 | 4 | 0 | 2 | 2 | 84 | 31.0909 | 7 | 4 | 1 | 23 | 0 | 0 | 9 | 1 | 0.72996 | 1 | 5.8229 | 4.2505 | High | Low | High | Mid | 464 | 646 | 5.8229
CARMEL 0402 | 182040402 | CENTRAL COAST | CENTRAL COAST | 0.32816 | 137085.6667 | 43.6364 | 1.047% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 80.99% | 18.18% | 0 | 3 | 0 | 0 | 6 | 0 | 0 | 1 | 1 | 11 | 4.3333 | 2 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.25216 | 1 | 5.8204 | 1.4677 | Low | Low | High | Bottom | 663 | 647 | 5.8204
FAIRVIEW 2207 | 013432207 | BAY AREA | DIABLO | 19.4269 | 1298953.3333 | 45.1845 | 0% | 5.883% | 33.15% | 20.54% | 2 | 3 | 24 | 18.87% | 51.21% | 13.57% | 110 | 168 | 0 | 1 | 148 | 8 | 22 | 12 | 35 | 516 | 29.1304 | 31 | 47 | 16 | 127 | 0 | 1 | 24 | 0 | 0.56089 | 1 | 5.8156 | 3.2619 | Medium | Low | High | Mid | 514 | 648 | 5.8156
OAKLAND J 1106 | 012091106 | BAY AREA | EAST BAY | 2.1598 | 785426.6667 | 44.6939 | 12.6% | 0% | 84.43% | 0% | 1 | 0 | 4 | 42.42% | 48.74% | 30.61% | 18 | 15 | 0 | 0 | 67 | 5 | 0 | 2 | 5 | 98 | 31.7273 | 5 | 9 | 3 | 24 | 0 | 0 | 4 | 0 | 0.40115 | 1 | 5.7729 | 2.3158 | Medium | Low | High | Bottom | 579 | 649 | 5.7729
SARATOGA 1115 | 083371115 | CENTRAL COAST | DE ANZA | 2.7261 | 861060.6667 | 43.0137 | 15.13% | 0% | 38.53% | 57.64% | 2 | 0 | 10 | 38.53% | 61.47% | 13.7% | 15 | 21 | 1 | 0 | 37 | 5 | 0 | 1 | 1 | 73 | 1.8684 | 9 | 8 | 2 | 38 | 0 | 0 | 9 | 0 | 0.60994 | 1 | 5.7678 | 3.518 | Medium | Low | High | Mid | 502 | 650 | 5.7678
DEL MAR 2109 | 152582109 | NORTHERN | SIERRA | 2.624 | 1116486 | 46.5385 | 117.4% | 0.5586% | 32.91% | 8.774% | 0 | 0 | 2 | 33.47% | 8.774% | 15.38% | 10 | 7 | 0 | 0 | 2 | 3 | 0 | 2 | 7 | 26 | 44 | 7 | 3 | 0 | 11 | 0 | 0 | 2 | 0 | 0.35594 | 1.3653 | 4.2223 | 2.0519 | Medium | Low | Medium | Bottom | 598 | 651 | 5.7648
FRANKLIN 1101 | 013921101 | BAY AREA | EAST BAY | 1.5676 | 1072709.6667 | 50.1923 | 0% | 0% | 6.206% | 20.54% | 0 | 0 | 1 | 0% | 36.62% | 7.692% | 7 | 5 | 0 | 0 | 8 | 8 | 0 | 0 | 3 | 26 | 15.4 | 1 | 3 | 0 | 5 | 0 | 0 | 1 | 0 | 0.26112 | 1 | 5.7623 | 1.5047 | Low | Low | High | Bottom | 654 | 652 | 5.7623
CARMEL 0405 | 182040405 | CENTRAL COAST | CENTRAL COAST | 0.54211 | 183473.6667 | 0 | 14.22% | 0% | 82.89% | 17.11% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14108 | 1 | 5.7517 | 0.81142 | Low | Low | High | Bottom | 736 | 653 | 5.7517
COAST RD 0401 | 088820401 | CENTRAL COAST | CENTRAL COAST | 2.6666 | 0 | 40 | 36.1% | 36.1% | 0% | 16.75% | 0 | 0 | 1 | 0% | 100% | 0% | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 1 | 0 | 0.17721 | 1 | 5.7489 | 1.0187 | Low | Low | High | Bottom | 708 | 654 | 5.7489
CAROLANDS 0404 | 024060404 | CENTRAL COAST | PENINSULA | 4.1147 | 322109 | 44.3949 | 46.95% | 3.653% | 18.37% | 52.56% | 7 | 0 | 24 | 16.49% | 83.51% | 19.75% | 21 | 39 | 0 | 0 | 93 | 20 | 6 | 0 | 3 | 157 | 43.913 | 13 | 36 | 8 | 71 | 0 | 0 | 24 | 1 | 0.79292 | 1 | 5.7269 | 4.541 | High | Low | High | Mid | 449 | 655 | 5.7269
COVELO 1101 | 043061101 | NORTHERN | HUMBOLDT | 18.5991 | 367965 | 41.3529 | 4.242% | 62.02% | 34.97% | 0% | 1 | 0 | 7 | 100% | 0% | 7.059% | 11 | 68 | 0 | 1 | 32 | 19 | 0 | 1 | 2 | 170 | 28.7045 | 15 | 7 | 0 | 49 | 0 | 0 | 7 | 0 | 0.30522 | 9.0051 | 0.63351 | 1.7412 | Low | Medium | Low | Bottom | 632 | 656 | 5.7048
CLARKSVILLE 2106 | 153612106 | NORTHERN | SIERRA | 0.99996 | 1619131.3333 | 48.3333 | 197.4% | 0% | 0% | 0% | 0 | 0 | 1 | 0% | 0% | 0% | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.2699 | 1 | 5.6989 | 1.5381 | Low | Low | High | Bottom | 649 | 657 | 5.6989
HIGHLANDS 1104 | 043361104 | NORTHERN | HUMBOLDT | 12.02 | 1046439 | 45.9626 | 24.73% | 0% | 75.88% | 1.167% | 0 | 1 | 28 | 75.88% | 1.167% | 7.467% | 128 | 189 | 0 | 2 | 118 | 39 | 15 | 5 | 9 | 375 | 51.0793 | 53 | 71 | 20 | 170 | 0 | 0 | 28 | 1 | 0.29309 | 1 | 5.6794 | 1.6645 | Low | Low | High | Bottom | 639 | 658 | 5.6794
EDENVALE 2107 | 082952107 | CENTRAL COAST | SAN JOSE | 4.8106 | 2048224.3333 | 42.8571 | 18.79% | 0% | 54.93% | 0% | 0 | 0 | 0 | 54.93% | 0% | 14.29% | 8 | 5 | 0 | 3 | 16 | 0 | 0 | 2 | 3 | 28 | 0 | 1 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.2962 | 1.8399 | 3.081 | 1.6792 | Low | Low | Low | Bottom | 637 | 659 | 5.6689
LOYOLA 1102 | 082161102 | CENTRAL COAST | DE ANZA | 0.10967 | 1120181.3333 | 42.5 | 0.365% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.26157 | 1 | 5.6407 | 1.4755 | Low | Low | High | Bottom | 662 | 660 | 5.6407
TAR FLAT 0401 | 163240401 | CENTRAL VALLEY | YOSEMITE | 3.63 | 84058.6667 | 43.2394 | 0% | 0% | 25.68% | 42.5% | 4 | 0 | 4 | 6.884% | 93.12% | 14.79% | 33 | 41 | 0 | 0 | 51 | 17 | 0 | 0 | 1 | 142 | 29.4308 | 13 | 26 | 11 | 70 | 0 | 0 | 4 | 1 | 0.79867 | 1 | 5.6149 | 4.4845 | High | Low | High | Mid | 452 | 661 | 5.6149
STELLING 1109 | 083481109 | CENTRAL COAST | DE ANZA | 0.65955 | 933086 | 45.5769 | 16.19% | 0% | 83.51% | 4.856% | 0 | 0 | 2 | 83.51% | 16.49% | 3.846% | 6 | 11 | 0 | 0 | 8 | 3 | 0 | 0 | 0 | 26 | 0 | 6 | 3 | 0 | 12 | 0 | 0 | 2 | 0 | 0.15296 | 1 | 5.6048 | 0.85733 | Low | Low | High | Bottom | 730 | 662 | 5.6048
SNEATH LANE 1101 | 022721101 | CENTRAL COAST | PENINSULA | 3.4169 | 423290.3333 | 42.5287 | 25.96% | 6.254% | 33.09% | 28.1% | 3 | 1 | 3 | 37.01% | 45.54% | 0% | 6 | 6 | 0 | 0 | 78 | 1 | 0 | 1 | 5 | 87 | 22.4286 | 9 | 13 | 4 | 29 | 0 | 0 | 3 | 1 | 0.65732 | 1 | 5.5993 | 3.6805 | Medium | Low | High | Mid | 491 | 663 | 5.5993
CLAYTON 2211 | 012022211 | BAY AREA | DIABLO | 0.14792 | 1278512.6667 | 45 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31499 | 1 | 5.5818 | 1.7582 | Low | Low | High | Bottom | 629 | 664 | 5.5818
DEL MAR 1103 | 152581103 | NORTHERN | SIERRA | 0.034858 | 435349.3333 | 0 | 0.3486% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15089 | 1 | 5.5468 | 0.83698 | Low | Low | High | Bottom | 733 | 665 | 5.5468
HIGHLANDS 1101 | 043361101 | NORTHERN | HUMBOLDT | 0.026418 | 0 | 40 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36313 | 1 | 5.5033 | 1.9984 | Medium | Low | High | Bottom | 602 | 666 | 5.5033
DEL MONTE 2103 | 182222103 | CENTRAL COAST | CENTRAL COAST | 13.5735 | 1826126 | 43.6569 | 10.44% | 0.9828% | 60.53% | 9.887% | 13 | 3 | 47 | 19.33% | 53.28% | 10.76% | 95 | 132 | 0 | 9 | 120 | 31 | 5 | 12 | 18 | 446 | 33.367 | 43 | 34 | 2 | 121 | 0 | 0 | 47 | 1 | 0.73565 | 1 | 5.4971 | 4.044 | High | Low | High | Mid | 474 | 667 | 5.4971
PANORAMA 1101 | 103461101 | NORTHERN | NORTH VALLEY | 12.3478 | 578348.6667 | 46.6862 | 34.74% | 89.3% | 5.86% | 0% | 0 | 0 | 16 | 95.16% | 0% | 6.776% | 192 | 291 | 4 | 1 | 16 | 76 | 0 | 0 | 2 | 428 | 60.6062 | 127 | 128 | 25 | 302 | 0 | 1 | 16 | 0 | 0.19097 | 1 | 5.4631 | 1.0433 | Low | Low | High | Bottom | 706 | 668 | 5.4631
PLACER 1101 | 152461101 | NORTHERN | SIERRA | 0.97559 | 370014.6667 | 42.3333 | 14.04% | 0% | 2.378% | 12.82% | 0 | 0 | 2 | 3.106% | 66.22% | 6.667% | 6 | 14 | 0 | 0 | 15 | 1 | 0 | 1 | 2 | 30 | 32.25 | 5 | 1 | 0 | 9 | 0 | 0 | 2 | 0 | 0.40024 | 1 | 5.4221 | 2.1702 | Medium | Low | High | Bottom | 587 | 669 | 5.4221
CLARKSVILLE 2109 | 153612109 | NORTHERN | SIERRA | 5.6918 | 1630300.3333 | 48.0851 | 110.3% | 0% | 67.47% | 0% | 0 | 0 | 13 | 67.47% | 0% | 1.064% | 39 | 42 | 0 | 0 | 19 | 7 | 0 | 2 | 4 | 94 | 28.3514 | 12 | 18 | 2 | 37 | 0 | 0 | 13 | 1 | 0.3464 | 1 | 5.4176 | 1.8767 | Medium | Low | High | Bottom | 617 | 670 | 5.4176
HIGGINS 1107 | 152691107 | NORTHERN | SIERRA | 17.5954 | 691949.3333 | 43.0574 | 37.22% | 0.02922% | 94.44% | 0% | 3 | 0 | 17 | 94.47% | 0% | 5.96% | 25 | 384 | 1 | 0 | 15 | 18 | 10 | 7 | 12 | 453 | 46.5368 | 92 | 59 | 6 | 192 | 0 | 0 | 17 | 0 | 0.21897 | 1.3406 | 4.0406 | 1.1861 | Low | Low | Medium | Bottom | 689 | 671 | 5.4168
SNEATH LANE 1106 | 022721106 | CENTRAL COAST | PENINSULA | 2.2996 | 639751.6667 | 42.5 | 30.17% | 0% | 43.71% | 15.94% | 6 | 0 | 6 | 43.71% | 19.05% | 8% | 4 | 10 | 0 | 0 | 34 | 0 | 0 | 3 | 8 | 50 | 38.2 | 2 | 5 | 3 | 18 | 0 | 0 | 6 | 1 | 0.58134 | 1 | 5.4125 | 3.1465 | Medium | Low | High | Mid | 519 | 672 | 5.4125
CLARKSVILLE 2110 | 153612110 | NORTHERN | SIERRA | 0.17765 | 1795877.6667 | 0 | 658.2% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29789 | 1 | 5.3871 | 1.6048 | Low | Low | High | Bottom | 646 | 673 | 5.3871
BAY MEADOWS 2102 | 024012102 | CENTRAL COAST | PENINSULA | 4.3938 | 1456927.6667 | 45.2119 | 33.71% | 0% | 37.33% | 2.397% | 7 | 0 | 9 | 27.78% | 13.79% | 11.86% | 24 | 29 | 1 | 1 | 67 | 11 | 0 | 3 | 8 | 118 | 28.5435 | 17 | 10 | 6 | 49 | 1 | 0 | 9 | 1 | 0.63615 | 1 | 5.3811 | 3.4232 | Medium | Low | High | Mid | 508 | 674 | 5.3811
BERESFORD 0403 | 024040403 | CENTRAL COAST | PENINSULA | 4.6093 | 327613.3333 | 42.0574 | 43.53% | 0% | 29.31% | 48.72% | 5 | 0 | 24 | 16.62% | 83.15% | 17.22% | 14 | 54 | 0 | 0 | 100 | 21 | 7 | 1 | 6 | 209 | 47.2625 | 13 | 44 | 8 | 80 | 1 | 0 | 24 | 1 | 0.80333 | 1 | 5.3755 | 4.3183 | High | Low | Medium | Mid | 460 | 675 | 5.3755
NORTH TOWER 2101 | 042042101 | BAY AREA | NORTH BAY | 1.3548 | 0 | 47 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0.4196% | 0% | 3 | 3 | 0 | 0 | 1 | 0 | 0 | 3 | 6 | 5 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0.38534 | 1 | 5.3717 | 2.0699 | Medium | Low | Medium | Bottom | 596 | 676 | 5.3717
OCEANO 1102 | 182601102 | CENTRAL COAST | LOS PADRES | 38.3364 | 0 | 42.0799 | 32.16% | 3.398% | 47.22% | 25.9% | 5 | 4 | 84 | 46.52% | 30.1% | 4.941% | 93 | 60 | 0 | 156 | 272 | 104 | 0 | 17 | 25 | 850 | 30.953 | 105 | 53 | 12 | 334 | 0 | 0 | 84 | 0 | 0.45559 | 1.1592 | 4.629 | 2.4447 | Medium | Low | Medium | Bottom | 563 | 677 | 5.3661
HIGGINS 1104 | 152691104 | NORTHERN | SIERRA | 71.3117 | 882750.6667 | 43.8098 | 60.2% | 44.82% | 29.59% | 0% | 8 | 0 | 107 | 79.96% | 0% | 13.54% | 308 | 1332 | 13 | 1 | 60 | 229 | 0 | 19 | 34 | 1890 | 49.9248 | 434 | 324 | 31 | 902 | 0 | 2 | 100 | 0 | 0.088904 | 1.0484 | 5.0837 | 0.47386 | Low | Low | Medium | Bottom | 766 | 678 | 5.33
OCEANO 1105 | 182601105 | CENTRAL COAST | LOS PADRES | 4.2689 | 1490372.6667 | 40.9722 | 23.17% | 4.358% | 11.27% | 54.32% | 0 | 0 | 2 | 1.35% | 68.6% | 19.44% | 3 | 2 | 0 | 3 | 20 | 6 | 0 | 4 | 5 | 36 | 17.4 | 3 | 2 | 3 | 11 | 0 | 0 | 2 | 0 | 0.46324 | 1 | 5.285 | 2.4483 | Medium | Low | Medium | Bottom | 562 | 679 | 5.285
FLINT 1102 | 152531102 | NORTHERN | SIERRA | 0.092844 | 193432.6667 | 46.6667 | 21.4% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36537 | 1 | 5.272 | 1.9262 | Medium | Low | Medium | Bottom | 612 | 680 | 5.272
MARTELL 1101 | 163011101 | CENTRAL VALLEY | STOCKTON | 74.5727 | 692481.6667 | 42.5623 | 56.3% | 16.45% | 73.74% | 2.423% | 4 | 0 | 79 | 91.43% | 2.88% | 4.213% | 176 | 820 | 0 | 0 | 334 | 222 | 0 | 15 | 27 | 1614 | 36.5019 | 283 | 119 | 4 | 547 | 0 | 1 | 79 | 0 | 0.044052 | 1.0495 | 5.0105 | 0.23166 | Low | Low | Medium | Bottom | 778 | 681 | 5.2587
PLACER 1102 | 152461102 | NORTHERN | SIERRA | 2.1407 | 8964.6667 | 44.9 | 150.8% | 0% | 15.97% | 28.73% | 0 | 0 | 7 | 18.98% | 28.73% | 0% | 18 | 30 | 0 | 0 | 13 | 3 | 0 | 1 | 2 | 50 | 33.15 | 8 | 5 | 0 | 20 | 0 | 0 | 7 | 0 | 0.45496 | 1 | 5.2537 | 2.3902 | Medium | Low | Medium | Bottom | 574 | 682 | 5.2537
BUTTE 1105 | 103081105 | NORTHERN | NORTH VALLEY | 2.5574 | 849032.6667 | 43.2143 | 15.51% | 1.765% | 65.2% | 0% | 0 | 0 | 26 | 66.97% | 0% | 2.381% | 8 | 16 | 0 | 0 | 8 | 1 | 0 | 11 | 15 | 42 | 38.7328 | 116 | 83 | 5 | 273 | 0 | 0 | 26 | 0 | 0.28197 | 1 | 5.2496 | 1.4802 | Low | Low | Medium | Bottom | 660 | 683 | 5.2496
SNEATH LANE 1107 | 022721107 | CENTRAL COAST | PENINSULA | 3.0548 | 542027.6667 | 43.125 | 16.98% | 0% | 47.72% | 3.012% | 3 | 0 | 3 | 47.72% | 25.42% | 7.317% | 8 | 3 | 0 | 0 | 33 | 4 | 0 | 3 | 6 | 41 | 0 | 0 | 4 | 2 | 7 | 0 | 0 | 3 | 0 | 0.49868 | 1 | 5.241 | 2.6136 | Medium | Low | Medium | Bottom | 552 | 684 | 5.241
VINEYARD 2107 | 014502107 | CENTRAL COAST | MISSION | 1.9947 | 1499744.3333 | 43.0233 | 12.4% | 0% | 50.79% | 49.21% | 0 | 1 | 10 | 50.79% | 49.21% | 13.95% | 5 | 36 | 0 | 1 | 26 | 3 | 0 | 3 | 4 | 86 | 20.973 | 14 | 20 | 0 | 40 | 0 | 0 | 10 | 1 | 0.69409 | 1 | 5.2344 | 3.6331 | High | Low | Medium | Mid | 499 | 685 | 5.2344
SNEATH LANE 1102 | 022721102 | CENTRAL COAST | PENINSULA | 0.46314 | 607738.6667 | 42.4242 | 53.37% | 0% | 16.94% | 13.26% | 2 | 0 | 1 | 16.94% | 58.58% | 12.12% | 7 | 5 | 0 | 0 | 22 | 2 | 0 | 0 | 3 | 33 | 0.25 | 3 | 2 | 0 | 8 | 0 | 0 | 1 | 0 | 0.38201 | 1 | 5.2218 | 1.9948 | Medium | Low | Medium | Bottom | 604 | 686 | 5.2218
PENRYN 1106 | 152561106 | NORTHERN | SIERRA | 1.0234 | 977537 | 39.0909 | 1.374% | 0% | 37.58% | 62.42% | 0 | 0 | 0 | 37.58% | 62.42% | 18.18% | 1 | 12 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 22 | 17.75 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 0 | 0.18875 | 1 | 5.2111 | 0.98359 | Low | Low | Medium | Bottom | 713 | 687 | 5.2111
TULE POWER HOUSE 1101 | 258591101 | CENTRAL VALLEY | FRESNO | 4.0927 | 0 | 38.9041 | 0% | 81.39% | 18.61% | 0% | 0 | 0 | 1 | 3.215% | 96.78% | 55.26% | 4 | 0 | 0 | 5 | 48 | 5 | 0 | 0 | 1 | 76 | 1 | 2 | 1 | 0 | 6 | 0 | 0 | 1 | 0 | 0.30988 | 2.0821 | 2.5025 | 1.6146 | Low | Low | Low | Bottom | 645 | 688 | 5.2104
AUBURN 1101 | 152161101 | NORTHERN | SIERRA | 3.3599 | 215030.6667 | 44.5122 | 22.65% | 35.45% | 30.38% | 32.38% | 0 | 0 | 5 | 24.3% | 75.7% | 4.839% | 33 | 73 | 0 | 0 | 26 | 2 | 0 | 0 | 0 | 124 | 27.6111 | 22 | 16 | 8 | 56 | 0 | 0 | 5 | 0 | 0.52955 | 1 | 5.2096 | 2.7587 | Medium | Low | Medium | Bottom | 543 | 689 | 5.2096
PLACER 1104 | 152461104 | NORTHERN | SIERRA | 1.6895 | 1114406.3333 | 42.5 | 29.92% | 2.335% | 25.27% | 24.57% | 0 | 0 | 2 | 25.35% | 26.82% | 0% | 3 | 12 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 16 | 29.2 | 1 | 2 | 0 | 6 | 0 | 0 | 2 | 0 | 0.2546 | 1 | 5.2079 | 1.3259 | Low | Low | Medium | Bottom | 676 | 690 | 5.2079
REEDLEY 1112 | 252341112 | CENTRAL VALLEY | FRESNO | 1.4284 | 1165789 | 44.0909 | 20.53% | 0% | 99.8% | 0.1962% | 0 | 0 | 1 | 99.8% | 0.1962% | 18.18% | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 11 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0.24502 | 2.0451 | 2.5413 | 1.2734 | Low | Low | Low | Bottom | 680 | 691 | 5.1972
CASTRO VALLEY 1104 | 014091104 | CENTRAL COAST | MISSION | 4.1983 | 925694.6667 | 43.25 | 16.78% | 0% | 46.38% | 24.52% | 0 | 0 | 5 | 8.709% | 63.59% | 6.931% | 6 | 20 | 0 | 0 | 61 | 2 | 0 | 1 | 3 | 101 | 9.6667 | 5 | 15 | 4 | 31 | 0 | 0 | 5 | 0 | 0.4875 | 1 | 5.1934 | 2.5318 | Medium | Low | Medium | Bottom | 557 | 692 | 5.1934
DIVIDE 1103 | 182571103 | CENTRAL COAST | LOS PADRES | 2.3909 | 265550 | 42.1918 | 11.28% | 0% | 30.11% | 67.53% | 1 | 0 | 3 | 30.11% | 66.02% | 0% | 16 | 4 | 0 | 5 | 53 | 7 | 0 | 0 | 0 | 78 | 25.2778 | 6 | 3 | 0 | 19 | 0 | 0 | 3 | 1 | 0.55177 | 1 | 5.17 | 2.8526 | Medium | Low | Medium | Mid | 536 | 693 | 5.17
SYCAMORE CREEK 1109 | 102971109 | NORTHERN | NORTH VALLEY | 0.79158 | 908767 | 45 | 1.821% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26871 | 1 | 5.1691 | 1.389 | Low | Low | Medium | Bottom | 673 | 694 | 5.1691
CMC 1102 | 183111102 | CENTRAL COAST | LOS PADRES | 0.46264 | 0 | 0 | 0% | 0% | 0% | 6.672% | 0 | 0 | 0 | 0% | 6.672% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36318 | 1 | 5.1474 | 1.8694 | Medium | Low | Medium | Bottom | 620 | 695 | 5.1474
OCEANO 1106 | 182601106 | CENTRAL COAST | LOS PADRES | 2.3362 | 1355756.3333 | 46.3265 | 113.1% | 0% | 11.98% | 23.42% | 0 | 0 | 2 | 11.98% | 23.42% | 6.122% | 13 | 0 | 0 | 10 | 8 | 11 | 0 | 2 | 3 | 49 | 25.5714 | 8 | 2 | 1 | 15 | 0 | 0 | 2 | 0 | 0.33198 | 1 | 5.1395 | 1.7062 | Medium | Low | Medium | Bottom | 634 | 696 | 5.1395
OAKLAND J 1118 | 012091118 | BAY AREA | EAST BAY | 0.75276 | 549257.6667 | 44.6667 | 21.9% | 0% | 92.61% | 7.387% | 0 | 0 | 0 | 17.8% | 82.2% | 0% | 0 | 1 | 0 | 0 | 11 | 1 | 0 | 0 | 0 | 15 | 15 | 0 | 3 | 2 | 5 | 0 | 0 | 0 | 0 | 0.17051 | 1 | 5.115 | 0.87215 | Low | Low | Medium | Bottom | 727 | 697 | 5.115
KIRKER 2104 | 014452104 | BAY AREA | DIABLO | 5.6758 | 1460458 | 45.3472 | 150% | 24.28% | 41.33% | 12.22% | 0 | 0 | 5 | 41.33% | 36.49% | 33.33% | 14 | 19 | 0 | 0 | 11 | 7 | 0 | 2 | 5 | 72 | 19.6 | 2 | 2 | 1 | 8 | 0 | 0 | 5 | 0 | 0.35726 | 1 | 5.0593 | 1.8075 | Medium | Low | Medium | Bottom | 624 | 698 | 5.0593
AUBURN 1102 | 152161102 | NORTHERN | SIERRA | 2.613 | 435039 | 42.4 | 11.25% | 0% | 47.57% | 52.43% | 0 | 0 | 6 | 22.24% | 77.76% | 6.349% | 26 | 82 | 0 | 0 | 24 | 10 | 4 | 0 | 0 | 126 | 36.9818 | 25 | 10 | 8 | 55 | 0 | 0 | 6 | 0 | 0.57566 | 1 | 5.0497 | 2.9069 | Medium | Low | Medium | Mid | 533 | 699 | 5.0497
HALSEY 1101 | 152241101 | NORTHERN | SIERRA | 72.9255 | 833727 | 42.2922 | 33.29% | 20.02% | 53.78% | 13.84% | 11 | 1 | 137 | 71.04% | 16.6% | 5.404% | 221 | 1275 | 6 | 1 | 391 | 134 | 7 | 20 | 37 | 2091 | 34.1417 | 377 | 315 | 42 | 908 | 0 | 1 | 137 | 1 | 0.4571 | 1.1192 | 4.492 | 2.298 | Medium | Low | Medium | Bottom | 582 | 700 | 5.0274
ALHAMBRA 1102 | 014101102 | BAY AREA | DIABLO | 0.37374 | 999803 | 44.1667 | 0.05608% | 31.31% | 27.66% | 31.86% | 0 | 0 | 2 | 31.31% | 59.51% | 50% | 2 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 12 | 20.6 | 0 | 3 | 1 | 5 | 0 | 0 | 2 | 1 | 0.29792 | 1 | 5.0186 | 1.4952 | Low | Low | Medium | Bottom | 658 | 701 | 5.0186
JESSUP 1103 | 103441103 | NORTHERN | NORTH VALLEY | 4.4405 | 665870.6667 | 42.4419 | 0% | 48.78% | 44.06% | 0.7795% | 1 | 0 | 9 | 97.48% | 2.521% | 13.18% | 20 | 65 | 6 | 0 | 23 | 17 | 0 | 2 | 2 | 129 | 40.0182 | 26 | 17 | 1 | 56 | 0 | 0 | 9 | 0 | 0.33083 | 1.2953 | 3.8162 | 1.6353 | Medium | Low | Medium | Bottom | 641 | 702 | 4.9431
SERRAMONTE 1104 | 022861104 | CENTRAL COAST | PENINSULA | 0.061541 | 836402 | 0 | 12.92% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1413 | 1 | 4.9418 | 0.69828 | Low | Low | Medium | Bottom | 745 | 703 | 4.9418
CLAY 1102 | 163341102 | CENTRAL VALLEY | STOCKTON | 1.2491 | 70737.6667 | 48.125 | 345.3% | 0% | 0% | 0% | 1 | 0 | 0 | 0% | 0% | 6.25% | 7 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 2 | 16 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.30842 | 1 | 4.8947 | 1.5096 | Low | Low | Medium | Bottom | 653 | 704 | 4.8947
WILLOW PASS 2107 | 013912107 | BAY AREA | DIABLO | 0.64814 | 1229122.3333 | 50 | 20.04% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 20% | 10 | 0 | 0 | 0 | 8 | 2 | 0 | 0 | 0 | 10 | 2.6667 | 3 | 0 | 0 | 3 | 0 | 0 | 1 | 0 | 0.25197 | 1 | 4.8811 | 1.2299 | Low | Low | Medium | Bottom | 685 | 705 | 4.8811
DOLAN ROAD 1101 | 182381101 | CENTRAL COAST | CENTRAL COAST | 6.1776 | 415279.6667 | 39.9324 | 9.734% | 0% | 69.26% | 21.58% | 0 | 0 | 2 | 73.63% | 21.58% | 14.86% | 1 | 30 | 0 | 0 | 34 | 2 | 0 | 0 | 1 | 74 | 19.7179 | 12 | 5 | 0 | 40 | 0 | 0 | 2 | 0 | 0.22086 | 1 | 4.8606 | 1.0735 | Low | Low | Medium | Bottom | 699 | 706 | 4.8606
WILLOW PASS 2108 | 013912108 | BAY AREA | DIABLO | 0.19204 | 1123036.3333 | 45 | 18.01% | 0% | 75.41% | 24.59% | 0 | 0 | 1 | 75.41% | 24.59% | 0% | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 87 | 0 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 0.23051 | 1 | 4.8379 | 1.1152 | Low | Low | Medium | Bottom | 695 | 707 | 4.8379
NARROWS 2104 | 153132104 | NORTHERN | SIERRA | 0.002841 | 0 | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.38633 | 1 | 4.8141 | 1.8598 | Medium | Low | Medium | Bottom | 621 | 708 | 4.8141
GRASS VALLEY 1102 | 152031102 | NORTHERN | SIERRA | 0.032103 | 368676.6667 | 38 | 5.665% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 60% | 1 | 0 | 0 | 0 | 3 | 1 | 0 | 1 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.44211 | 1 | 4.7939 | 2.1194 | Medium | Low | Medium | Bottom | 592 | 709 | 4.7939
CAMBRIA 1101 | 182771101 | CENTRAL COAST | LOS PADRES | 27.8539 | 191645.6667 | 39.814 | 163% | 0% | 66.28% | 19.72% | 1 | 0 | 16 | 1.731% | 84.26% | 1.163% | 14 | 39 | 1 | 16 | 228 | 89 | 0 | 9 | 11 | 430 | 27.8571 | 9 | 10 | 5 | 44 | 0 | 0 | 16 | 0 | 0.30267 | 1.4617 | 3.2384 | 1.4327 | Low | Low | Low | Bottom | 667 | 710 | 4.7336
SAN LEANDRO U 1107 | 013111107 | CENTRAL COAST | MISSION | 0.097818 | 1147965 | 0 | 1.3% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20554 | 1 | 4.68 | 0.96191 | Low | Low | Medium | Bottom | 717 | 711 | 4.68
MESA 1103 | 182821103 | CENTRAL COAST | LOS PADRES | 12.4594 | 1425053 | 44.5775 | 7.311% | 0% | 72.42% | 11.33% | 2 | 0 | 21 | 72.42% | 11.33% | 9.722% | 56 | 8 | 0 | 44 | 66 | 50 | 0 | 1 | 2 | 216 | 27.7941 | 37 | 9 | 1 | 105 | 0 | 0 | 20 | 0 | 0.19267 | 1.1375 | 4.0787 | 0.89387 | Low | Low | Medium | Bottom | 725 | 712 | 4.6394
MC KEE 1103 | 083531103 | CENTRAL COAST | SAN JOSE | 3.2596 | 768497.3333 | 44.5652 | 24.26% | 0% | 23.43% | 63.61% | 0 | 0 | 2 | 13.27% | 73.77% | 17.39% | 6 | 13 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 23 | 13.6667 | 0 | 1 | 0 | 6 | 0 | 0 | 2 | 0 | 0.2612 | 1.3747 | 3.3365 | 1.1981 | Low | Low | Low | Bottom | 688 | 713 | 4.5867
SAN LEANDRO U 1114 | 013111114 | CENTRAL COAST | MISSION | 15.182 | 1226301 | 43.9513 | 28.75% | 0.1848% | 49.53% | 42.91% | 4 | 1 | 30 | 37.32% | 55.94% | 17.69% | 41 | 73 | 1 | 3 | 204 | 9 | 0 | 4 | 6 | 390 | 22.0924 | 26 | 56 | 14 | 125 | 0 | 0 | 30 | 0 | 0.6688 | 1 | 4.5847 | 3.0663 | High | Low | Medium | Mid | 521 | 714 | 4.5847
SANTA ROSA A 1107 | 042151107 | NORTHERN | SONOMA | 3.0424 | 623638.3333 | 45.6061 | 14.02% | 0% | 70.89% | 15.09% | 1 | 2 | 10 | 70.89% | 15.09% | 6.061% | 30 | 27 | 0 | 2 | 53 | 9 | 0 | 5 | 5 | 99 | 50.3784 | 6 | 13 | 5 | 37 | 0 | 0 | 10 | 1 | 0.57087 | 1 | 4.5577 | 2.6019 | Medium | Low | Medium | Bottom | 553 | 715 | 4.5577
PLACERVILLE 1111 | 153081111 | NORTHERN | SIERRA | 14.075 | 967719 | 41.9258 | 32.86% | 24.43% | 35.77% | 20.67% | 4 | 1 | 28 | 60.2% | 20.84% | 1.047% | 74 | 245 | 3 | 0 | 166 | 31 | 5 | 8 | 12 | 573 | 44.498 | 102 | 76 | 20 | 255 | 0 | 0 | 28 | 1 | 0.46103 | 1 | 4.5462 | 2.096 | Medium | Low | Medium | Bottom | 594 | 716 | 4.5462
SANTA ROSA A 1110 | 042151110 | NORTHERN | SONOMA | 0.037484 | 897090.6667 | 0 | 1.125% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19275 | 1 | 4.513 | 0.8699 | Low | Low | Medium | Bottom | 728 | 717 | 4.513
FORT ORD 2106 | 182402106 | CENTRAL COAST | CENTRAL COAST | 2.0208 | 481847.3333 | 45.25 | 110.4% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 64.18% | 0% | 1 | 0 | 0 | 0 | 39 | 1 | 0 | 5 | 9 | 40 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.29315 | 1 | 4.487 | 1.3154 | Low | Low | Medium | Bottom | 677 | 718 | 4.487
CHESTER 1101 | 103181101 | NORTHERN | NORTH VALLEY | 2.9117 | 277170.3333 | 41.6162 | 6.963% | 86.02% | 9.547% | 3.579% | 0 | 0 | 4 | 95.56% | 3.579% | 15.84% | 3 | 7 | 5 | 0 | 33 | 16 | 0 | 0 | 0 | 101 | 54.0345 | 11 | 13 | 3 | 29 | 0 | 0 | 4 | 0 | 0.33112 | 1 | 4.4592 | 1.4765 | Medium | Low | Medium | Bottom | 661 | 719 | 4.4592
FORT ORD 2107 | 182402107 | CENTRAL COAST | CENTRAL COAST | 4.2048 | 0 | 44.4175 | 29.09% | 18.37% | 1.01% | 9.598% | 0 | 0 | 11 | 1.01% | 88.05% | 2.913% | 3 | 12 | 0 | 1 | 71 | 6 | 0 | 3 | 4 | 103 | 9.7143 | 2 | 1 | 1 | 8 | 1 | 0 | 11 | 0 | 0.39817 | 1 | 4.4491 | 1.7715 | Medium | Low | Medium | Bottom | 627 | 720 | 4.4491
BELL 1109 | 152701109 | NORTHERN | SIERRA | 13.5619 | 554865.3333 | 42.1143 | 18.6% | 0% | 65.29% | 17.96% | 1 | 0 | 22 | 51.05% | 32.2% | 5.698% | 41 | 211 | 2 | 0 | 50 | 22 | 0 | 4 | 5 | 351 | 35.5733 | 68 | 39 | 6 | 152 | 0 | 0 | 22 | 0 | 0.29387 | 1 | 4.4251 | 1.3004 | Low | Low | Medium | Bottom | 679 | 721 | 4.4251
CHESTER 1102 | 103181102 | NORTHERN | NORTH VALLEY | 2.5304 | 123687.6667 | 43.4375 | 63.74% | 98.2% | 0% | 1.801% | 5 | 0 | 6 | 98.2% | 1.801% | 17.65% | 5 | 1 | 2 | 0 | 15 | 6 | 0 | 2 | 3 | 68 | 30.1111 | 3 | 3 | 3 | 10 | 0 | 0 | 6 | 1 | 0.63055 | 1 | 4.408 | 2.7794 | Medium | Low | Medium | Mid | 540 | 722 | 4.408
HIGGINS 1110 | 152691110 | NORTHERN | SIERRA | 51.6137 | 531035.6667 | 43.0525 | 38.98% | 2.132% | 82.19% | 0% | 6 | 1 | 79 | 87.32% | 0% | 11.38% | 102 | 808 | 9 | 3 | 41 | 127 | 5 | 13 | 19 | 1186 | 39.8986 | 219 | 103 | 6 | 444 | 0 | 5 | 79 | 0 | 0.098957 | 1.0828 | 4.0439 | 0.43328 | Low | Low | Medium | Bottom | 767 | 723 | 4.3785
TEMPLETON 2108 | 183052108 | CENTRAL COAST | LOS PADRES | 3.1369 | 953723.3333 | 40.9694 | 26.48% | 0% | 51.92% | 32.41% | 2 | 0 | 19 | 51.92% | 32.41% | 10.71% | 20 | 9 | 0 | 41 | 78 | 20 | 0 | 1 | 5 | 196 | 57.2439 | 31 | 30 | 3 | 83 | 0 | 0 | 19 | 0 | 0.43947 | 1 | 4.3687 | 1.9199 | Medium | Low | Medium | Bottom | 613 | 724 | 4.3687
SAN LEANDRO U 1109 | 013111109 | CENTRAL COAST | MISSION | 13.1527 | 1027629.6667 | 44.4837 | 20.73% | 2.227% | 41.32% | 36.26% | 6 | 2 | 28 | 37.43% | 43.23% | 18.93% | 57 | 68 | 0 | 2 | 287 | 12 | 3 | 17 | 21 | 523 | 22.1133 | 37 | 68 | 21 | 156 | 0 | 0 | 28 | 0 | 0.73818 | 1 | 4.3591 | 3.2178 | High | Low | Medium | Mid | 517 | 725 | 4.3591
ESTUDILLO 0401 | 013480401 | CENTRAL COAST | MISSION | 0.86867 | 127000 | 39.5652 | 9.741% | 0% | 70.62% | 23.67% | 1 | 0 | 3 | 21.47% | 72.82% | 13.04% | 1 | 4 | 0 | 0 | 10 | 1 | 0 | 0 | 0 | 23 | 14.5 | 2 | 7 | 1 | 10 | 0 | 0 | 3 | 0 | 0.28808 | 1 | 4.3503 | 1.2532 | Low | Low | Medium | Bottom | 681 | 726 | 4.3503
HALSEY 1102 | 152241102 | NORTHERN | SIERRA | 58.9603 | 966228.3333 | 42.6053 | 32.47% | 32.96% | 36.23% | 21.19% | 12 | 3 | 73 | 64.36% | 27.04% | 8.07% | 186 | 983 | 5 | 0 | 242 | 92 | 0 | 12 | 25 | 1549 | 35.5795 | 276 | 177 | 10 | 637 | 0 | 0 | 70 | 0 | 0.41881 | 1.0367 | 4.1798 | 1.8148 | Medium | Low | Medium | Bottom | 622 | 727 | 4.3333
CLEAR LAKE 1102 | 042141102 | NORTHERN | HUMBOLDT | 4.9879 | 888198.3333 | 47.0139 | 12.15% | 0% | 54.06% | 4.215% | 0 | 0 | 4 | 54.06% | 4.215% | 12.5% | 37 | 38 | 0 | 1 | 18 | 9 | 0 | 0 | 1 | 72 | 29.75 | 18 | 11 | 1 | 38 | 0 | 0 | 4 | 0 | 0.44438 | 1 | 4.3199 | 1.9197 | Medium | Low | Medium | Bottom | 614 | 728 | 4.3199
PLACERVILLE 1112 | 153081112 | NORTHERN | SIERRA | 27.7419 | 782510.3333 | 42.0833 | 27.34% | 53.09% | 21.45% | 9.376% | 5 | 0 | 49 | 73.74% | 10.17% | 1.063% | 108 | 405 | 23 | 0 | 257 | 50 | 2 | 4 | 10 | 941 | 51.9846 | 163 | 130 | 29 | 395 | 0 | 0 | 49 | 0 | 0.14218 | 1 | 4.2874 | 0.60958 | Low | Low | Medium | Bottom | 754 | 729 | 4.2874
MONROE 2107 | 043302107 | NORTHERN | SONOMA | 0.75479 | 2185651 | 45 | 2.435% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 61.54% | 0 | 2 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 13 | 60.6667 | 1 | 1 | 0 | 6 | 0 | 0 | 1 | 1 | 0.39704 | 1 | 4.2684 | 1.6947 | Medium | Low | Medium | Bottom | 635 | 730 | 4.2684
BANCROFT 0402 | 013030402 | BAY AREA | EAST BAY | 1.1676 | 137398.3333 | 43.3333 | 0% | 0% | 66.62% | 25.97% | 0 | 0 | 0 | 1.548% | 91.05% | 50% | 1 | 2 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 12 | 44.6 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 0 | 0.23001 | 1 | 4.2377 | 0.97474 | Low | Low | Medium | Bottom | 716 | 731 | 4.2377
RINCON 1104 | 043321104 | NORTHERN | SONOMA | 2.7394 | 1072176.6667 | 42.5 | 124.6% | 0% | 21.97% | 15.06% | 2 | 1 | 8 | 21.97% | 15.06% | 20.31% | 11 | 24 | 0 | 0 | 26 | 8 | 0 | 4 | 6 | 64 | 38.6774 | 7 | 11 | 6 | 31 | 0 | 0 | 8 | 1 | 0.65299 | 1 | 4.2342 | 2.7649 | Medium | Low | Medium | Bottom | 542 | 732 | 4.2342
PRUNEDALE 1110 | 182961110 | CENTRAL COAST | CENTRAL COAST | 0.11844 | 1394297.3333 | 41.6667 | 0.2327% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 0.29459 | 1 | 4.2019 | 1.2378 | Low | Low | Medium | Bottom | 682 | 733 | 4.2019
COTATI 1104 | 042271104 | NORTHERN | SONOMA | 8.881 | 508263 | 43.7449 | 25.11% | 2.544% | 37.12% | 46.68% | 1 | 0 | 26 | 37.12% | 49.23% | 1.639% | 54 | 110 | 0 | 3 | 88 | 18 | 2 | 0 | 5 | 244 | 32.835 | 37 | 16 | 2 | 105 | 0 | 0 | 26 | 0 | 0.44174 | 1.0792 | 3.7782 | 1.8011 | Medium | Low | Medium | Bottom | 625 | 734 | 4.0773
MORGAN HILL 2109 | 083242109 | CENTRAL COAST | SAN JOSE | 2.6411 | 1764272 | 43.2609 | 6.413% | 39.24% | 60.41% | 0% | 1 | 0 | 3 | 99.65% | 0% | 4.348% | 13 | 21 | 0 | 1 | 19 | 1 | 0 | 0 | 1 | 46 | 15.8571 | 8 | 17 | 8 | 42 | 0 | 0 | 3 | 0 | 0.33392 | 1 | 4.0649 | 1.3574 | Medium | Low | Medium | Bottom | 674 | 735 | 4.0649
PLACERVILLE 1109 | 153081109 | NORTHERN | SIERRA | 0.020146 | 0 | 50 | 1.037% | 42.3% | 0% | 0% | 0 | 0 | 1 | 0% | 42.3% | 0% | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.39891 | 1 | 4.0646 | 1.6214 | Medium | Low | Medium | Bottom | 643 | 736 | 4.0646
PEABODY 2106 | 063642106 | NORTHERN | SACRAMENTO | 1.0067 | 1339227.6667 | 44.375 | 294.9% | 0% | 71.61% | 0% | 0 | 0 | 1 | 71.61% | 0% | 12.5% | 0 | 9 | 0 | 0 | 4 | 2 | 0 | 0 | 0 | 16 | 13 | 0 | 0 | 1 | 4 | 0 | 0 | 1 | 0 | 0.17102 | 1 | 4.056 | 0.69365 | Low | Low | Medium | Bottom | 746 | 737 | 4.056
WEIMAR 1102 | 152491102 | NORTHERN | SIERRA | 23.0263 | 158885.3333 | 41.8349 | 22.14% | 53.36% | 15.48% | 14.14% | 1 | 5 | 41 | 73.63% | 14.14% | 6.56% | 44 | 402 | 3 | 0 | 79 | 45 | 6 | 6 | 12 | 625 | 36.6398 | 154 | 111 | 5 | 350 | 0 | 0 | 40 | 0 | 0.24313 | 1.0248 | 3.9433 | 0.98249 | Low | Low | Medium | Bottom | 714 | 738 | 4.041
WILLOW PASS 1101 | 013911101 | BAY AREA | DIABLO | 0.8295 | 370736.6667 | 47 | 63.82% | 10.52% | 62.15% | 0% | 0 | 0 | 2 | 72.66% | 0% | 40% | 9 | 6 | 0 | 0 | 1 | 3 | 0 | 0 | 1 | 15 | 0.66667 | 1 | 1 | 0 | 4 | 0 | 0 | 2 | 0 | 0.27234 | 1 | 3.9927 | 1.0874 | Low | Low | Medium | Bottom | 697 | 739 | 3.9927
SCE VEGAS 1701 | 188881701 | CENTRAL COAST | LOS PADRES | 0.17032 | 0 | 0 | 0% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.23885 | 1 | 3.9643 | 0.94686 | Low | Low | Medium | Bottom | 718 | 740 | 3.9643
LONE TREE 2105 | 013232105 | BAY AREA | DIABLO | 10.6094 | 907615.3333 | 46.4773 | 17.08% | 0% | 96.44% | 3.562% | 0 | 0 | 9 | 95.57% | 4.426% | 14.77% | 34 | 94 | 0 | 0 | 12 | 6 | 0 | 0 | 0 | 176 | 35.5946 | 11 | 18 | 1 | 42 | 0 | 0 | 9 | 0 | 0.21788 | 1 | 3.9619 | 0.86319 | Low | Low | Medium | Bottom | 729 | 741 | 3.9619
CALPELLA 1102 | 043411102 | NORTHERN | HUMBOLDT | 8.9876 | 855830 | 43.4234 | 13.53% | 0% | 71% | 20.72% | 0 | 0 | 4 | 71% | 20.72% | 14.41% | 13 | 57 | 0 | 4 | 14 | 27 | 0 | 1 | 2 | 111 | 56.9783 | 11 | 8 | 3 | 50 | 0 | 0 | 4 | 0 | 0.41149 | 1.5474 | 2.5544 | 1.6265 | Medium | Low | Low | Bottom | 642 | 742 | 3.9527
SAN JOAQUIN #2 1103 | 252521103 | CENTRAL VALLEY | YOSEMITE | 82.7368 | 0 | 40.7023 | 70.75% | 24.8% | 64.51% | 0.9869% | 4 | 1 | 63 | 95.56% | 3.878% | 24.95% | 55 | 282 | 0 | 3 | 535 | 189 | 0 | 11 | 19 | 1551 | 24.2935 | 267 | 99 | 18 | 659 | 0 | 2 | 62 | 0 | 0.19463 | 1.3732 | 2.847 | 0.7609 | Low | Low | Low | Bottom | 743 | 743 | 3.9094
HIGGINS 1108 | 152691108 | NORTHERN | SIERRA | 0.020411 | 0 | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38633 | 1 | 3.8713 | 1.4956 | Medium | Low | Medium | Bottom | 656 | 744 | 3.8713
LLAGAS 2105 | 083182105 | CENTRAL COAST | SAN JOSE | 1.0027 | 1887415.3333 | 39.1667 | 44.62% | 0% | 28.55% | 71.45% | 0 | 0 | 0 | 28.55% | 71.45% | 25% | 2 | 6 | 0 | 0 | 4 | 0 | 0 | 1 | 1 | 12 | 2.3333 | 1 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.17908 | 1 | 3.8581 | 0.69092 | Low | Low | Medium | Bottom | 747 | 745 | 3.8581
LINCOLN 1101 | 153701101 | NORTHERN | SIERRA | 15.4033 | 1254118 | 42.8797 | 17.41% | 0.2279% | 69.74% | 15.81% | 3 | 0 | 24 | 69.66% | 16.12% | 8.857% | 47 | 232 | 1 | 0 | 26 | 15 | 0 | 3 | 5 | 350 | 31.0065 | 72 | 43 | 3 | 158 | 0 | 0 | 24 | 0 | 0.2797 | 1 | 3.7779 | 1.0567 | Low | Low | Medium | Bottom | 703 | 746 | 3.7779
FORT BRAGG A 1103 | 042761103 | NORTHERN | HUMBOLDT | 0.50874 | 386751 | 40 | 2.71% | 0% | 0% | 100% | 1 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 49 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0.15568 | 1 | 3.7413 | 0.58244 | Low | Low | Low | Bottom | 760 | 747 | 3.7413
SAN JOAQUIN #3 1102 | 252531102 | CENTRAL VALLEY | YOSEMITE | 11.5194 | 0 | 41.5593 | 25.3% | 37.17% | 21.4% | 0% | 0 | 0 | 5 | 68.21% | 30.26% | 18.18% | 46 | 29 | 0 | 0 | 155 | 8 | 0 | 2 | 4 | 297 | 27.3223 | 28 | 33 | 8 | 127 | 0 | 0 | 5 | 0 | 0.4064 | 1.2475 | 2.8926 | 1.4666 | Medium | Low | Low | Bottom | 664 | 748 | 3.6086
TRIDAM POWERHOUSE 2101 | 168152101 | CENTRAL VALLEY | YOSEMITE | 0.050313 | 0 | 45 | 0% | 100% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50016 | 1 | 3.5959 | 1.7985 | Medium | Low | Low | Bottom | 626 | 749 | 3.5959
ATASCADERO 1102 | 182541102 | CENTRAL COAST | LOS PADRES | 0.06615 | 401190.6667 | 40.5405 | 2.402% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 13.51% | 5 | 1 | 0 | 1 | 29 | 1 | 0 | 0 | 0 | 37 | 50.625 | 7 | 5 | 0 | 16 | 0 | 0 | 1 | 0 | 0.18797 | 1 | 3.5119 | 0.66013 | Low | Low | Low | Bottom | 749 | 750 | 3.5119
SUMMIT 1102 | 152591102 | NORTHERN | SIERRA | 5.1556 | 79007.6667 | 44.9682 | 7.908% | 35.59% | 12.9% | 0% | 1 | 0 | 17 | 50.08% | 12.9% | 48.78% | 40 | 42 | 2 | 0 | 14 | 11 | 0 | 8 | 14 | 164 | 18.2 | 9 | 8 | 5 | 50 | 0 | 0 | 17 | 1 | 0.67488 | 1 | 3.4497 | 2.3281 | High | Low | Low | Bottom | 578 | 751 | 3.4497
POSO MOUNTAIN 2103 | 253642103 | CENTRAL VALLEY | KERN | 19.5559 | 2531102 | 41.4823 | 634.8% | 53.78% | 6.828% | 4.128% | 0 | 0 | 4 | 59.97% | 4.774% | 13.72% | 7 | 7 | 0 | 39 | 17 | 19 | 0 | 1 | 5 | 226 | 9.2308 | 5 | 1 | 0 | 26 | 0 | 0 | 4 | 0 | 0.30673 | 11.9418 | 0.2873 | 1.0524 | Low | Medium | Low | Bottom | 704 | 752 | 3.4309
SUMMIT 1101 | 152591101 | NORTHERN | SIERRA | 8.961 | 191693.3333 | 44.9231 | 9.625% | 37.13% | 22.51% | 0% | 1 | 0 | 24 | 37.55% | 22.3% | 43.73% | 55 | 69 | 0 | 1 | 33 | 19 | 6 | 15 | 26 | 263 | 29.8889 | 31 | 12 | 5 | 71 | 0 | 1 | 24 | 1 | 0.64235 | 1 | 3.2921 | 2.1147 | Medium | Low | Low | Bottom | 593 | 753 | 3.2921
EAST MARYSVILLE 1108 | 152331108 | NORTHERN | SIERRA | 0.72214 | 645128.6667 | 49.4737 | 235.6% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 0% | 6 | 3 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 19 | 58 | 1 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0.22041 | 1 | 3.2275 | 0.71136 | Low | Low | Low | Bottom | 744 | 754 | 3.2275
MILPITAS 1105 | 082831105 | CENTRAL COAST | SAN JOSE | 0.10454 | 946778.6667 | 45 | 1.045% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0.11479 | 1 | 3.2168 | 0.36927 | Low | Low | Low | Bottom | 771 | 755 | 3.2168
BELLEVUE 1102 | 043181102 | NORTHERN | SONOMA | 0.26889 | 926382.3333 | 55 | 0.1733% | 0% | 2.546% | 0% | 0 | 0 | 0 | 0% | 2.546% | 0% | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 70 | 0 | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 0.27028 | 1 | 3.1712 | 0.8571 | Low | Low | Low | Bottom | 731 | 756 | 3.1712
BURNEY 1102 | 103311102 | NORTHERN | NORTH VALLEY | 0.75732 | 217117 | 43.1667 | 27.27% | 95.7% | 4.303% | 0% | 0 | 0 | 3 | 65.2% | 34.8% | 6.667% | 8 | 16 | 0 | 0 | 9 | 2 | 0 | 5 | 8 | 30 | 48.4444 | 0 | 3 | 1 | 9 | 0 | 0 | 3 | 0 | 0.39507 | 1 | 3.0566 | 1.2076 | Medium | Low | Low | Bottom | 686 | 757 | 3.0566
TEJON 1103 | 252931103 | CENTRAL VALLEY | KERN | 3.2497 | 897475.6667 | 40.8824 | 4.224% | 0% | 100% | 0% | 0 | 0 | 1 | 88.41% | 11.59% | 52.94% | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 17 | 1.2 | 1 | 0 | 0 | 6 | 0 | 0 | 1 | 0 | 0.18525 | 1 | 2.954 | 0.54721 | Low | Low | Low | Bottom | 762 | 758 | 2.954
WESTLEY 1103 | 162671103 | CENTRAL VALLEY | YOSEMITE | 0.92376 | 1373691.3333 | 0 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.20126 | 1 | 2.9097 | 0.5856 | Low | Low | Low | Bottom | 757 | 759 | 2.9097
NEWBURG 1132 | 192151132 | NORTHERN | HUMBOLDT | 2.5461 | 888833.3333 | 40.119 | 3.343% | 0% | 16% | 83.22% | 0 | 0 | 1 | 16% | 83.22% | 42.86% | 2 | 5 | 0 | 0 | 30 | 2 | 4 | 0 | 0 | 42 | 40.9333 | 2 | 1 | 0 | 16 | 0 | 0 | 1 | 0 | 0.31788 | 1 | 2.8437 | 0.90395 | Low | Low | Low | Bottom | 722 | 760 | 2.8437
SWIFT 2109 | 083392109 | CENTRAL COAST | SAN JOSE | 0.49434 | 1180547 | 43.3333 | 4.779% | 0% | 54.76% | 45.24% | 0 | 0 | 1 | 54.15% | 45.85% | 33.33% | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 27.5 | 2 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0.22298 | 1 | 2.6247 | 0.58525 | Low | Low | Low | Bottom | 758 | 761 | 2.6247
RED BLUFF 1105 | 103541105 | NORTHERN | NORTH VALLEY | 16.0727 | 975762 | 42.9052 | 46.95% | 0.2553% | 83.45% | 0.8702% | 0 | 0 | 14 | 83.71% | 0.8702% | 6.728% | 22 | 117 | 16 | 0 | 88 | 26 | 0 | 1 | 2 | 327 | 50.9636 | 61 | 77 | 9 | 168 | 0 | 1 | 14 | 0 | 0.12081 | 1.085 | 2.4168 | 0.31682 | Low | Low | Low | Bottom | 772 | 762 | 2.6224
RAWSON 1103 | 103531103 | NORTHERN | NORTH VALLEY | 5.0552 | 1257835.6667 | 40.1695 | 10.33% | 0% | 90.01% | 9.99% | 0 | 0 | 2 | 90.01% | 9.99% | 1.695% | 3 | 18 | 2 | 0 | 23 | 2 | 0 | 1 | 1 | 59 | 19 | 0 | 1 | 0 | 2 | 0 | 0 | 2 | 0 | 0.14966 | 6.7789 | 0.38645 | 0.39207 | Low | Medium | Low | Bottom | 770 | 763 | 2.6197
SAN BERNARD 1101 | 253191101 | CENTRAL VALLEY | KERN | 1.7421 | 784387.3333 | 42.1429 | 70.29% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 42.86% | 2 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 14 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.22097 | 1 | 2.5803 | 0.57017 | Low | Low | Low | Bottom | 761 | 764 | 2.5803
RISING RIVER 1101 | 103551101 | NORTHERN | NORTH VALLEY | 49.9892 | 170107.3333 | 40.6554 | 93.85% | 84.68% | 0.9855% | 0.04943% | 10 | 2 | 39 | 83.99% | 1.994% | 25.66% | 45 | 423 | 2 | 0 | 388 | 80 | 18 | 8 | 17 | 1091 | 28.8968 | 113 | 63 | 4 | 320 | 0 | 3 | 39 | 0 | 0.31716 | 1.5403 | 1.6242 | 0.79347 | Low | Low | Low | Bottom | 737 | 765 | 2.5018
SWIFT 2107 | 083392107 | CENTRAL COAST | SAN JOSE | 3.1689 | 1385965 | 43 | 8.6% | 0% | 50.39% | 49.61% | 1 | 0 | 3 | 50.39% | 49.61% | 7.5% | 0 | 7 | 1 | 1 | 13 | 2 | 0 | 1 | 1 | 40 | 33.1765 | 4 | 5 | 1 | 17 | 0 | 0 | 3 | 1 | 0.50063 | 1 | 2.4641 | 1.2336 | Medium | Low | Low | Bottom | 684 | 766 | 2.4641
ECHO SUMMIT 1101 | 158031101 |  |  | 7.2766 | 57440 | 42.0245 | 77.68% | 99.88% | 0% | 0% | 9 | 0 | 12 | 99.88% | 0% | 1.198% | 26 | 14 | 0 | 0 | 18 | 9 | 4 | 7 | 17 | 167 | 35.7674 | 23 | 10 | 0 | 43 | 0 | 0 | 12 | 1 | 0.6628 | 1 | 2.3846 | 1.5805 | High | Low | Low | Bottom | 647 | 767 | 2.3846
SO. CAL. EDISON #2 1101 | 258851101 | CENTRAL VALLEY | YOSEMITE | 1.1766 | 1647 | 44.375 | 0% | 64.34% | 35.66% | 0% | 0 | 0 | 0 | 100% | 0% | 27.27% | 4 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36946 | 1 | 2.3755 | 0.87763 | Medium | Low | Low | Bottom | 726 | 768 | 2.3755
SWIFT 2102 | 083392102 | CENTRAL COAST | SAN JOSE | 0.43953 | 1152399 | 44.5 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0.24835 | 1 | 2.373 | 0.58934 | Low | Low | Low | Bottom | 756 | 769 | 2.373
PIT NO 1 1101 | 103721101 | NORTHERN | NORTH VALLEY | 27.8419 | 391147 | 41.2516 | 91.04% | 80.42% | 7.618% | 0.6016% | 0 | 0 | 31 | 79.09% | 20.74% | 17.39% | 33 | 408 | 1 | 39 | 134 | 70 | 0 | 7 | 13 | 782 | 29.2965 | 77 | 45 | 4 | 212 | 0 | 2 | 30 | 0 | 0.20078 | 1.1824 | 1.7429 | 0.41377 | Low | Low | Low | Bottom | 769 | 770 | 2.0608
BRENTWOOD 2105 | 014592105 | BAY AREA | DIABLO | 10.7235 | 1598214.6667 | 48.0282 | 23.28% | 0% | 79.56% | 0.7279% | 3 | 0 | 18 | 79.56% | 0.7279% | 14.08% | 56 | 36 | 1 | 0 | 17 | 19 | 0 | 3 | 6 | 142 | 33.3421 | 12 | 7 | 1 | 50 | 0 | 0 | 18 | 0 | 0.28358 | 1 | 1.8205 | 0.51626 | Low | Low | Low | Bottom | 764 | 771 | 1.8205
COPPERMINE 1104 | 252411104 | CENTRAL VALLEY | FRESNO | 9.886 | 1003301.3333 | 41.5625 | 17.21% | 9.552% | 90.37% | 0% | 0 | 0 | 4 | 97.34% | 2.581% | 14.84% | 6 | 18 | 0 | 8 | 48 | 5 | 0 | 0 | 0 | 128 | 9.8889 | 22 | 10 | 0 | 48 | 0 | 0 | 4 | 0 | 0.14052 | 1.5859 | 1.1235 | 0.25038 | Low | Low | Low | Bottom | 776 | 772 | 1.7818
SOLEDAD 1114 | 182051114 | CENTRAL COAST | CENTRAL COAST | 1.7938 | 597876.6667 | 39.4118 | 6.374% | 0% | 18.9% | 74.54% | 0 | 0 | 0 | 18.9% | 74.54% | 17.65% | 0 | 4 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 17 | 17.25 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0.15817 | 1 | 1.7451 | 0.27603 | Low | Low | Low | Bottom | 774 | 773 | 1.7451
SOLEDAD 2101 | 182052101 | CENTRAL COAST | CENTRAL COAST | 7.4381 | 1365073.3333 | 39.569 | 32.52% | 0% | 83.79% | 16.21% | 0 | 0 | 1 | 83.79% | 16.21% | 5.085% | 3 | 24 | 0 | 1 | 20 | 6 | 0 | 0 | 0 | 59 | 33.3333 | 3 | 1 | 1 | 12 | 0 | 0 | 1 | 0 | 0.1398 | 3.375 | 0.50049 | 0.23613 | Low | Medium | Low | Bottom | 777 | 774 | 1.6891
RED BLUFF 1103 | 103541103 | NORTHERN | NORTH VALLEY | 15.9772 | 989293.3333 | 41.8375 | 31.22% | 0% | 100% | 0% | 1 | 0 | 14 | 100% | 0% | 7.463% | 21 | 220 | 38 | 2 | 76 | 12 | 0 | 3 | 6 | 402 | 47.6957 | 74 | 25 | 0 | 141 | 0 | 2 | 14 | 0 | 0.16041 | 2.6012 | 0.61946 | 0.25847 | Low | Medium | Low | Bottom | 775 | 775 | 1.6113
MC ARTHUR 1102 | 103491102 | NORTHERN | NORTH VALLEY | 2.2681 | 280004 | 42.2973 | 16.68% | 100% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 37.84% | 0 | 6 | 0 | 0 | 15 | 4 | 0 | 0 | 0 | 37 | 28.8333 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0.39471 | 3.3784 | 0.37689 | 0.50258 | Medium | Medium | Low | Bottom | 765 | 776 | 1.2733
PIT NO 7 1101 | 103501101 | NORTHERN | NORTH VALLEY | 2.7098 | 24 | 37.2881 | 46.77% | 100% | 0% | 0% | 0 | 0 | 1 | 100% | 0% | 1.695% | 0 | 31 | 3 | 0 | 15 | 0 | 0 | 0 | 0 | 59 | 75 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.35697 | 1 | 1.1934 | 0.42598 | Medium | Low | Low | Bottom | 768 | 777 | 1.1934
SPAULDING 1101 | 152251101 | NORTHERN | SIERRA | 20.6639 | 74813.3333 | 41.5306 | 37.59% | 78.87% | 19.25% | 1.193% | 1 | 0 | 33 | 71.79% | 28.19% | 17.71% | 94 | 121 | 1 | 0 | 147 | 46 | 0 | 5 | 15 | 463 | 30.2105 | 30 | 13 | 0 | 85 | 0 | 0 | 33 | 0 | 0.33581 | 14.0857 | 0.065741 | 0.31097 | Medium | High | Low | Bottom | 773 | 778 | 0.926
OROSI 1102 | 252841102 | CENTRAL VALLEY | FRESNO | 1.0335 | 201733.6667 | 40 | 2.259% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 0 | 0 | 8 | 7 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.17536 | 1 | 0.7238 | 0.12693 | Low | Low | Low | Bottom | 779 | 779 | 0.7238
EEL RIVER 1103 | 192381103 | NORTHERN | HUMBOLDT | 3.2275 | 0 | 39.717 | 3.864% | 0% | 5.057% | 94.94% | 0 | 0 | 1 | 0% | 100% | 15.09% | 0 | 1 | 0 | 0 | 42 | 2 | 0 | 0 | 0 | 53 | 10.3846 | 3 | 1 | 1 | 14 | 0 | 0 | 1 | 0 | 0.28292 | 1 | 0.37138 | 0.10507 | Low | Low | Low | Bottom | 780 | 780 | 0.37138
MC ARTHUR 1101 | 103491101 | NORTHERN | NORTH VALLEY | 76.2929 | 713606.6667 | 41.1192 | 53.09% | 80.41% | 18.32% | 1.11% | 4 | 0 | 38 | 80.84% | 19% | 18.85% | 86 | 642 | 11 | 1 | 363 | 134 | 11 | 7 | 17 | 1379 | 30.9336 | 108 | 47 | 5 | 305 | 0 | 2 | 38 | 0 | 0.21959 | 11.1195 | 0.012434 | 0.030362 | Low | Medium | Low | Bottom | 781 | 781 | 0.13826
ANTELOPE 1101 | 252021101 | CENTRAL VALLEY | KERN | 1.4593 | 220377.6667 | 45.2941 | 32.34% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 31.6667 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.21502 | 1 | 0 | 0 | Low | Low | Low | Bottom | 782 | 782 | 0
ARBUCKLE 1104 | 062081104 | NORTHERN | SACRAMENTO | 2.7857 | 1582717.6667 | 42.9167 | 25.06% | 0% | 53.89% | 0% | 0 | 0 | 0 | 53.89% | 0% | 30.56% | 0 | 24 | 0 | 0 | 1 | 11 | 0 | 0 | 0 | 36 | 36.4286 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0.26855 | 35.4977 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
BOGARD 1101 | 103301101 | NORTHERN | NORTH VALLEY | 0.51623 | 4451.6667 | 44.0909 | 1.719% | 100% | 0% | 0% | 1 | 0 | 2 | 100% | 0% | 18.18% | 5 | 0 | 0 | 0 | 4 | 1 | 0 | 0 | 0 | 11 | 44.5 | 1 | 0 | 2 | 4 | 0 | 0 | 2 | 1 | 0.54342 | 1 | 0 | 0 | Medium | Low | Low | Bottom | 782 | 782 | 0
CAL WATER 1102 | 255451102 | CENTRAL VALLEY | KERN | 4.089 | 1154810.3333 | 38.5 | 258.7% | 2.159% | 97.84% | 0% | 0 | 0 | 1 | 100% | 0% | 4.545% | 5 | 1 | 0 | 0 | 31 | 3 | 0 | 0 | 0 | 44 | 20.2 | 0 | 0 | 1 | 6 | 0 | 0 | 1 | 0 | 0.143 | 21.9936 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
CHOLAME 2102 | 182562102 | CENTRAL COAST | LOS PADRES | 61.1274 | 747236.6667 | 43.55 | 43.58% | 0% | 99.9% | 0% | 0 | 0 | 15 | 99.99% | 0% | 4.558% | 143 | 4 | 1 | 25 | 275 | 133 | 0 | 3 | 3 | 702 | 32.6042 | 57 | 15 | 4 | 155 | 0 | 0 | 15 | 0 | 0.136 | 12.0996 | 0 | 0 | Low | Medium | Low | Bottom | 782 | 782 | 0
CORTINA 1101 | 063121101 | NORTHERN | SACRAMENTO | 1.8918 | 629529.6667 | 39.6667 | 33.7% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 9.625 | 2 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0.11269 | 57.3601 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
CUYAMA 1103 | 253141103 | CENTRAL VALLEY | KERN | 3.0287 | 510804.3333 | 36.9048 | 151.4% | 100% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 2.381% | 0 | 0 | 0 | 0 | 29 | 1 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.28678 | 19.2951 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
GONZALES 1101 | 182131101 | CENTRAL COAST | CENTRAL COAST | 4.0882 | 645442.6667 | 39.3636 | 5.493% | 0% | 100% | 0% | 1 | 0 | 3 | 100% | 0% | 9.091% | 0 | 16 | 0 | 3 | 29 | 3 | 0 | 2 | 3 | 55 | 6.3333 | 8 | 1 | 0 | 16 | 0 | 0 | 3 | 0 | 0.16692 | 23.766 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
GONZALES 1104 | 182131104 | CENTRAL COAST | CENTRAL COAST | 1.2503 | 882987 | 33.5 | 12.61% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 8 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 10 | 11.8 | 1 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0.13772 | 33.2799 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
HOLLISTER 2105 | 182492105 | CENTRAL COAST | CENTRAL COAST | 65.1927 | 929904.3333 | 39.1655 | 39.8% | 0% | 93.72% | 6.248% | 1 | 1 | 28 | 72.38% | 27.58% | 14.62% | 15 | 170 | 0 | 6 | 378 | 37 | 0 | 3 | 6 | 732 | 13.0778 | 68 | 18 | 4 | 181 | 0 | 0 | 28 | 0 | 0.11723 | 30.1446 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
HOLLISTER 2106 | 182492106 | CENTRAL COAST | CENTRAL COAST | 7.5432 | 1499231.3333 | 38.8372 | 10.94% | 13.15% | 47.54% | 39.32% | 1 | 0 | 6 | 60.68% | 39.32% | 6.154% | 4 | 69 | 0 | 1 | 48 | 1 | 0 | 2 | 2 | 130 | 7.875 | 1 | 6 | 0 | 25 | 0 | 0 | 6 | 0 | 0.38778 | 22.2831 | 0 | 0 | Medium | High | Low | Bottom | 782 | 782 | 0
KERN OIL 1106 | 252721106 | CENTRAL VALLEY | KERN | 1.699 | 2034157.3333 | 44.375 | 64.02% | 71.87% | 14.58% | 0% | 0 | 0 | 0 | 33.5% | 54.13% | 12.5% | 4 | 0 | 1 | 1 | 6 | 2 | 0 | 1 | 2 | 16 | 8.25 | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 0.22347 | 1 | 0 | 0 | Low | Low | Low | Bottom | 782 | 782 | 0
LAMONT 1102 | 253911102 | CENTRAL VALLEY | KERN | 2.6581 | 1861598.6667 | 30 | 268.1% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0.18236 | 15.9013 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
LOGAN CREEK 2102 | 103142102 | NORTHERN | NORTH VALLEY | 3.7103 | 5213559.3333 | 39.7321 | 18.3% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 5.357% | 0 | 47 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 56 | 38.5 | 1 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 0.14988 | 43.0895 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
LOS MOLINOS 1101 | 103481101 | NORTHERN | NORTH VALLEY | 0.48216 | 389350.6667 | 40.8333 | 2.935% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 2 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6 | 46.6667 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.20779 | 6.0236 | 0 | 0 | Low | Medium | Low | Bottom | 782 | 782 | 0
MADISON 1105 | 063171105 | NORTHERN | SACRAMENTO | 0.39195 | 665239 | 41.6667 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 11.11% | 3 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0.19729 | 1 | 0 | 0 | Low | Low | Low | Bottom | 782 | 782 | 0
MADISON 2101 | 063172101 | NORTHERN | SACRAMENTO | 11.0838 | 2158591 | 39.7436 | 43.35% | 0% | 92.2% | 0% | 0 | 0 | 0 | 98.13% | 1.654% | 0% | 4 | 31 | 4 | 0 | 24 | 1 | 0 | 1 | 1 | 78 | 34.7391 | 4 | 3 | 1 | 25 | 0 | 0 | 0 | 0 | 0.18239 | 33.1406 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
MAXWELL 1105 | 062881105 | NORTHERN | SACRAMENTO | 5.6752 | 0 | 39.3333 | 163.5% | 0% | 100% | 0% | 0 | 0 | 3 | 100% | 0% | 1.667% | 3 | 33 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 60 | 33.2 | 1 | 1 | 1 | 6 | 0 | 0 | 3 | 0 | 0.2019 | 20.9871 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
PANOCHE 1103 | 253671103 | CENTRAL VALLEY | YOSEMITE | 45.8174 | 375649.3333 | 39.2123 | 0% | 5.007% | 94.85% | 0% | 0 | 0 | 13 | 99.86% | 0% | 9.06% | 10 | 99 | 0 | 7 | 419 | 29 | 0 | 4 | 5 | 585 | 12.4105 | 30 | 8 | 0 | 100 | 0 | 0 | 13 | 0 | 0.1229 | 18.0183 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
POSO MOUNTAIN 2104 | 253642104 | CENTRAL VALLEY | KERN | 10.6702 | 636738.6667 | 45.6306 | 256.2% | 36.67% | 12.88% | 4.505% | 0 | 0 | 6 | 7.714% | 46.34% | 9.91% | 42 | 0 | 0 | 22 | 6 | 2 | 0 | 3 | 8 | 111 | 15.2727 | 0 | 0 | 0 | 12 | 0 | 1 | 6 | 0 | 0.27482 | 1 | 0 | 0 | Low | Low | Low | Bottom | 782 | 782 | 0
SISQUOC 1103 | 182811103 | CENTRAL COAST | LOS PADRES | 31.0209 | 410840.6667 | 41.4564 | 66.35% | 7.979% | 81.09% | 10.21% | 0 | 2 | 14 | 75.22% | 24.06% | 9.153% | 41 | 29 | 0 | 78 | 143 | 50 | 0 | 2 | 3 | 437 | 25.2137 | 40 | 8 | 1 | 138 | 0 | 0 | 14 | 0 | 0.1372 | 18.4213 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
SPENCE 1122 | 182201122 | CENTRAL COAST | CENTRAL COAST | 10.095 | 1053579.3333 | 38.2432 | 12.27% | 0% | 70.1% | 29.9% | 0 | 0 | 8 | 40.54% | 59.46% | 9.189% | 2 | 101 | 1 | 5 | 36 | 9 | 0 | 3 | 3 | 185 | 14.8378 | 25 | 5 | 0 | 77 | 0 | 0 | 8 | 0 | 0.34488 | 17.4168 | 0 | 0 | Medium | High | Low | Bottom | 782 | 782 | 0
SPENCE 1123 | 182201123 | CENTRAL COAST | CENTRAL COAST | 3.6031 | 662970.6667 | 40.5128 | 8.968% | 0% | 72.53% | 27.47% | 0 | 0 | 3 | 72.53% | 27.47% | 17.95% | 2 | 1 | 0 | 0 | 35 | 3 | 0 | 0 | 0 | 39 | 11.7778 | 2 | 1 | 0 | 9 | 0 | 0 | 3 | 0 | 0.22621 | 8.3263 | 0 | 0 | Low | Medium | Low | Bottom | 782 | 782 | 0
STONE CORRAL 1108 | 252921108 | CENTRAL VALLEY | FRESNO | 3.1209 | 556516.3333 | 40.3125 | 12.95% | 0% | 72.81% | 27.19% | 0 | 0 | 1 | 15.34% | 84.66% | 41.18% | 4 | 0 | 0 | 0 | 17 | 7 | 0 | 0 | 1 | 51 | 0 | 0 | 2 | 0 | 7 | 0 | 0 | 1 | 0 | 0.25854 | 1 | 0 | 0 | Low | Low | Low | Bottom | 782 | 782 | 0
STONE CORRAL 1110 | 252921110 | CENTRAL VALLEY | FRESNO | 3.0023 | 354094.6667 | 38.8462 | 3.702% | 0% | 82.82% | 17.18% | 0 | 0 | 1 | 53.37% | 46.63% | 33.33% | 3 | 0 | 0 | 10 | 7 | 1 | 0 | 0 | 0 | 42 | 8.5556 | 3 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 0.19694 | 3.3888 | 0 | 0 | Low | Medium | Low | Bottom | 782 | 782 | 0
TRES PINOS 1111 | 183221111 | CENTRAL COAST | CENTRAL COAST | 0.10269 | 110901.6667 | 35 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.21599 | 19.9979 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0

## Tx - Inspection
Tx Prioritization Output - Inspections
Circuit Information |  |  |  | Independent Variables | [7 empty] | Dependent Variable | Risk Scoring |  |  |  |  | Risk Tiers
Feeder Name | Circuit ID | District | Number of structures | # of Bird Notifications | # of Structure Crack Notifications | % of Horizontal frames along line | % of Tri-arm frames along line | % of Wishbone frames along line | Miles of Conductor Size - 4/0 | % Conductor Type - Copper | % of structures steel | Above average outage indicator | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Consolidated Risk Score | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Rank Cons Risk | Rank P*C | P*C
DRUM-GRASS VALLEY-WEIMAR - 60 kV | ETL.6760 | SIERRA | 722 | 5 | 0 | 2.014% | 80.43% | 0% | 0 | 76.79% | 6.043% | 1 | 0.99999 | 61.4248 | 1.6093 | 98.852 | High | High | Medium | 1 | 1 | 61.4243
DONNELLS-CURTIS - 115 kV | ETL.1400 | YOSEMITE | 261 | 0 | 0 | 0.3831% | 0% | 0% | 0 | 0% | 28.35% | 1 | 0.83858 | 43.9281 | 2.5696 | 94.658 | High | High | High | 2 | 4 | 36.8371
COLGATE-CHALLENGE - 60 kV | ETL.6480 | SIERRA | 231 | 0 | 0 | 1.299% | 86.15% | 0% | 0 | 39.37% | 3.896% | 1 | 0.88412 | 53.9348 | 1.6444 | 78.4139 | High | High | Medium | 3 | 2 | 47.685
SNEATH LANE-HALF MOON BAY - 60 kV | ETL.7212 | PENINSULA | 145 | 0 | 0 | 8.271% | 11.28% | 20.3% | 0 | 0% | 27.07% | 1 | 0.49769 | 56.971 | 2.7544 | 78.0978 | High | High | High | 4 | 10 | 28.3536
FULTON-CALISTOGA - 60 kV | ETL.6880 | SONOMA | 411 | 0 | 0 | 1.496% | 29.93% | 0% | 0 | 32.66% | 35.91% | 1 | 0.99284 | 34.4741 | 2.1816 | 74.6698 | High | High | High | 5 | 5 | 34.2273
IGNACIO-BOLINAS #2 - 60 kV | ETL.7180 | NORTH BAY | 304 | 0 | 0 | 12.76% | 49.31% | 0% | 0 | 2.157% | 15.17% | 1 | 0.91039 | 30.0537 | 2.6424 | 72.2984 | High | High | High | 6 | 12 | 27.3605
COLGATE-ALLEGHANY - 60 kV | ETL.6470 | SIERRA | 673 | 0 | 0 | 2.526% | 91.53% | 0% | 0 | 8.346e-05% | 2.377% | 1 | 0.9999 | 42.804 | 1.4581 | 62.404 | High | High | Low | 7 | 3 | 42.7996
TIGER CREEK-VALLEY SPRINGS - 230 kV | ETL.5790 | STOCKTON | 129 | 0 | 0 | 0% | 1.55% | 0% | 0 | 0% | 100% | 1 | 0.61815 | 40.1602 | 2.4336 | 60.4132 | High | High | High | 8 | 17 | 24.825
IGNACIO-BOLINAS #1 - 60 kV | ETL.7140 | NORTH BAY | 192 | 0 | 0 | 3.684% | 23.16% | 0% | 0 | 0% | 3.158% | 0 | 0.58811 | 30.7705 | 3.2833 | 59.4163 | High | High | High | 9 | 37 | 18.0964
DRUM-HIGGINS - 115 kV | ETL.4393 | SIERRA | 271 | 0 | 0 | 0.3717% | 0.3717% | 0% | 17.15 | 0.08243% | 85.5% | 1 | 0.92443 | 34.4371 | 1.8446 | 58.7222 | High | High | Medium | 10 | 8 | 31.8348
MIDDLE FORK-GOLD HILL - 230 kV | ETL.5140 | SIERRA | 309 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 32.68% | 1 | 0.89699 | 33.5605 | 1.8785 | 56.5498 | High | High | Medium | 11 | 9 | 30.1034
VALLEY SPRINGS #2 - 60 kV | ETL.9460 | STOCKTON | 177 | 0 | 0 | 3.55% | 82.84% | 0% | 1.96 | 96.38% | 2.367% | 1 | 0.87735 | 27.3903 | 2.3528 | 56.5388 | High | High | High | 12 | 19 | 24.0309
CARIBOU-PLUMAS JCT - 60 kV | ETL.6290 | NORTH VALLEY | 316 | 0 | 0 | 0% | 76.71% | 0% | 0 | 9.544% | 10.96% | 1 | 0.91037 | 37.4705 | 1.6483 | 56.2262 | High | High | Medium | 13 | 6 | 34.1121
DRUM-RIO OSO #1 - 115 kV | ETL.1420 | SIERRA | 253 | 0 | 0 | 0% | 15.92% | 0% | 39248.74 | 62.17% | 100% | 1 | 0.92417 | 34.6401 | 1.6999 | 54.4181 | High | High | Medium | 14 | 7 | 32.0133
BURNS-LONE STAR #2 - 60 kV | ETL.6240 | CENTRAL COAST | 120 | 0 | 0 | 0% | 71.67% | 0% | 5.88 | 100% | 3.333% | 1 | 0.6844 | 27.3586 | 2.8962 | 54.2296 | High | High | High | 15 | 36 | 18.7243
MONTA VISTA-BURNS-60 kV | ETL.7590 | CENTRAL COAST | 192 | 0 | 0 | 0% | 37.37% | 0.5263% | 2.86 | 15.95% | 3.158% | 1 | 0.74624 | 26.9169 | 2.5939 | 52.1025 | High | High | High | 16 | 29 | 20.0865
MORAGA-OAKLAND #3 - 115 kV | ETL.2740 | EAST BAY | 32 | 0 | 0 | 3.125% | 0% | 0% | 4.69 | 92.14% | 96.88% | 0 | 0.45876 | 38.9244 | 2.8994 | 51.775 | High | High | High | 17 | 39 | 17.857
LOWER LAKE-HOMESTAKE - 115 kV | ETL.1481 | NORTH BAY | 286 | 0 | 0 | 1.099% | 77.66% | 0% | 0 | 0% | 0.7326% | 1 | 0.89488 | 26.1579 | 2.0768 | 48.6142 | High | High | Medium | 18 | 22 | 23.4083
FULTON-PUEBLO - 115 kV | ETL.1600 | SONOMA | 236 | 0 | 0 | 0% | 7.547% | 0% | 0 | 52.55% | 90.09% | 1 | 0.92191 | 25.8687 | 1.9488 | 46.4771 | High | High | Medium | 19 | 21 | 23.8486
KESWICK-CASCADE - 60 kV | ETL.7260 | NORTH VALLEY | 173 | 0 | 0 | 7.784% | 72.46% | 0% | 0 | 95.04% | 2.395% | 1 | 0.83687 | 25.1187 | 2.1885 | 46.0052 | High | High | High | 20 | 26 | 21.0211
OLEUM-G #1 - 115 kV | ETL.3150 | EAST BAY | 70 | 0 | 0 | 0% | 1.562% | 0% | 0 | 97.34% | 100% | 0 | 0.69963 | 19.9899 | 3.1716 | 44.3565 | High | High | High | 21 | 54 | 13.9855
EL DORADO-MISSOURI FLAT #1 - 115 kV | ETL.1530 | SIERRA | 123 | 0 | 0 | 0% | 14.78% | 0% | 8.7 | 52.37% | 80% | 1 | 0.58562 | 44.9626 | 1.6434 | 43.272 | High | High | Medium | 22 | 13 | 26.3311
WEIMAR #1 - 60 kV | ETL.7560 | SIERRA | 208 | 0 | 0 | 0% | 60.1% | 0% | 0 | 3.154% | 9.615% | 1 | 0.67014 | 35.5947 | 1.7849 | 42.5755 | High | High | Medium | 23 | 20 | 23.8534
SOBRANTE-GRIZZLY-CLAREMONT #1 - 115 kV | ETL.3740 | EAST BAY | 72 | 0 | 0 | 0% | 0% | 0% | 2.47 | 45.95% | 94.03% | 1 | 0.28433 | 50.2279 | 2.9401 | 41.9877 | Medium | High | High | 24 | 53 | 14.2811
SOBRANTE-R #1 - 115 kV | ETL.3770 | DIABLO | 39 | 0 | 0 | 0% | 0% | 0% | 4.99 | 90.89% | 100% | 0 | 0.3256 | 34.917 | 3.4918 | 39.6988 | Medium | High | High | 25 | 77 | 11.3691
CASCADE-BENTON-DESCHUTES - 60 kV | ETL.6310 | NORTH VALLEY | 216 | 0 | 0 | 3.646% | 80.73% | 0% | 0 | 27.28% | 3.646% | 1 | 0.73686 | 26.702 | 1.9397 | 38.1647 | High | High | Medium | 26 | 32 | 19.6756
WOODLEAF-PALERMO - 115 kV | ETL.4220 | NORTH VALLEY | 216 | 0 | 0 | 6.863% | 10.78% | 20.59% | 0 | 0% | 23.53% | 1 | 0.7943 | 19.3341 | 2.4478 | 37.5916 | High | High | High | 27 | 47 | 15.3571
CARIBOU #2 - 60 kV | ETL.6280 | NORTH VALLEY | 979 | 0 | 0 | 0% | 77.27% | 0% | 0 | 46.53% | 6.025% | 1 | 1 | 26.0762 | 1.4257 | 37.1764 | High | High | Low | 28 | 15 | 26.0762
LAURELES-OTTER - 60 kV | ETL.7380 | CENTRAL COAST | 186 | 0 | 0 | 0.5495% | 43.41% | 3.297% | 0 | 0% | 1.648% | 1 | 0.68883 | 29.7893 | 1.8027 | 36.9913 | High | High | Medium | 29 | 27 | 20.5197
DESABLA-CENTERVILLE-60 kV | ETL.6720 | NORTH VALLEY | 118 | 0 | 0 | 2.586% | 33.62% | 0% | 0 | 0% | 7.759% | 1 | 0.32671 | 40.6722 | 2.7737 | 36.8568 | Medium | High | High | 30 | 58 | 13.2881
GOLD HILL #1 - 60 kV | ETL.6950 | STOCKTON | 309 | 0 | 0 | 3.448% | 73.56% | 0% | 0 | 0% | 21.46% | 1 | 0.87734 | 19.7877 | 2.101 | 36.4738 | High | High | Medium | 31 | 41 | 17.3605
CORTINA-MENDOCINO #1 - 115 kV | ETL.1330 | HUMBOLDT | 279 | 1 | 0 | 0% | 0% | 0% | 0 | 0% | 99.62% | 1 | 0.93671 | 21.4265 | 1.7981 | 36.0883 | High | High | Medium | 32 | 30 | 20.0705
VACA-SUISUN - 115 kV | ETL.4070 | SACRAMENTO | 60 | 0 | 0 | 0% | 0% | 0% | 0 | 80.46% | 100% | 0 | 0.34087 | 59.1312 | 1.7846 | 35.9715 | Medium | High | Medium | 33 | 28 | 20.1561
EAGLE ROCK-REDBUD - 115 kV | ETL.1480 | HUMBOLDT | 210 | 0 | 0 | 0.4785% | 53.11% | 0% | 0 | 0% | 38.76% | 1 | 0.74696 | 19.8086 | 2.3308 | 34.487 | High | High | High | 34 | 50 | 14.7963
MORRO BAY-MESA - 230 kV | ETL.5290 | LOS PADRES | 142 | 2 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.59752 | 25.4896 | 2.2562 | 34.3625 | High | High | High | 35 | 48 | 15.2305
SOBRANTE-GRIZZLY-CLAREMONT #2 - 115 kV | ETL.3750 | EAST BAY | 51 | 0 | 0 | 0% | 0% | 0% | 2.92 | 52.61% | 93.48% | 0 | 0.23186 | 51.1677 | 2.8735 | 34.091 | Medium | High | High | 36 | 73 | 11.864
WEST POINT-VALLEY SPRINGS - 60 kV | ETL.8350 | STOCKTON | 243 | 0 | 0 | 2.49% | 61.41% | 0% | 9.84 | 2.865% | 4.149% | 1 | 0.80835 | 18.1513 | 2.3207 | 34.0502 | High | Medium | High | 37 | 51 | 14.6726
MORAGA-CLAREMONT #1 - 115 kV | ETL.2700 | EAST BAY | 28 | 0 | 0 | 0% | 0% | 0% | 0.5 | 54.61% | 78.57% | 0 | 0.16808 | 71.155 | 2.8221 | 33.7502 | Medium | High | High | 38 | 71 | 11.9594
KESWICK-TRINITY - 60 kV | ETL.7270 | NORTH VALLEY | 559 | 0 | 0 | 0.1842% | 45.49% | 0% | 0 | 0.3941% | 29.1% | 1 | 0.99907 | 19.4324 | 1.7309 | 33.6046 | High | High | Medium | 39 | 33 | 19.4143
CARIBOU-WESTWOOD - 60 kV | ETL.6300 | NORTH VALLEY | 471 | 0 | 0 | 0% | 63.12% | 0% | 0 | 0% | 0.2169% | 1 | 0.99339 | 17.0098 | 1.9829 | 33.505 | High | Medium | Medium | 40 | 44 | 16.8973
BRIDGEVILLE-COTTONWOOD - 115 kV | ETL.1110 | NORTH VALLEY | 615 | 0 | 0 | 0% | 0.1664% | 0% | 0 | 0% | 47.75% | 1 | 0.99967 | 26.1443 | 1.2791 | 33.4312 | High | High | Low | 41 | 14 | 26.1358
MORAGA-LAKEWOOD - 115 kV | ETL.3741 | DIABLO | 38 | 0 | 0 | 0% | 0% | 0% | 7.01 | 89.99% | 100% | 0 | 0.29211 | 38.833 | 2.9063 | 32.9682 | Medium | High | High | 42 | 78 | 11.3436
MORAGA-OAKLAND #1 - 115 kV | ETL.2720 | EAST BAY | 34 | 0 | 0 | 0% | 0% | 0% | 5.08 | 100% | 100% | 0 | 0.34143 | 33.1672 | 2.9027 | 32.8706 | Medium | High | High | 43 | 79 | 11.3242
TIGER CREEK-ELECTRA - 230 kV | ETL.5780 | STOCKTON | 108 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.29608 | 42.8453 | 2.4711 | 31.3479 | Medium | High | High | 44 | 63 | 12.6858
MORAGA-CLAREMONT #2 - 115 kV | ETL.2710 | DIABLO | 5 | 0 | 0 | 0% | 0% | 0% | 0 | 58.46% | 80% | 0 | 0.12578 | 85.4511 | 2.8877 | 31.0378 | Medium | High | High | 45 | 85 | 10.7483
VACA-VACAVILLE-JAMESON-NORTH TOWER - 115 kV | ETL.4100 | SACRAMENTO | 64 | 0 | 1 | 0% | 0% | 0% | 20.42 | 65.56% | 100% | 1 | 0.29048 | 59.1312 | 1.784 | 30.6436 | Medium | High | Medium | 46 | 42 | 17.1765
KONOCTI-MIDDLETOWN-60 kV | ETL.6380 | HUMBOLDT | 200 | 0 | 0 | 2.809% | 44.38% | 0% | 0 | 0% | 29.78% | 1 | 0.59745 | 22.9913 | 2.1952 | 30.1533 | High | High | High | 47 | 55 | 13.7361
ELK-GUALALA - 60 kV | ETL.8410 | HUMBOLDT | 281 | 0 | 0 | 2.632% | 1.128% | 50.38% | 0 | 0.2315% | 8.271% | 1 | 0.9027 | 24.7621 | 1.3336 | 29.8106 | High | High | Low | 48 | 23 | 22.3527
EAGLE ROCK-CORTINA - 115 kV | ETL.1470 | HUMBOLDT | 139 | 0 | 0 | 1.439% | 82.73% | 0% | 0 | 0% | 7.914% | 1 | 0.49119 | 25.2351 | 2.3948 | 29.6841 | High | High | High | 49 | 67 | 12.3951
OAKHURST TAP - 115 kV | ETL.1252 | YOSEMITE | 229 | 0 | 0 | 26.67% | 0.8889% | 0% | 0 | 0% | 98.67% | 0 | 0.86013 | 20.9951 | 1.6281 | 29.4008 | High | High | Medium | 50 | 38 | 18.0585
SALINAS-LAURELES - 60 kV | ETL.7930 | CENTRAL COAST | 352 | 1 | 0 | 4.334% | 71.83% | 0.3096% | 12.03 | 48.34% | 3.715% | 1 | 0.99115 | 15.7708 | 1.8636 | 29.1309 | High | Medium | Medium | 51 | 46 | 15.6312
FORT ROSS-GUALALA-60 kV | ETL.6980 | SONOMA | 347 | 0 | 0 | 8.116% | 27.83% | 0.5797% | 0 | 0.1345% | 9.275% | 1 | 0.97451 | 20.2736 | 1.4732 | 29.105 | High | High | Low | 52 | 31 | 19.7568
TRINITY-COTTONWOOD - 115 kV | ETL.4040 | NORTH VALLEY | 358 | 0 | 0 | 0.2849% | 0% | 0% | 0 | 0% | 34.47% | 1 | 0.96283 | 17.7613 | 1.6847 | 28.8109 | High | Medium | Medium | 53 | 43 | 17.101
MONTE RIO-FORT ROSS-60 kV | ETL.6979 | SONOMA | 107 | 0 | 0 | 5.941% | 17.82% | 0.9901% | 0 | 0% | 16.83% | 0 | 0.36878 | 36.6287 | 2.0774 | 28.0616 | Medium | High | Medium | 54 | 56 | 13.5078
MORAGA-OAKLAND #4 - 115 kV | ETL.2750 | DIABLO | 1 | 0 | 0 | 0% | 0% | 0% | 4.69 | 91.96% | 0% | 0 | 0.11062 | 85.4511 | 2.8615 | 27.0487 | Low | High | High | 55 | 90 | 9.4527
CASCADE-COTTONWOOD-115 kV | ETL.1240 | NORTH VALLEY | 125 | 0 | 0 | 0% | 0% | 0% | 0 | 73.26% | 39.82% | 1 | 0.47998 | 29.817 | 1.8377 | 26.2996 | High | High | Medium | 56 | 52 | 14.3115
JOLON TAP - 60 kV | ETL.7321 | CENTRAL COAST | 239 | 0 | 0 | 2.532% | 74.68% | 0% | 0 | 0% | 0.4219% | 0 | 0.83995 | 21.1123 | 1.474 | 26.1385 | High | High | Low | 57 | 40 | 17.7332
CABRILLO-SANTA YNEZ SW STA - 115 kV | ETL.1200 | LOS PADRES | 121 | 0 | 0 | 6.034% | 47.41% | 0% | 0 | 0% | 99.14% | 1 | 0.55894 | 21.2809 | 2.1513 | 25.5891 | High | High | High | 58 | 72 | 11.8948
HUMBOLDT-TRINITY - 115 kV | ETL.1820 |  | 459 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 11.73% | 1 | 0.99018 | 15.2143 | 1.6866 | 25.4077 | High | Medium | Medium | 59 | 49 | 15.0649
DIABLO-MIDWAY #3 - 500 kV | ETL.5980 | LOS PADRES | 205 | 21 | 10 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.82048 | 13.5839 | 2.1095 | 23.5106 | High | Medium | Medium | 60 | 80 | 11.1453
PHILO JCT-ELK - 60 kV | ETL.7780 | HUMBOLDT | 372 | 0 | 0 | 0% | 49.12% | 0% | 0 | 0% | 2.924% | 1 | 0.95021 | 20.1257 | 1.2279 | 23.4827 | High | High | Low | 61 | 34 | 19.1237
DRUM-RIO OSO #2 - 115 kV | ETL.1430 | SIERRA | 124 | 0 | 0 | 0% | 0% | 0% | 39248.74 | 66.44% | 99.19% | 1 | 0.41869 | 51.148 | 1.0915 | 23.3745 | High | High | Low | 62 | 24 | 21.4153
GREEN VALLEY-LLAGAS - 115 kV | ETL.1720 | SAN JOSE | 100 | 0 | 0 | 1.087% | 3.261% | 0% | 13.88 | 56.08% | 43.48% | 0 | 0.52714 | 23.9919 | 1.8163 | 22.9715 | High | High | Medium | 63 | 64 | 12.6471
TRINITY-MAPLE CREEK - 60 kV | ETL.8170 |  | 690 | 0 | 0 | 0% | 44.13% | 0% | 0 | 0% | 8.798% | 1 | 0.99988 | 19.0199 | 1.2009 | 22.8391 | High | High | Low | 64 | 35 | 19.0177
DIABLO-MIDWAY #2 - 500 kV | ETL.5970 | LOS PADRES | 199 | 8 | 8 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.80133 | 13.303 | 2.1027 | 22.4149 | High | Medium | Medium | 65 | 86 | 10.6601
CARIBOU-PALERMO - 115 kV | ETL.3190 | NORTH VALLEY | 416 | 0 | 0 | 0.2421% | 0% | 0% | 13.17 | 0.008246% | 99.52% | 1 | 0.99301 | 11.062 | 2.0087 | 22.0649 | High | Medium | Medium | 66 | 82 | 10.9848
MONTE RIO-FULTON-60 kV | ETL.7630 | SONOMA | 67 | 0 | 0 | 0% | 31.15% | 0% | 0 | 0.5814% | 21.31% | 1 | 0.14207 | 61.445 | 2.4798 | 21.6477 | Medium | High | High | 67 | 97 | 8.7296
COLGATE-GRASS VALLEY - 60 kV | ETL.6490 | SIERRA | 318 | 0 | 0 | 1.045% | 82.23% | 0% | 0 | 100% | 4.53% | 1 | 0.97627 | 11.036 | 1.9598 | 21.1148 | High | Medium | Medium | 68 | 84 | 10.7741
ATASCADERO-CAYUCOS-70 kV | ETL.8480 | LOS PADRES | 78 | 0 | 0 | 0% | 26.32% | 30.26% | 11.77 | 0% | 9.211% | 1 | 0.39088 | 31.2999 | 1.7198 | 21.041 | Medium | High | Medium | 69 | 69 | 12.2345
MONTA VISTA-COYOTE SW STA - 230 kV | ETL.5090 | SAN JOSE | 118 | 1 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.47387 | 19.2506 | 2.3056 | 21.0321 | High | High | High | 70 | 95 | 9.1222
WATSONVILLE-SALINAS - 60 kV | ETL.8310 | CENTRAL COAST | 114 | 0 | 0 | 6.542% | 39.25% | 0% | 13.89 | 98.95% | 0% | 1 | 0.62734 | 20.2425 | 1.6512 | 20.9684 | High | High | Medium | 71 | 62 | 12.6989
DIVIDE-CABRILLO #2 - 115 kV | ETL.1370 | LOS PADRES | 88 | 10 | 0 | 2.817% | 5.634% | 0% | 0 | 0% | 7.042% | 1 | 0.36218 | 20.0715 | 2.8774 | 20.9167 | Medium | High | High | 72 | 111 | 7.2694
LAKEVILLE #2 - 60 kV | ETL.7340 | NORTH BAY | 135 | 0 | 0 | 2.542% | 80.51% | 0% | 0 | 55.51% | 0.8475% | 1 | 0.60017 | 20.6905 | 1.6469 | 20.4512 | High | High | Medium | 73 | 66 | 12.4178
BRIDGEVILLE-GARBERVILLE - 60 kV | ETL.6220 | HUMBOLDT | 385 | 0 | 0 | 0% | 64.84% | 0% | 0 | 0% | 5.859% | 1 | 0.826 | 29.4235 | 0.82836 | 20.1322 | High | High | Low | 74 | 18 | 24.3038
VOLTA-DESCHUTES - 60 kV | ETL.8290 | NORTH VALLEY | 452 | 0 | 0 | 0.2257% | 93.91% | 0% | 0 | 98.66% | 6.095% | 1 | 0.99859 | 12.2897 | 1.6223 | 19.9096 | High | Medium | Medium | 75 | 68 | 12.2723
EAGLE ROCK-FULTON-SILVERADO - 115 kV | ETL.4392 | SONOMA | 132 | 0 | 0 | 0% | 0% | 0% | 0 | 18.43% | 100% | 1 | 0.46278 | 27.2597 | 1.4902 | 18.7994 | High | High | Medium | 76 | 65 | 12.6153
DEER CREEK-DRUM - 60 kV | ETL.6690 | SIERRA | 149 | 0 | 0 | 0.6711% | 77.18% | 0% | 0 | 100% | 12.75% | 1 | 0.8129 | 34.8559 | 0.65761 | 18.6327 | High | High | Low | 77 | 11 | 28.3342
KONOCTI-EAGLE ROCK - 60 kV | ETL.6861 | SONOMA | 122 | 0 | 0 | 1.786% | 21.43% | 0% | 0 | 0% | 8.929% | 0 | 0.33835 | 27.224 | 2.0219 | 18.624 | Medium | High | Medium | 78 | 93 | 9.2112
CORDELIA #1 TAP - 60 kV | ETL.8182 | SACRAMENTO | 70 | 0 | 0 | 4.478% | 62.69% | 0% | 0 | 92.89% | 2.985% | 0 | 0.58387 | 15.7603 | 2.0137 | 18.5298 | High | Medium | Medium | 79 | 94 | 9.202
CLAY-MARTEL - 60 kV | ETL.8250 | STOCKTON | 339 | 0 | 0 | 2.857% | 74.6% | 0% | 0 | 21.08% | 5.397% | 1 | 0.96289 | 8.2748 | 2.3219 | 18.5006 | High | Medium | High | 80 | 102 | 7.9678
MAPLE CREEK-HOOPA - 60 kV | ETL.7490 | HUMBOLDT | 302 | 0 | 0 | 0% | 86.69% | 0% | 0 | 0% | 12.23% | 1 | 0.89043 | 23.6929 | 0.86821 | 18.3166 | High | High | Low | 81 | 25 | 21.0969
MORRO BAY-SOLAR SW STA #1 - 230 kV | ETL.5300 | LOS PADRES | 162 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.4843 | 22.7322 | 1.6471 | 18.1336 | High | High | Medium | 82 | 81 | 11.0091
ORO FINO TAP - 60 kV | ETL.6721 | NORTH VALLEY | 21 | 0 | 0 | 0% | 57.14% | 0% | 0 | 0% | 0% | 0 | 0.070214 | 98.1657 | 2.6165 | 18.0342 | Low | High | High | 83 | 116 | 6.8926
GREEN VALLEY-PAUL SWEET - 115 kV | ETL.1730 | CENTRAL COAST | 89 | 0 | 0 | 3.529% | 1.176% | 1.176% | 0 | 0% | 34.12% | 0 | 0.36819 | 18.5437 | 2.583 | 17.6358 | Medium | High | High | 84 | 118 | 6.8276
PARKWAY-MORAGA - 230 kV | ETL.5930 | DIABLO | 93 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.23696 | 26.2836 | 2.8197 | 17.5612 | Medium | High | High | 85 | 131 | 6.228
PITTSBURG-SAN MATEO - 230 kV | ETL.5463 | MISSION | 75 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.17334 | 36.8125 | 2.7367 | 17.4633 | Medium | High | High | 86 | 126 | 6.3812
FULTON-IGNACIO #1 - 230 kV | ETL.4680 | SONOMA | 103 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.25011 | 38.2444 | 1.778 | 17.0066 | Medium | High | Medium | 87 | 89 | 9.5651
CHRISTIE-SOBRANTE - 115 kV | ETL.1260 | DIABLO | 48 | 1 | 0 | 0% | 0% | 0% | 0 | 60.31% | 100% | 0 | 0.46455 | 13.2892 | 2.7172 | 16.7744 | High | Medium | High | 88 | 132 | 6.1734
CONTRA COSTA-MORAGA #1 - 230 kV | ETL.5452 | DIABLO | 84 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.18381 | 31.9897 | 2.8304 | 16.6433 | Medium | High | High | 89 | 139 | 5.8802
VALLEY SPRINGS #1 - 60 kV | ETL.8210 | STOCKTON | 258 | 0 | 0 | 1.456% | 87.86% | 0% | 10 | 63.45% | 3.865% | 1 | 0.8768 | 7.5551 | 2.4628 | 16.3145 | High | Medium | High | 90 | 121 | 6.6243
ATASCADERO-SAN LUIS OBISPO - 70 kV | ETL.8490 | LOS PADRES | 135 | 0 | 0 | 0.9174% | 55.05% | 0% | 0 | 0% | 100% | 0 | 0.52956 | 18.5 | 1.644 | 16.1058 | High | High | Medium | 91 | 88 | 9.7969
SAN LUIS OBISPO-CAYUCOS - 70 kV | ETL.9090 | LOS PADRES | 114 | 5 | 0 | 0% | 6.604% | 15.09% | 0 | 0% | 0.9434% | 0 | 0.54085 | 13.1078 | 2.2712 | 16.101 | High | Medium | High | 92 | 114 | 7.0894
MORAGA-SAN LEANDRO #1 - 115 kV | ETL.2770 | MISSION | 65 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.16093 | 37.37 | 2.6685 | 16.0479 | Medium | High | High | 93 | 135 | 6.0138
SAN RAMON-MORAGA - 230 kV | ETL.5660 | MISSION | 24 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.084467 | 65.076 | 2.8801 | 15.8316 | Low | High | High | 94 | 144 | 5.4968
MORAGA-SAN LEANDRO #3 - 115 kV | ETL.2790 | MISSION | 67 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15853 | 37.1227 | 2.6749 | 15.7419 | Medium | High | High | 95 | 138 | 5.8851
GREEN VALLEY-CAMP EVERS - 115 kV | ETL.1710 | CENTRAL COAST | 110 | 0 | 0 | 0% | 1.961% | 0% | 0 | 0% | 22.55% | 0 | 0.30512 | 19.6234 | 2.5987 | 15.5596 | Medium | High | High | 96 | 136 | 5.9876
COTTONWOOD-RED BLUFF-60 kV | ETL.6660 | NORTH VALLEY | 231 | 0 | 0 | 2.752% | 89.91% | 0% | 0 | 32.99% | 11.01% | 0 | 0.87152 | 11.547 | 1.5085 | 15.1802 | High | Medium | Medium | 97 | 87 | 10.0634
METCALF-GREEN VALLEY - 115 kV | ETL.2540 | SAN JOSE | 93 | 0 | 0 | 2.439% | 7.317% | 0% | 14.85 | 59% | 35.37% | 0 | 0.51905 | 15.9312 | 1.7851 | 14.7613 | High | Medium | Medium | 98 | 99 | 8.2691
MISSOURI FLAT-GOLD HILL #1 - 115 kV | ETL.2660 | SIERRA | 74 | 0 | 0 | 1.493% | 0% | 0% | 0 | 0% | 100% | 1 | 0.24614 | 27.0187 | 2.2195 | 14.7608 | Medium | High | High | 99 | 120 | 6.6505
ROSSMOOR #2 TAP - 230 kV | ETL.5461 | DIABLO | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 85.4511 | 2.9397 | 14.732 | Low | High | High | 100 | 153 | 5.0113
DIABLO-GATES #1 - 500 kV | ETL.5960 | LOS PADRES | 149 | 23 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.54511 | 12.0892 | 2.2246 | 14.6603 | High | Medium | High | 101 | 123 | 6.59
STANISLAUS-MANTECA #2 - 115 kV | ETL.3820 | STOCKTON | 163 | 1 | 0 | 0% | 0% | 0% | 0 | 66.59% | 100% | 1 | 0.83915 | 8.1034 | 2.1426 | 14.5694 | High | Medium | High | 102 | 119 | 6.8
GEYSERS #3-CLOVERDALE - 115 kV | ETL.1650 | SONOMA | 137 | 1 | 0 | 2.273% | 12.88% | 27.27% | 0 | 0% | 25.76% | 1 | 0.71774 | 18.344 | 1.0961 | 14.4312 | High | Medium | Low | 103 | 59 | 13.1662
DEL MONTE-FORT ORD #1 - 60 kV | ETL.8400 | CENTRAL COAST | 4 | 4 | 0 | 0% | 0% | 0% | 0 | 67.27% | 100% | 1 | 0.29486 | 14.9507 | 3.2599 | 14.3705 | Medium | Medium | High | 104 | 166 | 4.4083
SOBRANTE-MORAGA - 115 kV | ETL.3742 | DIABLO | 27 | 0 | 0 | 11.54% | 0% | 0% | 0 | 53.12% | 76.92% | 0 | 0.23288 | 20.9352 | 2.9376 | 14.322 | Medium | High | High | 105 | 155 | 4.8755
FULTON-HOPLAND - 60 kV | ETL.6890 | SONOMA | 423 | 0 | 0 | 5.729% | 71.88% | 0% | 0 | 0.1792% | 5.729% | 1 | 0.98005 | 11.7783 | 1.2205 | 14.0891 | High | Medium | Low | 106 | 75 | 11.5434
ROSSMOOR #1 TAP - 230 kV | ETL.5451 | DIABLO | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 78.7645 | 2.9473 | 14.0787 | Low | High | High | 107 | 159 | 4.7769
MENDOCINO-HARTLEY - 60 kV | ETL.7510 | HUMBOLDT | 203 | 1 | 0 | 0.5128% | 43.59% | 0% | 0 | 0% | 16.41% | 1 | 0.81995 | 14.4552 | 1.1845 | 14.0398 | High | Medium | Low | 108 | 74 | 11.8525
SALT SPRINGS-TIGER CREEK - 115 kV | ETL.3500 | STOCKTON | 129 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 100% | 1 | 0.74544 | 10.8896 | 1.727 | 14.0189 | High | Medium | Medium | 109 | 100 | 8.1176
SAN LUIS OBISPO-SANTA MARIA *-70 kV | ETL.9100 | LOS PADRES | 159 | 0 | 0 | 6.299% | 74.8% | 9.449% | 0 | 0% | 0% | 0 | 0.53973 | 13.5383 | 1.9157 | 13.998 | High | Medium | Medium | 110 | 110 | 7.307
STANISLAUS-MELONES SW STA-MANTECA #1 - 115 kV | ETL.3830 | STOCKTON | 214 | 2 | 0 | 0% | 0% | 0% | 0 | 63.66% | 100% | 1 | 0.92889 | 7.1298 | 2.0949 | 13.8739 | High | Medium | Medium | 111 | 122 | 6.6228
MELONES-RACETRACK - 115 kV | ETL.2400 | YOSEMITE | 164 | 0 | 0 | 1.829% | 52.44% | 0% | 0 | 0% | 16.46% | 0 | 0.54953 | 13.1733 | 1.914 | 13.8556 | High | Medium | Medium | 112 | 112 | 7.2391
MADISON-VACA - 115 kV | ETL.2170 | SACRAMENTO | 28 | 0 | 0 | 0% | 0% | 0% | 15.73 | 68.19% | 90% | 0 | 0.1909 | 47.2462 | 1.5325 | 13.8215 | Medium | High | Medium | 113 | 96 | 9.0192
VALLEY SPRINGS-MARTELL #1 - 60 kV | ETL.8240 | STOCKTON | 147 | 0 | 0 | 2.381% | 79.37% | 0% | 0 | 81.13% | 22.22% | 1 | 0.75213 | 8.6642 | 2.12 | 13.8154 | High | Medium | Medium | 114 | 125 | 6.5166
COTTONWOOD-BENTON #1 - 60 kV | ETL.6640 | NORTH VALLEY | 153 | 0 | 0 | 1.653% | 87.6% | 0% | 0 | 44.61% | 10.74% | 0 | 0.55031 | 14.1226 | 1.7764 | 13.8063 | High | Medium | Medium | 115 | 105 | 7.7719
CASTRO VALLEY-NEWARK - 230 kV | ETL.4450 | MISSION | 58 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.13826 | 38.3261 | 2.5251 | 13.3801 | Medium | High | High | 116 | 149 | 5.2989
LAYTONVILLE-WILLITS - 60 kV | ETL.8360 | HUMBOLDT | 168 | 0 | 0 | 0% | 29.33% | 0% | 0 | 0% | 30.67% | 1 | 0.46288 | 26.4063 | 1.0804 | 13.2053 | High | High | Low | 117 | 70 | 12.2229
ROUND MTN-TABLE MTN #2 - 500 kV | ETL.6070 | NORTH VALLEY | 336 | 0 | 3 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.94958 | 8.7331 | 1.5887 | 13.1748 | High | Medium | Medium | 118 | 98 | 8.2928
FULTON-LAKEVILLE - 230 kV | ETL.4950 | SONOMA | 65 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15383 | 48.1674 | 1.7767 | 13.1643 | Medium | High | Medium | 119 | 107 | 7.4094
COLGATE-PALERMO - 60 kV | ETL.6500 | SIERRA | 450 | 0 | 0 | 2.294% | 75.69% | 0% | 0 | 91.72% | 12.39% | 1 | 0.99844 | 5.7267 | 2.2868 | 13.075 | High | Medium | High | 120 | 141 | 5.7177
SNEATH LANE-PACIFICA - 60 kV | ETL.7575 | PENINSULA | 26 | 0 | 0 | 26.09% | 30.43% | 0% | 0 | 0% | 8.696% | 1 | 0.13491 | 37.4097 | 2.5649 | 12.9451 | Medium | High | High | 121 | 152 | 5.0471
SLY CREEK TAP-115 kV | ETL.4221 | NORTH VALLEY | 67 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 40.3% | 0 | 0.1146 | 81.3433 | 1.3796 | 12.8608 | Low | High | Low | 122 | 92 | 9.3222
MORRO BAY-TEMPLETON - 230 kV | ETL.5933 | LOS PADRES | 41 | 1 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.2171 | 33.8305 | 1.7446 | 12.8136 | Medium | High | Medium | 123 | 109 | 7.3447
SOBRANTE-G #1 - 115 kV | ETL.3720 | DIABLO | 39 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.10933 | 32.8223 | 3.5139 | 12.6099 | Low | High | High | 124 | 189 | 3.5886
LAKEVILLE #1 - 60 kV | ETL.7360 | SONOMA | 92 | 0 | 0 | 1.205% | 55.42% | 0% | 0 | 0% | 6.024% | 0 | 0.20998 | 29.3876 | 2.0086 | 12.3942 | Medium | High | Medium | 125 | 133 | 6.1707
TULE-SPRINGVILLE - 70 kV | ETL.9040 | FRESNO | 250 | 0 | 0 | 6.8% | 83.6% | 0% | 0 | 97.54% | 11.6% | 0 | 0.96576 | 6.5337 | 1.9522 | 12.3185 | High | Medium | Medium | 126 | 129 | 6.3101
COTTONWOOD-BENTON #2-60 kV | ETL.6650 | NORTH VALLEY | 119 | 0 | 0 | 0% | 0% | 0% | 0 | 33.59% | 20.91% | 0 | 0.28981 | 23.7227 | 1.753 | 12.0518 | Medium | High | Medium | 127 | 117 | 6.8751
LAYTONVILLE-COVELO-60 kV | ETL.7390 | HUMBOLDT | 156 | 0 | 0 | 0% | 39.56% | 0% | 0 | 0% | 17.58% | 1 | 0.23104 | 56.1906 | 0.92584 | 12.0195 | Medium | High | Low | 128 | 60 | 12.9823
BRUNSWICK #1 TAP - 115 kV | ETL.1422 | SIERRA | 49 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.12211 | 50.5163 | 1.9411 | 11.9732 | Medium | High | Medium | 129 | 134 | 6.1684
ROUND MTN-TABLE MTN #1 - 500 kV | ETL.6060 | NORTH VALLEY | 317 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.94229 | 8.2624 | 1.5197 | 11.8321 | High | Medium | Medium | 130 | 104 | 7.7856
MONTA VISTA-JEFFERSON #1 - 230 kV | ETL.5220 | DE ANZA | 78 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.18651 | 21.606 | 2.8977 | 11.6767 | Medium | High | High | 131 | 180 | 4.0297
SMARTVILLE-CAMP FAR WEST (12KV)-60 kV | ETL.7970 | SIERRA | 202 | 0 | 0 | 0.5882% | 90.59% | 0% | 12.92 | 72.87% | 1.176% | 0 | 0.80957 | 8.8778 | 1.6099 | 11.5703 | High | Medium | Medium | 132 | 113 | 7.1871
CARIBOU-TABLE MTN - 230 kV | ETL.4440 | NORTH VALLEY | 364 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 99.73% | 1 | 0.9759 | 5.8371 | 2.028 | 11.5526 | High | Medium | Medium | 133 | 143 | 5.6964
MENDOCINO-WILLITS-60 kV | ETL.7540 | HUMBOLDT | 137 | 0 | 0 | 0% | 68.25% | 0% | 0 | 100% | 15.08% | 0 | 0.70514 | 15.3023 | 1.0505 | 11.3354 | High | Medium | Low | 134 | 83 | 10.7903
TIDEWATER-SOBRANTE - 230 kV | ETL.5770 | DIABLO | 29 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.09163 | 44.2993 | 2.7623 | 11.2123 | Low | High | High | 135 | 179 | 4.0591
VACA-PARKWAY - 230 kV | ETL.5850 | SACRAMENTO | 78 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.1708 | 33.4455 | 1.9396 | 11.0802 | Medium | High | Medium | 136 | 142 | 5.7125
POTTER VALLEY-WILLITS - 60 kV | ETL.7820 | HUMBOLDT | 128 | 0 | 0 | 0% | 61.11% | 0% | 0 | 0% | 7.937% | 1 | 0.32143 | 35.8966 | 0.92196 | 10.6377 | Medium | High | Low | 137 | 76 | 11.5382
PINE GROVE TAP - 60 kV | ETL.8351 | STOCKTON | 61 | 0 | 0 | 1.639% | 36.07% | 0% | 0 | 0% | 0% | 0 | 0.14644 | 28.6948 | 2.4978 | 10.4957 | Medium | High | High | 138 | 176 | 4.202
SONOMA-PUEBLO-115 kV | ETL.3810 | SONOMA | 59 | 0 | 0 | 7.692% | 71.79% | 0% | 0 | 0% | 12.82% | 0 | 0.17628 | 42.8745 | 1.3815 | 10.4412 | Medium | High | Low | 139 | 106 | 7.558
BURNS-LONE STAR #1 - 60 kV | ETL.6230 | CENTRAL COAST | 76 | 0 | 0 | 0% | 64.47% | 0% | 5.3 | 94.31% | 10.53% | 1 | 0.44686 | 8.2597 | 2.8196 | 10.4072 | High | Medium | High | 140 | 186 | 3.691
KILARC-DESCHUTES - 60 kV | ETL.7300 | NORTH VALLEY | 511 | 0 | 0 | 1.042% | 90.83% | 0% | 0 | 0% | 3.125% | 1 | 0.99679 | 6.265 | 1.6316 | 10.1894 | High | Medium | Medium | 141 | 130 | 6.2449
MTN GATE JCT-CASCADE - 60 kV | ETL.7640 | NORTH VALLEY | 79 | 0 | 0 | 0% | 49.37% | 0% | 0 | 56.22% | 2.532% | 0 | 0.32162 | 15.7763 | 1.9995 | 10.1454 | Medium | Medium | Medium | 142 | 151 | 5.074
ROCK CREEK-POE - 230 kV | ETL.5630 | NORTH VALLEY | 210 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 97.14% | 1 | 0.71771 | 7.6521 | 1.8212 | 10.0023 | High | Medium | Medium | 143 | 145 | 5.492
CORDELIA #2 TAP - 60 kV | ETL.8184 | SACRAMENTO | 68 | 0 | 0 | 5.769% | 76.92% | 0% | 0 | 94.91% | 9.615% | 0 | 0.47767 | 9.2746 | 2.2539 | 9.9853 | High | Medium | High | 144 | 165 | 4.4302
MENDOCINO-WILLITS-FORT BRAGG - 60 kV | ETL.7550 | HUMBOLDT | 464 | 0 | 0 | 0.2242% | 49.1% | 0% | 0 | 0.2473% | 8.744% | 1 | 0.99389 | 8.0077 | 1.2514 | 9.9595 | High | Medium | Low | 145 | 103 | 7.9588
STANISLAUS-NEWARK #2 (12KV)-115 kV | ETL.3860 | MISSION | 10 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 100% | 0 | 0.23929 | 24.3184 | 1.6895 | 9.8315 | Medium | High | Medium | 146 | 140 | 5.819
LOS ESTEROS-METCALF - 230 kV | ETL.5353 | SAN JOSE | 105 | 1 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.48277 | 14.6793 | 1.3743 | 9.7392 | High | Medium | Low | 147 | 115 | 7.0868
HAMILTON BRANCH-CHESTER-60 kV | ETL.7000 | NORTH VALLEY | 211 | 0 | 0 | 3.846% | 75% | 0% | 0 | 18.59% | 3.365% | 1 | 0.78454 | 5.7331 | 2.1502 | 9.6713 | High | Medium | High | 148 | 164 | 4.4978
MOSS LANDING-METCALF - 500 kV | ETL.6050 | CENTRAL COAST | 95 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.22429 | 24.359 | 1.7645 | 9.6403 | Medium | High | Medium | 149 | 146 | 5.4635
DRUM-SUMMIT #2 - 115 kV | ETL.1450 | SIERRA | 369 | 0 | 0 | 0.2786% | 0% | 0% | 0 | 0% | 10.03% | 1 | 0.96007 | 14.0077 | 0.70775 | 9.5181 | High | Medium | Low | 150 | 57 | 13.4484
PALERMO-OROVILLE #1 - 60 kV | ETL.7730 | NORTH VALLEY | 34 | 0 | 0 | 0% | 91.67% | 0% | 0 | 71.28% | 0% | 0 | 0.36861 | 10.3019 | 2.4926 | 9.4654 | Medium | Medium | High | 151 | 184 | 3.7974
CENTERVILLE-TABLE MTN-OROVILLE - 60 kV | ETL.6330 | NORTH VALLEY | 250 | 0 | 0 | 1.471% | 76.47% | 0% | 0 | 5.701% | 20.1% | 1 | 0.71968 | 5.0692 | 2.57 | 9.3759 | High | Medium | High | 152 | 188 | 3.6482
POTTER VALLEY-MENDOCINO - 60 kV | ETL.7810 | HUMBOLDT | 70 | 0 | 0 | 4.918% | 14.75% | 0% | 8.83 | 80.27% | 67.21% | 1 | 0.56781 | 16.4832 | 0.985 | 9.219 | High | Medium | Low | 153 | 91 | 9.3593
LAKEWOOD-MEADOW LANE-CLAYTON - 115 kV | ETL.2080 | DIABLO | 11 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.064845 | 51.7285 | 2.7428 | 9.2003 | Low | High | High | 154 | 194 | 3.3543
DRUM-SPAULDING-60 kV | ETL.6770 | SIERRA | 240 | 0 | 0 | 1.25% | 80.42% | 0% | 0 | 0.1479% | 6.667% | 1 | 0.81522 | 31.1007 | 0.35929 | 9.1093 | High | High | Low | 155 | 16 | 25.3538
PLACER-GOLD HILL #1 - 115 kV | ETL.3340 | SIERRA | 73 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.16093 | 24.9379 | 2.2668 | 9.0971 | Medium | High | High | 156 | 181 | 4.0132
CLEAR LAKE-HOPLAND - 60 kV | ETL.6390 | HUMBOLDT | 99 | 0 | 0 | 0% | 37.5% | 0% | 0 | 0% | 19.32% | 0 | 0.22391 | 28.1878 | 1.4179 | 8.9494 | Medium | High | Low | 157 | 128 | 6.3116
MELONES-CURTIS - 115 kV | ETL.2390 | YOSEMITE | 135 | 0 | 0 | 0% | 2.256% | 0% | 0 | 0% | 6.767% | 0 | 0.36964 | 11.599 | 2.0786 | 8.912 | Medium | Medium | Medium | 158 | 172 | 4.2875
GARBERVILLE-LAYTONVILLE - 60 kV | ETL.8365 | HUMBOLDT | 209 | 0 | 0 | 0% | 32.29% | 0% | 0 | 0% | 23.96% | 1 | 0.25626 | 31.1751 | 1.099 | 8.7796 | Medium | High | Low | 159 | 101 | 7.989
SAN LUIS OBISPO-OCEANO - 115 kV | ETL.3530 | LOS PADRES | 108 | 0 | 0 | 3.659% | 4.878% | 0% | 0 | 0% | 52.44% | 0 | 0.26981 | 16.2584 | 1.9633 | 8.6122 | Medium | Medium | Medium | 160 | 169 | 4.3867
MORRO BAY-SAN LUIS OBISPO #1 - 115 kV | ETL.2810 | LOS PADRES | 75 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15853 | 22.3563 | 2.424 | 8.5911 | Medium | High | High | 161 | 191 | 3.5442
PLACER-DEL MAR - 60 kV | ETL.7800 | SIERRA | 113 | 0 | 0 | 0% | 86.96% | 0% | 0 | 0% | 13.04% | 0 | 0.2549 | 15.3025 | 2.1065 | 8.2166 | Medium | Medium | Medium | 162 | 182 | 3.9007
APPLE HILL #2 TAP - 115 kV | ETL.1541 | SIERRA | 36 | 0 | 0 | 0% | 69.44% | 0% | 0 | 0% | 11.11% | 0 | 0.11041 | 41.1042 | 1.8034 | 8.1842 | Low | High | Medium | 163 | 163 | 4.5381
METCALF-MOSS LANDING #1 - 230 kV | ETL.5100 | CENTRAL COAST | 71 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.1708 | 25.5515 | 1.8421 | 8.0395 | Medium | High | Medium | 164 | 170 | 4.3642
CRAG VIEW-CASCADE - 115 kV | ETL.1350 | NORTH VALLEY | 189 | 2 | 0 | 0.5348% | 0% | 0% | 0 | 100% | 20.86% | 1 | 0.93996 | 5.1187 | 1.6538 | 7.9571 | High | Medium | Medium | 165 | 158 | 4.8114
DIVIDE-CABRILLO #1 - 115 kV | ETL.1380 | LOS PADRES | 94 | 2 | 0 | 0% | 0% | 0% | 0 | 0% | 7.692% | 1 | 0.22416 | 12.3046 | 2.8685 | 7.9118 | Medium | Medium | High | 166 | 209 | 2.7582
DRUM-SUMMIT #1 - 115 kV | ETL.1440 | SIERRA | 342 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 24.62% | 1 | 0.92005 | 13.9593 | 0.6087 | 7.8177 | High | Medium | Low | 167 | 61 | 12.8433
ELECTRA-BELLOTA - 230 kV | ETL.4670 | STOCKTON | 103 | 0 | 0 | 0% | 0% | 0% | 0 | 54.25% | 100% | 0 | 0.425 | 7.8762 | 2.2355 | 7.4831 | High | Medium | High | 168 | 195 | 3.3474
PITTSBURG-SAN RAMON - 230 kV | ETL.5490 | MISSION | 58 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.14257 | 19.8618 | 2.5983 | 7.3574 | Medium | High | High | 169 | 207 | 2.8316
MORAGA-CASTRO VALLEY - 230 kV | ETL.5250 | MISSION | 58 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.12403 | 20.8469 | 2.837 | 7.3356 | Medium | High | High | 170 | 214 | 2.5857
AUBERRY TAP - 70 kV | ETL.9331 | FRESNO | 38 | 0 | 0 | 0% | 78.95% | 0% | 0 | 0% | 76.32% | 0 | 0.15331 | 22.9945 | 2.0626 | 7.2709 | Medium | High | Medium | 171 | 192 | 3.5252
CRESTA-RIO OSO-230 kV | ETL.4590 | NORTH VALLEY | 150 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.47094 | 6.7598 | 2.2643 | 7.2084 | High | Medium | High | 172 | 197 | 3.1834
WASHOE TAP - 60 kV | ETL.6911 | SONOMA | 20 | 0 | 0 | 0% | 85% | 0% | 0 | 0% | 5% | 0 | 0.10205 | 48.0744 | 1.4685 | 7.2044 | Low | High | Low | 173 | 154 | 4.9058
WINDSOR-FITCH MOUNTAIN-60 kV | ETL.6900 | SONOMA | 23 | 0 | 0 | 21.43% | 64.29% | 0% | 0 | 87.17% | 7.143% | 0 | 0.33946 | 19.2589 | 1.1 | 7.1911 | Medium | High | Low | 174 | 124 | 6.5375
COLEMAN-RED BLUFF - 60 kV | ETL.6440 | NORTH VALLEY | 322 | 0 | 0 | 0.9615% | 83.33% | 0% | 0 | 77.46% | 6.731% | 1 | 0.97754 | 4.9413 | 1.4686 | 7.0936 | High | Medium | Low | 175 | 157 | 4.8303
PIT #1-COTTONWOOD - 230 kV | ETL.5390 | NORTH VALLEY | 481 | 12 | 1 | 0% | 0% | 0% | 0 | 53.22% | 99.77% | 1 | 0.9989 | 5.4111 | 1.2916 | 6.9812 | High | Medium | Low | 176 | 148 | 5.4051
APPLE HILL #1 TAP - 115 kV | ETL.1531 | SIERRA | 33 | 0 | 0 | 3.03% | 72.73% | 0% | 0 | 0% | 18.18% | 0 | 0.11801 | 32.5892 | 1.7777 | 6.8366 | Medium | High | Medium | 177 | 183 | 3.8457
VOLTA-SOUTH - 60 kV | ETL.8300 | NORTH VALLEY | 106 | 0 | 0 | 0% | 93.4% | 0% | 0 | 100% | 2.83% | 0 | 0.66072 | 8.1846 | 1.2482 | 6.7501 | High | Medium | Low | 178 | 147 | 5.4077
GEYSERS #12-FULTON - 230 kV | ETL.4750 | SONOMA | 104 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.26028 | 16.9231 | 1.5237 | 6.7114 | Medium | Medium | Medium | 179 | 167 | 4.4048
SOBRANTE-G #2 | ETL.3730 | DIABLO | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.061672 | 35.3263 | 2.9751 | 6.4816 | Low | High | High | 180 | 225 | 2.1787
COTTONWOOD-DELEVAN #2 - 230 kV | ETL.4580 | NORTH VALLEY | 115 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.16093 | 26.2598 | 1.5215 | 6.4296 | Medium | High | Medium | 181 | 174 | 4.2259
COTTONWOOD-DELEVAN #1 - 230 kV | ETL.4550 | NORTH VALLEY | 115 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15853 | 26.6607 | 1.5208 | 6.4276 | Medium | High | Medium | 182 | 173 | 4.2265
HUMBOLDT BAY-HUMBOLDT #1 - 115 kV | ETL.1800 | HUMBOLDT | 15 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.071649 | 27.4389 | 3.2495 | 6.3884 | Low | High | High | 183 | 236 | 1.966
POE-RIO OSO - 230 kV | ETL.5540 | NORTH VALLEY | 136 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.35066 | 7.7264 | 2.3308 | 6.3149 | Medium | Medium | High | 184 | 211 | 2.7093
VALLEY SPRINGS-CLAY - 60 kV | ETL.8264 | STOCKTON | 181 | 0 | 0 | 3.974% | 51.66% | 0% | 0 | 0% | 27.81% | 1 | 0.51292 | 5.7271 | 2.1466 | 6.3057 | High | Medium | High | 185 | 200 | 2.9376
NORTH DUBLIN-CAYETANO - 230 kV | ETL.4500 | MISSION | 13 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.071649 | 34.2648 | 2.5406 | 6.2373 | Low | High | High | 186 | 220 | 2.455
ROUND MTN-COTTONWOOD #3 - 230 kV | ETL.5650 | NORTH VALLEY | 262 | 0 | 0 | 0% | 0% | 0% | 0 | 94.71% | 100% | 1 | 0.95896 | 4.4821 | 1.4455 | 6.2128 | High | Medium | Low | 187 | 171 | 4.2982
TEMPLETON-ATASCADERO - 70 kV | ETL.9410 | LOS PADRES | 92 | 0 | 0 | 0% | 82.76% | 0% | 0 | 0% | 0% | 0 | 0.22106 | 13.2748 | 2.0918 | 6.1384 | Medium | Medium | Medium | 188 | 201 | 2.9346
SANTA ROSA-CORONA - 115 kV | ETL.4309 | SONOMA | 31 | 0 | 17 | 0% | 86.96% | 0% | 0 | 0% | 0% | 0 | 0.10353 | 33.253 | 1.7528 | 6.0348 | Low | High | Medium | 189 | 193 | 3.4428
FRUITLAND TAP - 60 kV | ETL.6221 | HUMBOLDT | 55 | 1 | 0 | 0% | 36.73% | 0% | 0 | 0% | 8.163% | 0 | 0.23651 | 31.1256 | 0.80932 | 5.9577 | Medium | High | Low | 190 | 108 | 7.3614
IGNACIO-SOBRANTE - 230 kV | ETL.4920 | DIABLO | 73 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15853 | 13.3276 | 2.7472 | 5.8044 | Medium | Medium | High | 191 | 228 | 2.1128
UKIAH-HOPLAND-CLOVERDALE - 115 kV | ETL.4050 | SONOMA | 221 | 0 | 0 | 62.98% | 8.654% | 0% | 0 | 0% | 20.67% | 1 | 0.73412 | 8.1275 | 0.95966 | 5.7258 | High | Medium | Low | 192 | 137 | 5.9665
KERCKHOFF-CLOVIS-SANGER #1 - 115 kV | ETL.1890 | FRESNO | 74 | 3 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.24564 | 19.8199 | 1.1657 | 5.6753 | Medium | High | Low | 193 | 156 | 4.8686
NEWARK-LIVERMORE - 60 kV | ETL.7660 | MISSION | 60 | 0 | 0 | 0% | 23.53% | 0% | 15.04 | 92.93% | 61.76% | 0 | 0.42836 | 6.6688 | 1.9573 | 5.5914 | High | Medium | Medium | 194 | 206 | 2.8567
FULTON-MOLINO-COTATI-60 kV | ETL.6910 | SONOMA | 37 | 0 | 0 | 2.941% | 85.29% | 0% | 0 | 0% | 2.941% | 1 | 0.15382 | 24.5452 | 1.4744 | 5.5669 | Medium | High | Medium | 195 | 185 | 3.7756
BAHIA-MORAGA - 230 kV | ETL.4340 | EAST BAY | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 33.1956 | 2.7655 | 5.475 | Low | High | High | 196 | 235 | 1.9797
NEWARK-JARVIS #1 - 115 kV | ETL.3020 | MISSION | 15 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.062713 | 39.6873 | 2.1568 | 5.368 | Low | High | High | 197 | 219 | 2.4889
HIGGINS-BELL - 115 kV | ETL.1412 | SIERRA | 60 | 0 | 0 | 0% | 0% | 0% | 8.3 | 79.27% | 100% | 0 | 0.3569 | 8.0509 | 1.86 | 5.3444 | Medium | Medium | Medium | 198 | 205 | 2.8734
BRICEBURG JCT-MARIPOSA TAP-70 kV | ETL.8651 | YOSEMITE | 159 | 0 | 0 | 0% | 76.1% | 0% | 0 | 0% | 3.145% | 0 | 0.51228 | 7.9535 | 1.3046 | 5.3157 | High | Medium | Low | 199 | 178 | 4.0745
VIEJO-MONTEREY - 60 kV | ETL.8270 | CENTRAL COAST | 18 | 0 | 0 | 14.29% | 64.29% | 0% | 0 | 0% | 0% | 1 | 0.15694 | 13.2834 | 2.5329 | 5.2804 | Medium | Medium | High | 200 | 230 | 2.0847
VALLEY SPRINGS-CALAVERAS CEMENT - 60 kV | ETL.8220 | STOCKTON | 97 | 0 | 0 | 0% | 67.02% | 0% | 0 | 0% | 0% | 0 | 0.21747 | 11.5528 | 2.0852 | 5.2388 | Medium | Medium | Medium | 201 | 217 | 2.5124
MENDOCINO-PHILO JCT-HOPLAND - 60 kV | ETL.7520 | HUMBOLDT | 207 | 0 | 0 | 2.618% | 71.73% | 0% | 21.34 | 90.54% | 12.57% | 1 | 0.8716 | 5.9217 | 1.0001 | 5.1617 | High | Medium | Low | 202 | 150 | 5.1614
HALSEY-PLACER - 60 kV | ETL.6990 | SIERRA | 50 | 1 | 0 | 0% | 76.47% | 0% | 0 | 0% | 2.941% | 0 | 0.2087 | 11.571 | 2.0612 | 4.9774 | Medium | Medium | Medium | 203 | 221 | 2.4148
CAMP EVERS-PAUL SWEET-115 kV | ETL.1220 | CENTRAL COAST | 2 | 0 | 0 | 50% | 0% | 0% | 0 | 0% | 50% | 0 | 0.10201 | 18.1631 | 2.6683 | 4.9439 | Low | Medium | High | 204 | 240 | 1.8528
PIT #1-HAT CREEK #2-BURNEY - 60 kV | ETL.7040 | NORTH VALLEY | 156 | 0 | 0 | 4.605% | 70.39% | 0% | 3.44 | 25.75% | 1.974% | 1 | 0.59732 | 7.8133 | 1.0522 | 4.9108 | High | Medium | Low | 205 | 162 | 4.667
MORRO BAY-SAN LUIS OBISPO #2 - 115 kV | ETL.2820 | LOS PADRES | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 35.3263 | 2.3373 | 4.8423 | Low | High | High | 206 | 231 | 2.0717
SOBRANTE-STANDARD OIL SW STA #1 - 115 kV | ETL.3800 | DIABLO | 53 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 98% | 0 | 0.12829 | 12.9722 | 2.8218 | 4.6959 | Medium | Medium | High | 207 | 248 | 1.6642
CALLENDER SW STA-MESA-115 kV | ETL.1210 | LOS PADRES | 66 | 1 | 0 | 30.23% | 0% | 0% | 0 | 0% | 55.81% | 1 | 0.26354 | 11.4832 | 1.5456 | 4.6773 | Medium | Medium | Medium | 208 | 199 | 3.0263
LAKEVILLE-SONOMA #1 - 115 kV | ETL.2063 | SONOMA | 32 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.085858 | 33.9799 | 1.5569 | 4.5422 | Low | High | Medium | 209 | 202 | 2.9174
CLEAR LAKE-KONOCTI-60 kV | ETL.6852 | HUMBOLDT | 52 | 0 | 0 | 0% | 50% | 0% | 0 | 0% | 16.67% | 1 | 0.11164 | 18.0084 | 2.2425 | 4.5085 | Low | Medium | High | 210 | 234 | 2.0105
WISHON-SAN JOAQUIN #3 - 70 kV | ETL.9340 | YOSEMITE | 116 | 0 | 0 | 0% | 83.62% | 0% | 0 | 100% | 43.1% | 1 | 0.71159 | 5.043 | 1.2458 | 4.4705 | High | Medium | Low | 211 | 190 | 3.5886
PEORIA TAP - 115 kV | ETL.2391 | YOSEMITE | 11 | 0 | 0 | 0% | 72.73% | 0% | 0 | 0% | 0% | 0 | 0.085275 | 30.24 | 1.6368 | 4.2207 | Low | High | Medium | 212 | 215 | 2.5787
COTTONWOOD-LOGAN CREEK - 230 kV | ETL.4570 | NORTH VALLEY | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 47.6367 | 1.4961 | 4.1797 | Low | High | Medium | 213 | 208 | 2.7937
SALINAS-FORT ORD #2 - 60 kV | ETL.8423 | CENTRAL COAST | 46 | 6 | 0 | 0% | 0% | 0% | 0 | 99.4% | 100% | 1 | 0.55922 | 3.8242 | 1.9307 | 4.1289 | High | Medium | Medium | 214 | 226 | 2.1386
MENDOCINO-UKIAH - 115 kV | ETL.2420 | HUMBOLDT | 66 | 0 | 0 | 31.03% | 12.07% | 0% | 0 | 0% | 55.17% | 0 | 0.21612 | 15.4176 | 1.2364 | 4.1197 | Medium | Medium | Low | 215 | 196 | 3.332
LAKEVILLE-IGNACIO #2 - 230 kV | ETL.3745 | NORTH BAY | 19 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 23.8842 | 2.8386 | 4.1118 | Low | High | High | 216 | 265 | 1.4485
PARADISE-BUTTE - 115 kV | ETL.4396 | NORTH VALLEY | 98 | 0 | 0 | 2.247% | 11.24% | 0% | 0 | 0% | 100% | 0 | 0.44063 | 3.5439 | 2.6142 | 4.0823 | High | Medium | High | 217 | 257 | 1.5616
DUNLAP TAP - 70 kV | ETL.9061 | FRESNO | 131 | 1 | 0 | 0.7812% | 61.72% | 0% | 0 | 0% | 39.06% | 0 | 0.62003 | 4.9797 | 1.2753 | 3.9376 | High | Medium | Low | 218 | 198 | 3.0876
DEL MONTE-VIEJO - 60 kV | ETL.6710 | CENTRAL COAST | 130 | 0 | 0 | 11.76% | 68.07% | 0% | 0 | 0% | 3.361% | 1 | 0.45397 | 3.5892 | 2.4052 | 3.919 | High | Medium | High | 219 | 250 | 1.6294
RINCON #1 TAP - 115 kV | ETL.1601 | SONOMA | 5 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.062713 | 36.5812 | 1.7059 | 3.9136 | Low | High | Medium | 220 | 223 | 2.2941
SANTA YNEZ TAP - 115 kV | ETL.3701 | LOS PADRES | 130 | 0 | 0 | 2.941% | 38.24% | 0% | 0 | 0% | 14.71% | 0 | 0.11716 | 24.6206 | 1.3466 | 3.8842 | Medium | High | Low | 221 | 204 | 2.8845
GRANITE ROCK TAP - 60 kV | ETL.8311 | CENTRAL COAST | 27 | 0 | 0 | 0% | 70.37% | 0% | 0 | 0% | 0% | 0 | 0.11035 | 24.2838 | 1.4298 | 3.8316 | Low | High | Low | 222 | 213 | 2.6797
GOLDTREE TAP-115 kV | ETL.2821 | LOS PADRES | 36 | 0 | 0 | 10% | 0% | 0% | 0 | 0% | 0% | 0 | 0.053861 | 30.3689 | 2.2874 | 3.7415 | Low | High | High | 223 | 249 | 1.6357
RIO DELL JCT-BRIDGEVILLE - 60 kV | ETL.7850 | HUMBOLDT | 199 | 0 | 0 | 1.163% | 58.14% | 0% | 0 | 0.1406% | 2.326% | 1 | 0.55921 | 8.5185 | 0.78075 | 3.7192 | High | Medium | Low | 224 | 160 | 4.7637
DRUM PH #2 TAP - 115 kV | ETL.6375 | SIERRA | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 50% | 0 | 0.18316 | 34.713 | 0.58054 | 3.6911 | Medium | High | Low | 225 | 127 | 6.3582
HILLSDALE JCT-HALF MOON BAY - 60 kV | ETL.7060 | PENINSULA | 68 | 0 | 0 | 6.897% | 13.79% | 0% | 0 | 0% | 12.07% | 1 | 0.15109 | 9.6421 | 2.4536 | 3.5745 | Medium | Medium | High | 226 | 263 | 1.4569
SPAULDING-SUMMIT - 60 kV | ETL.8060 | SIERRA | 482 | 0 | 0 | 2.179% | 69.72% | 0% | 0 | 2.811% | 6.754% | 1 | 0.99566 | 4.7316 | 0.75111 | 3.5385 | High | Medium | Low | 227 | 161 | 4.711
PARADISE-TABLE MTN - 115 kV | ETL.4316 | NORTH VALLEY | 168 | 0 | 0 | 0% | 9.036% | 0% | 0 | 0% | 73.49% | 1 | 0.61237 | 2.3622 | 2.3592 | 3.4127 | High | Low | High | 228 | 266 | 1.4466
PARDEE #1 TAP-60 kV | ETL.8231 | STOCKTON | 3 | 0 | 0 | 33.33% | 0% | 0% | 0 | 100% | 0% | 0 | 0.21675 | 7.8122 | 1.9731 | 3.341 | Medium | Medium | Medium | 229 | 247 | 1.6933
VINEYARD-NEWARK - 230 kV | ETL.4536 | MISSION | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 26.5534 | 2.1284 | 3.3145 | Low | High | Medium | 230 | 258 | 1.5572
RIO DELL TAP - 60 kV | ETL.7851 | HUMBOLDT | 9 | 0 | 0 | 0% | 0% | 0% | 0 | 92.88% | 20% | 0 | 0.13601 | 18.8205 | 1.2939 | 3.3121 | Medium | High | Low | 231 | 216 | 2.5597
COTTONWOOD-PANORAMA - 115 kV | ETL.1340 | NORTH VALLEY | 35 | 0 | 0 | 6.667% | 0% | 76.67% | 0 | 0% | 10% | 0 | 0.18099 | 10.2504 | 1.7753 | 3.2935 | Medium | Medium | Medium | 232 | 239 | 1.8552
PIT #3-PIT #1 - 230 kV | ETL.5400 | NORTH VALLEY | 174 | 16 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.7099 | 4.1096 | 1.1257 | 3.2841 | High | Medium | Low | 233 | 203 | 2.9174
TULUCAY-NAPA #1 - 60 kV | ETL.8180 | NORTH BAY | 75 | 0 | 1 | 16.18% | 8.824% | 41.18% | 0 | 0% | 7.353% | 1 | 0.23194 | 7.0004 | 2.0049 | 3.2552 | Medium | Medium | Medium | 234 | 251 | 1.6237
HUMBOLDT-MAPLE CREEK - 60 kV | ETL.7130 | HUMBOLDT | 103 | 1 | 0 | 2.151% | 21.51% | 0% | 0 | 0.3595% | 6.452% | 1 | 0.42871 | 3.1488 | 2.3953 | 3.2334 | High | Medium | High | 235 | 270 | 1.3499
LAS POSITAS-NEWARK - 230 kV | ETL.4980 | MISSION | 50 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.09163 | 17.1079 | 1.9982 | 3.1324 | Low | Medium | Medium | 236 | 256 | 1.5676
HARTLEY-CLEARLAKE - 60 kV | ETL.7515 | HUMBOLDT | 55 | 0 | 0 | 2.5% | 67.5% | 0% | 0 | 0% | 5% | 0 | 0.13895 | 13.1263 | 1.704 | 3.1078 | Medium | Medium | Medium | 237 | 242 | 1.8239
COLGATE PH-COLGATE SW STA - 60 kV | ETL.6460 | SIERRA | 3 | 0 | 0 | 0% | 33.33% | 0% | 0 | 0% | 100% | 0 | 0.21742 | 7.3326 | 1.8937 | 3.0191 | Medium | Medium | Medium | 238 | 252 | 1.5943
CAPE HORN TAP - 60 kV | ETL.6761 | SIERRA | 6 | 0 | 0 | 0% | 33.33% | 0% | 0 | 0% | 0% | 0 | 0.078567 | 23.8842 | 1.6088 | 3.019 | Low | High | Medium | 239 | 237 | 1.8765
IBM HARRY RD #1 TAP - 115 kV | ETL.2501 | SAN JOSE | 7 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.064845 | 34.073 | 1.361 | 3.0072 | Low | High | Low | 240 | 224 | 2.2095
COLGATE-SMARTVILLE #2 - 60 kV | ETL.6520 | SIERRA | 155 | 0 | 0 | 0% | 60% | 0% | 0 | 97.48% | 5.806% | 1 | 0.78257 | 1.961 | 1.9468 | 2.9877 | High | Low | Medium | 241 | 259 | 1.5347
RACETRACK TAP - 115 kV | ETL.2393 | YOSEMITE | 52 | 0 | 0 | 5.769% | 53.85% | 0% | 0 | 0% | 1.923% | 0 | 0.11969 | 10.4549 | 2.3414 | 2.9299 | Medium | Medium | High | 242 | 275 | 1.2514
TESLA-NEWARK #2 - 230 kV | ETL.5354 | MISSION | 58 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.096185 | 15.1725 | 2.0026 | 2.9225 | Low | Medium | Medium | 243 | 262 | 1.4594
ROUND MTN-COTTONWOOD #2 - 230 kV | ETL.5640 | NORTH VALLEY | 193 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.60326 | 3.5005 | 1.3808 | 2.9158 | High | Medium | Low | 244 | 229 | 2.1117
DUTCH FLAT #2 TAP - 115 kV | ETL.1421 | SIERRA | 9 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 11.11% | 0 | 0.035633 | 77.203 | 1.0341 | 2.8449 | Low | High | Low | 245 | 210 | 2.751
WEIMAR-HALSEY-60 kV | ETL.8340 | SIERRA | 139 | 0 | 0 | 0% | 73.38% | 0% | 0 | 0% | 0.7194% | 0 | 0.47932 | 3.3 | 1.7926 | 2.8355 | High | Medium | Medium | 246 | 255 | 1.5818
IBM HARRY RD #2 TAP - 115 kV | ETL.2481 | SAN JOSE | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 35.3263 | 1.3659 | 2.8297 | Low | High | Low | 247 | 231 | 2.0717
CENTERVILLE-TABLE MTN - 60 kV | ETL.6320 | NORTH VALLEY | 128 | 0 | 0 | 3.361% | 82.35% | 0% | 0 | 0% | 24.37% | 1 | 0.39408 | 2.7385 | 2.6091 | 2.8157 | High | Low | High | 248 | 283 | 1.0792
MTN QUARRIES TAP - 60 kV | ETL.6991 | SIERRA | 29 | 0 | 0 | 4% | 20% | 0% | 0 | 0% | 84% | 0 | 0.18233 | 7.493 | 2.0513 | 2.8025 | Medium | Medium | Medium | 249 | 268 | 1.3662
FORT BRAGG-ELK - 60 kV | ETL.2060 | HUMBOLDT | 293 | 0 | 0 | 0.3745% | 1.498% | 0% | 0 | 0% | 4.12% | 1 | 0.86512 | 1.5755 | 2.0302 | 2.7673 | High | Low | Medium | 250 | 269 | 1.363
METCALF-EDENVALE #1 - 115 kV | ETL.2480 | SAN JOSE | 13 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.065935 | 30.9398 | 1.3535 | 2.7613 | Low | High | Low | 251 | 233 | 2.04
MANVILLE TAP - 115 kV | ETL.1372 | LOS PADRES | 29 | 0 | 0 | 5.263% | 5.263% | 0% | 0 | 0% | 47.37% | 0 | 0.11477 | 9.147 | 2.6302 | 2.7612 | Low | Medium | High | 252 | 286 | 1.0498
PARDEE #2 TAP - 60 kV | ETL.8251 | STOCKTON | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 0% | 0 | 0.12363 | 11.2183 | 1.9729 | 2.7363 | Medium | Medium | Medium | 253 | 267 | 1.387
PALERMO-WYANDOTTE - 115 kV | ETL.4315 | NORTH VALLEY | 13 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.065935 | 16.344 | 2.5311 | 2.7277 | Low | Medium | High | 254 | 284 | 1.0777
EXCHEQUER-YOSEMITE - 70 kV | ETL.8650 | YOSEMITE | 241 | 3 | 0 | 0% | 0% | 0% | 60380.9 | 0.0006683% | 99.58% | 1 | 0.74668 | 2.4937 | 1.4623 | 2.7229 | High | Low | Low | 255 | 238 | 1.862
IGNACIO-ALTO-SAUSALITO #2 - 60 kV | ETL.7170 | NORTH BAY | 7 | 0 | 0 | 0% | 0% | 0% | 0 | 10.49% | 16.67% | 0 | 0.041249 | 24.3184 | 2.6882 | 2.6965 | Low | High | High | 256 | 296 | 1.0031
CAYUCOS-CAMBRIA-70 kV | ETL.8560 | LOS PADRES | 80 | 0 | 0 | 5.797% | 21.74% | 0% | 0 | 0% | 47.83% | 1 | 0.22061 | 5.4658 | 2.2009 | 2.6538 | Medium | Medium | High | 257 | 277 | 1.2058
METCALF-EL PATIO #1 - 115 kV | ETL.2500 | SAN JOSE | 15 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.07406 | 24.6539 | 1.4188 | 2.5905 | Low | High | Low | 258 | 241 | 1.8259
EXCHEQUER-MARIPOSA - 70 kV | ETL.8640 | YOSEMITE | 157 | 0 | 0 | 9.032% | 72.26% | 0% | 0 | 0% | 82.58% | 1 | 0.69191 | 3.6004 | 1.0232 | 2.5489 | High | Medium | Low | 259 | 218 | 2.4911
LAKEVILLE-IGNACIO #1 - 230 kV | ETL.4940 | NORTH BAY | 21 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.061672 | 13.9866 | 2.952 | 2.5463 | Low | Medium | High | 260 | 306 | 0.86259
TESLA-NEWARK #1 - 230 kV | ETL.5720 | MISSION | 44 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.087269 | 14.3508 | 1.9802 | 2.48 | Low | Medium | Medium | 261 | 274 | 1.2524
HUMBOLDT BAY-RIO DELL JCT - 60 kV | ETL.7100 | HUMBOLDT | 28 | 0 | 0 | 6.667% | 13.33% | 0% | 0 | 0% | 0% | 1 | 0.11244 | 15.2359 | 1.4347 | 2.4578 | Low | Medium | Low | 262 | 246 | 1.7131
VASONA-METCALF - 230 kV | ETL.5932 | SAN JOSE | 15 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.07406 | 23.2955 | 1.4185 | 2.4473 | Low | High | Low | 263 | 245 | 1.7253
BELLOTA-RIVERBANK-MELONES SW STA-115 kV | ETL.1070 | STOCKTON | 146 | 0 | 0 | 7.965% | 36.28% | 11.5% | 0 | 0% | 7.08% | 1 | 0.40221 | 3.3186 | 1.8272 | 2.4389 | High | Medium | Medium | 264 | 271 | 1.3348
HUMBOLDT-BRIDGEVILLE - 115 kV | ETL.1810 | HUMBOLDT | 161 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 90.91% | 0 | 0.15661 | 6.333 | 2.4403 | 2.4203 | Medium | Medium | High | 265 | 297 | 0.99179
VACA-BAHIA - 230 kV | ETL.5810 | SACRAMENTO | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 24.3184 | 1.6227 | 2.3534 | Low | High | Medium | 266 | 264 | 1.4503
PALERMO-NICOLAUS - 115 kV | ETL.3210 | NORTH VALLEY | 9 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.067043 | 13.679 | 2.5088 | 2.3008 | Low | Medium | High | 267 | 302 | 0.91709
TESLA-METCALF - 500 kV | ETL.6110 | SAN JOSE | 121 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.33857 | 6.2884 | 1.079 | 2.2973 | Medium | Medium | Low | 268 | 227 | 2.1291
OLEUM-MARTINEZ - 115 kV | ETL.3170 | DIABLO | 31 | 5 | 0 | 0% | 0% | 0% | 0 | 72.9% | 100% | 0 | 0.4164 | 2.4614 | 2.2389 | 2.2946 | High | Low | High | 269 | 291 | 1.0249
NEWARK-VALLECITOS - 60 kV | ETL.7670 | MISSION | 19 | 0 | 0 | 0% | 0% | 0% | 0 | 56.75% | 100% | 0 | 0.1604 | 6.8018 | 2.0915 | 2.2819 | Medium | Medium | Medium | 270 | 282 | 1.091
MOSS LANDING-COBURN - 230 kV | ETL.5330 | CENTRAL COAST | 154 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 98.57% | 0 | 0.4242 | 9.7186 | 0.52954 | 2.1831 | High | Medium | Low | 271 | 177 | 4.1226
FITCH MTN #1 TAP - 60 kV | ETL.6891 | SONOMA | 8 | 0 | 0 | 0% | 66.67% | 0% | 0 | 0% | 0% | 0 | 0.11618 | 14.9507 | 1.2404 | 2.1545 | Low | Medium | Low | 272 | 244 | 1.737
METCALF-EDENVALE #2 - 115 kV | ETL.2490 | SAN JOSE | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 26.5534 | 1.3418 | 2.1249 | Low | High | Low | 273 | 254 | 1.5836
KILARC-CEDAR CREEK - 60 kV | ETL.7290 | NORTH VALLEY | 285 | 0 | 0 | 2.456% | 82.81% | 0% | 0 | 98.94% | 8.07% | 1 | 0.97905 | 16.473 | 0.13083 | 2.11 | High | Medium | Low | 274 | 45 | 16.1279
BUENA VISTA BIOMASS POWER TAP - 60 kV | ETL.8252 | STOCKTON | 8 | 0 | 0 | 0% | 16.67% | 0% | 0 | 0% | 66.67% | 0 | 0.12313 | 7.9754 | 2.1044 | 2.0666 | Medium | Medium | Medium | 275 | 298 | 0.98201
NARROWS #1 TAP - 60 kV | ETL.6511 | SIERRA | 35 | 0 | 0 | 2.857% | 45.71% | 0% | 0 | 98.91% | 2.857% | 0 | 0.36774 | 2.7386 | 2.0499 | 2.0644 | Medium | Low | Medium | 276 | 294 | 1.0071
CARBERRY SW STA-ROUND MTN - 230 kV | ETL.5410 | NORTH VALLEY | 107 | 0 | 0 | 0% | 0% | 0% | 0 | 1.577% | 100% | 0 | 0.29751 | 9.0701 | 0.76387 | 2.0613 | Medium | Medium | Low | 277 | 212 | 2.6985
PLACER-GOLD HILL #2 - 115 kV | ETL.4290 | SIERRA | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.058646 | 14.9507 | 2.3223 | 2.0362 | Low | Medium | High | 278 | 303 | 0.87679
RINCON #2 TAP - 115 kV | ETL.1611 | SONOMA | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 19.9979 | 1.7143 | 2.0105 | Low | High | Medium | 279 | 279 | 1.1728
SISQUOC-SANTA YNEZ SW STA - 115 kV | ETL.3700 | LOS PADRES | 209 | 0 | 0 | 2.01% | 45.73% | 0% | 0 | 0% | 10.55% | 0 | 0.68552 | 3.4359 | 0.84239 | 1.9841 | High | Medium | Low | 280 | 222 | 2.3554
ROLLINS TAP - 60 kV | ETL.6762 | SIERRA | 14 | 0 | 0 | 0% | 28.57% | 0% | 0 | 0% | 7.143% | 0 | 0.065688 | 18.6162 | 1.6163 | 1.9765 | Low | High | Medium | 281 | 276 | 1.2228
STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA - 115 kV | ETL.3840 | STOCKTON | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 94.33% | 100% | 1 | 0.22977 | 4.4061 | 1.9495 | 1.9737 | Medium | Medium | Medium | 282 | 292 | 1.0124
COLGATE-SMARTVILLE #1 - 60 kV | ETL.6510 | SIERRA | 147 | 0 | 0 | 1.361% | 57.14% | 0% | 0 | 0% | 29.93% | 0 | 0.49903 | 2.0231 | 1.9467 | 1.9654 | High | Low | Medium | 283 | 293 | 1.0096
COLEMAN-SOUTH - 60 kV | ETL.6450 | NORTH VALLEY | 285 | 0 | 0 | 1.053% | 89.47% | 0% | 0 | 0% | 3.509% | 0 | 0.91502 | 1.675 | 1.2793 | 1.9608 | High | Low | Low | 284 | 260 | 1.5327
METCALF-HICKS 1 & 2-115 kV | ETL.4317 | SAN JOSE | 15 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.071649 | 18.4058 | 1.443 | 1.903 | Low | High | Low | 285 | 272 | 1.3188
LIMESTONE TAP - 60 kV | ETL.6951 | SIERRA | 15 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.035232 | 24.4349 | 2.1549 | 1.8552 | Low | High | High | 286 | 307 | 0.86089
PALERMO-COLGATE - 230 kV | ETL.5360 | SIERRA | 83 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.19477 | 4.3458 | 2.1658 | 1.8332 | Medium | Medium | High | 287 | 308 | 0.84642
FLINT TAP - 115 kV | ETL.3341 | SIERRA | 29 | 0 | 0 | 9.524% | 47.62% | 0% | 0 | 0% | 23.81% | 0 | 0.11687 | 6.9205 | 2.2484 | 1.8185 | Medium | Medium | High | 288 | 312 | 0.80878
FORBESTOWN TAP - 115 kV | ETL.4222 | NORTH VALLEY | 10 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 60% | 0 | 0.051442 | 21.4427 | 1.632 | 1.8002 | Low | High | Medium | 289 | 281 | 1.103
CHINESE CAMP (ULTRA POWER) TAP - 115 kV | ETL.2392 | YOSEMITE | 28 | 0 | 0 | 0% | 73.68% | 0% | 0 | 0% | 0% | 0 | 0.097093 | 11.3729 | 1.6132 | 1.7813 | Low | Medium | Medium | 290 | 280 | 1.1042
GARCIA TAP - 60 kV | ETL.8411 | HUMBOLDT | 34 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 8.824% | 0 | 0.053703 | 29.5269 | 1.1095 | 1.7594 | Low | High | Low | 291 | 253 | 1.5857
MIDDLE FORK #1-60 kV | ETL.8405 | SIERRA | 140 | 0 | 0 | 0% | 56.43% | 0% | 0 | 0% | 4.286% | 1 | 0.34383 | 3.1094 | 1.6015 | 1.7121 | Medium | Medium | Medium | 292 | 285 | 1.0691
MORRO BAY-SOLAR SW STA #2 - 230 kV | ETL.5310 | LOS PADRES | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.063771 | 12.4421 | 2.146 | 1.7027 | Low | Medium | High | 293 | 313 | 0.79344
CRAZY HORSE CANYON-SALINAS-SOLEDAD #1-115 kV | ETL.2900 | CENTRAL COAST | 90 | 1 | 0 | 0% | 0% | 0% | 4.71 | 20.51% | 100% | 1 | 0.45606 | 8.0653 | 0.44956 | 1.6536 | High | Medium | Low | 294 | 187 | 3.6783
PALERMO-OROVILLE #2 - 60 kV | ETL.7740 | NORTH VALLEY | 26 | 0 | 0 | 0% | 71.43% | 0% | 2.19 | 21.64% | 0% | 0 | 0.13523 | 4.2065 | 2.8893 | 1.6436 | Medium | Medium | High | 295 | 327 | 0.56884
DIVIDE-VANDENBERG #1 - 70 kV | ETL.8620 | LOS PADRES | 66 | 2 | 0 | 6.25% | 7.812% | 0% | 0 | 0% | 0% | 0 | 0.2799 | 2.2323 | 2.4872 | 1.5541 | Medium | Low | High | 296 | 323 | 0.62484
SMARTVILLE-NICOLAUS #1 - 60 kV | ETL.7990 | SIERRA | 99 | 0 | 0 | 3.191% | 81.91% | 0% | 0 | 39.61% | 10.53% | 1 | 0.45049 | 1.8155 | 1.8264 | 1.4938 | High | Low | Medium | 297 | 311 | 0.81788
STANISLAUS-NEWARK #1 (12KV)-115 kV | ETL.3850 | MISSION | 43 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.076546 | 9.1224 | 2.0433 | 1.4268 | Low | Medium | Medium | 298 | 317 | 0.69828
MALIN-ROUND MTN #2 - 500 kV | ETL.6020 | NORTH VALLEY | 302 | 0 | 1 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.93064 | 4.7226 | 0.32103 | 1.4109 | High | Medium | Low | 299 | 168 | 4.395
SMARTVILLE-NICOLAUS #2 - 60 kV | ETL.8000 | SIERRA | 95 | 0 | 0 | 2.105% | 83.16% | 0% | 0 | 89.13% | 91.58% | 1 | 0.76869 | 1 | 1.8274 | 1.4047 | High | Low | Medium | 300 | 316 | 0.76869
NORTH TOWER-MARTINEZ JCT #1 (21KV)-115 kV | ETL.3130 | EAST BAY | 12 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.070471 | 7.8135 | 2.522 | 1.3887 | Low | Medium | High | 301 | 330 | 0.55063
OCEANO-CALLENDER SW STA-115 kV | ETL.2394 | LOS PADRES | 50 | 0 | 0 | 9.302% | 32.56% | 0% | 0 | 0% | 0% | 0 | 0.12249 | 5.3295 | 2.0624 | 1.3464 | Medium | Medium | Medium | 302 | 319 | 0.65283
GEYSERS #11-EAGLE ROCK - 115 kV | ETL.4391 | SONOMA | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.061672 | 12.6592 | 1.719 | 1.342 | Low | Medium | Medium | 303 | 315 | 0.78072
JEFFERSON-LAS PULGAS - 60 kV | ETL.7200 | PENINSULA | 6 | 0 | 0 | 0% | 100% | 0% | 0 | 0% | 0% | 0 | 0.35719 | 1 | 3.6666 | 1.3097 | Medium | Low | High | 304 | 348 | 0.35719
SPI (BURNEY) TAP - 230 kV | ETL.5392 | NORTH VALLEY | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 14.9507 | 1.4639 | 1.2835 | Low | Medium | Low | 305 | 303 | 0.87679
BELL-PLACER - 115 kV | ETL.4395 | SIERRA | 21 | 0 | 0 | 0% | 0% | 0% | 2.89 | 57.57% | 100% | 0 | 0.15037 | 3.6855 | 2.2704 | 1.2582 | Medium | Medium | High | 306 | 329 | 0.55417
GEYSERS #13 TAP - 230 kV | ETL.4781 | HUMBOLDT | 11 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.069311 | 11.8328 | 1.4729 | 1.208 | Low | Medium | Low | 307 | 310 | 0.82014
DELTA-MTN GATE JCT - 60 kV | ETL.6750 | NORTH VALLEY | 191 | 0 | 0 | 3.158% | 34.74% | 0% | 0 | 99.21% | 9.474% | 1 | 0.91983 | 1 | 1.2525 | 1.1521 | High | Low | Low | 308 | 301 | 0.91983
EL DORADO-MISSOURI FLAT #2-115 kV | ETL.1540 | SIERRA | 21 | 0 | 0 | 4.762% | 33.33% | 0% | 8.7 | 53.84% | 52.38% | 1 | 0.24471 | 2.6346 | 1.7022 | 1.0974 | Medium | Low | Medium | 309 | 322 | 0.64472
MENDOCINO #1 - 60 kV | ETL.7530 | HUMBOLDT | 53 | 0 | 0 | 3.774% | 62.26% | 0% | 3.15 | 71.56% | 5.66% | 0 | 0.348 | 2.9465 | 1.062 | 1.0889 | Medium | Low | Low | 310 | 290 | 1.0254
IGNACIO-ALTO-SAUSALITO #1 - 60 kV | ETL.7160 | NORTH BAY | 41 | 0 | 0 | 0% | 0% | 0% | 0 | 9.188% | 81.25% | 0 | 0.098061 | 3.9148 | 2.6865 | 1.0313 | Low | Medium | High | 311 | 346 | 0.38389
DIABLO-MESA - 230 kV | ETL.4620 | LOS PADRES | 46 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.11833 | 3.4238 | 2.507 | 1.0157 | Medium | Medium | High | 312 | 344 | 0.40514
PORT COSTA BRICK TAP - 60 kV | ETL.6371 | DIABLO | 31 | 0 | 0 | 0% | 9.677% | 3.226% | 1.49 | 100% | 3.226% | 0 | 0.42961 | 1 | 2.3115 | 0.99303 | High | Low | High | 313 | 339 | 0.42961
MOSS LANDING-LOS BANOS - 500 kV | ETL.6040 | CENTRAL COAST | 94 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.132 | 9.0027 | 0.8104 | 0.96305 | Medium | Medium | Low | 314 | 278 | 1.1884
SMARTVILLE-MARYSVILLE - 60 kV | ETL.7980 | SIERRA | 109 | 0 | 0 | 1.031% | 83.51% | 0% | 0 | 65.15% | 10.31% | 1 | 0.52297 | 1 | 1.7718 | 0.9266 | High | Low | Medium | 315 | 331 | 0.52297
FORKS OF THE BUTTE TAP - 60 kV | ETL.6722 | NORTH VALLEY | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.030161 | 11.463 | 2.6042 | 0.90038 | Low | Medium | High | 316 | 350 | 0.34574
WISHON-COPPERMINE - 70 kV | ETL.9330 | FRESNO | 108 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.28505 | 1.9756 | 1.5652 | 0.8814 | Medium | Low | Medium | 317 | 328 | 0.56314
FRENCH MEADOWS-MIDDLE FORK - 60 kV | ETL.6870 | SIERRA | 240 | 0 | 0 | 0% | 87.5% | 0% | 0 | 0% | 14.58% | 1 | 0.80761 | 1.5569 | 0.67927 | 0.85409 | High | Low | Low | 318 | 273 | 1.2574
TEJON-LEBEC - 70 kV | ETL.9250 | KERN | 97 | 1 | 0 | 11.49% | 58.62% | 0% | 0 | 0% | 18.39% | 0 | 0.40208 | 1 | 2.056 | 0.82666 | High | Low | Medium | 319 | 345 | 0.40208
SALMON CREEK TAP - 60 kV | ETL.6981 | SONOMA | 80 | 0 | 0 | 43.06% | 0% | 0% | 0 | 0% | 6.944% | 0 | 0.13171 | 3.1309 | 1.9979 | 0.82389 | Medium | Medium | Medium | 320 | 343 | 0.41237
GEYSERS #16 TAP - 230 kV | ETL.4760 | HUMBOLDT | 7 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.064845 | 7.6624 | 1.6396 | 0.81465 | Low | Medium | Medium | 321 | 334 | 0.49687
BOTTLE ROCK TAP D.W.R. - 230 kV | ETL.4771 | HUMBOLDT | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.063771 | 6.721 | 1.8892 | 0.80973 | Low | Medium | Medium | 322 | 340 | 0.42861
MIDWAY-WHIRLWIND - 500 kV | ETL.6030 | KERN | 38 | 2 | 7 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.2111 | 2.2333 | 1.6917 | 0.79756 | Medium | Low | Medium | 323 | 337 | 0.47145
MISSION POWER TAP-115 kV | ETL.1651 | SONOMA | 22 | 1 | 0 | 13.64% | 0% | 0% | 0 | 0% | 54.55% | 0 | 0.22227 | 2.9024 | 1.1636 | 0.75064 | Medium | Low | Low | 324 | 321 | 0.64512
IGNACIO-STAFFORD-60 kV | ETL.1042 | NORTH BAY | 20 | 0 | 0 | 30.77% | 46.15% | 0% | 0 | 0% | 0% | 0 | 0.087593 | 3.3581 | 2.5477 | 0.74938 | Low | Medium | High | 325 | 356 | 0.29414
BELDEN TAP - 230 kV | ETL.4441 | NORTH VALLEY | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 16.5456 | 0.73184 | 0.73437 | Low | Medium | Low | 326 | 295 | 1.0034
HAT CREEK #1-WESTWOOD - 60 kV | ETL.7030 | NORTH VALLEY | 1023 | 0 | 0 | 0.7752% | 89.04% | 0% | 0 | 100% | 2.993% | 1 | 1 | 1.0339 | 0.70458 | 0.7285 | High | Low | Low | 327 | 288 | 1.0339
LONE STAR TAP - 60 kV | ETL.6231 | CENTRAL COAST | 16 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.032884 | 8.2286 | 2.6652 | 0.72118 | Low | Medium | High | 328 | 364 | 0.27059
CHRISTIE-WILLOW PASS - 60 kV | ETL.6370 | DIABLO | 47 | 0 | 0 | 6.977% | 41.86% | 0% | 12.86 | 81.55% | 6.977% | 1 | 0.31965 | 1 | 2.1817 | 0.69739 | Medium | Low | High | 329 | 353 | 0.31965
DIVIDE-VANDENBERG #2 - 70 kV | ETL.8630 | LOS PADRES | 52 | 0 | 0 | 37.25% | 1.961% | 0% | 0 | 0% | 0% | 0 | 0.13869 | 1.9478 | 2.4969 | 0.67451 | Medium | Low | High | 330 | 365 | 0.27014
MOSS LANDING-DEL MONTE #1 - 115 kV | ETL.2830 | CENTRAL COAST | 53 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.11466 | 2.6032 | 2.2536 | 0.67267 | Low | Low | High | 331 | 355 | 0.29848
HELMS-GREGG #1 - 230 kV | ETL.4870 | FRESNO | 182 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.55546 | 1.2035 | 0.99638 | 0.66606 | High | Low | Low | 332 | 318 | 0.66848
PLUMAS-SIERRA TAP - 60 kV | ETL.6291 | NORTH VALLEY | 8 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.029134 | 11.2183 | 1.9892 | 0.65014 | Low | Medium | Medium | 333 | 352 | 0.32684
IONE TAP - 60 kV | ETL.8253 | STOCKTON | 53 | 0 | 0 | 0% | 56.82% | 0% | 0 | 0% | 4.545% | 0 | 0.10537 | 2.7598 | 2.2241 | 0.6468 | Low | Low | High | 334 | 357 | 0.29081
JEFFERSON-STANFORD - 60 kV | ETL.7220 | PENINSULA | 67 | 0 | 0 | 20.97% | 1.613% | 0% | 0 | 0% | 3.226% | 0 | 0.15176 | 1 | 4.0198 | 0.61007 | Medium | Low | High | 335 | 393 | 0.15176
ELK CREEK TAP - 60 kV | ETL.6921 | NORTH VALLEY | 61 | 0 | 0 | 0% | 53.33% | 0% | 0 | 0.835% | 3.333% | 1 | 0.077126 | 6.6027 | 1.157 | 0.58918 | Low | Medium | Low | 336 | 332 | 0.50924
EVERGREEN-ALMADEN - 60 kV | ETL.6830 | SAN JOSE | 8 | 0 | 0 | 0% | 100% | 0% | 0 | 0% | 0% | 0 | 0.3531 | 1 | 1.629 | 0.57521 | Medium | Low | Medium | 337 | 349 | 0.3531
BRIGHTON-CLAYTON #1-115 kV | ETL.1120 | DIABLO | 13 | 0 | 0 | 0% | 0% | 0% | 6.64 | 100% | 100% | 0 | 0.25929 | 1 | 2.2084 | 0.57261 | Medium | Low | High | 338 | 366 | 0.25929
OLEUM-NORTH TOWER-CHRISTIE - 115 kV | ETL.3180 | DIABLO | 30 | 0 | 0 | 0% | 0% | 0% | 1.48 | 67.31% | 93.33% | 1 | 0.22195 | 1 | 2.482 | 0.55087 | Medium | Low | High | 339 | 376 | 0.22195
CHRISTIE-FRANKLIN #2 - 60 kV | ETL.6360 | EAST BAY | 22 | 0 | 0 | 4.545% | 13.64% | 50% | 0 | 0% | 4.545% | 0 | 0.19878 | 1 | 2.541 | 0.5051 | Medium | Low | High | 340 | 379 | 0.19878
MONTICELLO PH TAP - 115 kV | ETL.1602 | SACRAMENTO | 16 | 0 | 0 | 0% | 18.75% | 0% | 0 | 0% | 26.32% | 0 | 0.088685 | 8.9217 | 0.63341 | 0.50117 | Low | Medium | Low | 341 | 314 | 0.79122
TABLE MTN-PALERMO - 230 kV | ETL.5690 | NORTH VALLEY | 43 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 97.37% | 0 | 0.10573 | 1.6725 | 2.7651 | 0.48895 | Low | Low | High | 342 | 382 | 0.17683
HAT CREEK #1-PIT #1 - 60 kV | ETL.7020 | NORTH VALLEY | 89 | 0 | 0 | 0% | 49.44% | 0% | 5.86 | 96.95% | 34.83% | 1 | 0.57724 | 1 | 0.80722 | 0.46596 | High | Low | Low | 343 | 325 | 0.57724
FROGTOWN #1 TAP - 115 kV | ETL.3831 | STOCKTON | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 100% | 0 | 0.22968 | 1 | 2.0276 | 0.46569 | Medium | Low | Medium | 344 | 371 | 0.22968
NARROWS #2 TAP-60 kV | ETL.6521 | SIERRA | 48 | 0 | 0 | 0% | 39.58% | 0% | 0 | 0% | 6.25% | 0 | 0.11357 | 1.9771 | 2.059 | 0.46233 | Low | Low | Medium | 345 | 375 | 0.22455
MERCED FALLS-EXCHEQUER - 70 kV | ETL.8990 | YOSEMITE | 30 | 0 | 0 | 0% | 0% | 0% | 0 | 93.98% | 100% | 1 | 0.29771 | 1.393 | 1.0875 | 0.45101 | Medium | Low | Low | 346 | 342 | 0.41472
PIT #5-ROUND MTN #2 - 230 kV | ETL.5430 | NORTH VALLEY | 134 | 0 | 0 | 1.493% | 1.493% | 0% | 0 | 0% | 41.04% | 0 | 0.44052 | 1.9709 | 0.51681 | 0.44871 | High | Low | Low | 347 | 305 | 0.86823
SURF TAP - 115 kV | ETL.1381 | LOS PADRES | 35 | 1 | 0 | 0% | 68.75% | 0% | 0 | 0% | 6.25% | 0 | 0.16981 | 1 | 2.4883 | 0.42254 | Medium | Low | High | 348 | 384 | 0.16981
PITTSBURG-TESLA #1 - 230 kV | ETL.5510 | DIABLO | 77 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.18651 | 1 | 2.2232 | 0.41465 | Medium | Low | High | 349 | 380 | 0.18651
IGNACIO-ALTO - 60 kV | ETL.7150 | NORTH BAY | 38 | 0 | 0 | 4.545% | 50% | 0% | 0 | 1.34% | 4.545% | 0 | 0.13169 | 1 | 3.0733 | 0.40472 | Medium | Low | High | 350 | 399 | 0.13169
KANAKA TAP-115 kV | ETL.4223 | NORTH VALLEY | 33 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 36.36% | 0 | 0.064113 | 4.252 | 1.4609 | 0.39826 | Low | Medium | Low | 351 | 363 | 0.27261
CHRISTIE-FRANKLIN #1 - 60 kV | ETL.6350 | EAST BAY | 25 | 0 | 0 | 8.696% | 17.39% | 39.13% | 0 | 0% | 0% | 0 | 0.15486 | 1 | 2.5427 | 0.39376 | Medium | Low | High | 352 | 392 | 0.15486
MONTA VISTA-LOS GATOS - 60 kV | ETL.7610 | DE ANZA | 39 | 0 | 0 | 2.857% | 77.14% | 0% | 0 | 0% | 0% | 1 | 0.12447 | 1 | 3.0933 | 0.38504 | Medium | Low | High | 353 | 404 | 0.12447
GEYSERS #18 TAP - 230 kV | ETL.4784 | SONOMA | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.061672 | 4.4877 | 1.363 | 0.37723 | Low | Medium | Low | 354 | 361 | 0.27677
CHOWCHILLA-KERCKHOFF - 115 kV | ETL.1250 | YOSEMITE | 120 | 0 | 0 | 3.093% | 54.64% | 0% | 0 | 0% | 36.08% | 1 | 0.2816 | 1 | 1.2617 | 0.35529 | Medium | Low | Low | 355 | 359 | 0.2816
IGNACIO-SAN RAFAEL #3 - 115 kV | ETL.1860 | NORTH BAY | 10 | 0 | 0 | 0% | 50% | 0% | 0 | 0% | 0% | 0 | 0.11436 | 1 | 3.038 | 0.34744 | Low | Low | High | 356 | 407 | 0.11436
CASTAIC TAP - 70 kV | ETL.9253 | KERN | 1 | 0 | 0 | 100% | 0% | 0% | 0 | 0% | 0% | 0 | 0.16658 | 1 | 2.0854 | 0.34739 | Medium | Low | Medium | 357 | 385 | 0.16658
BUCKS CREEK-ROCK CREEK-CRESTA - 230 kV | ETL.4430 | NORTH VALLEY | 85 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.21814 | 1.2843 | 1.2165 | 0.34081 | Medium | Low | Low | 358 | 360 | 0.28017
BEALE AFB (WAPA) #1 TAP - 60 kV | ETL.8001 | SIERRA | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 100% | 0 | 0.22968 | 1 | 1.4333 | 0.3292 | Medium | Low | Low | 359 | 371 | 0.22968
DINOSAUR POINT TAP-70 kV | ETL.8961 | CENTRAL COAST | 13 | 0 | 0 | 18.18% | 27.27% | 0% | 0 | 65.69% | 0% | 0 | 0.24807 | 1 | 1.2955 | 0.32137 | Medium | Low | Low | 360 | 369 | 0.24807
WINTU TAP-60 kV | ETL.6311 | NORTH VALLEY | 13 | 0 | 0 | 27.27% | 45.45% | 0% | 0 | 0% | 0% | 0 | 0.14999 | 1 | 2.0875 | 0.31309 | Medium | Low | Medium | 361 | 394 | 0.14999
PITTSBURG-COLUMBIA STEEL - 115 kV | ETL.3300 | DIABLO | 9 | 1 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.13966 | 1 | 2.1957 | 0.30666 | Medium | Low | High | 362 | 398 | 0.13966
CRUSHER TAP - 60 kV | ETL.6241 | CENTRAL COAST | 25 | 0 | 0 | 8% | 8% | 0% | 0 | 0% | 4% | 0 | 0.10917 | 1 | 2.7507 | 0.30028 | Low | Low | High | 363 | 408 | 0.10917
CONTRA COSTA-LAS POSITAS - 230 kV | ETL.4510 | MISSION | 66 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.14924 | 1 | 1.9509 | 0.29114 | Medium | Low | Medium | 364 | 395 | 0.14924
PITTSBURG-MARTINEZ #1 - 115 kV | ETL.3320 | DIABLO | 7 | 1 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.1313 | 1 | 2.2121 | 0.29045 | Medium | Low | High | 365 | 401 | 0.1313
BRIONES TAP - 60 kV | ETL.7055 | DIABLO | 91 | 0 | 0 | 0% | 80.56% | 0% | 0 | 0% | 0% | 0 | 0.14549 | 1 | 1.9905 | 0.2896 | Medium | Low | Medium | 366 | 396 | 0.14549
TESLA-SALADO-MANTECA - 115 kV | ETL.4000 | YOSEMITE | 44 | 0 | 0 | 0% | 21.05% | 10.53% | 0 | 18.28% | 0% | 0 | 0.22462 | 1 | 1.2632 | 0.28375 | Medium | Low | Low | 367 | 374 | 0.22462
COLEMAN-COTTONWOOD - 60 kV | ETL.6430 | NORTH VALLEY | 37 | 0 | 0 | 0% | 74.07% | 0% | 0 | 0% | 3.704% | 0 | 0.07954 | 2.0334 | 1.6429 | 0.26572 | Low | Low | Medium | 368 | 386 | 0.16174
ARCO-POLONIO PASS PP - 70 kV | ETL.8450 | KERN | 129 | 2 | 0 | 1.653% | 84.3% | 0% | 0 | 0% | 2.479% | 0 | 0.57257 | 1 | 0.45771 | 0.26207 | High | Low | Low | 369 | 326 | 0.57257
IGNACIO-SAN RAFAEL #1 - 115 kV | ETL.1850 | NORTH BAY | 23 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.075294 | 1 | 3.3963 | 0.25572 | Low | Low | High | 370 | 420 | 0.075294
BEALE AFB (WAPA) #2 TAP - 60 kV | ETL.7971 | SIERRA | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 50% | 0 | 0.17272 | 1 | 1.4324 | 0.2474 | Medium | Low | Low | 371 | 383 | 0.17272
PIT #5-ROUND MTN #1 - 230 kV | ETL.5420 | NORTH VALLEY | 131 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 41.22% | 0 | 0.29001 | 1.603 | 0.52519 | 0.24415 | Medium | Low | Low | 372 | 338 | 0.46488
PIT #3-CARBERRY SW STA - 230 kV | ETL.5450 | NORTH VALLEY | 82 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.18381 | 1.14 | 1.1176 | 0.23419 | Medium | Low | Low | 373 | 377 | 0.20954
FORT SEWARD TAP - 60 kV | ETL.6222 | HUMBOLDT | 58 | 0 | 0 | 0% | 12.5% | 0% | 0 | 0% | 12.5% | 0 | 0.078687 | 3.4952 | 0.84794 | 0.23321 | Low | Medium | Low | 374 | 362 | 0.27503
TULLOCH TAP - 115 kV | ETL.1071 | STOCKTON | 5 | 0 | 0 | 0% | 66.67% | 0% | 0 | 0% | 0% | 0 | 0.11618 | 1 | 1.8639 | 0.21656 | Low | Low | Medium | 375 | 405 | 0.11618
JEFFERSON-HILLSDALE JCT - 60 kV | ETL.7190 | PENINSULA | 28 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 77.78% | 0 | 0.06669 | 1 | 3.1931 | 0.21295 | Low | Low | High | 376 | 434 | 0.06669
UNION CHEMICAL TAP - 60 kV | ETL.6351 | EAST BAY | 11 | 0 | 0 | 0% | 75% | 0% | 0 | 0% | 0% | 0 | 0.08119 | 1 | 2.573 | 0.2089 | Low | Low | High | 377 | 415 | 0.08119
TESLA-LOS BANOS #1 - 500 kV | ETL.6100 | YOSEMITE | 18 | 5 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.16011 | 1 | 1.2754 | 0.20419 | Medium | Low | Low | 378 | 388 | 0.16011
TRACY-LOS BANOS - 500 kV | ETL.6130 | YOSEMITE | 16 | 10 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15772 | 1 | 1.2703 | 0.20034 | Medium | Low | Low | 379 | 390 | 0.15772
OXBOW TAP - 60 kV | ETL.7561 | SIERRA | 3 | 0 | 0 | 0% | 33.33% | 0% | 0 | 0% | 0% | 0 | 0.11618 | 1 | 1.7161 | 0.19938 | Low | Low | Medium | 380 | 405 | 0.11618
FIBREBOARD STANDARD TAP - 115 kV | ETL.1404 | YOSEMITE | 3 | 0 | 0 | 66.67% | 0% | 0% | 0 | 0% | 0% | 0 | 0.073687 | 1 | 2.6129 | 0.19254 | Low | Low | High | 381 | 423 | 0.073687
BUTTE VALLEY-CARIBOU-115 kV | ETL.1180 | NORTH VALLEY | 65 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 93.75% | 1 | 0.15471 | 1.1597 | 1.0396 | 0.18651 | Medium | Low | Low | 382 | 381 | 0.17941
PITTSBURG-CLAYTON #1 - 115 kV | ETL.3280 | DIABLO | 20 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.079108 | 1 | 2.3268 | 0.18406 | Low | Low | High | 383 | 416 | 0.079108
BEARDSLEY TAP - 115 kV | ETL.1401 | YOSEMITE | 38 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 16.67% | 0 | 0.058707 | 2.4196 | 1.2908 | 0.18336 | Low | Low | Low | 384 | 397 | 0.14205
PITTSBURG-CLAYTON #3 - 115 kV | ETL.3290 | DIABLO | 16 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.075294 | 1 | 2.3404 | 0.17622 | Low | Low | High | 385 | 420 | 0.075294
SAN MATEO-HILLSDALE JCT - 60 kV | ETL.7950 | PENINSULA | 18 | 0 | 0 | 35.71% | 0% | 0% | 0 | 0% | 7.143% | 0 | 0.069099 | 1 | 2.4707 | 0.17073 | Low | Low | High | 386 | 430 | 0.069099
TOCALOMA TAP - 60 kV | ETL.7721 | NORTH BAY | 10 | 0 | 0 | 0% | 30% | 0% | 0 | 0% | 0% | 0 | 0.066994 | 1 | 2.5224 | 0.16899 | Low | Low | High | 387 | 433 | 0.066994
HELMS-GREGG #2 - 230 kV | ETL.4880 | FRESNO | 104 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.25347 | 1 | 0.64108 | 0.16249 | Medium | Low | Low | 388 | 367 | 0.25347
NEWARK-LAWRENCE LAB - 115 kV | ETL.3060 | MISSION | 1 | 0 | 0 | 0% | 0% | 0% | 64486.08 | 100% | 100% | 0 | 0.07622 | 1 | 2.1299 | 0.16234 | Low | Low | Medium | 389 | 419 | 0.07622
GRIZZLY TAP - 115 kV | ETL.2395 | NORTH VALLEY | 28 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.077912 | 23.3943 | 0.088896 | 0.16203 | Low | High | Low | 390 | 243 | 1.8227
ARCO-CHOLAME - 70 kV | ETL.8440 | KERN | 82 | 12 | 0 | 4.255% | 63.83% | 0% | 23.2 | 0% | 8.511% | 1 | 0.35869 | 1 | 0.45011 | 0.16145 | Medium | Low | Low | 391 | 347 | 0.35869
PITTSBURG-EASTSHORE - 230 kV | ETL.5462 | DIABLO | 13 | 0 | 1 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.071649 | 1 | 2.249 | 0.16114 | Low | Low | High | 392 | 425 | 0.071649
MUSTANG TAP - 70 kV | ETL.9091 | LOS PADRES | 9 | 0 | 0 | 66.67% | 0% | 0% | 0 | 0% | 0% | 0 | 0.081339 | 1 | 1.9588 | 0.15932 | Low | Low | Medium | 393 | 414 | 0.081339
MTN GATE TAP - 60 kV | ETL.7641 | NORTH VALLEY | 11 | 0 | 0 | 0% | 72.73% | 0% | 0 | 0% | 0% | 0 | 0.085275 | 1 | 1.8682 | 0.15931 | Low | Low | Medium | 394 | 411 | 0.085275
DIABLO UNIT #2 - 500 kV | ETL.5950 | LOS PADRES | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.063771 | 1 | 2.4808 | 0.1582 | Low | Low | High | 395 | 439 | 0.063771
DIABLO UNIT #1 - 500 kV | ETL.5940 | LOS PADRES | 5 | 0 | 1 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.062713 | 1 | 2.4859 | 0.1559 | Low | Low | High | 396 | 442 | 0.062713
MILLBRAE-SNEATH LANE - 60 kV | ETL.7570 | PENINSULA | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 4.846% | 100% | 0 | 0.067324 | 1 | 2.3087 | 0.15543 | Low | Low | High | 397 | 431 | 0.067324
PIT #6 JCT-ROUND MTN - 230 kV | ETL.5440 | NORTH VALLEY | 80 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 38.75% | 0 | 0.13894 | 1.6386 | 0.67814 | 0.1544 | Medium | Low | Low | 398 | 373 | 0.22767
GEYSERS #5-GEYSERS #3 - 115 kV | ETL.1670 | SONOMA | 9 | 0 | 0 | 22.22% | 22.22% | 0% | 0 | 0% | 0% | 0 | 0.10219 | 1 | 1.4634 | 0.14954 | Low | Low | Low | 399 | 409 | 0.10219
BUELLTON TAP - 115 kV | ETL.1201 | LOS PADRES | 28 | 0 | 0 | 4% | 56% | 0% | 0 | 0% | 0% | 0 | 0.13152 | 1 | 1.13 | 0.14862 | Medium | Low | Low | 400 | 400 | 0.13152
DIABLO PP STANDBY SUPPLY - 230 kV | ETL.4610 | LOS PADRES | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 1 | 2.484 | 0.14814 | Low | Low | High | 401 | 449 | 0.059639
MONTA VISTA-SARATOGA - 230 kV | ETL.5240 | DE ANZA | 5 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 1 | 2.4828 | 0.14807 | Low | Low | High | 402 | 449 | 0.059639
JEFFERSON-MARTIN - 230 kV | ETL.5710 | PENINSULA | 13 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.065935 | 1 | 2.2286 | 0.14694 | Low | Low | High | 403 | 435 | 0.065935
GRAPEVINE TAP - 70 kV | ETL.9252 | KERN | 3 | 0 | 0 | 33.33% | 0% | 0% | 0 | 0% | 0% | 0 | 0.073687 | 1 | 1.9596 | 0.1444 | Low | Low | Medium | 404 | 423 | 0.073687
SILVERADO-FULTON JCT - 115 kV | ETL.1610 | NORTH BAY | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 99.73% | 0% | 1 | 0.12512 | 1 | 1.1339 | 0.14188 | Medium | Low | Low | 405 | 403 | 0.12512
MARTIN-SNEATH LANE - 60 kV | ETL.7210 | PENINSULA | 8 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 1 | 2.322 | 0.14082 | Low | Low | High | 406 | 443 | 0.060648
MELONES-WILSON - 230 kV | ETL.5080 | YOSEMITE | 28 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.084467 | 1 | 1.6558 | 0.13986 | Low | Low | Medium | 407 | 412 | 0.084467
JEFFERSON #1 - 60 kV | ETL.6831 | PENINSULA | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 33.33% | 0 | 0.037725 | 1 | 3.6885 | 0.13915 | Low | Low | High | 408 | 466 | 0.037725
PITTSBURG-TASSAJARA - 230 kV | ETL.5470 | DIABLO | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 1 | 2.2494 | 0.13642 | Low | Low | High | 409 | 443 | 0.060648
CONTRA COSTA-MORAGA #2 - 230 kV | ETL.5453 | DIABLO | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 1 | 2.2504 | 0.13421 | Low | Low | High | 410 | 449 | 0.059639
US WINDPOWER #3 TAP - 230 kV | ETL.4521 | MISSION | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 1 | 2.2728 | 0.13329 | Low | Low | High | 411 | 455 | 0.058646
PITTSBURG-CLAYTON #4 - 115 kV | ETL.3291 | DIABLO | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 1 | 2.2207 | 0.13023 | Low | Low | High | 412 | 455 | 0.058646
CRYSTAL SPRINGS TAP-60 kV | ETL.7211 | PENINSULA | 5 | 0 | 0 | 20% | 0% | 0% | 0 | 0% | 20% | 0 | 0.056012 | 1 | 2.2732 | 0.12733 | Low | Low | High | 413 | 461 | 0.056012
LONE TREE-CAYETANO - 230 kV | ETL.6160 | MISSION | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 1 | 2.0663 | 0.12532 | Low | Low | Medium | 414 | 443 | 0.060648
MCSWAIN TAP - 70 kV | ETL.8991 | YOSEMITE | 13 | 0 | 0 | 0% | 62.5% | 0% | 0 | 0% | 0% | 0 | 0.12567 | 1 | 0.94815 | 0.11915 | Medium | Low | Low | 415 | 402 | 0.12567
MONTA VISTA-PERMANENTE - 60 kV | ETL.7620 | DE ANZA | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 1 | 2.0112 | 0.11795 | Low | Low | Medium | 416 | 455 | 0.058646
KERCKHOFF #1-KERCKHOFF #2 - 115 kV | ETL.1880 | FRESNO | 13 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.071649 | 1 | 1.6245 | 0.1164 | Low | Low | Medium | 417 | 425 | 0.071649
JESSUP TAP - 115 kV | ETL.4041 | NORTH VALLEY | 9 | 0 | 0 | 0% | 22.22% | 0% | 0 | 0% | 22.22% | 0 | 0.067151 | 1 | 1.7222 | 0.11564 | Low | Low | Medium | 418 | 432 | 0.067151
PIT #1-MCARTHUR | ETL.7790 | NORTH VALLEY | 44 | 0 | 0 | 6.977% | 62.79% | 0% | 0 | 0% | 41.86% | 1 | 0.16033 | 1 | 0.70971 | 0.11379 | Medium | Low | Low | 419 | 387 | 0.16033
GEYSERS #17-FULTON - 230 kV | ETL.4770 | SONOMA | 8 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.065935 | 1 | 1.7045 | 0.11239 | Low | Low | Medium | 420 | 435 | 0.065935
BRUNSWICK #2 TAP - 115 kV | ETL.1431 | SIERRA | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 1 | 1.8401 | 0.10791 | Low | Low | Medium | 421 | 455 | 0.058646
COTTLE-MELONES - 230 kV | ETL.4530 | STOCKTON | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 1 | 1.6592 | 0.097305 | Low | Low | Medium | 422 | 455 | 0.058646
SANTA FE GEOTHERMAL TAP - 230 kV | ETL.4782 | SONOMA | 8 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.065935 | 1 | 1.4721 | 0.097064 | Low | Low | Low | 423 | 435 | 0.065935
MESA-SISQUOC - 115 kV | ETL.2460 | LOS PADRES | 21 | 0 | 0 | 0% | 44.44% | 0% | 0 | 0% | 11.11% | 0 | 0.082574 | 1 | 1.1534 | 0.095243 | Low | Low | Low | 424 | 413 | 0.082574
GEYSERS #3-EAGLE ROCK - 115 kV | ETL.1660 | SONOMA | 20 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 65% | 0 | 0.063056 | 1 | 1.4649 | 0.092369 | Low | Low | Low | 425 | 441 | 0.063056
TESLA-SALADO #1 - 115 kV | ETL.3990 | YOSEMITE | 12 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.070471 | 1 | 1.2655 | 0.089179 | Low | Low | Low | 426 | 427 | 0.070471
QUINTO SW STA-WESTLEY - 230 kV | ETL.5070 | YOSEMITE | 12 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.070471 | 1 | 1.2646 | 0.089119 | Low | Low | Low | 427 | 427 | 0.070471
GEYSERS #7-EAGLE ROCK - 115 kV | ETL.1680 | SONOMA | 16 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 56.25% | 0 | 0.055437 | 1 | 1.5297 | 0.084803 | Low | Low | Medium | 428 | 462 | 0.055437
YANKE (NORTH FORK) TAP-70 kV | ETL.9341 | YOSEMITE | 8 | 0 | 0 | 0% | 12.5% | 0% | 0 | 0% | 0% | 0 | 0.064797 | 1 | 1.1743 | 0.07609 | Low | Low | Low | 429 | 438 | 0.064797
SAN BRUNO TAP - 60 kV | ETL.7572 | PENINSULA | 13 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.031223 | 1 | 2.335 | 0.072905 | Low | Low | High | 430 | 468 | 0.031223
SPRING GAP TAP - 115 kV | ETL.1402 | YOSEMITE | 21 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 14.29% | 0 | 0.044777 | 1 | 1.5822 | 0.070848 | Low | Low | Medium | 431 | 464 | 0.044777
MESA-SANTA MARIA - 115 kV | ETL.2450 | LOS PADRES | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 1 | 1.1658 | 0.06953 | Low | Low | Low | 432 | 449 | 0.059639
LUCERNE #2 TAP - 115 kV | ETL.2411 | HUMBOLDT | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 50% | 0 | 0.041802 | 1 | 1.6445 | 0.068743 | Low | Low | Medium | 433 | 465 | 0.041802
PERMANENTE #2 TAP - 60 kV | ETL.7622 | DE ANZA | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.030161 | 1 | 2.007 | 0.060533 | Low | Low | Medium | 434 | 469 | 0.030161
SMARTVILLE TAP - 60 kV | ETL.6522 | SIERRA | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.028634 | 1 | 2.0448 | 0.05855 | Low | Low | Medium | 435 | 473 | 0.028634
PERMANENTE #1 TAP - 60 kV | ETL.7621 | DE ANZA | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.028634 | 1 | 2.0089 | 0.057521 | Low | Low | Medium | 436 | 473 | 0.028634
COLLINS PINE TAP | ETL.7001 | NORTH VALLEY | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.029134 | 1 | 1.9662 | 0.057285 | Low | Low | Medium | 437 | 471 | 0.029134
MORRO BAY-GATES #2 - 230 kV | ETL.5280 | LOS PADRES | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 1 | 0.87602 | 0.051375 | Low | Low | Low | 438 | 455 | 0.058646
LUCERNE #1 TAP - 115 kV | ETL.1331 | HUMBOLDT | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.029643 | 1 | 1.6452 | 0.04877 | Low | Low | Medium | 439 | 470 | 0.029643
PIT #7 TAP - 230 kV | ETL.5442 | NORTH VALLEY | 34 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 55.88% | 0 | 0.074679 | 1 | 0.63028 | 0.047068 | Low | Low | Low | 440 | 422 | 0.074679
SANDBAR TAP - 115 kV | ETL.1403 | YOSEMITE | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.029134 | 1 | 1.5673 | 0.045661 | Low | Low | Medium | 441 | 471 | 0.029134
COBURN-OIL FIELDS #1 - 60 kV | ETL.6410 | CENTRAL COAST | 11 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.028634 | 1 | 1.3363 | 0.038263 | Low | Low | Low | 442 | 473 | 0.028634
MALACHA TAP - 230 kV | ETL.5910 | NORTH VALLEY | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 1 | 0.54048 | 0.032234 | Low | Low | Low | 443 | 449 | 0.059639
HUMBOLDT #1 - 60 kV | ETL.7113 | HUMBOLDT | 9 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.028634 | 1 | 0.83674 | 0.023959 | Low | Low | Low | 444 | 473 | 0.028634
JANES CREEK TAP - 60 kV | ETL.6805 | HUMBOLDT | 5 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.028634 | 1 | 0.83596 | 0.023937 | Low | Low | Low | 445 | 473 | 0.028634
PIT #4 TAP - 230 kV | ETL.5432 | NORTH VALLEY | 62 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15616 | 1 | 0.083247 | 0.013 | Medium | Low | Low | 446 | 391 | 0.15616
PIT #6 TAP - 230 kV | ETL.5441 | NORTH VALLEY | 41 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 29.27% | 0 | 0.069709 | 4.0454 | 0.031412 | 0.0088581 | Low | Medium | Low | 447 | 358 | 0.282
BRENTWOOD-KELSO - 230 kV | ETL.4410 | DIABLO | 22 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.079108 | 1 | 0.077202 | 0.0061072 | Low | Low | Low | 448 | 416 | 0.079108
BLACK TAP - 230 kV | ETL.5431 | NORTH VALLEY | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 1 | 0.086236 | 0.00523 | Low | Low | Low | 449 | 443 | 0.060648
CLOVER CREEK TAP - 60 kV | ETL.7291 | NORTH VALLEY | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.028634 | 1 | 0.018613 | 0.00053297 | Low | Low | Low | 450 | 473 | 0.028634
KINGS RIVER-SANGER-REEDLEY - 115 kV | ETL.2030 | FRESNO | 26 | 0 | 0 | 5% | 10% | 25% | 0 | 0% | 55% | 1 | 0.20768 | 7.2289 | 0 | 0 | Medium | Medium | Low | 451 | 261 | 1.5013
MIDWAY-SANTA MARIA-115 kV | ETL.9240 | LOS PADRES | 170 | 0 | 0 | 0% | 0% | 1.98% | 0 | 0% | 88.12% | 0 | 0.46596 | 9.0233 | 0 | 0 | High | Medium | Low | 451 | 175 | 4.2045
COBURN-PANOCHE - 230 kV | ETL.4460 | CENTRAL COAST | 81 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.17852 | 5.178 | 0 | 0 | Medium | Medium | Low | 451 | 299 | 0.92438
DELEVAN-VACA #2 - 230 kV | ETL.4231 | SACRAMENTO | 51 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.065935 | 14.0021 | 0 | 0 | Low | Medium | Low | 451 | 300 | 0.92324
COALINGA #1-SAN MIGUEL - 70 kV | ETL.8580 | LOS PADRES | 114 | 0 | 0 | 0% | 5.208% | 0% | 18.15 | 48.09% | 95.83% | 1 | 0.64888 | 1 | 0 | 0 | High | Low | Low | 451 | 320 | 0.64888
HAAS-MCCALL - 230 kV | ETL.4850 | FRESNO | 136 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.37542 | 1.3485 | 0 | 0 | Medium | Low | Low | 451 | 333 | 0.50624
BALCH-SANGER - 115 kV | ETL.1050 | FRESNO | 113 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.29608 | 1.1292 | 0 | 0 | Medium | Low | Low | 451 | 351 | 0.33433
TEMPLETON-GATES - 230 kV | ETL.5934 | LOS PADRES | 57 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.097748 | 1 | 0 | 0 | Low | Low | Low | 451 | 410 | 0.097748
TEMBLOR-SAN LUIS OBISPO - 115 kV | ETL.3960 | LOS PADRES | 185 | 0 | 0 | 0% | 0% | 0% | 0 | 99.7% | 100% | 1 | 0.83275 | 1 | 0 | 0 | High | Low | Low | 451 | 309 | 0.83275
CRAZY HORSE CANYON-SAN BENITO-115 kV | ETL.2152 | CENTRAL COAST | 21 | 2 | 0 | 0% | 0% | 0% | 0 | 86.25% | 100% | 0 | 0.4282 | 1 | 0 | 0 | High | Low | Low | 451 | 341 | 0.4282
COTTONWOOD #1 - 60 kV | ETL.6620 | NORTH VALLEY | 66 | 0 | 0 | 0% | 0% | 0% | 0 | 2.224% | 100% | 1 | 0.15841 | 1 | 0 | 0 | Medium | Low | Low | 451 | 389 | 0.15841
COPPERMINE-TIVY VALLEY - 70 kV | ETL.8590 | FRESNO | 116 | 0 | 0 | 15.38% | 30.77% | 0% | 0 | 0% | 23.08% | 1 | 0.12685 | 8.1495 | 0 | 0 | Medium | Medium | Low | 451 | 289 | 1.0338
SISQUOC-GAREY - 115 kV | ETL.3690 | LOS PADRES | 11 | 0 | 0 | 0% | 12.5% | 0% | 0 | 0% | 0% | 0 | 0.064797 | 7.3865 | 0 | 0 | Low | Medium | Low | 451 | 336 | 0.47862
VEDDER TAP - 115 kV | ETL.2141 | KERN | 54 | 0 | 0 | 11.32% | 62.26% | 0% | 44754.84 | 99.64% | 15.09% | 0 | 0.29985 | 1 | 0 | 0 | Medium | Low | Low | 451 | 354 | 0.29985
CORTINA #4 - 60 kV | ETL.6610 | SACRAMENTO | 16 | 0 | 0 | 0% | 75% | 0% | 0 | 45.48% | 25% | 1 | 0.24748 | 1 | 0 | 0 | Medium | Low | Low | 451 | 370 | 0.24748
HAAS-WOODCHUCK - 70 kV | ETL.8730 | FRESNO | 109 | 0 | 0 | 2.174% | 63.04% | 0% | 0 | 0% | 1.087% | 1 | 0.25231 | 1 | 0 | 0 | Medium | Low | Low | 451 | 368 | 0.25231
VACA-LAKEVILLE #1 - 230 kV | ETL.5840 | NORTH BAY | 97 | 0 | 1 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.20915 | 1 | 0 | 0 | Medium | Low | Low | 451 | 378 | 0.20915
GLENN #2-60 kV | ETL.6930 | NORTH VALLEY | 5 | 1 | 0 | 0% | 100% | 0% | 0 | 0% | 0% | 1 | 0.57849 | 1 | 0 | 0 | High | Low | Low | 451 | 324 | 0.57849
TULUCAY-VACA - 230 kV | ETL.5800 | SACRAMENTO | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 1 | 0 | 0 | Low | Low | Low | 451 | 449 | 0.059639
COVE ROAD TAP-230 kV | ETL.5421 | NORTH VALLEY | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.063771 | 1 | 0 | 0 | Low | Low | Low | 451 | 439 | 0.063771
KM GREEN TAP-115 kV | ETL.3505 | STOCKTON | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 1 | 0 | 0 | Low | Low | Low | 451 | 443 | 0.060648
GRIZZLY TAP (SVP) - 115 kV | ETL.1231 | NORTH VALLEY | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 25% | 0 | 0.036142 | 1 | 0 | 0 | Low | Low | Low | 451 | 467 | 0.036142
OROVILLE-THERMALITO-TABLE MTN #1 (CDWR) - 230 kV | ETL.6621 | NORTH VALLEY | 33 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.079108 | 1 | 0 | 0 | Low | Low | Low | 451 | 416 | 0.079108
OROVILLE-THERMALITO-TABLE MTN #3 (CDWR) - 230 kV | ETL.6622 | NORTH VALLEY | 23 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.070471 | 1 | 0 | 0 | Low | Low | Low | 451 | 427 | 0.070471
PINE FLAT PH TAP (CDWR) - 230 kV | ETL.4821 | FRESNO | 5 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 1 | 0 | 0 | Low | Low | Low | 451 | 443 | 0.060648
PITTSBURG-TESLA #2 - 230 kV | ETL.5520 | DIABLO | 11 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 45.45% | 0 | 0.047178 | 1 | -0.087351 | -0.0041211 | Low | Low | Low | 476 | 463 | 0.047178
SPAULDING #3-SPAULDING #1 - 60 kV | ETL.8050 | SIERRA | 27 | 0 | 0 | 0% | 59.26% | 0% | 0 | 100% | 0% | 1 | 0.49124 | 1 | -0.028496 | -0.013998 | High | Low | Low | 477 | 335 | 0.49124
CORTINA-VACA - 230 kV | ETL.4540 | SACRAMENTO | 56 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.070471 | 14.8543 | -2.0491 | -2.145 | Low | Medium | Low | 478 | 287 | 1.0468

## Notes
Notes
(1) Number of miles and number of circuits vary between EVM and SH / Inspection since circuits without trees tagged to them were considered out of scope for the prioritization
(2) Number of miles and number of circuits vary between Dx-SH and Dx-Inspection due to the methodologies used to arrive at the estimated miles. Whereas System Hardening was based upon protection zones with at least some area touching HFTD, Distribution Prioritization miles were based on the true miles within HFTD, potentially not including the entire circuit. This was done intentionally due to the operational nature of the work since it is difficult to complete system hardening intermittently on a line; whereas, it is less difficult to complete Distribution Prioritization intermittently
(3) Prioritization may vary during the implementation of the programs due to operational considerations (e.g. land and environment, safety, planned projects, geographic access, weather, government relations, production-related, and customer communications).
(4) Total miles for across protection zones in Dx-SH and Dx-Inspection is greater than the established 25,200 circuit miles in the HFTD. In the STAR dataset, which is the source of the conductor information, some segments are identified as either idle and proposed segments. These segments were included for analysis to allow futher analysis to be conducted for operational planning. Additionally, the STAR conductor dataset identified if a segment was located in Tier 2 or Tier 3. The analysis relied on this identification.
(5) Dx - EVM planned implementation: Not all portions of circuits highlighted for implementation in 2019 will be worked during 2019. Operational considerations limited work to certain portions of these selected circuits.