## FieldVisist2021
Dx Prioritization Output - System Hardening
| Circuit Information |  |  |  | Independent Variables | [5 empty] | Dependent Variable | Risk Scoring |  |  |  |  | Risk Tiers
Field Visits | Protection Zone | Feeder Name | District | Tier 2/3 OH Miles | Env Risk Component | Material A - % of total miles | Vegetation Outages | Company Outages | HFTD Miles per Total Miles | Tier 3 per HFTD Miles | Ignition Indicator (1+ ignition occurred) | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Consolidated Risk Score | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Rank Cons Risk | Rank P*C | P*C
Feb | BRUNSWICK 110350070 | BRUNSWICK 1103 | SIERRA | 28.1191 | 94.0552 | 99.83% | 13 | 12 | 100% | 100% | 1 | 0.54169 | 102.1389 | 2.325 | 128.6353 | High | High | Medium | 7 | 8 | 55.3273
Mar | EL DORADO PH 210119752 | EL DORADO PH 2101 | SIERRA | 38.577 | 80.8747 | 99.99% | 20 | 11 | 100% | 99.16% | 1 | 0.69086 | 102.1389 | 1.6995 | 119.922 | High | High | Low | 13 | 2 | 70.5639
Mar | PLACERVILLE 21061104 | PLACERVILLE 2106 | SIERRA | 50.3628 | 96.0676 | 90.37% | 13 | 6 | 100% | 100% | 1 | 0.49422 | 102.1389 | 2.2151 | 111.8183 | High | High | Low | 16 | 13 | 50.479
Mar | MIWUK 1702CB | MIWUK 1702 | YOSEMITE | 10.2382 | 90.3115 | 82.25% | 5 | 6 | 100% | 100% | 0 | 0.28839 | 102.1389 | 3.3177 | 97.7246 | High | High | High | 25 | 65 | 29.4558
Feb | UPPER LAKE 1101CB | UPPER LAKE 1101 | HUMBOLDT | 1.1134 | 70.0562 | 95.06% | 2 | 2 | 100% | 0% | 0 | 0.049432 | 1 | 1.7447 | 0.086245 | Medium | Medium | Low | 1866 | 1690 | 0.049432

## Dx - EVM
Dx Prioritization Output - Enhanced Vegetation Management | [8 empty] | Planned 2019 implementation
Circuit Information |  |  | Independent Variables |  |  |  | Dependent Variable | Risk Scoring |  |  |  |  | Risk Tiers
Feeder name | District | Tier 2/3 OH Miles | Tagged trees per mile | # of tagged trees | HFTD Miles per Total Miles | Tier 3 per HFTD Miles | Ignition Indicator (1+ ignition occurred) | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Consolidated Risk Score | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Rank Cons Risk | Rank P*C | P*C
MIWUK 1701 | YOSEMITE | 77.1453 | 7.4105 | 571.3 | 100% | 97.77% | 1 | 0.84354 | 102.1389 | 2.7773 | 239.2862 | High | High | High | 1 | 2 | 86.1578
WOODACRE 1101 | NORTH BAY | 36.2703 | 156.5268 | 6651.2 | 85.36% | 71.43% | 0 | 0.6809 | 102.1389 | 3.1852 | 221.5201 | High | High | High | 2 | 10 | 69.546
MONTE RIO 1113 | SONOMA | 61.2941 | 99.1695 | 6079.1 | 99.99% | 100% | 1 | 0.93391 | 85.4511 | 2.601 | 207.5661 | High | High | High | 3 | 4 | 79.8036
STANISLAUS 1702 | YOSEMITE | 85.5755 | 16.3403 | 1397.79 | 100% | 92.5% | 0 | 0.76675 | 102.1389 | 2.4941 | 195.3255 | High | High | High | 4 | 5 | 78.3147
ORO FINO 1102 | NORTH VALLEY | 109.5969 | 17.2976 | 1899 | 99.83% | 75.7% | 1 | 0.68219 | 102.1389 | 2.501 | 174.2643 | High | High | High | 5 | 9 | 69.6785
MIWUK 1702 | YOSEMITE | 75.7688 | 0.82734 | 62.7 | 99.98% | 98.32% | 0 | 0.55447 | 102.1389 | 3.0491 | 172.6822 | High | High | High | 6 | 18 | 56.6335
WOODSIDE 1101 | PENINSULA | 42.209 | 285.1669 | 17974.3 | 66.97% | 99.11% | 0 | 0.89308 | 65.3912 | 2.8786 | 168.1085 | High | High | High | 7 | 17 | 58.3993
EL DORADO PH 2101 | SIERRA | 156.2859 | 130.0322 | 21677.5 | 93.75% | 82.3% | 0 | 0.97524 | 102.1389 | 1.4541 | 144.8389 | High | High | Low | 8 | 1 | 99.6103
MIDDLETOWN 1101 | HUMBOLDT | 93.5404 | 50.0386 | 5602.4 | 83.55% | 90.53% | 1 | 0.70848 | 102.1389 | 1.8992 | 137.4312 | High | High | Medium | 9 | 7 | 72.3631
MOLINO 1102 | SONOMA | 111.6641 | 99.4196 | 17711.5 | 62.68% | 81.73% | 1 | 0.97108 | 65.3912 | 2.116 | 134.3658 | High | High | Medium | 10 | 15 | 63.5003
ORO FINO 1101 | NORTH VALLEY | 46.3606 | 286.837 | 13336.6 | 99.71% | 100% | 1 | 0.45474 | 102.1389 | 2.8711 | 133.3506 | High | High | High | 11 | 26 | 46.4462
BRUNSWICK 1105 | SIERRA | 121.3812 | 4.8689 | 592.5 | 99.75% | 93.48% | 1 | 0.8365 | 102.1389 | 1.5525 | 132.6436 | High | High | Low | 12 | 3 | 85.4388
BRUNSWICK 1106 | SIERRA | 171.6273 | 45.8179 | 8382.6 | 93.81% | 72.18% | 1 | 0.84416 | 85.4511 | 1.8009 | 129.9055 | High | High | Medium | 13 | 8 | 72.1347
FITCH MOUNTAIN 1113 | SONOMA | 71.7242 | 123.815 | 18517.3 | 47.96% | 38.48% | 1 | 0.7917 | 85.4511 | 1.8073 | 122.2658 | High | High | Medium | 14 | 11 | 67.652
MONTE RIO 1112 | SONOMA | 20.2317 | 256.0419 | 5214.6 | 99.34% | 100% | 0 | 0.56345 | 85.4511 | 2.5369 | 122.1459 | High | High | High | 15 | 23 | 48.1473
SALT SPRINGS 2102 | STOCKTON | 52.0669 | 274.3811 | 14280.22 | 100% | 78.88% | 0 | 0.65297 | 102.1389 | 1.7662 | 117.7973 | High | High | Medium | 16 | 12 | 66.6938
BRUNSWICK 1103 | SIERRA | 55.5518 | 74.8354 | 4688.5 | 88.67% | 72.71% | 1 | 0.6063 | 102.1389 | 1.874 | 116.0496 | High | High | Medium | 17 | 16 | 61.9267
WEST POINT 1101 | STOCKTON | 63.0247 | 94.79 | 5975.19 | 99.98% | 100% | 0 | 0.54643 | 102.1389 | 2.0741 | 115.7578 | High | High | Medium | 18 | 19 | 55.8118
CHALLENGE 1102 | NORTH VALLEY | 63.9131 | 158.4626 | 10015.8 | 100% | 97.43% | 0 | 0.62542 | 102.1389 | 1.7937 | 114.581 | High | High | Medium | 19 | 14 | 63.8802
FORESTHILL 1101 | SIERRA | 65.2463 | 222.4185 | 14478 | 100% | 100% | 1 | 0.63906 | 102.1389 | 1.6905 | 110.3457 | High | High | Medium | 20 | 13 | 65.273
APPLE HILL 1104 | SIERRA | 91.8994 | 113.5688 | 10941.58 | 95.39% | 63.88% | 1 | 0.75734 | 102.1389 | 1.4126 | 109.2734 | High | High | Low | 21 | 6 | 77.3537
BRUNSWICK 1104 | SIERRA | 56.553 | 156.2805 | 9029.4 | 97.88% | 51.09% | 1 | 0.53349 | 102.1389 | 1.987 | 108.2731 | High | High | Medium | 22 | 20 | 54.4906
MIRABEL 1101 | SONOMA | 29.3053 | 373.4114 | 19421.8 | 56.34% | 71.1% | 1 | 0.45576 | 85.4511 | 2.3345 | 90.9172 | High | High | Medium | 23 | 29 | 38.9449
SYCAMORE CREEK 1111 | NORTH VALLEY | 53.4772 | 106.1279 | 6944.7 | 81.72% | 52.39% | 1 | 0.37047 | 102.1389 | 2.1453 | 81.1785 | High | High | Medium | 24 | 30 | 37.8399
BRUNSWICK 1102 | SIERRA | 51.0222 | 117.5978 | 6332.9 | 94.74% | 90.55% | 0 | 0.47031 | 102.1389 | 1.6284 | 78.2224 | High | High | Low | 25 | 24 | 48.037
PARADISE 1106 | NORTH VALLEY | 24.5474 | 22.3524 | 1315 | 41.73% | 100% | 1 | 0.21864 | 102.1389 | 3.2416 | 72.3904 | Medium | High | High | 26 | 45 | 22.3317
EL DORADO PH 2102 | SIERRA | 34.253 | 248.1202 | 8500.5 | 99.98% | 100% | 0 | 0.43516 | 102.1389 | 1.6274 | 72.332 | High | High | Low | 27 | 27 | 44.4472
WILLITS 1104 | HUMBOLDT | 84.9199 | 117.6971 | 11210.5 | 89.16% | 56.68% | 1 | 0.79745 | 65.3912 | 1.33 | 69.3522 | High | High | Low | 28 | 21 | 52.146
PIKE CITY 1101 | SIERRA | 34.5379 | 200.5189 | 6925.5 | 100% | 100% | 1 | 0.46619 | 102.1389 | 1.3946 | 66.4074 | High | High | Low | 29 | 25 | 47.616
CHALLENGE 1101 | NORTH VALLEY | 48.3743 | 117.1487 | 5684.5 | 99.69% | 99.37% | 0 | 0.47698 | 102.1389 | 1.3623 | 66.3697 | High | High | Low | 30 | 22 | 48.7187
PARADISE 1101 | NORTH VALLEY | 23.8829 | 180.1078 | 5230.6 | 82.24% | 100% | 0 | 0.34527 | 65.3912 | 2.9331 | 66.2224 | High | High | High | 31 | 44 | 22.5779
BIG BEND 1102 | NORTH VALLEY | 38.1787 | 184.083 | 7027 | 100% | 100% | 0 | 0.35413 | 85.4511 | 2.0415 | 61.7771 | High | High | Medium | 32 | 34 | 30.2604
SILVERADO 2105 | NORTH BAY | 37.4725 | 150.701 | 9686.5 | 58.3% | 94.51% | 1 | 0.38023 | 65.3912 | 2.3865 | 59.3371 | High | High | Medium | 33 | 41 | 24.8635
PUEBLO 2102 | NORTH BAY | 21.5581 | 127.4127 | 12684 | 21.66% | 93.12% | 0 | 0.32308 | 85.4511 | 1.9904 | 54.9503 | High | High | Medium | 34 | 37 | 27.6079
SHADY GLEN 1102 | SIERRA | 39.0599 | 97.1034 | 4076.4 | 93.04% | 34.11% | 0 | 0.39355 | 85.4511 | 1.5463 | 51.9996 | High | High | Low | 35 | 32 | 33.6292
MOLINO 1101 | SONOMA | 33.6923 | 133.9868 | 12117.7 | 37.25% | 24.8% | 0 | 0.43165 | 65.3912 | 1.7461 | 49.2861 | High | High | Medium | 36 | 35 | 28.2264
SHINGLE SPRINGS 1104 | SIERRA | 42.6451 | 204.2501 | 12204.6 | 71.37% | 86.51% | 0 | 0.36466 | 65.3912 | 2.0063 | 47.8425 | High | High | Medium | 37 | 42 | 23.8458
BONNIE NOOK 1102 | SIERRA | 34.3352 | 243.2045 | 8351.4 | 99.99% | 100% | 0 | 0.39869 | 102.1389 | 1.155 | 47.034 | High | High | Low | 38 | 28 | 40.7222
PENRYN 1103 | SIERRA | 67.0371 | 107.5792 | 8477.8 | 85.07% | 0% | 0 | 0.46834 | 47.6367 | 2.0579 | 45.9118 | High | High | Medium | 39 | 46 | 22.3103
DIAMOND SPRINGS 1107 | SIERRA | 53.8326 | 183.5826 | 10826.6 | 91.28% | 63% | 0 | 0.39258 | 65.3912 | 1.7838 | 45.7924 | High | High | Medium | 40 | 39 | 25.6711
RINCON 1103 | SONOMA | 45.4469 | 162.6005 | 7799.7 | 94.74% | 89.85% | 0 | 0.54363 | 47.6367 | 1.7507 | 45.3385 | High | High | Medium | 41 | 38 | 25.8967
FORESTHILL 1102 | SIERRA | 29.7452 | 330.0154 | 9817.1 | 99.99% | 72.96% | 0 | 0.27132 | 102.1389 | 1.6253 | 45.0397 | Medium | High | Low | 42 | 36 | 27.7119
CLARKSVILLE 2104 | SIERRA | 65.9498 | 68.6078 | 5311.9 | 85.18% | 68.08% | 1 | 0.39857 | 47.6367 | 2.2889 | 43.4576 | High | High | Medium | 43 | 51 | 18.9864
TIGER CREEK 0201 | STOCKTON | 3.8998 | 49.9154 | 194.7 | 99.98% | 66.65% | 0 | 0.32439 | 65.3912 | 1.939 | 41.1306 | High | High | Medium | 44 | 48 | 21.2124
HIGHLANDS 1103 | HUMBOLDT | 111.6966 | 53.6769 | 6675.8 | 89.81% | 0% | 1 | 0.52144 | 35.3263 | 2.1747 | 40.059 | High | High | Medium | 45 | 52 | 18.4205
MORAGA 1105 | DIABLO | 9.2376 | 70.5672 | 1398 | 46.63% | 72.19% | 1 | 0.12304 | 102.1389 | 2.9115 | 36.5908 | Medium | High | High | 46 | 62 | 12.5675
SPANISH CREEK 4401 | NORTH VALLEY | 7.9163 | 52.7192 | 418 | 99.84% | 0% | 0 | 0.22342 | 85.4511 | 1.7867 | 34.1108 | Medium | High | Medium | 47 | 50 | 19.0912
CORRAL 1101 | STOCKTON | 121.6695 | 22.4845 | 4245 | 64.44% | 0% | 1 | 0.32273 | 47.6367 | 2.1917 | 33.6945 | High | High | Medium | 48 | 57 | 15.3737
BELL 1107 | SIERRA | 42.044 | 0.27863 | 14 | 83.68% | 0% | 1 | 0.27859 | 65.3912 | 1.8316 | 33.3663 | Medium | High | Medium | 49 | 53 | 18.2174
LAS GALLINAS A 1105 | NORTH BAY | 12.199 | 104.5283 | 2254.3 | 56.56% | 74.01% | 0 | 0.15567 | 65.3912 | 3.2653 | 33.238 | Medium | High | High | 50 | 69 | 10.1793
RACETRACK 1704 | YOSEMITE | 45.5677 | 97.5233 | 4506.3 | 98.62% | 0% | 1 | 0.3278 | 47.6367 | 2.0613 | 32.1874 | High | High | Medium | 51 | 56 | 15.6152
FULTON 1107 | SONOMA | 37.7898 | 9.2877 | 482 | 72.82% | 100% | 1 | 0.33283 | 47.6367 | 1.9961 | 31.647 | High | High | Medium | 52 | 55 | 15.8548
SAN RAMON 2108 | MISSION | 16.5718 | 120.3107 | 2100 | 94.94% | 100% | 0 | 0.21818 | 47.6367 | 2.8147 | 29.254 | Medium | High | High | 53 | 66 | 10.3932
PARADISE 1105 | NORTH VALLEY | 13.5303 | 193.9796 | 3835.5 | 68.43% | 100% | 1 | 0.15371 | 65.3912 | 2.9097 | 29.2471 | Medium | High | High | 54 | 70 | 10.0515
BEN LOMOND 1101 | CENTRAL COAST | 15.4019 | 408.4071 | 6255 | 100% | 100% | 0 | 0.31249 | 26.5534 | 3.5017 | 29.0556 | High | High | High | 55 | 75 | 8.2976
BONNIE NOOK 1101 | SIERRA | 24.4427 | 203.2987 | 4894.7 | 100% | 100% | 0 | 0.27204 | 85.4511 | 1.2213 | 28.3918 | Medium | High | Low | 56 | 43 | 23.2464
PARADISE 1102 | NORTH VALLEY | 15.078 | 209.2721 | 6818 | 46.28% | 100% | 0 | 0.13414 | 65.3912 | 3.0258 | 26.5402 | Medium | High | High | 57 | 73 | 8.7714
RINCON 1101 | SONOMA | 21.5282 | 78.8433 | 2741.8 | 61.91% | 82.79% | 0 | 0.22435 | 65.3912 | 1.7747 | 26.0369 | Medium | High | Medium | 58 | 60 | 14.6708
BRUNSWICK 1110 | SIERRA | 24.5712 | 64.2735 | 2208 | 71.53% | 0% | 0 | 0.2574 | 47.6367 | 2.1175 | 25.9649 | Medium | High | Medium | 59 | 64 | 12.2619
PETALUMA C 1108 | SONOMA | 73.6987 | 44.0843 | 5229.6 | 62.13% | 0% | 0 | 0.29967 | 65.3912 | 1.2912 | 25.3025 | High | High | Low | 60 | 49 | 19.5957
COTTONWOOD 1103 | NORTH VALLEY | 126.1767 | 75.3761 | 12151 | 78.27% | 0% | 1 | 0.57016 | 26.5534 | 1.5299 | 23.1621 | High | High | Low | 61 | 58 | 15.1397
PENNGROVE 1101 | SONOMA | 19.2167 | 0.1925 | 8 | 46.24% | 0% | 0 | 0.21065 | 65.3912 | 1.6185 | 22.2941 | Medium | High | Low | 62 | 61 | 13.7748
BELLEVUE 2103 | SONOMA | 28.6386 | 4.3285 | 306 | 40.51% | 33.51% | 0 | 0.19058 | 65.3912 | 1.6105 | 20.071 | Medium | High | Low | 63 | 63 | 12.4623
ROSSMOOR 1108 | DIABLO | 12.7515 | 167.0344 | 3459.5 | 61.57% | 55.79% | 0 | 0.099586 | 65.3912 | 2.9972 | 19.5179 | Low | High | High | 64 | 81 | 6.512
LAYTONVILLE 1101 | HUMBOLDT | 51.196 | 53.2824 | 4252.7 | 64.14% | 0% | 1 | 0.47695 | 65.3912 | 0.62176 | 19.3917 | High | High | Low | 65 | 33 | 31.1882
BUCKS CREEK 1103 | NORTH VALLEY | 11.1849 | 94.6553 | 1236 | 85.66% | 78.68% | 0 | 0.29586 | 85.4511 | 0.75889 | 19.1861 | Medium | High | Low | 66 | 40 | 25.2817
BELL 1110 | SIERRA | 0.30639 | 0.52971 | 6 | 2.705% | 0% | 0 | 0.10309 | 85.4511 | 2.0427 | 17.994 | Low | High | Medium | 67 | 72 | 8.809
CAMP EVERS 2104 | CENTRAL COAST | 27.8231 | 223.757 | 8211.5 | 75.82% | 98.69% | 0 | 0.49604 | 11.2183 | 3.2209 | 17.9234 | High | High | High | 68 | 85 | 5.5647
LAKEVILLE 1102 | SONOMA | 20.015 | 22.2542 | 1116.7 | 39.89% | 0% | 0 | 0.15735 | 65.3912 | 1.6756 | 17.2413 | Medium | High | Medium | 69 | 68 | 10.2894
WILLOW CREEK 1102 | HUMBOLDT | 9.6275 | 111.4738 | 1072.3 | 100% | 52.31% | 0 | 0.33882 | 65.3912 | 0.75226 | 16.667 | High | High | Low | 70 | 47 | 22.1559
BERKELEY F 1103 | EAST BAY | 1.8512 | 114.7029 | 715.7 | 29.67% | 100% | 0 | 0.07875 | 65.3912 | 3.1071 | 16.0001 | Low | High | High | 71 | 90 | 5.1495
PIKE CITY 1102 | SIERRA | 9.4149 | 129.3375 | 1217.7 | 100% | 100% | 0 | 0.2477 | 65.3912 | 0.96632 | 15.6516 | Medium | High | Low | 72 | 54 | 16.1971
PACIFICA 1101 | PENINSULA | 2.9053 | 0.10906 | 1 | 31.69% | 85.89% | 0 | 0.11762 | 47.6367 | 2.6487 | 14.8406 | Medium | High | High | 73 | 84 | 5.6029
VACA DIXON 1101 | SACRAMENTO | 0.82637 | 34.1483 | 320 | 8.819% | 0% | 0 | 0.098707 | 85.4511 | 1.7286 | 14.5797 | Low | High | Medium | 74 | 74 | 8.4346
CORNING 1101 | NORTH VALLEY | 50.3181 | 28.4447 | 4598 | 31.13% | 0% | 1 | 0.22804 | 35.3263 | 1.75 | 14.0977 | Medium | High | Medium | 75 | 76 | 8.0558
ALLEGHANY 1102 | SIERRA | 18.0939 | 139.6914 | 2490 | 100% | 100% | 1 | 0.22668 | 65.3912 | 0.94709 | 14.0387 | Medium | High | Low | 76 | 59 | 14.823
COTATI 1105 | SONOMA | 37.492 | 0.33385 | 44 | 28.45% | 0% | 0 | 0.15878 | 65.3912 | 1.2994 | 13.4908 | Medium | High | Low | 77 | 67 | 10.3826
VINEYARD 2108 | MISSION | 3.1184 | 96.4724 | 1296 | 23.21% | 100% | 1 | 0.075819 | 65.3912 | 2.5523 | 12.6542 | Low | High | High | 78 | 91 | 4.9579
PANORAMA 1101 | NORTH VALLEY | 11.7268 | 41.5904 | 1624 | 30.03% | 0% | 0 | 0.14741 | 35.3263 | 2.3726 | 12.3554 | Medium | High | Medium | 79 | 89 | 5.2075
GARCIA 0401 | HUMBOLDT | 2.4735 | 195.6161 | 483.7 | 100% | 0% | 0 | 0.18633 | 65.3912 | 1.0043 | 12.2362 | Medium | High | Low | 80 | 65 | 12.1844
PASO ROBLES 1103 | LOS PADRES | 39.5134 | 0.016068 | 1 | 63.49% | 0% | 1 | 0.19775 | 35.3263 | 1.726 | 12.0574 | Medium | High | Medium | 81 | 78 | 6.9856
BRIDGEVILLE 1101 | HUMBOLDT | 22.5401 | 93.278 | 2318.5 | 90.68% | 3.572% | 1 | 0.40628 | 85.4511 | 0.34191 | 11.8701 | High | High | Low | 82 | 31 | 34.7173
PUTAH CREEK 1102 | SACRAMENTO | 26.0826 | 58.6358 | 3017.2 | 50.69% | 0% | 0 | 0.20919 | 47.6367 | 1.1824 | 11.7826 | Medium | High | Low | 83 | 71 | 9.965
TASSAJARA 2108 | DIABLO | 1.2025 | 139.2395 | 2985.1 | 5.609% | 100% | 0 | 0.050229 | 85.4511 | 2.63 | 11.2884 | Low | High | High | 84 | 95 | 4.2922
SANTA ROSA A 1111 | SONOMA | 5.593 | 74.3305 | 1937.5 | 21.46% | 0.05081% | 0 | 0.1018 | 65.3912 | 1.6309 | 10.857 | Low | High | Low | 85 | 80 | 6.657
SONOMA 1106 | SONOMA | 1.1258 | 52.424 | 576.9 | 10.23% | 100% | 0 | 0.094417 | 47.6367 | 2.3971 | 10.7815 | Low | High | High | 86 | 94 | 4.4977
EAST QUINCY 1101 | NORTH VALLEY | 3.3666 | 62.1461 | 1079 | 19.39% | 17.1% | 0 | 0.10361 | 47.6367 | 2.1529 | 10.6262 | Low | High | Medium | 87 | 92 | 4.9357
BUELLTON 1102 | LOS PADRES | 15.6243 | 87.2194 | 2386.2 | 57.11% | 0% | 0 | 0.15557 | 47.6367 | 1.3574 | 10.059 | Medium | High | Low | 88 | 77 | 7.4107
JARVIS 1101 | MISSION | 0.45193 | 32.174 | 452 | 3.217% | 0% | 0 | 0.075561 | 47.6367 | 2.7563 | 9.9213 | Low | High | High | 89 | 102 | 3.5995
PEABODY 2113 | SACRAMENTO | 1.6686 | 4.5925 | 44 | 17.42% | 0% | 0 | 0.1134 | 47.6367 | 1.8105 | 9.7799 | Medium | High | Medium | 90 | 86 | 5.4018
PUTAH CREEK 1103 | SACRAMENTO | 3.6658 | 57.1436 | 2096.9 | 9.99% | 0% | 0 | 0.10677 | 65.3912 | 1.3925 | 9.7223 | Low | High | Low | 91 | 79 | 6.9821
MEADOW LANE 2106 | DIABLO | 0.20712 | 132.7473 | 3117 | 0.8821% | 100% | 0 | 0.03891 | 85.4511 | 2.7735 | 9.2215 | Low | High | High | 92 | 104 | 3.3249
SAN RAMON 2102 | MISSION | 1.535 | 2.1422 | 5 | 65.77% | 0% | 0 | 0.15119 | 19.9979 | 2.9688 | 8.9761 | Medium | High | High | 93 | 107 | 3.0235
RED BLUFF 1104 | NORTH VALLEY | 69.4411 | 32.3911 | 3034.7 | 74.12% | 0% | 0 | 0.32066 | 19.9979 | 1.3797 | 8.8475 | High | High | Low | 94 | 82 | 6.4126
RESEARCH 2102 | DIABLO | 1.2814 | 172.3046 | 3568.6 | 6.187% | 100% | 0 | 0.038888 | 85.4511 | 2.5899 | 8.6062 | Low | High | High | 95 | 105 | 3.323
COTATI 1102 | SONOMA | 15.7671 | 4.0219 | 141 | 44.97% | 0% | 0 | 0.15222 | 35.3263 | 1.5958 | 8.5813 | Medium | High | Low | 96 | 87 | 5.3775
FREMONT 1104 | MISSION | 2.6857 | 58.4301 | 1782.9 | 8.802% | 0% | 0 | 0.057909 | 65.3912 | 2.222 | 8.4141 | Low | High | Medium | 97 | 99 | 3.7867
MOLINO 1104 | SONOMA | 2.046 | 50.0802 | 3069.1 | 3.339% | 0% | 0 | 0.08155 | 65.3912 | 1.5463 | 8.2461 | Low | High | Low | 98 | 88 | 5.3326
UKIAH 1113 | HUMBOLDT | 6.3928 | 0.2519 | 4 | 40.26% | 0% | 0 | 0.17238 | 35.3263 | 1.3023 | 7.9304 | Medium | High | Low | 99 | 83 | 6.0894
SILVERADO 2103 | NORTH BAY | 9.8107 | 404.0574 | 13434.1 | 29.51% | 100% | 0 | 0.07608 | 47.6367 | 2.0797 | 7.5371 | Low | High | Medium | 100 | 101 | 3.6242
FULTON 1104 | SONOMA | 0.51664 | 11.6356 | 111 | 5.416% | 0% | 0 | 0.089226 | 47.6367 | 1.7166 | 7.2964 | Low | High | Medium | 101 | 96 | 4.2504
ROSSMOOR 1102 | DIABLO | 0.0028423 | 80.7015 | 115.5 | 0.1986% | 100% | 0 | 0.036984 | 65.3912 | 2.9669 | 7.1754 | Low | High | High | 102 | 109 | 2.4185
SAN RAMON 2101 | MISSION | 0.57317 | 20.5147 | 22 | 53.45% | 0% | 0 | 0.11568 | 19.9979 | 2.9563 | 6.839 | Medium | High | High | 103 | 110 | 2.3134
WYANDOTTE 1106 | NORTH VALLEY | 1.9508 | 33.0439 | 3091 | 2.086% | 0% | 0 | 0.11761 | 26.5534 | 2.1542 | 6.7275 | Medium | High | Medium | 104 | 106 | 3.123
VALLEY VIEW 1103 | EAST BAY | 0.34789 | 2.2678 | 41 | 1.924% | 100% | 0 | 0.057126 | 35.3263 | 3.2827 | 6.6246 | Low | High | High | 105 | 113 | 2.018
RESERVATION ROAD 1101 | CENTRAL COAST | 25.5742 | 163.2438 | 5215.1 | 80.05% | 0% | 1 | 0.21014 | 19.9979 | 1.5502 | 6.5145 | Medium | High | Low | 106 | 97 | 4.2025
PEABODY 2108 | SACRAMENTO | 0.82253 | 26.141 | 90.5 | 23.76% | 0% | 0 | 0.099538 | 35.3263 | 1.7932 | 6.3054 | Low | High | Medium | 107 | 103 | 3.5163
JAMESON 1102 | SACRAMENTO | 8.3727 | 110.5885 | 2231.1 | 41.5% | 0% | 0 | 0.11003 | 19.9979 | 2.8442 | 6.2585 | Low | High | High | 108 | 111 | 2.2004
MILPITAS 1108 | SAN JOSE | 0.28331 | 52.0143 | 691 | 2.133% | 0% | 0 | 0.047221 | 85.4511 | 1.432 | 5.7784 | Low | High | Low | 109 | 98 | 4.0351
JARVIS 1110 | MISSION | 0.094443 | 35.6649 | 214 | 1.574% | 0% | 0 | 0.048533 | 35.3263 | 3.0938 | 5.3042 | Low | High | High | 110 | 117 | 1.7145
SAN LUIS OBISPO 1108 | LOS PADRES | 1.2137 | 27.6591 | 435 | 7.717% | 0% | 0 | 0.073268 | 26.5534 | 2.3814 | 4.633 | Low | High | Medium | 111 | 114 | 1.9455
SANTA ROSA A 1108 | SONOMA | 0.13621 | 25.5587 | 183 | 1.902% | 0% | 0 | 0.051292 | 47.6367 | 1.6989 | 4.151 | Low | High | Medium | 112 | 108 | 2.4434
SEACLIFF 0402 | CENTRAL COAST | 0.96395 | 343.4682 | 533.2 | 62.09% | 63.7% | 0 | 0.032259 | 47.6367 | 2.6022 | 3.9989 | Low | High | High | 113 | 118 | 1.5367
CLEAR LAKE 1102 | HUMBOLDT | 3.7822 | 75.1062 | 2804 | 10.13% | 0% | 0 | 0.07809 | 26.5534 | 1.8761 | 3.8902 | Low | High | Medium | 114 | 112 | 2.0735
VACAVILLE 1109 | SACRAMENTO | 0.50066 | 60.9601 | 239 | 12.77% | 0% | 0 | 0.054836 | 35.3263 | 1.8589 | 3.6009 | Low | High | Medium | 115 | 115 | 1.9372
CAMP EVERS 2105 | CENTRAL COAST | 88.8213 | 214.3597 | 19560.9 | 97.34% | 98.85% | 1 | 0.99887 | 1 | 3.4754 | 3.4715 | High | Low | High | 116 | 123 | 0.99887
HORSESHOE 1104 | SIERRA | 1.0628 | 302.2247 | 3511.7 | 9.146% | 0% | 0 | 0.032736 | 35.3263 | 2.7724 | 3.2061 | Low | High | High | 117 | 120 | 1.1565
CAMP EVERS 2106 | CENTRAL COAST | 128.2102 | 99.8162 | 13913.2 | 91.98% | 98.66% | 1 | 0.99814 | 1 | 3.0301 | 3.0244 | High | Low | High | 118 | 124 | 0.99814
BIG BASIN 1101 | CENTRAL COAST | 56.1051 | 224.865 | 12617.6 | 99.99% | 100% | 0 | 0.97503 | 1 | 3.0189 | 2.9435 | High | Low | High | 119 | 129 | 0.97503
TASSAJARA 2106 | DIABLO | 0.13696 | 100.7735 | 314 | 4.395% | 0% | 0 | 0.043626 | 19.9979 | 3.279 | 2.8607 | Low | High | High | 120 | 145 | 0.87242
SAN MIGUEL 1105 | LOS PADRES | 0.96596 | 35.4496 | 719 | 4.763% | 0% | 0 | 0.095887 | 19.9979 | 1.399 | 2.6826 | Low | High | Low | 121 | 116 | 1.9175
BIG BASIN 1102 | CENTRAL COAST | 73.4523 | 685.0537 | 53077 | 94.8% | 94.78% | 1 | 0.99803 | 1 | 2.6614 | 2.6562 | High | Low | High | 122 | 125 | 0.99803
GOLDTREE 1105 | LOS PADRES | 7.1045 | 84.8773 | 1221.3 | 49.37% | 0% | 0 | 0.10706 | 11.2183 | 2.1281 | 2.5561 | Low | High | Medium | 123 | 119 | 1.2011
SILVERADO 2104 | NORTH BAY | 121.7013 | 168.4106 | 24366 | 84.12% | 64.08% | 1 | 0.93788 | 1 | 2.6952 | 2.5278 | High | Low | High | 124 | 137 | 0.93788
LOS GATOS 1106 | DE ANZA | 70.6799 | 255.34 | 18225.3 | 99.02% | 99.2% | 1 | 0.94316 | 1 | 2.548 | 2.4032 | High | Low | High | 125 | 136 | 0.94316
HALF MOON BAY 1103 | PENINSULA | 138.142 | 86.2493 | 15111.05 | 78.85% | 1.152% | 1 | 0.9705 | 1 | 2.4043 | 2.3334 | High | Low | High | 126 | 130 | 0.9705
ROB ROY 2104 | CENTRAL COAST | 102.3975 | 30.1005 | 4036.8 | 76.35% | 40.31% | 1 | 0.99347 | 1 | 2.3478 | 2.3325 | High | Low | Medium | 127 | 126 | 0.99347
PINE GROVE 1102 | STOCKTON | 177.6802 | 155.3906 | 27670.22 | 99.78% | 52.09% | 0 | 0.95059 | 1 | 2.448 | 2.3271 | High | Low | High | 128 | 133 | 0.95059
LOS GATOS 1107 | DE ANZA | 94.47 | 201.9318 | 19473.6 | 97.96% | 87.06% | 1 | 0.9298 | 1 | 2.42 | 2.2501 | High | Low | High | 129 | 138 | 0.9298
ROB ROY 2105 | CENTRAL COAST | 42.0766 | 296.2096 | 21276.5 | 58.58% | 71.18% | 1 | 0.84093 | 1 | 2.5914 | 2.1792 | High | Low | High | 130 | 154 | 0.84093
GOLDTREE 1107 | LOS PADRES | 1.1277 | 18.9072 | 69 | 30.9% | 0% | 0 | 0.085536 | 11.2183 | 2.2378 | 2.1473 | Low | High | Medium | 131 | 132 | 0.95957
SAN RAFAEL 1108 | NORTH BAY | 37.3748 | 160.2128 | 7528.8 | 79.53% | 97.7% | 1 | 0.54286 | 1 | 3.8165 | 2.0718 | High | Low | High | 132 | 196 | 0.54286
MONTE RIO 1111 | SONOMA | 58.0584 | 184.273 | 11931.2 | 89.67% | 78.57% | 0 | 0.86945 | 1 | 2.3469 | 2.0405 | High | Low | Medium | 133 | 147 | 0.86945
CLARKSVILLE 2110 | SIERRA | 0.17765 | 63.769 | 448.5 | 2.526% | 0% | 0 | 0.043535 | 19.9979 | 2.3396 | 2.0369 | Low | High | Medium | 134 | 146 | 0.8706
MORAGA 1102 | DIABLO | 3.3475 | 136.8517 | 1274.5 | 35.94% | 35.27% | 0 | 0.061173 | 11.2183 | 2.9081 | 1.9957 | Low | High | High | 135 | 168 | 0.68626
WEST POINT 1102 | STOCKTON | 230.9017 | 86.5887 | 22278.25 | 89.74% | 72% | 1 | 0.96739 | 1 | 2.0586 | 1.9915 | High | Low | Medium | 136 | 131 | 0.96739
ELECTRA 1102 | STOCKTON | 83.9596 | 134.607 | 2625.2 | 100% | 28.82% | 0 | 0.99252 | 1 | 1.9171 | 1.9028 | High | Low | Medium | 137 | 127 | 0.99252
OLEMA 1101 | NORTH BAY | 61.001 | 71.2227 | 8664.6 | 50.14% | 18.76% | 1 | 0.80779 | 1 | 2.3211 | 1.875 | High | Low | Medium | 138 | 156 | 0.80779
BIG RIVER 1101 | HUMBOLDT | 71.4583 | 101.7584 | 8757.6 | 83.03% | 0% | 1 | 0.88115 | 1 | 2.0103 | 1.7714 | High | Low | Medium | 139 | 142 | 0.88115
BEN LOMOND 0401 | CENTRAL COAST | 21.1277 | 328.4372 | 6922.7 | 100% | 100% | 0 | 0.50343 | 1 | 3.4434 | 1.7335 | High | Low | High | 140 | 211 | 0.50343
LAKEWOOD 2110 | DIABLO | 0.42837 | 128.5111 | 2940.5 | 1.872% | 100% | 0 | 0.04951 | 11.2183 | 3.0948 | 1.7189 | Low | High | High | 141 | 194 | 0.55542
BANGOR 1101 | NORTH VALLEY | 197.9775 | 62.6538 | 14347.5 | 86.45% | 0.7535% | 1 | 0.75918 | 1 | 2.2417 | 1.7019 | High | Low | Medium | 142 | 162 | 0.75918
ALTO 1125 | NORTH BAY | 37.0494 | 129.6468 | 5802.2 | 82.78% | 77.44% | 1 | 0.52563 | 1 | 3.2314 | 1.6985 | High | Low | High | 143 | 199 | 0.52563
GREEN VALLEY 2101 | CENTRAL COAST | 43.1017 | 158.6756 | 24887.3 | 27.48% | 83.01% | 1 | 0.85678 | 1 | 1.9816 | 1.6978 | High | Low | Medium | 144 | 150 | 0.85678
BRYANT 0402 | DIABLO | 1.2282 | 150.9373 | 1168.3 | 15.87% | 0% | 0 | 0.037528 | 14.9507 | 2.9149 | 1.6355 | Low | High | High | 145 | 192 | 0.56107
CALISTOGA 1101 | NORTH BAY | 91.75 | 165.8288 | 18630.5 | 81.67% | 85.96% | 1 | 0.84787 | 1 | 1.8867 | 1.5996 | High | Low | Medium | 146 | 152 | 0.84787
CLARKSVILLE 2109 | SIERRA | 5.0217 | 328.5061 | 4024.2 | 40.99% | 37.96% | 0 | 0.044201 | 14.9507 | 2.3528 | 1.5548 | Low | High | Medium | 147 | 170 | 0.66083
BELLEVUE 1102 | SONOMA | 0.13708 | 0.045922 | 2 | 0.3148% | 0% | 0 | 0.056099 | 19.9979 | 1.3772 | 1.5451 | Low | High | Low | 148 | 121 | 1.1219
PARADISE 1103 | NORTH VALLEY | 41.0163 | 140.6142 | 6365.1 | 90.61% | 65.43% | 1 | 0.54801 | 1 | 2.7927 | 1.5304 | High | Low | High | 149 | 195 | 0.54801
WOODACRE 1102 | NORTH BAY | 32.7082 | 184.4969 | 5733 | 100% | 49.48% | 0 | 0.39711 | 1 | 3.8248 | 1.5189 | High | Low | High | 150 | 246 | 0.39711
APPLE HILL 2102 | SIERRA | 336.4685 | 64.7636 | 22557.2 | 96.6% | 31.51% | 1 | 0.98048 | 1 | 1.5121 | 1.4826 | High | Low | Low | 151 | 128 | 0.98048
CURTIS 1702 | YOSEMITE | 111.3399 | 13.2129 | 1563.61 | 94.08% | 22.51% | 1 | 0.51745 | 1 | 2.8567 | 1.4782 | High | Low | High | 152 | 202 | 0.51745
MIRABEL 1102 | SONOMA | 36.4964 | 215.8593 | 12523.9 | 62.9% | 86.71% | 1 | 0.64889 | 1 | 2.2561 | 1.464 | High | Low | Medium | 153 | 172 | 0.64889
PLACERVILLE 2106 | SIERRA | 276.5055 | 0.40168 | 111 | 100% | 68.24% | 1 | 0.858 | 1 | 1.6591 | 1.4235 | High | Low | Low | 154 | 148 | 0.858
WYANDOTTE 1107 | NORTH VALLEY | 100.7594 | 72.3283 | 10326.7 | 70.57% | 2.23% | 1 | 0.52043 | 1 | 2.7345 | 1.4231 | High | Low | High | 155 | 201 | 0.52043
FORT BRAGG A 1102 | HUMBOLDT | 64.6396 | 143.498 | 11604.9 | 79.93% | 0% | 1 | 0.9048 | 1 | 1.5679 | 1.4186 | High | Low | Low | 156 | 141 | 0.9048
SARATOGA 1107 | DE ANZA | 33.2409 | 226.5397 | 10305.7 | 73.07% | 48.48% | 0 | 0.53711 | 1 | 2.6156 | 1.4049 | High | Low | High | 157 | 197 | 0.53711
DIAMOND SPRINGS 1106 | SIERRA | 109.9116 | 247.6294 | 30350.4 | 89.68% | 0% | 0 | 0.87448 | 1 | 1.5783 | 1.3801 | High | Low | Low | 158 | 144 | 0.87448
NEWBURG 1132 | HUMBOLDT | 2.1979 | 0.043554 | 1 | 9.573% | 0% | 0 | 0.074726 | 14.9507 | 1.235 | 1.3797 | Low | High | Low | 159 | 122 | 1.1172
OCEANO 1104 | LOS PADRES | 87.6347 | 97.8791 | 11070.7 | 77.48% | 5.106% | 1 | 0.66048 | 1 | 2.0827 | 1.3756 | High | Low | Medium | 160 | 171 | 0.66048
HALSEY 1101 | SIERRA | 72.6826 | 281.9943 | 20821.7 | 98.44% | 0% | 1 | 0.69793 | 1 | 1.9508 | 1.3615 | High | Low | Medium | 161 | 167 | 0.69793
PUEBLO 2103 | NORTH BAY | 47.1879 | 166.9581 | 13136 | 59.98% | 82.28% | 1 | 0.64259 | 1 | 2.1163 | 1.3599 | High | Low | Medium | 162 | 175 | 0.64259
FORT ROSS 1121 | SONOMA | 93.2788 | 115.3428 | 10761 | 99.98% | 23.24% | 0 | 0.78851 | 1 | 1.6844 | 1.3282 | High | Low | Medium | 163 | 159 | 0.78851
NARROWS 2102 | SIERRA | 95.95 | 97.6526 | 11434.5 | 81.94% | 0% | 0 | 0.59701 | 1 | 2.209 | 1.3188 | High | Low | Medium | 164 | 182 | 0.59701
PAUL SWEET 2106 | CENTRAL COAST | 37.5441 | 251.8505 | 13205.3 | 71.6% | 84.81% | 1 | 0.46936 | 1 | 2.7736 | 1.3018 | High | Low | High | 165 | 226 | 0.46936
CURTIS 1703 | YOSEMITE | 195.8329 | 2.5397 | 510.69 | 97.39% | 8.933% | 1 | 0.62304 | 1 | 2.059 | 1.2828 | High | Low | Medium | 166 | 177 | 0.62304
KANAKA 1101 | NORTH VALLEY | 92.5364 | 7.1724 | 663.5 | 100% | 69.28% | 1 | 0.6185 | 1 | 2.0603 | 1.2743 | High | Low | Medium | 167 | 178 | 0.6185
CURTIS 1704 | YOSEMITE | 75.6221 | 24.9869 | 1911.21 | 98.87% | 32.9% | 0 | 0.51399 | 1 | 2.4706 | 1.2698 | High | Low | High | 168 | 204 | 0.51399
WYANDOTTE 1103 | NORTH VALLEY | 84.2744 | 37.6969 | 3685 | 86.21% | 80.44% | 1 | 0.48799 | 1 | 2.5396 | 1.2393 | High | Low | High | 169 | 218 | 0.48799
KONOCTI 1102 | HUMBOLDT | 119.7343 | 3.8196 | 562 | 81.38% | 49.82% | 1 | 0.5617 | 1 | 2.206 | 1.2391 | High | Low | Medium | 170 | 191 | 0.5617
PINE GROVE 1101 | STOCKTON | 73.0596 | 140.622 | 10247.6 | 100% | 0% | 0 | 0.56237 | 1 | 2.1837 | 1.2281 | High | Low | Medium | 171 | 190 | 0.56237
PINECREST 0401 | YOSEMITE | 1.957 | 323.5331 | 1031.1 | 61.41% | 49.36% | 0 | 0.058551 | 14.9507 | 1.3947 | 1.2209 | Low | High | Low | 172 | 143 | 0.87538
COLUMBIA HILL 1101 | SIERRA | 90.9452 | 2.545 | 230.7 | 100% | 81.67% | 1 | 0.74379 | 1 | 1.6251 | 1.2088 | High | Low | Low | 173 | 164 | 0.74379
GARBERVILLE 1102 | HUMBOLDT | 124.8867 | 8.5849 | 1151.7 | 93.09% | 0% | 1 | 0.9451 | 1 | 1.2368 | 1.1689 | High | Low | Low | 174 | 135 | 0.9451
BIG BEND 1101 | NORTH VALLEY | 56.7162 | 126.4735 | 7308.5 | 98.15% | 73.8% | 1 | 0.48296 | 1 | 2.4179 | 1.1677 | High | Low | High | 175 | 220 | 0.48296
MENLO 1103 | PENINSULA | 39.9636 | 46.9951 | 2660.2 | 70.6% | 0% | 1 | 0.57213 | 1 | 2.0361 | 1.1649 | High | Low | Medium | 176 | 188 | 0.57213
CURTIS 1705 | YOSEMITE | 84.6611 | 15.4976 | 1385.3 | 94.71% | 17.45% | 0 | 0.42065 | 1 | 2.7589 | 1.1605 | High | Low | High | 177 | 241 | 0.42065
MOUNTAIN QUARRIES 2101 | SIERRA | 224.6216 | 0.72682 | 164 | 99.55% | 11.18% | 1 | 0.60078 | 1 | 1.9176 | 1.1521 | High | Low | Medium | 178 | 181 | 0.60078
PARADISE 1104 | NORTH VALLEY | 37.9174 | 166.7696 | 8590 | 73.61% | 96.14% | 1 | 0.38991 | 1 | 2.9513 | 1.1508 | High | Low | High | 179 | 249 | 0.38991
FORT BRAGG A 1101 | HUMBOLDT | 70.4672 | 18.613 | 1514.3 | 86.61% | 0% | 1 | 0.77591 | 1 | 1.4603 | 1.133 | High | Low | Low | 180 | 161 | 0.77591
WISE 1102 | SIERRA | 114.9602 | 105.724 | 12547.7 | 96.86% | 0% | 1 | 0.62726 | 1 | 1.7985 | 1.1281 | High | Low | Medium | 181 | 176 | 0.62726
PERRY 1101 | LOS PADRES | 67.3591 | 69.6209 | 5626.6 | 83.35% | 9.487% | 1 | 0.49166 | 1 | 2.2943 | 1.128 | High | Low | Medium | 182 | 216 | 0.49166
STANISLAUS 1701 | YOSEMITE | 45.3745 | 171.8414 | 7829.23 | 99.59% | 52.72% | 0 | 0.43032 | 1 | 2.5728 | 1.1071 | High | Low | High | 183 | 238 | 0.43032
ELECTRA 1101 | STOCKTON | 83.2829 | 63.2177 | 5412.5 | 97.27% | 0% | 1 | 0.51415 | 1 | 2.1328 | 1.0966 | High | Low | Medium | 184 | 203 | 0.51415
BIG TREES 0402 | CENTRAL COAST | 16.1073 | 434.8182 | 7278.9 | 96.22% | 98.33% | 0 | 0.31612 | 1 | 3.4226 | 1.082 | High | Low | High | 185 | 298 | 0.31612
ELK 1101 | HUMBOLDT | 76.2893 | 43.1063 | 4571.1 | 71.94% | 0% | 1 | 0.80648 | 1 | 1.3373 | 1.0785 | High | Low | Low | 186 | 157 | 0.80648
GRASS VALLEY 1103 | SIERRA | 86.1203 | 94.5478 | 8361.3 | 97.38% | 0% | 0 | 0.52251 | 1 | 2.0518 | 1.0721 | High | Low | Medium | 187 | 200 | 0.52251
MONTICELLO 1101 | NORTH BAY | 109.7815 | 85.5856 | 10807.2 | 86.94% | 0% | 1 | 0.60413 | 1 | 1.7603 | 1.0634 | High | Low | Medium | 188 | 180 | 0.60413
MARTELL 1101 | STOCKTON | 73.5469 | 102.7281 | 8640.4 | 87.44% | 0% | 1 | 0.48855 | 1 | 2.176 | 1.0631 | High | Low | Medium | 189 | 217 | 0.48855
ALTO 1124 | NORTH BAY | 30.5495 | 331.9086 | 11694.3 | 86.71% | 100% | 0 | 0.3069 | 1 | 3.4528 | 1.0597 | High | Low | High | 190 | 304 | 0.3069
OREGON TRAIL 1103 | NORTH VALLEY | 116.3748 | 66.5339 | 7999.7 | 96.79% | 0% | 1 | 0.5573 | 1 | 1.8758 | 1.0454 | High | Low | Medium | 191 | 193 | 0.5573
VOLTA 1102 | NORTH VALLEY | 128.1663 | 157.4847 | 20468.8 | 98.61% | 66.76% | 1 | 0.85728 | 1 | 1.2176 | 1.0438 | High | Low | Low | 192 | 149 | 0.85728
OAKHURST 1103 | YOSEMITE | 128.8237 | 0.19057 | 25 | 98.2% | 69.49% | 1 | 0.64287 | 1 | 1.6217 | 1.0425 | High | Low | Low | 193 | 174 | 0.64287
FRUITLAND 1142 | HUMBOLDT | 59.3604 | 139.7042 | 9479.1 | 87.49% | 0% | 1 | 0.8564 | 1 | 1.2147 | 1.0403 | High | Low | Low | 194 | 151 | 0.8564
DOBBINS 1101 | SIERRA | 80.2916 | 165.4492 | 13557.7 | 97.98% | 35.11% | 0 | 0.58245 | 1 | 1.7818 | 1.0378 | High | Low | Medium | 195 | 184 | 0.58245
LAURELES 1111 | CENTRAL COAST | 105.4438 | 167.2407 | 17867.5 | 98.7% | 5.882% | 1 | 0.75833 | 1 | 1.3268 | 1.0062 | High | Low | Low | 196 | 163 | 0.75833
EMERALD LAKE 0402 | PENINSULA | 7.9738 | 1.2715 | 12 | 84.49% | 0% | 0 | 0.22432 | 1 | 4.4394 | 0.99583 | Medium | Low | High | 197 | 364 | 0.22432
GARBERVILLE 1101 | HUMBOLDT | 84.4121 | 19.9292 | 3227.6 | 52.12% | 0% | 1 | 0.81691 | 1 | 1.2027 | 0.98246 | High | Low | Low | 198 | 155 | 0.81691
COARSEGOLD 2104 | YOSEMITE | 248.3114 | 15.5338 | 4129.1 | 93.42% | 1.219% | 1 | 0.58022 | 1 | 1.6845 | 0.97737 | High | Low | Medium | 199 | 185 | 0.58022
MARIPOSA 2101 | YOSEMITE | 261.2126 | 13.1443 | 3482.59 | 98.59% | 34.76% | 1 | 0.78157 | 1 | 1.2358 | 0.96586 | High | Low | Low | 200 | 160 | 0.78157
OAKLAND X 1104 | EAST BAY | 12.9831 | 115.3827 | 1626.7 | 92.09% | 92.36% | 0 | 0.32976 | 1 | 2.8926 | 0.95388 | High | Low | High | 201 | 287 | 0.32976
WILLITS 1103 | HUMBOLDT | 141.581 | 101.7383 | 15609.56 | 92.28% | 34.63% | 1 | 0.94802 | 1 | 0.99475 | 0.94305 | High | Low | Low | 202 | 134 | 0.94802
STELLING 1110 | DE ANZA | 36.507 | 0.39919 | 20 | 72.87% | 36.18% | 0 | 0.42956 | 1 | 2.1628 | 0.92904 | High | Low | Medium | 203 | 239 | 0.42956
OTTER 1101 | CENTRAL COAST | 24.3091 | 146.8885 | 3957.5 | 90.23% | 61.35% | 1 | 0.49892 | 1 | 1.837 | 0.91651 | High | Low | Medium | 204 | 213 | 0.49892
HIGGINS 1103 | SIERRA | 75.3648 | 0.18705 | 15 | 93.98% | 0% | 1 | 0.46833 | 1 | 1.9391 | 0.90816 | High | Low | Medium | 205 | 227 | 0.46833
STILLWATER 1102 | NORTH VALLEY | 77.8002 | 106.8573 | 8440.1 | 98.5% | 0% | 0 | 0.49291 | 1 | 1.8073 | 0.89082 | High | Low | Medium | 206 | 215 | 0.49291
VIEJO 2201 | CENTRAL COAST | 15.761 | 271.832 | 5043 | 84.96% | 0% | 1 | 0.31308 | 1 | 2.8441 | 0.89045 | High | Low | High | 207 | 301 | 0.31308
RACETRACK 1703 | YOSEMITE | 56.2669 | 0.38757 | 24 | 90.87% | 2.511% | 1 | 0.37971 | 1 | 2.3259 | 0.88318 | High | Low | Medium | 208 | 256 | 0.37971
KESWICK 1101 | NORTH VALLEY | 50.8481 | 20.8645 | 1092 | 97.15% | 93.98% | 0 | 0.37921 | 1 | 2.294 | 0.86992 | High | Low | Medium | 209 | 257 | 0.37921
AUBERRY 1101 | FRESNO | 243.3723 | 57.7119 | 14182.11 | 99.04% | 14.06% | 1 | 0.84142 | 1 | 1.032 | 0.86836 | High | Low | Low | 210 | 153 | 0.84142
COARSEGOLD 2102 | YOSEMITE | 69.5656 | 83.9889 | 5882.5 | 99.32% | 79.94% | 0 | 0.57582 | 1 | 1.5055 | 0.86691 | High | Low | Low | 211 | 187 | 0.57582
FROGTOWN 1701 | STOCKTON | 70.5021 | 3.62 | 260.4 | 98.01% | 11.51% | 0 | 0.35892 | 1 | 2.4075 | 0.86409 | High | Low | High | 212 | 270 | 0.35892
CLARK ROAD 1102 | NORTH VALLEY | 117.7302 | 0.21135 | 29 | 85.8% | 28.19% | 1 | 0.37067 | 1 | 2.2993 | 0.85229 | High | Low | Medium | 213 | 260 | 0.37067
DUNBAR 1102 | SONOMA | 48.6409 | 0.94499 | 59 | 77.91% | 12.82% | 1 | 0.36183 | 1 | 2.3412 | 0.84711 | High | Low | Medium | 214 | 266 | 0.36183
ATASCADERO 1101 | LOS PADRES | 48.0205 | 175.2943 | 11084.4 | 75.94% | 30.41% | 1 | 0.4038 | 1 | 2.0754 | 0.83804 | High | Low | Medium | 215 | 244 | 0.4038
WILLOW CREEK 1103 | HUMBOLDT | 84.7815 | 171.8351 | 14798.7 | 98.44% | 0.5494% | 1 | 0.90591 | 1 | 0.92024 | 0.83365 | High | Low | Low | 216 | 140 | 0.90591
HALF MOON BAY 1101 | PENINSULA | 30.1489 | 94.6023 | 4633.8 | 61.55% | 62.01% | 1 | 0.28848 | 1 | 2.889 | 0.83344 | Medium | Low | High | 217 | 315 | 0.28848
SAN RAFAEL 1107 | NORTH BAY | 20.6975 | 176.315 | 4719.9 | 77.32% | 89.65% | 0 | 0.22296 | 1 | 3.7235 | 0.83019 | Medium | Low | High | 218 | 367 | 0.22296
LUCERNE 1106 | HUMBOLDT | 35.3522 | 69.4187 | 3263.9 | 75.19% | 0% | 1 | 0.33667 | 1 | 2.4545 | 0.82635 | High | Low | High | 219 | 282 | 0.33667
MORGAN HILL 2111 | SAN JOSE | 51.2335 | 89.7023 | 6563.3 | 70.02% | 29.88% | 1 | 0.44389 | 1 | 1.8491 | 0.82077 | High | Low | Medium | 220 | 234 | 0.44389
CLAYTON 2212 | DIABLO | 47.4011 | 1.4599 | 84 | 82.38% | 50.62% | 0 | 0.33511 | 1 | 2.4353 | 0.81609 | High | Low | High | 221 | 285 | 0.33511
HIGGINS 1109 | SIERRA | 140.5007 | 11.1731 | 1582.3 | 99.21% | 0% | 1 | 0.47196 | 1 | 1.7034 | 0.80392 | High | Low | Medium | 222 | 225 | 0.47196
HIGGINS 1110 | SIERRA | 51.0959 | 357.0037 | 20576.8 | 88.65% | 0% | 0 | 0.45253 | 1 | 1.7562 | 0.79475 | High | Low | Medium | 223 | 232 | 0.45253
HALSEY 1102 | SIERRA | 57.8088 | 0.48483 | 33 | 84.93% | 0% | 1 | 0.43624 | 1 | 1.8153 | 0.79189 | High | Low | Medium | 224 | 235 | 0.43624
OAKLAND X 1106 | EAST BAY | 16.5816 | 141.7435 | 3332.9 | 70.52% | 43.14% | 0 | 0.28371 | 1 | 2.791 | 0.79183 | Medium | Low | High | 225 | 318 | 0.28371
STILLWATER 1101 | NORTH VALLEY | 34.9345 | 118.2002 | 4354.2 | 94.83% | 0% | 0 | 0.40123 | 1 | 1.9609 | 0.78677 | High | Low | Medium | 226 | 245 | 0.40123
CASTRO VALLEY 1108 | MISSION | 22.9915 | 6.5541 | 168 | 89.7% | 69.23% | 0 | 0.28196 | 1 | 2.7723 | 0.78169 | Medium | Low | High | 227 | 320 | 0.28196
OAKLAND K 1102 | EAST BAY | 15.6371 | 153.4327 | 2398 | 100% | 100% | 1 | 0.27319 | 1 | 2.8557 | 0.78016 | Medium | Low | High | 228 | 326 | 0.27319
GIRVAN 1101 | NORTH VALLEY | 105.6311 | 61.117 | 6709.25 | 96.22% | 40.56% | 0 | 0.47263 | 1 | 1.6353 | 0.77289 | High | Low | Low | 229 | 224 | 0.47263
SHINGLE SPRINGS 2105 | SIERRA | 31.7746 | 67.1179 | 2235.2 | 95.41% | 85.39% | 0 | 0.33572 | 1 | 2.293 | 0.76981 | High | Low | Medium | 230 | 283 | 0.33572
TEMPLETON 2110 | LOS PADRES | 131.8393 | 37.268 | 6618 | 74.24% | 24.45% | 1 | 0.48709 | 1 | 1.5652 | 0.76238 | High | Low | Low | 231 | 219 | 0.48709
BEAR VALLEY 2105 | YOSEMITE | 133.2806 | 5.2436 | 697.9 | 100% | 9.068% | 1 | 0.56239 | 1 | 1.351 | 0.75981 | High | Low | Low | 232 | 189 | 0.56239
DESCHUTES 1101 | NORTH VALLEY | 109.6858 | 74.8939 | 9783.9 | 83.96% | 5.359% | 1 | 0.49693 | 1 | 1.5211 | 0.75589 | High | Low | Low | 233 | 214 | 0.49693
VOLTA 1101 | NORTH VALLEY | 153.0474 | 52.4817 | 8055.6 | 99.71% | 6.239% | 0 | 0.72021 | 1 | 1.0395 | 0.74866 | High | Low | Low | 234 | 165 | 0.72021
BIG MEADOWS 2101 | NORTH VALLEY | 57.1862 | 64.6614 | 5021 | 73.65% | 0% | 0 | 0.39165 | 1 | 1.9107 | 0.74835 | High | Low | Medium | 235 | 247 | 0.39165
NARROWS 2101 | SIERRA | 61.1189 | 1.0306 | 63 | 99.99% | 0% | 0 | 0.38331 | 1 | 1.9498 | 0.74739 | High | Low | Medium | 236 | 253 | 0.38331
SPRUCE 0401 | EAST BAY | 4.123 | 93.7879 | 386.5 | 100% | 23.86% | 0 | 0.18844 | 1 | 3.9252 | 0.73968 | Medium | Low | High | 237 | 406 | 0.18844
EL CERRITO G 1105 | EAST BAY | 18.498 | 89.1521 | 2163 | 76.24% | 31.71% | 0 | 0.20445 | 1 | 3.6127 | 0.73862 | Medium | Low | High | 238 | 385 | 0.20445
WEIMAR 1101 | SIERRA | 74.3116 | 6.8492 | 509 | 100% | 0% | 0 | 0.44451 | 1 | 1.6561 | 0.73613 | High | Low | Low | 239 | 233 | 0.44451
SAN LUIS OBISPO 1107 | LOS PADRES | 47.5671 | 128.564 | 6830.9 | 89.53% | 58.19% | 0 | 0.34103 | 1 | 2.1508 | 0.73348 | High | Low | Medium | 240 | 278 | 0.34103
ATASCADERO 1103 | LOS PADRES | 93.8432 | 106.8884 | 14248.6 | 70.4% | 41.58% | 0 | 0.50034 | 1 | 1.4655 | 0.73326 | High | Low | Low | 241 | 212 | 0.50034
OREGON TRAIL 1102 | NORTH VALLEY | 43.9113 | 52.4522 | 2580.5 | 89.26% | 0% | 0 | 0.34709 | 1 | 2.11 | 0.73237 | High | Low | Medium | 242 | 275 | 0.34709
GUALALA 1112 | HUMBOLDT | 46.2029 | 5.6547 | 265 | 98.59% | 0% | 1 | 0.50419 | 1 | 1.452 | 0.73207 | High | Low | Low | 243 | 209 | 0.50419
GUALALA 1111 | HUMBOLDT | 35.7279 | 5.0047 | 188.5 | 94.86% | 0% | 0 | 0.51384 | 1 | 1.4212 | 0.73027 | High | Low | Low | 244 | 205 | 0.51384
HOOPA 1101 | HUMBOLDT | 103.3689 | 45.8592 | 6148.1 | 77.1% | 2.741% | 1 | 0.92115 | 1 | 0.7914 | 0.729 | High | Low | Low | 245 | 139 | 0.92115
BOLINAS 1101 | NORTH BAY | 36.2161 | 152.1348 | 7849 | 70.2% | 79.57% | 1 | 0.24155 | 1 | 3.0084 | 0.72668 | Medium | Low | High | 246 | 352 | 0.24155
HAMILTON BRANCH 1101 | NORTH VALLEY | 26.7473 | 33.2133 | 1140 | 77.93% | 0% | 0 | 0.29319 | 1 | 2.4741 | 0.72539 | Medium | Low | High | 247 | 311 | 0.29319
SAND CREEK 1103 | FRESNO | 149.2192 | 22.7349 | 3443.9 | 98.51% | 0% | 0 | 0.50802 | 1 | 1.4193 | 0.72104 | High | Low | Low | 248 | 208 | 0.50802
TEMPLETON 2111 | LOS PADRES | 45.7387 | 252.6481 | 16081.1 | 71.86% | 0.6756% | 0 | 0.43041 | 1 | 1.6439 | 0.70754 | High | Low | Low | 249 | 237 | 0.43041
ANNAPOLIS 1101 | HUMBOLDT | 51.2424 | 153.2835 | 7851.9 | 100% | 0% | 0 | 0.69873 | 1 | 1.0113 | 0.7066 | High | Low | Low | 250 | 166 | 0.69873
SANTA ROSA A 1104 | SONOMA | 44.3006 | 126.4689 | 7084.8 | 79.08% | 85.89% | 0 | 0.38767 | 1 | 1.8117 | 0.70235 | High | Low | Medium | 251 | 250 | 0.38767
PHILO 1102 | HUMBOLDT | 87.2659 | 0.078916 | 8 | 86.08% | 0% | 1 | 0.6461 | 1 | 1.0843 | 0.70058 | High | Low | Low | 252 | 173 | 0.6461
ALHAMBRA 1105 | DIABLO | 37.4334 | 94.8612 | 4257 | 83.42% | 1.365% | 1 | 0.27084 | 1 | 2.579 | 0.69848 | Medium | Low | High | 253 | 327 | 0.27084
SOBRANTE 1102 | DIABLO | 27.4867 | 152.1974 | 4215 | 99.25% | 6.682% | 0 | 0.2569 | 1 | 2.6964 | 0.6927 | Medium | Low | High | 254 | 338 | 0.2569
DEL MONTE 2104 | CENTRAL COAST | 60.5977 | 162.8902 | 12940 | 76.28% | 0% | 0 | 0.38584 | 1 | 1.7925 | 0.69161 | High | Low | Medium | 255 | 252 | 0.38584
OLETA 1101 | STOCKTON | 89.0724 | 16.341 | 1902.7 | 76.5% | 6.991% | 0 | 0.30681 | 1 | 2.2468 | 0.68934 | High | Low | Medium | 256 | 305 | 0.30681
OLETA 1102 | STOCKTON | 58.6793 | 93.0145 | 9270.4 | 58.88% | 1.085% | 0 | 0.33146 | 1 | 2.0749 | 0.68774 | High | Low | Medium | 257 | 286 | 0.33146
CORRAL 1102 | STOCKTON | 49.8209 | 0.031174 | 2 | 77.66% | 0% | 1 | 0.28896 | 1 | 2.3748 | 0.68624 | Medium | Low | Medium | 258 | 313 | 0.28896
DESCHUTES 1104 | NORTH VALLEY | 80.0303 | 55.7135 | 7294.1 | 61.13% | 0% | 1 | 0.36212 | 1 | 1.8914 | 0.68492 | High | Low | Medium | 259 | 265 | 0.36212
PEORIA 1701 | YOSEMITE | 80.3858 | 2.7552 | 234 | 94.65% | 0% | 1 | 0.33799 | 1 | 2.0046 | 0.67751 | High | Low | Medium | 260 | 281 | 0.33799
PLACERVILLE 1112 | SIERRA | 27.7534 | 0.6342 | 19 | 92.64% | 0.05594% | 1 | 0.36226 | 1 | 1.862 | 0.67452 | High | Low | Medium | 261 | 264 | 0.36226
FELTON 0401 | CENTRAL COAST | 2.2987 | 63.2591 | 162.5 | 89.49% | 100% | 0 | 0.19109 | 1 | 3.5174 | 0.67216 | Medium | Low | High | 262 | 403 | 0.19109
WEIMAR 1102 | SIERRA | 23.0263 | 2.3451 | 54 | 100% | 0% | 0 | 0.3916 | 1 | 1.7125 | 0.67062 | High | Low | Medium | 263 | 248 | 0.3916
POINT ARENA 1101 | HUMBOLDT | 43.137 | 151.6844 | 10042.9 | 65.15% | 0% | 0 | 0.59484 | 1 | 1.0925 | 0.64989 | High | Low | Low | 264 | 183 | 0.59484
GIRVAN 1102 | NORTH VALLEY | 44.1977 | 51.5354 | 3919.7 | 58.11% | 74.49% | 1 | 0.3243 | 1 | 2.0036 | 0.64977 | High | Low | Medium | 265 | 289 | 0.3243
GANSNER 1101 | NORTH VALLEY | 38.7574 | 38.6947 | 1867 | 80.33% | 1.24% | 1 | 0.35862 | 1 | 1.8076 | 0.64822 | High | Low | Medium | 266 | 271 | 0.35862
MIDDLETOWN 1102 | HUMBOLDT | 39.5462 | 48.716 | 2738.7 | 70.34% | 0.6611% | 0 | 0.27646 | 1 | 2.3228 | 0.64216 | Medium | Low | Medium | 267 | 322 | 0.27646
OTTER 1102 | CENTRAL COAST | 53.8017 | 139.1766 | 7616.4 | 98.31% | 6.912% | 1 | 0.47954 | 1 | 1.332 | 0.63873 | High | Low | Low | 268 | 221 | 0.47954
WOODSIDE 1104 | PENINSULA | 13.9759 | 265.3381 | 9679.4 | 38.31% | 28.63% | 0 | 0.16337 | 1 | 3.8964 | 0.63657 | Medium | Low | High | 269 | 432 | 0.16337
WYANDOTTE 1109 | NORTH VALLEY | 52.4768 | 57.8365 | 7001.3 | 43.35% | 0% | 0 | 0.25504 | 1 | 2.495 | 0.63633 | Medium | Low | High | 270 | 342 | 0.25504
ANTLER 1101 | NORTH VALLEY | 60.0715 | 11.1936 | 704 | 95.51% | 6.842% | 1 | 0.46349 | 1 | 1.3699 | 0.63494 | High | Low | Low | 271 | 229 | 0.46349
SHADY GLEN 1101 | SIERRA | 41.667 | 138.676 | 6500.3 | 88.89% | 1.898% | 0 | 0.35351 | 1 | 1.7857 | 0.63127 | High | Low | Medium | 272 | 273 | 0.35351
OREGON TRAIL 1104 | NORTH VALLEY | 45.1213 | 128.9869 | 7087.6 | 82.12% | 0% | 1 | 0.3403 | 1 | 1.8465 | 0.62838 | High | Low | Medium | 273 | 279 | 0.3403
PEORIA 1705 | YOSEMITE | 59.0992 | 0.069953 | 5 | 82.68% | 0% | 1 | 0.29754 | 1 | 2.1069 | 0.62688 | High | Low | Medium | 274 | 309 | 0.29754
MARIPOSA 2102 | YOSEMITE | 245.1385 | 6.3765 | 1661.56 | 94.08% | 22.38% | 1 | 0.50363 | 1 | 1.2175 | 0.61319 | High | Low | Low | 275 | 210 | 0.50363
EMERALD LAKE 0401 | PENINSULA | 15.5314 | 136.1011 | 2877.3 | 73.47% | 27.29% | 0 | 0.15761 | 1 | 3.8666 | 0.60944 | Medium | Low | High | 276 | 439 | 0.15761
OCEANO 1102 | LOS PADRES | 36.4985 | 170.6492 | 9154 | 68.04% | 0% | 1 | 0.30224 | 1 | 2.0104 | 0.60762 | High | Low | Medium | 277 | 307 | 0.30224
PLACERVILLE 1110 | SIERRA | 34.3071 | 3.7768 | 132 | 98.16% | 4.685% | 1 | 0.34903 | 1 | 1.7162 | 0.59902 | High | Low | Medium | 278 | 274 | 0.34903
NORTH BRANCH 1101 | STOCKTON | 59.7793 | 24.8834 | 2229.9 | 66.71% | 0% | 0 | 0.25616 | 1 | 2.3237 | 0.59524 | Medium | Low | Medium | 279 | 340 | 0.25616
CALISTOGA 1102 | NORTH BAY | 23.8756 | 172.9752 | 7974 | 51.79% | 92.34% | 1 | 0.2553 | 1 | 2.3058 | 0.58866 | Medium | Low | Medium | 280 | 341 | 0.2553
DUNBAR 1103 | SONOMA | 30.1397 | 7.1433 | 388 | 55.49% | 92.61% | 0 | 0.23869 | 1 | 2.4649 | 0.58835 | Medium | Low | High | 281 | 357 | 0.23869
OILFIELDS 1103 | CENTRAL COAST | 115.2449 | 27.8747 | 4007.6 | 80.16% | 0% | 1 | 0.36659 | 1 | 1.5686 | 0.57502 | High | Low | Low | 282 | 261 | 0.36659
CLAYTON 2213 | DIABLO | 3.8789 | 30.8603 | 191.3 | 62.57% | 0% | 0 | 0.2147 | 1 | 2.6752 | 0.57436 | Medium | Low | High | 283 | 375 | 0.2147
NORTH DUBLIN 2103 | MISSION | 18.9008 | 73.7274 | 1635 | 85.23% | 0.2897% | 0 | 0.20907 | 1 | 2.7439 | 0.57368 | Medium | Low | High | 284 | 380 | 0.20907
MENLO 1102 | PENINSULA | 27.048 | 142.3143 | 9172.5 | 41.97% | 0.9515% | 0 | 0.24042 | 1 | 2.3772 | 0.57153 | Medium | Low | Medium | 285 | 353 | 0.24042
FORT SEWARD 1121 | HUMBOLDT | 38.0083 | 88.0582 | 4240.9 | 78.92% | 0% | 0 | 0.51133 | 1 | 1.1175 | 0.57139 | High | Low | Low | 286 | 207 | 0.51133
BUCKS CREEK 1101 | NORTH VALLEY | 20.005 | 20.9987 | 420 | 100% | 23.08% | 0 | 0.27046 | 1 | 2.0923 | 0.56587 | Medium | Low | Medium | 287 | 328 | 0.27046
SAN JOAQUIN #2 1103 | YOSEMITE | 82.7368 | 75.5396 | 6261.9 | 99.81% | 11.29% | 0 | 0.45754 | 1 | 1.2364 | 0.56572 | High | Low | Low | 288 | 230 | 0.45754
NOTRE DAME 1104 | NORTH VALLEY | 27.4274 | 59.5612 | 2333 | 70.02% | 63.41% | 1 | 0.22274 | 1 | 2.5324 | 0.56407 | Medium | Low | High | 289 | 368 | 0.22274
OAK 0401 | EAST BAY | 4.3198 | 91.1427 | 493 | 79.86% | 0% | 0 | 0.13597 | 1 | 4.1407 | 0.563 | Medium | Low | High | 290 | 460 | 0.13597
MORAGA 1104 | DIABLO | 16.8835 | 142.8466 | 3110 | 77.55% | 2.528% | 0 | 0.19957 | 1 | 2.8198 | 0.56276 | Medium | Low | High | 291 | 393 | 0.19957
REDBUD 1101 | HUMBOLDT | 47.7517 | 2.8354 | 199.5 | 67.87% | 51.84% | 0 | 0.2763 | 1 | 2.0254 | 0.55961 | Medium | Low | Medium | 292 | 323 | 0.2763
JESSUP 1101 | NORTH VALLEY | 65.0048 | 68.0599 | 5453 | 81.13% | 0.4339% | 1 | 0.36291 | 1 | 1.5369 | 0.55775 | High | Low | Low | 293 | 262 | 0.36291
OAKLAND K 1104 | EAST BAY | 15.128 | 222.4716 | 3360.9 | 100% | 68.04% | 0 | 0.1901 | 1 | 2.8976 | 0.55083 | Medium | Low | High | 294 | 404 | 0.1901
APPLE HILL 1103 | SIERRA | 58.8848 | 16.9136 | 1213.13 | 82.1% | 28.25% | 1 | 0.35946 | 1 | 1.5186 | 0.54587 | High | Low | Low | 295 | 268 | 0.35946
SARATOGA 1105 | DE ANZA | 9.8848 | 0.84274 | 14 | 59.5% | 0% | 0 | 0.20932 | 1 | 2.5772 | 0.53948 | Medium | Low | High | 296 | 379 | 0.20932
CABRILLO 1103 | LOS PADRES | 53.8552 | 28.4006 | 2761.5 | 55.39% | 0% | 1 | 0.21429 | 1 | 2.5143 | 0.5388 | Medium | Low | High | 297 | 377 | 0.21429
GEYSERVILLE 1101 | SONOMA | 69.1228 | 71.1042 | 9890.2 | 49.69% | 0% | 1 | 0.38011 | 1 | 1.4138 | 0.53738 | High | Low | Low | 298 | 255 | 0.38011
EDES 1112 | EAST BAY | 15.8364 | 103.0601 | 1771.5 | 92.13% | 4.695% | 0 | 0.22246 | 1 | 2.4124 | 0.53666 | Medium | Low | High | 299 | 369 | 0.22246
DUNBAR 1101 | SONOMA | 40.6225 | 4.3182 | 280 | 62.65% | 58.74% | 0 | 0.26425 | 1 | 2.0305 | 0.53655 | Medium | Low | Medium | 300 | 333 | 0.26425
NORTH DUBLIN 2101 | MISSION | 3.6193 | 9.24 | 40 | 83.61% | 0% | 0 | 0.19317 | 1 | 2.7631 | 0.53375 | Medium | Low | High | 301 | 401 | 0.19317
SONOMA 1103 | SONOMA | 13.7402 | 0.07711 | 2 | 52.98% | 100% | 0 | 0.24035 | 1 | 2.2177 | 0.53302 | Medium | Low | Medium | 302 | 354 | 0.24035
ARCATA 1122 | HUMBOLDT | 20.5455 | 163.2894 | 11115.5 | 30.18% | 0% | 1 | 0.2388 | 1 | 2.2303 | 0.5326 | Medium | Low | Medium | 303 | 355 | 0.2388
DUNLAP 1103 | FRESNO | 70.8013 | 75.8838 | 5398.1 | 99.53% | 0% | 0 | 0.53449 | 1 | 0.99361 | 0.53107 | High | Low | Low | 304 | 198 | 0.53449
SAN LUIS OBISPO 1104 | LOS PADRES | 50.6677 | 83.4369 | 7050 | 59.97% | 44.06% | 1 | 0.26401 | 1 | 2.0087 | 0.53031 | Medium | Low | Medium | 305 | 334 | 0.26401
CAYETANO 2109 | MISSION | 35.4993 | 13.1584 | 659 | 70.88% | 35.99% | 1 | 0.22211 | 1 | 2.3856 | 0.52985 | Medium | Low | Medium | 306 | 370 | 0.22211
DIAMOND SPRINGS 1103 | SIERRA | 33.9542 | 144.2323 | 7367.5 | 66.47% | 27.9% | 1 | 0.28798 | 1 | 1.8342 | 0.5282 | Medium | Low | Medium | 307 | 316 | 0.28798
FRENCH GULCH 1102 | NORTH VALLEY | 22.3415 | 79.3501 | 1770 | 100% | 13.78% | 0 | 0.32691 | 1 | 1.6111 | 0.5267 | High | Low | Low | 308 | 288 | 0.32691
WILLOW CREEK 1101 | HUMBOLDT | 47.0234 | 171.5062 | 9921.6 | 81.29% | 61.34% | 1 | 0.80386 | 1 | 0.65498 | 0.52651 | High | Low | Low | 309 | 158 | 0.80386
VIEJO 2202 | CENTRAL COAST | 14.2864 | 4.3971 | 206 | 30.49% | 0% | 1 | 0.19509 | 1 | 2.695 | 0.52576 | Medium | Low | High | 310 | 400 | 0.19509
FRENCH GULCH 1101 | NORTH VALLEY | 18.8732 | 86.0309 | 1622.5 | 100% | 0% | 0 | 0.33821 | 1 | 1.5534 | 0.52539 | High | Low | Low | 311 | 280 | 0.33821
PHILO 1101 | HUMBOLDT | 73.7188 | 0.24667 | 23 | 79.06% | 0% | 1 | 0.47445 | 1 | 1.1048 | 0.5242 | High | Low | Low | 312 | 222 | 0.47445
CLARKSVILLE 2103 | SIERRA | 33.626 | 35.6071 | 1778.5 | 67.32% | 59.03% | 1 | 0.27558 | 1 | 1.8952 | 0.52227 | Medium | Low | Medium | 313 | 324 | 0.27558
WALDO 0402 | EAST BAY | 3.0716 | 42.0757 | 216 | 59.83% | 0% | 0 | 0.13537 | 1 | 3.8554 | 0.5219 | Medium | Low | High | 314 | 461 | 0.13537
BROWNS VALLEY 1101 | SIERRA | 37.7491 | 47.3498 | 3021.8 | 59.15% | 0% | 1 | 0.26976 | 1 | 1.9284 | 0.5202 | Medium | Low | Medium | 315 | 330 | 0.26976
SAN JOAQUIN #3 1103 | YOSEMITE | 54.5173 | 108.2787 | 5905.4 | 99.96% | 58.36% | 0 | 0.46504 | 1 | 1.1123 | 0.51727 | High | Low | Low | 316 | 228 | 0.46504
CURTIS 1701 | YOSEMITE | 13.4152 | 1.2008 | 24.9 | 64.69% | 0% | 0 | 0.20009 | 1 | 2.5773 | 0.51568 | Medium | Low | High | 317 | 390 | 0.20009
HATTON 1102 | CENTRAL COAST | 10.7188 | 3.349 | 75 | 47.86% | 0% | 0 | 0.23467 | 1 | 2.1903 | 0.51402 | Medium | Low | Medium | 318 | 360 | 0.23467
CLAY 1101 | STOCKTON | 26.5733 | 64.6332 | 2666.8 | 64.4% | 0% | 0 | 0.23659 | 1 | 2.1529 | 0.50936 | Medium | Low | Medium | 319 | 358 | 0.23659
AUBERRY 1102 | FRESNO | 127.9128 | 35.9165 | 4605.1 | 99.76% | 0% | 1 | 0.45711 | 1 | 1.1132 | 0.50884 | High | Low | Low | 320 | 231 | 0.45711
LOS GATOS 1108 | DE ANZA | 4.2689 | 49.7215 | 303.5 | 69.94% | 12.91% | 0 | 0.17492 | 1 | 2.9083 | 0.50871 | Medium | Low | High | 321 | 421 | 0.17492
CASTRO VALLEY 1109 | MISSION | 5.7287 | 0.12153 | 1 | 69.62% | 49.57% | 0 | 0.18308 | 1 | 2.7674 | 0.50666 | Medium | Low | High | 322 | 414 | 0.18308
BELL 1108 | SIERRA | 66.6823 | 0.074134 | 6 | 82.39% | 0% | 0 | 0.28608 | 1 | 1.7453 | 0.49931 | Medium | Low | Medium | 323 | 317 | 0.28608
WYANDOTTE 1105 | NORTH VALLEY | 20.9182 | 45.9165 | 1101 | 87.24% | 0.3284% | 1 | 0.19533 | 1 | 2.5559 | 0.49925 | Medium | Low | High | 324 | 399 | 0.19533
LOW GAP 1101 | HUMBOLDT | 71.107 | 2.249 | 164 | 97.51% | 0% | 0 | 0.57857 | 1 | 0.86126 | 0.4983 | High | Low | Low | 325 | 186 | 0.57857
MARTELL 1103 | STOCKTON | 20.372 | 30.2173 | 893.9 | 68.87% | 0% | 0 | 0.22697 | 1 | 2.1763 | 0.49395 | Medium | Low | Medium | 326 | 362 | 0.22697
LAYTONVILLE 1102 | HUMBOLDT | 111.1176 | 22.1416 | 2687.9 | 91.53% | 2.684% | 1 | 0.66913 | 1 | 0.73466 | 0.49159 | High | Low | Low | 327 | 169 | 0.66913
JESSUP 1102 | NORTH VALLEY | 51.0333 | 64.1412 | 5572 | 58.75% | 0% | 0 | 0.32267 | 1 | 1.521 | 0.49077 | High | Low | Low | 328 | 292 | 0.32267
FORT BRAGG A 1104 | HUMBOLDT | 25.9146 | 98.8899 | 3769 | 67.99% | 0% | 0 | 0.31064 | 1 | 1.5649 | 0.48612 | High | Low | Low | 329 | 302 | 0.31064
RIDGE 0401 | EAST BAY | 2.662 | 150.4115 | 400.2 | 100% | 0% | 0 | 0.14736 | 1 | 3.2957 | 0.48566 | Medium | Low | High | 330 | 449 | 0.14736
HIGHLANDS 1102 | HUMBOLDT | 35.815 | 38.7995 | 2335.5 | 59.5% | 23.07% | 0 | 0.20558 | 1 | 2.3412 | 0.48129 | Medium | Low | Medium | 331 | 384 | 0.20558
WHITMORE 1101 | NORTH VALLEY | 92.5696 | 60.8238 | 5627.04 | 100% | 35.14% | 0 | 0.51164 | 1 | 0.93924 | 0.48055 | High | Low | Low | 332 | 206 | 0.51164
BELL 1109 | SIERRA | 13.433 | 0.4486 | 8 | 75.33% | 0% | 0 | 0.25005 | 1 | 1.9218 | 0.48055 | Medium | Low | Medium | 333 | 344 | 0.25005
RALSTON 1101 | PENINSULA | 8.6411 | 0.69774 | 10 | 60.29% | 0% | 0 | 0.1857 | 1 | 2.5532 | 0.47412 | Medium | Low | High | 334 | 408 | 0.1857
SAN RAFAEL 1109 | NORTH BAY | 10.8025 | 134.9188 | 3525.9 | 41.34% | 0% | 0 | 0.1313 | 1 | 3.5715 | 0.46894 | Medium | Low | High | 335 | 465 | 0.1313
CENTERVILLE 1101 | NORTH VALLEY | 36.3928 | 0 | 5396.6 | 0% | 96.65% | 1 | 0.17029 | 1 | 2.7454 | 0.46751 | Medium | Low | High | 336 | 425 | 0.17029
BUELLTON 1101 | LOS PADRES | 77.7776 | 37.5644 | 3943 | 74.1% | 2.521% | 1 | 0.2926 | 1 | 1.5921 | 0.46585 | Medium | Low | Low | 337 | 312 | 0.2926
COTTONWOOD 1102 | NORTH VALLEY | 59.3351 | 49.5356 | 4117.5 | 71.38% | 0% | 1 | 0.31871 | 1 | 1.4441 | 0.46026 | High | Low | Low | 338 | 294 | 0.31871
SUNOL 1101 | MISSION | 34.5067 | 79.6588 | 4405.1 | 62.4% | 34.83% | 0 | 0.2083 | 1 | 2.2066 | 0.45963 | Medium | Low | Medium | 339 | 381 | 0.2083
PAUL SWEET 2104 | CENTRAL COAST | 17.3184 | 177.171 | 6289.5 | 48.78% | 100% | 0 | 0.17204 | 1 | 2.666 | 0.45867 | Medium | Low | High | 340 | 423 | 0.17204
REDBUD 1102 | HUMBOLDT | 27.3864 | 27.6857 | 1619 | 46.83% | 5.522% | 0 | 0.19984 | 1 | 2.2912 | 0.45789 | Medium | Low | Medium | 341 | 392 | 0.19984
MORAGA 1101 | DIABLO | 18.7524 | 231.2458 | 4714.5 | 91.98% | 84.96% | 0 | 0.15195 | 1 | 2.9884 | 0.45408 | Medium | Low | High | 342 | 442 | 0.15195
LUCERNE 1103 | HUMBOLDT | 31.8489 | 0.075386 | 4 | 60.02% | 0% | 0 | 0.21456 | 1 | 2.0942 | 0.44933 | Medium | Low | Medium | 343 | 376 | 0.21456
HARRIS 1109 | HUMBOLDT | 13.0569 | 90.5332 | 4585.5 | 25.78% | 0% | 0 | 0.16591 | 1 | 2.7044 | 0.4487 | Medium | Low | High | 344 | 428 | 0.16591
LOS GATOS 1101 | DE ANZA | 9.9179 | 0.4769 | 10 | 47.3% | 0% | 0 | 0.16551 | 1 | 2.6755 | 0.44281 | Medium | Low | High | 345 | 429 | 0.16551
MORGAN HILL 2105 | SAN JOSE | 49.4076 | 60.3391 | 4988.4 | 59.76% | 26.88% | 1 | 0.24901 | 1 | 1.7734 | 0.4416 | Medium | Low | Medium | 346 | 347 | 0.24901
VALLEY VIEW 1106 | EAST BAY | 8.5618 | 3.2562 | 68 | 41% | 0% | 0 | 0.13774 | 1 | 3.1897 | 0.43936 | Medium | Low | High | 347 | 458 | 0.13774
COTATI 1103 | SONOMA | 82.6114 | 2.9792 | 332 | 74.13% | 0% | 1 | 0.33531 | 1 | 1.31 | 0.43924 | High | Low | Low | 348 | 284 | 0.33531
CRESCENT MILLS 2101 | NORTH VALLEY | 43.6463 | 62.7115 | 4950 | 55.3% | 0% | 0 | 0.28184 | 1 | 1.5412 | 0.43438 | Medium | Low | Low | 349 | 321 | 0.28184
STAFFORD 1102 | NORTH BAY | 21.3206 | 92.1724 | 3462.9 | 56.75% | 4.149% | 1 | 0.17116 | 1 | 2.5212 | 0.43153 | Medium | Low | High | 350 | 424 | 0.17116
INDIAN FLAT 1104 | YOSEMITE | 16.7358 | 46.4525 | 780.7 | 99.58% | 0% | 0 | 0.31705 | 1 | 1.3602 | 0.43126 | High | Low | Low | 351 | 295 | 0.31705
BURNEY 1101 | NORTH VALLEY | 51.5022 | 48.9487 | 2928.5 | 86.08% | 0% | 0 | 0.38258 | 1 | 1.1254 | 0.43057 | High | Low | Low | 352 | 254 | 0.38258
CLOVERDALE 1102 | SONOMA | 80.9762 | 48.6873 | 5260.3 | 74.95% | 58.94% | 0 | 0.41198 | 1 | 1.0437 | 0.42998 | High | Low | Low | 353 | 242 | 0.41198
TASSAJARA 2104 | DIABLO | 7.2573 | 128.4661 | 1249.5 | 74.62% | 25.11% | 0 | 0.14744 | 1 | 2.8959 | 0.42696 | Medium | Low | High | 354 | 448 | 0.14744
DUNLAP 1102 | FRESNO | 55.7604 | 79.3908 | 4445.3 | 99.59% | 0% | 1 | 0.47294 | 1 | 0.89144 | 0.42159 | High | Low | Low | 355 | 223 | 0.47294
SWIFT 2110 | SAN JOSE | 83.3204 | 0.95201 | 79 | 100% | 0% | 0 | 0.36227 | 1 | 1.1587 | 0.41975 | High | Low | Low | 356 | 263 | 0.36227
PUEBLO 1104 | NORTH BAY | 30.8506 | 212.953 | 11215.7 | 58.58% | 0% | 1 | 0.19921 | 1 | 2.1042 | 0.41918 | Medium | Low | Medium | 357 | 394 | 0.19921
COTTONWOOD 1101 | NORTH VALLEY | 70.4171 | 16.6714 | 1666 | 70.47% | 0% | 1 | 0.34668 | 1 | 1.202 | 0.4167 | High | Low | Low | 358 | 276 | 0.34668
CEDAR CREEK 1101 | NORTH VALLEY | 110.9 | 74 | 8214 | 99.91% | 16.25% | 0 | 0.60431 | 1 | 0.68853 | 0.41609 | High | Low | Low | 359 | 179 | 0.60431
GREENBRAE 1102 | NORTH BAY | 7.1787 | 133.0435 | 1734.9 | 55.05% | 100% | 0 | 0.126 | 1 | 3.2978 | 0.41551 | Medium | Low | High | 360 | 473 | 0.126
DEL MONTE 2103 | CENTRAL COAST | 12.8349 | 162.3707 | 5647.4 | 36.9% | 0% | 0 | 0.17404 | 1 | 2.3874 | 0.41549 | Medium | Low | High | 361 | 422 | 0.17404
SAN RAMON 2107 | MISSION | 13.2045 | 78.7075 | 2176.6 | 47.75% | 97.71% | 0 | 0.14562 | 1 | 2.8353 | 0.41289 | Medium | Low | High | 362 | 452 | 0.14562
SAN LEANDRO U 1109 | MISSION | 12.917 | 50.8296 | 1000.5 | 65.62% | 7.254% | 0 | 0.21802 | 1 | 1.8932 | 0.41274 | Medium | Low | Medium | 363 | 372 | 0.21802
CASTRO VALLEY 1106 | MISSION | 19.2033 | 76.1582 | 3117.1 | 46.92% | 76.11% | 0 | 0.14998 | 1 | 2.707 | 0.406 | Medium | Low | High | 364 | 445 | 0.14998
HIGHLANDS 1104 | HUMBOLDT | 11.8923 | 0.23778 | 7 | 40.4% | 0% | 0 | 0.16341 | 1 | 2.4665 | 0.40305 | Medium | Low | High | 365 | 431 | 0.16341
CALPELLA 1101 | HUMBOLDT | 72.0108 | 65.4062 | 6000.3 | 78.5% | 5.015% | 1 | 0.38639 | 1 | 1.0408 | 0.40215 | High | Low | Low | 366 | 251 | 0.38639
LAS GALLINAS A 1106 | NORTH BAY | 4.998 | 42.8648 | 675 | 31.74% | 39.74% | 0 | 0.1226 | 1 | 3.2664 | 0.40047 | Medium | Low | High | 367 | 475 | 0.1226
RALSTON 1102 | PENINSULA | 3.2655 | 0.09353 | 1 | 30.54% | 0% | 0 | 0.11938 | 1 | 3.3318 | 0.39776 | Medium | Low | High | 368 | 488 | 0.11938
HIGGINS 1107 | SIERRA | 16.8285 | 2.8864 | 94 | 51.67% | 0% | 0 | 0.22612 | 1 | 1.7548 | 0.39679 | Medium | Low | Medium | 369 | 363 | 0.22612
SAN LUIS OBISPO 1101 | LOS PADRES | 27.4591 | 61.777 | 2353.4 | 72.08% | 37.5% | 0 | 0.20369 | 1 | 1.9385 | 0.39484 | Medium | Low | Medium | 370 | 386 | 0.20369
MAPLE CREEK 1101 | HUMBOLDT | 9.8748 | 0.39268 | 13 | 29.83% | 0% | 0 | 0.2005 | 1 | 1.9619 | 0.39336 | Medium | Low | Medium | 371 | 389 | 0.2005
SANTA MARIA 1108 | LOS PADRES | 73.0359 | 41.6543 | 3939.8 | 77.22% | 60.25% | 1 | 0.3454 | 1 | 1.1384 | 0.39321 | High | Low | Low | 372 | 277 | 0.3454
SAN JOAQUIN #3 1101 | YOSEMITE | 24.668 | 172.7328 | 4259.4 | 100% | 94.57% | 0 | 0.28198 | 1 | 1.3766 | 0.38818 | Medium | Low | Low | 373 | 319 | 0.28198
WYANDOTTE 1110 | NORTH VALLEY | 13.8013 | 69.0873 | 2755.5 | 34.6% | 0% | 0 | 0.12906 | 1 | 2.989 | 0.38577 | Medium | Low | High | 374 | 470 | 0.12906
SAN CARLOS 1104 | PENINSULA | 8.3888 | 79.6449 | 1757.5 | 38.02% | 0% | 0 | 0.10317 | 1 | 3.7132 | 0.38309 | Low | Low | High | 375 | 527 | 0.10317
SARATOGA 1106 | DE ANZA | 13.394 | 184.9638 | 4935 | 50.2% | 4.959% | 0 | 0.12542 | 1 | 3.0513 | 0.38269 | Medium | Low | High | 376 | 474 | 0.12542
MERCED FALLS 1102 | YOSEMITE | 120.7817 | 9.0416 | 1726.7 | 63.25% | 0% | 1 | 0.25626 | 1 | 1.4882 | 0.38136 | Medium | Low | Low | 377 | 339 | 0.25626
TAR FLAT 0402 | YOSEMITE | 5.4986 | 73.2444 | 485.2 | 83% | 23.55% | 0 | 0.16545 | 1 | 2.2965 | 0.37995 | Medium | Low | Medium | 378 | 430 | 0.16545
TAMARACK 1101 | SIERRA | 16.4477 | 84.0596 | 1509.4 | 91.6% | 0% | 0 | 0.41125 | 1 | 0.9203 | 0.37847 | High | Low | Low | 379 | 243 | 0.41125
PETALUMA C 1109 | SONOMA | 47.7751 | 37.3436 | 2497.5 | 71.44% | 0% | 0 | 0.24335 | 1 | 1.5475 | 0.37658 | Medium | Low | Low | 380 | 351 | 0.24335
PASO ROBLES 1104 | LOS PADRES | 37.5318 | 122.939 | 8272.1 | 55.78% | 0% | 0 | 0.23873 | 1 | 1.5762 | 0.3763 | Medium | Low | Low | 381 | 356 | 0.23873
PLACERVILLE 1111 | SIERRA | 13.2951 | 129.5107 | 2399.6 | 71.76% | 0% | 0 | 0.18947 | 1 | 1.9744 | 0.3741 | Medium | Low | Medium | 382 | 405 | 0.18947
SOBRANTE 1101 | DIABLO | 15.9136 | 157.462 | 3382 | 74.09% | 0.7306% | 0 | 0.13531 | 1 | 2.7637 | 0.37397 | Medium | Low | High | 383 | 462 | 0.13531
PALO SECO 0401 | EAST BAY | 4.7078 | 182.9243 | 867.5 | 99.27% | 18.75% | 0 | 0.12716 | 1 | 2.9264 | 0.37214 | Medium | Low | High | 384 | 471 | 0.12716
WISHON 1101 | YOSEMITE | 7.7822 | 27.8513 | 216.8 | 99.97% | 51.22% | 0 | 0.32238 | 1 | 1.1392 | 0.36726 | High | Low | Low | 385 | 293 | 0.32238
SUMMIT 1102 | SIERRA | 5.1556 | 81.6334 | 421 | 99.97% | 0% | 0 | 0.24499 | 1 | 1.4982 | 0.36703 | Medium | Low | Low | 386 | 350 | 0.24499
ZACA 1102 | LOS PADRES | 64.9618 | 56.5808 | 4540 | 80.96% | 36.17% | 1 | 0.31531 | 1 | 1.1576 | 0.365 | High | Low | Low | 387 | 299 | 0.31531
SONOMA 1102 | SONOMA | 5.4359 | 0.43651 | 8 | 29.66% | 100% | 0 | 0.14754 | 1 | 2.4622 | 0.36326 | Medium | Low | High | 388 | 447 | 0.14754
UPPER LAKE 1101 | HUMBOLDT | 53.0863 | 91.0265 | 7983.8 | 60.53% | 1.399% | 0 | 0.31613 | 1 | 1.1472 | 0.36268 | High | Low | Low | 389 | 297 | 0.31613
SOBRANTE 1103 | DIABLO | 3.7247 | 134.2739 | 695.7 | 71.89% | 15.89% | 0 | 0.1215 | 1 | 2.9819 | 0.36231 | Medium | Low | High | 390 | 480 | 0.1215
GRAYS FLAT 0401 | NORTH VALLEY | 10.7057 | 75.9501 | 813 | 100% | 0% | 0 | 0.29592 | 1 | 1.2228 | 0.36185 | Medium | Low | Low | 391 | 310 | 0.29592
MENDOCINO 1101 | HUMBOLDT | 40.8852 | 96.2417 | 8109.4 | 48.52% | 30.15% | 0 | 0.30054 | 1 | 1.2002 | 0.36072 | High | Low | Low | 392 | 308 | 0.30054
TIVY VALLEY 1107 | FRESNO | 118.6456 | 22.2285 | 3890.3 | 67.79% | 0% | 1 | 0.32304 | 1 | 1.1078 | 0.35787 | High | Low | Low | 393 | 291 | 0.32304
LAURELES 1112 | CENTRAL COAST | 28.5944 | 269.5468 | 9658.4 | 79.8% | 0% | 0 | 0.19579 | 1 | 1.8213 | 0.35659 | Medium | Low | Medium | 394 | 397 | 0.19579
VACAVILLE 1108 | SACRAMENTO | 28.2253 | 17.9844 | 872.1 | 58.21% | 0% | 0 | 0.22757 | 1 | 1.5528 | 0.35338 | Medium | Low | Low | 395 | 361 | 0.22757
TEJON 1102 | KERN | 32.2059 | 17.6568 | 1105.5 | 51.44% | 0% | 0 | 0.18524 | 1 | 1.9041 | 0.35273 | Medium | Low | Medium | 396 | 410 | 0.18524
SPRUCE 0402 | EAST BAY | 1.905 | 68.1248 | 244.5 | 53.08% | 19.04% | 0 | 0.095782 | 1 | 3.6749 | 0.35199 | Low | Low | High | 397 | 554 | 0.095782
EL CERRITO G 1113 | EAST BAY | 0.20892 | 22.2103 | 212 | 2.189% | 0% | 0 | 0.093665 | 1 | 3.7545 | 0.35167 | Low | Low | High | 398 | 560 | 0.093665
IONE 1101 | STOCKTON | 15.6336 | 68.2479 | 1976.2 | 53.99% | 0% | 0 | 0.18325 | 1 | 1.9134 | 0.35064 | Medium | Low | Medium | 399 | 413 | 0.18325
CABRILLO 1104 | LOS PADRES | 30.2749 | 13.5021 | 1030.25 | 39.68% | 0% | 1 | 0.13172 | 1 | 2.6604 | 0.35043 | Medium | Low | High | 400 | 464 | 0.13172
FOOTHILL 1101 | LOS PADRES | 17.8092 | 85.4395 | 3318.4 | 45.85% | 0% | 0 | 0.13992 | 1 | 2.5032 | 0.35024 | Medium | Low | High | 401 | 455 | 0.13992
MORRO BAY 1102 | LOS PADRES | 21.4127 | 32.5118 | 1876.5 | 37.1% | 18.72% | 1 | 0.11824 | 1 | 2.9365 | 0.3472 | Medium | Low | High | 402 | 493 | 0.11824
SAN RAFAEL 1105 | NORTH BAY | 4.1168 | 79.9253 | 1839.6 | 17.89% | 0% | 0 | 0.10483 | 1 | 3.311 | 0.34708 | Low | Low | High | 403 | 522 | 0.10483
SONOMA 1104 | SONOMA | 19.5383 | 0.053642 | 3 | 34.94% | 0% | 1 | 0.15663 | 1 | 2.1994 | 0.34448 | Medium | Low | Medium | 404 | 441 | 0.15663
KING CITY 1103 | CENTRAL COAST | 17.5881 | 88.4434 | 2428 | 64.07% | 0% | 0 | 0.20663 | 1 | 1.6667 | 0.34439 | Medium | Low | Low | 405 | 383 | 0.20663
KERCKHOFF 1101 | YOSEMITE | 34.5924 | 140.6862 | 4795.4 | 100% | 0% | 0 | 0.26925 | 1 | 1.2691 | 0.3417 | Medium | Low | Low | 406 | 332 | 0.26925
PUEBLO 1105 | NORTH BAY | 23.9073 | 36.3841 | 2583.5 | 33.67% | 0% | 0 | 0.1782 | 1 | 1.9065 | 0.33975 | Medium | Low | Medium | 407 | 417 | 0.1782
LAS AROMAS 0401 | DIABLO | 5.9862 | 211.8395 | 1323.7 | 95.8% | 0% | 0 | 0.11738 | 1 | 2.8362 | 0.33291 | Medium | Low | High | 408 | 495 | 0.11738
VALLEY VIEW 1105 | EAST BAY | 5.4093 | 0.69571 | 13 | 28.95% | 0% | 0 | 0.1088 | 1 | 3.0206 | 0.32865 | Low | Low | High | 409 | 513 | 0.1088
VIEJO 2203 | CENTRAL COAST | 3.5033 | 132.9307 | 1846.5 | 25.22% | 0% | 0 | 0.12942 | 1 | 2.5288 | 0.32727 | Medium | Low | High | 410 | 469 | 0.12942
TAR FLAT 0401 | YOSEMITE | 3.5092 | 140.2515 | 519.8 | 94.68% | 18.46% | 0 | 0.13406 | 1 | 2.4385 | 0.32691 | Medium | Low | High | 411 | 463 | 0.13406
SALMON CREEK 1101 | SONOMA | 26.7666 | 46.0934 | 2187.8 | 56.39% | 34.84% | 0 | 0.17748 | 1 | 1.8364 | 0.32592 | Medium | Low | Medium | 412 | 418 | 0.17748
SAN RAFAEL 1101 | NORTH BAY | 8.619 | 100.8045 | 2375.8 | 36.57% | 75.53% | 1 | 0.095181 | 1 | 3.4172 | 0.32525 | Low | Low | High | 413 | 556 | 0.095181
PURISIMA 1101 | LOS PADRES | 15.9907 | 3.8902 | 230 | 27.05% | 0% | 0 | 0.10891 | 1 | 2.9811 | 0.32467 | Low | Low | High | 414 | 512 | 0.10891
CARLOTTA 1121 | HUMBOLDT | 21.1982 | 72.3697 | 3511.9 | 43.68% | 0% | 1 | 0.26139 | 1 | 1.2391 | 0.32387 | Medium | Low | Low | 415 | 335 | 0.26139
FRUITLAND 1141 | HUMBOLDT | 24.0637 | 134.2847 | 3692.4 | 87.51% | 0% | 1 | 0.36081 | 1 | 0.89333 | 0.32232 | High | Low | Low | 416 | 267 | 0.36081
TASSAJARA 2109 | DIABLO | 0.80761 | 2.0601 | 4 | 41.59% | 0% | 0 | 0.10579 | 1 | 3.0369 | 0.32126 | Low | Low | High | 417 | 518 | 0.10579
SO. CAL. EDISON #3 1101 | FRESNO | 6.4255 | 1.9313 | 11 | 100% | 34.58% | 0 | 0.30414 | 1 | 1.0515 | 0.3198 | High | Low | Low | 418 | 306 | 0.30414
RIDGE 0402 | EAST BAY | 1.6674 | 151.6823 | 362.9 | 69.69% | 0% | 0 | 0.098308 | 1 | 3.2442 | 0.31893 | Low | Low | High | 419 | 548 | 0.098308
PAUL SWEET 2105 | CENTRAL COAST | 8.6024 | 84.5429 | 3445.9 | 21.11% | 85.61% | 0 | 0.11899 | 1 | 2.6738 | 0.31815 | Medium | Low | High | 420 | 490 | 0.11899
UKIAH 1114 | HUMBOLDT | 51.9619 | 68.1974 | 7022.4 | 50.46% | 0% | 1 | 0.31473 | 1 | 1.0096 | 0.31773 | High | Low | Low | 421 | 300 | 0.31473
LAS PULGAS 0401 | PENINSULA | 0.063561 | 48.5621 | 294 | 1.05% | 0% | 0 | 0.081206 | 1 | 3.8914 | 0.31601 | Low | Low | High | 422 | 585 | 0.081206
VACAVILLE 1104 | SACRAMENTO | 15.6565 | 122.8252 | 2194.1 | 87.64% | 0% | 0 | 0.18224 | 1 | 1.7281 | 0.31493 | Medium | Low | Medium | 423 | 416 | 0.18224
LONE TREE 2105 | DIABLO | 9.5646 | 12.3004 | 256.5 | 45.87% | 0% | 0 | 0.18285 | 1 | 1.7206 | 0.31462 | Medium | Low | Medium | 424 | 415 | 0.18285
MILPITAS 1109 | SAN JOSE | 29.4495 | 0.22548 | 11 | 60.37% | 0% | 0 | 0.24961 | 1 | 1.2599 | 0.31449 | Medium | Low | Low | 425 | 345 | 0.24961
TASSAJARA 2112 | DIABLO | 10.4417 | 108.27 | 2017.6 | 56.03% | 73.38% | 0 | 0.11268 | 1 | 2.7879 | 0.31414 | Medium | Low | High | 426 | 506 | 0.11268
EL CERRITO G 1112 | EAST BAY | 4.6851 | 47.8544 | 1170.5 | 19.15% | 89.29% | 0 | 0.084501 | 1 | 3.7125 | 0.31371 | Low | Low | High | 427 | 580 | 0.084501
HOLLYWOOD 0401 | EAST BAY | 2.9599 | 45.3292 | 240 | 55.9% | 0% | 0 | 0.10852 | 1 | 2.884 | 0.31296 | Low | Low | High | 428 | 515 | 0.10852
SAUSALITO 1102 | NORTH BAY | 8.6501 | 55.5336 | 984.6 | 48.79% | 0% | 0 | 0.12034 | 1 | 2.5917 | 0.31188 | Medium | Low | High | 429 | 484 | 0.12034
BEAR VALLEY 2101 | YOSEMITE | 108.2666 | 7.661 | 1277.1 | 64.95% | 0% | 0 | 0.27005 | 1 | 1.1403 | 0.30793 | Medium | Low | Low | 430 | 329 | 0.27005
ROSSMOOR 1101 | DIABLO | 12.9199 | 148.0625 | 4521 | 42.31% | 16.47% | 0 | 0.11909 | 1 | 2.5847 | 0.30782 | Medium | Low | High | 431 | 489 | 0.11909
STAFFORD 1101 | NORTH BAY | 7.6052 | 129.288 | 2835.7 | 34.67% | 0% | 0 | 0.12031 | 1 | 2.5554 | 0.30745 | Medium | Low | High | 432 | 485 | 0.12031
FOOTHILL 1102 | LOS PADRES | 10.2766 | 105.2891 | 2223.2 | 48.67% | 0% | 0 | 0.13118 | 1 | 2.3401 | 0.30697 | Medium | Low | Medium | 433 | 466 | 0.13118
RIO DEL MAR 0401 | CENTRAL COAST | 1.702 | 49.8711 | 176 | 48.23% | 0% | 0 | 0.12014 | 1 | 2.5466 | 0.30594 | Medium | Low | High | 434 | 486 | 0.12014
HALF MOON BAY 1102 | PENINSULA | 7.682 | 93.825 | 4052.2 | 17.79% | 72.22% | 0 | 0.094603 | 1 | 3.2201 | 0.30463 | Low | Low | High | 435 | 558 | 0.094603
WALDO 0401 | EAST BAY | 1.6612 | 31.6439 | 180 | 29.2% | 0% | 0 | 0.082439 | 1 | 3.673 | 0.3028 | Low | Low | High | 436 | 581 | 0.082439
HUMBOLDT BAY 1102 | HUMBOLDT | 7.0458 | 0.31454 | 13 | 17.05% | 0% | 0 | 0.10093 | 1 | 2.9917 | 0.30196 | Low | Low | High | 437 | 536 | 0.10093
FAIRMOUNT 0401 | EAST BAY | 1.4849 | 13.3911 | 77 | 25.82% | 0% | 0 | 0.078967 | 1 | 3.8023 | 0.30026 | Low | Low | High | 438 | 590 | 0.078967
PAUL SWEET 2107 | CENTRAL COAST | 10.6088 | 137.878 | 6735.2 | 21.72% | 44.56% | 0 | 0.11338 | 1 | 2.6376 | 0.29905 | Medium | Low | High | 439 | 505 | 0.11338
PRUNEDALE 1110 | CENTRAL COAST | 0.046537 | 177.6947 | 14170 | 0.05836% | 0% | 0 | 0.16321 | 1 | 1.8248 | 0.29784 | Medium | Low | Medium | 440 | 433 | 0.16321
FULTON 1102 | SONOMA | 28.1813 | 0.26946 | 17 | 44.67% | 12.65% | 0 | 0.18719 | 1 | 1.5859 | 0.29685 | Medium | Low | Low | 441 | 407 | 0.18719
CLEAR LAKE 1101 | HUMBOLDT | 18.1143 | 29.5531 | 3379.6 | 15.84% | 31.9% | 0 | 0.13818 | 1 | 2.1474 | 0.29672 | Medium | Low | Medium | 442 | 457 | 0.13818
VACAVILLE 1111 | SACRAMENTO | 12.1732 | 94.4466 | 1657 | 69.39% | 0% | 0 | 0.15702 | 1 | 1.8873 | 0.29636 | Medium | Low | Medium | 443 | 440 | 0.15702
COAST RD 0401 | CENTRAL COAST | 1.6617 | 17.5143 | 54 | 53.9% | 0% | 0 | 0.11855 | 1 | 2.4967 | 0.29599 | Medium | Low | High | 444 | 492 | 0.11855
CAMBRIA 1102 | LOS PADRES | 17.1255 | 61.511 | 1658.7 | 63.51% | 0% | 0 | 0.16048 | 1 | 1.844 | 0.29593 | Medium | Low | Medium | 445 | 436 | 0.16048
SAN LEANDRO U 1114 | MISSION | 13.8938 | 32.3118 | 935.2 | 48% | 0% | 0 | 0.14809 | 1 | 1.9911 | 0.29486 | Medium | Low | Medium | 446 | 446 | 0.14809
PLACER 1103 | SIERRA | 12.2492 | 68.8595 | 2024.4 | 41.67% | 0% | 0 | 0.13769 | 1 | 2.1392 | 0.29455 | Medium | Low | Medium | 447 | 459 | 0.13769
FRANKLIN 1104 | EAST BAY | 5.6687 | 0.06576 | 1 | 37.28% | 0% | 0 | 0.11211 | 1 | 2.6229 | 0.29404 | Medium | Low | High | 448 | 507 | 0.11211
OAKLAND K 1103 | EAST BAY | 6.0941 | 141.8873 | 1523.6 | 56.75% | 36.68% | 0 | 0.10303 | 1 | 2.8454 | 0.29317 | Low | Low | High | 449 | 528 | 0.10303
MORAGA 1103 | DIABLO | 3.4716 | 77.9372 | 1410 | 19.19% | 4.457% | 1 | 0.091048 | 1 | 3.2148 | 0.2927 | Low | Low | High | 450 | 566 | 0.091048
GEYSERVILLE 1102 | SONOMA | 54.2117 | 50.389 | 5951.9 | 45.9% | 34.72% | 0 | 0.27337 | 1 | 1.065 | 0.29113 | Medium | Low | Low | 451 | 325 | 0.27337
CHESTER 1102 | NORTH VALLEY | 2.4094 | 54.9614 | 296 | 44.74% | 0% | 0 | 0.15173 | 1 | 1.9144 | 0.29046 | Medium | Low | Medium | 452 | 443 | 0.15173
FAIRVIEW 2207 | DIABLO | 18.7684 | 16.7938 | 853 | 36.95% | 0% | 1 | 0.11443 | 1 | 2.5257 | 0.28901 | Medium | Low | High | 453 | 504 | 0.11443
HICKS 1116 | SAN JOSE | 10.7423 | 155.6132 | 5361.7 | 31.18% | 0% | 0 | 0.11205 | 1 | 2.5723 | 0.28823 | Low | Low | High | 454 | 508 | 0.11205
CAROLANDS 0404 | PENINSULA | 3.9545 | 1.1721 | 12 | 38.63% | 0% | 0 | 0.11531 | 1 | 2.4872 | 0.28679 | Medium | Low | High | 455 | 500 | 0.11531
HARTLEY 1101 | HUMBOLDT | 28.4012 | 30.64 | 1997.2 | 43.57% | 0% | 0 | 0.18458 | 1 | 1.5501 | 0.28612 | Medium | Low | Low | 456 | 411 | 0.18458
CAYETANO 2111 | MISSION | 5.4093 | 22.3271 | 272 | 44.4% | 0% | 0 | 0.12049 | 1 | 2.3726 | 0.28587 | Medium | Low | Medium | 457 | 483 | 0.12049
SAN CARLOS 1103 | PENINSULA | 3.983 | 76.8569 | 1260 | 24.3% | 0% | 0 | 0.073453 | 1 | 3.8842 | 0.28531 | Low | Low | High | 458 | 603 | 0.073453
HICKS 2103 | SAN JOSE | 10.8958 | 136.6541 | 3729.4 | 39.92% | 27.73% | 0 | 0.13059 | 1 | 2.1701 | 0.2834 | Medium | Low | Medium | 459 | 468 | 0.13059
CAMBRIA 1101 | LOS PADRES | 27.64 | 26.6582 | 858 | 85.88% | 0% | 1 | 0.20082 | 1 | 1.4064 | 0.28243 | Medium | Low | Low | 460 | 388 | 0.20082
HORSESHOE 1101 | SIERRA | 6.4051 | 60.2483 | 2184.9 | 17.66% | 0% | 0 | 0.10362 | 1 | 2.7162 | 0.28145 | Low | Low | High | 461 | 526 | 0.10362
OAKLAND J 1102 | EAST BAY | 6.2044 | 46.5645 | 857.5 | 33.69% | 0% | 0 | 0.10164 | 1 | 2.7444 | 0.27893 | Low | Low | High | 462 | 534 | 0.10164
RIO DELL 1102 | HUMBOLDT | 47.0229 | 106.5689 | 7819.8 | 64.08% | 0% | 1 | 0.42685 | 1 | 0.65331 | 0.27887 | High | Low | Low | 463 | 240 | 0.42685
PANORAMA 1102 | NORTH VALLEY | 32.1467 | 56.945 | 4816.4 | 38.01% | 0% | 0 | 0.17497 | 1 | 1.5851 | 0.27735 | Medium | Low | Low | 464 | 420 | 0.17497
PIERCY 2110 | SAN JOSE | 14.4387 | 57.4246 | 1584 | 52.34% | 0% | 0 | 0.20709 | 1 | 1.3322 | 0.2759 | Medium | Low | Low | 465 | 382 | 0.20709
WILDWOOD 1101 | NORTH VALLEY | 32.6037 | 56.7915 | 1691 | 100% | 0% | 1 | 0.43227 | 1 | 0.62979 | 0.27224 | High | Low | Low | 466 | 236 | 0.43227
LAKEWOOD 2107 | DIABLO | 7.3667 | 88.4957 | 2558.5 | 25.48% | 1.068% | 0 | 0.092658 | 1 | 2.8742 | 0.26632 | Low | Low | High | 467 | 561 | 0.092658
UKIAH 1115 | HUMBOLDT | 17.5263 | 38.8731 | 977.3 | 69.71% | 0% | 0 | 0.22334 | 1 | 1.1842 | 0.26447 | Medium | Low | Low | 468 | 366 | 0.22334
ANDERSON 1101 | NORTH VALLEY | 9.8615 | 58.5247 | 1174 | 49.16% | 0% | 0 | 0.15133 | 1 | 1.7454 | 0.26413 | Medium | Low | Medium | 469 | 444 | 0.15133
CAYUCOS 1102 | LOS PADRES | 13.8993 | 42.5264 | 2457.9 | 24.05% | 62.92% | 0 | 0.14223 | 1 | 1.8563 | 0.26402 | Medium | Low | Medium | 470 | 453 | 0.14223
EL CERRITO G 1110 | EAST BAY | 1.9753 | 34.2051 | 347 | 19.47% | 0% | 0 | 0.070004 | 1 | 3.765 | 0.26356 | Low | Low | High | 471 | 617 | 0.070004
RED BLUFF 1101 | NORTH VALLEY | 46.1055 | 0.040201 | 3 | 61.78% | 0% | 1 | 0.24502 | 1 | 1.0703 | 0.26225 | Medium | Low | Low | 472 | 349 | 0.24502
EEL RIVER 1102 | HUMBOLDT | 38.97 | 71.5696 | 10410.2 | 26.79% | 0% | 0 | 0.35914 | 1 | 0.72131 | 0.25905 | High | Low | Low | 473 | 269 | 0.35914
PACIFICA 1103 | PENINSULA | 4.0354 | 3.1893 | 60 | 21.45% | 74.37% | 0 | 0.090312 | 1 | 2.8097 | 0.25375 | Low | Low | High | 474 | 568 | 0.090312
RISING RIVER 1101 | NORTH VALLEY | 46.3641 | 41.1784 | 2451.5 | 77.88% | 0% | 0 | 0.35847 | 1 | 0.7054 | 0.25286 | High | Low | Low | 475 | 272 | 0.35847
SAN LUIS OBISPO 1102 | LOS PADRES | 0.61698 | 77.5643 | 991.9 | 4.825% | 0% | 0 | 0.079225 | 1 | 3.1792 | 0.25187 | Low | Low | High | 476 | 589 | 0.079225
ALTO 1122 | NORTH BAY | 8.8537 | 263.1656 | 4654.4 | 50.06% | 65.63% | 0 | 0.079305 | 1 | 3.1723 | 0.25158 | Low | Low | High | 477 | 588 | 0.079305
SEACLIFF 0401 | CENTRAL COAST | 8.5745 | 367.0421 | 3398.7 | 92.6% | 81.87% | 0 | 0.092298 | 1 | 2.6626 | 0.24576 | Low | Low | High | 478 | 562 | 0.092298
LOYOLA 1102 | DE ANZA | 0.10967 | 139.6629 | 7116.9 | 0.2152% | 0% | 0 | 0.10013 | 1 | 2.4497 | 0.24529 | Low | Low | High | 479 | 541 | 0.10013
SARATOGA 1115 | DE ANZA | 2.7261 | 0.7909 | 10 | 21.56% | 0% | 0 | 0.097367 | 1 | 2.5049 | 0.2439 | Low | Low | High | 480 | 551 | 0.097367
SAN MIGUEL 1106 | LOS PADRES | 37.1788 | 14.6587 | 1058.2 | 51.5% | 0% | 0 | 0.21893 | 1 | 1.1061 | 0.24216 | Medium | Low | Low | 481 | 371 | 0.21893
TYLER 1105 | NORTH VALLEY | 60.5727 | 42.7408 | 4721 | 54.84% | 0% | 0 | 0.2697 | 1 | 0.89474 | 0.24131 | Medium | Low | Low | 482 | 331 | 0.2697
CORNING 1102 | NORTH VALLEY | 81.1492 | 15.9848 | 3210 | 40.41% | 0% | 1 | 0.21678 | 1 | 1.1124 | 0.24114 | Medium | Low | Low | 483 | 374 | 0.21678
SAN RAFAEL 1104 | NORTH BAY | 11.3584 | 303.4563 | 7546.2 | 45.68% | 4.206% | 0 | 0.063863 | 1 | 3.7706 | 0.2408 | Low | Low | High | 484 | 632 | 0.063863
HATTON 1101 | CENTRAL COAST | 14.8111 | 258.8027 | 5969 | 64.22% | 9.429% | 1 | 0.12167 | 1 | 1.9413 | 0.23619 | Medium | Low | Medium | 485 | 479 | 0.12167
HOPLAND 1101 | HUMBOLDT | 82.4026 | 0.25226 | 33 | 62.99% | 0% | 0 | 0.24946 | 1 | 0.94514 | 0.23577 | Medium | Low | Low | 486 | 346 | 0.24946
PACIFICA 1102 | PENINSULA | 5.0009 | 3.4984 | 70 | 24.99% | 58.95% | 0 | 0.084575 | 1 | 2.7714 | 0.2344 | Low | Low | High | 487 | 578 | 0.084575
CHESTER 1101 | NORTH VALLEY | 2.5695 | 64.7245 | 521 | 31.92% | 0% | 0 | 0.12056 | 1 | 1.9366 | 0.23348 | Medium | Low | Medium | 488 | 481 | 0.12056
UKIAH 1111 | HUMBOLDT | 22.4731 | 19.3083 | 744.6 | 58.28% | 0% | 0 | 0.23588 | 1 | 0.98939 | 0.23338 | Medium | Low | Low | 489 | 359 | 0.23588
EL CERRITO G 1111 | EAST BAY | 0.94606 | 22.2933 | 281 | 7.506% | 0% | 0 | 0.059807 | 1 | 3.8959 | 0.233 | Low | Low | High | 490 | 640 | 0.059807
SNEATH LANE 1107 | PENINSULA | 2.5458 | 15.7601 | 167 | 24.03% | 0% | 0 | 0.10236 | 1 | 2.2761 | 0.23298 | Low | Low | Medium | 491 | 530 | 0.10236
VASCO 1102 | MISSION | 41.9238 | 27.6714 | 2461.1 | 47.14% | 0% | 0 | 0.20194 | 1 | 1.1484 | 0.23191 | Medium | Low | Low | 492 | 387 | 0.20194
LAS POSITAS 2108 | MISSION | 7.3474 | 5.525 | 112 | 36.25% | 0% | 0 | 0.11452 | 1 | 2.0246 | 0.23186 | Medium | Low | Medium | 493 | 503 | 0.11452
PALMER 1101 | LOS PADRES | 37.0218 | 21.6138 | 1331 | 60.12% | 0% | 0 | 0.1844 | 1 | 1.245 | 0.22959 | Medium | Low | Low | 494 | 412 | 0.1844
HARRIS 1108 | HUMBOLDT | 2.5554 | 18.9526 | 618.7 | 7.828% | 0% | 0 | 0.070432 | 1 | 3.2534 | 0.22914 | Low | Low | High | 495 | 616 | 0.070432
CLAYTON 2215 | DIABLO | 8.5821 | 88.5228 | 2717.5 | 27.96% | 13.23% | 0 | 0.077122 | 1 | 2.97 | 0.22905 | Low | Low | High | 496 | 591 | 0.077122
BALCH NO 1 1101 | FRESNO | 14.6983 | 24.0733 | 354 | 99.95% | 0% | 0 | 0.32415 | 1 | 0.70256 | 0.22774 | High | Low | Low | 497 | 290 | 0.32415
SANTA ROSA A 1107 | SONOMA | 2.9541 | 140.0185 | 861.1 | 48.03% | 100% | 0 | 0.115 | 1 | 1.9794 | 0.22762 | Medium | Low | Medium | 498 | 501 | 0.115
LLAGAS 2101 | SAN JOSE | 19.8062 | 31.8184 | 3239.5 | 19.45% | 0% | 0 | 0.16055 | 1 | 1.4164 | 0.22741 | Medium | Low | Low | 499 | 435 | 0.16055
ORINDA 0401 | DIABLO | 9.3864 | 287.0654 | 3454 | 78.01% | 25.23% | 0 | 0.075976 | 1 | 2.9927 | 0.22737 | Low | Low | High | 500 | 594 | 0.075976
SHINGLE SPRINGS 1103 | SIERRA | 8.4534 | 233.596 | 3206.9 | 61.58% | 64.3% | 1 | 0.099664 | 1 | 2.279 | 0.22713 | Low | Low | Medium | 501 | 543 | 0.099664
WYANDOTTE 1102 | NORTH VALLEY | 4.5597 | 46.3866 | 1089 | 19.42% | 0% | 0 | 0.089417 | 1 | 2.5358 | 0.22674 | Low | Low | High | 502 | 570 | 0.089417
WILLOW PASS 2107 | DIABLO | 0.15832 | 0.84686 | 3 | 4.469% | 0% | 0 | 0.10569 | 1 | 2.1198 | 0.22404 | Low | Low | Medium | 503 | 519 | 0.10569
BERKELEY F 1105 | EAST BAY | 1.7869 | 64.7043 | 735.5 | 15.72% | 0% | 0 | 0.068434 | 1 | 3.2675 | 0.22361 | Low | Low | High | 504 | 619 | 0.068434
DOLAN ROAD 1101 | CENTRAL COAST | 3.8209 | 57.6437 | 3956.9 | 5.566% | 0% | 0 | 0.10527 | 1 | 2.1109 | 0.22221 | Low | Low | Medium | 505 | 520 | 0.10527
SONOMA 1105 | SONOMA | 14.5812 | 0.73753 | 46 | 23.38% | 31.42% | 0 | 0.11057 | 1 | 1.9985 | 0.22098 | Low | Low | Medium | 506 | 510 | 0.11057
ARCATA 1121 | HUMBOLDT | 6.629 | 2.6967 | 78 | 22.92% | 0% | 0 | 0.1205 | 1 | 1.8296 | 0.22047 | Medium | Low | Medium | 507 | 482 | 0.1205
SMARTVILLE 1101 | SIERRA | 15.8868 | 404.905 | 6432.2 | 100% | 0% | 0 | 0.10646 | 1 | 2.0689 | 0.22024 | Low | Low | Medium | 508 | 516 | 0.10646
OAKLAND X 1105 | EAST BAY | 3.475 | 52.0985 | 770 | 23.51% | 0% | 0 | 0.075775 | 1 | 2.8409 | 0.21527 | Low | Low | High | 509 | 596 | 0.075775
SANTA YNEZ 1101 | LOS PADRES | 30.6514 | 98.3916 | 7214.7 | 41.8% | 44.97% | 0 | 0.19903 | 1 | 1.0807 | 0.21509 | Medium | Low | Low | 510 | 395 | 0.19903
COTATI 1104 | SONOMA | 7.1785 | 3.6067 | 69 | 37.52% | 0% | 0 | 0.13107 | 1 | 1.6408 | 0.21507 | Medium | Low | Low | 511 | 467 | 0.13107
CLOVERDALE 1101 | SONOMA | 24.0395 | 83.1986 | 3030.8 | 65.99% | 0% | 0 | 0.22357 | 1 | 0.95033 | 0.21246 | Medium | Low | Low | 512 | 365 | 0.22357
OAKLAND D 1112 | EAST BAY | 2.6688 | 89.2166 | 1061 | 22.44% | 77.45% | 0 | 0.071051 | 1 | 2.99 | 0.21244 | Low | Low | High | 513 | 614 | 0.071051
JAMESON 1103 | SACRAMENTO | 3.6313 | 77.1526 | 840.3 | 33.34% | 0% | 0 | 0.11642 | 1 | 1.8208 | 0.21198 | Medium | Low | Medium | 514 | 498 | 0.11642
BELMONT 1103 | PENINSULA | 1.5331 | 86.6921 | 1624.8 | 8.18% | 0% | 0 | 0.061024 | 1 | 3.4689 | 0.21169 | Low | Low | High | 515 | 639 | 0.061024
SUMMIT 1101 | SIERRA | 8.7537 | 84.6905 | 1442.5 | 51.39% | 0% | 0 | 0.14736 | 1 | 1.4297 | 0.21068 | Medium | Low | Low | 516 | 450 | 0.14736
FORT SEWARD 1122 | HUMBOLDT | 17.3427 | 44.8588 | 983 | 79.14% | 0% | 0 | 0.28852 | 1 | 0.72632 | 0.20956 | Medium | Low | Low | 517 | 314 | 0.28852
ROSSMOOR 1106 | DIABLO | 4.0278 | 131.4697 | 2771.5 | 19.11% | 34.23% | 0 | 0.071194 | 1 | 2.9421 | 0.20946 | Low | Low | High | 518 | 613 | 0.071194
KIRKER 2104 | DIABLO | 5.4258 | 48.97 | 944.5 | 28.13% | 0% | 0 | 0.095285 | 1 | 2.1972 | 0.20936 | Low | Low | Medium | 519 | 555 | 0.095285
TIDEWATER 2106 | DIABLO | 8.1253 | 1.26 | 42 | 24.38% | 0% | 0 | 0.088717 | 1 | 2.3405 | 0.20764 | Low | Low | Medium | 520 | 572 | 0.088717
JARVIS 1108 | MISSION | 2.1719 | 39.8668 | 748 | 11.58% | 0% | 0 | 0.072228 | 1 | 2.8739 | 0.20757 | Low | Low | High | 521 | 609 | 0.072228
MARTELL 1102 | STOCKTON | 8.6112 | 263.8696 | 3200 | 71.01% | 0% | 0 | 0.088743 | 1 | 2.3343 | 0.20715 | Low | Low | Medium | 522 | 571 | 0.088743
LOS GATOS 1102 | DE ANZA | 1.1034 | 103.8413 | 635 | 18.04% | 0% | 0 | 0.067648 | 1 | 3.0578 | 0.20686 | Low | Low | High | 523 | 620 | 0.067648
MORGAN HILL 2104 | SAN JOSE | 4.9492 | 65.5542 | 1382 | 23.48% | 0% | 0 | 0.11704 | 1 | 1.7652 | 0.2066 | Medium | Low | Medium | 524 | 497 | 0.11704
OAKLAND J 1106 | EAST BAY | 1.9819 | 31.0726 | 613 | 10.05% | 0% | 0 | 0.081922 | 1 | 2.5071 | 0.20539 | Low | Low | High | 525 | 583 | 0.081922
OAKLAND K 1101 | EAST BAY | 2.7602 | 98.8794 | 720 | 37.91% | 65.54% | 0 | 0.075188 | 1 | 2.6645 | 0.20034 | Low | Low | High | 526 | 597 | 0.075188
CASTRO VALLEY 1101 | MISSION | 2.976 | 55.911 | 1242.6 | 13.39% | 0% | 0 | 0.072256 | 1 | 2.7708 | 0.2002 | Low | Low | High | 527 | 608 | 0.072256
SARATOGA 1103 | DE ANZA | 4.2157 | 183.5114 | 1906.5 | 40.58% | 0% | 0 | 0.071804 | 1 | 2.7531 | 0.19768 | Low | Low | High | 528 | 611 | 0.071804
HICKS 2101 | SAN JOSE | 11.134 | 65.1711 | 2767.7 | 26.22% | 17.93% | 0 | 0.11737 | 1 | 1.6776 | 0.19691 | Medium | Low | Medium | 529 | 496 | 0.11737
NOVATO 1104 | NORTH BAY | 4.2213 | 51.7699 | 1264.2 | 17.29% | 0% | 0 | 0.080358 | 1 | 2.4233 | 0.19473 | Low | Low | High | 530 | 587 | 0.080358
LLAGAS 2107 | SAN JOSE | 7.8323 | 69.5229 | 1556.5 | 34.98% | 39.23% | 0 | 0.11554 | 1 | 1.672 | 0.19317 | Medium | Low | Medium | 531 | 499 | 0.11554
BUTTE 1105 | NORTH VALLEY | 1.8432 | 87.173 | 1304.5 | 12.32% | 0% | 0 | 0.084537 | 1 | 2.2799 | 0.19273 | Low | Low | Medium | 532 | 579 | 0.084537
FLORENCE 0401 | EAST BAY | 1.7158 | 140.8044 | 604.6 | 39.96% | 0% | 0 | 0.06431 | 1 | 2.9373 | 0.1889 | Low | Low | High | 533 | 631 | 0.06431
LAKEWOOD 2109 | DIABLO | 0.21818 | 138.8407 | 999.5 | 3.031% | 100% | 0 | 0.056491 | 1 | 3.3292 | 0.18807 | Low | Low | High | 534 | 650 | 0.056491
VIEJO 2204 | CENTRAL COAST | 3.9584 | 200.1178 | 4925 | 16.08% | 0% | 0 | 0.07302 | 1 | 2.5741 | 0.18796 | Low | Low | High | 535 | 605 | 0.07302
JOLON 1102 | CENTRAL COAST | 66.2788 | 0.018962 | 2 | 62.84% | 0% | 0 | 0.20003 | 1 | 0.93912 | 0.18785 | Medium | Low | Low | 536 | 391 | 0.20003
PAUL SWEET 2102 | CENTRAL COAST | 5.198 | 260.6733 | 4746.6 | 28.55% | 80.79% | 0 | 0.064706 | 1 | 2.9017 | 0.18776 | Low | Low | High | 537 | 630 | 0.064706
EL CERRITO G 1108 | EAST BAY | 0.57918 | 52.4668 | 756 | 4.02% | 0% | 0 | 0.048895 | 1 | 3.8114 | 0.18636 | Low | Low | High | 538 | 667 | 0.048895
SAN LEANDRO U 1107 | MISSION | 0.061986 | 25.3999 | 381.1 | 0.4131% | 0% | 0 | 0.091216 | 1 | 2.0325 | 0.1854 | Low | Low | Medium | 539 | 565 | 0.091216
OAKLAND J 1105 | EAST BAY | 3.7186 | 38.6359 | 904.4 | 15.89% | 0% | 0 | 0.069116 | 1 | 2.6711 | 0.18462 | Low | Low | High | 540 | 618 | 0.069116
ECHO SUMMIT 1101 | xx | 6.1677 | 89.7501 | 1320 | 41.94% | 0% | 0 | 0.17692 | 1 | 1.0356 | 0.18321 | Medium | Low | Low | 541 | 419 | 0.17692
MONROE 2107 | SONOMA | 0.75479 | 28.657 | 308.2 | 7.018% | 100% | 0 | 0.098586 | 1 | 1.8538 | 0.18275 | Low | Low | Medium | 542 | 546 | 0.098586
MONROE 2103 | SONOMA | 1.4327 | 24.5777 | 432.6 | 8.14% | 100% | 0 | 0.09636 | 1 | 1.8837 | 0.18151 | Low | Low | Medium | 543 | 553 | 0.09636
FRANKLIN 1101 | EAST BAY | 1.5325 | 0.31796 | 3 | 16.24% | 0% | 0 | 0.072128 | 1 | 2.5025 | 0.1805 | Low | Low | High | 544 | 610 | 0.072128
OCEANO 1103 | LOS PADRES | 1.291 | 64.1861 | 733.5 | 11.3% | 0% | 0 | 0.086198 | 1 | 2.093 | 0.18041 | Low | Low | Medium | 545 | 576 | 0.086198
ANDERSON 1103 | NORTH VALLEY | 5.8182 | 84.3714 | 2668.5 | 18.4% | 0% | 0 | 0.10874 | 1 | 1.6553 | 0.18 | Low | Low | Low | 546 | 514 | 0.10874
SALT SPRINGS 2101 | STOCKTON | 16.764 | 106.976 | 2344.4 | 76.49% | 0% | 0 | 0.26125 | 1 | 0.68887 | 0.17997 | Medium | Low | Low | 547 | 336 | 0.26125
BERKELEY F 0402 | EAST BAY | 0.47631 | 102.5882 | 218 | 22.41% | 0% | 0 | 0.05592 | 1 | 3.1937 | 0.17859 | Low | Low | High | 548 | 652 | 0.05592
MORGAN HILL 2109 | SAN JOSE | 1.7684 | 37.4103 | 998.2 | 6.628% | 0% | 0 | 0.10014 | 1 | 1.7654 | 0.17679 | Low | Low | Medium | 549 | 540 | 0.10014
IGNACIO 1101 | NORTH BAY | 5.4039 | 248.3226 | 3068.1 | 43.74% | 11.33% | 0 | 0.058178 | 1 | 3.0082 | 0.17501 | Low | Low | High | 550 | 646 | 0.058178
SAN MIGUEL 1104 | LOS PADRES | 25.5295 | 7.7017 | 1102.6 | 17.83% | 0% | 0 | 0.13821 | 1 | 1.2642 | 0.17473 | Medium | Low | Low | 551 | 456 | 0.13821
BAY MEADOWS 2102 | PENINSULA | 4.2519 | 111.0862 | 1584.9 | 29.8% | 0% | 0 | 0.074656 | 1 | 2.337 | 0.17447 | Low | Low | Medium | 552 | 598 | 0.074656
MORRO BAY 1101 | LOS PADRES | 6.3279 | 64.6413 | 2970.7 | 13.77% | 10.63% | 0 | 0.076002 | 1 | 2.2858 | 0.17372 | Low | Low | Medium | 553 | 593 | 0.076002
SAN RAFAEL 1106 | NORTH BAY | 2.8567 | 156.7324 | 3281.6 | 13.64% | 0% | 0 | 0.048872 | 1 | 3.5064 | 0.17137 | Low | Low | High | 554 | 668 | 0.048872
JESSUP 1103 | NORTH VALLEY | 3.7231 | 134.3412 | 5113.2 | 9.782% | 0% | 0 | 0.10265 | 1 | 1.6574 | 0.17012 | Low | Low | Low | 555 | 529 | 0.10265
RED BLUFF 1105 | NORTH VALLEY | 15.2954 | 41.808 | 1578 | 40.52% | 0% | 0 | 0.16165 | 1 | 1.0496 | 0.16967 | Medium | Low | Low | 556 | 434 | 0.16165
VINEYARD 2107 | MISSION | 1.7807 | 64.4641 | 883.5 | 12.99% | 0% | 0 | 0.074528 | 1 | 2.2733 | 0.16942 | Low | Low | Medium | 557 | 599 | 0.074528
ZACA 1101 | LOS PADRES | 18.6848 | 28.6781 | 743 | 72.12% | 7.874% | 0 | 0.19189 | 1 | 0.87943 | 0.16876 | Medium | Low | Low | 558 | 402 | 0.19189
BRIDGEVILLE 1102 | HUMBOLDT | 33.3457 | 109.1054 | 5095.2 | 71.4% | 64.9% | 0 | 0.37184 | 1 | 0.44802 | 0.16659 | High | Low | Low | 559 | 259 | 0.37184
PACIFICA 1104 | PENINSULA | 0.50255 | 0.27895 | 2 | 7.009% | 0% | 0 | 0.06234 | 1 | 2.6655 | 0.16617 | Low | Low | High | 560 | 636 | 0.06234
SARATOGA 1104 | DE ANZA | 1.7714 | 181.8242 | 3279.2 | 9.822% | 0% | 0 | 0.051455 | 1 | 3.2268 | 0.16604 | Low | Low | High | 561 | 662 | 0.051455
DIVIDE 1103 | LOS PADRES | 2.2423 | 26.329 | 537 | 10.99% | 0% | 0 | 0.07382 | 1 | 2.2453 | 0.16575 | Low | Low | Medium | 562 | 602 | 0.07382
WOOD 0401 | EAST BAY | 0.4018 | 105.8273 | 352.5 | 12.06% | 0% | 0 | 0.055516 | 1 | 2.9705 | 0.16491 | Low | Low | High | 563 | 654 | 0.055516
ALTO 1123 | NORTH BAY | 2.3955 | 75.8605 | 1564.6 | 11.61% | 4.121% | 0 | 0.054202 | 1 | 3.0362 | 0.16457 | Low | Low | High | 564 | 657 | 0.054202
TULE POWER HOUSE 1101 | FRESNO | 4.0927 | 126.3618 | 517.3 | 99.97% | 0% | 0 | 0.14702 | 1 | 1.0868 | 0.15979 | Medium | Low | Low | 565 | 451 | 0.14702
OAKHURST 1102 | YOSEMITE | 11.3331 | 352.2874 | 5880.1 | 67.9% | 11.35% | 1 | 0.094676 | 1 | 1.6857 | 0.1596 | Low | Low | Medium | 566 | 557 | 0.094676
POSO MOUNTAIN 2101 | KERN | 49.4434 | 6.8941 | 413 | 82.53% | 0% | 1 | 0.25701 | 1 | 0.61759 | 0.15873 | Medium | Low | Low | 567 | 337 | 0.25701
PEABODY 2106 | SACRAMENTO | 0.58049 | 41.6388 | 112 | 21.58% | 0% | 0 | 0.08699 | 1 | 1.7615 | 0.15323 | Low | Low | Medium | 568 | 574 | 0.08699
MORGAN HILL 2110 | SAN JOSE | 2.054 | 25.1241 | 826.3 | 6.245% | 0% | 0 | 0.084977 | 1 | 1.7964 | 0.15265 | Low | Low | Medium | 569 | 577 | 0.084977
CASTRO VALLEY 1104 | MISSION | 3.6017 | 32.9628 | 916.5 | 12.95% | 0% | 0 | 0.067374 | 1 | 2.2554 | 0.15196 | Low | Low | Medium | 570 | 621 | 0.067374
BUCKS CREEK 1102 | NORTH VALLEY | 29.5609 | 41.7418 | 1233.7 | 100% | 23.04% | 0 | 0.30696 | 1 | 0.49433 | 0.15174 | High | Low | Low | 571 | 303 | 0.30696
ARLINGTON 0401 | EAST BAY | 0.76473 | 112.5678 | 446.5 | 19.28% | 0% | 0 | 0.044083 | 1 | 3.4267 | 0.15106 | Low | Low | High | 572 | 676 | 0.044083
STELLING 1109 | DE ANZA | 0.52786 | 116.8956 | 1926.1 | 3.204% | 0% | 0 | 0.061968 | 1 | 2.4341 | 0.15084 | Low | Low | High | 573 | 637 | 0.061968
OROVILLE 1104 | NORTH VALLEY | 0.2392 | 56.2036 | 556.5 | 2.416% | 0% | 0 | 0.056784 | 1 | 2.6537 | 0.15069 | Low | Low | High | 574 | 649 | 0.056784
MC KEE 1111 | SAN JOSE | 8.3733 | 46.2158 | 1247.3 | 31.03% | 0% | 0 | 0.11942 | 1 | 1.2586 | 0.15031 | Medium | Low | Low | 575 | 487 | 0.11942
OAKLAND J 1118 | EAST BAY | 0.38627 | 16.6579 | 196.5 | 3.275% | 0% | 0 | 0.067359 | 1 | 2.2214 | 0.14963 | Low | Low | Medium | 576 | 622 | 0.067359
CORONA 1103 | SONOMA | 0.968 | 36.1818 | 623.8 | 5.615% | 0% | 0 | 0.087372 | 1 | 1.711 | 0.14949 | Low | Low | Medium | 577 | 573 | 0.087372
MONTEREY 0402 | CENTRAL COAST | 0.7655 | 61.7929 | 241.4 | 19.59% | 0% | 0 | 0.058548 | 1 | 2.553 | 0.14947 | Low | Low | High | 578 | 645 | 0.058548
PIT NO 1 1101 | NORTH VALLEY | 25.7108 | 31.6065 | 1677.5 | 48.44% | 0% | 0 | 0.19615 | 1 | 0.75692 | 0.14847 | Medium | Low | Low | 579 | 396 | 0.19615
BAYWOOD 1101 | LOS PADRES | 1.4233 | 61.3561 | 1783.1 | 4.897% | 0% | 0 | 0.06584 | 1 | 2.2327 | 0.147 | Low | Low | Medium | 580 | 628 | 0.06584
AUBURN 1102 | SIERRA | 2.2817 | 92.0082 | 812 | 25.85% | 0% | 0 | 0.066602 | 1 | 2.193 | 0.14606 | Low | Low | Medium | 581 | 625 | 0.066602
SAN LUIS OBISPO 1105 | LOS PADRES | 1.9887 | 111.0125 | 1301 | 16.97% | 0% | 0 | 0.06651 | 1 | 2.1947 | 0.14597 | Low | Low | Medium | 582 | 626 | 0.06651
EAST MARYSVILLE 1108 | SIERRA | 0.35809 | 22.6124 | 1522.8 | 0.5317% | 0% | 0 | 0.10377 | 1 | 1.4017 | 0.14545 | Low | Low | Low | 583 | 525 | 0.10377
SYCAMORE CREEK 1109 | NORTH VALLEY | 0.58228 | 131.795 | 1758 | 4.365% | 0% | 0 | 0.064735 | 1 | 2.2449 | 0.14532 | Low | Low | Medium | 584 | 629 | 0.064735
TASSAJARA 2103 | DIABLO | 1.7119 | 125.7307 | 2473.5 | 8.702% | 35.07% | 0 | 0.046769 | 1 | 3.1066 | 0.1453 | Low | Low | High | 585 | 671 | 0.046769
TEMPLETON 2112 | LOS PADRES | 2.5848 | 16.2347 | 613 | 6.845% | 0% | 0 | 0.101 | 1 | 1.4381 | 0.14525 | Low | Low | Low | 586 | 535 | 0.101
LAKEWOOD 2224 | DIABLO | 0.72014 | 122.1338 | 2970 | 2.961% | 100% | 0 | 0.0494 | 1 | 2.9387 | 0.14517 | Low | Low | High | 587 | 665 | 0.0494
OAKLAND J 1116 | EAST BAY | 0.031861 | 22.9977 | 429.5 | 0.1706% | 0% | 0 | 0.051875 | 1 | 2.7948 | 0.14498 | Low | Low | High | 588 | 661 | 0.051875
OCEANO 1105 | LOS PADRES | 3.6627 | 45.7122 | 1133 | 14.78% | 0% | 0 | 0.063148 | 1 | 2.2953 | 0.14494 | Low | Low | Medium | 589 | 634 | 0.063148
DRUM 1101 | SIERRA | 18.8373 | 140.8712 | 2654 | 99.99% | 100% | 0 | 0.31704 | 1 | 0.45622 | 0.14464 | High | Low | Low | 590 | 296 | 0.31704
LAS GALLINAS A 1104 | NORTH BAY | 1.1639 | 140.8806 | 1822.6 | 8.996% | 0% | 0 | 0.041798 | 1 | 3.4288 | 0.14332 | Low | Low | High | 591 | 678 | 0.041798
LLAGAS 2104 | SAN JOSE | 1.6348 | 32.5627 | 979.5 | 5.435% | 0% | 0 | 0.10085 | 1 | 1.4196 | 0.14318 | Low | Low | Low | 592 | 537 | 0.10085
NEWBURG 1131 | HUMBOLDT | 6.672 | 10.1068 | 399 | 16.9% | 0% | 0 | 0.10164 | 1 | 1.4078 | 0.14308 | Low | Low | Low | 593 | 533 | 0.10164
VASONA 1102 | DE ANZA | 0.06716 | 101.8373 | 1570.3 | 0.4355% | 0% | 0 | 0.038682 | 1 | 3.6689 | 0.14192 | Low | Low | High | 594 | 681 | 0.038682
GREENBRAE 1104 | NORTH BAY | 0.079918 | 41.4788 | 757.1 | 0.4378% | 0% | 0 | 0.048912 | 1 | 2.8879 | 0.14125 | Low | Low | High | 595 | 666 | 0.048912
WOODWARD 2108 | FRESNO | 30.1544 | 19.2531 | 1994 | 29.12% | 0% | 0 | 0.16813 | 1 | 0.83522 | 0.14042 | Medium | Low | Low | 596 | 427 | 0.16813
TEJON 1103 | KERN | 2.7582 | 0.046004 | 2 | 6.344% | 0% | 0 | 0.10915 | 1 | 1.2829 | 0.14003 | Low | Low | Low | 597 | 511 | 0.10915
RINCON 1104 | SONOMA | 2.6764 | 69.3638 | 835.3 | 22.23% | 77.17% | 0 | 0.075816 | 1 | 1.8389 | 0.13942 | Low | Low | Medium | 598 | 595 | 0.075816
ESTUDILLO 0401 | MISSION | 0.69789 | 24.7934 | 117 | 14.79% | 0% | 0 | 0.073357 | 1 | 1.8893 | 0.1386 | Low | Low | Medium | 599 | 604 | 0.073357
SNEATH LANE 1101 | PENINSULA | 2.4892 | 147.801 | 1391 | 26.45% | 0% | 0 | 0.056375 | 1 | 2.4318 | 0.13709 | Low | Low | High | 600 | 651 | 0.056375
OAKLAND X 1101 | EAST BAY | 0.53647 | 122.1199 | 644.5 | 10.17% | 0% | 0 | 0.045316 | 1 | 2.9835 | 0.1352 | Low | Low | High | 601 | 674 | 0.045316
TULUCAY 1101 | NORTH BAY | 4.4167 | 81.0638 | 1556.4 | 23% | 0% | 0 | 0.07244 | 1 | 1.8524 | 0.13419 | Low | Low | Medium | 602 | 607 | 0.07244
WESTLEY 1103 | YOSEMITE | 0.92376 | 11.6299 | 1127 | 0.9533% | 0% | 0 | 0.10608 | 1 | 1.2637 | 0.13405 | Low | Low | Low | 603 | 517 | 0.10608
PIT NO 5 1101 | NORTH VALLEY | 23.7942 | 87.3832 | 2066.5 | 100% | 0% | 1 | 0.37222 | 1 | 0.35683 | 0.13282 | High | Low | Low | 604 | 258 | 0.37222
RINCON 1102 | SONOMA | 3.5536 | 62.5648 | 1236.9 | 17.97% | 7.097% | 1 | 0.07654 | 1 | 1.7248 | 0.13202 | Low | Low | Medium | 605 | 592 | 0.07654
JARVIS 1111 | MISSION | 1.1185 | 51.7293 | 995.5 | 5.812% | 100% | 0 | 0.053741 | 1 | 2.4441 | 0.13135 | Low | Low | High | 606 | 658 | 0.053741
WOODSIDE 1102 | PENINSULA | 0.10582 | 135.7016 | 2319.1 | 0.6192% | 0% | 0 | 0.03505 | 1 | 3.7245 | 0.13054 | Low | Low | High | 607 | 683 | 0.03505
WILLITS 1102 | HUMBOLDT | 5.2584 | 82.94 | 931.4 | 46.83% | 0% | 0 | 0.097209 | 1 | 1.3417 | 0.13043 | Low | Low | Low | 608 | 552 | 0.097209
EDENVALE 2107 | SAN JOSE | 0.76864 | 12.2993 | 451 | 2.096% | 0% | 0 | 0.097415 | 1 | 1.3381 | 0.13035 | Low | Low | Low | 609 | 550 | 0.097415
HARTLEY 1102 | HUMBOLDT | 4.13 | 61.8764 | 1709.2 | 14.95% | 0% | 0 | 0.086633 | 1 | 1.4904 | 0.12911 | Low | Low | Low | 610 | 575 | 0.086633
SNEATH LANE 1106 | PENINSULA | 1.101 | 134.6382 | 1541.5 | 9.617% | 0% | 0 | 0.054926 | 1 | 2.3506 | 0.12911 | Low | Low | Medium | 611 | 655 | 0.054926
FITCH MOUNTAIN 1111 | SONOMA | 2.7214 | 0.49011 | 15 | 8.892% | 0% | 0 | 0.081834 | 1 | 1.5662 | 0.12817 | Low | Low | Low | 612 | 584 | 0.081834
CALPELLA 1102 | HUMBOLDT | 5.8421 | 60.5445 | 1573.2 | 22.48% | 0% | 1 | 0.1146 | 1 | 1.1094 | 0.12713 | Medium | Low | Low | 613 | 502 | 0.1146
GOLDTREE 1108 | LOS PADRES | 2.5563 | 123.4945 | 1809.8 | 17.44% | 0% | 0 | 0.059088 | 1 | 2.1453 | 0.12676 | Low | Low | Medium | 614 | 643 | 0.059088
MC KEE 1108 | SAN JOSE | 1.0836 | 60.3492 | 632.2 | 10.34% | 0% | 0 | 0.091388 | 1 | 1.3857 | 0.12664 | Low | Low | Low | 615 | 564 | 0.091388
LLAGAS 2106 | SAN JOSE | 1.5959 | 27.4852 | 909 | 4.825% | 0% | 0 | 0.10177 | 1 | 1.2297 | 0.12515 | Low | Low | Low | 616 | 531 | 0.10177
PACIFIC GROVE 0422 | CENTRAL COAST | 0.61996 | 84.4855 | 586 | 8.938% | 0% | 0 | 0.045387 | 1 | 2.7492 | 0.12478 | Low | Low | High | 617 | 673 | 0.045387
LLAGAS 2105 | SAN JOSE | 0.40589 | 48.4729 | 901 | 2.184% | 0% | 0 | 0.074274 | 1 | 1.6756 | 0.12445 | Low | Low | Medium | 618 | 601 | 0.074274
AUBURN 1101 | SIERRA | 3.1166 | 253.2817 | 1242.6 | 63.53% | 0% | 0 | 0.054328 | 1 | 2.2625 | 0.12292 | Low | Low | Medium | 619 | 656 | 0.054328
SONOMA 1107 | SONOMA | 2.3737 | 0.78936 | 41 | 4.57% | 0% | 0 | 0.072608 | 1 | 1.6698 | 0.12124 | Low | Low | Medium | 620 | 606 | 0.072608
MC KEE 1107 | SAN JOSE | 2.6945 | 49.4006 | 1880 | 7.08% | 0% | 0 | 0.093763 | 1 | 1.2862 | 0.1206 | Low | Low | Low | 621 | 559 | 0.093763
ALTO 1120 | NORTH BAY | 2.2169 | 197.8696 | 3705.9 | 11.84% | 0% | 0 | 0.03938 | 1 | 3.0547 | 0.12029 | Low | Low | High | 622 | 680 | 0.03938
BURNEY 1102 | NORTH VALLEY | 0.71383 | 41.7807 | 168 | 17.75% | 0% | 0 | 0.089873 | 1 | 1.3275 | 0.1193 | Low | Low | Low | 623 | 569 | 0.089873
PLACER 1104 | SIERRA | 1.3434 | 89.4281 | 1228 | 9.783% | 0% | 0 | 0.05272 | 1 | 2.2618 | 0.11924 | Low | Low | Medium | 624 | 659 | 0.05272
ALTO 1121 | NORTH BAY | 0.013093 | 76.5651 | 663 | 0.1512% | 0% | 0 | 0.040029 | 1 | 2.9783 | 0.11922 | Low | Low | High | 625 | 679 | 0.040029
GREENBRAE 1103 | NORTH BAY | 5.1674 | 390.2998 | 5709.5 | 35.32% | 45.87% | 0 | 0.032461 | 1 | 3.627 | 0.11774 | Low | Low | High | 626 | 684 | 0.032461
OCEANO 1106 | LOS PADRES | 1.8831 | 156.8283 | 5341.1 | 5.529% | 0% | 0 | 0.052641 | 1 | 2.2321 | 0.1175 | Low | Low | Medium | 627 | 660 | 0.052641
WILLOW PASS 2108 | DIABLO | 0.047227 | 1.9853 | 36 | 0.2604% | 0% | 0 | 0.05568 | 1 | 2.1011 | 0.11699 | Low | Low | Medium | 628 | 653 | 0.05568
LAKEWOOD 1102 | DIABLO | 0.47236 | 89.9728 | 863.1 | 4.924% | 0% | 0 | 0.045836 | 1 | 2.5521 | 0.11698 | Low | Low | High | 629 | 672 | 0.045836
BANCROFT 0402 | EAST BAY | 1.0716 | 53.641 | 245 | 23.46% | 0% | 0 | 0.063524 | 1 | 1.8404 | 0.11691 | Low | Low | Medium | 630 | 633 | 0.063524
BERESFORD 0403 | PENINSULA | 4.1458 | 234.4513 | 2838.9 | 34.24% | 0% | 0 | 0.049683 | 1 | 2.3346 | 0.11599 | Low | Low | Medium | 631 | 664 | 0.049683
REEDLEY 1104 | FRESNO | 1.9028 | 5.211 | 625.1 | 1.586% | 0% | 0 | 0.10427 | 1 | 1.0862 | 0.11325 | Low | Low | Low | 632 | 524 | 0.10427
TEMPLETON 2108 | LOS PADRES | 2.5794 | 242.7456 | 8795.5 | 7.119% | 0% | 0 | 0.059186 | 1 | 1.8973 | 0.11229 | Low | Low | Medium | 633 | 642 | 0.059186
SAN BERNARD 1101 | KERN | 0.91753 | 39.6888 | 1758 | 2.071% | 0% | 0 | 0.099863 | 1 | 1.1206 | 0.11191 | Low | Low | Low | 634 | 542 | 0.099863
RADUM 1105 | MISSION | 2.1702 | 211.3073 | 2499.3 | 18.35% | 37.28% | 0 | 0.047243 | 1 | 2.3277 | 0.10997 | Low | Low | Medium | 635 | 670 | 0.047243
MONTEREY 0401 | CENTRAL COAST | 0.26645 | 75.7453 | 373 | 5.411% | 0% | 0 | 0.042472 | 1 | 2.5698 | 0.10914 | Low | Low | High | 636 | 677 | 0.042472
ALHAMBRA 1102 | DIABLO | 0.24414 | 57.5853 | 812.5 | 1.73% | 0% | 0 | 0.048128 | 1 | 2.1796 | 0.1049 | Low | Low | Medium | 637 | 669 | 0.048128
SO. CAL. EDISON #2 1101 | YOSEMITE | 1.1766 | 0 | 10 | 0% | 37.67% | 0 | 0.099229 | 1 | 1.0317 | 0.10237 | Low | Low | Low | 638 | 545 | 0.099229
CAYUCOS 1101 | LOS PADRES | 2.0954 | 62.8302 | 2897 | 4.545% | 0% | 0 | 0.071036 | 1 | 1.4406 | 0.10233 | Low | Low | Low | 639 | 615 | 0.071036
ROSSMOOR 1104 | DIABLO | 0.24893 | 134.119 | 2611.9 | 1.278% | 0% | 0 | 0.036855 | 1 | 2.749 | 0.10132 | Low | Low | High | 640 | 682 | 0.036855
GLENN 1101 | NORTH VALLEY | 2.3498 | 17.4579 | 2361 | 1.737% | 0% | 0 | 0.11765 | 1 | 0.82835 | 0.097452 | Medium | Low | Low | 641 | 494 | 0.11765
FORT BRAGG A 1103 | HUMBOLDT | 0.37656 | 35.7437 | 95.5 | 14.09% | 0% | 0 | 0.058574 | 1 | 1.6248 | 0.095172 | Low | Low | Low | 642 | 644 | 0.058574
BRENTWOOD 2105 | DIABLO | 9.8403 | 32.0715 | 2821 | 11.19% | 0% | 0 | 0.11866 | 1 | 0.79064 | 0.093818 | Medium | Low | Low | 643 | 491 | 0.11866
MC KEE 1103 | SAN JOSE | 2.8083 | 59.3192 | 1308 | 12.74% | 0% | 0 | 0.062858 | 1 | 1.449 | 0.091084 | Low | Low | Low | 644 | 635 | 0.062858
SWIFT 2107 | SAN JOSE | 2.6821 | 54.8728 | 659 | 22.33% | 0% | 0 | 0.08203 | 1 | 1.0702 | 0.087785 | Low | Low | Low | 645 | 582 | 0.08203
NEWBURG 1133 | HUMBOLDT | 3.7712 | 114.96 | 1933.5 | 22.42% | 0% | 0 | 0.071452 | 1 | 1.1791 | 0.084247 | Low | Low | Low | 646 | 612 | 0.071452
SAUSALITO 1101 | NORTH BAY | 0.58117 | 157.5989 | 1070.9 | 8.553% | 0% | 0 | 0.032166 | 1 | 2.5729 | 0.08276 | Low | Low | High | 647 | 686 | 0.032166
SANTA YNEZ 1102 | LOS PADRES | 6.558 | 324.4663 | 6258.5 | 34% | 0% | 0 | 0.057906 | 1 | 1.3121 | 0.07598 | Low | Low | Low | 648 | 648 | 0.057906
ELK CREEK 1101 | NORTH VALLEY | 82.7232 | 10.5621 | 1916 | 45.6% | 0% | 0 | 0.21711 | 1 | 0.34119 | 0.074075 | Medium | Low | Low | 649 | 373 | 0.21711
SNEATH LANE 1102 | PENINSULA | 0.30787 | 146.875 | 1546.3 | 2.924% | 0% | 0 | 0.032278 | 1 | 2.2678 | 0.073201 | Low | Low | Medium | 650 | 685 | 0.032278
SWIFT 2109 | SAN JOSE | 0.30955 | 52.0533 | 280 | 5.755% | 0% | 0 | 0.059782 | 1 | 1.1399 | 0.068145 | Low | Low | Low | 651 | 641 | 0.059782
CARMEL 0405 | CENTRAL COAST | 0.33684 | 180.2265 | 1052 | 5.771% | 0% | 0 | 0.026235 | 1 | 2.4979 | 0.065534 | Low | Low | High | 652 | 688 | 0.026235
REEDLEY 1112 | FRESNO | 0.0028032 | 9.4725 | 852.5 | 0.003115% | 0% | 0 | 0.058029 | 1 | 1.1037 | 0.064046 | Low | Low | Low | 653 | 647 | 0.058029
COPPERMINE 1104 | FRESNO | 8.1519 | 24.5997 | 2161 | 9.28% | 0% | 0 | 0.12252 | 1 | 0.48792 | 0.059782 | Medium | Low | Low | 654 | 477 | 0.12252
PLACER 1101 | SIERRA | 0.77573 | 233.8154 | 1771.9 | 10.24% | 0% | 0 | 0.023381 | 1 | 2.3548 | 0.055058 | Low | Low | Medium | 655 | 689 | 0.023381
CAMPHORA 1101 | CENTRAL COAST | 1.4665 | 0.11504 | 5 | 3.374% | 0% | 0 | 0.10435 | 1 | 0.51261 | 0.053489 | Low | Low | Low | 656 | 523 | 0.10435
GRASS VALLEY 1101 | SIERRA | 17.394 | 833.7564 | 15666.7 | 92.57% | 14.84% | 1 | 0.026844 | 1 | 1.9915 | 0.05346 | Low | Low | Medium | 657 | 687 | 0.026844
RED BLUFF 1103 | NORTH VALLEY | 15.929 | 13.8952 | 526.5 | 42.04% | 0% | 1 | 0.18556 | 1 | 0.26903 | 0.04992 | Medium | Low | Low | 658 | 409 | 0.18556
POTTER VALLEY PH 1105 | HUMBOLDT | 0.0052407 | 78.6372 | 5732 | 0.00719% | 0% | 0 | 0.066957 | 1 | 0.64735 | 0.043345 | Low | Low | Low | 659 | 624 | 0.066957
SISQUOC 1102 | LOS PADRES | 48.4935 | 11.2634 | 1326.5 | 41.18% | 65.24% | 0 | 0.15775 | 1 | 0.2606 | 0.041108 | Medium | Low | Low | 660 | 438 | 0.15775
GONZALES 1103 | CENTRAL COAST | 1.0413 | 25.8595 | 560 | 4.808% | 0% | 0 | 0.074278 | 1 | 0.55053 | 0.040892 | Low | Low | Low | 661 | 600 | 0.074278
COVELO 1101 | HUMBOLDT | 9.9189 | 6.0057 | 675.5 | 8.819% | 0% | 1 | 0.14085 | 1 | 0.27513 | 0.038751 | Medium | Low | Low | 662 | 454 | 0.14085
SOLEDAD 1114 | CENTRAL COAST | 0.90872 | 104.7796 | 1950.2 | 4.882% | 0% | 0 | 0.044957 | 1 | 0.75791 | 0.034073 | Low | Low | Low | 663 | 675 | 0.044957
LOS COCHES 1101 | CENTRAL COAST | 2.6219 | 149.6639 | 4542 | 8.639% | 0% | 0 | 0.050557 | 1 | 0.66337 | 0.033538 | Low | Low | Low | 664 | 663 | 0.050557
CLAY 1102 | STOCKTON | 1.1664 | 433.7192 | 895.5 | 56.49% | 0% | 0 | 0.015108 | 1 | 2.1257 | 0.032116 | Low | Low | Medium | 665 | 690 | 0.015108
OROSI 1102 | FRESNO | 0.26307 | 6.3215 | 221 | 0.7525% | 0% | 0 | 0.099308 | 1 | 0.31434 | 0.031216 | Low | Low | Low | 666 | 544 | 0.099308
DIAMOND SPRINGS 1104 | SIERRA | 14.2466 | 902.6983 | 16914.4 | 76.03% | 61.8% | 0 | 0.013622 | 1 | 2.013 | 0.027421 | Low | Low | Medium | 667 | 691 | 0.013622
CARMEL 0402 | CENTRAL COAST | 0.30828 | 437.2599 | 1343 | 10.04% | 0% | 0 | 0.0071403 | 1 | 2.5278 | 0.018049 | Low | Low | High | 668 | 692 | 0.0071403
MC ARTHUR 1102 | NORTH VALLEY | 0.91154 | 10.5192 | 316 | 3.034% | 0% | 0 | 0.10164 | 1 | 0.16368 | 0.016637 | Low | Low | Low | 669 | 532 | 0.10164
RAWSON 1103 | NORTH VALLEY | 2.3781 | 43.8034 | 1730.3 | 6.02% | 0% | 0 | 0.091986 | 1 | 0.16783 | 0.015438 | Low | Low | Low | 670 | 563 | 0.091986
EEL RIVER 1103 | HUMBOLDT | 2.3658 | 38.1115 | 2275.5 | 3.962% | 0% | 0 | 0.061664 | 1 | 0.16129 | 0.0099458 | Low | Low | Low | 671 | 638 | 0.061664
BRUNSWICK 1107 | SIERRA | 7.6934 | 1170.784 | 22715.2 | 39.65% | 25.27% | 1 | 0.0033153 | 1 | 2.1776 | 0.0072194 | Low | Low | Medium | 672 | 693 | 0.0033153
SPAULDING 1101 | SIERRA | 20.1063 | 68.9488 | 1688.7 | 82.09% | 8.84% | 1 | 0.24777 | 1 | 0.028551 | 0.0070739 | Medium | Low | Low | 673 | 348 | 0.24777
MC ARTHUR 1101 | NORTH VALLEY | 68.9373 | 20.8696 | 3705.5 | 38.83% | 0% | 0 | 0.21153 | 1 | 0.0054002 | 0.0011423 | Medium | Low | Low | 674 | 378 | 0.21153
HOLLISTER 2104 | CENTRAL COAST | 6.0574 | 25.3778 | 3075 | 4.999% | 0% | 0 | 0.12715 | 1 | 0.0080867 | 0.0010282 | Medium | Low | Low | 675 | 472 | 0.12715
FLINT 1102 | SIERRA | 0.092844 | 16120.6897 | 1496 | 100% | 0% | 0 | 2.2204e-16 | 1 | 2.2896 | 5.0839e-16 | Low | Low | Medium | 676 | 694 | 2.2204e-16
PLACERVILLE 1109 | SIERRA | 0.020146 | 22114.4279 | 444.5 | 100% | 0% | 0 | 2.2204e-16 | 1 | 1.7652 | 3.9196e-16 | Low | Low | Medium | 677 | 694 | 2.2204e-16
HIGGINS 1108 | SIERRA | 0.020411 | 627063.7255 | 12792.1 | 100% | 0% | 0 | 2.2204e-16 | 1 | 1.6813 | 3.7332e-16 | Low | Low | Medium | 678 | 694 | 2.2204e-16
GONZALES 1104 | CENTRAL COAST | 0.90277 | 0.074226 | 4 | 1.675% | 0% | 0 | 0.1017 | 47.6367 | 0 | 0 | Low | High | Low | 679 | 93 | 4.8445
CORTINA 1101 | SACRAMENTO | 1.036 | 11.8 | 902 | 1.355% | 0% | 0 | 0.1043 | 35.3263 | 0 | 0 | Low | High | Low | 679 | 100 | 3.6847
HOLLISTER 2105 | CENTRAL COAST | 61.272 | 46.1925 | 7314.4 | 38.69% | 0% | 1 | 0.25084 | 1 | 0 | 0 | Medium | Low | Low | 679 | 343 | 0.25084
MADISON 2101 | SACRAMENTO | 7.647 | 37.6304 | 6246.5 | 4.607% | 0% | 0 | 0.15967 | 1 | 0 | 0 | Medium | Low | Low | 679 | 437 | 0.15967
GONZALES 1101 | CENTRAL COAST | 3.5612 | 14.01 | 362 | 13.78% | 0% | 0 | 0.12168 | 1 | 0 | 0 | Medium | Low | Low | 679 | 478 | 0.12168
CAL WATER 1102 | KERN | 2.9688 | 22.0304 | 583 | 11.22% | 0% | 0 | 0.11156 | 1 | 0 | 0 | Low | Low | Low | 679 | 509 | 0.11156
LOS MOLINOS 1101 | NORTH VALLEY | 0.1275 | 17.4317 | 974 | 0.2282% | 0% | 0 | 0.10041 | 1 | 0 | 0 | Low | Low | Low | 679 | 538 | 0.10041
STONE CORRAL 1110 | FRESNO | 2.3189 | 12.2808 | 771.1 | 3.693% | 0% | 0 | 0.080627 | 1 | 0 | 0 | Low | Low | Low | 679 | 586 | 0.080627
SISQUOC 1103 | LOS PADRES | 27.7554 | 31.2985 | 1567 | 55.44% | 86.45% | 1 | 0.19534 | 1 | 0 | 0 | Medium | Low | Low | 679 | 398 | 0.19534
KERN OIL 1106 | KERN | 1.5124 | 22.8666 | 1025 | 3.374% | 0% | 0 | 0.067355 | 1 | 0 | 0 | Low | Low | Low | 679 | 623 | 0.067355
SPENCE 1123 | CENTRAL COAST | 2.0801 | 63.6257 | 2140 | 6.184% | 0% | 0 | 0.097986 | 1 | 0 | 0 | Low | Low | Low | 679 | 549 | 0.097986
CHOLAME 2102 | LOS PADRES | 58.4006 | 6.9776 | 1509 | 27% | 0% | 0 | 0.16972 | 1 | 0 | 0 | Medium | Low | Low | 679 | 426 | 0.16972
SPENCE 1122 | CENTRAL COAST | 9.9861 | 4.7822 | 251 | 19.03% | 0% | 0 | 0.098373 | 1 | 0 | 0 | Low | Low | Low | 679 | 547 | 0.098373
STONE CORRAL 1108 | FRESNO | 2.9159 | 7.9922 | 611 | 3.814% | 0% | 0 | 0.065911 | 1 | 0 | 0 | Low | Low | Low | 679 | 627 | 0.065911
LAMONT 1102 | KERN | 0.50063 | 0.98972 | 73 | 0.6787% | 0% | 0 | 0.10039 | 1 | 0 | 0 | Low | Low | Low | 679 | 539 | 0.10039
ANTELOPE 1101 | KERN | 0.75322 | 113.4018 | 4500 | 1.898% | 0% | 0 | 0.090369 | 1 | 0 | 0 | Low | Low | Low | 679 | 567 | 0.090369
CUYAMA 1103 | KERN | 2.3769 | 4.7667 | 377.5 | 3.001% | 0% | 0 | 0.10517 | 1 | 0 | 0 | Low | Low | Low | 679 | 521 | 0.10517
LOGAN CREEK 2102 | NORTH VALLEY | 3.7103 | 10.2135 | 2448.2 | 1.548% | 0% | 0 | 0.12256 | 1 | 0 | 0 | Medium | Low | Low | 679 | 476 | 0.12256

## Dx - SH
Dx Prioritization Output - System Hardening | [5 empty] | Planned 2019 implementation
Circuit Information |  |  |  | Independent Variables | [5 empty] | Dependent Variable | Risk Scoring |  |  |  |  | Risk Tiers
Protection Zone | Feeder Name | District | Tier 2/3 OH Miles | Env Risk Component | Material A - % of total miles | Vegetation Outages | Company Outages | HFTD Miles per Total Miles | Tier 3 per HFTD Miles | Ignition Indicator (1+ ignition occurred) | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Consolidated Risk Score | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Rank Cons Risk | Rank P*C | P*C
MIWUK 170110600 | MIWUK 1701 | YOSEMITE | 10.9092 | 90.0653 | 100% | 20 | 16 | 100% | 100% | 1 | 0.80002 | 102.1389 | 3.3891 | 276.9352 | High | High | High | 1 | 1 | 81.7128
MIWUK 1701CB | MIWUK 1701 | YOSEMITE | 17.9054 | 91.659 | 81.59% | 16 | 15 | 100% | 100% | 0 | 0.65411 | 102.1389 | 2.9532 | 197.3013 | High | High | Medium | 2 | 4 | 66.8104
ORO FINO 1101CB | ORO FINO 1101 | NORTH VALLEY | 22.1887 | 87.2953 | 86.14% | 9 | 11 | 100% | 100% | 0 | 0.48349 | 102.1389 | 3.5195 | 173.8066 | High | High | High | 3 | 14 | 49.3837
STANISLAUS 17021888 | STANISLAUS 1702 | YOSEMITE | 18.9533 | 77.9476 | 99.71% | 9 | 14 | 100% | 100% | 0 | 0.44468 | 102.1389 | 2.9998 | 136.2467 | High | High | Medium | 4 | 19 | 45.4193
PINE GROVE 110245292 | PINE GROVE 1102 | STOCKTON | 10.8778 | 85.9329 | 100% | 1 | 11 | 100% | 99.38% | 0 | 0.44757 | 102.1389 | 2.8406 | 129.855 | High | High | Medium | 5 | 18 | 45.714
BRUNSWICK 11021010 | BRUNSWICK 1102 | SIERRA | 44.041 | 87.3695 | 84.93% | 12 | 13 | 100% | 98.91% | 0 | 0.59607 | 102.1389 | 2.1263 | 129.4525 | High | High | Low | 6 | 6 | 60.8822
BRUNSWICK 110350070 | BRUNSWICK 1103 | SIERRA | 28.1191 | 94.0552 | 99.83% | 13 | 12 | 100% | 100% | 1 | 0.54169 | 102.1389 | 2.325 | 128.6353 | High | High | Medium | 7 | 8 | 55.3273
SALT SPRINGS 21023142 | SALT SPRINGS 2102 | STOCKTON | 16.894 | 90.205 | 100% | 15 | 9 | 100% | 100% | 0 | 0.62396 | 102.1389 | 2.0116 | 128.2018 | High | High | Low | 8 | 5 | 63.7309
BRUNSWICK 110532536 | BRUNSWICK 1105 | SIERRA | 21.7333 | 94.8632 | 99.08% | 11 | 14 | 100% | 100% | 0 | 0.54536 | 102.1389 | 2.2664 | 126.2441 | High | High | Medium | 9 | 7 | 55.7026
ORO FINO 11012022 | ORO FINO 1101 | NORTH VALLEY | 24.1719 | 81.0032 | 94.33% | 6 | 13 | 100% | 100% | 1 | 0.36043 | 102.1389 | 3.4228 | 126.0056 | High | High | High | 10 | 35 | 36.814
WYANDOTTE 11031974 | WYANDOTTE 1103 | NORTH VALLEY | 22.8741 | 92.9076 | 99.55% | 6 | 6 | 100% | 100% | 1 | 0.45135 | 102.1389 | 2.7281 | 125.7679 | High | High | Medium | 11 | 16 | 46.1001
MIWUK 17018060 | MIWUK 1701 | YOSEMITE | 11.8537 | 93.2164 | 72.89% | 5 | 17 | 100% | 100% | 0 | 0.41847 | 102.1389 | 2.916 | 124.6332 | High | High | Medium | 12 | 23 | 42.7418
EL DORADO PH 210119752 | EL DORADO PH 2101 | SIERRA | 38.577 | 80.8747 | 99.99% | 20 | 11 | 100% | 99.16% | 1 | 0.69086 | 102.1389 | 1.6995 | 119.922 | High | High | Low | 13 | 2 | 70.5639
PARADISE 11062084 | PARADISE 1106 | NORTH VALLEY | 11.3566 | 77.2193 | 100% | 4 | 9 | 100% | 100% | 1 | 0.28289 | 102.1389 | 4.0673 | 117.5206 | High | High | High | 14 | 69 | 28.8939
LOS GATOS 110760114 | LOS GATOS 1107 | DE ANZA | 24.3274 | 75.5493 | 92.99% | 9 | 3 | 100% | 100% | 1 | 0.66312 | 65.3912 | 2.5859 | 112.1303 | High | High | Medium | 15 | 21 | 43.362
PLACERVILLE 21061104 | PLACERVILLE 2106 | SIERRA | 50.3628 | 96.0676 | 90.37% | 13 | 6 | 100% | 100% | 1 | 0.49422 | 102.1389 | 2.2151 | 111.8183 | High | High | Low | 16 | 13 | 50.479
MONTE RIO 1113524 | MONTE RIO 1113 | SONOMA | 6.2702 | 72.7249 | 28.23% | 16 | 4 | 100% | 100% | 0 | 0.30334 | 102.1389 | 3.5196 | 109.0471 | High | High | High | 17 | 55 | 30.9824
EL DORADO PH 21016852 | EL DORADO PH 2101 | SIERRA | 25.3514 | 89.3624 | 96.21% | 18 | 8 | 100% | 100% | 0 | 0.52183 | 102.1389 | 2.0051 | 106.8716 | High | High | Low | 18 | 10 | 53.299
STANISLAUS 17021804 | STANISLAUS 1702 | YOSEMITE | 8.3693 | 84.6121 | 100% | 9 | 6 | 100% | 100% | 0 | 0.38328 | 102.1389 | 2.7274 | 106.7718 | High | High | Medium | 19 | 29 | 39.1474
PINE GROVE 11021222 | PINE GROVE 1102 | STOCKTON | 17.2284 | 80.3851 | 88.79% | 6 | 14 | 100% | 93.15% | 0 | 0.35881 | 102.1389 | 2.8894 | 105.8932 | High | High | Medium | 20 | 36 | 36.6489
BRUNSWICK 11052210 | BRUNSWICK 1105 | SIERRA | 22.8031 | 97.1876 | 99.8% | 8 | 12 | 100% | 100% | 0 | 0.53048 | 102.1389 | 1.9441 | 105.3388 | High | High | Low | 21 | 9 | 54.1827
BRUNSWICK 11052140 | BRUNSWICK 1105 | SIERRA | 34.5645 | 95.4853 | 99.76% | 25 | 10 | 100% | 100% | 0 | 0.50651 | 102.1389 | 1.9239 | 99.5327 | High | High | Low | 22 | 12 | 51.7342
MIWUK 17026018 | MIWUK 1702 | YOSEMITE | 19.5117 | 86.3615 | 100% | 3 | 8 | 100% | 100% | 0 | 0.28867 | 102.1389 | 3.358 | 99.0086 | High | High | High | 23 | 64 | 29.4843
CALISTOGA 1101736 | CALISTOGA 1101 | NORTH BAY | 33.5094 | 79.1543 | 66.69% | 16 | 14 | 100% | 100% | 1 | 0.74565 | 47.6367 | 2.7749 | 98.5658 | High | High | Medium | 24 | 38 | 35.5203
MIWUK 1702CB | MIWUK 1702 | YOSEMITE | 10.2382 | 90.3115 | 82.25% | 5 | 6 | 100% | 100% | 0 | 0.28839 | 102.1389 | 3.3177 | 97.7246 | High | High | High | 25 | 65 | 29.4558
MIWUK 1702S2247 | MIWUK 1702 | YOSEMITE | 1.4764 | 81.7159 | 100% | 2 | 2 | 100% | 100% | 0 | 0.23034 | 102.1389 | 4.1204 | 96.9423 | High | High | High | 26 | 106 | 23.5271
ORO FINO 110276008 | ORO FINO 1102 | NORTH VALLEY | 15.9665 | 80.1873 | 99.98% | 4 | 7 | 100% | 100% | 1 | 0.36557 | 102.1389 | 2.5923 | 96.7928 | High | High | Medium | 27 | 33 | 37.3387
PARADISE 11062234 | PARADISE 1106 | NORTH VALLEY | 8.8367 | 79.1592 | 100% | 3 | 8 | 100% | 100% | 0 | 0.30628 | 85.4511 | 3.6642 | 95.9005 | High | High | High | 28 | 87 | 26.1721
FORESTHILL 11011802 | FORESTHILL 1101 | SIERRA | 22.1758 | 72.9192 | 91.83% | 12 | 21 | 100% | 100% | 0 | 0.40081 | 102.1389 | 2.3329 | 95.5024 | High | High | Medium | 29 | 26 | 40.9378
MIDDLETOWN 1101548 | MIDDLETOWN 1101 | HUMBOLDT | 22.1669 | 84.1532 | 73.95% | 13 | 16 | 88.6% | 97.32% | 1 | 0.42028 | 102.1389 | 2.2085 | 94.8039 | High | High | Low | 30 | 22 | 42.9273
WEST POINT 11014706 | WEST POINT 1101 | STOCKTON | 11.5214 | 90.5528 | 100% | 4 | 4 | 100% | 100% | 0 | 0.36745 | 102.1389 | 2.5195 | 94.5581 | High | High | Medium | 31 | 32 | 37.5307
MIWUK 170238218 | MIWUK 1702 | YOSEMITE | 10.8246 | 77.698 | 74.49% | 4 | 9 | 100% | 100% | 0 | 0.26818 | 102.1389 | 3.4335 | 94.0487 | High | High | High | 32 | 79 | 27.3914
WOODACRE 1101404 | WOODACRE 1101 | NORTH BAY | 12.4182 | 78.1166 | 26.88% | 20 | 20 | 100% | 92.07% | 0 | 0.22897 | 102.1389 | 3.9584 | 92.5757 | High | High | High | 33 | 107 | 23.3871
CALISTOGA 110143924 | CALISTOGA 1101 | NORTH BAY | 4.45 | 80.4513 | 94.31% | 6 | 6 | 47.81% | 100% | 0 | 0.32892 | 85.4511 | 3.2727 | 91.9855 | High | High | High | 34 | 73 | 28.1068
BRUNSWICK 110651486 | BRUNSWICK 1106 | SIERRA | 56.6992 | 84.1552 | 88.14% | 22 | 15 | 100% | 87.68% | 1 | 0.49605 | 85.4511 | 2.1451 | 90.9285 | High | High | Low | 35 | 24 | 42.3883
SILVERADO 2104632 | SILVERADO 2104 | NORTH BAY | 18.1239 | 77.5447 | 73.72% | 15 | 5 | 96.09% | 100% | 1 | 0.42045 | 65.3912 | 3.2929 | 90.5343 | High | High | High | 36 | 78 | 27.494
STANISLAUS 170237276 | STANISLAUS 1702 | YOSEMITE | 11.7226 | 82.7291 | 100% | 8 | 9 | 100% | 100% | 0 | 0.30163 | 102.1389 | 2.8831 | 88.8242 | High | High | Medium | 37 | 57 | 30.8083
WEST POINT 110136674 | WEST POINT 1101 | STOCKTON | 9.4896 | 86.8002 | 98.6% | 2 | 6 | 100% | 100% | 0 | 0.39381 | 102.1389 | 2.2058 | 88.7227 | High | High | Low | 38 | 27 | 40.2233
MOLINO 1102318 | MOLINO 1102 | SONOMA | 19.2803 | 89.5364 | 61.35% | 11 | 8 | 100% | 100% | 1 | 0.39524 | 85.4511 | 2.6124 | 88.2297 | High | High | Medium | 39 | 45 | 33.7736
PUEBLO 2102792 | PUEBLO 2102 | NORTH BAY | 17.9619 | 85.883 | 96.12% | 13 | 4 | 86.21% | 100% | 0 | 0.41118 | 85.4511 | 2.4971 | 87.7383 | High | High | Medium | 40 | 40 | 35.1362
EL DORADO PH 210219542 | EL DORADO PH 2102 | SIERRA | 9.4332 | 77.5631 | 77.77% | 6 | 4 | 100% | 100% | 0 | 0.31239 | 102.1389 | 2.74 | 87.4241 | High | High | Medium | 41 | 52 | 31.907
FORESTHILL 110150486 | FORESTHILL 1101 | SIERRA | 11.6566 | 81.112 | 97.86% | 4 | 8 | 100% | 100% | 0 | 0.43184 | 102.1389 | 1.9713 | 86.9475 | High | High | Low | 42 | 20 | 44.1076
MIRABEL 1101298 | MIRABEL 1101 | SONOMA | 12.8273 | 89.1513 | 37.51% | 16 | 9 | 99.59% | 100% | 0 | 0.33734 | 85.4511 | 2.9749 | 85.7551 | High | High | Medium | 43 | 70 | 28.8258
MARIPOSA 210110170 | MARIPOSA 2101 | YOSEMITE | 16.3113 | 93.2169 | 77.6% | 14 | 34 | 100% | 100% | 1 | 0.51304 | 102.1389 | 1.5869 | 83.1571 | High | High | Low | 44 | 11 | 52.4012
MIWUK 17018050 | MIWUK 1701 | YOSEMITE | 12.1253 | 91.2725 | 97.35% | 8 | 4 | 100% | 100% | 1 | 0.26086 | 102.1389 | 3.1093 | 82.8459 | High | High | High | 45 | 85 | 26.6441
CAMP EVERS 21065020 | CAMP EVERS 2106 | CENTRAL COAST | 15.2094 | 69.3374 | 87.56% | 19 | 11 | 100% | 100% | 1 | 0.52218 | 65.3912 | 2.4231 | 82.7401 | High | High | Medium | 46 | 44 | 34.1458
CHALLENGE 1101CB | CHALLENGE 1101 | NORTH VALLEY | 16.6203 | 96.135 | 99.73% | 4 | 3 | 100% | 100% | 0 | 0.37094 | 102.1389 | 2.1782 | 82.5265 | High | High | Low | 47 | 31 | 37.8874
MIWUK 1702S1547 | MIWUK 1702 | YOSEMITE | 2.7688 | 85.4231 | 100% | 1 | 5 | 100% | 100% | 0 | 0.24392 | 102.1389 | 3.3077 | 82.4079 | High | High | High | 48 | 95 | 24.9141
PINE GROVE 110213438 | PINE GROVE 1102 | STOCKTON | 16.4176 | 84.6476 | 100% | 6 | 6 | 100% | 85.87% | 0 | 0.38268 | 102.1389 | 2.1023 | 82.1729 | High | High | Low | 49 | 30 | 39.087
WILLITS 110434008 | WILLITS 1104 | HUMBOLDT | 22.9278 | 77.1143 | 100% | 14 | 12 | 100% | 97.76% | 0 | 0.3764 | 85.4511 | 2.5543 | 82.1564 | High | High | Medium | 50 | 49 | 32.1635
WYANDOTTE 11031976 | WYANDOTTE 1103 | NORTH VALLEY | 23.9896 | 86.4323 | 100% | 4 | 6 | 100% | 100% | 0 | 0.43481 | 85.4511 | 2.2058 | 81.9573 | High | High | Low | 51 | 34 | 37.155
EL DORADO PH 210219562 | EL DORADO PH 2102 | SIERRA | 14.8519 | 89.5871 | 100% | 10 | 7 | 100% | 100% | 0 | 0.33748 | 102.1389 | 2.3227 | 80.0616 | High | High | Medium | 52 | 42 | 34.4696
STANISLAUS 170275348 | STANISLAUS 1702 | YOSEMITE | 5.3962 | 93.3092 | 100% | 1 | 9 | 100% | 100% | 0 | 0.29738 | 102.1389 | 2.6132 | 79.3742 | High | High | Medium | 53 | 59 | 30.3738
MONTE RIO 1112120 | MONTE RIO 1112 | SONOMA | 6.8692 | 90.5188 | 64.49% | 17 | 9 | 100% | 100% | 0 | 0.33336 | 85.4511 | 2.7822 | 79.2535 | High | High | Medium | 54 | 72 | 28.4857
ALLEGHANY 1101VR816 | ALLEGHANY 1101 | SIERRA | 4.1512 | 96.2894 | 73.9% | 6 | 8 | 100% | 100% | 0 | 0.294 | 102.1389 | 2.6166 | 78.5756 | High | High | Medium | 55 | 60 | 30.0293
PIKE CITY 1101CB | PIKE CITY 1101 | SIERRA | 19.8554 | 96.0592 | 99.76% | 13 | 13 | 100% | 100% | 1 | 0.38542 | 102.1389 | 1.982 | 78.0243 | High | High | Low | 56 | 28 | 39.3662
CAMP EVERS 210660124 | CAMP EVERS 2106 | CENTRAL COAST | 22.5394 | 63.6568 | 80.34% | 20 | 3 | 100% | 100% | 1 | 0.4923 | 65.3912 | 2.4068 | 77.4809 | High | High | Medium | 57 | 48 | 32.1923
MONTE RIO 1113202 | MONTE RIO 1113 | SONOMA | 5.2496 | 89.4483 | 68.59% | 13 | 9 | 100% | 100% | 0 | 0.2988 | 85.4511 | 3.0343 | 77.4749 | High | High | Medium | 58 | 92 | 25.5328
WOODSIDE 11018974 | WOODSIDE 1101 | PENINSULA | 13.435 | 54.2631 | 29.29% | 40 | 16 | 100% | 100% | 0 | 0.50532 | 47.6367 | 3.1586 | 76.0338 | High | High | High | 59 | 99 | 24.0717
RINCON 1103474 | RINCON 1103 | SONOMA | 18.561 | 87.2265 | 99.41% | 8 | 6 | 100% | 100% | 0 | 0.44799 | 65.3912 | 2.5873 | 75.7944 | High | High | Medium | 60 | 67 | 29.2949
ORO FINO 11022560 | ORO FINO 1102 | NORTH VALLEY | 16.7196 | 97.5242 | 100% | 5 | 6 | 100% | 81.54% | 1 | 0.26733 | 102.1389 | 2.775 | 75.7698 | High | High | Medium | 61 | 81 | 27.3045
COLUMBIA HILL 110135424 | COLUMBIA HILL 1101 | SIERRA | 13.9113 | 71.6588 | 100% | 8 | 11 | 100% | 100% | 1 | 0.44882 | 65.3912 | 2.5252 | 74.113 | High | High | Medium | 62 | 66 | 29.3488
WEST POINT 110113444 | WEST POINT 1101 | STOCKTON | 16.633 | 82.1566 | 100% | 5 | 15 | 100% | 100% | 0 | 0.31924 | 102.1389 | 2.2583 | 73.6364 | High | High | Medium | 63 | 46 | 32.6072
SILVERADO 210478268 | SILVERADO 2104 | NORTH BAY | 11.9793 | 67.2464 | 60.11% | 10 | 4 | 100% | 100% | 0 | 0.3351 | 65.3912 | 3.3562 | 73.5434 | High | High | High | 64 | 126 | 21.9127
CHALLENGE 1102CB | CHALLENGE 1102 | NORTH VALLEY | 15.5217 | 96.52 | 90.77% | 6 | 5 | 100% | 100% | 0 | 0.4019 | 102.1389 | 1.7913 | 73.5318 | High | High | Low | 65 | 25 | 41.0501
STANISLAUS 17021850 | STANISLAUS 1702 | YOSEMITE | 13.465 | 54.7158 | 83.98% | 13 | 14 | 100% | 100% | 0 | 0.32626 | 65.3912 | 3.431 | 73.1995 | High | High | High | 66 | 135 | 21.3346
EL DORADO PH 210126000 | EL DORADO PH 2101 | SIERRA | 34.0468 | 93.5067 | 99.32% | 9 | 8 | 100% | 100% | 0 | 0.57184 | 85.4511 | 1.4969 | 73.1469 | High | High | Low | 67 | 15 | 48.8647
BIG BEND 11021972 | BIG BEND 1102 | NORTH VALLEY | 21.0549 | 95.6632 | 96.1% | 4 | 6 | 100% | 100% | 0 | 0.40978 | 85.4511 | 2.086 | 73.0443 | High | High | Low | 68 | 41 | 35.0163
WEST POINT 1101L373 | WEST POINT 1101 | STOCKTON | 7.4413 | 94.6949 | 100% | 2 | 9 | 100% | 100% | 0 | 0.30215 | 102.1389 | 2.361 | 72.8632 | High | High | Medium | 69 | 56 | 30.8608
SAN RAFAEL 11081250 | SAN RAFAEL 1108 | NORTH BAY | 3.5796 | 93.2481 | 59.75% | 1 | 1 | 100% | 100% | 1 | 0.20419 | 85.4511 | 4.1107 | 71.7241 | High | High | High | 70 | 180 | 17.4483
BONNIE NOOK 1102CB | BONNIE NOOK 1102 | SIERRA | 34.3352 | 94.488 | 85.18% | 18 | 16 | 100% | 100% | 0 | 0.44981 | 102.1389 | 1.5484 | 71.1385 | High | High | Low | 71 | 17 | 45.9434
ORO FINO 11022090 | ORO FINO 1102 | NORTH VALLEY | 14.7385 | 94.0575 | 68.97% | 5 | 5 | 100% | 100% | 1 | 0.1964 | 102.1389 | 3.5409 | 71.0314 | High | High | High | 72 | 151 | 20.0604
STANISLAUS 1702L611 | STANISLAUS 1702 | YOSEMITE | 2.9906 | 79.5104 | 100% | 2 | 2 | 100% | 100% | 0 | 0.27802 | 85.4511 | 2.9655 | 70.4504 | High | High | Medium | 73 | 103 | 23.757
SYCAMORE CREEK 11112268 | SYCAMORE CREEK 1111 | NORTH VALLEY | 22.2352 | 96.7379 | 99.96% | 3 | 8 | 100% | 99.53% | 1 | 0.2744 | 102.1389 | 2.495 | 69.9295 | High | High | Medium | 74 | 75 | 28.0273
BIG TREES 04025300 | BIG TREES 0402 | CENTRAL COAST | 9.8017 | 22.3436 | 42.94% | 37 | 4 | 100% | 100% | 1 | 0.37529 | 47.6367 | 3.9078 | 69.8624 | High | High | High | 75 | 173 | 17.8776
EL DORADO PH 2101CB | EL DORADO PH 2101 | SIERRA | 16.7983 | 90.3781 | 74.43% | 12 | 5 | 100% | 100% | 0 | 0.3182 | 102.1389 | 2.1319 | 69.2868 | High | High | Low | 76 | 47 | 32.5001
BRUNSWICK 11041020 | BRUNSWICK 1104 | SIERRA | 28.7777 | 77.1 | 87.63% | 9 | 9 | 100% | 83.4% | 1 | 0.27484 | 102.1389 | 2.4581 | 69.005 | High | High | Medium | 77 | 74 | 28.0721
MOLINO 1102104 | MOLINO 1102 | SONOMA | 21.7365 | 84.6047 | 53.29% | 22 | 10 | 100% | 100% | 1 | 0.38423 | 65.3912 | 2.69 | 67.5877 | High | High | Medium | 78 | 93 | 25.1255
PARADISE 11011155 | PARADISE 1101 | NORTH VALLEY | 0.42051 | 84.3729 | 100% | 5 | 1 | 100% | 100% | 0 | 0.21365 | 85.4511 | 3.701 | 67.5683 | High | High | High | 79 | 167 | 18.257
PINE GROVE 11023172 | PINE GROVE 1102 | STOCKTON | 36.8095 | 74.2107 | 73.54% | 9 | 20 | 100% | 71.26% | 1 | 0.23027 | 85.4511 | 3.4298 | 67.4865 | High | High | High | 80 | 154 | 19.6764
BIG BEND 1101CB | BIG BEND 1101 | NORTH VALLEY | 23.102 | 80.4105 | 77.16% | 7 | 10 | 100% | 100% | 1 | 0.34627 | 85.4511 | 2.2328 | 66.0668 | High | High | Medium | 81 | 62 | 29.5895
STANISLAUS 17024905 | STANISLAUS 1702 | YOSEMITE | 2.3422 | 97.8548 | 99.88% | 2 | 2 | 100% | 100% | 0 | 0.25032 | 102.1389 | 2.5717 | 65.75 | High | High | Medium | 82 | 91 | 25.567
MIWUK 17028130 | MIWUK 1702 | YOSEMITE | 9.8769 | 52.0925 | 100% | 2 | 8 | 100% | 100% | 0 | 0.29268 | 65.3912 | 3.427 | 65.5898 | High | High | High | 83 | 160 | 19.1389
KANAKA 110165606 | KANAKA 1101 | NORTH VALLEY | 12.8238 | 91.9272 | 96.33% | 13 | 4 | 100% | 100% | 1 | 0.30035 | 85.4511 | 2.5523 | 65.5039 | High | High | Medium | 84 | 89 | 25.6651
DOWNIEVILLE DIESEL 1101CB | DOWNIEVILLE DIESEL 1101 | SIERRA | 0.022979 | 98 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21467 | 102.1389 | 2.9787 | 65.3131 | High | High | Medium | 85 | 123 | 21.9265
DOWNIEVILLE DIESEL 11011101/2 | DOWNIEVILLE DIESEL 1101 | SIERRA | 0.0097328 | 98 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21467 | 102.1389 | 2.9743 | 65.2163 | High | High | Medium | 86 | 124 | 21.9265
ORO FINO 110265932 | ORO FINO 1102 | NORTH VALLEY | 4.3114 | 96.8708 | 92.73% | 3 | 5 | 100% | 100% | 0 | 0.25228 | 102.1389 | 2.5076 | 64.6157 | High | High | Medium | 87 | 88 | 25.7678
CHALLENGE 11021064 | CHALLENGE 1102 | NORTH VALLEY | 19.9876 | 84.0327 | 100% | 6 | 2 | 100% | 94.93% | 0 | 0.33496 | 102.1389 | 1.8763 | 64.191 | High | High | Low | 88 | 43 | 34.2124
STANISLAUS 1702L5381 | STANISLAUS 1702 | YOSEMITE | 1.2094 | 89.7596 | 100% | 0 | 1 | 100% | 100% | 0 | 0.20877 | 102.1389 | 2.9893 | 63.7424 | High | High | Medium | 89 | 136 | 21.3233
BRUNSWICK 11052130 | BRUNSWICK 1105 | SIERRA | 14.272 | 96.3517 | 99.69% | 5 | 6 | 100% | 100% | 0 | 0.29909 | 102.1389 | 2.0794 | 63.5253 | High | High | Low | 90 | 58 | 30.5492
STANISLAUS 170237278 | STANISLAUS 1702 | YOSEMITE | 6.8063 | 74.4331 | 100% | 1 | 5 | 100% | 100% | 0 | 0.2075 | 102.1389 | 2.9637 | 62.8122 | High | High | Medium | 91 | 137 | 21.1942
MONTE RIO 11138299 | MONTE RIO 1113 | SONOMA | 1.1981 | 94.52 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21069 | 102.1389 | 2.9055 | 62.524 | High | High | Medium | 92 | 133 | 21.5193
ORO FINO 110239154 | ORO FINO 1102 | NORTH VALLEY | 0.88251 | 98 | 100% | 3 | 0 | 100% | 100% | 1 | 0.22144 | 102.1389 | 2.7583 | 62.3862 | High | High | Medium | 93 | 114 | 22.618
WOODACRE 11011238 | WOODACRE 1101 | NORTH BAY | 3.6828 | 94.4368 | 22.55% | 16 | 2 | 100% | 100% | 0 | 0.19161 | 85.4511 | 3.808 | 62.3489 | High | High | High | 94 | 198 | 16.373
BIG BASIN 110110720 | BIG BASIN 1101 | CENTRAL COAST | 4.6838 | 66.6097 | 31.56% | 7 | 1 | 100% | 100% | 0 | 0.21501 | 85.4511 | 3.3585 | 61.7049 | High | High | High | 95 | 164 | 18.3729
WEST POINT 110112256 | WEST POINT 1101 | STOCKTON | 6.5157 | 90.9675 | 74.92% | 4 | 4 | 100% | 100% | 0 | 0.21727 | 102.1389 | 2.7434 | 60.8819 | High | High | Medium | 96 | 119 | 22.192
SILVERADO 2104645 | SILVERADO 2104 | NORTH BAY | 1.0113 | 86.4283 | 53.43% | 4 | 2 | 100% | 100% | 0 | 0.17771 | 85.4511 | 3.9922 | 60.6227 | High | High | High | 97 | 215 | 15.1851
STANISLAUS 1702 | STANISLAUS 1702 | YOSEMITE | 0.0021222 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 102.1389 | 2.8405 | 59.6463 | High | High | Medium | 98 | 140 | 20.9988
APPLE HILL 110413512 | APPLE HILL 1104 | SIERRA | 27.848 | 80.8375 | 86.09% | 15 | 14 | 89.98% | 77.01% | 0 | 0.27338 | 102.1389 | 2.12 | 59.1969 | High | High | Low | 99 | 76 | 27.9228
CAMP EVERS 210510214 | CAMP EVERS 2105 | CENTRAL COAST | 14.0274 | 70.1914 | 71.02% | 31 | 1 | 100% | 100% | 0 | 0.29021 | 65.3912 | 3.1151 | 59.1158 | High | High | High | 100 | 161 | 18.9774
MONTE RIO 111164758 | MONTE RIO 1111 | SONOMA | 10.5474 | 85.3267 | 35.52% | 9 | 6 | 100% | 100% | 0 | 0.26838 | 85.4511 | 2.5622 | 58.7581 | High | High | Medium | 101 | 112 | 22.933
MIWUK 17028090 | MIWUK 1702 | YOSEMITE | 4.0244 | 68.0843 | 40.03% | 1 | 7 | 100% | 100% | 0 | 0.1541 | 102.1389 | 3.6986 | 58.2148 | High | High | High | 102 | 204 | 15.7396
WEST POINT 1101L1969 | WEST POINT 1101 | STOCKTON | 1.0816 | 86.0606 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20122 | 102.1389 | 2.8277 | 58.1165 | High | High | Medium | 103 | 143 | 20.5528
SILVERADO 2105658898 | SILVERADO 2105 | NORTH BAY | 17.239 | 89.5362 | 92.68% | 6 | 3 | 99.53% | 97.17% | 1 | 0.28431 | 65.3912 | 3.1133 | 57.8818 | High | High | High | 104 | 162 | 18.5917
COLUMBIA HILL 1101764 | COLUMBIA HILL 1101 | SIERRA | 14.8572 | 87.6214 | 100% | 5 | 10 | 100% | 100% | 1 | 0.36409 | 85.4511 | 1.8603 | 57.8773 | High | High | Low | 105 | 54 | 31.1119
HALF MOON BAY 11012500 | HALF MOON BAY 1101 | PENINSULA | 5.7745 | 85.7148 | 84.59% | 4 | 6 | 82.94% | 96.61% | 1 | 0.2396 | 65.3912 | 3.6617 | 57.3712 | High | High | High | 106 | 207 | 15.668
VOLTA 110253130 | VOLTA 1102 | NORTH VALLEY | 13.8858 | 76.696 | 100% | 3 | 7 | 100% | 92.09% | 0 | 0.29929 | 85.4511 | 2.2396 | 57.2769 | High | High | Medium | 107 | 90 | 25.5745
PARADISE 110195728 | PARADISE 1101 | NORTH VALLEY | 5.026 | 85.7627 | 38.06% | 1 | 6 | 100% | 100% | 0 | 0.18459 | 85.4511 | 3.6211 | 57.1177 | High | High | High | 108 | 203 | 15.7736
STANISLAUS 17026028 | STANISLAUS 1702 | YOSEMITE | 5.3481 | 47.3801 | 91.01% | 3 | 4 | 100% | 100% | 0 | 0.28374 | 65.3912 | 3.0384 | 56.3747 | High | High | Medium | 109 | 163 | 18.5544
MONTE RIO 11131991 | MONTE RIO 1113 | SONOMA | 7.0583 | 93.2573 | 64.98% | 0 | 4 | 100% | 100% | 0 | 0.19767 | 102.1389 | 2.7908 | 56.3455 | High | High | Medium | 110 | 146 | 20.1896
KANAKA 110183288 | KANAKA 1101 | NORTH VALLEY | 17.5828 | 90.1927 | 100% | 7 | 4 | 100% | 100% | 0 | 0.26111 | 102.1389 | 2.1087 | 56.2379 | High | High | Low | 111 | 84 | 26.6692
SHINGLE SPRINGS 210912392 | SHINGLE SPRINGS 2109 | SIERRA | 14.9169 | 46.1952 | 91.69% | 7 | 8 | 100% | 100% | 0 | 0.31183 | 65.3912 | 2.7319 | 55.7055 | High | High | Medium | 112 | 144 | 20.3908
STELLING 111060094 | STELLING 1110 | DE ANZA | 13.9579 | 79.5 | 89.71% | 7 | 6 | 100% | 94.63% | 1 | 0.27357 | 65.3912 | 3.1124 | 55.6768 | High | High | High | 113 | 172 | 17.8888
WEST POINT 11021303 | WEST POINT 1102 | STOCKTON | 15.8188 | 90.4672 | 99.8% | 4 | 11 | 100% | 100% | 0 | 0.28235 | 85.4511 | 2.2984 | 55.4538 | High | High | Medium | 114 | 98 | 24.1273
MONTE RIO 1113652 | MONTE RIO 1113 | SONOMA | 1.6252 | 74.26 | 59.28% | 4 | 0 | 100% | 100% | 0 | 0.16674 | 102.1389 | 3.2389 | 55.1604 | High | High | High | 115 | 187 | 17.0307
PUEBLO 21033583 | PUEBLO 2103 | NORTH BAY | 9.4952 | 94.4646 | 44.31% | 6 | 11 | 100% | 100% | 1 | 0.25545 | 85.4511 | 2.5196 | 54.9993 | High | High | Medium | 116 | 129 | 21.8289
BRUNSWICK 11032200 | BRUNSWICK 1103 | SIERRA | 5.571 | 90.9239 | 99.7% | 2 | 4 | 100% | 100% | 0 | 0.22488 | 102.1389 | 2.3873 | 54.8339 | High | High | Medium | 117 | 111 | 22.9688
CAMP EVERS 210574170 | CAMP EVERS 2105 | CENTRAL COAST | 3.5599 | 43.1898 | 71.52% | 10 | 5 | 100% | 100% | 0 | 0.19742 | 65.3912 | 4.2334 | 54.6522 | High | High | High | 118 | 254 | 12.9096
MOUNTAIN QUARRIES 21011184 | MOUNTAIN QUARRIES 2101 | SIERRA | 11.7903 | 85.233 | 82.22% | 1 | 4 | 100% | 100% | 0 | 0.21412 | 85.4511 | 2.9723 | 54.3825 | High | High | Medium | 119 | 166 | 18.2964
ALTO 11243121 | ALTO 1124 | NORTH BAY | 2.756 | 78.1169 | 17.87% | 3 | 11 | 100% | 100% | 0 | 0.1536 | 85.4511 | 4.1251 | 54.1442 | High | High | High | 120 | 247 | 13.1255
EL DORADO PH 21026645 | EL DORADO PH 2102 | SIERRA | 4.2976 | 91.6097 | 86.84% | 4 | 3 | 100% | 100% | 0 | 0.23151 | 102.1389 | 2.2842 | 54.0125 | High | High | Medium | 121 | 105 | 23.6465
ORO FINO 11022096 | ORO FINO 1102 | NORTH VALLEY | 14.098 | 93.7734 | 100% | 8 | 2 | 100% | 100% | 0 | 0.28682 | 85.4511 | 2.1974 | 53.8569 | High | High | Low | 122 | 96 | 24.5089
OAKHURST 110310190 | OAKHURST 1103 | YOSEMITE | 11.5271 | 95.517 | 27.67% | 12 | 10 | 100% | 100% | 1 | 0.26739 | 102.1389 | 1.9347 | 52.8379 | High | High | Low | 123 | 80 | 27.311
BRUNSWICK 1105 | BRUNSWICK 1105 | SIERRA | 0.032568 | 98 | 100% | 2 | 0 | 100% | 100% | 0 | 0.21917 | 102.1389 | 2.3469 | 52.5372 | High | High | Medium | 124 | 116 | 22.3858
SILVERADO 21051421 | SILVERADO 2105 | NORTH BAY | 9.2052 | 85.2373 | 78.89% | 5 | 4 | 92.75% | 100% | 1 | 0.22901 | 65.3912 | 3.5009 | 52.427 | High | High | High | 125 | 220 | 14.9751
WEST POINT 11021535 | WEST POINT 1102 | STOCKTON | 3.0651 | 85.9665 | 100% | 1 | 1 | 100% | 100% | 0 | 0.2539 | 85.4511 | 2.4158 | 52.4127 | High | High | Medium | 126 | 131 | 21.6957
MIDDLETOWN 11011079 | MIDDLETOWN 1101 | HUMBOLDT | 3.6508 | 95.1699 | 100% | 2 | 3 | 100% | 100% | 1 | 0.22672 | 102.1389 | 2.2574 | 52.2754 | High | High | Medium | 127 | 108 | 23.1571
PARADISE 11052214 | PARADISE 1105 | NORTH VALLEY | 9.8398 | 58.7584 | 53.2% | 6 | 6 | 86.04% | 100% | 1 | 0.14771 | 102.1389 | 3.4298 | 51.746 | High | High | High | 128 | 217 | 15.0873
PINE GROVE 110235576 | PINE GROVE 1102 | STOCKTON | 7.978 | 78.3459 | 100% | 3 | 1 | 100% | 100% | 0 | 0.22493 | 85.4511 | 2.6836 | 51.5795 | High | High | Medium | 129 | 159 | 19.2204
FORESTHILL 11022106 | FORESTHILL 1102 | SIERRA | 28.0974 | 67.1045 | 99.85% | 8 | 14 | 100% | 71.38% | 1 | 0.26076 | 102.1389 | 1.936 | 51.5625 | High | High | Low | 130 | 86 | 26.6336
MOLINO 110266006 | MOLINO 1102 | SONOMA | 9.0487 | 82.4735 | 54.27% | 8 | 4 | 100% | 100% | 1 | 0.25799 | 65.3912 | 3.052 | 51.4882 | High | High | Medium | 131 | 189 | 16.8704
CURTIS 17022123 | CURTIS 1702 | YOSEMITE | 1.861 | 56.934 | 100% | 1 | 0 | 100% | 100% | 0 | 0.19293 | 65.3912 | 4.0222 | 50.7428 | High | High | High | 132 | 260 | 12.6157
SALT SPRINGS 21024796 | SALT SPRINGS 2102 | STOCKTON | 7.1845 | 85.6584 | 100% | 4 | 1 | 100% | 100% | 0 | 0.34533 | 102.1389 | 1.4356 | 50.6348 | High | High | Low | 133 | 39 | 35.2718
FORESTHILL 1101CB | FORESTHILL 1101 | SIERRA | 9.3514 | 78.4608 | 92.08% | 4 | 4 | 100% | 100% | 0 | 0.33375 | 65.3912 | 2.3144 | 50.5099 | High | High | Medium | 134 | 130 | 21.8245
MOLINO 1102658 | MOLINO 1102 | SONOMA | 10.901 | 83.5071 | 77.94% | 19 | 4 | 100% | 73.87% | 0 | 0.26881 | 65.3912 | 2.8576 | 50.2302 | High | High | Medium | 135 | 176 | 17.5775
SAN RAFAEL 110863598 | SAN RAFAEL 1108 | NORTH BAY | 1.9128 | 87.2214 | 45.64% | 1 | 1 | 100% | 100% | 0 | 0.14368 | 85.4511 | 4.0853 | 50.1574 | High | High | High | 136 | 268 | 12.2776
WEST POINT 1101L2219 | WEST POINT 1101 | STOCKTON | 3.4094 | 90.8965 | 100% | 0 | 2 | 100% | 100% | 0 | 0.26183 | 85.4511 | 2.2217 | 49.7088 | High | High | Low | 137 | 117 | 22.3739
MONTE RIO 1113320 | MONTE RIO 1113 | SONOMA | 2.745 | 95.3298 | 21.97% | 16 | 1 | 100% | 100% | 1 | 0.16899 | 102.1389 | 2.8782 | 49.6792 | High | High | Medium | 138 | 182 | 17.2604
MIWUK 170111800 | MIWUK 1701 | YOSEMITE | 9.4843 | 50.073 | 65.97% | 8 | 9 | 100% | 100% | 0 | 0.20689 | 65.3912 | 3.6538 | 49.4316 | High | High | High | 139 | 239 | 13.5287
ALTO 1125510 | ALTO 1125 | NORTH BAY | 7.3822 | 55.9602 | 19.39% | 13 | 14 | 100% | 100% | 0 | 0.45487 | 26.5534 | 4.0428 | 48.8305 | High | High | High | 140 | 272 | 12.0783
MIWUK 170219772 | MIWUK 1702 | YOSEMITE | 3.8508 | 59.5505 | 82.54% | 2 | 3 | 100% | 100% | 0 | 0.16594 | 85.4511 | 3.4321 | 48.6675 | High | High | High | 141 | 229 | 14.1801
MONTE RIO 1113180 | MONTE RIO 1113 | SONOMA | 1.9463 | 80.579 | 66.84% | 3 | 0 | 100% | 100% | 0 | 0.1611 | 102.1389 | 2.9572 | 48.6589 | High | High | Medium | 142 | 197 | 16.4543
ALLEGHANY 1101806 | ALLEGHANY 1101 | SIERRA | 11.8065 | 97.171 | 100% | 0 | 7 | 100% | 100% | 0 | 0.2646 | 102.1389 | 1.7958 | 48.5336 | High | High | Low | 143 | 82 | 27.0262
MONTE RIO 1113678 | MONTE RIO 1113 | SONOMA | 1.8444 | 89.0499 | 49.28% | 0 | 1 | 100% | 100% | 0 | 0.20505 | 85.4511 | 2.7668 | 48.4785 | High | High | Medium | 144 | 179 | 17.5214
WOODSIDE 11018884 | WOODSIDE 1101 | PENINSULA | 7.7125 | 85.1128 | 91.16% | 13 | 3 | 100% | 100% | 0 | 0.30526 | 65.3912 | 2.4202 | 48.3096 | High | High | Medium | 145 | 152 | 19.9613
OAKHURST 110310723 | OAKHURST 1103 | YOSEMITE | 0.0026429 | 95 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21123 | 102.1389 | 2.2385 | 48.2953 | High | High | Medium | 146 | 132 | 21.5751
CAMP EVERS 210510294 | CAMP EVERS 2105 | CENTRAL COAST | 8.3995 | 27.1368 | 59.21% | 34 | 11 | 100% | 100% | 0 | 0.26177 | 47.6367 | 3.864 | 48.1828 | High | High | High | 147 | 264 | 12.4698
APPLE HILL 110497086 | APPLE HILL 1104 | SIERRA | 25.6232 | 83.1632 | 99.98% | 8 | 5 | 100% | 100% | 1 | 0.28482 | 102.1389 | 1.6526 | 48.0777 | High | High | Low | 148 | 68 | 29.0916
CURTIS 1705843 | CURTIS 1705 | YOSEMITE | 6.6016 | 54.6165 | 100% | 2 | 2 | 100% | 93.53% | 0 | 0.18286 | 85.4511 | 3.052 | 47.6886 | High | High | Medium | 149 | 209 | 15.6252
ELECTRA 110277204 | ELECTRA 1102 | STOCKTON | 18.6351 | 80.9647 | 100% | 2 | 8 | 100% | 100% | 0 | 0.27848 | 85.4511 | 1.9943 | 47.458 | High | High | Low | 150 | 101 | 23.7964
WILLITS 1104504 | WILLITS 1104 | HUMBOLDT | 22.5336 | 70.0895 | 92.93% | 13 | 8 | 100% | 60.82% | 1 | 0.2605 | 85.4511 | 2.1292 | 47.3973 | High | High | Low | 151 | 118 | 22.2602
MIDDLETOWN 1101614 | MIDDLETOWN 1101 | HUMBOLDT | 1.393 | 87.6673 | 76.7% | 0 | 1 | 100% | 100% | 0 | 0.19696 | 85.4511 | 2.8133 | 47.348 | High | High | Medium | 152 | 191 | 16.8302
KONOCTI 1102532 | KONOCTI 1102 | HUMBOLDT | 9.613 | 73.4923 | 78.9% | 8 | 7 | 100% | 100% | 1 | 0.20006 | 85.4511 | 2.7651 | 47.2701 | High | High | Medium | 153 | 186 | 17.0951
WEST POINT 11024790 | WEST POINT 1102 | STOCKTON | 28.9338 | 75.0976 | 91.62% | 9 | 12 | 100% | 75.46% | 1 | 0.35051 | 65.3912 | 2.0584 | 47.1793 | High | High | Low | 154 | 113 | 22.92
MIWUK 170193062 | MIWUK 1701 | YOSEMITE | 8.21 | 73.287 | 98.21% | 5 | 3 | 100% | 79.03% | 0 | 0.17366 | 85.4511 | 3.1781 | 47.1632 | High | High | High | 155 | 223 | 14.8399
PINE GROVE 11029145 | PINE GROVE 1102 | STOCKTON | 2.9225 | 81.0955 | 99.74% | 0 | 0 | 100% | 100% | 0 | 0.19549 | 85.4511 | 2.812 | 46.973 | High | High | Medium | 156 | 193 | 16.7046
MONTE RIO 111264682 | MONTE RIO 1112 | SONOMA | 1.7634 | 73.4411 | 19.23% | 8 | 4 | 100% | 100% | 0 | 0.12546 | 102.1389 | 3.654 | 46.8247 | High | High | High | 157 | 257 | 12.8145
FORESTHILL 11011820 | FORESTHILL 1101 | SIERRA | 5.5828 | 97.995 | 99.82% | 0 | 0 | 100% | 100% | 1 | 0.23777 | 102.1389 | 1.9221 | 46.6794 | High | High | Low | 158 | 97 | 24.2855
SALT SPRINGS 2102L485 | SALT SPRINGS 2102 | STOCKTON | 0.82893 | 87.1462 | 100% | 0 | 2 | 100% | 100% | 0 | 0.23224 | 102.1389 | 1.9664 | 46.6444 | High | High | Low | 159 | 104 | 23.721
SILVERADO 2104722 | SILVERADO 2104 | NORTH BAY | 7.8999 | 65.7561 | 63.09% | 2 | 4 | 100% | 100% | 0 | 0.17105 | 85.4511 | 3.1898 | 46.6231 | High | High | High | 160 | 224 | 14.6165
MOLINO 1102396 | MOLINO 1102 | SONOMA | 16.1282 | 58.4363 | 35.51% | 9 | 10 | 100% | 100% | 0 | 0.275 | 65.3912 | 2.5855 | 46.494 | High | High | Medium | 161 | 171 | 17.9823
WOODACRE 110196844 | WOODACRE 1101 | NORTH BAY | 5.9237 | 87.2691 | 22.46% | 5 | 8 | 100% | 88.33% | 0 | 0.12278 | 102.1389 | 3.7061 | 46.4791 | High | High | High | 162 | 261 | 12.5411
MONTE RIO 1113CB | MONTE RIO 1113 | SONOMA | 4.5623 | 78.3408 | 32.43% | 11 | 4 | 100% | 100% | 0 | 0.18356 | 85.4511 | 2.9514 | 46.2948 | High | High | Medium | 163 | 206 | 15.6855
STANISLAUS 17011331 | STANISLAUS 1701 | YOSEMITE | 4.3931 | 65.9467 | 100% | 5 | 0 | 100% | 100% | 0 | 0.18999 | 85.4511 | 2.846 | 46.2045 | High | High | Medium | 164 | 201 | 16.2348
MIWUK 17021808 | MIWUK 1702 | YOSEMITE | 1.8341 | 72.798 | 17.3% | 1 | 2 | 100% | 100% | 0 | 0.10942 | 102.1389 | 4.1225 | 46.0745 | High | High | High | 165 | 288 | 11.1764
PIKE CITY 11011730 | PIKE CITY 1101 | SIERRA | 8.599 | 94.8581 | 99.91% | 4 | 2 | 100% | 100% | 0 | 0.33402 | 85.4511 | 1.6102 | 45.9608 | High | High | Low | 166 | 71 | 28.5428
PINE GROVE 110283098 | PINE GROVE 1102 | STOCKTON | 8.0988 | 80.2841 | 100% | 2 | 7 | 100% | 98.1% | 0 | 0.21828 | 65.3912 | 3.1987 | 45.6583 | High | High | High | 167 | 228 | 14.2738
VOLTA 11021504 | VOLTA 1102 | NORTH VALLEY | 8.3043 | 82.9659 | 100% | 2 | 3 | 100% | 100% | 0 | 0.23562 | 85.4511 | 2.2543 | 45.389 | High | High | Medium | 168 | 149 | 20.1342
LOS GATOS 110760118 | LOS GATOS 1107 | DE ANZA | 20.0923 | 57.6089 | 83.76% | 25 | 2 | 100% | 100% | 1 | 0.5667 | 47.6367 | 1.6789 | 45.3221 | High | High | Low | 169 | 83 | 26.9958
CAMP EVERS 210510225 | CAMP EVERS 2105 | CENTRAL COAST | 0.18205 | 47.7189 | 100% | 3 | 0 | 100% | 100% | 0 | 0.1873 | 65.3912 | 3.6862 | 45.1466 | High | High | High | 170 | 269 | 12.2475
CAMP EVERS 21061625 | CAMP EVERS 2106 | CENTRAL COAST | 0.904 | 67.0004 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18108 | 65.3912 | 3.8121 | 45.1386 | High | High | High | 171 | 277 | 11.841
SPRING GAP 17029690 | SPRING GAP 1702 | YOSEMITE | 17.3345 | 90.5752 | 98.76% | 12 | 12 | 100% | 100% | 0 | 0.65826 | 102.1389 | 0.67026 | 45.0638 | High | High | Low | 172 | 3 | 67.2336
SAN RAFAEL 11081247 | SAN RAFAEL 1108 | NORTH BAY | 0.2757 | 81.1642 | 57.56% | 3 | 0 | 100% | 100% | 0 | 0.16951 | 65.3912 | 4.0604 | 45.007 | High | High | High | 173 | 292 | 11.0844
EL DORADO PH 2102CB | EL DORADO PH 2102 | SIERRA | 5.6703 | 93.9988 | 79.03% | 2 | 2 | 100% | 100% | 0 | 0.19325 | 102.1389 | 2.2785 | 44.974 | High | High | Medium | 174 | 153 | 19.7388
ORO FINO 1102CB | ORO FINO 1102 | NORTH VALLEY | 2.0939 | 90.4736 | 31.39% | 1 | 0 | 100% | 100% | 0 | 0.1458 | 102.1389 | 3.0047 | 44.7473 | High | High | Medium | 175 | 221 | 14.8924
WEST POINT 1101L3355 | WEST POINT 1101 | STOCKTON | 2.2225 | 89.0928 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20458 | 102.1389 | 2.1399 | 44.7134 | High | High | Low | 176 | 141 | 20.8954
MONTE RIO 11131313 | MONTE RIO 1113 | SONOMA | 1.2316 | 65.332 | 67.8% | 0 | 1 | 100% | 100% | 0 | 0.14614 | 85.4511 | 3.5696 | 44.576 | High | High | High | 177 | 262 | 12.4876
FULTON 1107214 | FULTON 1107 | SONOMA | 12.2376 | 47.3525 | 63.1% | 7 | 19 | 100% | 100% | 0 | 0.43673 | 47.6367 | 2.1422 | 44.5667 | High | High | Low | 178 | 142 | 20.8046
MONTE RIO 11131989 | MONTE RIO 1113 | SONOMA | 0.72387 | 90 | 37.43% | 0 | 0 | 100% | 100% | 0 | 0.13376 | 102.1389 | 3.26 | 44.5399 | High | High | High | 179 | 234 | 13.6625
BRUNSWICK 11062796 | BRUNSWICK 1106 | SIERRA | 19.8739 | 59.7898 | 71.67% | 4 | 4 | 100% | 99.1% | 0 | 0.19738 | 85.4511 | 2.6385 | 44.5007 | High | High | Medium | 180 | 190 | 16.8661
WILLITS 110391810 | WILLITS 1103 | HUMBOLDT | 29.3984 | 69.6626 | 100% | 19 | 14 | 100% | 85.03% | 1 | 0.25809 | 85.4511 | 2.0026 | 44.1654 | High | High | Low | 181 | 121 | 22.0543
WOODACRE 1102851 | WOODACRE 1102 | NORTH BAY | 1.2766 | 60.3664 | 19.35% | 1 | 3 | 100% | 100% | 0 | 0.10492 | 85.4511 | 4.9245 | 44.1492 | High | High | High | 182 | 340 | 8.9652
ALLEGHANY 1102CB | ALLEGHANY 1102 | SIERRA | 18.0939 | 92.7974 | 39.16% | 4 | 24 | 100% | 100% | 1 | 0.48104 | 65.3912 | 1.4 | 44.0392 | High | High | Low | 183 | 53 | 31.4559
BONNIE NOOK 1101CB | BONNIE NOOK 1101 | SIERRA | 14.7401 | 89.8232 | 47.01% | 8 | 12 | 100% | 100% | 0 | 0.28941 | 102.1389 | 1.4893 | 44.0242 | High | High | Low | 184 | 63 | 29.5604
PAUL SWEET 2104 | PAUL SWEET 2104 | CENTRAL COAST | 0.043661 | 75 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18934 | 65.3912 | 3.5423 | 43.8565 | High | High | High | 185 | 266 | 12.3809
SILVERADO 2103CB | SILVERADO 2103 | NORTH BAY | 8.6664 | 84.0044 | 89.49% | 1 | 4 | 46.48% | 100% | 0 | 0.27216 | 47.6367 | 3.3783 | 43.8001 | High | High | High | 186 | 252 | 12.965
MONTE RIO 11111703 | MONTE RIO 1111 | SONOMA | 1.2714 | 84.0743 | 95.02% | 2 | 1 | 100% | 100% | 0 | 0.20007 | 85.4511 | 2.5488 | 43.5738 | High | High | Medium | 187 | 185 | 17.096
BRUNSWICK 110584480 | BRUNSWICK 1105 | SIERRA | 4.5786 | 96.5256 | 65.31% | 1 | 0 | 100% | 100% | 0 | 0.17078 | 102.1389 | 2.4965 | 43.5454 | High | High | Medium | 188 | 181 | 17.4429
MIRABEL 11027347 | MIRABEL 1102 | SONOMA | 0.81707 | 70.8306 | 59.55% | 4 | 1 | 100% | 100% | 0 | 0.14897 | 102.1389 | 2.8575 | 43.4787 | High | High | Medium | 189 | 213 | 15.2154
FORESTHILL 110175340 | FORESTHILL 1101 | SIERRA | 4.974 | 93.375 | 69.57% | 0 | 2 | 100% | 100% | 0 | 0.19715 | 102.1389 | 2.1578 | 43.4515 | High | High | Low | 190 | 148 | 20.1366
PAUL SWEET 21045394 | PAUL SWEET 2104 | CENTRAL COAST | 14.2856 | 38.4642 | 72.86% | 5 | 2 | 93.82% | 100% | 0 | 0.25339 | 47.6367 | 3.5996 | 43.4504 | High | High | High | 191 | 274 | 12.0708
WEST POINT 1101 | WEST POINT 1101 | STOCKTON | 0.004924 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 85.4511 | 2.4491 | 43.0255 | High | High | Medium | 192 | 178 | 17.5679
PARADISE 11011212 | PARADISE 1101 | NORTH VALLEY | 8.5723 | 27.6396 | 21.52% | 13 | 13 | 100% | 100% | 0 | 0.17074 | 65.3912 | 3.8308 | 42.7709 | High | High | High | 193 | 289 | 11.1651
WEST POINT 110234416 | WEST POINT 1102 | STOCKTON | 10.524 | 86.8553 | 100% | 7 | 3 | 100% | 100% | 1 | 0.25274 | 65.3912 | 2.5592 | 42.2967 | High | High | Medium | 194 | 194 | 16.5271
WEST POINT 1102L3733 | WEST POINT 1102 | STOCKTON | 1.754 | 90.0843 | 100% | 0 | 0 | 100% | 94.99% | 0 | 0.19267 | 85.4511 | 2.5527 | 42.0286 | High | High | Medium | 195 | 195 | 16.464
VOLTA 110280982 | VOLTA 1102 | NORTH VALLEY | 0.52007 | 92.783 | 99.45% | 2 | 0 | 100% | 100% | 1 | 0.23557 | 85.4511 | 2.084 | 41.9505 | High | High | Low | 196 | 150 | 20.1294
LOS GATOS 1107LA60 | LOS GATOS 1107 | DE ANZA | 8.6011 | 90.5119 | 96.22% | 1 | 0 | 100% | 100% | 0 | 0.24993 | 85.4511 | 1.9634 | 41.9315 | High | High | Low | 197 | 134 | 21.3565
COLUMBIA HILL 11012212 | COLUMBIA HILL 1101 | SIERRA | 9.1875 | 95.8225 | 100% | 9 | 3 | 100% | 100% | 0 | 0.35537 | 102.1389 | 1.1517 | 41.805 | High | High | Low | 198 | 37 | 36.2974
COLUMBIA HILL 11018233 | COLUMBIA HILL 1101 | SIERRA | 5.0061 | 92.4069 | 99.94% | 1 | 3 | 100% | 100% | 0 | 0.27044 | 102.1389 | 1.5103 | 41.7175 | High | High | Low | 199 | 77 | 27.6227
CHALLENGE 11015460 | CHALLENGE 1101 | NORTH VALLEY | 11.8115 | 93.9312 | 100% | 4 | 4 | 100% | 100% | 0 | 0.31277 | 102.1389 | 1.2968 | 41.4261 | High | High | Low | 200 | 51 | 31.9457
CLARKSVILLE 210419772 | CLARKSVILLE 2104 | SIERRA | 18.3365 | 58.7112 | 99.97% | 3 | 3 | 99.31% | 100% | 1 | 0.20806 | 65.3912 | 3.04 | 41.3598 | High | High | Medium | 201 | 236 | 13.6054
CURTIS 17048140 | CURTIS 1704 | YOSEMITE | 26.2498 | 65.6672 | 76.6% | 12 | 12 | 100% | 76.04% | 0 | 0.17401 | 85.4511 | 2.7756 | 41.2728 | High | High | Medium | 202 | 222 | 14.8696
OAKLAND X 1106CR020 | OAKLAND X 1106 | EAST BAY | 2.4457 | 82.3898 | 55.47% | 10 | 1 | 100% | 99.48% | 0 | 0.18349 | 65.3912 | 3.4295 | 41.1503 | High | High | High | 203 | 276 | 11.9989
MONTE RIO 111215401 | MONTE RIO 1112 | SONOMA | 0.86292 | 85.2793 | 87.8% | 1 | 3 | 100% | 100% | 0 | 0.19647 | 85.4511 | 2.4508 | 41.1456 | High | High | Medium | 204 | 192 | 16.7884
RINCON 1103198 | RINCON 1103 | SONOMA | 6.4573 | 72.5696 | 80.26% | 6 | 3 | 100% | 100% | 0 | 0.20459 | 65.3912 | 3.0723 | 41.1018 | High | High | Medium | 205 | 244 | 13.3782
MIWUK 17029270 | MIWUK 1702 | YOSEMITE | 5.8553 | 48.3944 | 46.92% | 2 | 9 | 100% | 95.13% | 0 | 0.12583 | 85.4511 | 3.8062 | 40.9252 | High | High | High | 206 | 301 | 10.7524
BURNS 2101 | BURNS 2101 | CENTRAL COAST | 0.0053489 | 65 | 100% | 0 | 0 | 100% | 100% | 0 | 0.17906 | 65.3912 | 3.488 | 40.84 | High | High | High | 207 | 279 | 11.7089
POINT MORETTI 1101 | POINT MORETTI 1101 | CENTRAL COAST | 0.0096753 | 65 | 100% | 0 | 0 | 100% | 100% | 0 | 0.17906 | 65.3912 | 3.4875 | 40.8347 | High | High | High | 208 | 279 | 11.7089
FITCH MOUNTAIN 111324918 | FITCH MOUNTAIN 1113 | SONOMA | 5.4494 | 96.6209 | 46.61% | 13 | 1 | 100% | 100% | 0 | 0.17452 | 102.1389 | 2.2832 | 40.6989 | High | High | Medium | 209 | 174 | 17.8255
ORO FINO 11022556 | ORO FINO 1102 | NORTH VALLEY | 6.6623 | 79.6419 | 97.8% | 0 | 4 | 100% | 100% | 0 | 0.25169 | 65.3912 | 2.4528 | 40.3695 | High | High | Medium | 210 | 196 | 16.4582
BRUNSWICK 11052204 | BRUNSWICK 1105 | SIERRA | 7.2073 | 87.5526 | 78.12% | 3 | 0 | 100% | 100% | 0 | 0.2017 | 85.4511 | 2.3292 | 40.1437 | High | High | Medium | 211 | 183 | 17.2351
RINCON 1103568 | RINCON 1103 | SONOMA | 12.8289 | 71.6958 | 48.67% | 11 | 11 | 100% | 100% | 0 | 0.32682 | 47.6367 | 2.5697 | 40.0064 | High | High | Medium | 212 | 210 | 15.5685
LAS GALLINAS A 110599904 | LAS GALLINAS A 1105 | NORTH BAY | 5.5637 | 84.5434 | 55.29% | 2 | 2 | 100% | 100% | 0 | 0.17422 | 65.3912 | 3.4864 | 39.7192 | High | High | High | 213 | 283 | 11.3927
CALISTOGA 11011085 | CALISTOGA 1101 | NORTH BAY | 2.0832 | 81.9335 | 72.65% | 1 | 1 | 100% | 100% | 0 | 0.23189 | 65.3912 | 2.6122 | 39.6091 | High | High | Medium | 214 | 216 | 15.1634
FORESTHILL 110137238 | FORESTHILL 1101 | SIERRA | 11.5057 | 97.4901 | 100% | 2 | 5 | 100% | 100% | 1 | 0.26202 | 85.4511 | 1.7672 | 39.5663 | High | High | Low | 215 | 115 | 22.3899
ROSSMOOR 110837848 | ROSSMOOR 1108 | DIABLO | 5.9561 | 79.6593 | 23.72% | 0 | 5 | 100% | 88.12% | 0 | 0.14934 | 65.3912 | 4.0336 | 39.3891 | High | High | High | 216 | 322 | 9.7653
PARADISE 11022098 | PARADISE 1102 | NORTH VALLEY | 4.2185 | 79.6766 | 65.19% | 0 | 7 | 42.14% | 100% | 0 | 0.13292 | 85.4511 | 3.448 | 39.1629 | High | High | High | 217 | 284 | 11.3582
FITCH MOUNTAIN 11136751 | FITCH MOUNTAIN 1113 | SONOMA | 22.3305 | 96.8838 | 61.93% | 21 | 1 | 100% | 75.68% | 1 | 0.19015 | 85.4511 | 2.409 | 39.1424 | High | High | Medium | 218 | 200 | 16.2482
PARADISE 1106CB | PARADISE 1106 | NORTH VALLEY | 4.354 | 81.9365 | 3.23% | 2 | 3 | 96.39% | 100% | 0 | 0.10412 | 102.1389 | 3.6651 | 38.9782 | High | High | High | 219 | 302 | 10.6351
DUNBAR 1101343 | DUNBAR 1101 | SONOMA | 4.4643 | 78.5129 | 81.48% | 1 | 3 | 100% | 97.94% | 0 | 0.21869 | 65.3912 | 2.7227 | 38.9349 | High | High | Medium | 220 | 227 | 14.3001
SHINGLE SPRINGS 210961892 | SHINGLE SPRINGS 2109 | SIERRA | 30.1835 | 48.4981 | 100% | 2 | 8 | 100% | 100% | 0 | 0.31574 | 47.6367 | 2.5856 | 38.8898 | High | High | Medium | 221 | 219 | 15.0409
BRUNSWICK 11062104 | BRUNSWICK 1106 | SIERRA | 9.719 | 86.4087 | 57.37% | 4 | 1 | 100% | 100% | 0 | 0.17938 | 85.4511 | 2.5365 | 38.8801 | High | High | Medium | 222 | 212 | 15.3282
PARADISE 110135976 | PARADISE 1101 | NORTH VALLEY | 3.5298 | 50.3669 | 45.43% | 3 | 2 | 100% | 100% | 0 | 0.1201 | 85.4511 | 3.7758 | 38.7488 | High | High | High | 223 | 308 | 10.2625
ALLEGHANY 1101CB | ALLEGHANY 1101 | SIERRA | 4.3289 | 94.1851 | 45.96% | 2 | 2 | 100% | 100% | 0 | 0.23753 | 85.4511 | 1.9061 | 38.6887 | High | High | Low | 224 | 145 | 20.2969
FULTON 1107604 | FULTON 1107 | SONOMA | 17.5324 | 71.8219 | 64.8% | 2 | 17 | 100% | 100% | 0 | 0.3284 | 47.6367 | 2.4442 | 38.2377 | High | High | Medium | 225 | 208 | 15.6441
APPLE HILL 21027502 | APPLE HILL 2102 | SIERRA | 23.0839 | 77.5827 | 99.99% | 4 | 7 | 100% | 82.95% | 0 | 0.24712 | 85.4511 | 1.8048 | 38.1112 | High | High | Low | 226 | 138 | 21.1165
SALT SPRINGS 210237300 | SALT SPRINGS 2102 | STOCKTON | 6.9933 | 87.6909 | 82.66% | 1 | 2 | 100% | 100% | 0 | 0.21052 | 85.4511 | 2.1022 | 37.8154 | High | High | Low | 227 | 170 | 17.9888
CHALLENGE 11025462 | CHALLENGE 1102 | NORTH VALLEY | 23.3648 | 66.9386 | 100% | 8 | 5 | 100% | 97.29% | 1 | 0.30821 | 65.3912 | 1.8735 | 37.7585 | High | High | Low | 228 | 147 | 20.154
VOLTA 11029742 | VOLTA 1102 | NORTH VALLEY | 9.1189 | 78.986 | 100% | 1 | 2 | 100% | 94.08% | 0 | 0.25585 | 85.4511 | 1.7244 | 37.6993 | High | High | Low | 229 | 127 | 21.8624
KANAKA 11011034 | KANAKA 1101 | NORTH VALLEY | 13.1567 | 96.9359 | 65.02% | 4 | 2 | 100% | 100% | 0 | 0.22603 | 85.4511 | 1.9382 | 37.4363 | High | High | Low | 230 | 158 | 19.3146
PARADISE 11042472 | PARADISE 1104 | NORTH VALLEY | 7.3384 | 31.16 | 42.96% | 7 | 6 | 100% | 100% | 0 | 0.14941 | 65.3912 | 3.8266 | 37.3865 | High | High | High | 231 | 321 | 9.7702
WEST POINT 1102CB | WEST POINT 1102 | STOCKTON | 17.7809 | 76.7324 | 62.09% | 5 | 4 | 100% | 79.61% | 1 | 0.19732 | 65.3912 | 2.8754 | 37.101 | High | High | Medium | 232 | 255 | 12.9027
RINCON 1101578 | RINCON 1101 | SONOMA | 17.3381 | 67.0315 | 100% | 2 | 9 | 93.38% | 92.03% | 0 | 0.20486 | 65.3912 | 2.768 | 37.0801 | High | High | Medium | 233 | 243 | 13.3958
MORAGA 1105CB | MORAGA 1105 | DIABLO | 7.1365 | 67.7298 | 20.75% | 5 | 12 | 65.86% | 77.06% | 1 | 0.092052 | 102.1389 | 3.9271 | 36.9227 | High | High | High | 234 | 329 | 9.4021
MIDDLETOWN 11014646 | MIDDLETOWN 1101 | HUMBOLDT | 18.5612 | 85.1867 | 99.86% | 4 | 10 | 100% | 100% | 0 | 0.35694 | 47.6367 | 2.1685 | 36.8721 | High | High | Low | 235 | 188 | 17.0035
DUNBAR 1103534 | DUNBAR 1103 | SONOMA | 15.5924 | 79.0775 | 96.69% | 3 | 12 | 89.43% | 96.98% | 1 | 0.28566 | 47.6367 | 2.69 | 36.606 | High | High | Medium | 236 | 235 | 13.6079
FORT ROSS 112170288 | FORT ROSS 1121 | SONOMA | 11.744 | 93.8091 | 82.61% | 5 | 5 | 100% | 100% | 0 | 0.2145 | 85.4511 | 1.9739 | 36.1799 | High | High | Low | 237 | 165 | 18.3292
EL DORADO PH 210119612 | EL DORADO PH 2101 | SIERRA | 9.1713 | 87.7197 | 45.56% | 7 | 1 | 100% | 100% | 0 | 0.19221 | 102.1389 | 1.8339 | 36.0017 | High | High | Low | 238 | 155 | 19.6316
WOODSIDE 11018601 | WOODSIDE 1101 | PENINSULA | 0.59795 | 81.8692 | 48.65% | 2 | 0 | 100% | 100% | 0 | 0.14129 | 65.3912 | 3.8817 | 35.8642 | High | High | High | 239 | 335 | 9.2392
HIGHLANDS 1103520 | HIGHLANDS 1103 | HUMBOLDT | 46.4816 | 67.4675 | 99% | 5 | 17 | 100% | 0% | 0 | 0.27204 | 47.6367 | 2.7667 | 35.8548 | High | High | Medium | 240 | 253 | 12.9592
WILLITS 1104934 | WILLITS 1104 | HUMBOLDT | 30.5846 | 72.5028 | 89.66% | 17 | 12 | 100% | 39.29% | 1 | 0.29588 | 65.3912 | 1.8491 | 35.7756 | High | High | Low | 241 | 157 | 19.3479
MOLINO 1101322 | MOLINO 1101 | SONOMA | 15.8907 | 58.1086 | 71.61% | 14 | 10 | 100% | 44.47% | 0 | 0.22351 | 65.3912 | 2.4422 | 35.6935 | High | High | Medium | 242 | 225 | 14.6154
AUBERRY 1101R324 | AUBERRY 1101 | FRESNO | 10.7908 | 83.7222 | 99.89% | 3 | 1 | 100% | 100% | 0 | 0.25584 | 85.4511 | 1.6256 | 35.538 | High | High | Low | 243 | 128 | 21.8618
DIAMOND SPRINGS 11071402 | DIAMOND SPRINGS 1107 | SIERRA | 44.1487 | 51.2712 | 86.92% | 1 | 21 | 100% | 76.75% | 0 | 0.24689 | 65.3912 | 2.1929 | 35.4032 | High | High | Low | 244 | 202 | 16.1444
WILLITS 1103 | WILLITS 1103 | HUMBOLDT | 0.065999 | 98 | 100% | 0 | 0 | 100% | 100% | 0 | 0.21467 | 102.1389 | 1.6051 | 35.1936 | High | High | Low | 245 | 124 | 21.9265
MORGAN HILL 21114461 | MORGAN HILL 2111 | SAN JOSE | 2.2769 | 88.7487 | 84.71% | 4 | 2 | 100% | 100% | 0 | 0.19916 | 65.3912 | 2.6877 | 35.0025 | High | High | Medium | 246 | 249 | 13.0233
MONTE RIO 111153477 | MONTE RIO 1111 | SONOMA | 2.1403 | 90.336 | 44.25% | 6 | 1 | 100% | 100% | 0 | 0.21276 | 85.4511 | 1.9244 | 34.9877 | High | High | Low | 247 | 168 | 18.1807
SHINGLE SPRINGS 210519522 | SHINGLE SPRINGS 2105 | SIERRA | 9.9042 | 70.9474 | 99.53% | 2 | 6 | 96.11% | 80.98% | 0 | 0.17524 | 65.3912 | 2.9822 | 34.1738 | High | High | Medium | 248 | 281 | 11.4593
WEST POINT 110236676 | WEST POINT 1102 | STOCKTON | 16.994 | 84.9293 | 78.04% | 3 | 4 | 100% | 93.46% | 0 | 0.24051 | 65.3912 | 2.1683 | 34.1012 | High | High | Low | 249 | 205 | 15.7272
SILVERADO 210258626 | SILVERADO 2102 | NORTH BAY | 15.2462 | 83.9933 | 97.52% | 2 | 7 | 100% | 88.88% | 0 | 0.23976 | 47.6367 | 2.967 | 33.8868 | High | High | Medium | 250 | 282 | 11.4212
SALT SPRINGS 2102L491 | SALT SPRINGS 2102 | STOCKTON | 2.2143 | 88.9765 | 100% | 2 | 2 | 100% | 100% | 0 | 0.21581 | 102.1389 | 1.5318 | 33.7654 | High | High | Low | 251 | 122 | 22.0423
MIRABEL 1101116 | MIRABEL 1101 | SONOMA | 9.7562 | 60.7427 | 68.47% | 10 | 5 | 91.79% | 57.41% | 1 | 0.21711 | 47.6367 | 3.2592 | 33.7085 | High | High | High | 252 | 306 | 10.3426
WILLITS 1103968 | WILLITS 1103 | HUMBOLDT | 24.6966 | 68.3381 | 85.93% | 14 | 10 | 88.86% | 68.54% | 1 | 0.21234 | 85.4511 | 1.8563 | 33.6814 | High | High | Low | 253 | 169 | 18.1447
AUBERRY 1101D4982 | AUBERRY 1101 | FRESNO | 2.6789 | 91.9989 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20783 | 85.4511 | 1.8789 | 33.3678 | High | High | Low | 254 | 175 | 17.7595
APPLE HILL 210297982 | APPLE HILL 2102 | SIERRA | 10.1443 | 88.7232 | 100% | 1 | 1 | 100% | 100% | 0 | 0.23278 | 102.1389 | 1.3898 | 33.0445 | High | High | Low | 255 | 102 | 23.7764
OAKLAND K 110217430 | OAKLAND K 1102 | EAST BAY | 2.0764 | 84.0676 | 31.48% | 0 | 1 | 100% | 100% | 0 | 0.12601 | 85.4511 | 3.0426 | 32.7603 | High | High | Medium | 256 | 300 | 10.7674
BEN LOMOND 04015144 | BEN LOMOND 0401 | CENTRAL COAST | 3.9861 | 45.8832 | 59.52% | 1 | 1 | 100% | 100% | 0 | 0.13946 | 65.3912 | 3.5854 | 32.6969 | High | High | High | 257 | 337 | 9.1195
BRUNSWICK 11053611 | BRUNSWICK 1105 | SIERRA | 1.6138 | 98 | 100% | 0 | 3 | 100% | 100% | 0 | 0.22548 | 102.1389 | 1.4025 | 32.3002 | High | High | Low | 258 | 110 | 23.03
CHALLENGE 11021902 | CHALLENGE 1102 | NORTH VALLEY | 5.0391 | 84.0879 | 100% | 3 | 2 | 100% | 100% | 0 | 0.21241 | 65.3912 | 2.2968 | 31.9012 | High | High | Medium | 259 | 231 | 13.8896
BRUNSWICK 110663124 | BRUNSWICK 1106 | SIERRA | 5.9024 | 71.9691 | 59.9% | 2 | 1 | 100% | 94.93% | 0 | 0.17164 | 65.3912 | 2.8195 | 31.6447 | High | High | Medium | 260 | 286 | 11.2236
PARADISE 11015185 | PARADISE 1101 | NORTH VALLEY | 0.8075 | 38.303 | 73.08% | 0 | 1 | 100% | 100% | 0 | 0.12937 | 65.3912 | 3.7374 | 31.6174 | High | High | High | 261 | 349 | 8.4598
PLACERVILLE 21062224 | PLACERVILLE 2106 | SIERRA | 10.4972 | 65.7358 | 76.35% | 3 | 1 | 100% | 100% | 0 | 0.2002 | 47.6367 | 3.3086 | 31.5533 | High | High | High | 262 | 325 | 9.5368
CABRILLO 1103Y12 | CABRILLO 1103 | LOS PADRES | 26.1562 | 62.7349 | 69.42% | 1 | 11 | 84.42% | 0% | 0 | 0.20939 | 47.6367 | 3.1607 | 31.5264 | High | High | High | 263 | 315 | 9.9744
ROB ROY 21055166 | ROB ROY 2105 | CENTRAL COAST | 5.4938 | 45.154 | 99.95% | 6 | 2 | 100% | 100% | 0 | 0.19719 | 47.6367 | 3.3223 | 31.2078 | High | High | High | 264 | 330 | 9.3933
OAKLAND K 1102CB | OAKLAND K 1102 | EAST BAY | 3.0081 | 48.3984 | 19.08% | 4 | 5 | 100% | 100% | 0 | 0.11788 | 65.3912 | 4.048 | 31.203 | High | High | High | 265 | 368 | 7.7083
OAKHURST 11015490 | OAKHURST 1101 | YOSEMITE | 24.9631 | 65.8497 | 73.62% | 1 | 51 | 100% | 0% | 0 | 0.18555 | 65.3912 | 2.5688 | 31.1673 | High | High | Medium | 266 | 271 | 12.1331
CLAYTON 22122951 | CLAYTON 2212 | DIABLO | 10.1032 | 61.4187 | 78.88% | 4 | 1 | 100% | 100% | 0 | 0.27294 | 35.3263 | 3.2196 | 31.0433 | High | High | High | 267 | 323 | 9.6421
MONTE RIO 11131137 | MONTE RIO 1113 | SONOMA | 2.8427 | 88.9858 | 48.94% | 0 | 5 | 100% | 100% | 0 | 0.15775 | 65.3912 | 2.9968 | 30.9141 | High | High | Medium | 268 | 307 | 10.3156
LOS GATOS 110712041 | LOS GATOS 1107 | DE ANZA | 6.3296 | 61.8932 | 100% | 5 | 1 | 100% | 100% | 0 | 0.28444 | 47.6367 | 2.2717 | 30.7809 | High | High | Medium | 269 | 238 | 13.5499
MIRABEL 1102332 | MIRABEL 1102 | SONOMA | 5.7552 | 66.9134 | 43.76% | 9 | 11 | 100% | 100% | 1 | 0.16469 | 65.3912 | 2.8565 | 30.7615 | High | High | Medium | 270 | 299 | 10.7691
PARADISE 11022206 | PARADISE 1102 | NORTH VALLEY | 5.1983 | 53.3962 | 55.37% | 4 | 4 | 89% | 100% | 0 | 0.12523 | 65.3912 | 3.7528 | 30.7318 | High | High | High | 271 | 358 | 8.1891
MIRABEL 11014859 | MIRABEL 1101 | SONOMA | 1.8526 | 77.0765 | 99.9% | 8 | 0 | 100% | 100% | 0 | 0.23121 | 47.6367 | 2.7808 | 30.6275 | High | High | Medium | 272 | 296 | 11.014
MONTE RIO 111137520 | MONTE RIO 1111 | SONOMA | 2.1617 | 88.6545 | 55.37% | 6 | 0 | 100% | 100% | 0 | 0.18002 | 85.4511 | 1.984 | 30.52 | High | High | Low | 273 | 211 | 15.383
CLARKSVILLE 210413352 | CLARKSVILLE 2104 | SIERRA | 32.6724 | 49.7642 | 94.33% | 3 | 19 | 89.71% | 64.9% | 0 | 0.20162 | 47.6367 | 3.1662 | 30.4103 | High | High | High | 274 | 324 | 9.6046
APPLE HILL 2102CB | APPLE HILL 2102 | SIERRA | 41.3043 | 54.0794 | 88.14% | 11 | 9 | 100% | 60.25% | 1 | 0.23023 | 65.3912 | 1.9699 | 29.6561 | High | High | Low | 275 | 218 | 15.0548
MONTE RIO 11111701 | MONTE RIO 1111 | SONOMA | 1.3661 | 76.5396 | 84.13% | 0 | 0 | 100% | 100% | 0 | 0.17154 | 65.3912 | 2.6378 | 29.5889 | High | High | Medium | 276 | 287 | 11.217
SALT SPRINGS 2102L7283 | SALT SPRINGS 2102 | STOCKTON | 0.66272 | 87.1614 | 100% | 0 | 1 | 100% | 100% | 0 | 0.20585 | 102.1389 | 1.3967 | 29.3663 | High | High | Low | 277 | 139 | 21.0249
GRASS VALLEY 11012766 | GRASS VALLEY 1101 | SIERRA | 3.3601 | 83.6304 | 59.47% | 0 | 1 | 100% | 75.75% | 0 | 0.10872 | 102.1389 | 2.6373 | 29.2861 | High | High | Medium | 278 | 291 | 11.1047
CAMP EVERS 210611533 | CAMP EVERS 2106 | CENTRAL COAST | 2.6563 | 88.3756 | 100% | 3 | 0 | 100% | 100% | 0 | 0.2103 | 65.3912 | 2.1282 | 29.2669 | High | High | Low | 279 | 233 | 13.7518
POINT MORETTI 110136516 | POINT MORETTI 1101 | CENTRAL COAST | 4.1652 | 32.5436 | 68.9% | 12 | 2 | 100% | 100% | 0 | 0.17749 | 47.6367 | 3.4455 | 29.1317 | High | High | High | 280 | 350 | 8.4551
APPLE HILL 110412832 | APPLE HILL 1104 | SIERRA | 15.3272 | 73.0049 | 95.88% | 8 | 6 | 99.79% | 19.25% | 1 | 0.22229 | 65.3912 | 1.9946 | 28.9929 | High | High | Low | 281 | 226 | 14.536
PARADISE 110136042 | PARADISE 1101 | NORTH VALLEY | 2.7098 | 42.4595 | 41.3% | 5 | 3 | 86.87% | 100% | 0 | 0.11607 | 65.3912 | 3.8047 | 28.8767 | High | High | High | 282 | 372 | 7.5898
VOLTA 11021648 | VOLTA 1102 | NORTH VALLEY | 4.8649 | 85.7622 | 100% | 2 | 2 | 100% | 79.51% | 0 | 0.16163 | 85.4511 | 2.0849 | 28.7959 | High | High | Low | 283 | 232 | 13.8114
ALTO 11221212 | ALTO 1122 | NORTH BAY | 1.5919 | 41.9573 | 53.59% | 1 | 4 | 67.44% | 92.64% | 0 | 0.09288 | 85.4511 | 3.6174 | 28.7098 | High | High | High | 284 | 363 | 7.9367
BELLEVUE 2103646 | BELLEVUE 2103 | SONOMA | 9.4191 | 67.7942 | 94.53% | 3 | 3 | 77.28% | 93.12% | 0 | 0.17965 | 65.3912 | 2.4439 | 28.7093 | High | High | Medium | 285 | 278 | 11.7473
MOLINO 11026917 | MOLINO 1102 | SONOMA | 7.1386 | 86.8229 | 45.11% | 6 | 1 | 100% | 100% | 0 | 0.18864 | 65.3912 | 2.3255 | 28.6861 | High | High | Medium | 286 | 267 | 12.3355
KONOCTI 11024300 | KONOCTI 1102 | HUMBOLDT | 26.3294 | 77.3617 | 62.75% | 9 | 28 | 97.14% | 84.42% | 1 | 0.28482 | 47.6367 | 2.1132 | 28.6726 | High | High | Low | 287 | 237 | 13.5681
MONTE RIO 1112999 | MONTE RIO 1112 | SONOMA | 0.78347 | 81.1849 | 29.39% | 4 | 2 | 100% | 100% | 0 | 0.13014 | 85.4511 | 2.5578 | 28.4436 | High | High | Medium | 288 | 290 | 11.1202
MIRABEL 11022043 | MIRABEL 1102 | SONOMA | 0.56871 | 88.7155 | 17.22% | 0 | 1 | 100% | 100% | 0 | 0.11685 | 85.4511 | 2.8327 | 28.2828 | High | High | Medium | 289 | 314 | 9.9846
SALT SPRINGS 210297924 | SALT SPRINGS 2102 | STOCKTON | 5.0873 | 68.1168 | 100% | 5 | 4 | 100% | 100% | 0 | 0.22834 | 85.4511 | 1.4445 | 28.1851 | High | High | Low | 290 | 156 | 19.5118
MIWUK 170236888 | MIWUK 1702 | YOSEMITE | 0.61573 | 72.472 | 39.92% | 0 | 2 | 100% | 100% | 0 | 0.12726 | 65.3912 | 3.3823 | 28.1466 | High | High | High | 291 | 353 | 8.3216
BRUNSWICK 1106CB | BRUNSWICK 1106 | SIERRA | 8.5018 | 76.2711 | 34.63% | 3 | 2 | 96.43% | 63.8% | 0 | 0.11976 | 85.4511 | 2.733 | 27.9679 | High | High | Medium | 292 | 309 | 10.2335
VOLTA 11021502 | VOLTA 1102 | NORTH VALLEY | 7.6156 | 84.4703 | 99.46% | 2 | 2 | 100% | 100% | 0 | 0.2099 | 47.6367 | 2.778 | 27.777 | High | High | Medium | 293 | 313 | 9.999
VINEYARD 2108MR172 | VINEYARD 2108 | MISSION | 3.1156 | 86.4654 | 47.06% | 1 | 2 | 35.54% | 100% | 1 | 0.13362 | 65.3912 | 3.178 | 27.7695 | High | High | High | 294 | 342 | 8.7379
SILVERADO 2104563322 | SILVERADO 2104 | NORTH BAY | 3.653 | 77.3083 | 48.88% | 3 | 1 | 100% | 100% | 1 | 0.14188 | 65.3912 | 2.9772 | 27.6225 | High | High | Medium | 295 | 334 | 9.2779
CAMP EVERS 210660120 | CAMP EVERS 2106 | CENTRAL COAST | 4.3678 | 67.866 | 79.91% | 12 | 0 | 100% | 100% | 0 | 0.20157 | 65.3912 | 2.0826 | 27.4498 | High | High | Low | 296 | 246 | 13.1807
SARATOGA 1107167792 | SARATOGA 1107 | DE ANZA | 4.6876 | 89.4882 | 89.82% | 13 | 1 | 100% | 18.23% | 0 | 0.1289 | 65.3912 | 3.2524 | 27.4146 | High | High | High | 297 | 352 | 8.429
MONTE RIO 1113532 | MONTE RIO 1113 | SONOMA | 0.51993 | 90.7851 | 10.39% | 0 | 0 | 100% | 100% | 0 | 0.11048 | 85.4511 | 2.896 | 27.3401 | High | High | Medium | 298 | 327 | 9.4408
LOS GATOS 11072917 | LOS GATOS 1107 | DE ANZA | 7.7152 | 64.4105 | 89.16% | 10 | 1 | 100% | 100% | 0 | 0.23223 | 65.3912 | 1.7943 | 27.2488 | High | High | Low | 299 | 214 | 15.1861
PLACERVILLE 210692012 | PLACERVILLE 2106 | SIERRA | 18.5713 | 72.0312 | 64.51% | 6 | 1 | 100% | 92.15% | 0 | 0.22084 | 47.6367 | 2.5843 | 27.1879 | High | High | Medium | 300 | 303 | 10.5203
MONTE RIO 1111240 | MONTE RIO 1111 | SONOMA | 3.0687 | 71.6003 | 66.68% | 5 | 7 | 100% | 100% | 0 | 0.21886 | 47.6367 | 2.6045 | 27.1546 | High | High | Medium | 301 | 304 | 10.4259
CAMP EVERS 21059031 | CAMP EVERS 2105 | CENTRAL COAST | 1.0934 | 18.456 | 18.86% | 2 | 2 | 100% | 100% | 0 | 0.10201 | 65.3912 | 4.0458 | 26.9866 | High | High | High | 302 | 388 | 6.6703
MONTE RIO 1112212 | MONTE RIO 1112 | SONOMA | 2.2491 | 44.7156 | 75.38% | 4 | 1 | 100% | 100% | 0 | 0.14298 | 65.3912 | 2.8824 | 26.9492 | High | High | Medium | 303 | 332 | 9.3496
KANAKA 110175744 | KANAKA 1101 | NORTH VALLEY | 10.5898 | 74.5656 | 100% | 3 | 3 | 100% | 74.87% | 0 | 0.16375 | 85.4511 | 1.9254 | 26.9403 | High | High | Low | 304 | 230 | 13.9922
BIG BASIN 1101CB | BIG BASIN 1101 | CENTRAL COAST | 4.7811 | 77.9416 | 33.87% | 2 | 0 | 100% | 100% | 0 | 0.13944 | 65.3912 | 2.9497 | 26.897 | High | High | Medium | 305 | 338 | 9.1184
WOODSIDE 11018912 | WOODSIDE 1101 | PENINSULA | 3.8497 | 42.1497 | 27.37% | 5 | 2 | 96.59% | 100% | 0 | 0.15841 | 47.6367 | 3.5396 | 26.7098 | High | High | High | 306 | 373 | 7.5459
OAKLAND X 1104CR214 | OAKLAND X 1104 | EAST BAY | 2.8836 | 10 | 25.8% | 4 | 2 | 100% | 100% | 0 | 0.13215 | 47.6367 | 4.2427 | 26.7088 | High | High | High | 307 | 396 | 6.2952
BURNS 2101CB | BURNS 2101 | CENTRAL COAST | 1.6587 | 56.6807 | 25.38% | 1 | 0 | 100% | 100% | 0 | 0.11419 | 65.3912 | 3.5716 | 26.6705 | High | High | High | 308 | 375 | 7.4673
DUNBAR 11021249 | DUNBAR 1102 | SONOMA | 13.5745 | 82.3664 | 58.44% | 5 | 8 | 100% | 36.11% | 1 | 0.11715 | 85.4511 | 2.6217 | 26.2453 | High | High | Medium | 309 | 312 | 10.0108
WEST POINT 110293116 | WEST POINT 1102 | STOCKTON | 24.1031 | 66.8044 | 100% | 9 | 9 | 100% | 51.27% | 1 | 0.16857 | 65.3912 | 2.3737 | 26.1657 | High | High | Medium | 310 | 295 | 11.0231
SHINGLE SPRINGS 110419502 | SHINGLE SPRINGS 1104 | SIERRA | 42.2119 | 45.6817 | 99.02% | 5 | 5 | 73.54% | 87.16% | 0 | 0.15459 | 65.3912 | 2.57 | 25.9791 | High | High | Medium | 311 | 310 | 10.1086
MONTE RIO 111123916 | MONTE RIO 1111 | SONOMA | 5.2149 | 69.8916 | 48.27% | 12 | 5 | 100% | 100% | 0 | 0.20017 | 65.3912 | 1.981 | 25.9302 | High | High | Low | 312 | 248 | 13.0895
WOODACRE 11011456 | WOODACRE 1101 | NORTH BAY | 3.8267 | 75.1652 | 37.76% | 1 | 5 | 100% | 88.56% | 0 | 0.14581 | 85.4511 | 2.0696 | 25.7865 | High | High | Low | 313 | 265 | 12.4595
BEN LOMOND 1101BL 1101 | BEN LOMOND 1101 | CENTRAL COAST | 8.6011 | 33.9399 | 41.85% | 31 | 2 | 100% | 100% | 0 | 0.22644 | 26.5534 | 4.227 | 25.4156 | High | High | High | 314 | 400 | 6.0127
CASTRO VALLEY 1108MR748 | CASTRO VALLEY 1108 | MISSION | 6.2273 | 76.3747 | 18.01% | 3 | 1 | 100% | 95.99% | 0 | 0.13481 | 47.6367 | 3.945 | 25.335 | High | High | High | 315 | 394 | 6.422
VOLTA 110254932 | VOLTA 1102 | NORTH VALLEY | 4.3783 | 73.0618 | 100% | 0 | 1 | 100% | 95.18% | 0 | 0.19916 | 65.3912 | 1.937 | 25.2264 | High | High | Low | 316 | 250 | 13.0232
WEST POINT 11021391 | WEST POINT 1102 | STOCKTON | 3.974 | 89.103 | 100% | 2 | 3 | 100% | 100% | 0 | 0.26869 | 65.3912 | 1.4346 | 25.2057 | High | High | Low | 317 | 177 | 17.57
STANISLAUS 1702L3151 | STANISLAUS 1702 | YOSEMITE | 0.9933 | 86.9694 | 85.25% | 0 | 0 | 100% | 100% | 0 | 0.1833 | 47.6367 | 2.8637 | 25.0046 | High | High | Medium | 318 | 343 | 8.7317
MORAGA 1101108540 | MORAGA 1101 | DIABLO | 4.7825 | 66.0707 | 6.533% | 0 | 5 | 99.19% | 93.66% | 1 | 0.10343 | 65.3912 | 3.6968 | 25.0018 | High | High | High | 319 | 385 | 6.7632
APPLE HILL 110412842 | APPLE HILL 1104 | SIERRA | 15.4186 | 86.4877 | 86.23% | 1 | 6 | 91.92% | 56.31% | 0 | 0.11821 | 102.1389 | 2.0647 | 24.9288 | High | High | Low | 320 | 273 | 12.0736
MOLINO 1102178 | MOLINO 1102 | SONOMA | 13.3443 | 48.7979 | 52.24% | 13 | 10 | 88.89% | 58.63% | 0 | 0.18298 | 47.6367 | 2.8177 | 24.5608 | High | High | Medium | 321 | 345 | 8.7167
BIG BASIN 11015000 | BIG BASIN 1101 | CENTRAL COAST | 1.9973 | 72.3321 | 15.8% | 2 | 1 | 100% | 100% | 0 | 0.10717 | 65.3912 | 3.5025 | 24.5467 | High | High | High | 322 | 380 | 7.0083
BIG BEND 1101180398 | BIG BEND 1101 | NORTH VALLEY | 5.6176 | 75.1769 | 68.58% | 0 | 2 | 100% | 100% | 0 | 0.15837 | 65.3912 | 2.3657 | 24.4991 | High | High | Medium | 323 | 305 | 10.3561
MONTE RIO 1111 | MONTE RIO 1111 | SONOMA | 0.032125 | 95 | 0% | 0 | 1 | 100% | 100% | 0 | 0.107 | 85.4511 | 2.6749 | 24.4578 | High | High | Medium | 324 | 336 | 9.1434
BRUNSWICK 11052102 | BRUNSWICK 1105 | SIERRA | 3.6478 | 67.9602 | 63.58% | 1 | 3 | 100% | 48.36% | 1 | 0.091021 | 102.1389 | 2.6251 | 24.4045 | High | High | Medium | 325 | 333 | 9.2968
MONTE RIO 1111256 | MONTE RIO 1111 | SONOMA | 7.2865 | 62.779 | 22.47% | 12 | 6 | 100% | 100% | 1 | 0.22703 | 35.3263 | 3.0231 | 24.2464 | High | High | Medium | 326 | 361 | 8.0203
WOODSIDE 11018972 | WOODSIDE 1101 | PENINSULA | 6.2078 | 92.0365 | 25.89% | 9 | 0 | 100% | 100% | 1 | 0.17321 | 65.3912 | 2.1359 | 24.1909 | High | High | Low | 327 | 285 | 11.3261
PARADISE 1101CB | PARADISE 1101 | NORTH VALLEY | 2.6336 | 51.0801 | 25.12% | 2 | 4 | 70.38% | 100% | 0 | 0.092062 | 65.3912 | 4.0044 | 24.1067 | High | High | High | 328 | 399 | 6.02
CASTRO VALLEY 110810315 | CASTRO VALLEY 1108 | MISSION | 5.494 | 83.0408 | 14.23% | 2 | 0 | 100% | 100% | 0 | 0.14022 | 47.6367 | 3.6086 | 24.1042 | High | High | High | 329 | 387 | 6.6796
SHINGLE SPRINGS 21092679 | SHINGLE SPRINGS 2109 | SIERRA | 7.0526 | 59.0742 | 100% | 0 | 2 | 100% | 100% | 1 | 0.17927 | 47.6367 | 2.7934 | 23.8549 | High | High | Medium | 330 | 348 | 8.5398
BEAR VALLEY 210513430 | BEAR VALLEY 2105 | YOSEMITE | 13.3191 | 78.8388 | 99.94% | 4 | 1 | 100% | 48.72% | 0 | 0.12752 | 85.4511 | 2.1818 | 23.7734 | High | High | Low | 331 | 298 | 10.8965
BUCKS CREEK 11032414 | BUCKS CREEK 1103 | NORTH VALLEY | 6.1362 | 87.0222 | 100% | 6 | 5 | 76.6% | 80.44% | 0 | 0.28097 | 85.4511 | 0.98592 | 23.6715 | High | High | Low | 332 | 100 | 24.0095
ORO FINO 1102127563 | ORO FINO 1102 | NORTH VALLEY | 6.9027 | 86.7717 | 100% | 0 | 2 | 100% | 100% | 1 | 0.23179 | 47.6367 | 2.1334 | 23.5558 | High | High | Low | 333 | 294 | 11.0415
ATASCADERO 1103A06 | ATASCADERO 1103 | LOS PADRES | 34.0507 | 59.0569 | 96.54% | 3 | 5 | 91.06% | 64.46% | 1 | 0.13601 | 65.3912 | 2.647 | 23.5413 | High | High | Medium | 334 | 341 | 8.8937
PIKE CITY 11011720 | PIKE CITY 1101 | SIERRA | 6.0835 | 93.4602 | 100% | 4 | 2 | 100% | 100% | 0 | 0.24982 | 65.3912 | 1.4389 | 23.5061 | High | High | Low | 335 | 199 | 16.3363
CLARKSVILLE 210419632 | CLARKSVILLE 2104 | SIERRA | 5.4715 | 65.8905 | 97.91% | 0 | 0 | 60.07% | 97.91% | 1 | 0.12258 | 65.3912 | 2.9244 | 23.441 | High | High | Medium | 336 | 362 | 8.0156
SPRING GAP 170210720 | SPRING GAP 1702 | YOSEMITE | 4.7512 | 90.1119 | 100% | 2 | 3 | 100% | 100% | 0 | 0.27005 | 85.4511 | 1.0152 | 23.4266 | High | High | Low | 337 | 109 | 23.076
CAMP EVERS 210510786 | CAMP EVERS 2105 | CENTRAL COAST | 4.5287 | 29.7458 | 98.51% | 7 | 0 | 100% | 100% | 1 | 0.21707 | 26.5534 | 4.044 | 23.3096 | High | High | High | 338 | 408 | 5.764
MONTE RIO 1112CB | MONTE RIO 1112 | SONOMA | 3.7135 | 57.2951 | 17.86% | 14 | 2 | 100% | 100% | 0 | 0.14693 | 47.6367 | 3.2898 | 23.026 | High | High | High | 339 | 381 | 6.9992
OAKLAND X 1106CR266 | OAKLAND X 1106 | EAST BAY | 1.1822 | 88.5589 | 1.895% | 0 | 0 | 100% | 100% | 0 | 0.10237 | 65.3912 | 3.4355 | 22.9974 | High | High | High | 340 | 386 | 6.6941
ALLEGHANY 1101804 | ALLEGHANY 1101 | SIERRA | 21.9183 | 93.3631 | 99.35% | 2 | 14 | 100% | 31.47% | 0 | 0.15061 | 85.4511 | 1.7753 | 22.8471 | High | High | Low | 341 | 256 | 12.8696
LOS GATOS 110760024 | LOS GATOS 1107 | DE ANZA | 3.9994 | 92.5853 | 100% | 0 | 0 | 100% | 100% | 0 | 0.28225 | 47.6367 | 1.6969 | 22.8161 | High | High | Low | 342 | 240 | 13.4456
REDBUD 1101323962 | REDBUD 1101 | HUMBOLDT | 18.9728 | 78.4739 | 90.21% | 1 | 14 | 68.24% | 71.99% | 0 | 0.19082 | 65.3912 | 1.8051 | 22.5244 | High | High | Low | 343 | 263 | 12.4782
WHITMORE 11011598 | WHITMORE 1101 | NORTH VALLEY | 33.6511 | 71.823 | 81.12% | 6 | 5 | 100% | 75.5% | 0 | 0.37493 | 85.4511 | 0.69773 | 22.3538 | High | High | Low | 344 | 50 | 32.038
TIGER CREEK 0201CB | TIGER CREEK 0201 | STOCKTON | 3.8998 | 93.0419 | 100% | 1 | 1 | 100% | 66.65% | 0 | 0.15361 | 65.3912 | 2.2115 | 22.2145 | High | High | Low | 345 | 311 | 10.0449
CHALLENGE 110198174 | CHALLENGE 1101 | NORTH VALLEY | 12.1176 | 88.3942 | 100% | 4 | 1 | 100% | 100% | 0 | 0.34958 | 85.4511 | 0.74174 | 22.157 | High | High | Low | 346 | 61 | 29.8716
MONTE RIO 11113891 | MONTE RIO 1111 | SONOMA | 3.5454 | 89.5117 | 50.47% | 2 | 0 | 100% | 100% | 1 | 0.14965 | 65.3912 | 2.2281 | 21.8036 | High | High | Low | 347 | 320 | 9.7859
BEN LOMOND 110196738 | BEN LOMOND 1101 | CENTRAL COAST | 6.8007 | 19.3556 | 74.88% | 14 | 2 | 100% | 100% | 0 | 0.21743 | 26.5534 | 3.7528 | 21.6668 | High | High | High | 348 | 407 | 5.7735
SHADY GLEN 1102CB | SHADY GLEN 1102 | SIERRA | 20.4139 | 69.5808 | 89.02% | 6 | 13 | 95.14% | 27.66% | 0 | 0.14313 | 85.4511 | 1.7682 | 21.6268 | High | High | Low | 349 | 270 | 12.231
PUEBLO 2103 | PUEBLO 2103 | NORTH BAY | 0.012243 | 90 | 0% | 0 | 0 | 100% | 100% | 0 | 0.11472 | 65.3912 | 2.8801 | 21.6062 | High | High | Medium | 350 | 374 | 7.502
BRUNSWICK 11051030 | BRUNSWICK 1105 | SIERRA | 4.9418 | 79.0296 | 79.8% | 3 | 3 | 100% | 45.4% | 0 | 0.084675 | 102.1389 | 2.4972 | 21.5975 | High | High | Medium | 351 | 347 | 8.6486
BRUNSWICK 11032784 | BRUNSWICK 1103 | SIERRA | 14.361 | 51.6275 | 64.59% | 9 | 6 | 93.84% | 32.3% | 0 | 0.11661 | 65.3912 | 2.7674 | 21.1031 | High | High | Medium | 352 | 371 | 7.6256
DRUM 1101CB | DRUM 1101 | SIERRA | 2.1059 | 96.8742 | 100% | 2 | 0 | 100% | 100% | 0 | 0.2937 | 85.4511 | 0.83984 | 21.0773 | High | High | Low | 353 | 94 | 25.0967
BIG BASIN 110110296 | BIG BASIN 1101 | CENTRAL COAST | 14.4399 | 15.6542 | 52.28% | 39 | 5 | 100% | 100% | 0 | 0.45917 | 14.9507 | 3.0498 | 20.9366 | High | High | Medium | 354 | 384 | 6.8649
MONTE RIO 11125040 | MONTE RIO 1112 | SONOMA | 3.9901 | 73.555 | 15.29% | 9 | 5 | 100% | 100% | 1 | 0.12574 | 65.3912 | 2.5232 | 20.7454 | High | High | Medium | 355 | 357 | 8.222
BRUNSWICK 1105CB | BRUNSWICK 1105 | SIERRA | 2.0209 | 50.1126 | 64.77% | 1 | 2 | 85.09% | 53.11% | 0 | 0.075406 | 102.1389 | 2.6516 | 20.4226 | High | High | Medium | 356 | 369 | 7.7019
OLEMA 110150396 | OLEMA 1101 | NORTH BAY | 12.5505 | 59.0331 | 35.48% | 29 | 15 | 95.94% | 0% | 0 | 0.11931 | 65.3912 | 2.6117 | 20.3759 | High | High | Medium | 357 | 367 | 7.8017
CAMP EVERS 210533542 | CAMP EVERS 2105 | CENTRAL COAST | 2.4779 | 18.5991 | 43.01% | 16 | 2 | 100% | 100% | 0 | 0.1603 | 35.3263 | 3.5621 | 20.1718 | High | High | High | 358 | 410 | 5.6629
CALISTOGA 1102706 | CALISTOGA 1102 | NORTH BAY | 0.14479 | 80 | 100% | 0 | 1 | 2.91% | 100% | 0 | 0.085322 | 65.3912 | 3.5861 | 20.0081 | High | High | High | 359 | 411 | 5.5793
PARADISE 1105CB | PARADISE 1105 | NORTH VALLEY | 3.6905 | 42.5038 | 17.46% | 4 | 4 | 44.69% | 100% | 0 | 0.058684 | 85.4511 | 3.9436 | 19.7758 | Medium | Medium | High | 360 | 427 | 5.0146
FULTON 110777670 | FULTON 1107 | SONOMA | 6.8809 | 26.8333 | 74.89% | 3 | 6 | 100% | 100% | 0 | 0.17389 | 47.6367 | 2.3868 | 19.7715 | High | High | Medium | 361 | 354 | 8.2837
BRUNSWICK 11052100 | BRUNSWICK 1105 | SIERRA | 3.9656 | 82.5395 | 61.98% | 2 | 1 | 100% | 39.89% | 0 | 0.074817 | 102.1389 | 2.5653 | 19.6029 | High | High | Medium | 362 | 370 | 7.6417
LOS GATOS 1106LA46 | LOS GATOS 1106 | DE ANZA | 1.5345 | 25.7114 | 95.32% | 1 | 0 | 100% | 100% | 0 | 0.15665 | 47.6367 | 2.6204 | 19.5546 | High | High | Medium | 363 | 376 | 7.4623
COARSEGOLD 21045310 | COARSEGOLD 2104 | YOSEMITE | 17.6177 | 41.6297 | 82.56% | 2 | 60 | 100% | 0% | 0 | 0.18205 | 47.6367 | 2.2493 | 19.5069 | High | High | Medium | 364 | 346 | 8.6723
SILVERADO 2102 | SILVERADO 2102 | NORTH BAY | 0.0045192 | 80 | 100% | 0 | 0 | 100% | 100% | 0 | 0.19464 | 35.3263 | 2.7872 | 19.1644 | High | High | Medium | 365 | 383 | 6.876
MIRABEL 11021139 | MIRABEL 1102 | SONOMA | 2.0153 | 64.752 | 50.11% | 2 | 2 | 100% | 100% | 0 | 0.1338 | 47.6367 | 2.9996 | 19.1194 | High | High | Medium | 366 | 395 | 6.374
MONTE RIO 1111506 | MONTE RIO 1111 | SONOMA | 1.1523 | 40.8732 | 25.9% | 6 | 0 | 100% | 100% | 0 | 0.097983 | 47.6367 | 4.0934 | 19.1062 | High | High | High | 367 | 446 | 4.6676
PARADISE 110476064 | PARADISE 1104 | NORTH VALLEY | 6.3823 | 13.6814 | 48.59% | 6 | 11 | 100% | 100% | 1 | 0.13538 | 35.3263 | 3.9849 | 19.0574 | High | High | High | 368 | 440 | 4.7824
MENDOCINO 110148750 | MENDOCINO 1101 | HUMBOLDT | 17.302 | 87.2326 | 98.93% | 5 | 5 | 100% | 70.23% | 0 | 0.19367 | 65.3912 | 1.5047 | 19.056 | High | High | Low | 369 | 259 | 12.6646
KANAKA 11011044 | KANAKA 1101 | NORTH VALLEY | 6.134 | 63.1535 | 33.69% | 2 | 5 | 100% | 70.49% | 0 | 0.080757 | 102.1389 | 2.2945 | 18.9261 | High | High | Medium | 370 | 355 | 8.2484
SHINGLE SPRINGS 21092053 | SHINGLE SPRINGS 2109 | SIERRA | 5.7202 | 32.6339 | 100% | 0 | 1 | 100% | 100% | 0 | 0.16944 | 47.6367 | 2.343 | 18.912 | High | High | Medium | 371 | 360 | 8.0716
SAN RAMON 2108CB | SAN RAMON 2108 | MISSION | 8.6488 | 65.614 | 48.13% | 2 | 4 | 90.54% | 100% | 0 | 0.12664 | 47.6367 | 3.1076 | 18.7479 | High | High | High | 372 | 398 | 6.0329
SILVERADO 2104 | SILVERADO 2104 | NORTH BAY | 0.061489 | 85 | 0% | 0 | 0 | 100% | 100% | 0 | 0.098754 | 65.3912 | 2.8976 | 18.7118 | High | High | Medium | 373 | 391 | 6.4577
CASTRO VALLEY 11068971 | CASTRO VALLEY 1106 | MISSION | 7.918 | 68.6499 | 16.36% | 0 | 1 | 100% | 100% | 0 | 0.11574 | 47.6367 | 3.3887 | 18.6837 | High | High | High | 374 | 414 | 5.5135
MIDDLETOWN 110148212 | MIDDLETOWN 1101 | HUMBOLDT | 10.2049 | 74.7586 | 62.81% | 5 | 4 | 94.29% | 99.65% | 0 | 0.19647 | 47.6367 | 1.9845 | 18.5737 | High | High | Low | 375 | 331 | 9.3592
BERKELEY F 1103BR110 | BERKELEY F 1103 | EAST BAY | 1.8512 | 58.149 | 51.38% | 3 | 2 | 32.55% | 100% | 0 | 0.071417 | 65.3912 | 3.9728 | 18.5534 | High | High | High | 376 | 445 | 4.67
OAKLAND K 110491060 | OAKLAND K 1104 | EAST BAY | 0.36025 | 77.0512 | 0% | 0 | 0 | 100% | 100% | 0 | 0.094019 | 47.6367 | 4.1348 | 18.5187 | High | High | High | 377 | 457 | 4.4788
WASHINGTON CITY GEN. 1101CB | WASHINGTON CITY GEN. 1101 | SIERRA | 0.012645 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 65.3912 | 1.3761 | 18.5003 | High | High | Low | 378 | 241 | 13.4438
WASHINGTON CITY GEN. 11011101/2 | WASHINGTON CITY GEN. 1101 | SIERRA | 0.0035486 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 65.3912 | 1.3746 | 18.4792 | High | High | Low | 379 | 241 | 13.4438
KONOCTI 11024421 | KONOCTI 1102 | HUMBOLDT | 0.36385 | 69.0599 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18318 | 47.6367 | 2.1152 | 18.4571 | High | High | Low | 380 | 344 | 8.726
WILLOW CREEK 11015002 | WILLOW CREEK 1101 | HUMBOLDT | 12.8071 | 51.1134 | 93.52% | 24 | 21 | 94.53% | 2.43% | 0 | 0.18408 | 65.3912 | 1.5331 | 18.4537 | High | High | Low | 381 | 275 | 12.0369
BRUNSWICK 110750010 | BRUNSWICK 1107 | SIERRA | 4.0845 | 61.0721 | 60.14% | 3 | 2 | 43.91% | 47.61% | 1 | 0.056677 | 102.1389 | 3.1817 | 18.4187 | Medium | Medium | High | 382 | 405 | 5.789
CALPINE 1146200-G | CALPINE 1146 | SONOMA | 0.0085256 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 47.6367 | 1.8538 | 18.1558 | High | High | Low | 383 | 317 | 9.7937
CALPINE 1146394G | CALPINE 1146 | SONOMA | 0.011293 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 47.6367 | 1.8534 | 18.1516 | High | High | Low | 384 | 317 | 9.7937
CORRAL 1101CB | CORRAL 1101 | STOCKTON | 26.1508 | 58.878 | 76.15% | 2 | 13 | 95.28% | 0% | 0 | 0.12599 | 65.3912 | 2.1911 | 18.0518 | High | High | Low | 385 | 356 | 8.2388
POINT MORETTI 11015401 | POINT MORETTI 1101 | CENTRAL COAST | 2.5449 | 35.7837 | 49.53% | 3 | 0 | 100% | 100% | 0 | 0.12284 | 47.6367 | 3.0798 | 18.0223 | High | High | High | 386 | 402 | 5.8517
ORO FINO 11022040 | ORO FINO 1102 | NORTH VALLEY | 9.1589 | 98 | 100% | 4 | 1 | 100% | 12.34% | 0 | 0.10744 | 102.1389 | 1.639 | 17.9858 | High | High | Low | 387 | 297 | 10.9734
PINE GROVE 1102CB | PINE GROVE 1102 | STOCKTON | 10.707 | 66.221 | 86.49% | 3 | 11 | 100% | 3.567% | 1 | 0.074056 | 65.3912 | 3.6625 | 17.7359 | High | High | High | 388 | 434 | 4.8426
POINT MORETTI 11015078 | POINT MORETTI 1101 | CENTRAL COAST | 14.6844 | 28.4071 | 32.64% | 18 | 2 | 100% | 99.93% | 1 | 0.2007 | 26.5534 | 3.3009 | 17.5911 | High | High | High | 389 | 418 | 5.3293
PUEBLO 2102618 | PUEBLO 2102 | NORTH BAY | 2.0485 | 88.1559 | 93.93% | 0 | 0 | 12.3% | 100% | 0 | 0.11649 | 47.6367 | 3.1658 | 17.5673 | High | High | High | 390 | 412 | 5.5491
SAN RAMON 210853732 | SAN RAMON 2108 | MISSION | 7.923 | 73.3065 | 51.9% | 0 | 2 | 100% | 100% | 0 | 0.15613 | 35.3263 | 3.1822 | 17.5521 | High | High | High | 391 | 413 | 5.5156
CAMP EVERS 210510912 | CAMP EVERS 2105 | CENTRAL COAST | 4.9849 | 57.147 | 56.28% | 17 | 4 | 100% | 100% | 0 | 0.22661 | 19.9979 | 3.8168 | 17.2965 | High | High | High | 392 | 456 | 4.5316
WOODSIDE 11011922 | WOODSIDE 1101 | PENINSULA | 3.7722 | 56.2856 | 79.83% | 3 | 6 | 79.05% | 92.98% | 1 | 0.14505 | 47.6367 | 2.5025 | 17.2916 | High | High | Medium | 393 | 382 | 6.9098
SHINGLE SPRINGS 210551738 | SHINGLE SPRINGS 2105 | SIERRA | 0.38011 | 59.0013 | 92.98% | 0 | 0 | 33.17% | 96.59% | 0 | 0.087308 | 65.3912 | 3.0193 | 17.2376 | High | High | Medium | 394 | 409 | 5.7091
TASSAJARA 21126392 | TASSAJARA 2112 | DIABLO | 5.4625 | 75.7434 | 2.892% | 0 | 3 | 100% | 100% | 0 | 0.10087 | 47.6367 | 3.5168 | 16.8979 | High | High | High | 395 | 438 | 4.8049
OAKLAND K 1104CR326 | OAKLAND K 1104 | EAST BAY | 1.3049 | 10 | 98.1% | 3 | 0 | 100% | 100% | 0 | 0.14914 | 26.5534 | 4.2299 | 16.7511 | High | High | High | 396 | 480 | 3.9602
MONTE RIO 1111140 | MONTE RIO 1111 | SONOMA | 2.6327 | 49.961 | 28.63% | 14 | 1 | 100% | 100% | 0 | 0.18634 | 26.5534 | 3.3089 | 16.3721 | High | High | High | 397 | 432 | 4.9479
SHADY GLEN 11022232 | SHADY GLEN 1102 | SIERRA | 10.57 | 94.8997 | 90.23% | 5 | 11 | 100% | 60.37% | 0 | 0.14836 | 85.4511 | 1.2808 | 16.2381 | High | High | Low | 398 | 258 | 12.6776
OTTER 11012052 | OTTER 1101 | CENTRAL COAST | 4.8416 | 80.234 | 20.15% | 9 | 2 | 100% | 100% | 0 | 0.14395 | 65.3912 | 1.7174 | 16.1669 | High | High | Low | 399 | 328 | 9.4134
SANTA ROSA A 1104642 | SANTA ROSA A 1104 | SONOMA | 13.3386 | 23.4287 | 85.18% | 3 | 22 | 100% | 84.73% | 0 | 0.24187 | 26.5534 | 2.5097 | 16.1186 | High | High | Medium | 400 | 393 | 6.4225
BEN LOMOND 04015206 | BEN LOMOND 0401 | CENTRAL COAST | 7.179 | 20.3543 | 52.81% | 22 | 2 | 100% | 100% | 0 | 0.16558 | 26.5534 | 3.6563 | 16.0757 | High | High | High | 401 | 463 | 4.3967
FORT ROSS 11212987 | FORT ROSS 1121 | SONOMA | 2.0798 | 87.0149 | 100% | 0 | 1 | 100% | 83.64% | 0 | 0.16552 | 47.6367 | 2.0189 | 15.9187 | High | High | Low | 402 | 366 | 7.8847
POINT MORETTI 110139126 | POINT MORETTI 1101 | CENTRAL COAST | 2.2477 | 14.3797 | 26.31% | 9 | 1 | 100% | 100% | 0 | 0.099437 | 47.6367 | 3.3437 | 15.8387 | High | High | High | 403 | 443 | 4.7369
OAKHURST 11035120 | OAKHURST 1103 | YOSEMITE | 6.3491 | 97.3123 | 0.04473% | 0 | 2 | 100% | 100% | 0 | 0.11061 | 85.4511 | 1.6703 | 15.7864 | High | High | Low | 404 | 326 | 9.4514
POINT MORETTI 110110726 | POINT MORETTI 1101 | CENTRAL COAST | 10.5855 | 11.8484 | 44.34% | 15 | 5 | 100% | 100% | 1 | 0.18125 | 26.5534 | 3.2767 | 15.7704 | High | High | High | 405 | 436 | 4.8128
PINE GROVE 11021765 | PINE GROVE 1102 | STOCKTON | 1.4479 | 48.9693 | 100% | 0 | 0 | 100% | 66.6% | 0 | 0.10186 | 47.6367 | 3.2382 | 15.7126 | High | High | High | 406 | 433 | 4.8523
WILLITS 1103826 | WILLITS 1103 | HUMBOLDT | 7.7428 | 68.4696 | 97.36% | 4 | 8 | 100% | 35.78% | 0 | 0.11113 | 65.3912 | 2.1617 | 15.7088 | High | High | Low | 407 | 377 | 7.267
SCE REFUGIO 1101CB | SCE REFUGIO 1101 | LOS PADRES | 0.29161 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 47.6367 | 1.5755 | 15.4297 | High | High | Low | 408 | 317 | 9.7937
MORAGA 110118216 | MORAGA 1101 | DIABLO | 5.0361 | 38.4811 | 22.22% | 5 | 16 | 100% | 100% | 0 | 0.24183 | 19.9979 | 3.1723 | 15.3416 | High | High | High | 409 | 435 | 4.8362
PIKE CITY 1102CB | PIKE CITY 1102 | SIERRA | 9.4149 | 96.7439 | 75.24% | 4 | 3 | 100% | 100% | 0 | 0.19876 | 65.3912 | 1.1735 | 15.2521 | High | High | Low | 410 | 251 | 12.9975
PARADISE 1103CB | PARADISE 1103 | NORTH VALLEY | 2.4339 | 10 | 32.27% | 5 | 0 | 48.95% | 100% | 0 | 0.058983 | 65.3912 | 3.9165 | 15.1058 | Medium | Medium | High | 411 | 483 | 3.857
TASSAJARA 210865438 | TASSAJARA 2108 | DIABLO | 0.52908 | 90 | 0% | 0 | 2 | 14.01% | 100% | 0 | 0.054006 | 85.4511 | 3.2509 | 15.0026 | Medium | Medium | High | 412 | 451 | 4.6148
MIDDLETOWN 1101CB | MIDDLETOWN 1101 | HUMBOLDT | 8.5904 | 74.5605 | 79.65% | 0 | 4 | 45.66% | 67.1% | 0 | 0.067737 | 85.4511 | 2.5869 | 14.9736 | High | High | Medium | 413 | 406 | 5.7882
DUNBAR 1101302 | DUNBAR 1101 | SONOMA | 7.7166 | 55.3691 | 64.87% | 1 | 11 | 75.08% | 68.56% | 0 | 0.15076 | 35.3263 | 2.7974 | 14.8986 | High | High | Medium | 414 | 419 | 5.3259
OAKHURST 11035470 | OAKHURST 1103 | YOSEMITE | 9.6183 | 65.532 | 32.55% | 7 | 21 | 100% | 20.07% | 0 | 0.090249 | 65.3912 | 2.5209 | 14.8769 | High | High | Medium | 415 | 401 | 5.9015
WEST POINT 110272036 | WEST POINT 1102 | STOCKTON | 2.3575 | 87.7642 | 47.51% | 4 | 2 | 100% | 22.74% | 0 | 0.055692 | 85.4511 | 3.115 | 14.8241 | Medium | Medium | High | 416 | 441 | 4.759
CLAYTON 22127758 | CLAYTON 2212 | DIABLO | 3.2393 | 62.3034 | 85.96% | 2 | 0 | 100% | 100% | 0 | 0.16375 | 26.5534 | 3.2939 | 14.3225 | High | High | High | 417 | 466 | 4.3482
SHINGLE SPRINGS 210851476 | SHINGLE SPRINGS 2108 | SIERRA | 2.9778 | 55.1791 | 91.84% | 0 | 4 | 47.94% | 85.32% | 1 | 0.09969 | 47.6367 | 3.0157 | 14.3213 | High | High | Medium | 418 | 442 | 4.7489
BIG BASIN 11029741 | BIG BASIN 1102 | CENTRAL COAST | 0.65144 | 10 | 32.18% | 5 | 0 | 100% | 100% | 0 | 0.10666 | 47.6367 | 2.8083 | 14.2687 | High | High | Medium | 419 | 425 | 5.0809
SANTA ROSA A 1104716 | SANTA ROSA A 1104 | SONOMA | 8.9162 | 55.6538 | 91.58% | 1 | 3 | 100% | 100% | 0 | 0.19056 | 26.5534 | 2.7943 | 14.1391 | High | High | Medium | 420 | 426 | 5.06
POINT MORETTI 110110722 | POINT MORETTI 1101 | CENTRAL COAST | 0.60606 | 15.6405 | 41.46% | 0 | 0 | 100% | 100% | 0 | 0.087584 | 47.6367 | 3.3583 | 14.0116 | High | High | High | 421 | 473 | 4.1722
VOLTA 110237350 | VOLTA 1102 | NORTH VALLEY | 24.2981 | 64.1392 | 95.8% | 2 | 5 | 100% | 58.24% | 1 | 0.17108 | 47.6367 | 1.7111 | 13.9446 | High | High | Low | 422 | 359 | 8.1495
WILLOW CREEK 1102CB | WILLOW CREEK 1102 | HUMBOLDT | 7.3308 | 78.4297 | 99.3% | 9 | 9 | 100% | 47.32% | 0 | 0.15188 | 65.3912 | 1.3937 | 13.8422 | High | High | Low | 423 | 316 | 9.9319
CAMP EVERS 210616000 | CAMP EVERS 2106 | CENTRAL COAST | 2.1434 | 16.7013 | 23.49% | 1 | 3 | 54.85% | 97.54% | 1 | 0.067002 | 65.3912 | 3.147 | 13.7878 | High | High | High | 424 | 464 | 4.3813
CAMP EVERS 210511384 | CAMP EVERS 2105 | CENTRAL COAST | 4.1064 | 10 | 25.57% | 1 | 1 | 100% | 100% | 0 | 0.11123 | 26.5534 | 4.6612 | 13.7668 | High | High | High | 425 | 535 | 2.9535
EAST QUINCY 11012452 | EAST QUINCY 1101 | NORTH VALLEY | 1.102 | 63.1536 | 79.93% | 0 | 1 | 13.25% | 52.23% | 1 | 0.04476 | 102.1389 | 3.0006 | 13.7179 | Medium | Medium | Medium | 426 | 455 | 4.5718
VOLTA 11021646 | VOLTA 1102 | NORTH VALLEY | 22.2648 | 70.368 | 99.98% | 0 | 4 | 92.24% | 75.72% | 0 | 0.14906 | 47.6367 | 1.9175 | 13.6151 | High | High | Low | 427 | 379 | 7.1006
ELECTRA 11017104 | ELECTRA 1101 | STOCKTON | 12.3464 | 47.2231 | 81.14% | 1 | 3 | 100% | 0% | 0 | 0.072301 | 65.3912 | 2.8473 | 13.4619 | High | High | Medium | 428 | 444 | 4.7279
MONTE RIO 1111CB | MONTE RIO 1111 | SONOMA | 0.26962 | 44.4262 | 0% | 0 | 1 | 100% | 100% | 0 | 0.078152 | 47.6367 | 3.5806 | 13.3304 | High | High | High | 429 | 491 | 3.7229
MIWUK 170179118 | MIWUK 1701 | YOSEMITE | 0.019355 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 26.5534 | 3.7802 | 13.0713 | High | High | High | 430 | 507 | 3.4578
ANNAPOLIS 1101554 | ANNAPOLIS 1101 | HUMBOLDT | 27.1366 | 85.1288 | 100% | 26 | 12 | 100% | 0% | 0 | 0.1656 | 47.6367 | 1.6533 | 13.0418 | High | High | Low | 431 | 365 | 7.8886
SONOMA 1106376 | SONOMA 1106 | SONOMA | 0.6618 | 42.582 | 100% | 0 | 0 | 12.23% | 100% | 0 | 0.072044 | 47.6367 | 3.7402 | 12.8361 | High | High | High | 432 | 508 | 3.4319
SALMON CREEK 110188998 | SALMON CREEK 1101 | SONOMA | 8.1183 | 72.1541 | 32.11% | 1 | 1 | 59.97% | 96.61% | 1 | 0.10072 | 47.6367 | 2.6582 | 12.7544 | High | High | Medium | 433 | 439 | 4.7981
VOLTA 1102CB | VOLTA 1102 | NORTH VALLEY | 3.2998 | 84.686 | 16.79% | 3 | 0 | 100% | 100% | 0 | 0.11557 | 47.6367 | 2.3012 | 12.6696 | High | High | Medium | 434 | 415 | 5.5056
OAKLAND X 1104CR022 | OAKLAND X 1104 | EAST BAY | 5.946 | 14.8032 | 44.25% | 8 | 4 | 100% | 100% | 0 | 0.14986 | 19.9979 | 4.2262 | 12.6657 | High | High | High | 435 | 532 | 2.997
MONTE RIO 1113250 | MONTE RIO 1113 | SONOMA | 1.2254 | 74.4629 | 18.87% | 1 | 1 | 100% | 100% | 0 | 0.1235 | 35.3263 | 2.8957 | 12.6334 | High | High | Medium | 436 | 465 | 4.3628
CAMP EVERS 21045096 | CAMP EVERS 2104 | CENTRAL COAST | 20.6359 | 43.5028 | 64.15% | 34 | 7 | 100% | 100% | 0 | 0.33163 | 11.2183 | 3.3817 | 12.581 | High | High | High | 437 | 492 | 3.7203
BRUNSWICK 110456468 | BRUNSWICK 1104 | SIERRA | 5.7301 | 68.1683 | 52.05% | 5 | 6 | 95.81% | 0% | 0 | 0.070779 | 65.3912 | 2.7112 | 12.5481 | High | High | Medium | 438 | 449 | 4.6283
SILVERADO 21038401 | SILVERADO 2103 | NORTH BAY | 0.63211 | 87.9301 | 93.73% | 0 | 0 | 9.105% | 100% | 0 | 0.088787 | 65.3912 | 2.1595 | 12.5377 | High | High | Low | 439 | 404 | 5.8059
RINCON 11035152 | RINCON 1103 | SONOMA | 1.5925 | 84.6014 | 46.06% | 2 | 0 | 100% | 100% | 0 | 0.14097 | 35.3263 | 2.5132 | 12.5158 | High | High | Medium | 440 | 430 | 4.9799
CAMP EVERS 210511010 | CAMP EVERS 2105 | CENTRAL COAST | 2.2251 | 32.8132 | 34.55% | 4 | 3 | 100% | 100% | 0 | 0.11572 | 26.5534 | 3.9822 | 12.2369 | High | High | High | 441 | 526 | 3.0729
CRESCENT MILLS 21013113 | CRESCENT MILLS 2101 | NORTH VALLEY | 1.193 | 94.468 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049705 | 85.4511 | 2.837 | 12.0498 | Medium | Medium | Medium | 442 | 472 | 4.2473
MEADOW LANE 2106C558R | MEADOW LANE 2106 | DIABLO | 0.20712 | 95 | 0% | 0 | 0 | 1.459% | 100% | 0 | 0.041876 | 85.4511 | 3.36 | 12.0232 | Medium | Medium | High | 443 | 501 | 3.5783
MIDDLETOWN 11011325 | MIDDLETOWN 1101 | HUMBOLDT | 8.5949 | 66.5337 | 99.94% | 1 | 2 | 100% | 100% | 0 | 0.23318 | 26.5534 | 1.9402 | 12.0132 | High | High | Low | 444 | 397 | 6.1918
BIG BASIN 110165444 | BIG BASIN 1101 | CENTRAL COAST | 0.47094 | 48.0736 | 0% | 2 | 0 | 100% | 100% | 0 | 0.090816 | 35.3263 | 3.743 | 12.0083 | High | High | High | 445 | 518 | 3.2082
GARBERVILLE 11022500 | GARBERVILLE 1102 | HUMBOLDT | 16.0185 | 91.6655 | 50.61% | 18 | 6 | 100% | 0% | 0 | 0.098692 | 85.4511 | 1.4185 | 11.9622 | High | High | Low | 446 | 351 | 8.4333
CORRAL 110112608 | CORRAL 1101 | STOCKTON | 35.0176 | 52.1044 | 87.04% | 0 | 19 | 100% | 0% | 0 | 0.16618 | 47.6367 | 1.4909 | 11.8026 | High | High | Low | 447 | 364 | 7.9163
MIDDLETOWN 1101622 | MIDDLETOWN 1101 | HUMBOLDT | 15.6831 | 77.1942 | 76.84% | 4 | 8 | 78.63% | 70.55% | 1 | 0.1922 | 26.5534 | 2.3118 | 11.7983 | High | High | Medium | 448 | 424 | 5.1034
DUNBAR 11021285 | DUNBAR 1102 | SONOMA | 4.061 | 83.8717 | 58.26% | 1 | 2 | 100% | 27.24% | 1 | 0.053737 | 65.3912 | 3.3515 | 11.7769 | Medium | Medium | High | 449 | 505 | 3.5139
PETALUMA C 1108208 | PETALUMA C 1108 | SONOMA | 12.4029 | 84.7631 | 33.65% | 1 | 1 | 100% | 0% | 0 | 0.07858 | 65.3912 | 2.287 | 11.7516 | High | High | Medium | 450 | 423 | 5.1384
RESEARCH 21029746 | RESEARCH 2102 | DIABLO | 0.70252 | 57.1565 | 2.503% | 0 | 3 | 24.99% | 100% | 0 | 0.044375 | 85.4511 | 3.091 | 11.7205 | Medium | Medium | High | 451 | 487 | 3.7919
MONTE RIO 11135024 | MONTE RIO 1113 | SONOMA | 0.33932 | 27.3622 | 58.73% | 2 | 0 | 100% | 100% | 0 | 0.10965 | 35.3263 | 3.0239 | 11.7136 | High | High | Medium | 452 | 482 | 3.8736
PARADISE 110181966 | PARADISE 1101 | NORTH VALLEY | 0.1834 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 47.6367 | 3.9719 | 11.6474 | High | High | High | 453 | 540 | 2.9325
COTATI 1105CB | COTATI 1105 | SONOMA | 3.1602 | 63.5412 | 54.85% | 1 | 0 | 100% | 0% | 0 | 0.061793 | 65.3912 | 2.8768 | 11.6244 | High | High | Medium | 454 | 477 | 4.0407
BRUNSWICK 1102CB | BRUNSWICK 1102 | SIERRA | 6.3271 | 51.9471 | 61.35% | 4 | 0 | 99.87% | 31.38% | 0 | 0.047536 | 85.4511 | 2.763 | 11.2233 | Medium | Medium | Medium | 455 | 476 | 4.062
BONNIE NOOK 110186696 | BONNIE NOOK 1101 | SIERRA | 9.7026 | 94.616 | 77.04% | 2 | 5 | 100% | 100% | 0 | 0.2013 | 85.4511 | 0.64933 | 11.1691 | High | High | Low | 456 | 184 | 17.2011
KONOCTI 110275382 | KONOCTI 1102 | HUMBOLDT | 21.8665 | 65.7136 | 85.11% | 11 | 7 | 94.25% | 84.3% | 0 | 0.27016 | 19.9979 | 2.0627 | 11.1439 | High | High | Low | 457 | 417 | 5.4025
PARADISE 110236656 | PARADISE 1102 | NORTH VALLEY | 3.3309 | 17.0477 | 19.52% | 3 | 5 | 87.51% | 100% | 0 | 0.076178 | 35.3263 | 4.1355 | 11.129 | High | High | High | 458 | 552 | 2.6911
HAMILTON BRANCH 110190334 | HAMILTON BRANCH 1101 | NORTH VALLEY | 3.3715 | 83.9014 | 99.76% | 0 | 0 | 100% | 0% | 0 | 0.046313 | 85.4511 | 2.8026 | 11.0913 | Medium | Medium | Medium | 459 | 481 | 3.9575
WILLOW CREEK 11013050 | WILLOW CREEK 1101 | HUMBOLDT | 2.7741 | 81.978 | 100% | 0 | 2 | 100% | 100% | 1 | 0.20349 | 65.3912 | 0.83142 | 11.0633 | High | High | Low | 460 | 245 | 13.3065
FORT ROSS 1121204 | FORT ROSS 1121 | SONOMA | 18.7577 | 93.0498 | 90.41% | 0 | 2 | 100% | 39.05% | 1 | 0.10967 | 65.3912 | 1.5385 | 11.0336 | High | High | Low | 461 | 378 | 7.1716
OLEMA 11011252 | OLEMA 1101 | NORTH BAY | 4.0529 | 83.346 | 14.42% | 10 | 5 | 98.65% | 0% | 0 | 0.042756 | 85.4511 | 3.0154 | 11.0171 | Medium | Medium | Medium | 462 | 494 | 3.6535
WILLOW CREEK 110237374 | WILLOW CREEK 1102 | HUMBOLDT | 2.2967 | 96.0041 | 99.34% | 1 | 0 | 100% | 68.24% | 0 | 0.13938 | 65.3912 | 1.2034 | 10.9677 | High | High | Low | 463 | 339 | 9.1142
BELL 11072400 | BELL 1107 | SIERRA | 24.3699 | 40.733 | 58.06% | 2 | 11 | 87.78% | 0% | 0 | 0.061332 | 65.3912 | 2.7006 | 10.8308 | Medium | Medium | Medium | 464 | 479 | 4.0106
BIG MEADOWS 21012474 | BIG MEADOWS 2101 | NORTH VALLEY | 8.0369 | 74.0553 | 100% | 0 | 14 | 96.17% | 0% | 0 | 0.062896 | 65.3912 | 2.6243 | 10.7933 | High | High | Medium | 465 | 474 | 4.1128
APPLE HILL 110412947 | APPLE HILL 1104 | SIERRA | 3.4561 | 89.425 | 100% | 0 | 1 | 100% | 0% | 0 | 0.04907 | 102.1389 | 2.1335 | 10.6933 | Medium | Medium | Low | 466 | 429 | 5.012
PENNGROVE 1101170 | PENNGROVE 1101 | SONOMA | 18.4109 | 61.4183 | 85.26% | 5 | 17 | 81.28% | 0% | 0 | 0.065227 | 65.3912 | 2.4598 | 10.4915 | High | High | Medium | 467 | 468 | 4.2653
TASSAJARA 210812712 | TASSAJARA 2108 | DIABLO | 0.60405 | 70.6966 | 76.13% | 0 | 2 | 18.42% | 100% | 0 | 0.089254 | 35.3263 | 3.2876 | 10.366 | High | High | High | 468 | 520 | 3.153
PASO ROBLES 1103N04 | PASO ROBLES 1103 | LOS PADRES | 0.58532 | 54.1264 | 3.167% | 0 | 8 | 100% | 0% | 0 | 0.051036 | 65.3912 | 3.1021 | 10.3524 | Medium | Medium | High | 469 | 514 | 3.3373
RACETRACK 1704CB | RACETRACK 1704 | YOSEMITE | 22.0312 | 55.84 | 32.56% | 4 | 25 | 99.99% | 0% | 0 | 0.18885 | 26.5534 | 2.0435 | 10.2471 | High | High | Low | 470 | 428 | 5.0145
OAKHURST 110363334 | OAKHURST 1103 | YOSEMITE | 17.2522 | 47.378 | 100% | 1 | 11 | 100% | 10.77% | 0 | 0.054511 | 65.3912 | 2.871 | 10.2339 | Medium | Medium | Medium | 471 | 503 | 3.5646
PINE GROVE 1101CB | PINE GROVE 1101 | STOCKTON | 4.2594 | 78.3336 | 50.63% | 0 | 5 | 100% | 0% | 0 | 0.038055 | 85.4511 | 3.1345 | 10.1928 | Medium | Medium | High | 472 | 517 | 3.2518
CAMP EVERS 21055577 | CAMP EVERS 2105 | CENTRAL COAST | 1.1615 | 10 | 45.86% | 6 | 1 | 100% | 100% | 0 | 0.10796 | 19.9979 | 4.695 | 10.1361 | High | High | High | 473 | 595 | 2.1589
WEST POINT 11025357 | WEST POINT 1102 | STOCKTON | 3.286 | 83.7938 | 100% | 3 | 2 | 100% | 17.3% | 0 | 0.065365 | 65.3912 | 2.3603 | 10.0887 | High | High | Medium | 474 | 467 | 4.2743
BRUNSWICK 1104761310 | BRUNSWICK 1104 | SIERRA | 0.029625 | 37.5776 | 100% | 0 | 0 | 100% | 100% | 0 | 0.15312 | 26.5534 | 2.4455 | 9.9432 | High | High | Medium | 475 | 475 | 4.0659
OLEMA 11011318 | OLEMA 1101 | NORTH BAY | 6.3563 | 77.6358 | 7.161% | 18 | 6 | 61.46% | 0% | 0 | 0.045105 | 85.4511 | 2.535 | 9.7705 | Medium | Medium | Medium | 476 | 484 | 3.8543
SILVERADO 210365334 | SILVERADO 2103 | NORTH BAY | 0.51221 | 90 | 100% | 0 | 0 | 7.915% | 100% | 0 | 0.093253 | 47.6367 | 2.1963 | 9.7565 | High | High | Low | 477 | 458 | 4.4422
LOW GAP 1101CB | LOW GAP 1101 | HUMBOLDT | 2.17 | 82.2052 | 100% | 6 | 1 | 100% | 0% | 0 | 0.073547 | 65.3912 | 2.01 | 9.6669 | High | High | Low | 478 | 437 | 4.8093
TASSAJARA 21123202 | TASSAJARA 2112 | DIABLO | 0.99352 | 84.671 | 60.56% | 0 | 0 | 100% | 100% | 0 | 0.15269 | 19.9979 | 3.1551 | 9.6344 | High | High | High | 479 | 530 | 3.0536
REDBUD 1101708166 | REDBUD 1101 | HUMBOLDT | 10.1809 | 81.1955 | 96.21% | 0 | 3 | 49.7% | 53.54% | 1 | 0.096142 | 47.6367 | 2.1005 | 9.6203 | High | High | Low | 480 | 454 | 4.5799
SIERRA CITY GEN 1101CB | SIERRA CITY GEN 1101 | SIERRA | 0.013222 | 95 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049877 | 85.4511 | 2.24 | 9.5471 | Medium | Medium | Medium | 481 | 469 | 4.262
SIERRA CITY GEN 11011101/2 | SIERRA CITY GEN 1101 | SIERRA | 0.0052893 | 95 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049877 | 85.4511 | 2.2291 | 9.5007 | Medium | Medium | Low | 482 | 469 | 4.262
SANTA ROSA A 1104220 | SANTA ROSA A 1104 | SONOMA | 9.5297 | 27.599 | 64.91% | 1 | 14 | 100% | 64.31% | 0 | 0.11149 | 26.5534 | 3.1942 | 9.4563 | High | High | High | 483 | 534 | 2.9604
PARADISE 11041571 | PARADISE 1104 | NORTH VALLEY | 0.64266 | 10 | 49.69% | 2 | 2 | 100% | 100% | 0 | 0.10792 | 19.9979 | 4.3768 | 9.4463 | High | High | High | 484 | 596 | 2.1582
SILVERADO 21051306 | SILVERADO 2105 | NORTH BAY | 2.7442 | 84.7075 | 83.99% | 0 | 2 | 34.98% | 54.43% | 0 | 0.068801 | 47.6367 | 2.8813 | 9.4434 | High | High | Medium | 485 | 516 | 3.2775
MIDDLETOWN 1102998 | MIDDLETOWN 1102 | HUMBOLDT | 14.694 | 30.2565 | 100% | 0 | 1 | 86% | 0% | 0 | 0.055128 | 47.6367 | 3.5751 | 9.3887 | Medium | Medium | High | 486 | 555 | 2.6261
MENLO 11028952 | MENLO 1102 | PENINSULA | 6.6194 | 37.3674 | 79.3% | 6 | 6 | 97.26% | 0% | 0 | 0.07359 | 35.3263 | 3.5512 | 9.2318 | High | High | High | 487 | 557 | 2.5996
MOUNTAIN QUARRIES 2101CB | MOUNTAIN QUARRIES 2101 | SIERRA | 24.9741 | 44.4478 | 67.2% | 2 | 3 | 100% | 0% | 0 | 0.056988 | 65.3912 | 2.4457 | 9.1138 | Medium | Medium | Medium | 488 | 490 | 3.7265
MESA 11016111 | MESA 1101 | LOS PADRES | 23.8724 | 66.2721 | 84.61% | 0 | 7 | 92.83% | 48.37% | 0 | 0.23056 | 19.9979 | 1.9723 | 9.0938 | High | High | Low | 489 | 452 | 4.6108
HATTON 1101 | HATTON 1101 | CENTRAL COAST | 0.058169 | 90 | 100% | 0 | 0 | 100% | 0% | 0 | 0.054802 | 65.3912 | 2.5228 | 9.0405 | Medium | Medium | Medium | 490 | 500 | 3.5836
FORT ROSS 11214947 | FORT ROSS 1121 | SONOMA | 10.2762 | 93.0727 | 99.97% | 4 | 1 | 100% | 8.448% | 0 | 0.11096 | 47.6367 | 1.71 | 9.0384 | High | High | Low | 491 | 421 | 5.2856
DESCHUTES 110449024 | DESCHUTES 1104 | NORTH VALLEY | 16.4286 | 33.9792 | 100% | 0 | 7 | 97.93% | 0% | 0 | 0.055326 | 65.3912 | 2.4946 | 9.0253 | Medium | Medium | Medium | 492 | 499 | 3.6179
BRUNSWICK 11042112 | BRUNSWICK 1104 | SIERRA | 19.306 | 55.1614 | 89% | 4 | 7 | 100% | 25.18% | 0 | 0.10285 | 35.3263 | 2.4774 | 9.0016 | High | High | Medium | 493 | 497 | 3.6335
CAMP EVERS 210595394 | CAMP EVERS 2105 | CENTRAL COAST | 0.49589 | 10 | 8.806% | 0 | 0 | 100% | 100% | 0 | 0.065893 | 35.3263 | 3.8628 | 8.9916 | High | High | High | 494 | 575 | 2.3278
MENLO 11038512 | MENLO 1103 | PENINSULA | 16.8652 | 73.7343 | 67.92% | 14 | 5 | 100% | 0% | 0 | 0.10603 | 35.3263 | 2.3875 | 8.9425 | High | High | Medium | 495 | 489 | 3.7456
MORAGA 110183424 | MORAGA 1101 | DIABLO | 1.6164 | 79.1593 | 0% | 0 | 0 | 100% | 62.3% | 0 | 0.053892 | 47.6367 | 3.4366 | 8.8227 | Medium | Medium | High | 496 | 560 | 2.5672
WISE 11022230 | WISE 1102 | SIERRA | 22.0893 | 25.2486 | 59.65% | 3 | 10 | 89.01% | 0% | 0 | 0.09262 | 47.6367 | 1.9917 | 8.7874 | High | High | Low | 497 | 461 | 4.4121
BIG BASIN 110112838 | BIG BASIN 1101 | CENTRAL COAST | 2.3481 | 22.8055 | 19.65% | 7 | 1 | 100% | 100% | 0 | 0.097327 | 26.5534 | 3.3758 | 8.7244 | High | High | High | 498 | 559 | 2.5844
HOOPA 11017468 | HOOPA 1101 | HUMBOLDT | 5.6936 | 54.3189 | 96.19% | 3 | 8 | 47.51% | 49.77% | 1 | 0.076067 | 65.3912 | 1.7487 | 8.6983 | High | High | Low | 499 | 431 | 4.9741
GARBERVILLE 11028652 | GARBERVILLE 1102 | HUMBOLDT | 13.0139 | 91.1649 | 97.21% | 18 | 2 | 100% | 0% | 0 | 0.11424 | 47.6367 | 1.5713 | 8.5506 | High | High | Low | 500 | 416 | 5.4418
FITCH MOUNTAIN 1113356 | FITCH MOUNTAIN 1113 | SONOMA | 9.9757 | 80.7752 | 75.25% | 5 | 1 | 65.83% | 51.2% | 1 | 0.073371 | 47.6367 | 2.443 | 8.5386 | High | High | Medium | 501 | 506 | 3.4951
CALPINE 1144962 | CALPINE 1144 | SONOMA | 4.058 | 94.9648 | 64.72% | 0 | 0 | 100% | 100% | 0 | 0.16674 | 26.5534 | 1.9214 | 8.5068 | High | High | Low | 502 | 460 | 4.4275
MIRABEL 110213597 | MIRABEL 1102 | SONOMA | 0.47204 | 30.1701 | 51.63% | 3 | 0 | 100% | 100% | 0 | 0.10712 | 26.5534 | 2.9615 | 8.4237 | High | High | Medium | 503 | 546 | 2.8444
SANTA ROSA A 1111114 | SANTA ROSA A 1111 | SONOMA | 5.593 | 82.824 | 61.55% | 3 | 5 | 48.78% | 0.05081% | 0 | 0.039882 | 65.3912 | 3.2275 | 8.4172 | Medium | Medium | High | 504 | 556 | 2.608
PENRYN 1103604 | PENRYN 1103 | SIERRA | 26.4899 | 35.3404 | 72.55% | 7 | 11 | 100% | 0% | 0 | 0.061577 | 47.6367 | 2.8611 | 8.3925 | High | High | Medium | 505 | 539 | 2.9333
CHALLENGE 110113026 | CHALLENGE 1101 | NORTH VALLEY | 7.8248 | 63.8642 | 100% | 1 | 1 | 97.67% | 96.11% | 0 | 0.25947 | 85.4511 | 0.3778 | 8.3764 | High | High | Low | 506 | 120 | 22.1717
PINE GROVE 11011021 | PINE GROVE 1101 | STOCKTON | 4.1934 | 79.4355 | 93.37% | 0 | 1 | 100% | 0% | 0 | 0.043638 | 65.3912 | 2.9314 | 8.3647 | Medium | Medium | Medium | 507 | 545 | 2.8535
SANTA YNEZ 1104Y66 | SANTA YNEZ 1104 | LOS PADRES | 16.6796 | 85.1619 | 76.69% | 1 | 3 | 92.13% | 26.5% | 0 | 0.10816 | 35.3263 | 2.1886 | 8.3621 | High | High | Low | 508 | 485 | 3.8208
MONROE 2103CB | MONROE 2103 | SONOMA | 0.73533 | 61.5712 | 100% | 0 | 0 | 5.132% | 100% | 0 | 0.076074 | 47.6367 | 2.2963 | 8.3215 | High | High | Medium | 509 | 498 | 3.6239
DIAMOND SPRINGS 110518935 | DIAMOND SPRINGS 1105 | SIERRA | 6.6942 | 21.2209 | 100% | 2 | 4 | 100% | 72.5% | 0 | 0.11646 | 26.5534 | 2.6792 | 8.2855 | High | High | Medium | 510 | 523 | 3.0925
CORNING 110185152 | CORNING 1101 | NORTH VALLEY | 23.0821 | 26.0719 | 100% | 2 | 8 | 100% | 0% | 0 | 0.11691 | 26.5534 | 2.6425 | 8.2029 | High | High | Medium | 511 | 521 | 3.1042
PACIFICA 1101CB | PACIFICA 1101 | PENINSULA | 1.1754 | 10 | 25.99% | 0 | 0 | 43.55% | 100% | 0 | 0.044128 | 47.6367 | 3.8732 | 8.142 | Medium | Medium | High | 512 | 598 | 2.1021
SILVERADO 21051308 | SILVERADO 2105 | NORTH BAY | 0.01945 | 80.9995 | 16% | 3 | 1 | 0.3576% | 100% | 0 | 0.045462 | 47.6367 | 3.7584 | 8.1396 | Medium | Medium | High | 513 | 594 | 2.1657
DUNBAR 11014817 | DUNBAR 1101 | SONOMA | 3.1798 | 21.7127 | 52.45% | 3 | 3 | 100% | 100% | 0 | 0.15344 | 19.9979 | 2.6498 | 8.1309 | High | High | Medium | 514 | 527 | 3.0685
GIRVAN 11021028 | GIRVAN 1102 | NORTH VALLEY | 17.4682 | 30.4656 | 99.97% | 3 | 19 | 100% | 100% | 1 | 0.28494 | 14.9507 | 1.8976 | 8.084 | High | High | Low | 515 | 471 | 4.26
ATASCADERO 11012537 | ATASCADERO 1101 | LOS PADRES | 15.4143 | 42.2463 | 87.6% | 5 | 1 | 100% | 82.31% | 1 | 0.15256 | 19.9979 | 2.6276 | 8.0166 | High | High | Medium | 516 | 531 | 3.0509
COTATI 110379140 | COTATI 1103 | SONOMA | 9.8425 | 61.4372 | 48.82% | 7 | 2 | 79.77% | 0% | 0 | 0.047459 | 65.3912 | 2.5749 | 7.9908 | Medium | Medium | Medium | 517 | 522 | 3.1034
CAMP EVERS 21035753 | CAMP EVERS 2103 | CENTRAL COAST | 2.4228 | 18.1993 | 27.31% | 10 | 4 | 100% | 100% | 0 | 0.13875 | 14.9507 | 3.8491 | 7.9846 | High | High | High | 518 | 600 | 2.0744
MIDDLETOWN 11011314 | MIDDLETOWN 1101 | HUMBOLDT | 0.82482 | 85.7951 | 100% | 0 | 0 | 88.81% | 5.14% | 1 | 0.051914 | 65.3912 | 2.3199 | 7.8754 | Medium | Medium | Medium | 519 | 512 | 3.3947
BRUNSWICK 11102664 | BRUNSWICK 1110 | SIERRA | 9.7807 | 42.9965 | 66.17% | 2 | 0 | 90.12% | 0% | 0 | 0.042278 | 65.3912 | 2.8403 | 7.8524 | Medium | Medium | Medium | 520 | 549 | 2.7646
KONOCTI 110264664 | KONOCTI 1102 | HUMBOLDT | 27.2111 | 54.3183 | 71% | 3 | 9 | 94.13% | 22.47% | 0 | 0.10647 | 26.5534 | 2.7454 | 7.7618 | High | High | Medium | 521 | 547 | 2.8272
FRUITLAND 114293234 | FRUITLAND 1142 | HUMBOLDT | 11.3813 | 94.4975 | 76.78% | 16 | 5 | 100% | 0% | 0 | 0.081313 | 65.3912 | 1.4517 | 7.7189 | High | High | Low | 522 | 420 | 5.3172
CALISTOGA 11011087 | CALISTOGA 1101 | NORTH BAY | 1.9847 | 74.7271 | 70.51% | 0 | 0 | 100% | 100% | 0 | 0.15452 | 19.9979 | 2.4735 | 7.6433 | High | High | Medium | 523 | 524 | 3.0901
FORT SEWARD 11211690 | FORT SEWARD 1121 | HUMBOLDT | 10.4929 | 86.5731 | 100% | 15 | 3 | 64.42% | 0% | 0 | 0.055586 | 65.3912 | 2.046 | 7.4369 | Medium | Medium | Low | 524 | 496 | 3.6348
CLOVERDALE 1101 | CLOVERDALE 1101 | SONOMA | 0.067026 | 85 | 100% | 0 | 0 | 100% | 0% | 0 | 0.046733 | 65.3912 | 2.4317 | 7.4312 | Medium | Medium | Medium | 525 | 529 | 3.0559
SHADY GLEN 11012768 | SHADY GLEN 1101 | SIERRA | 7.6983 | 67.5569 | 97.78% | 0 | 5 | 95.39% | 10.27% | 0 | 0.057683 | 65.3912 | 1.9636 | 7.4066 | Medium | Medium | Low | 526 | 488 | 3.7719
TEMPLETON 2113A10 | TEMPLETON 2113 | LOS PADRES | 30.9401 | 69.101 | 70.57% | 5 | 5 | 100% | 93.66% | 0 | 0.21943 | 26.5534 | 1.2694 | 7.3966 | High | High | Low | 527 | 403 | 5.8266
BRUNSWICK 1102940 | BRUNSWICK 1102 | SIERRA | 0.6541 | 82.3173 | 27.04% | 0 | 0 | 18.81% | 100% | 0 | 0.056253 | 47.6367 | 2.7437 | 7.3523 | Medium | Medium | Medium | 528 | 553 | 2.6797
WILLOW CREEK 1101CB | WILLOW CREEK 1101 | HUMBOLDT | 0.28035 | 73.844 | 25.25% | 2 | 0 | 100% | 100% | 0 | 0.11379 | 35.3263 | 1.829 | 7.3523 | High | High | Low | 529 | 478 | 4.0198
CAMP EVERS 21055188 | CAMP EVERS 2105 | CENTRAL COAST | 1.985 | 10 | 58.42% | 1 | 0 | 100% | 100% | 0 | 0.10955 | 19.9979 | 3.3123 | 7.2566 | High | High | High | 530 | 592 | 2.1908
BRUNSWICK 11047181 | BRUNSWICK 1104 | SIERRA | 0.77307 | 57.8754 | 100% | 1 | 1 | 100% | 0% | 0 | 0.040435 | 65.3912 | 2.6834 | 7.0953 | Medium | Medium | Medium | 531 | 554 | 2.6441
NORTH BRANCH 110111206 | NORTH BRANCH 1101 | STOCKTON | 17.2475 | 65.0034 | 87.98% | 1 | 4 | 96.4% | 0% | 0 | 0.057888 | 35.3263 | 3.4658 | 7.0874 | Medium | Medium | High | 532 | 601 | 2.045
OCEANO 1104Q10 | OCEANO 1104 | LOS PADRES | 23.5484 | 28.2238 | 59% | 7 | 3 | 100% | 0% | 0 | 0.065893 | 35.3263 | 3.0376 | 7.0708 | High | High | Medium | 533 | 576 | 2.3277
MOLINO 1101338 | MOLINO 1101 | SONOMA | 7.3596 | 75.7123 | 66.21% | 4 | 4 | 51.47% | 0% | 0 | 0.035347 | 65.3912 | 3.0506 | 7.0511 | Medium | Medium | Medium | 534 | 579 | 2.3114
COTATI 110599720 | COTATI 1105 | SONOMA | 7.8564 | 53.7004 | 71.89% | 3 | 7 | 63.87% | 0% | 0 | 0.042996 | 65.3912 | 2.5058 | 7.0451 | Medium | Medium | Medium | 535 | 548 | 2.8115
BIG BASIN 11026219 | BIG BASIN 1102 | CENTRAL COAST | 0.89903 | 23.7161 | 100% | 1 | 0 | 100% | 100% | 0 | 0.14284 | 19.9979 | 2.4506 | 6.9999 | High | High | Medium | 536 | 544 | 2.8564
BIG BASIN 110212758 | BIG BASIN 1102 | CENTRAL COAST | 6.1262 | 42.4144 | 40.92% | 12 | 2 | 100% | 100% | 0 | 0.21481 | 11.2183 | 2.8889 | 6.9619 | High | High | Medium | 537 | 570 | 2.4099
PETALUMA C 1108296 | PETALUMA C 1108 | SONOMA | 14.7729 | 78.7625 | 21.22% | 3 | 7 | 100% | 0% | 0 | 0.037166 | 65.3912 | 2.8405 | 6.9034 | Medium | Medium | Medium | 538 | 566 | 2.4303
DUNBAR 11022359 | DUNBAR 1102 | SONOMA | 4.5098 | 82.5925 | 84.36% | 0 | 1 | 100% | 0% | 0 | 0.041489 | 47.6367 | 3.4865 | 6.8907 | Medium | Medium | High | 539 | 606 | 1.9764
LOW GAP 110186816 | LOW GAP 1101 | HUMBOLDT | 4.4169 | 87.0623 | 100% | 0 | 8 | 100% | 0% | 0 | 0.071339 | 65.3912 | 1.4627 | 6.8232 | High | High | Low | 540 | 447 | 4.6649
CLARKSVILLE 2104CB | CLARKSVILLE 2104 | SIERRA | 9.4695 | 34.2727 | 54.5% | 0 | 3 | 89.57% | 0% | 0 | 0.028962 | 65.3912 | 3.5993 | 6.8166 | Medium | Medium | High | 541 | 618 | 1.8939
COTATI 110536536 | COTATI 1105 | SONOMA | 14.0222 | 66.9943 | 49.66% | 3 | 4 | 71.19% | 0% | 0 | 0.039741 | 65.3912 | 2.6116 | 6.7868 | Medium | Medium | Medium | 542 | 558 | 2.5987
RACETRACK 170455798 | RACETRACK 1704 | YOSEMITE | 15.7881 | 56.8107 | 46.06% | 3 | 13 | 100% | 0% | 0 | 0.064582 | 47.6367 | 2.1973 | 6.7599 | High | High | Low | 543 | 525 | 3.0765
SPANISH CREEK 4401CB | SPANISH CREEK 4401 | NORTH VALLEY | 7.9163 | 94.7918 | 10.89% | 2 | 9 | 99.83% | 0% | 0 | 0.034339 | 85.4511 | 2.2893 | 6.7174 | Medium | Medium | Medium | 544 | 538 | 2.9343
PHILO 11022600 | PHILO 1102 | HUMBOLDT | 19.2386 | 94.0358 | 55.52% | 12 | 3 | 96.16% | 0% | 0 | 0.060847 | 85.4511 | 1.2847 | 6.6795 | Medium | Medium | Low | 545 | 422 | 5.1995
OCEANO 1104V36 | OCEANO 1104 | LOS PADRES | 8.9209 | 45.6964 | 61.88% | 2 | 5 | 67.02% | 0% | 0 | 0.047581 | 47.6367 | 2.9332 | 6.6484 | Medium | Medium | Medium | 546 | 586 | 2.2666
PASO ROBLES 1103N50 | PASO ROBLES 1103 | LOS PADRES | 2.1383 | 48.485 | 34.16% | 0 | 1 | 100% | 0% | 0 | 0.042301 | 47.6367 | 3.2748 | 6.599 | Medium | Medium | High | 547 | 603 | 2.0151
DUNBAR 1102246 | DUNBAR 1102 | SONOMA | 14.7102 | 40.7068 | 52.1% | 6 | 13 | 100% | 1.558% | 0 | 0.064871 | 35.3263 | 2.8342 | 6.495 | High | High | Medium | 548 | 583 | 2.2917
MORAGA 110531512 | MORAGA 1105 | DIABLO | 1.6381 | 82.7006 | 6.913% | 0 | 1 | 35.45% | 68.16% | 0 | 0.035075 | 47.6367 | 3.886 | 6.493 | Medium | Medium | High | 549 | 633 | 1.6709
BELLEVUE 2103478 | BELLEVUE 2103 | SONOMA | 7.8213 | 71.5626 | 88.7% | 0 | 2 | 38.92% | 0% | 0 | 0.02921 | 65.3912 | 3.3117 | 6.3256 | Medium | Medium | High | 550 | 615 | 1.9101
PACIFICA 11015001 | PACIFICA 1101 | PENINSULA | 1.7299 | 13.6047 | 57.13% | 0 | 0 | 33.8% | 76.31% | 0 | 0.036346 | 47.6367 | 3.6453 | 6.3114 | Medium | Medium | High | 551 | 628 | 1.7314
JESSUP 110276068 | JESSUP 1102 | NORTH VALLEY | 15.5129 | 23.0172 | 100% | 2 | 4 | 80.72% | 0% | 0 | 0.061753 | 47.6367 | 2.125 | 6.2511 | High | High | Low | 552 | 537 | 2.9417
MOLINO 11015042 | MOLINO 1101 | SONOMA | 5.4336 | 70.9721 | 53.86% | 5 | 2 | 79.32% | 0% | 0 | 0.030542 | 65.3912 | 3.0912 | 6.1735 | Medium | Medium | High | 553 | 605 | 1.9971
SHINGLE SPRINGS 21099372 | SHINGLE SPRINGS 2109 | SIERRA | 17.5824 | 48.8833 | 68.76% | 2 | 5 | 100% | 52.97% | 0 | 0.1201 | 26.5534 | 1.9275 | 6.147 | High | High | Low | 554 | 519 | 3.1891
BIG BASIN 11019773 | BIG BASIN 1101 | CENTRAL COAST | 0.4507 | 10 | 17.07% | 7 | 0 | 100% | 100% | 0 | 0.097654 | 19.9979 | 3.1187 | 6.0905 | High | High | High | 555 | 611 | 1.9529
LAYTONVILLE 1101CB | LAYTONVILLE 1101 | HUMBOLDT | 7.0679 | 79.2729 | 100% | 10 | 7 | 78.03% | 0% | 0 | 0.054066 | 85.4511 | 1.3144 | 6.0728 | Medium | Medium | Low | 556 | 450 | 4.62
CAMP EVERS 2105BL 2101 | CAMP EVERS 2105 | CENTRAL COAST | 0.0032282 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 26.5534 | 3.7013 | 6.0502 | High | High | High | 557 | 638 | 1.6346
GREENBRAE 1103 | GREENBRAE 1103 | NORTH BAY | 0.019268 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 26.5534 | 3.6958 | 6.0412 | High | High | High | 558 | 638 | 1.6346
PETALUMA C 1108628 | PETALUMA C 1108 | SONOMA | 9.0995 | 58.7807 | 34.73% | 0 | 3 | 82.01% | 0% | 0 | 0.035008 | 65.3912 | 2.6389 | 6.041 | Medium | Medium | Medium | 559 | 584 | 2.2892
ROSSMOOR 1102CB | ROSSMOOR 1102 | DIABLO | 0.0028423 | 10 | 0% | 0 | 0 | 0.1985% | 100% | 0 | 0.023559 | 65.3912 | 3.8658 | 5.9555 | Medium | Medium | High | 560 | 645 | 1.5406
HIGHLANDS 1103828 | HIGHLANDS 1103 | HUMBOLDT | 6.7375 | 63.3162 | 90.74% | 0 | 3 | 64.07% | 0% | 0 | 0.032181 | 65.3912 | 2.8231 | 5.9408 | Medium | Medium | Medium | 561 | 597 | 2.1043
ZACA 1102CB | ZACA 1102 | LOS PADRES | 15.8871 | 63.476 | 75.75% | 0 | 4 | 76.4% | 37.44% | 0 | 0.096438 | 35.3263 | 1.7385 | 5.9226 | High | High | Low | 562 | 510 | 3.4068
BRUNSWICK 110378862 | BRUNSWICK 1103 | SIERRA | 0.84386 | 75.0835 | 56.54% | 0 | 0 | 62.09% | 0% | 0 | 0.021418 | 85.4511 | 3.1475 | 5.7606 | Low | Low | High | 563 | 621 | 1.8302
REDBUD 1102CB | REDBUD 1102 | HUMBOLDT | 15.5011 | 65.2981 | 72.86% | 2 | 2 | 77.01% | 9.757% | 0 | 0.048504 | 47.6367 | 2.492 | 5.7579 | Medium | Medium | Medium | 564 | 580 | 2.3106
VALLEY VIEW 1103CB | VALLEY VIEW 1103 | EAST BAY | 0.06028 | 65 | 0% | 0 | 0 | 0.9308% | 100% | 0 | 0.034198 | 35.3263 | 4.6903 | 5.6663 | Medium | Medium | High | 565 | 682 | 1.2081
COARSEGOLD 2104570682 | COARSEGOLD 2104 | YOSEMITE | 2.0271 | 37.4462 | 79.77% | 2 | 5 | 100% | 0% | 0 | 0.037588 | 65.3912 | 2.2997 | 5.6525 | Medium | Medium | Medium | 566 | 565 | 2.4579
MOLINO 110279306 | MOLINO 1102 | SONOMA | 3.6243 | 55.9348 | 57.2% | 3 | 2 | 44.33% | 48.34% | 1 | 0.037109 | 65.3912 | 2.3082 | 5.6012 | Medium | Medium | Medium | 567 | 567 | 2.4266
MIRABEL 11027401 | MIRABEL 1102 | SONOMA | 1.0644 | 17.3394 | 6.536% | 3 | 1 | 100% | 100% | 0 | 0.071799 | 26.5534 | 2.9335 | 5.5928 | High | High | Medium | 568 | 616 | 1.9065
COTATI 1103CB | COTATI 1103 | SONOMA | 12.0212 | 77.6953 | 26.01% | 1 | 5 | 100% | 0% | 0 | 0.046374 | 47.6367 | 2.5255 | 5.5791 | Medium | Medium | Medium | 569 | 591 | 2.2091
LAYTONVILLE 1102CB | LAYTONVILLE 1102 | HUMBOLDT | 10.2076 | 95.4582 | 95.78% | 0 | 7 | 78.57% | 0% | 0 | 0.051516 | 85.4511 | 1.2662 | 5.5739 | Medium | Medium | Low | 570 | 462 | 4.4021
PARADISE 110299226 | PARADISE 1102 | NORTH VALLEY | 0.94174 | 38.0724 | 24.71% | 0 | 0 | 9.702% | 100% | 0 | 0.037935 | 35.3263 | 4.1275 | 5.5313 | Medium | Medium | High | 571 | 664 | 1.3401
SEACLIFF 0402CB | SEACLIFF 0402 | CENTRAL COAST | 0.96395 | 10 | 24.34% | 2 | 0 | 62.04% | 63.7% | 0 | 0.030212 | 47.6367 | 3.8167 | 5.4929 | Medium | Medium | High | 572 | 653 | 1.4392
PETALUMA C 1108636 | PETALUMA C 1108 | SONOMA | 9.2277 | 74.6783 | 45.5% | 1 | 1 | 100% | 0% | 0 | 0.048927 | 47.6367 | 2.3419 | 5.4583 | Medium | Medium | Medium | 573 | 574 | 2.3307
HALF MOON BAY 11038894 | HALF MOON BAY 1103 | PENINSULA | 11.2938 | 71.3584 | 49.24% | 24 | 2 | 100% | 0% | 0 | 0.052113 | 47.6367 | 2.1795 | 5.4107 | Medium | Medium | Low | 574 | 562 | 2.4825
NORTH DUBLIN 210311101 | NORTH DUBLIN 2103 | MISSION | 3.6926 | 66.2488 | 89.68% | 0 | 0 | 100% | 0% | 0 | 0.05582 | 26.5534 | 3.6138 | 5.3564 | Medium | Medium | High | 575 | 650 | 1.4822
FORESTHILL 1102CB | FORESTHILL 1102 | SIERRA | 1.6478 | 87.6992 | 97.59% | 0 | 0 | 100% | 100% | 0 | 0.19983 | 11.2183 | 2.3825 | 5.3411 | High | High | Medium | 576 | 589 | 2.2418
BRUNSWICK 111063100 | BRUNSWICK 1110 | SIERRA | 4.1271 | 39.6111 | 66.99% | 1 | 2 | 100% | 0% | 0 | 0.041392 | 47.6367 | 2.706 | 5.3357 | Medium | Medium | Medium | 577 | 607 | 1.9718
SAN LUIS OBISPO 110342344 | SAN LUIS OBISPO 1103 | LOS PADRES | 7.6647 | 51.698 | 64.08% | 0 | 1 | 70.58% | 0% | 0 | 0.031898 | 65.3912 | 2.5342 | 5.286 | Medium | Medium | Medium | 578 | 599 | 2.0859
SHADY GLEN 1101CB | SHADY GLEN 1101 | SIERRA | 4.4237 | 59.4195 | 32.95% | 0 | 5 | 80.65% | 0% | 0 | 0.027502 | 85.4511 | 2.2374 | 5.2579 | Medium | Medium | Medium | 579 | 573 | 2.3501
VACA DIXON 110540092 | VACA DIXON 1105 | SACRAMENTO | 23.831 | 65.7788 | 89.52% | 2 | 6 | 55.42% | 0% | 0 | 0.036947 | 65.3912 | 2.1635 | 5.227 | Medium | Medium | Low | 580 | 569 | 2.416
CRESCENT MILLS 2101CB | CRESCENT MILLS 2101 | NORTH VALLEY | 4.0564 | 89.8056 | 75.4% | 0 | 1 | 71.09% | 0% | 0 | 0.030639 | 65.3912 | 2.6018 | 5.2128 | Medium | Medium | Medium | 581 | 604 | 2.0035
SILVERADO 2104726 | SILVERADO 2104 | NORTH BAY | 29.6312 | 77.5719 | 85.35% | 3 | 1 | 83.81% | 20.91% | 0 | 0.072604 | 26.5534 | 2.6935 | 5.1927 | High | High | Medium | 582 | 614 | 1.9279
HIGHLANDS 1102628 | HIGHLANDS 1102 | HUMBOLDT | 14.1896 | 81.6211 | 32.89% | 0 | 6 | 100% | 58.23% | 1 | 0.095308 | 19.9979 | 2.6661 | 5.0814 | High | High | Medium | 583 | 617 | 1.906
LAYTONVILLE 1102572 | LAYTONVILLE 1102 | HUMBOLDT | 21.4369 | 82.6922 | 96.68% | 7 | 18 | 100% | 0% | 0 | 0.14346 | 26.5534 | 1.3283 | 5.0602 | High | High | Low | 584 | 486 | 3.8094
COTATI 1105634 | COTATI 1105 | SONOMA | 6.9392 | 85.5117 | 61.91% | 2 | 3 | 100% | 0% | 0 | 0.037803 | 65.3912 | 2.0438 | 5.0522 | Medium | Medium | Low | 585 | 563 | 2.472
PENRYN 11032198 | PENRYN 1103 | SIERRA | 19.8234 | 39.0911 | 53.27% | 4 | 16 | 94.86% | 0% | 0 | 0.048469 | 47.6367 | 2.1684 | 5.0067 | Medium | Medium | Low | 586 | 582 | 2.3089
VACA DIXON 110118292 | VACA DIXON 1101 | SACRAMENTO | 0.82637 | 74.5954 | 100% | 0 | 2 | 13.83% | 0% | 0 | 0.019682 | 85.4511 | 2.9566 | 4.9725 | Low | Low | Medium | 587 | 631 | 1.6818
GARCIA 0401666 | GARCIA 0401 | HUMBOLDT | 2.4311 | 97.9965 | 100% | 2 | 2 | 100% | 0% | 0 | 0.054265 | 65.3912 | 1.3953 | 4.9513 | Medium | Medium | Low | 588 | 504 | 3.5484
CORNING 110164090 | CORNING 1101 | NORTH VALLEY | 13.6992 | 19.4323 | 100% | 1 | 9 | 100% | 0% | 0 | 0.061365 | 35.3263 | 2.2782 | 4.9386 | Medium | Medium | Medium | 589 | 593 | 2.1678
VACAVILLE 111113652 | VACAVILLE 1111 | SACRAMENTO | 4.3673 | 25.6376 | 64.23% | 1 | 3 | 100% | 0% | 0 | 0.033137 | 47.6367 | 3.0974 | 4.8893 | Medium | Medium | High | 590 | 643 | 1.5785
STELLING 11102243 | STELLING 1110 | DE ANZA | 1.8981 | 73.5691 | 46.49% | 9 | 0 | 100% | 0% | 0 | 0.031796 | 47.6367 | 3.2106 | 4.8628 | Medium | Medium | High | 591 | 646 | 1.5146
IGNACIO 11042447 | IGNACIO 1104 | NORTH BAY | 0.96609 | 32.7068 | 67.19% | 4 | 5 | 90.01% | 0% | 0 | 0.034924 | 47.6367 | 2.9164 | 4.852 | Medium | Medium | Medium | 592 | 634 | 1.6637
GIRVAN 11019732 | GIRVAN 1101 | NORTH VALLEY | 21.139 | 36.4737 | 100% | 2 | 6 | 100% | 100% | 0 | 0.1928 | 14.9507 | 1.6805 | 4.844 | High | High | Low | 593 | 542 | 2.8825
GARBERVILLE 110135706 | GARBERVILLE 1101 | HUMBOLDT | 9.7846 | 69.4909 | 86.47% | 18 | 6 | 100% | 0% | 0 | 0.099644 | 65.3912 | 0.74027 | 4.8235 | High | High | Low | 594 | 390 | 6.5159
MORAGA 110518396 | MORAGA 1105 | DIABLO | 0.21093 | 45.5725 | 100% | 0 | 2 | 18.41% | 0% | 0 | 0.016943 | 65.3912 | 4.3309 | 4.7983 | Low | Low | High | 595 | 698 | 1.1079
TIVY VALLEY 1107869946 | TIVY VALLEY 1107 | FRESNO | 29.8533 | 31.5996 | 100% | 0 | 2 | 100% | 0% | 0 | 0.044292 | 65.3912 | 1.6429 | 4.7585 | Medium | Medium | Low | 596 | 541 | 2.8963
OILFIELDS 1103N46 | OILFIELDS 1103 | CENTRAL COAST | 5.8257 | 79.2916 | 67.5% | 0 | 4 | 100% | 0% | 0 | 0.062709 | 35.3263 | 2.1379 | 4.736 | High | High | Low | 597 | 590 | 2.2153
GARCIA 0401CB | GARCIA 0401 | HUMBOLDT | 0.042407 | 98 | 100% | 0 | 0 | 100% | 0% | 0 | 0.050859 | 65.3912 | 1.4156 | 4.7078 | Medium | Medium | Low | 598 | 515 | 3.3257
COARSEGOLD 2104369777 | COARSEGOLD 2104 | YOSEMITE | 18.4298 | 46.1002 | 90.43% | 1 | 34 | 100% | 0% | 0 | 0.066997 | 35.3263 | 1.9853 | 4.6987 | High | High | Low | 599 | 572 | 2.3668
CRESCENT MILLS 21012232 | CRESCENT MILLS 2101 | NORTH VALLEY | 17.0798 | 82.544 | 99.96% | 2 | 0 | 84.55% | 0% | 0 | 0.052465 | 65.3912 | 1.3664 | 4.6879 | Medium | Medium | Low | 600 | 509 | 3.4308
FORT ROSS 1121124 | FORT ROSS 1121 | SONOMA | 18.5728 | 86.0744 | 76.02% | 1 | 2 | 100% | 0% | 0 | 0.077065 | 47.6367 | 1.2649 | 4.6437 | High | High | Low | 601 | 493 | 3.6711
BELL 111056214 | BELL 1110 | SIERRA | 0.30639 | 85 | 100% | 0 | 0 | 4.593% | 0% | 0 | 0.018495 | 85.4511 | 2.9334 | 4.636 | Low | Low | Medium | 602 | 642 | 1.5804
LAURELES 111110141 | LAURELES 1111 | CENTRAL COAST | 2.922 | 83.2816 | 100% | 0 | 0 | 100% | 100% | 0 | 0.22027 | 11.2183 | 1.8674 | 4.6144 | High | High | Low | 603 | 564 | 2.471
HALF MOON BAY 11038089 | HALF MOON BAY 1103 | PENINSULA | 2.9815 | 77.4451 | 41.57% | 4 | 4 | 100% | 0% | 0 | 0.036303 | 65.3912 | 1.9337 | 4.5903 | Medium | Medium | Low | 604 | 571 | 2.3739
HALF MOON BAY 110398440 | HALF MOON BAY 1103 | PENINSULA | 8.1037 | 78.0886 | 41.99% | 8 | 1 | 100% | 0% | 0 | 0.041193 | 47.6367 | 2.3386 | 4.589 | Medium | Medium | Medium | 605 | 608 | 1.9623
HIGHLANDS 11031282 | HIGHLANDS 1103 | HUMBOLDT | 15.0139 | 42.6416 | 99.84% | 3 | 8 | 89.98% | 0% | 0 | 0.050585 | 35.3263 | 2.5601 | 4.5749 | Medium | Medium | Medium | 606 | 623 | 1.787
PARADISE 1104CB | PARADISE 1104 | NORTH VALLEY | 0.54287 | 10 | 13.72% | 1 | 1 | 13.43% | 100% | 0 | 0.030938 | 35.3263 | 4.1742 | 4.5621 | Medium | Medium | High | 607 | 700 | 1.0929
WILLITS 110337506 | WILLITS 1103 | HUMBOLDT | 11.4286 | 90.7952 | 60.25% | 4 | 3 | 100% | 0% | 0 | 0.04503 | 65.3912 | 1.5483 | 4.5592 | Medium | Medium | Low | 608 | 536 | 2.9446
COARSEGOLD 210210207 | COARSEGOLD 2102 | YOSEMITE | 3.5762 | 10 | 99.5% | 3 | 11 | 100% | 100% | 0 | 0.20336 | 11.2183 | 1.996 | 4.5536 | High | High | Low | 609 | 585 | 2.2814
WILLOW CREEK 11037514 | WILLOW CREEK 1103 | HUMBOLDT | 9.2339 | 70.9692 | 70.67% | 10 | 14 | 91.91% | 2.029% | 1 | 0.062494 | 47.6367 | 1.4859 | 4.4235 | High | High | Low | 610 | 533 | 2.977
SHADY GLEN 110248894 | SHADY GLEN 1102 | SIERRA | 8.076 | 49.6205 | 67.94% | 0 | 5 | 80.69% | 16.07% | 0 | 0.038596 | 65.3912 | 1.7515 | 4.4204 | Medium | Medium | Low | 611 | 561 | 2.5239
OLEMA 11011200 | OLEMA 1101 | NORTH BAY | 2.8963 | 61.7343 | 11.72% | 2 | 7 | 100% | 0% | 0 | 0.026697 | 65.3912 | 2.5297 | 4.4162 | Medium | Medium | Medium | 612 | 627 | 1.7458
SILVERADO 2104CB | SILVERADO 2104 | NORTH BAY | 1.8059 | 23.2702 | 84.92% | 2 | 1 | 36.1% | 66.89% | 0 | 0.044573 | 26.5534 | 3.6993 | 4.3783 | Medium | Medium | High | 613 | 686 | 1.1836
OCEANO 1104Q08 | OCEANO 1104 | LOS PADRES | 12.4392 | 24.3462 | 67.44% | 7 | 8 | 100% | 0% | 0 | 0.040257 | 35.3263 | 3.0746 | 4.3725 | Medium | Medium | Medium | 614 | 657 | 1.4221
COTTONWOOD 11031344 | COTTONWOOD 1103 | NORTH VALLEY | 7.7962 | 44.5024 | 98.83% | 0 | 5 | 62.89% | 0% | 0 | 0.035503 | 65.3912 | 1.8686 | 4.338 | Medium | Medium | Low | 615 | 577 | 2.3216
PUTAH CREEK 11033851 | PUTAH CREEK 1103 | SACRAMENTO | 3.6658 | 82.0611 | 100% | 0 | 0 | 70.81% | 0% | 0 | 0.034621 | 65.3912 | 1.8797 | 4.2555 | Medium | Medium | Low | 616 | 587 | 2.2639
BUELLTON 1102Y50 | BUELLTON 1102 | LOS PADRES | 11.1963 | 40.402 | 55.79% | 1 | 7 | 87.11% | 0% | 0 | 0.037194 | 47.6367 | 2.389 | 4.2328 | Medium | Medium | Medium | 617 | 624 | 1.7718
MOUNTAIN QUARRIES 21016953 | MOUNTAIN QUARRIES 2101 | SIERRA | 5.7089 | 53.1337 | 100% | 0 | 0 | 100% | 0% | 0 | 0.037926 | 35.3263 | 3.1367 | 4.2025 | Medium | Medium | High | 618 | 665 | 1.3398
COTTONWOOD 11039072 | COTTONWOOD 1103 | NORTH VALLEY | 28.4061 | 60.3164 | 100% | 4 | 3 | 99.13% | 0% | 0 | 0.06438 | 47.6367 | 1.3689 | 4.1983 | High | High | Low | 619 | 528 | 3.0669
LAKEVILLE 11023341 | LAKEVILLE 1102 | SONOMA | 8.3809 | 81.4101 | 63.14% | 2 | 0 | 66.79% | 0% | 0 | 0.02532 | 65.3912 | 2.4798 | 4.1058 | Medium | Medium | Medium | 620 | 635 | 1.6557
HICKS 2101XR250 | HICKS 2101 | SAN JOSE | 7.0147 | 55.6197 | 44.17% | 2 | 7 | 53.71% | 28.46% | 0 | 0.042978 | 26.5534 | 3.5951 | 4.1027 | Medium | Medium | High | 621 | 692 | 1.1412
ORO FINO 110238698 | ORO FINO 1102 | NORTH VALLEY | 15.5224 | 87.0508 | 99.92% | 2 | 6 | 100% | 0% | 0 | 0.070272 | 65.3912 | 0.89227 | 4.1001 | High | High | Low | 622 | 453 | 4.5952
CAMP EVERS 2106834583 | CAMP EVERS 2106 | CENTRAL COAST | 0.60497 | 39.087 | 36.91% | 0 | 0 | 100% | 69.26% | 0 | 0.069915 | 14.9507 | 3.9087 | 4.0857 | High | High | High | 623 | 714 | 1.0453
COTATI 1103132 | COTATI 1103 | SONOMA | 25.3022 | 74.6812 | 24.81% | 4 | 9 | 100% | 0% | 0 | 0.073801 | 26.5534 | 2.0508 | 4.0188 | High | High | Low | 624 | 609 | 1.9597
APPLE HILL 1104CB | APPLE HILL 1104 | SIERRA | 4.2262 | 51.4608 | 51.9% | 3 | 4 | 100% | 0% | 0 | 0.03278 | 47.6367 | 2.5597 | 3.9971 | Medium | Medium | Medium | 625 | 644 | 1.5616
PAUL SWEET 2102 | PAUL SWEET 2102 | CENTRAL COAST | 0.085046 | 10 | 0% | 3 | 0 | 100% | 100% | 0 | 0.063894 | 19.9979 | 3.0738 | 3.9275 | High | High | Medium | 626 | 669 | 1.2777
EL CERRITO G 1112BR180 | EL CERRITO G 1112 | EAST BAY | 1.3621 | 12.166 | 3.332% | 1 | 0 | 71.61% | 74.96% | 0 | 0.038138 | 19.9979 | 5.1411 | 3.9211 | Medium | Medium | High | 627 | 766 | 0.76268
RINCON 1103CB | RINCON 1103 | SONOMA | 2.6796 | 27.7294 | 25.63% | 1 | 1 | 89.08% | 47% | 0 | 0.034549 | 35.3263 | 3.169 | 3.8678 | Medium | Medium | High | 628 | 679 | 1.2205
LOW GAP 11012094 | LOW GAP 1101 | HUMBOLDT | 15.318 | 83.9747 | 100% | 2 | 4 | 90.42% | 0% | 0 | 0.077716 | 35.3263 | 1.4008 | 3.8459 | High | High | Low | 629 | 550 | 2.7454
SHINGLE SPRINGS 211051800 | SHINGLE SPRINGS 2110 | SIERRA | 9.4169 | 11.4226 | 65.37% | 2 | 2 | 96.5% | 41.26% | 0 | 0.049018 | 26.5534 | 2.9295 | 3.813 | Medium | Medium | Medium | 630 | 666 | 1.3016
TAR FLAT 0401 | TAR FLAT 0401 | YOSEMITE | 0.026649 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 19.9979 | 3.0633 | 3.771 | High | High | Medium | 631 | 676 | 1.2311
BUCKS CREEK 11031131 | BUCKS CREEK 1103 | NORTH VALLEY | 2.7493 | 88.8735 | 99.9% | 0 | 1 | 100% | 56.92% | 0 | 0.12924 | 85.4511 | 0.34069 | 3.7624 | High | High | Low | 632 | 293 | 11.0435
BASALT 11065039 | BASALT 1106 | NORTH BAY | 1.6775 | 85.8937 | 60.16% | 0 | 1 | 30.77% | 0% | 0 | 0.017795 | 65.3912 | 3.2158 | 3.7421 | Low | Low | High | 633 | 688 | 1.1636
ALTO 1125935 | ALTO 1125 | NORTH BAY | 3.0231 | 20.8124 | 24.9% | 7 | 7 | 94.09% | 0% | 0 | 0.038197 | 35.3263 | 2.7615 | 3.7263 | Medium | Medium | Medium | 634 | 663 | 1.3494
UKIAH 1113CB | UKIAH 1113 | HUMBOLDT | 6.3928 | 56.8513 | 87.48% | 1 | 9 | 40.25% | 0% | 0 | 0.040164 | 35.3263 | 2.6035 | 3.694 | Medium | Medium | Medium | 635 | 658 | 1.4188
MORAGA 11058354 | MORAGA 1105 | DIABLO | 0.25208 | 83.2522 | 100% | 0 | 0 | 8.053% | 20.65% | 0 | 0.026277 | 35.3263 | 3.9671 | 3.6826 | Medium | Medium | High | 636 | 732 | 0.92827
COTTONWOOD 11031616 | COTTONWOOD 1103 | NORTH VALLEY | 45.6614 | 47.3529 | 99.79% | 2 | 10 | 92.93% | 0% | 0 | 0.10209 | 26.5534 | 1.3519 | 3.6648 | High | High | Low | 637 | 551 | 2.7109
WISE 1102307494 | WISE 1102 | SIERRA | 32.9312 | 34.3215 | 79.46% | 1 | 9 | 98.67% | 0% | 0 | 0.082577 | 19.9979 | 2.2151 | 3.6579 | High | High | Low | 638 | 636 | 1.6514
MONTE RIO 1113477 | MONTE RIO 1113 | SONOMA | 1.8187 | 34.6297 | 52.03% | 0 | 3 | 100% | 100% | 0 | 0.11271 | 11.2183 | 2.8387 | 3.5893 | High | High | Medium | 639 | 673 | 1.2644
BRIDGEVILLE 110137484 | BRIDGEVILLE 1101 | HUMBOLDT | 7.5279 | 94.876 | 100% | 3 | 6 | 74.55% | 0% | 0 | 0.051968 | 85.4511 | 0.80668 | 3.5822 | Medium | Medium | Low | 640 | 459 | 4.4407
DESCHUTES 11049726 | DESCHUTES 1104 | NORTH VALLEY | 14.9653 | 23.7872 | 88.61% | 1 | 3 | 89% | 0% | 0 | 0.03574 | 35.3263 | 2.837 | 3.5819 | Medium | Medium | Medium | 641 | 674 | 1.2626
TEMPLETON 2113A70 | TEMPLETON 2113 | LOS PADRES | 22.5502 | 49.7318 | 87.96% | 0 | 9 | 33.69% | 0% | 0 | 0.03134 | 47.6367 | 2.3941 | 3.5742 | Medium | Medium | Medium | 642 | 648 | 1.4929
BRIDGEVILLE 110169866 | BRIDGEVILLE 1101 | HUMBOLDT | 6.5416 | 93.8748 | 99.88% | 6 | 2 | 100% | 0% | 0 | 0.071282 | 65.3912 | 0.75814 | 3.5339 | High | High | Low | 643 | 448 | 4.6612
LAYTONVILLE 110268436 | LAYTONVILLE 1102 | HUMBOLDT | 9.1013 | 91.8828 | 93.46% | 1 | 2 | 100% | 32.77% | 1 | 0.091162 | 26.5534 | 1.4538 | 3.5192 | High | High | Low | 644 | 568 | 2.4207
BIG BASIN 1102 | BIG BASIN 1102 | CENTRAL COAST | 0.014511 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 11.2183 | 2.3875 | 3.4878 | High | High | Medium | 645 | 651 | 1.4609
WISE 11022054 | WISE 1102 | SIERRA | 12.9562 | 34.6019 | 54.65% | 2 | 5 | 100% | 0% | 0 | 0.030193 | 47.6367 | 2.4077 | 3.463 | Medium | Medium | Medium | 646 | 654 | 1.4383
FULTON 1107CB | FULTON 1107 | SONOMA | 0.65239 | 10 | 62.57% | 2 | 0 | 4.947% | 100% | 0 | 0.053816 | 26.5534 | 2.4231 | 3.4626 | Medium | Medium | Medium | 647 | 656 | 1.429
SAND CREEK 11037140 | SAND CREEK 1103 | FRESNO | 26.314 | 18.5001 | 91.83% | 0 | 4 | 100% | 0% | 0 | 0.03967 | 35.3263 | 2.47 | 3.4614 | Medium | Medium | Medium | 648 | 661 | 1.4014
RACETRACK 170423195 | RACETRACK 1704 | YOSEMITE | 7.7484 | 59.3101 | 42.51% | 0 | 0 | 100% | 0% | 0 | 0.036794 | 47.6367 | 1.973 | 3.4581 | Medium | Medium | Low | 649 | 626 | 1.7528
CLARKSVILLE 210575884 | CLARKSVILLE 2105 | SIERRA | 10.3522 | 19.5403 | 73.75% | 1 | 8 | 92.27% | 38.69% | 1 | 0.049935 | 19.9979 | 3.4349 | 3.4301 | Medium | Medium | High | 650 | 721 | 0.9986
GANSNER 110199388 | GANSNER 1101 | NORTH VALLEY | 2.0835 | 75.9591 | 98.87% | 1 | 0 | 93.65% | 0% | 0 | 0.041605 | 26.5534 | 3.0558 | 3.3759 | Medium | Medium | Medium | 651 | 699 | 1.1048
CORRAL 110112612 | CORRAL 1101 | STOCKTON | 18.7862 | 47.6011 | 68.25% | 0 | 10 | 93.49% | 0% | 0 | 0.042229 | 35.3263 | 2.2608 | 3.3727 | Medium | Medium | Medium | 652 | 649 | 1.4918
SHEPHERD 2111R1400 | SHEPHERD 2111 | FRESNO | 19.9144 | 43.3803 | 100% | 0 | 4 | 86.57% | 0% | 0 | 0.063987 | 35.3263 | 1.487 | 3.3613 | High | High | Low | 653 | 588 | 2.2604
WEIMER 1101 | WEIMER 1101 | (blank) | 0.15676 | 70 | 100% | 0 | 0 | 100% | 0% | 0 | 0.042368 | 47.6367 | 1.6634 | 3.3572 | Medium | Medium | Low | 654 | 602 | 2.0183
TEMPLETON 21136055 | TEMPLETON 2113 | LOS PADRES | 39.7266 | 74.9616 | 83.37% | 3 | 5 | 100% | 12.3% | 1 | 0.24234 | 26.5534 | 0.51413 | 3.3084 | High | High | Low | 655 | 392 | 6.435
PUEBLO 11042802 | PUEBLO 1104 | NORTH BAY | 9.7765 | 58.2394 | 48.14% | 0 | 5 | 89.72% | 0% | 0 | 0.072026 | 14.9507 | 3.0683 | 3.3041 | High | High | Medium | 656 | 705 | 1.0768
PEORIA 170411232 | PEORIA 1704 | YOSEMITE | 13.0063 | 19.4612 | 87.58% | 0 | 2 | 75.44% | 0% | 0 | 0.029217 | 35.3263 | 3.195 | 3.2976 | Medium | Medium | High | 657 | 715 | 1.0321
CRESCENT MILLS 21012056 | CRESCENT MILLS 2101 | NORTH VALLEY | 2.8566 | 93.184 | 33.06% | 0 | 0 | 44.02% | 0% | 0 | 0.016743 | 85.4511 | 2.3025 | 3.2941 | Low | Low | Medium | 658 | 655 | 1.4307
HAMILTON BRANCH 11012046 | HAMILTON BRANCH 1101 | NORTH VALLEY | 9.1511 | 77.8147 | 51.04% | 2 | 2 | 99.57% | 0% | 0 | 0.036581 | 35.3263 | 2.517 | 3.2527 | Medium | Medium | Medium | 659 | 667 | 1.2923
STAFFORD 1102524 | STAFFORD 1102 | NORTH BAY | 3.4472 | 66.1749 | 51.31% | 1 | 2 | 26.91% | 0% | 0 | 0.024387 | 47.6367 | 2.779 | 3.2285 | Medium | Medium | Medium | 660 | 689 | 1.1617
DUNBAR 11033135 | DUNBAR 1103 | SONOMA | 0.22216 | 10 | 100% | 0 | 0 | 29.43% | 100% | 0 | 0.068741 | 11.2183 | 4.1817 | 3.2247 | High | High | High | 661 | 764 | 0.77116
MOLINO 110241392 | MOLINO 1102 | SONOMA | 3.7264 | 58.0945 | 65.77% | 1 | 0 | 25.48% | 0% | 0 | 0.016595 | 65.3912 | 2.9568 | 3.2086 | Low | Low | Medium | 662 | 704 | 1.0852
OAKHURST 110348842 | OAKHURST 1103 | YOSEMITE | 2.3666 | 32.8421 | 100% | 0 | 9 | 82.85% | 0% | 0 | 0.033725 | 35.3263 | 2.6913 | 3.2064 | Medium | Medium | Medium | 663 | 685 | 1.1914
EAST QUINCY 1101CB | EAST QUINCY 1101 | NORTH VALLEY | 2.2646 | 54.1438 | 97.01% | 0 | 2 | 28.47% | 0% | 0 | 0.022042 | 47.6367 | 3.0485 | 3.2009 | Medium | Medium | Medium | 664 | 711 | 1.05
CORRAL 110112606 | CORRAL 1101 | STOCKTON | 22.4607 | 31.7729 | 96.48% | 1 | 4 | 100% | 0% | 0 | 0.040006 | 35.3263 | 2.252 | 3.1827 | Medium | Medium | Medium | 665 | 659 | 1.4133
PETALUMA C 1108618 | PETALUMA C 1108 | SONOMA | 8.1405 | 67.3719 | 25.14% | 5 | 1 | 74.64% | 0% | 0 | 0.022157 | 47.6367 | 3.0104 | 3.1775 | Medium | Medium | Medium | 666 | 709 | 1.0555
JESSUP 11011993 | JESSUP 1101 | NORTH VALLEY | 2.9672 | 23.0128 | 100% | 0 | 1 | 100% | 0% | 0 | 0.031722 | 47.6367 | 2.0979 | 3.1701 | Medium | Medium | Low | 667 | 647 | 1.5111
FOOTHILL 1101CB | FOOTHILL 1101 | LOS PADRES | 10.7012 | 70.0715 | 52.58% | 0 | 2 | 48.74% | 0% | 0 | 0.039956 | 26.5534 | 2.9872 | 3.1694 | Medium | Medium | Medium | 668 | 708 | 1.061
FLINT 1101750 | FLINT 1101 | SIERRA | 3.8545 | 52.6304 | 83.81% | 0 | 0 | 41.31% | 0% | 0 | 0.018732 | 65.3912 | 2.5792 | 3.1593 | Low | Low | Medium | 669 | 678 | 1.2249
BOLINAS 11011232 | BOLINAS 1101 | NORTH BAY | 2.4469 | 73.1714 | 0% | 0 | 1 | 100% | 0% | 0 | 0.019829 | 47.6367 | 3.3269 | 3.1425 | Low | Low | High | 670 | 729 | 0.94457
FRUITLAND 1142CB | FRUITLAND 1142 | HUMBOLDT | 10.4822 | 87.3271 | 88.71% | 7 | 4 | 68.32% | 0% | 0 | 0.071375 | 47.6367 | 0.91967 | 3.1269 | High | High | Low | 671 | 511 | 3.4
VACAVILLE 1108 | VACAVILLE 1108 | SACRAMENTO | 0.027876 | 65 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041002 | 47.6367 | 1.5966 | 3.1185 | Medium | Medium | Low | 672 | 610 | 1.9532
NAPA 1112 | NAPA 1112 | NORTH BAY | 0.032215 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 35.3263 | 3.0858 | 3.108 | Medium | Medium | High | 673 | 717 | 1.0072
CAMP EVERS 210510996 | CAMP EVERS 2105 | CENTRAL COAST | 0.7626 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 4.4922 | 3.1023 | High | High | High | 674 | 786 | 0.69059
COARSEGOLD 21046288 | COARSEGOLD 2104 | YOSEMITE | 10.4247 | 64.6171 | 98.8% | 1 | 30 | 100% | 0% | 0 | 0.084064 | 19.9979 | 1.84 | 3.0932 | High | High | Low | 675 | 632 | 1.6811
DEL MAR 210975802 | DEL MAR 2109 | SIERRA | 0.35089 | 17.4936 | 85.01% | 0 | 1 | 84.46% | 0% | 0 | 0.026543 | 47.6367 | 2.444 | 3.0902 | Medium | Medium | Medium | 676 | 672 | 1.2644
CORRAL 1101 | CORRAL 1101 | STOCKTON | 0.001152 | 75 | 100% | 0 | 0 | 100% | 0% | 0 | 0.043778 | 65.3912 | 1.0736 | 3.0735 | Medium | Medium | Low | 677 | 543 | 2.8627
PASO ROBLES 1103N54 | PASO ROBLES 1103 | LOS PADRES | 19.5682 | 48.3867 | 60.55% | 1 | 29 | 90.91% | 0% | 0 | 0.065373 | 35.3263 | 1.33 | 3.0715 | High | High | Low | 678 | 581 | 2.3094
BELL 110750172 | BELL 1107 | SIERRA | 17.5892 | 13.0992 | 68.99% | 0 | 6 | 94.29% | 0% | 0 | 0.046234 | 26.5534 | 2.5016 | 3.0712 | Medium | Medium | Medium | 679 | 677 | 1.2277
LAURELES 111184523 | LAURELES 1111 | CENTRAL COAST | 1.2223 | 80.6528 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045426 | 35.3263 | 1.8947 | 3.0405 | Medium | Medium | Low | 680 | 640 | 1.6047
WOODSIDE 11012299 | WOODSIDE 1101 | PENINSULA | 1.6209 | 33.6689 | 6.985% | 2 | 3 | 88.38% | 100% | 0 | 0.073666 | 11.2183 | 3.6727 | 3.0352 | High | High | High | 681 | 749 | 0.82641
CORRAL 110214026 | CORRAL 1102 | STOCKTON | 10.1342 | 44.5079 | 47.19% | 1 | 3 | 100% | 0% | 0 | 0.03277 | 35.3263 | 2.6188 | 3.0316 | Medium | Medium | Medium | 682 | 690 | 1.1576
OAKHURST 1101CB | OAKHURST 1101 | YOSEMITE | 2.8974 | 35.5621 | 74.52% | 0 | 12 | 97.3% | 1.934% | 0 | 0.040153 | 26.5534 | 2.8286 | 3.0158 | Medium | Medium | Medium | 683 | 707 | 1.0662
VACAVILLE 110838316 | VACAVILLE 1108 | SACRAMENTO | 14.7024 | 65.6281 | 99.57% | 1 | 4 | 63.02% | 0% | 0 | 0.052621 | 35.3263 | 1.6146 | 3.0014 | Medium | Medium | Low | 684 | 620 | 1.8589
MENLO 11028896 | MENLO 1102 | PENINSULA | 0.53492 | 85.6249 | 0.9567% | 0 | 0 | 34.58% | 0% | 0 | 0.01116 | 65.3912 | 4.0778 | 2.9759 | Low | Low | High | 685 | 776 | 0.72979
BRUNSWICK 110633050 | BRUNSWICK 1106 | SIERRA | 1.709 | 18.2327 | 78.9% | 2 | 0 | 44.77% | 0% | 0 | 0.015167 | 65.3912 | 2.9867 | 2.9622 | Low | Low | Medium | 686 | 722 | 0.99181
CORRAL 110336680 | CORRAL 1103 | STOCKTON | 9.9701 | 19.0488 | 89.57% | 1 | 2 | 49.8% | 0% | 0 | 0.017976 | 47.6367 | 3.438 | 2.944 | Low | Low | High | 687 | 744 | 0.85633
WOODSIDE 1101 | WOODSIDE 1101 | PENINSULA | 0.091557 | 33.2557 | 52.71% | 3 | 2 | 100% | 100% | 0 | 0.1142 | 11.2183 | 2.2665 | 2.9039 | High | High | Medium | 688 | 668 | 1.2812
FROGTOWN 1702 | FROGTOWN 1702 | STOCKTON | 0.0028747 | 65 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041002 | 26.5534 | 2.6562 | 2.8919 | Medium | Medium | Medium | 689 | 702 | 1.0887
OLETA 1101CB | OLETA 1101 | STOCKTON | 3.1205 | 69.4789 | 19.21% | 0 | 0 | 92.33% | 0% | 0 | 0.02053 | 47.6367 | 2.9528 | 2.8878 | Low | Low | Medium | 690 | 726 | 0.97799
EL CERRITO G 1105R6998 | EL CERRITO G 1105 | EAST BAY | 0.025405 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 4.1798 | 2.8865 | High | High | High | 691 | 786 | 0.69059
LAYTONVILLE 1102500 | LAYTONVILLE 1102 | HUMBOLDT | 20.1821 | 81.3832 | 99.67% | 9 | 6 | 69.04% | 0% | 0 | 0.048589 | 47.6367 | 1.2335 | 2.855 | Medium | Medium | Low | 692 | 578 | 2.3146
LINCOLN 11045391 | LINCOLN 1104 | SIERRA | 0.95086 | 68.8646 | 19.08% | 0 | 0 | 100% | 0% | 0 | 0.022019 | 47.6367 | 2.7141 | 2.8468 | Medium | Medium | Medium | 693 | 712 | 1.0489
SANTA YNEZ 1104Y04 | SANTA YNEZ 1104 | LOS PADRES | 15.3206 | 51.8152 | 75.91% | 0 | 12 | 68.36% | 0% | 0 | 0.033153 | 35.3263 | 2.4224 | 2.837 | Medium | Medium | Medium | 694 | 687 | 1.1712
SPRING GAP 17029280 | SPRING GAP 1702 | YOSEMITE | 6.3606 | 34.7112 | 42.89% | 5 | 5 | 100% | 100% | 0 | 0.14642 | 11.2183 | 1.7184 | 2.8225 | High | High | Low | 695 | 637 | 1.6426
BELLEVUE 2103648 | BELLEVUE 2103 | SONOMA | 2.2962 | 73.8161 | 100% | 0 | 2 | 14.14% | 0% | 0 | 0.019638 | 47.6367 | 2.9986 | 2.8051 | Low | Low | Medium | 696 | 730 | 0.93548
MONTICELLO 1101720 | MONTICELLO 1101 | NORTH BAY | 7.5573 | 64.5271 | 99.74% | 1 | 2 | 90.69% | 0% | 0 | 0.057594 | 19.9979 | 2.4222 | 2.7897 | Medium | Medium | Medium | 697 | 691 | 1.1518
GRASS VALLEY 1101CB | GRASS VALLEY 1101 | SIERRA | 1.7504 | 55.588 | 24.73% | 1 | 1 | 65.41% | 2.088% | 0 | 0.027071 | 35.3263 | 2.9159 | 2.7885 | Medium | Medium | Medium | 698 | 727 | 0.9563
BRUNSWICK 11038918 | BRUNSWICK 1103 | SIERRA | 0.62743 | 83.4132 | 18.44% | 0 | 0 | 29.2% | 0% | 0 | 0.012022 | 85.4511 | 2.7121 | 2.7862 | Low | Low | Medium | 699 | 716 | 1.0273
PUTAH CREEK 110267858 | PUTAH CREEK 1102 | SACRAMENTO | 11.5068 | 51.7319 | 80.2% | 2 | 0 | 99.07% | 0% | 0 | 0.037122 | 47.6367 | 1.5751 | 2.7854 | Medium | Medium | Low | 700 | 625 | 1.7684
LINCOLN 11042070 | LINCOLN 1104 | SIERRA | 21.0429 | 49.8208 | 65.19% | 5 | 11 | 72.52% | 0% | 0 | 0.042249 | 26.5534 | 2.4592 | 2.7588 | Medium | Medium | Medium | 701 | 695 | 1.1219
VALLEY VIEW 1103P160 | VALLEY VIEW 1103 | EAST BAY | 0.28761 | 80 | 0% | 0 | 0 | 7.876% | 100% | 0 | 0.040365 | 14.9507 | 4.5675 | 2.7565 | Medium | Medium | High | 702 | 821 | 0.60349
CORRAL 110136652 | CORRAL 1101 | STOCKTON | 18.0317 | 36.0873 | 87.44% | 1 | 8 | 100% | 0% | 0 | 0.053562 | 35.3263 | 1.4501 | 2.7438 | Medium | Medium | Low | 703 | 619 | 1.8922
ELECTRA 1101L1697 | ELECTRA 1101 | STOCKTON | 5.4545 | 12.0564 | 100% | 1 | 2 | 100% | 0% | 0 | 0.039464 | 26.5534 | 2.6165 | 2.7419 | Medium | Medium | Medium | 704 | 713 | 1.0479
BRUNSWICK 1106 | BRUNSWICK 1106 | SIERRA | 0.037997 | 60 | 100% | 0 | 0 | 100% | 0% | 0 | 0.039678 | 26.5534 | 2.6004 | 2.7397 | Medium | Medium | Medium | 705 | 710 | 1.0536
SAN RAFAEL 11071415 | SAN RAFAEL 1107 | NORTH BAY | 0.70882 | 10 | 28.8% | 0 | 0 | 59.59% | 100% | 0 | 0.059639 | 11.2183 | 4.0649 | 2.7196 | Medium | Medium | High | 706 | 799 | 0.66905
MOLINO 1101891 | MOLINO 1101 | SONOMA | 3.0063 | 38.1554 | 45.65% | 1 | 1 | 95.38% | 41.51% | 0 | 0.054529 | 19.9979 | 2.4796 | 2.7039 | Medium | Medium | Medium | 707 | 701 | 1.0905
SANTA YNEZ 110477098 | SANTA YNEZ 1104 | LOS PADRES | 10.6194 | 59.0619 | 89.18% | 0 | 4 | 81.31% | 0% | 0 | 0.037257 | 26.5534 | 2.7174 | 2.6883 | Medium | Medium | Medium | 708 | 723 | 0.98931
TEMPLETON 21132949 | TEMPLETON 2113 | LOS PADRES | 0.47714 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 35.3263 | 2.6464 | 2.6655 | Medium | Medium | Medium | 709 | 717 | 1.0072
HAMILTON BRANCH 11013049 | HAMILTON BRANCH 1101 | NORTH VALLEY | 0.54973 | 41.4686 | 100% | 0 | 1 | 32.98% | 0% | 0 | 0.018634 | 65.3912 | 2.1667 | 2.6401 | Low | Low | Low | 710 | 680 | 1.2185
BELLEVUE 2103552 | BELLEVUE 2103 | SONOMA | 9.102 | 59.5579 | 60.22% | 2 | 0 | 60.99% | 9.086% | 0 | 0.023335 | 35.3263 | 3.2018 | 2.6393 | Medium | Medium | High | 711 | 750 | 0.82433
GUALALA 11124431 | GUALALA 1112 | HUMBOLDT | 1.4123 | 70.1709 | 0% | 0 | 4 | 100% | 0% | 0 | 0.02067 | 65.3912 | 1.946 | 2.6304 | Low | Low | Low | 712 | 662 | 1.3517
SAUSALITO 110284278 | SAUSALITO 1102 | NORTH BAY | 1.3711 | 32.8864 | 5.777% | 0 | 2 | 90.29% | 0% | 0 | 0.021793 | 35.3263 | 3.3996 | 2.6173 | Low | Low | High | 713 | 765 | 0.76987
PUTAH CREEK 1102CB | PUTAH CREEK 1102 | SACRAMENTO | 4.8366 | 82.2611 | 100% | 0 | 0 | 37.85% | 0% | 0 | 0.025161 | 47.6367 | 2.1795 | 2.6123 | Medium | Medium | Low | 714 | 683 | 1.1986
LAYTONVILLE 110189606 | LAYTONVILLE 1101 | HUMBOLDT | 11.3479 | 67.7426 | 99.65% | 4 | 7 | 95.33% | 0% | 0 | 0.048183 | 35.3263 | 1.5294 | 2.6033 | Medium | Medium | Low | 715 | 629 | 1.7021
GIRVAN 1102 | GIRVAN 1102 | NORTH VALLEY | 0.038598 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 11.2183 | 1.7778 | 2.5971 | High | High | Low | 716 | 651 | 1.4609
LAYTONVILLE 1102682 | LAYTONVILLE 1102 | HUMBOLDT | 14.8214 | 90.6873 | 91.3% | 5 | 3 | 100% | 0% | 0 | 0.051212 | 65.3912 | 0.7707 | 2.5809 | Medium | Medium | Low | 717 | 513 | 3.3488
PASO ROBLES 1103N02 | PASO ROBLES 1103 | LOS PADRES | 0.044146 | 10 | 36.23% | 0 | 0 | 100% | 0% | 0 | 0.017045 | 47.6367 | 3.1571 | 2.5634 | Low | Low | High | 718 | 752 | 0.81194
PEORIA 170413494 | PEORIA 1704 | YOSEMITE | 3.2575 | 18.8459 | 98.09% | 0 | 1 | 43.79% | 0% | 0 | 0.017531 | 47.6367 | 3.0588 | 2.5544 | Low | Low | Medium | 719 | 747 | 0.8351
SILVERADO 210437632 | SILVERADO 2104 | NORTH BAY | 22.9342 | 51.0024 | 44.2% | 16 | 15 | 100% | 100% | 0 | 0.67223 | 1 | 3.7875 | 2.5461 | High | High | High | 720 | 798 | 0.67223
COARSEGOLD 2104CB | COARSEGOLD 2104 | YOSEMITE | 2.4475 | 54.0073 | 41.51% | 0 | 3 | 100% | 0% | 0 | 0.025403 | 47.6367 | 2.1019 | 2.5435 | Medium | Medium | Low | 721 | 681 | 1.2101
MOLINO 1104380 | MOLINO 1104 | SONOMA | 2.046 | 71.2548 | 46.79% | 0 | 0 | 7.207% | 0% | 0 | 0.011223 | 65.3912 | 3.36 | 2.4657 | Low | Low | High | 722 | 773 | 0.73385
CLOVERDALE 110247214 | CLOVERDALE 1102 | SONOMA | 0.027332 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 35.3263 | 2.4417 | 2.4593 | Medium | Medium | Medium | 723 | 717 | 1.0072
HIGHLANDS 110280660 | HIGHLANDS 1102 | HUMBOLDT | 5.365 | 78.0742 | 39.2% | 1 | 2 | 71.03% | 0% | 0 | 0.021888 | 35.3263 | 3.1794 | 2.4584 | Medium | Medium | High | 724 | 763 | 0.77324
ELK CREEK 11012008 | ELK CREEK 1101 | NORTH VALLEY | 2.1575 | 78.9163 | 100% | 0 | 1 | 11.89% | 0% | 0 | 0.019472 | 65.3912 | 1.9305 | 2.4581 | Low | Low | Low | 725 | 670 | 1.2733
MARIPOSA 210190130 | MARIPOSA 2101 | YOSEMITE | 0.091387 | 70 | 0% | 0 | 0 | 100% | 0% | 0 | 0.019016 | 47.6367 | 2.6983 | 2.4443 | Low | Low | Medium | 726 | 734 | 0.90585
LAKEWOOD 2110W577R | LAKEWOOD 2110 | DIABLO | 0.42837 | 10 | 37.2% | 0 | 0 | 46.99% | 100% | 0 | 0.056527 | 11.2183 | 3.8435 | 2.4373 | Medium | Medium | High | 727 | 810 | 0.63414
SHINGLE SPRINGS 210935598 | SHINGLE SPRINGS 2109 | SIERRA | 10.9289 | 31.2867 | 70.52% | 1 | 5 | 100% | 42.6% | 0 | 0.072647 | 14.9507 | 2.2274 | 2.4192 | High | High | Low | 728 | 703 | 1.0861
JESSUP 11023105 | JESSUP 1102 | NORTH VALLEY | 5.7601 | 31.7951 | 100% | 0 | 2 | 92.48% | 0% | 0 | 0.031899 | 35.3263 | 2.1459 | 2.4181 | Medium | Medium | Low | 729 | 694 | 1.1269
ATASCADERO 1101A02 | ATASCADERO 1101 | LOS PADRES | 11.1355 | 10.7743 | 66.74% | 2 | 2 | 100% | 7.928% | 0 | 0.044541 | 14.9507 | 3.626 | 2.4147 | Medium | Medium | High | 730 | 800 | 0.66592
MILPITAS 1108XR122 | MILPITAS 1108 | SAN JOSE | 0.28331 | 75 | 0% | 0 | 0 | 3.797% | 0% | 0 | 0.0075908 | 85.4511 | 3.7218 | 2.4142 | Low | Low | High | 731 | 806 | 0.64865
STAFFORD 11021202 | STAFFORD 1102 | NORTH BAY | 7.2996 | 85.3549 | 21.22% | 0 | 3 | 92.36% | 0% | 0 | 0.031995 | 35.3263 | 2.1233 | 2.3999 | Medium | Medium | Low | 732 | 693 | 1.1303
SONOMA 110310257 | SONOMA 1103 | SONOMA | 0.24108 | 10 | 100% | 0 | 0 | 12.38% | 100% | 0 | 0.058573 | 11.2183 | 3.6175 | 2.3771 | Medium | Medium | High | 733 | 803 | 0.65709
PEABODY 2113CB | PEABODY 2113 | SACRAMENTO | 1.6686 | 58.5758 | 80.04% | 0 | 1 | 27.33% | 0% | 0 | 0.01682 | 47.6367 | 2.9585 | 2.3705 | Low | Low | Medium | 734 | 754 | 0.80125
ELK CREEK 1101CB | ELK CREEK 1101 | NORTH VALLEY | 0.084247 | 80 | 68.8% | 0 | 0 | 100% | 0% | 0 | 0.035328 | 47.6367 | 1.406 | 2.3661 | Medium | Medium | Low | 735 | 630 | 1.6829
PETALUMA C 1108600 | PETALUMA C 1108 | SONOMA | 4.0703 | 32.8182 | 38.32% | 2 | 6 | 47.11% | 0% | 0 | 0.020667 | 47.6367 | 2.3993 | 2.3621 | Low | Low | Medium | 736 | 725 | 0.98451
RESERVATION ROAD 11013026 | RESERVATION ROAD 1101 | CENTRAL COAST | 21.8928 | 54.2364 | 36.93% | 7 | 8 | 96.87% | 0% | 0 | 0.070296 | 19.9979 | 1.6766 | 2.3569 | High | High | Low | 737 | 660 | 1.4058
COTATI 1102282 | COTATI 1102 | SONOMA | 4.4441 | 39.13 | 50.31% | 2 | 2 | 88.16% | 0% | 0 | 0.025185 | 35.3263 | 2.6402 | 2.349 | Medium | Medium | Medium | 738 | 738 | 0.8897
PARADISE 11022024 | PARADISE 1102 | NORTH VALLEY | 0.64392 | 10 | 28.85% | 0 | 1 | 39.71% | 100% | 0 | 0.044388 | 11.2183 | 4.7148 | 2.3477 | Medium | Medium | High | 739 | 859 | 0.49795
LAKEWOOD 2224W544R | LAKEWOOD 2224 | DIABLO | 0.041988 | 10 | 100% | 0 | 0 | 0.7884% | 100% | 0 | 0.052488 | 11.2183 | 3.9642 | 2.3342 | Medium | Medium | High | 740 | 826 | 0.58883
ROB ROY 21045082 | ROB ROY 2104 | CENTRAL COAST | 24.4071 | 49.5744 | 97.38% | 64 | 6 | 98.22% | 97.15% | 0 | 0.73013 | 1 | 3.1854 | 2.3258 | High | High | High | 741 | 775 | 0.73013
CLOVERDALE 110254760 | CLOVERDALE 1102 | SONOMA | 0.13003 | 10 | 100% | 0 | 0 | 93.87% | 0% | 0 | 0.026858 | 35.3263 | 2.4446 | 2.3195 | Medium | Medium | Medium | 742 | 728 | 0.94881
NARROWS 21052214 | NARROWS 2105 | SIERRA | 0.0028409 | 70 | 0% | 0 | 0 | 100% | 0% | 0 | 0.019016 | 47.6367 | 2.5602 | 2.3192 | Low | Low | Medium | 743 | 734 | 0.90585
RED BLUFF 110451238 | RED BLUFF 1104 | NORTH VALLEY | 39.381 | 43.7242 | 96.09% | 3 | 21 | 100% | 0% | 0 | 0.089857 | 19.9979 | 1.2852 | 2.3095 | High | High | Low | 744 | 622 | 1.7969
FULTON 110410281 | FULTON 1104 | SONOMA | 0.51664 | 22.43 | 74.95% | 0 | 1 | 49.63% | 0% | 0 | 0.015765 | 47.6367 | 3.068 | 2.3041 | Low | Low | Medium | 745 | 771 | 0.75099
CLEAR LAKE 110192870 | CLEAR LAKE 1101 | HUMBOLDT | 1.0943 | 58.4315 | 90.41% | 0 | 0 | 6.07% | 0% | 0 | 0.016559 | 47.6367 | 2.9112 | 2.2964 | Low | Low | Medium | 746 | 760 | 0.78881
GABILAN 11013090 | GABILAN 1101 | CENTRAL COAST | 1.8466 | 75 | 100% | 0 | 0 | 5.274% | 0% | 0 | 0.02262 | 35.3263 | 2.8398 | 2.2693 | Medium | Medium | Medium | 747 | 755 | 0.7991
PASO ROBLES 110359763 | PASO ROBLES 1103 | LOS PADRES | 2.8193 | 65.7222 | 66.01% | 0 | 0 | 100% | 0% | 0 | 0.031437 | 35.3263 | 2.0367 | 2.2619 | Medium | Medium | Low | 748 | 697 | 1.1106
OLETA 11011217 | OLETA 1101 | STOCKTON | 14.427 | 60.7702 | 100% | 1 | 3 | 83.71% | 43.16% | 1 | 0.071429 | 14.9507 | 2.1108 | 2.2542 | High | High | Low | 749 | 706 | 1.0679
VINEYARD 21086952 | VINEYARD 2108 | MISSION | 0.0028424 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 3.2583 | 2.2502 | High | High | High | 750 | 786 | 0.69059
HORSESHOE 110450142 | HORSESHOE 1104 | SIERRA | 0.99943 | 10 | 98.77% | 0 | 1 | 24.44% | 0% | 0 | 0.015652 | 35.3263 | 3.9959 | 2.2095 | Low | Low | High | 751 | 837 | 0.55294
BIG BASIN 11015479 | BIG BASIN 1101 | CENTRAL COAST | 0.17042 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 11.2183 | 3.0984 | 2.1397 | High | High | High | 752 | 786 | 0.69059
WILLITS 1103538 | WILLITS 1103 | HUMBOLDT | 6.4253 | 81.3489 | 100% | 3 | 1 | 100% | 27.62% | 0 | 0.083475 | 14.9507 | 1.7136 | 2.1386 | High | High | Low | 753 | 675 | 1.248
MOLINO 1101152 | MOLINO 1101 | SONOMA | 2.0022 | 35.0368 | 46.62% | 3 | 1 | 17.51% | 2.1% | 0 | 0.012176 | 65.3912 | 2.6304 | 2.0944 | Low | Low | Medium | 754 | 757 | 0.79623
PEORIA 170575274 | PEORIA 1705 | YOSEMITE | 0.58699 | 10 | 100% | 0 | 0 | 18.06% | 0% | 0 | 0.012746 | 47.6367 | 3.4448 | 2.0915 | Low | Low | High | 755 | 818 | 0.60716
MONTICELLO 110165454 | MONTICELLO 1101 | NORTH BAY | 0.17975 | 75.7164 | 100% | 0 | 0 | 9.577% | 0% | 0 | 0.018251 | 47.6367 | 2.4012 | 2.0876 | Low | Low | Medium | 756 | 741 | 0.8694
BRIDGEVILLE 1101CB | BRIDGEVILLE 1101 | HUMBOLDT | 8.4707 | 94.1626 | 99.27% | 7 | 0 | 100% | 9.505% | 1 | 0.10184 | 65.3912 | 0.31236 | 2.0801 | High | High | Low | 757 | 389 | 6.6593
DESCHUTES 11019722 | DESCHUTES 1101 | NORTH VALLEY | 2.8886 | 47.2823 | 92.43% | 0 | 2 | 60.75% | 0% | 0 | 0.024427 | 35.3263 | 2.3843 | 2.0574 | Medium | Medium | Medium | 758 | 742 | 0.8629
SANTA YNEZ 1101Y14 | SANTA YNEZ 1101 | LOS PADRES | 4.5467 | 84.753 | 58.25% | 0 | 0 | 27.67% | 0% | 0 | 0.016519 | 47.6367 | 2.6036 | 2.0488 | Low | Low | Medium | 759 | 761 | 0.78692
PUEBLO 2103678 | PUEBLO 2103 | NORTH BAY | 25.5805 | 63.7412 | 53.4% | 28 | 21 | 98.22% | 87.3% | 1 | 0.69166 | 1 | 2.9613 | 2.0482 | High | High | Medium | 760 | 784 | 0.69166
PANORAMA 11019092 | PANORAMA 1101 | NORTH VALLEY | 9.7913 | 10 | 99.08% | 0 | 8 | 48.48% | 0% | 0 | 0.033887 | 35.3263 | 1.6659 | 1.9943 | Medium | Medium | Low | 761 | 684 | 1.1971
JAMESON 11057652 | JAMESON 1105 | SACRAMENTO | 15.7797 | 54.8992 | 80.61% | 0 | 3 | 36.24% | 0% | 0 | 0.021376 | 35.3263 | 2.6329 | 1.9882 | Low | Low | Medium | 762 | 770 | 0.75514
VASCO 110211338 | VASCO 1102 | MISSION | 3.3669 | 79.9716 | 100% | 0 | 1 | 17.52% | 0% | 0 | 0.020726 | 35.3263 | 2.7006 | 1.9773 | Low | Low | Medium | 763 | 774 | 0.73217
JARVIS 1101MR210 | JARVIS 1101 | MISSION | 0.45193 | 56.1032 | 64.09% | 0 | 0 | 5.821% | 0% | 0 | 0.011506 | 47.6367 | 3.5376 | 1.939 | Low | Low | High | 764 | 838 | 0.54812
OAKHURST 1102CB | OAKHURST 1102 | YOSEMITE | 2.1514 | 10 | 95.52% | 0 | 10 | 44.96% | 59.79% | 0 | 0.050548 | 14.9507 | 2.5632 | 1.9371 | Medium | Medium | Medium | 765 | 769 | 0.75573
CAMP EVERS 210612760 | CAMP EVERS 2106 | CENTRAL COAST | 26.714 | 47.9231 | 63.13% | 29 | 6 | 100% | 100% | 0 | 0.75098 | 1 | 2.5548 | 1.9186 | High | High | Medium | 766 | 772 | 0.75098
SONOMA 1104414 | SONOMA 1104 | SONOMA | 0.58433 | 88.0945 | 100% | 0 | 0 | 3.279% | 0% | 0 | 0.018641 | 35.3263 | 2.89 | 1.9031 | Low | Low | Medium | 767 | 802 | 0.65851
PINECREST 0401CB | PINECREST 0401 | YOSEMITE | 0.021247 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 14.9507 | 0.97713 | 1.9024 | High | High | Low | 768 | 612 | 1.9469
PINECREST 0401 | PINECREST 0401 | YOSEMITE | 0.0016115 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 14.9507 | 0.97537 | 1.899 | High | High | Low | 769 | 612 | 1.9469
STAFFORD 1102361952 | STAFFORD 1102 | NORTH BAY | 1.3655 | 84.7322 | 98.54% | 0 | 1 | 100% | 0% | 0 | 0.04705 | 14.9507 | 2.6948 | 1.8956 | Medium | Medium | Medium | 770 | 781 | 0.70344
SALMON CREEK 1101196 | SALMON CREEK 1101 | SONOMA | 5.0547 | 72.9126 | 4.053% | 3 | 0 | 69.63% | 0% | 0 | 0.020086 | 35.3263 | 2.652 | 1.8817 | Low | Low | Medium | 771 | 780 | 0.70955
HIGGINS 11032194 | HIGGINS 1103 | SIERRA | 1.6953 | 10 | 78.66% | 3 | 1 | 63.02% | 0% | 0 | 0.017732 | 35.3263 | 3.0035 | 1.8815 | Low | Low | Medium | 772 | 813 | 0.62642
PETALUMA C 1109373772 | PETALUMA C 1109 | SONOMA | 0.017822 | 70 | 100% | 0 | 0 | 100% | 0% | 0 | 0.042368 | 14.9507 | 2.9557 | 1.8723 | Medium | Medium | Medium | 773 | 811 | 0.63344
GARBERVILLE 11022124 | GARBERVILLE 1102 | HUMBOLDT | 3.1243 | 97.624 | 0% | 0 | 1 | 100% | 0% | 0 | 0.023355 | 47.6367 | 1.6787 | 1.8676 | Medium | Medium | Low | 774 | 696 | 1.1125
VACA DIXON 11059792 | VACA DIXON 1105 | SACRAMENTO | 2.2981 | 58.3899 | 100% | 0 | 0 | 7.932% | 0% | 0 | 0.015982 | 47.6367 | 2.4313 | 1.8511 | Low | Low | Medium | 775 | 767 | 0.76135
PENRYN 110550548 | PENRYN 1105 | SIERRA | 4.6613 | 28.5134 | 63.43% | 0 | 1 | 38.43% | 0% | 0 | 0.013391 | 65.3912 | 2.1096 | 1.8472 | Low | Low | Low | 776 | 739 | 0.87563
STAFFORD 11021943 | STAFFORD 1102 | NORTH BAY | 1.2184 | 10 | 29.26% | 2 | 0 | 100% | 0% | 0 | 0.016531 | 35.3263 | 3.1358 | 1.8312 | Low | Low | High | 777 | 830 | 0.58398
GREEN VALLEY 210111054 | GREEN VALLEY 2101 | CENTRAL COAST | 24.5092 | 42.4361 | 63.08% | 38 | 3 | 95.34% | 97.52% | 1 | 0.59075 | 1 | 3.087 | 1.8236 | High | High | High | 778 | 824 | 0.59075
OLETA 110163500 | OLETA 1101 | STOCKTON | 4.0006 | 22.1026 | 38.92% | 0 | 1 | 53.39% | 0% | 0 | 0.012178 | 65.3912 | 2.271 | 1.8085 | Low | Low | Medium | 779 | 756 | 0.79634
STAFFORD 1102784704 | STAFFORD 1102 | NORTH BAY | 0.02728 | 80 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045233 | 14.9507 | 2.6732 | 1.8078 | Medium | Medium | Medium | 780 | 796 | 0.67626
PACIFICA 11026783 | PACIFICA 1102 | PENINSULA | 1.5821 | 10 | 0% | 0 | 2 | 24.72% | 24.2% | 0 | 0.010579 | 47.6367 | 3.5634 | 1.7958 | Low | Low | High | 781 | 856 | 0.50395
COTATI 1102681 | COTATI 1102 | SONOMA | 3.8076 | 32.2436 | 43.14% | 1 | 3 | 100% | 0% | 0 | 0.025685 | 26.5534 | 2.6252 | 1.7904 | Medium | Medium | Medium | 782 | 793 | 0.68203
RINCON 1102644 | RINCON 1102 | SONOMA | 0.010111 | 60 | 100% | 0 | 1 | 0.1009% | 0% | 0 | 0.015268 | 35.3263 | 3.2635 | 1.7602 | Low | Low | High | 783 | 843 | 0.53935
SANTA YNEZ 1101CB | SANTA YNEZ 1101 | LOS PADRES | 0.10675 | 60 | 100% | 0 | 1 | 0.6877% | 0% | 0 | 0.015356 | 35.3263 | 3.2382 | 1.7567 | Low | Low | High | 784 | 841 | 0.54248
PASO ROBLES 1104R56 | PASO ROBLES 1104 | LOS PADRES | 11.0427 | 56.2868 | 57.45% | 0 | 4 | 89.88% | 0% | 0 | 0.035115 | 26.5534 | 1.8717 | 1.7452 | Medium | Medium | Low | 785 | 731 | 0.93242
FRUITLAND 11426064 | FRUITLAND 1142 | HUMBOLDT | 6.4216 | 80.9642 | 100% | 2 | 4 | 77.51% | 0% | 0 | 0.076552 | 47.6367 | 0.47828 | 1.7441 | High | High | Low | 786 | 495 | 3.6467
PENRYN 11051342 | PENRYN 1105 | SIERRA | 20.5672 | 12.393 | 56.11% | 3 | 12 | 53.03% | 0% | 0 | 0.025263 | 35.3263 | 1.9483 | 1.7388 | Medium | Medium | Low | 787 | 736 | 0.89244
CLARKSVILLE 21096502 | CLARKSVILLE 2109 | SIERRA | 2.6781 | 10 | 70.1% | 1 | 1 | 48.48% | 45.39% | 0 | 0.03731 | 14.9507 | 3.0964 | 1.7272 | Medium | Medium | High | 788 | 836 | 0.55781
WOODACRE 110191900 | WOODACRE 1101 | NORTH BAY | 7.6804 | 74.1444 | 47.27% | 4 | 8 | 55.53% | 8.222% | 1 | 0.029825 | 26.5534 | 2.176 | 1.7233 | Medium | Medium | Low | 789 | 759 | 0.79194
WISE 1102697216 | WISE 1102 | SIERRA | 13.1816 | 10.264 | 71.09% | 2 | 0 | 100% | 0% | 0 | 0.026461 | 26.5534 | 2.4483 | 1.7203 | Medium | Medium | Medium | 790 | 783 | 0.70264
PETALUMA C 1109664732 | PETALUMA C 1109 | SONOMA | 0.8938 | 76.1937 | 84.67% | 0 | 0 | 100% | 0% | 0 | 0.039085 | 14.9507 | 2.9436 | 1.7201 | Medium | Medium | Medium | 791 | 829 | 0.58434
TEMPLETON 2113A60 | TEMPLETON 2113 | LOS PADRES | 7.4093 | 57.7033 | 62.45% | 1 | 2 | 82.52% | 0.05121% | 0 | 0.025802 | 26.5534 | 2.47 | 1.6923 | Medium | Medium | Medium | 792 | 791 | 0.68512
HIGHLANDS 1102556 | HIGHLANDS 1102 | HUMBOLDT | 0.14444 | 10 | 100% | 0 | 0 | 1.909% | 0% | 0 | 0.010862 | 47.6367 | 3.2484 | 1.6809 | Low | Low | High | 793 | 852 | 0.51744
JESSUP 110296554 | JESSUP 1102 | NORTH VALLEY | 6.2214 | 43.1199 | 99.72% | 1 | 1 | 41.3% | 0% | 0 | 0.030545 | 26.5534 | 2.0694 | 1.6784 | Medium | Medium | Low | 794 | 753 | 0.81106
RESEARCH 210263274 | RESEARCH 2102 | DIABLO | 0.57886 | 29.7225 | 25.19% | 0 | 1 | 5.113% | 100% | 0 | 0.035184 | 14.9507 | 3.1898 | 1.6779 | Medium | Medium | High | 795 | 849 | 0.52603
BUELLTON 1102CB | BUELLTON 1102 | LOS PADRES | 4.428 | 55.4455 | 60.97% | 0 | 2 | 34.48% | 0% | 0 | 0.02009 | 35.3263 | 2.346 | 1.6649 | Low | Low | Medium | 796 | 779 | 0.7097
HARTLEY 110158095 | HARTLEY 1101 | HUMBOLDT | 0.15659 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 19.9979 | 2.9173 | 1.6633 | Medium | Medium | Medium | 797 | 832 | 0.57017
SONOMA 11045661 | SONOMA 1104 | SONOMA | 2.0903 | 69.2654 | 50.64% | 0 | 1 | 41.25% | 0% | 0 | 0.016332 | 26.5534 | 3.8269 | 1.6596 | Low | Low | High | 798 | 879 | 0.43366
STAFFORD 11011082 | STAFFORD 1101 | NORTH BAY | 2.5227 | 43.9762 | 98.79% | 0 | 0 | 81.83% | 0% | 0 | 0.029652 | 19.9979 | 2.7906 | 1.6547 | Medium | Medium | Medium | 799 | 823 | 0.59297
HIGGINS 110432747 | HIGGINS 1104 | SIERRA | 1.0824 | 10 | 100% | 1 | 0 | 61.76% | 0% | 0 | 0.019868 | 26.5534 | 3.124 | 1.6482 | Low | Low | High | 800 | 848 | 0.52758
SAN JUSTO 11014339 | SAN JUSTO 1101 | CENTRAL COAST | 8.8141 | 41.5112 | 42.23% | 1 | 1 | 80.23% | 0% | 0 | 0.021456 | 35.3263 | 2.1555 | 1.6338 | Low | Low | Low | 801 | 768 | 0.75797
MARTELL 11016074 | MARTELL 1101 | STOCKTON | 3.6867 | 10 | 89.99% | 1 | 1 | 100% | 0% | 0 | 0.030968 | 19.9979 | 2.6262 | 1.6264 | Medium | Medium | Medium | 802 | 816 | 0.6193
CURTIS 1702 | CURTIS 1702 | YOSEMITE | 0.020195 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 14.9507 | 3.8121 | 1.625 | Medium | Medium | High | 803 | 883 | 0.42627
FULTON 11024522 | FULTON 1102 | SONOMA | 7.7633 | 52.5177 | 82.8% | 0 | 6 | 63.13% | 6.863% | 0 | 0.037536 | 14.9507 | 2.8909 | 1.6223 | Medium | Medium | Medium | 804 | 835 | 0.56119
DEL MONTE 21049500 | DEL MONTE 2104 | CENTRAL COAST | 6.5395 | 26.3217 | 40.33% | 0 | 7 | 96.32% | 0% | 0 | 0.03234 | 19.9979 | 2.4996 | 1.6166 | Medium | Medium | Medium | 805 | 808 | 0.64673
ATASCADERO 1103A18 | ATASCADERO 1103 | LOS PADRES | 8.0258 | 28.4878 | 70.03% | 3 | 2 | 44.28% | 0% | 0 | 0.023538 | 35.3263 | 1.9037 | 1.583 | Medium | Medium | Low | 806 | 748 | 0.8315
BIG MEADOWS 2101439 | BIG MEADOWS 2101 | NORTH VALLEY | 0.034644 | 85 | 100% | 0 | 0 | 3.714% | 0% | 0 | 0.018336 | 26.5534 | 3.2474 | 1.5811 | Low | Low | High | 807 | 862 | 0.48688
BEN LOMOND 0401CB | BEN LOMOND 0401 | CENTRAL COAST | 7.8222 | 35.8204 | 30.8% | 32 | 5 | 100% | 100% | 0 | 0.3629 | 1 | 4.3533 | 1.5799 | High | High | High | 808 | 916 | 0.3629
CORRAL 110313474 | CORRAL 1103 | STOCKTON | 3.1745 | 31.5086 | 69.33% | 0 | 0 | 44.02% | 0% | 0 | 0.019295 | 19.9979 | 3.99 | 1.5396 | Low | Low | High | 809 | 900 | 0.38586
COARSEGOLD 210410335 | COARSEGOLD 2104 | YOSEMITE | 5.8238 | 24.9128 | 98.65% | 0 | 10 | 100% | 0% | 0 | 0.043347 | 14.9507 | 2.3565 | 1.5272 | Medium | Medium | Medium | 810 | 807 | 0.64806
PENRYN 110551676 | PENRYN 1105 | SIERRA | 8.707 | 10 | 49.11% | 4 | 2 | 74.33% | 0% | 0 | 0.018392 | 35.3263 | 2.3475 | 1.5252 | Low | Low | Medium | 811 | 805 | 0.64971
PUTAH CREEK 110546162 | PUTAH CREEK 1105 | SACRAMENTO | 0.70535 | 84.6256 | 100% | 0 | 0 | 10.52% | 0% | 0 | 0.019556 | 35.3263 | 2.1866 | 1.5106 | Low | Low | Low | 812 | 785 | 0.69085
NORTH DUBLIN 21039473 | NORTH DUBLIN 2103 | MISSION | 2.5582 | 55.4552 | 10.6% | 0 | 1 | 86.9% | 2.14% | 0 | 0.019896 | 19.9979 | 3.7737 | 1.5015 | Low | Low | High | 813 | 893 | 0.39788
SALMON CREEK 1101 | SALMON CREEK 1101 | SONOMA | 0.026066 | 45.8588 | 0% | 0 | 0 | 100% | 51.23% | 0 | 0.036485 | 14.9507 | 2.7335 | 1.4911 | Medium | Medium | Medium | 814 | 839 | 0.54548
HALSEY 1101 | HALSEY 1101 | SIERRA | 0.058617 | 10 | 52.88% | 0 | 0 | 100% | 0% | 0 | 0.019506 | 35.3263 | 2.1628 | 1.4903 | Low | Low | Low | 815 | 790 | 0.68906
CLEAR LAKE 1102904 | CLEAR LAKE 1102 | HUMBOLDT | 3.3866 | 10 | 44.47% | 0 | 0 | 94.14% | 0% | 0 | 0.01961 | 26.5534 | 2.8334 | 1.4754 | Low | Low | Medium | 816 | 851 | 0.52071
BIG BEND 11011704 | BIG BEND 1101 | NORTH VALLEY | 2.999 | 64.818 | 100% | 0 | 0 | 100% | 0% | 0 | 0.040953 | 19.9979 | 1.7926 | 1.4681 | Medium | Medium | Low | 817 | 751 | 0.81898
SAN RAFAEL 11071166 | SAN RAFAEL 1107 | NORTH BAY | 8.1619 | 27.5709 | 35.32% | 8 | 36 | 90.61% | 87.37% | 0 | 0.30659 | 1 | 4.7682 | 1.4619 | High | High | High | 818 | 958 | 0.30659
SONOMA 1107294 | SONOMA 1107 | SONOMA | 0.1154 | 80 | 100% | 0 | 0 | 1.248% | 0% | 0 | 0.017305 | 35.3263 | 2.3851 | 1.458 | Low | Low | Medium | 819 | 817 | 0.61132
OREGON TRAIL 1102CB | OREGON TRAIL 1102 | NORTH VALLEY | 9.1345 | 24.6852 | 60.79% | 2 | 5 | 97.5% | 0% | 0 | 0.028979 | 19.9979 | 2.4938 | 1.4452 | Medium | Medium | Medium | 820 | 831 | 0.57952
OLEMA 11011686 | OLEMA 1101 | NORTH BAY | 0.41347 | 93.229 | 0% | 4 | 1 | 8.166% | 0% | 0 | 0.0096532 | 65.3912 | 2.2884 | 1.4445 | Low | Low | Medium | 821 | 812 | 0.63124
SHINGLE SPRINGS 21107742 | SHINGLE SPRINGS 2110 | SIERRA | 45.6192 | 28.4995 | 92.18% | 17 | 14 | 99.89% | 99.12% | 1 | 0.53387 | 1 | 2.6864 | 1.4342 | High | High | Medium | 822 | 844 | 0.53387
PUEBLO 2102698 | PUEBLO 2102 | NORTH BAY | 0.45229 | 80 | 34.45% | 0 | 0 | 2.749% | 0% | 0 | 0.0103 | 47.6367 | 2.9171 | 1.4313 | Low | Low | Medium | 823 | 861 | 0.49067
PENRYN 110351658 | PENRYN 1103 | SIERRA | 7.9841 | 27.4219 | 66.1% | 1 | 2 | 91.67% | 0% | 0 | 0.027021 | 19.9979 | 2.6417 | 1.4274 | Medium | Medium | Medium | 824 | 842 | 0.54036
PASO ROBLES 1103N58 | PASO ROBLES 1103 | LOS PADRES | 4.5123 | 48.6182 | 39.94% | 0 | 1 | 60.11% | 0% | 0 | 0.026481 | 26.5534 | 2.029 | 1.4267 | Medium | Medium | Low | 825 | 782 | 0.70315
JAMESON 11028842 | JAMESON 1102 | SACRAMENTO | 0.46739 | 47.8727 | 32.07% | 0 | 0 | 8.162% | 0% | 0 | 0.0097873 | 47.6367 | 3.045 | 1.4197 | Low | Low | Medium | 826 | 866 | 0.46623
BOLINAS 110146152 | BOLINAS 1101 | NORTH BAY | 0.43174 | 69.1568 | 0% | 0 | 0 | 4.254% | 0% | 0 | 0.0073288 | 47.6367 | 4.0187 | 1.403 | Low | Low | High | 827 | 920 | 0.34912
ANITA 1106CB | ANITA 1106 | NORTH VALLEY | 0.115 | 85 | 100% | 0 | 0 | 0.3281% | 0% | 0 | 0.017735 | 47.6367 | 1.6583 | 1.401 | Low | Low | Low | 828 | 745 | 0.84484
SAN RAFAEL 1108516 | SAN RAFAEL 1108 | NORTH BAY | 10.7797 | 42.2809 | 10.51% | 16 | 17 | 98.34% | 99.7% | 0 | 0.30979 | 1 | 4.4882 | 1.3904 | High | High | High | 829 | 956 | 0.30979
DESCHUTES 11043719 | DESCHUTES 1104 | NORTH VALLEY | 11.6781 | 40.3272 | 100% | 0 | 2 | 67.24% | 0% | 0 | 0.026406 | 19.9979 | 2.604 | 1.3751 | Medium | Medium | Medium | 830 | 847 | 0.52806
GONZALES 110422418 | GONZALES 1104 | CENTRAL COAST | 0.8424 | 88.5066 | 100% | 0 | 0 | 6.858% | 0% | 0 | 0.019362 | 47.6367 | 1.4832 | 1.368 | Low | Low | Low | 831 | 733 | 0.92235
BRUNSWICK 1104CB | BRUNSWICK 1104 | SIERRA | 1.9366 | 10 | 53.96% | 0 | 0 | 63.09% | 0% | 0 | 0.013676 | 35.3263 | 2.8083 | 1.3567 | Low | Low | Medium | 832 | 863 | 0.48311
BRUNSWICK 11064639 | BRUNSWICK 1106 | SIERRA | 3.2486 | 31.5408 | 99.46% | 0 | 1 | 100% | 1.568% | 1 | 0.034254 | 14.9507 | 2.6487 | 1.3565 | Medium | Medium | Medium | 833 | 853 | 0.51212
JAMESON 110265516 | JAMESON 1102 | SACRAMENTO | 7.9053 | 31.2245 | 60.83% | 1 | 6 | 69.63% | 0% | 0 | 0.023245 | 19.9979 | 2.861 | 1.3299 | Medium | Medium | Medium | 834 | 868 | 0.46484
AUBERRY 110149122 | AUBERRY 1101 | FRESNO | 3.8865 | 26.9324 | 92.34% | 0 | 3 | 100% | 0% | 0 | 0.036287 | 14.9507 | 2.4472 | 1.3276 | Medium | Medium | Medium | 835 | 840 | 0.54251
CAMP EVERS 210311046 | CAMP EVERS 2103 | CENTRAL COAST | 16.2531 | 44.8404 | 64.25% | 23 | 4 | 100% | 100% | 0 | 0.47552 | 1 | 2.7899 | 1.3267 | High | High | Medium | 836 | 864 | 0.47552
VIEJO 2202CB | VIEJO 2202 | CENTRAL COAST | 2.1755 | 10 | 21.89% | 2 | 2 | 100% | 0% | 0 | 0.018504 | 19.9979 | 3.5811 | 1.3252 | Low | Low | High | 837 | 911 | 0.37005
MADISON 210113372 | MADISON 2101 | SACRAMENTO | 3.7782 | 89.8591 | 100% | 0 | 0 | 99.16% | 0% | 0 | 0.047853 | 26.5534 | 1.0386 | 1.3197 | Medium | Medium | Low | 838 | 671 | 1.2706
MOLINO 1102344 | MOLINO 1102 | SONOMA | 1.1141 | 30.1016 | 80.53% | 0 | 2 | 18.52% | 0% | 0 | 0.013045 | 35.3263 | 2.8566 | 1.3164 | Low | Low | Medium | 839 | 869 | 0.46084
ATASCADERO 1101 | ATASCADERO 1101 | LOS PADRES | 0.011512 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 35.3263 | 2.9013 | 1.3012 | Low | Low | Medium | 840 | 872 | 0.44848
LOS GATOS 1106LB44 | LOS GATOS 1106 | DE ANZA | 19.5005 | 14.2956 | 68.84% | 20 | 1 | 100% | 100% | 0 | 0.44075 | 1 | 2.9349 | 1.2936 | High | High | Medium | 841 | 876 | 0.44075
ATASCADERO 1103CB | ATASCADERO 1103 | LOS PADRES | 7.2499 | 46.2369 | 39.81% | 0 | 1 | 74.99% | 13.24% | 0 | 0.025143 | 19.9979 | 2.5685 | 1.2915 | Medium | Medium | Medium | 842 | 858 | 0.50281
ELECTRA 11011238 | ELECTRA 1101 | STOCKTON | 4.7136 | 30.1636 | 44.85% | 1 | 1 | 66.69% | 0% | 0 | 0.015593 | 26.5534 | 3.1098 | 1.2876 | Low | Low | High | 843 | 888 | 0.41404
ROB ROY 21055090 | ROB ROY 2105 | CENTRAL COAST | 21.1859 | 44.752 | 78.23% | 40 | 3 | 100% | 97.19% | 1 | 0.37924 | 1 | 3.3344 | 1.2646 | High | High | High | 844 | 906 | 0.37924
VACAVILLE 110941782 | VACAVILLE 1109 | SACRAMENTO | 0.50066 | 79.3838 | 12.32% | 0 | 0 | 29.37% | 0% | 0 | 0.011149 | 35.3263 | 3.1982 | 1.2596 | Low | Low | High | 845 | 896 | 0.39386
COTTONWOOD 110335470 | COTTONWOOD 1103 | NORTH VALLEY | 18.2496 | 46.5174 | 67.33% | 0 | 6 | 73.33% | 0% | 0 | 0.03595 | 19.9979 | 1.7492 | 1.2576 | Medium | Medium | Low | 846 | 778 | 0.71893
GANSNER 110137550 | GANSNER 1101 | NORTH VALLEY | 0.5773 | 95.7309 | 100% | 0 | 0 | 12.36% | 0% | 0 | 0.021451 | 19.9979 | 2.9158 | 1.2508 | Low | Low | Medium | 847 | 880 | 0.42898
GEYSERVILLE 1102274 | GEYSERVILLE 1102 | SONOMA | 4.0814 | 46.8618 | 69.12% | 1 | 0 | 22.13% | 0% | 0 | 0.013409 | 35.3263 | 2.6258 | 1.2438 | Low | Low | Medium | 848 | 865 | 0.47371
CORRAL 110275622 | CORRAL 1102 | STOCKTON | 0.45257 | 14.2481 | 100% | 0 | 0 | 7.908% | 0% | 0 | 0.011863 | 35.3263 | 2.9665 | 1.2432 | Low | Low | Medium | 849 | 887 | 0.41909
PEORIA 1705CB | PEORIA 1705 | YOSEMITE | 7.2378 | 70.7531 | 12.14% | 0 | 3 | 100% | 0% | 0 | 0.022424 | 26.5534 | 2.0773 | 1.2369 | Medium | Medium | Low | 850 | 822 | 0.59543
SANTA ROSA A 1108626 | SANTA ROSA A 1108 | SONOMA | 0.13621 | 75 | 0% | 0 | 0 | 3.381% | 0% | 0 | 0.0075596 | 47.6367 | 3.4302 | 1.2353 | Low | Low | High | 851 | 917 | 0.36011
COTATI 110387402 | COTATI 1103 | SONOMA | 11.4171 | 74.8765 | 25.02% | 0 | 0 | 100% | 0% | 0 | 0.031179 | 19.9979 | 1.9793 | 1.2341 | Medium | Medium | Low | 852 | 815 | 0.62351
CLARKSVILLE 210551478 | CLARKSVILLE 2105 | SIERRA | 0.050363 | 10 | 0% | 0 | 0 | 89.86% | 0% | 0 | 0.011483 | 35.3263 | 3.0401 | 1.2332 | Low | Low | Medium | 853 | 890 | 0.40565
GEYSERVILLE 1102CB | GEYSERVILLE 1102 | SONOMA | 2.3641 | 61.3374 | 59.74% | 1 | 1 | 32.38% | 57.77% | 0 | 0.03873 | 19.9979 | 1.5774 | 1.2218 | Medium | Medium | Low | 854 | 762 | 0.77452
MIDDLETOWN 1102414 | MIDDLETOWN 1102 | HUMBOLDT | 5.0571 | 54.0321 | 100% | 0 | 3 | 42.26% | 0% | 0 | 0.026354 | 14.9507 | 3.0843 | 1.2153 | Medium | Medium | High | 855 | 895 | 0.39402
WOODSIDE 110147872 | WOODSIDE 1101 | PENINSULA | 4.1743 | 60.8207 | 75.33% | 12 | 4 | 100% | 100% | 0 | 0.39089 | 1 | 3.0893 | 1.2076 | High | High | High | 856 | 898 | 0.39089
RED BLUFF 11011334 | RED BLUFF 1101 | NORTH VALLEY | 1.7587 | 68.6115 | 100% | 0 | 0 | 11.05% | 0% | 0 | 0.017653 | 35.3263 | 1.9337 | 1.2059 | Low | Low | Low | 857 | 814 | 0.62362
COTATI 1104CB | COTATI 1104 | SONOMA | 2.3176 | 10.9581 | 56.63% | 1 | 1 | 30.19% | 0% | 0 | 0.010506 | 35.3263 | 3.2386 | 1.2019 | Low | Low | High | 858 | 910 | 0.37113
PEABODY 2108CB | PEABODY 2108 | SACRAMENTO | 0.80945 | 40.6035 | 58.6% | 0 | 0 | 21.91% | 0% | 0 | 0.01162 | 35.3263 | 2.9033 | 1.1917 | Low | Low | Medium | 859 | 889 | 0.41049
MARIPOSA 2102 | MARIPOSA 2102 | YOSEMITE | 0.0020154 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 19.9979 | 2.0892 | 1.1912 | Medium | Medium | Low | 860 | 832 | 0.57017
JESSUP 11021314 | JESSUP 1102 | NORTH VALLEY | 5.6244 | 41.4572 | 97.17% | 0 | 1 | 39.97% | 0% | 0 | 0.022232 | 26.5534 | 2.005 | 1.1836 | Medium | Medium | Low | 861 | 825 | 0.59034
ROSSMOOR 1106L522R | ROSSMOOR 1106 | DIABLO | 1.0378 | 10 | 19.41% | 3 | 11 | 24.6% | 0% | 0 | 0.011991 | 26.5534 | 3.6777 | 1.171 | Low | Low | High | 862 | 949 | 0.31841
MARIPOSA 21019400 | MARIPOSA 2101 | YOSEMITE | 62.7736 | 22.0188 | 81.32% | 9 | 129 | 100% | 40.79% | 1 | 0.72296 | 1 | 1.619 | 1.1705 | High | High | Low | 863 | 777 | 0.72296
WHEATLAND 110591170 | WHEATLAND 1105 | SIERRA | 9.9882 | 49.4424 | 100% | 0 | 0 | 18.55% | 0% | 0 | 0.019051 | 35.3263 | 1.7362 | 1.1684 | Low | Low | Low | 864 | 797 | 0.67299
LINCOLN 110451756 | LINCOLN 1104 | SIERRA | 15.5512 | 62.1844 | 61.25% | 0 | 6 | 27.35% | 0% | 0 | 0.031506 | 26.5534 | 1.3793 | 1.1539 | Medium | Medium | Low | 865 | 746 | 0.8366
WYANDOTTE 110641650 | WYANDOTTE 1106 | NORTH VALLEY | 1.9508 | 59.4004 | 100% | 0 | 0 | 12.07% | 0% | 0 | 0.01911 | 26.5534 | 2.2667 | 1.1502 | Low | Low | Medium | 866 | 855 | 0.50744
FOOTHILL 1101549904 | FOOTHILL 1101 | LOS PADRES | 7.1079 | 49.5665 | 45.77% | 1 | 3 | 40.61% | 0% | 0 | 0.021381 | 14.9507 | 3.5842 | 1.1457 | Low | Low | High | 867 | 947 | 0.31966
ALTO 1124430 | ALTO 1124 | NORTH BAY | 7.2931 | 30.5125 | 12.77% | 14 | 16 | 100% | 100% | 0 | 0.26455 | 1 | 4.3274 | 1.1448 | High | High | High | 868 | 984 | 0.26455
CRESCENT MILLS 21012230 | CRESCENT MILLS 2101 | NORTH VALLEY | 1.0766 | 89.5687 | 97.05% | 0 | 1 | 9.699% | 0% | 0 | 0.022777 | 26.5534 | 1.8892 | 1.1426 | Medium | Medium | Low | 869 | 820 | 0.60481
BIG BASIN 110212992 | BIG BASIN 1102 | CENTRAL COAST | 14.2865 | 29.6471 | 74.67% | 30 | 1 | 100% | 100% | 1 | 0.44527 | 1 | 2.5494 | 1.1352 | High | High | Medium | 870 | 873 | 0.44527
UPPER LAKE 11016663 | UPPER LAKE 1101 | HUMBOLDT | 2.3336 | 74.5453 | 100% | 0 | 0 | 100% | 0% | 0 | 0.043648 | 19.9979 | 1.2971 | 1.1322 | Medium | Medium | Low | 871 | 740 | 0.87287
WYANDOTTE 110932586 | WYANDOTTE 1109 | NORTH VALLEY | 1.4371 | 18.342 | 79.5% | 0 | 0 | 94.84% | 0% | 0 | 0.024309 | 11.2183 | 4.1406 | 1.1292 | Medium | Medium | High | 872 | 974 | 0.27271
JARVIS 1108MR576 | JARVIS 1108 | MISSION | 1.3706 | 10 | 32.22% | 0 | 0 | 22.29% | 0% | 0 | 0.0076408 | 35.3263 | 4.1701 | 1.1256 | Low | Low | High | 873 | 977 | 0.26992
CLAYTON 22159765 | CLAYTON 2215 | DIABLO | 0.13991 | 10 | 100% | 0 | 0 | 14.93% | 0% | 0 | 0.012358 | 26.5534 | 3.3958 | 1.1143 | Low | Low | High | 874 | 936 | 0.32814
SAN LUIS OBISPO 1108CB | SAN LUIS OBISPO 1108 | LOS PADRES | 0.74619 | 53.8272 | 22.96% | 0 | 1 | 8.668% | 0% | 0 | 0.012642 | 26.5534 | 3.3193 | 1.1142 | Low | Low | High | 875 | 931 | 0.33568
STAFFORD 1102CB | STAFFORD 1102 | NORTH BAY | 0.24035 | 10 | 0% | 0 | 0 | 45.06% | 0% | 0 | 0.0084029 | 47.6367 | 2.7618 | 1.1055 | Low | Low | Medium | 876 | 892 | 0.40029
JARVIS 1110CB | JARVIS 1110 | MISSION | 0.094443 | 65 | 0% | 0 | 0 | 1.965% | 0% | 0 | 0.0069643 | 35.3263 | 4.4419 | 1.0928 | Low | Low | High | 877 | 1006 | 0.24602
CAMP EVERS 210510728 | CAMP EVERS 2105 | CENTRAL COAST | 10.465 | 15.413 | 38.24% | 13 | 4 | 100% | 100% | 0 | 0.2598 | 1 | 4.1867 | 1.0877 | High | High | High | 878 | 988 | 0.2598
WEST POINT 11024788 | WEST POINT 1102 | STOCKTON | 70.3316 | 50.1461 | 97.21% | 9 | 19 | 100% | 60.3% | 0 | 0.45673 | 1 | 2.3714 | 1.0831 | High | High | Medium | 879 | 871 | 0.45673
HOOPA 1101561116 | HOOPA 1101 | HUMBOLDT | 0.012979 | 85 | 0% | 0 | 0 | 100% | 0% | 0 | 0.021028 | 47.6367 | 1.0757 | 1.0775 | Low | Low | Low | 880 | 720 | 1.0017
PUEBLO 21021326 | PUEBLO 2102 | NORTH BAY | 0.81465 | 66.7263 | 75.65% | 0 | 0 | 6.742% | 0% | 0 | 0.013708 | 26.5534 | 2.9185 | 1.0623 | Low | Low | Medium | 881 | 915 | 0.364
CALISTOGA 1101734 | CALISTOGA 1101 | NORTH BAY | 11.7939 | 55.3179 | 62.25% | 13 | 12 | 73.13% | 81.49% | 0 | 0.39061 | 1 | 2.7018 | 1.0554 | High | High | Medium | 882 | 899 | 0.39061
INDIAN FLAT 11044440 | INDIAN FLAT 1104 | YOSEMITE | 0.21912 | 58.2464 | 100% | 0 | 0 | 100% | 0% | 0 | 0.039224 | 14.9507 | 1.7987 | 1.0548 | Medium | Medium | Low | 883 | 828 | 0.58642
JESSUP 110141356 | JESSUP 1101 | NORTH VALLEY | 32.7394 | 40.1195 | 100% | 1 | 5 | 100% | 0% | 0 | 0.044331 | 14.9507 | 1.5857 | 1.051 | Medium | Medium | Low | 884 | 801 | 0.66278
SAN RAFAEL 1108322 | SAN RAFAEL 1108 | NORTH BAY | 7.1088 | 25.427 | 14.01% | 10 | 9 | 95.89% | 89.81% | 0 | 0.21074 | 1 | 4.9853 | 1.0506 | High | High | High | 885 | 1041 | 0.21074
ANDERSON 11012051 | ANDERSON 1101 | NORTH VALLEY | 4.6467 | 13.4745 | 100% | 0 | 2 | 87.22% | 0% | 0 | 0.030553 | 14.9507 | 2.2964 | 1.0489 | Medium | Medium | Medium | 886 | 870 | 0.45678
WISE 11022234 | WISE 1102 | SIERRA | 15.1055 | 10 | 57.56% | 1 | 4 | 100% | 0% | 0 | 0.025382 | 19.9979 | 2.055 | 1.0431 | Medium | Medium | Low | 887 | 854 | 0.5076
LAURELES 11116617 | LAURELES 1111 | CENTRAL COAST | 1.819 | 41.7117 | 100% | 1 | 0 | 100% | 0% | 0 | 0.040513 | 14.9507 | 1.7012 | 1.0304 | Medium | Medium | Low | 888 | 819 | 0.6057
OAKHURST 110310140 | OAKHURST 1103 | YOSEMITE | 16.859 | 26.9049 | 99.84% | 3 | 44 | 100% | 99.31% | 0 | 0.52553 | 1 | 1.9527 | 1.0262 | High | High | Low | 889 | 850 | 0.52553
MIRABEL 1101228 | MIRABEL 1101 | SONOMA | 2.2414 | 32.2817 | 68.07% | 3 | 1 | 22.76% | 0% | 0 | 0.012705 | 26.5534 | 3.0408 | 1.0258 | Low | Low | Medium | 890 | 928 | 0.33736
CAMP EVERS 21065302 | CAMP EVERS 2106 | CENTRAL COAST | 5.9826 | 48.1403 | 77.43% | 11 | 0 | 100% | 95.97% | 0 | 0.25415 | 1 | 4.0058 | 1.0181 | High | High | High | 891 | 997 | 0.25415
ALTO 11251226 | ALTO 1125 | NORTH BAY | 7.7199 | 13.4122 | 30.57% | 9 | 29 | 98.37% | 100% | 0 | 0.23095 | 1 | 4.3912 | 1.0142 | High | High | High | 892 | 1022 | 0.23095
ALTO 11243745 | ALTO 1124 | NORTH BAY | 4.5809 | 48.7454 | 24.8% | 4 | 26 | 100% | 100% | 0 | 0.24571 | 1 | 4.1069 | 1.0091 | High | High | High | 893 | 1007 | 0.24571
PASO ROBLES 1107CB | PASO ROBLES 1107 | LOS PADRES | 0.069192 | 75 | 100% | 0 | 0 | 0.6192% | 0% | 0 | 0.016629 | 47.6367 | 1.2733 | 1.0086 | Low | Low | Low | 894 | 758 | 0.79217
DUNBAR 1103CB | DUNBAR 1103 | SONOMA | 1.9287 | 52.9434 | 74.35% | 2 | 2 | 15.81% | 20.29% | 0 | 0.029588 | 11.2183 | 3.0334 | 1.0069 | Medium | Medium | Medium | 895 | 934 | 0.33193
COTATI 1105328 | COTATI 1105 | SONOMA | 0.42542 | 48.6287 | 27.07% | 0 | 1 | 3.098% | 0% | 0 | 0.0080325 | 47.6367 | 2.617 | 1.0014 | Low | Low | Medium | 896 | 904 | 0.38264
FREMONT 1104MR339 | FREMONT 1104 | MISSION | 1.2378 | 84.498 | 6.265% | 0 | 0 | 17.79% | 0% | 0 | 0.0097922 | 65.3912 | 1.5544 | 0.99533 | Low | Low | Low | 897 | 809 | 0.64033
DIAMOND SPRINGS 1105CB | DIAMOND SPRINGS 1105 | SIERRA | 1.4833 | 10 | 14.23% | 0 | 1 | 31.56% | 62.47% | 0 | 0.022985 | 14.9507 | 2.8916 | 0.99365 | Medium | Medium | Medium | 898 | 922 | 0.34364
WILLITS 110391948 | WILLITS 1103 | HUMBOLDT | 6.1069 | 55.6867 | 72.29% | 1 | 4 | 82.53% | 5.563% | 0 | 0.035629 | 14.9507 | 1.8551 | 0.98814 | Medium | Medium | Low | 899 | 846 | 0.53267
OAKLAND K 1102CR014 | OAKLAND K 1102 | EAST BAY | 10.5526 | 27.0866 | 16.24% | 14 | 8 | 100% | 100% | 1 | 0.23413 | 1 | 4.2072 | 0.98504 | High | High | High | 900 | 1017 | 0.23413
PENRYN 11052406 | PENRYN 1105 | SIERRA | 3.0306 | 20.0804 | 58.87% | 1 | 0 | 24.58% | 0% | 0 | 0.012032 | 35.3263 | 2.2969 | 0.97632 | Low | Low | Medium | 901 | 885 | 0.42506
VALLEY VIEW 1106P166 | VALLEY VIEW 1106 | EAST BAY | 3.4384 | 77.0381 | 8.804% | 5 | 1 | 75.32% | 0% | 0 | 0.020855 | 11.2183 | 4.1312 | 0.96654 | Low | Low | High | 902 | 1018 | 0.23396
MONTE RIO 1113346 | MONTE RIO 1113 | SONOMA | 10.1076 | 73.6223 | 44.96% | 12 | 4 | 100% | 100% | 0 | 0.29448 | 1 | 3.2807 | 0.9661 | High | High | High | 903 | 963 | 0.29448
ALTO 1124432 | ALTO 1124 | NORTH BAY | 7.823 | 44.0512 | 43.81% | 6 | 19 | 100% | 100% | 0 | 0.22255 | 1 | 4.3312 | 0.96392 | High | High | High | 904 | 1028 | 0.22255
CLARKSVILLE 210619642 | CLARKSVILLE 2106 | SIERRA | 0.81481 | 10 | 0% | 0 | 0 | 51.08% | 0% | 0 | 0.007814 | 35.3263 | 3.4847 | 0.96191 | Low | Low | High | 905 | 972 | 0.27604
FITCH MOUNTAIN 1113406 | FITCH MOUNTAIN 1113 | SONOMA | 1.4439 | 43.4794 | 97.1% | 1 | 1 | 15.43% | 0% | 0 | 0.01793 | 19.9979 | 2.6791 | 0.96064 | Low | Low | Medium | 906 | 918 | 0.35857
LLAGAS 2107XR178 | LLAGAS 2107 | SAN JOSE | 0.65323 | 27.1294 | 68.86% | 0 | 0 | 9.688% | 0% | 0 | 0.010217 | 26.5534 | 3.4762 | 0.94309 | Low | Low | High | 907 | 975 | 0.2713
LOS GATOS 1106LA64 | LOS GATOS 1106 | DE ANZA | 12.775 | 27.6673 | 77.8% | 17 | 7 | 100% | 100% | 1 | 0.50336 | 1 | 1.8673 | 0.93994 | High | High | Low | 908 | 857 | 0.50336
PENRYN 11072706 | PENRYN 1107 | SIERRA | 5.0792 | 12.8578 | 75.5% | 0 | 3 | 34.23% | 0% | 0 | 0.013291 | 26.5534 | 2.6628 | 0.93976 | Low | Low | Medium | 909 | 919 | 0.35292
SHINGLE SPRINGS 2109CB | SHINGLE SPRINGS 2109 | SIERRA | 27.1022 | 21.2732 | 81.89% | 8 | 12 | 97.37% | 94.72% | 0 | 0.31197 | 1 | 3.0034 | 0.93698 | High | High | Medium | 910 | 955 | 0.31197
VIEJO 220235388 | VIEJO 2202 | CENTRAL COAST | 0.45244 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.014786 | 14.9507 | 4.2357 | 0.93635 | Low | Low | High | 911 | 1030 | 0.22106
OILFIELDS 1103N40 | OILFIELDS 1103 | CENTRAL COAST | 0.75328 | 20.1382 | 3.227% | 0 | 2 | 100% | 0% | 0 | 0.01659 | 19.9979 | 2.785 | 0.92399 | Low | Low | Medium | 912 | 935 | 0.33177
PUTAH CREEK 110264044 | PUTAH CREEK 1102 | SACRAMENTO | 5.0213 | 75.9618 | 100% | 0 | 1 | 67.37% | 0% | 0 | 0.03282 | 14.9507 | 1.8721 | 0.91864 | Medium | Medium | Low | 913 | 860 | 0.49069
STANISLAUS 17011812 | STANISLAUS 1701 | YOSEMITE | 19.5078 | 54.4191 | 60.13% | 9 | 15 | 100% | 99.79% | 0 | 0.30454 | 1 | 2.9903 | 0.91067 | High | High | Medium | 914 | 960 | 0.30454
PENRYN 110790970 | PENRYN 1107 | SIERRA | 0.86048 | 10 | 69.3% | 0 | 0 | 20.31% | 0% | 0 | 0.011579 | 26.5534 | 2.9455 | 0.90563 | Low | Low | Medium | 915 | 957 | 0.30746
CABRILLO 1103CB | CABRILLO 1103 | LOS PADRES | 0.14089 | 80 | 0% | 0 | 0 | 3.139% | 0% | 0 | 0.0078018 | 35.3263 | 3.2473 | 0.89498 | Low | Low | High | 916 | 973 | 0.27561
LOS GATOS 110660116 | LOS GATOS 1106 | DE ANZA | 12.3794 | 30.6322 | 46% | 28 | 5 | 100% | 100% | 0 | 0.37151 | 1 | 2.4062 | 0.89393 | High | High | Medium | 917 | 909 | 0.37151
NARROWS 21052216 | NARROWS 2105 | SIERRA | 56.6943 | 15.1323 | 85.75% | 7 | 36 | 98.06% | 0% | 0 | 0.28652 | 1 | 3.1152 | 0.89257 | High | High | High | 918 | 966 | 0.28652
BIG BASIN 110169550 | BIG BASIN 1101 | CENTRAL COAST | 17.8925 | 32.0488 | 71.29% | 38 | 3 | 100% | 100% | 0 | 0.32055 | 1 | 2.7588 | 0.88433 | High | High | Medium | 919 | 940 | 0.32055
GOLDTREE 1105551904 | GOLDTREE 1105 | LOS PADRES | 0.022237 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 2.7356 | 0.87498 | Medium | Medium | Medium | 920 | 942 | 0.31985
FROGTOWN 170113412 | FROGTOWN 1701 | STOCKTON | 38.8157 | 21.4669 | 89.5% | 2 | 31 | 100% | 20.91% | 0 | 0.31378 | 1 | 2.7876 | 0.8747 | High | High | Medium | 921 | 952 | 0.31378
MERCED FALLS 110285002 | MERCED FALLS 1102 | YOSEMITE | 35.632 | 29.6878 | 97.17% | 0 | 6 | 100% | 0% | 0 | 0.059691 | 26.5534 | 0.55157 | 0.87425 | Medium | Medium | Low | 922 | 641 | 1.585
SAN RAMON 2102CB | SAN RAMON 2102 | MISSION | 1.535 | 41.2314 | 0% | 0 | 0 | 65.73% | 0% | 0 | 0.011168 | 19.9979 | 3.898 | 0.87053 | Low | Low | High | 923 | 1027 | 0.22333
MONTICELLO 1101666 | MONTICELLO 1101 | NORTH BAY | 10.1625 | 67.7354 | 65.91% | 1 | 1 | 73.12% | 0% | 0 | 0.025333 | 14.9507 | 2.2961 | 0.86964 | Medium | Medium | Medium | 924 | 907 | 0.37875
FOOTHILL 1102V06 | FOOTHILL 1102 | LOS PADRES | 1.4055 | 48.154 | 31.22% | 0 | 1 | 21.48% | 0% | 0 | 0.0099416 | 26.5534 | 3.2868 | 0.86767 | Low | Low | High | 925 | 985 | 0.26398
SARATOGA 1107413816 | SARATOGA 1107 | DE ANZA | 11.1604 | 62.8545 | 90.16% | 13 | 7 | 100% | 89.94% | 0 | 0.25675 | 1 | 3.3738 | 0.86623 | High | High | High | 926 | 993 | 0.25675
MONTICELLO 11011780 | MONTICELLO 1101 | NORTH BAY | 0.07232 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 19.9979 | 1.5173 | 0.86511 | Medium | Medium | Low | 927 | 832 | 0.57017
SHADY GLEN 110151696 | SHADY GLEN 1101 | SIERRA | 17.0578 | 38.8695 | 93.61% | 4 | 7 | 82.3% | 0% | 0 | 0.033526 | 11.2183 | 2.2918 | 0.86196 | Medium | Medium | Medium | 928 | 908 | 0.37611
CAMP EVERS 210312990 | CAMP EVERS 2103 | CENTRAL COAST | 13.5574 | 33.1797 | 62.33% | 16 | 15 | 100% | 100% | 0 | 0.32668 | 1 | 2.6325 | 0.85998 | High | High | Medium | 929 | 937 | 0.32668
MESA 11016113 | MESA 1101 | LOS PADRES | 1.5145 | 57.2852 | 100% | 0 | 0 | 15.55% | 0% | 0 | 0.017101 | 19.9979 | 2.5121 | 0.85911 | Low | Low | Medium | 930 | 925 | 0.34199
NARROWS 2105 | NARROWS 2105 | SIERRA | 0.056021 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 2.6731 | 0.85501 | Medium | Medium | Medium | 931 | 942 | 0.31985
MONTE RIO 11133970 | MONTE RIO 1113 | SONOMA | 7.3428 | 62.8724 | 47.81% | 13 | 10 | 100% | 100% | 0 | 0.25889 | 1 | 3.2812 | 0.84949 | High | High | High | 932 | 991 | 0.25889
COARSEGOLD 210410110 | COARSEGOLD 2104 | YOSEMITE | 49.586 | 26.2952 | 95.51% | 5 | 92 | 100% | 6.102% | 1 | 0.36439 | 1 | 2.3299 | 0.84901 | High | High | Medium | 933 | 914 | 0.36439
LAYTONVILLE 110264908 | LAYTONVILLE 1102 | HUMBOLDT | 3.5532 | 21.2702 | 61.98% | 6 | 8 | 55.85% | 0% | 0 | 0.021316 | 19.9979 | 1.9799 | 0.84396 | Low | Low | Low | 934 | 882 | 0.42627
GARBERVILLE 11012026 | GARBERVILLE 1101 | HUMBOLDT | 6.3529 | 96.5509 | 100% | 5 | 1 | 100% | 0% | 0 | 0.05472 | 65.3912 | 0.23353 | 0.83563 | Medium | Medium | Low | 935 | 502 | 3.5782
EEL RIVER 11024814 | EEL RIVER 1102 | HUMBOLDT | 27.3153 | 76.7361 | 63.94% | 7 | 10 | 97.55% | 0% | 0 | 0.42884 | 1 | 1.9361 | 0.83027 | High | High | Low | 936 | 881 | 0.42884
SPRING GAP 170286032 | SPRING GAP 1702 | YOSEMITE | 1.0066 | 66.0059 | 100% | 0 | 0 | 34.72% | 25.18% | 0 | 0.037122 | 26.5534 | 0.83455 | 0.82263 | Medium | Medium | Low | 937 | 724 | 0.98571
CAMP EVERS 210511004 | CAMP EVERS 2105 | CENTRAL COAST | 4.2954 | 13.9666 | 78.63% | 3 | 0 | 100% | 100% | 0 | 0.2074 | 1 | 3.9293 | 0.81496 | High | High | High | 938 | 1045 | 0.2074
GREENBRAE 11021254 | GREENBRAE 1102 | NORTH BAY | 7.0201 | 10 | 37.52% | 8 | 16 | 74.16% | 100% | 0 | 0.21468 | 1 | 3.7891 | 0.81344 | High | High | High | 939 | 1038 | 0.21468
MONTICELLO 110152910 | MONTICELLO 1101 | NORTH BAY | 2.1786 | 24.2187 | 98.28% | 0 | 1 | 69.32% | 0% | 0 | 0.026641 | 19.9979 | 1.5181 | 0.80879 | Medium | Medium | Low | 940 | 845 | 0.53277
CAMP EVERS 210612518 | CAMP EVERS 2106 | CENTRAL COAST | 15.9361 | 56.9453 | 43.9% | 39 | 3 | 100% | 100% | 0 | 0.3407 | 1 | 2.3547 | 0.80224 | High | High | Medium | 941 | 926 | 0.3407
ELECTRA 1101 | ELECTRA 1101 | STOCKTON | 0.02594 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 2.4984 | 0.79913 | Medium | Medium | Medium | 942 | 942 | 0.31985
BIG TREES 0402CB | BIG TREES 0402 | CENTRAL COAST | 6.3055 | 27.5904 | 28.63% | 15 | 5 | 91.1% | 95.73% | 0 | 0.19443 | 1 | 4.0842 | 0.7941 | High | High | High | 943 | 1072 | 0.19443
CLAYTON 221296224 | CLAYTON 2212 | DIABLO | 6.0784 | 53.8659 | 38.47% | 4 | 5 | 100% | 98.09% | 0 | 0.23534 | 1 | 3.3663 | 0.79223 | High | High | High | 944 | 1015 | 0.23534
LOS GATOS 1106LB48 | LOS GATOS 1106 | DE ANZA | 14.9866 | 67.642 | 90.94% | 14 | 1 | 100% | 100% | 1 | 0.39219 | 1 | 2.0173 | 0.79115 | High | High | Low | 945 | 897 | 0.39219
PURISIMA 110154728 | PURISIMA 1101 | LOS PADRES | 0.37057 | 45.459 | 76.61% | 0 | 0 | 8.245% | 0% | 0 | 0.012146 | 19.9979 | 3.2328 | 0.78525 | Low | Low | High | 946 | 1011 | 0.2429
COTATI 1102260 | COTATI 1102 | SONOMA | 1.6248 | 13.946 | 2.286% | 0 | 1 | 27.41% | 0% | 0 | 0.0075335 | 35.3263 | 2.9441 | 0.78353 | Low | Low | Medium | 947 | 983 | 0.26613
WOODSIDE 11043583 | WOODSIDE 1104 | PENINSULA | 2.721 | 71.077 | 98.47% | 8 | 4 | 97.67% | 92.99% | 0 | 0.28756 | 1 | 2.7171 | 0.78133 | High | High | Medium | 948 | 965 | 0.28756
OAKHURST 1103CB | OAKHURST 1103 | YOSEMITE | 29.7308 | 28.0867 | 78.34% | 5 | 58 | 96.61% | 65.89% | 1 | 0.32601 | 1 | 2.3864 | 0.77799 | High | High | Medium | 949 | 938 | 0.32601
OAKLAND X 1104CR288 | OAKLAND X 1104 | EAST BAY | 2.7135 | 13.3002 | 40.68% | 11 | 2 | 100% | 100% | 0 | 0.18087 | 1 | 4.2967 | 0.77715 | High | High | High | 950 | 1091 | 0.18087
LLAGAS 2101XR264 | LLAGAS 2101 | SAN JOSE | 0.73019 | 64.4385 | 100% | 0 | 0 | 3.559% | 0% | 0 | 0.015944 | 19.9979 | 2.4255 | 0.77337 | Low | Low | Medium | 951 | 948 | 0.31885
INDIAN FLAT 1104 | INDIAN FLAT 1104 | YOSEMITE | 0.0039208 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 14.9507 | 1.8025 | 0.76836 | Medium | Medium | Low | 952 | 883 | 0.42627
HALF MOON BAY 1103H82 | HALF MOON BAY 1103 | PENINSULA | 53.0127 | 52.0051 | 39.35% | 29 | 11 | 92.34% | 3.002% | 1 | 0.29233 | 1 | 2.6229 | 0.76674 | High | High | Medium | 953 | 964 | 0.29233
WOODACRE 1102137662 | WOODACRE 1102 | NORTH BAY | 8.5017 | 38.382 | 27.15% | 11 | 8 | 98.65% | 72.31% | 0 | 0.16033 | 1 | 4.753 | 0.76204 | High | High | High | 954 | 1129 | 0.16033
WEST POINT 11021305 | WEST POINT 1102 | STOCKTON | 11.4284 | 52.5642 | 100% | 4 | 5 | 100% | 100% | 1 | 0.34333 | 1 | 2.218 | 0.76151 | High | High | Low | 955 | 923 | 0.34333
COLUMBIA HILL 1101CB | COLUMBIA HILL 1101 | SIERRA | 39.662 | 48.9114 | 99.72% | 21 | 18 | 100% | 77.89% | 0 | 0.46568 | 1 | 1.6227 | 0.75567 | High | High | Low | 956 | 867 | 0.46568
DIAMOND SPRINGS 11052102 | DIAMOND SPRINGS 1105 | SIERRA | 37.6923 | 30.2782 | 83.99% | 5 | 15 | 95.84% | 86.14% | 1 | 0.30069 | 1 | 2.5037 | 0.75284 | High | High | Medium | 957 | 961 | 0.30069
SAN JOAQUIN #3 110110010 | SAN JOAQUIN #3 1101 | YOSEMITE | 12.729 | 58.6534 | 88.53% | 3 | 19 | 100% | 90.16% | 0 | 0.42208 | 1 | 1.7707 | 0.74736 | High | High | Low | 958 | 886 | 0.42208
MIRABEL 110238514 | MIRABEL 1102 | SONOMA | 10.5875 | 61.5593 | 46.21% | 16 | 8 | 100% | 100% | 0 | 0.25422 | 1 | 2.9393 | 0.74724 | High | High | Medium | 959 | 996 | 0.25422
TASSAJARA 2106CB | TASSAJARA 2106 | DIABLO | 0.13696 | 51.6086 | 30.65% | 0 | 2 | 4.465% | 0% | 0 | 0.0087354 | 19.9979 | 4.2753 | 0.74685 | Low | Low | High | 960 | 1104 | 0.17469
CORTINA 1101302192 | CORTINA 1101 | SACRAMENTO | 1.036 | 90 | 100% | 0 | 0 | 5.795% | 0% | 0 | 0.019354 | 35.3263 | 1.0872 | 0.74333 | Low | Low | Low | 961 | 792 | 0.6837
GEYSERVILLE 1101482 | GEYSERVILLE 1101 | SONOMA | 0.45328 | 77.9574 | 100% | 0 | 0 | 13.09% | 0% | 0 | 0.019179 | 35.3263 | 1.094 | 0.74117 | Low | Low | Low | 962 | 795 | 0.67751
CURTIS 170268380 | CURTIS 1702 | YOSEMITE | 6.6498 | 16.4166 | 99.81% | 2 | 11 | 100% | 65.93% | 0 | 0.18443 | 1 | 4.0104 | 0.73965 | High | High | High | 963 | 1084 | 0.18443
PENRYN 110550550 | PENRYN 1105 | SIERRA | 3.146 | 23.6879 | 96.13% | 0 | 1 | 22.41% | 0% | 0 | 0.014437 | 26.5534 | 1.9281 | 0.73914 | Low | Low | Low | 964 | 902 | 0.38336
SNEATH LANE 110715341 | SNEATH LANE 1107 | PENINSULA | 0.71839 | 10 | 29.45% | 0 | 0 | 55.75% | 0% | 0 | 0.010414 | 19.9979 | 3.5461 | 0.73852 | Low | Low | High | 965 | 1043 | 0.20826
FRUITLAND 1141CB | FRUITLAND 1141 | HUMBOLDT | 3.1926 | 94.3084 | 31.06% | 2 | 0 | 100% | 0% | 0 | 0.03355 | 26.5534 | 0.81784 | 0.72859 | Medium | Medium | Low | 966 | 737 | 0.89086
SAN RAMON 2107MR284 | SAN RAMON 2107 | MISSION | 13.084 | 58.0067 | 71.73% | 0 | 4 | 87.08% | 97.71% | 0 | 0.20548 | 1 | 3.5403 | 0.72747 | High | High | High | 967 | 1051 | 0.20548
WYANDOTTE 11091040 | WYANDOTTE 1109 | NORTH VALLEY | 0.63854 | 10 | 53.93% | 1 | 0 | 10.55% | 0% | 0 | 0.0082291 | 19.9979 | 4.416 | 0.72671 | Low | Low | High | 968 | 1121 | 0.16456
LAKEVILLE 1102280 | LAKEVILLE 1102 | SONOMA | 2.0715 | 72.9124 | 15.25% | 0 | 2 | 23.31% | 0% | 0 | 0.010728 | 26.5534 | 2.5448 | 0.72494 | Low | Low | Medium | 969 | 968 | 0.28487
ALTO 1125902 | ALTO 1125 | NORTH BAY | 12.0705 | 57.5388 | 0.5919% | 9 | 8 | 100% | 85.9% | 1 | 0.21954 | 1 | 3.287 | 0.72162 | High | High | High | 970 | 1034 | 0.21954
PINECREST 04011818 | PINECREST 0401 | YOSEMITE | 1.9342 | 47.9328 | 100% | 2 | 2 | 61.15% | 48.76% | 0 | 0.057579 | 14.9507 | 0.83639 | 0.72 | Medium | Medium | Low | 971 | 743 | 0.86084
WILDWOOD 1101CB | WILDWOOD 1101 | NORTH VALLEY | 0.055929 | 81.1882 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045585 | 14.9507 | 1.052 | 0.71699 | Medium | Medium | Low | 972 | 794 | 0.68153
HARTLEY 1102524 | HARTLEY 1102 | HUMBOLDT | 1.3594 | 63.3777 | 100% | 0 | 1 | 30.18% | 0% | 0 | 0.020999 | 14.9507 | 2.2759 | 0.71449 | Low | Low | Medium | 973 | 951 | 0.31394
MIDDLETOWN 1102CB | MIDDLETOWN 1102 | HUMBOLDT | 4.3813 | 57.1831 | 32.04% | 0 | 1 | 66.6% | 5.967% | 1 | 0.023754 | 11.2183 | 2.6792 | 0.71397 | Medium | Medium | Medium | 974 | 982 | 0.26649
BOLINAS 1101530 | BOLINAS 1101 | NORTH BAY | 10.9693 | 95.0787 | 44.47% | 2 | 3 | 100% | 100% | 1 | 0.19488 | 1 | 3.6256 | 0.70654 | High | High | High | 975 | 1069 | 0.19488
HALF MOON BAY 11038898 | HALF MOON BAY 1103 | PENINSULA | 0.64191 | 18.722 | 22.54% | 0 | 1 | 100% | 0% | 0 | 0.016511 | 14.9507 | 2.8619 | 0.70648 | Low | Low | Medium | 976 | 1004 | 0.24685
MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 2101 | SIERRA | 0.00097812 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 2.2083 | 0.70631 | Medium | Medium | Low | 977 | 942 | 0.31985
TEMPLETON 2111CB | TEMPLETON 2111 | LOS PADRES | 1.8275 | 10 | 27.26% | 0 | 0 | 16.54% | 0% | 0 | 0.0079104 | 35.3263 | 2.52 | 0.70419 | Low | Low | Medium | 978 | 970 | 0.27944
MOLINO 110251788 | MOLINO 1102 | SONOMA | 5.6218 | 26.7859 | 66.33% | 10 | 1 | 38.47% | 5.373% | 0 | 0.021877 | 11.2183 | 2.8624 | 0.70251 | Medium | Medium | Medium | 979 | 1008 | 0.24543
OCEANO 110391240 | OCEANO 1103 | LOS PADRES | 0.011387 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.014483 | 14.9507 | 3.2429 | 0.7022 | Low | Low | High | 980 | 1037 | 0.21654
KESWICK 110148480 | KESWICK 1101 | NORTH VALLEY | 10.8916 | 45.1063 | 95.79% | 1 | 7 | 100% | 100% | 0 | 0.2199 | 1 | 3.1927 | 0.70206 | High | High | High | 981 | 1031 | 0.2199
CALISTOGA 1102634 | CALISTOGA 1102 | NORTH BAY | 11.7799 | 49.1315 | 63.48% | 13 | 6 | 61.37% | 93.22% | 1 | 0.23196 | 1 | 3.0202 | 0.70058 | High | High | Medium | 982 | 1019 | 0.23196
SAN LUIS OBISPO 1101CB | SAN LUIS OBISPO 1101 | LOS PADRES | 6.447 | 57.4459 | 18.1% | 1 | 2 | 37.74% | 0% | 0 | 0.01156 | 19.9979 | 3.0286 | 0.70017 | Low | Low | Medium | 983 | 1020 | 0.23118
BRUNSWICK 110750008 | BRUNSWICK 1107 | SIERRA | 3.5553 | 10 | 37.92% | 1 | 5 | 44.72% | 0% | 0 | 0.01283 | 14.9507 | 3.6273 | 0.69578 | Low | Low | High | 984 | 1078 | 0.19182
CASTRO VALLEY 1108MR273 | CASTRO VALLEY 1108 | MISSION | 0.47624 | 26.7875 | 0% | 0 | 0 | 65.66% | 0% | 0 | 0.01155 | 14.9507 | 4.003 | 0.69126 | Low | Low | High | 985 | 1107 | 0.17268
CURTIS 17039180 | CURTIS 1703 | YOSEMITE | 56.1725 | 23.1853 | 91.13% | 4 | 41 | 100% | 0% | 0 | 0.26987 | 1 | 2.515 | 0.67872 | High | High | Medium | 986 | 978 | 0.26987
CAYETANO 21099504 | CAYETANO 2109 | MISSION | 14.1558 | 53.8418 | 95.53% | 0 | 2 | 97.78% | 75.62% | 1 | 0.20657 | 1 | 3.2662 | 0.67468 | High | High | High | 987 | 1047 | 0.20657
CLARK ROAD 110290548 | CLARK ROAD 1102 | NORTH VALLEY | 18.3619 | 41.0434 | 98.73% | 0 | 11 | 100% | 100% | 0 | 0.25625 | 1 | 2.6272 | 0.67323 | High | High | Medium | 988 | 994 | 0.25625
SAN RAMON 2119CB | SAN RAMON 2119 | MISSION | 0.46097 | 10 | 0% | 0 | 2 | 29.99% | 0% | 0 | 0.0066042 | 26.5534 | 3.8288 | 0.67144 | Low | Low | High | 989 | 1103 | 0.17536
UPPER LAKE 1101452 | UPPER LAKE 1101 | HUMBOLDT | 1.5567 | 30.5905 | 77.99% | 1 | 7 | 7.943% | 0% | 0 | 0.019247 | 19.9979 | 1.7433 | 0.67099 | Low | Low | Low | 990 | 901 | 0.3849
NARROWS 21021252 | NARROWS 2102 | SIERRA | 0.0028409 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 19.9979 | 2.6386 | 0.66989 | Low | Low | Medium | 991 | 998 | 0.25388
POINT MORETTI 110136514 | POINT MORETTI 1101 | CENTRAL COAST | 6.8197 | 17.0171 | 90.44% | 21 | 1 | 100% | 87.46% | 0 | 0.19239 | 1 | 3.4814 | 0.66979 | High | High | High | 992 | 1077 | 0.19239
COARSEGOLD 210410400 | COARSEGOLD 2104 | YOSEMITE | 42.0443 | 18.5406 | 94.25% | 4 | 95 | 94% | 0% | 0 | 0.26956 | 1 | 2.4779 | 0.66794 | High | High | Medium | 993 | 980 | 0.26956
ROB ROY 210410298 | ROB ROY 2104 | CENTRAL COAST | 11.1938 | 57.3937 | 79.09% | 34 | 2 | 83.3% | 78.37% | 0 | 0.2019 | 1 | 3.3081 | 0.6679 | High | High | High | 994 | 1055 | 0.2019
MORGAN HILL 2111XR398 | MORGAN HILL 2111 | SAN JOSE | 36.8919 | 62.4019 | 77.2% | 15 | 15 | 93.25% | 35.33% | 1 | 0.2433 | 1 | 2.7433 | 0.66742 | High | High | Medium | 995 | 1010 | 0.2433
BIG BASIN 110195690 | BIG BASIN 1101 | CENTRAL COAST | 3.9003 | 22.8227 | 33.75% | 15 | 4 | 100% | 100% | 0 | 0.19661 | 1 | 3.3684 | 0.66225 | High | High | High | 996 | 1063 | 0.19661
CLOVERDALE 1102672 | CLOVERDALE 1102 | SONOMA | 22.2941 | 69.8865 | 97.84% | 1 | 12 | 98.19% | 94.9% | 0 | 0.3373 | 1 | 1.9575 | 0.66027 | High | High | Low | 997 | 929 | 0.3373
CORRAL 1103CB | CORRAL 1103 | STOCKTON | 5.566 | 15.4342 | 82.99% | 0 | 1 | 19.4% | 0% | 0 | 0.013588 | 14.9507 | 3.2433 | 0.65886 | Low | Low | High | 998 | 1054 | 0.20315
SONOMA 11033052 | SONOMA 1103 | SONOMA | 13.4991 | 28.4052 | 91.89% | 6 | 9 | 83.64% | 100% | 0 | 0.18717 | 1 | 3.517 | 0.65829 | High | High | High | 999 | 1082 | 0.18717
MORGAN HILL 2105CB | MORGAN HILL 2105 | SAN JOSE | 0.38186 | 10 | 60.48% | 0 | 1 | 21.31% | 0% | 0 | 0.0097345 | 19.9979 | 3.3616 | 0.65441 | Low | Low | High | 1000 | 1071 | 0.19467
KESWICK 11019712 | KESWICK 1101 | NORTH VALLEY | 18.8507 | 17.0815 | 97.11% | 2 | 13 | 100% | 100% | 0 | 0.26099 | 1 | 2.4969 | 0.65166 | High | High | Medium | 1001 | 987 | 0.26099
ROB ROY 2104CB | ROB ROY 2104 | CENTRAL COAST | 14.3247 | 30.9167 | 85.32% | 22 | 10 | 100% | 61.11% | 0 | 0.20721 | 1 | 3.1441 | 0.6515 | High | High | High | 1002 | 1046 | 0.20721
SANTA YNEZ 1104Y30 | SANTA YNEZ 1104 | LOS PADRES | 0.89443 | 34.2503 | 70.68% | 0 | 2 | 6.535% | 0% | 0 | 0.010995 | 19.9979 | 2.9545 | 0.64959 | Low | Low | Medium | 1003 | 1032 | 0.21987
LAS GALLINAS A 1105532 | LAS GALLINAS A 1105 | NORTH BAY | 3.6841 | 80.5371 | 66.72% | 3 | 5 | 83.44% | 94.05% | 0 | 0.19645 | 1 | 3.3042 | 0.64912 | High | High | High | 1004 | 1064 | 0.19645
DEL MONTE 21042760 | DEL MONTE 2104 | CENTRAL COAST | 2.7139 | 31.1425 | 17.74% | 0 | 3 | 100% | 0% | 0 | 0.023371 | 11.2183 | 2.4707 | 0.64778 | Medium | Medium | Medium | 1005 | 986 | 0.26219
OAKHURST 110377384 | OAKHURST 1103 | YOSEMITE | 4.7334 | 12.9583 | 82.83% | 5 | 23 | 100% | 100% | 0 | 0.25524 | 1 | 2.5373 | 0.64761 | High | High | Medium | 1006 | 995 | 0.25524
WOODACRE 1102CB | WOODACRE 1102 | NORTH BAY | 12.3335 | 47.7292 | 17.58% | 11 | 6 | 98.44% | 71.03% | 1 | 0.14985 | 1 | 4.2881 | 0.64256 | High | High | High | 1007 | 1147 | 0.14985
HORSESHOE 1101CB | HORSESHOE 1101 | SIERRA | 1.5163 | 10 | 43.57% | 1 | 0 | 28.38% | 0% | 0 | 0.010302 | 14.9507 | 4.1553 | 0.63998 | Low | Low | High | 1008 | 1139 | 0.15402
SAN JOAQUIN #2 1103CB | SAN JOAQUIN #2 1103 | YOSEMITE | 67.7251 | 13.3684 | 94.77% | 0 | 65 | 100% | 13.79% | 0 | 0.44439 | 1 | 1.4392 | 0.63957 | High | High | Low | 1009 | 874 | 0.44439
COARSEGOLD 210210040 | COARSEGOLD 2102 | YOSEMITE | 17.3327 | 15.2245 | 73.22% | 8 | 45 | 100% | 100% | 0 | 0.31716 | 1 | 2.0156 | 0.63929 | High | High | Low | 1010 | 950 | 0.31716
FULTON 11024994 | FULTON 1102 | SONOMA | 1.7055 | 60.2868 | 44.56% | 0 | 1 | 40.25% | 0% | 0 | 0.014488 | 14.9507 | 2.9503 | 0.63906 | Low | Low | Medium | 1011 | 1036 | 0.21661
BIG BASIN 11015028 | BIG BASIN 1101 | CENTRAL COAST | 4.9702 | 16.4741 | 66.18% | 6 | 3 | 100% | 100% | 0 | 0.1889 | 1 | 3.3403 | 0.63099 | High | High | High | 1012 | 1081 | 0.1889
MIWUK 170247143 | MIWUK 1702 | YOSEMITE | 4.8917 | 41.2668 | 100% | 1 | 8 | 100% | 79.87% | 0 | 0.13801 | 1 | 4.5597 | 0.62928 | High | High | High | 1013 | 1174 | 0.13801
SAN RAFAEL 1101310 | SAN RAFAEL 1101 | NORTH BAY | 1.3967 | 10 | 2.818% | 0 | 0 | 39.65% | 0% | 0 | 0.0071371 | 19.9979 | 4.4071 | 0.62902 | Low | Low | High | 1014 | 1159 | 0.14273
WISE 1102 | WISE 1102 | SIERRA | 0.065469 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 11.2183 | 1.9642 | 0.62826 | Medium | Medium | Low | 1015 | 942 | 0.31985
PENRYN 1103660 | PENRYN 1103 | SIERRA | 10.4724 | 10.4096 | 69.5% | 2 | 4 | 53.75% | 0% | 0 | 0.018041 | 14.9507 | 2.329 | 0.62817 | Low | Low | Medium | 1016 | 979 | 0.26972
MIDDLETOWN 1102878 | MIDDLETOWN 1102 | HUMBOLDT | 0.98449 | 64.5076 | 97.38% | 0 | 3 | 16.45% | 0% | 0 | 0.018862 | 11.2183 | 2.9665 | 0.6277 | Low | Low | Medium | 1017 | 1040 | 0.2116
MIWUK 170153038 | MIWUK 1701 | YOSEMITE | 6.638 | 67.6188 | 100% | 3 | 9 | 100% | 100% | 0 | 0.26716 | 1 | 2.3412 | 0.62548 | High | High | Medium | 1018 | 981 | 0.26716
TEMPLETON 2110901690 | TEMPLETON 2110 | LOS PADRES | 36.531 | 44.497 | 99.02% | 7 | 6 | 93.11% | 83.54% | 1 | 0.29843 | 1 | 2.0943 | 0.625 | High | High | Low | 1019 | 962 | 0.29843
RED BLUFF 11051564 | RED BLUFF 1105 | NORTH VALLEY | 1.279 | 15.2296 | 100% | 0 | 0 | 12.04% | 0% | 0 | 0.012441 | 35.3263 | 1.4214 | 0.62469 | Low | Low | Low | 1020 | 877 | 0.43949
SUNOL 1101MR196 | SUNOL 1101 | MISSION | 2.4505 | 75.1937 | 26.76% | 0 | 1 | 18.84% | 0% | 0 | 0.011214 | 35.3263 | 1.5737 | 0.6234 | Low | Low | Low | 1021 | 894 | 0.39615
DUNBAR 11033127 | DUNBAR 1103 | SONOMA | 8.8393 | 48.2541 | 93.29% | 0 | 4 | 91.69% | 100% | 0 | 0.19391 | 1 | 3.2038 | 0.62125 | High | High | High | 1022 | 1074 | 0.19391
CENTERVILLE 11012448 | CENTERVILLE 1101 | NORTH VALLEY | 24.8271 | 10 | 80.77% | 5 | 8 | 100% | 95.09% | 1 | 0.182 | 1 | 3.4115 | 0.62089 | High | High | High | 1023 | 1088 | 0.182
MORAGA 1102CB | MORAGA 1102 | DIABLO | 3.3475 | 12.7577 | 17.22% | 0 | 6 | 36.14% | 35.27% | 0 | 0.015794 | 11.2183 | 3.4911 | 0.61857 | Low | Low | High | 1024 | 1097 | 0.17719
CAMP EVERS 2105CB | CAMP EVERS 2105 | CENTRAL COAST | 8.5381 | 22.2654 | 52.34% | 18 | 3 | 83.09% | 96.05% | 0 | 0.14927 | 1 | 4.1373 | 0.61755 | High | High | High | 1025 | 1149 | 0.14927
SONOMA 1105138 | SONOMA 1105 | SONOMA | 0.57477 | 60.5779 | 43.92% | 0 | 0 | 3.3% | 0% | 0 | 0.0098109 | 19.9979 | 3.1352 | 0.61511 | Low | Low | High | 1026 | 1065 | 0.1962
SAN RAMON 2101CB | SAN RAMON 2101 | MISSION | 0.57317 | 10 | 0% | 0 | 0 | 53.42% | 0% | 0 | 0.0079978 | 19.9979 | 3.8395 | 0.61409 | Low | Low | High | 1027 | 1131 | 0.15994
MARTELL 110292172 | MARTELL 1102 | STOCKTON | 1.6199 | 10 | 31.25% | 0 | 0 | 49.18% | 0% | 0 | 0.0099007 | 19.9979 | 3.0995 | 0.61369 | Low | Low | High | 1028 | 1060 | 0.19799
SANTA ROSA A 1104210 | SANTA ROSA A 1104 | SONOMA | 6.8749 | 10 | 33.39% | 9 | 10 | 88.77% | 100% | 0 | 0.17303 | 1 | 3.5409 | 0.61267 | High | High | High | 1029 | 1106 | 0.17303
SHINGLE SPRINGS 2105CB | SHINGLE SPRINGS 2105 | SIERRA | 19.4761 | 21.3342 | 76.42% | 1 | 7 | 100% | 96.24% | 0 | 0.20055 | 1 | 3.0516 | 0.612 | High | High | Medium | 1030 | 1056 | 0.20055
HOPLAND 110180620 | HOPLAND 1101 | HUMBOLDT | 0.61898 | 10 | 82.97% | 0 | 0 | 11.01% | 0% | 0 | 0.010345 | 35.3263 | 1.672 | 0.61103 | Low | Low | Low | 1031 | 913 | 0.36545
IGNACIO 11011264 | IGNACIO 1101 | NORTH BAY | 1.5242 | 13.9644 | 55.83% | 0 | 4 | 38.01% | 4.721% | 0 | 0.016971 | 11.2183 | 3.1948 | 0.60822 | Low | Low | High | 1032 | 1080 | 0.19038
OAKHURST 11035480 | OAKHURST 1103 | YOSEMITE | 17.1484 | 38.4474 | 78.11% | 4 | 31 | 100% | 97.69% | 0 | 0.33517 | 1 | 1.8045 | 0.6048 | High | High | Low | 1033 | 932 | 0.33517
MARIPOSA 210237288 | MARIPOSA 2102 | YOSEMITE | 85.1145 | 35.7142 | 99.54% | 6 | 74 | 100% | 7.812% | 0 | 0.40262 | 1 | 1.5019 | 0.60469 | High | High | Low | 1034 | 891 | 0.40262
PERRY 1101V88 | PERRY 1101 | LOS PADRES | 1.2286 | 10 | 3.935% | 0 | 0 | 39.45% | 0% | 0 | 0.0071884 | 26.5534 | 3.1534 | 0.6019 | Low | Low | High | 1035 | 1079 | 0.19088
CALISTOGA 1101890 | CALISTOGA 1101 | NORTH BAY | 22.5646 | 51.954 | 60.75% | 7 | 3 | 89.13% | 61.5% | 0 | 0.25974 | 1 | 2.3028 | 0.59812 | High | High | Medium | 1036 | 989 | 0.25974
CALISTOGA 110135588 | CALISTOGA 1101 | NORTH BAY | 3.0755 | 87.0174 | 100% | 0 | 0 | 100% | 100% | 0 | 0.24881 | 1 | 2.3966 | 0.59629 | High | High | Medium | 1037 | 1003 | 0.24881
PARADISE 110445674 | PARADISE 1104 | NORTH VALLEY | 5.0463 | 10.402 | 42.33% | 2 | 14 | 100% | 100% | 0 | 0.16095 | 1 | 3.7001 | 0.59555 | High | High | High | 1038 | 1128 | 0.16095
LLAGAS 2101XR244 | LLAGAS 2101 | SAN JOSE | 0.29573 | 10 | 100% | 0 | 1 | 2.088% | 0% | 0 | 0.01111 | 19.9979 | 2.6701 | 0.59322 | Low | Low | Medium | 1039 | 1029 | 0.22217
SAN MIGUEL 1105CB | SAN MIGUEL 1105 | LOS PADRES | 0.96596 | 53.2217 | 100% | 0 | 0 | 9.014% | 0% | 0 | 0.015601 | 19.9979 | 1.882 | 0.58717 | Low | Low | Low | 1040 | 954 | 0.312
SAN LUIS OBISPO 1104V46 | SAN LUIS OBISPO 1104 | LOS PADRES | 18.1965 | 66.1378 | 91.34% | 1 | 13 | 87.31% | 73.08% | 1 | 0.28268 | 1 | 2.0672 | 0.58435 | High | High | Low | 1041 | 969 | 0.28268
DEL MONTE 21029060 | DEL MONTE 2102 | CENTRAL COAST | 0.0023123 | 10 | 0% | 0 | 0 | 0.0258% | 0% | 0 | 0.0046992 | 26.5534 | 4.6351 | 0.57837 | Low | Low | High | 1042 | 1216 | 0.12478
CAMP EVERS 210610718 | CAMP EVERS 2106 | CENTRAL COAST | 8.4743 | 22.3341 | 66.06% | 7 | 3 | 100% | 100% | 0 | 0.17677 | 1 | 3.2715 | 0.57831 | High | High | High | 1043 | 1099 | 0.17677
PAUL SWEET 21065178 | PAUL SWEET 2106 | CENTRAL COAST | 7.3151 | 10 | 46.38% | 7 | 0 | 100% | 100% | 0 | 0.17066 | 1 | 3.3829 | 0.57733 | High | High | High | 1044 | 1109 | 0.17066
KESWICK 11011590 | KESWICK 1101 | NORTH VALLEY | 6.51 | 47.89 | 75.62% | 0 | 1 | 100% | 100% | 0 | 0.15625 | 1 | 3.693 | 0.57701 | High | High | High | 1045 | 1137 | 0.15625
SANTA MARIA 1108M18 | SANTA MARIA 1108 | LOS PADRES | 14.6945 | 77.5423 | 92.38% | 1 | 8 | 82.48% | 56.56% | 1 | 0.21976 | 1 | 2.6052 | 0.57252 | High | High | Medium | 1046 | 1033 | 0.21976
NORTH DUBLIN 2103 | NORTH DUBLIN 2103 | MISSION | 0.0011266 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 11.2183 | 4.0077 | 0.57078 | Low | Low | High | 1047 | 1161 | 0.14242
PENRYN 1103CB | PENRYN 1103 | SIERRA | 2.2673 | 10 | 57.81% | 1 | 1 | 71.12% | 0% | 0 | 0.015799 | 14.9507 | 2.4019 | 0.56734 | Low | Low | Medium | 1048 | 1014 | 0.23621
BRUNSWICK 11062416 | BRUNSWICK 1106 | SIERRA | 28.6672 | 22.1211 | 86.48% | 10 | 9 | 92.26% | 60.33% | 1 | 0.19856 | 1 | 2.8411 | 0.56415 | High | High | Medium | 1049 | 1059 | 0.19856
SAN BENITO 210136912 | SAN BENITO 2101 | CENTRAL COAST | 2.942 | 68.099 | 74.6% | 0 | 1 | 23.25% | 0% | 0 | 0.016483 | 14.9507 | 2.2757 | 0.5608 | Low | Low | Medium | 1050 | 1005 | 0.24643
WOODWARD 2108688294 | WOODWARD 2108 | FRESNO | 0.015135 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 26.5534 | 1.6587 | 0.55916 | Low | Low | Low | 1051 | 930 | 0.3371
BRUNSWICK 11103907 | BRUNSWICK 1110 | SIERRA | 0.89347 | 10 | 0% | 2 | 0 | 100% | 0% | 0 | 0.013031 | 14.9507 | 2.8579 | 0.55681 | Low | Low | Medium | 1052 | 1070 | 0.19483
SARATOGA 1107LC12 | SARATOGA 1107 | DE ANZA | 7.3147 | 36.5682 | 63.55% | 4 | 7 | 100% | 57.8% | 0 | 0.15388 | 1 | 3.6179 | 0.55673 | High | High | High | 1053 | 1141 | 0.15388
OAKLAND X 1104 | OAKLAND X 1104 | EAST BAY | 0.11526 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 4.2748 | 0.55668 | High | High | High | 1054 | 1197 | 0.13022
CAMP EVERS 21055146 | CAMP EVERS 2105 | CENTRAL COAST | 6.0305 | 10 | 32.63% | 11 | 6 | 100% | 100% | 0 | 0.14397 | 1 | 3.8493 | 0.55419 | High | High | High | 1055 | 1157 | 0.14397
CURTIS 17028000 | CURTIS 1702 | YOSEMITE | 14.3249 | 17.4723 | 99.98% | 1 | 11 | 100% | 50.67% | 0 | 0.14933 | 1 | 3.7034 | 0.55303 | High | High | High | 1056 | 1148 | 0.14933
PENRYN 1107CB | PENRYN 1107 | SIERRA | 5.4827 | 14.0733 | 57.47% | 3 | 1 | 34.07% | 0% | 0 | 0.01315 | 14.9507 | 2.8102 | 0.55251 | Low | Low | Medium | 1057 | 1062 | 0.19661
FRUITLAND 11418746 | FRUITLAND 1141 | HUMBOLDT | 0.40721 | 85 | 7.434% | 0 | 0 | 50.57% | 0% | 0 | 0.013725 | 47.6367 | 0.84229 | 0.55071 | Low | Low | Low | 1058 | 804 | 0.65382
PAUL SWEET 2106428102 | PAUL SWEET 2106 | CENTRAL COAST | 11.5695 | 14.0231 | 80.02% | 8 | 3 | 89.09% | 75.97% | 1 | 0.13775 | 1 | 3.9916 | 0.54983 | High | High | High | 1059 | 1176 | 0.13775
VIEJO 22029112 | VIEJO 2202 | CENTRAL COAST | 0.78302 | 10 | 22.17% | 1 | 0 | 23.74% | 0% | 0 | 0.008258 | 14.9507 | 4.4379 | 0.54792 | Low | Low | High | 1060 | 1218 | 0.12346
LLAGAS 2101XR584 | LLAGAS 2101 | SAN JOSE | 1.1341 | 38.093 | 49.38% | 0 | 3 | 12.45% | 0% | 0 | 0.010267 | 19.9979 | 2.6623 | 0.54662 | Low | Low | Medium | 1061 | 1052 | 0.20532
BOLINAS 1101806 | BOLINAS 1101 | NORTH BAY | 3.0453 | 88.6877 | 5.762% | 0 | 3 | 100% | 100% | 0 | 0.14085 | 1 | 3.8778 | 0.54618 | High | High | High | 1062 | 1165 | 0.14085
CLAYTON 2212CB | CLAYTON 2212 | DIABLO | 1.3959 | 28.1061 | 22.31% | 0 | 2 | 11% | 15.16% | 0 | 0.01235 | 11.2183 | 3.9394 | 0.5458 | Low | Low | High | 1063 | 1171 | 0.13855
PLACER 1102CB | PLACER 1102 | SIERRA | 2.1407 | 10 | 18.98% | 0 | 1 | 100% | 0% | 0 | 0.015126 | 11.2183 | 3.2057 | 0.54396 | Low | Low | High | 1064 | 1111 | 0.16968
PLACERVILLE 21069712 | PLACERVILLE 2106 | SIERRA | 24.7737 | 54.0303 | 80.14% | 10 | 4 | 100% | 89.29% | 1 | 0.25885 | 1 | 2.0967 | 0.54273 | High | High | Low | 1065 | 992 | 0.25885
SILVERADO 2104708 | SILVERADO 2104 | NORTH BAY | 4.377 | 40.803 | 65.23% | 1 | 8 | 88.72% | 99% | 0 | 0.16025 | 1 | 3.379 | 0.5415 | High | High | High | 1066 | 1130 | 0.16025
PLACERVILLE 210611132 | PLACERVILLE 2106 | SIERRA | 43.1899 | 37.6905 | 78.66% | 11 | 29 | 100% | 66.95% | 0 | 0.3241 | 1 | 1.6694 | 0.54105 | High | High | Low | 1067 | 939 | 0.3241
PENRYN 11072704 | PENRYN 1107 | SIERRA | 1.9532 | 10 | 45.97% | 0 | 0 | 34.19% | 0% | 0 | 0.010983 | 14.9507 | 3.2851 | 0.53943 | Low | Low | High | 1068 | 1123 | 0.1642
GUALALA 11121294 | GUALALA 1112 | HUMBOLDT | 19.9398 | 39.726 | 11.78% | 10 | 62 | 100% | 0% | 0 | 0.24042 | 1 | 2.2212 | 0.53402 | High | High | Low | 1069 | 1012 | 0.24042
PUEBLO 1105716 | PUEBLO 1105 | NORTH BAY | 2.9378 | 34.7126 | 67.65% | 0 | 0 | 14.86% | 0% | 0 | 0.01121 | 14.9507 | 3.18 | 0.53295 | Low | Low | High | 1070 | 1117 | 0.16759
COTATI 11055156 | COTATI 1105 | SONOMA | 3.6981 | 31.1041 | 18.22% | 1 | 1 | 37.15% | 0% | 0 | 0.012279 | 14.9507 | 2.8955 | 0.53156 | Low | Low | Medium | 1071 | 1085 | 0.18358
HARTLEY 1101658 | HARTLEY 1101 | HUMBOLDT | 2.7971 | 52.1185 | 100% | 0 | 1 | 20.57% | 0% | 0 | 0.020197 | 11.2183 | 2.3275 | 0.52735 | Low | Low | Medium | 1072 | 1024 | 0.22658
WYANDOTTE 1109CB | WYANDOTTE 1109 | NORTH VALLEY | 2.5841 | 10 | 31.89% | 0 | 1 | 27.38% | 0% | 0 | 0.0081836 | 14.9507 | 4.3025 | 0.52641 | Low | Low | High | 1073 | 1221 | 0.12235
SEACLIFF 0401CB | SEACLIFF 0401 | CENTRAL COAST | 5.8801 | 16.5923 | 59.63% | 6 | 2 | 97.46% | 83.75% | 0 | 0.13923 | 1 | 3.7795 | 0.52621 | High | High | High | 1074 | 1169 | 0.13923
SAN RAFAEL 11071276 | SAN RAFAEL 1107 | NORTH BAY | 3.842 | 10 | 17.39% | 6 | 6 | 100% | 100% | 0 | 0.12189 | 1 | 4.3125 | 0.52565 | High | High | High | 1075 | 1223 | 0.12189
STAFFORD 110233692 | STAFFORD 1102 | NORTH BAY | 0.31495 | 10 | 16.33% | 0 | 0 | 14.09% | 0% | 0 | 0.0061817 | 26.5534 | 3.2 | 0.52527 | Low | Low | High | 1076 | 1124 | 0.16415
APPLE HILL 21029722 | APPLE HILL 2102 | SIERRA | 38.3357 | 63.3481 | 100% | 10 | 4 | 100% | 82.49% | 1 | 0.36946 | 1 | 1.4151 | 0.52281 | High | High | Low | 1077 | 912 | 0.36946
EMERALD LAKE 0401CB | EMERALD LAKE 0401 | PENINSULA | 15.5314 | 21.1198 | 27.73% | 5 | 20 | 73.41% | 27.29% | 1 | 0.11416 | 1 | 4.5679 | 0.52148 | High | High | High | 1078 | 1241 | 0.11416
CAMP EVERS 21055232 | CAMP EVERS 2105 | CENTRAL COAST | 4.5381 | 18.453 | 49.44% | 6 | 6 | 100% | 100% | 0 | 0.14357 | 1 | 3.6265 | 0.52068 | High | High | High | 1079 | 1158 | 0.14357
COARSEGOLD 210210050 | COARSEGOLD 2102 | YOSEMITE | 7.18 | 18.0295 | 97.64% | 2 | 12 | 100% | 100% | 0 | 0.25905 | 1 | 2.0066 | 0.51979 | High | High | Low | 1080 | 990 | 0.25905
WEST POINT 11021341 | WEST POINT 1102 | STOCKTON | 10.0456 | 74.4483 | 100% | 1 | 5 | 100% | 100% | 0 | 0.33803 | 1 | 1.5377 | 0.51978 | High | High | Low | 1081 | 927 | 0.33803
COTATI 110475972 | COTATI 1104 | SONOMA | 2.7371 | 10 | 35.68% | 0 | 3 | 41.48% | 0% | 0 | 0.015037 | 11.2183 | 3.0719 | 0.51821 | Low | Low | Medium | 1082 | 1115 | 0.1687
ATASCADERO 1103A88 | ATASCADERO 1103 | LOS PADRES | 0.25306 | 10 | 42.36% | 0 | 0 | 9.428% | 0% | 0 | 0.0073051 | 26.5534 | 2.6184 | 0.50791 | Low | Low | Medium | 1083 | 1073 | 0.19397
SAN LUIS OBISPO 1107V60 | SAN LUIS OBISPO 1107 | LOS PADRES | 16.0455 | 59.2942 | 63.57% | 4 | 4 | 100% | 91.12% | 0 | 0.23106 | 1 | 2.1951 | 0.5072 | High | High | Low | 1084 | 1021 | 0.23106
COTTONWOOD 11011510 | COTTONWOOD 1101 | NORTH VALLEY | 0.7279 | 10 | 33.06% | 0 | 0 | 21.95% | 0% | 0 | 0.0076675 | 35.3263 | 1.8603 | 0.5039 | Low | Low | Low | 1085 | 976 | 0.27086
WYANDOTTE 11031508 | WYANDOTTE 1103 | NORTH VALLEY | 25.7036 | 27.6675 | 92.16% | 3 | 8 | 99.06% | 81.42% | 1 | 0.17558 | 1 | 2.8465 | 0.49977 | High | High | Medium | 1086 | 1101 | 0.17558
MORGAN HILL 210542348 | MORGAN HILL 2105 | SAN JOSE | 1.0024 | 17.5681 | 55.95% | 0 | 0 | 23.75% | 0% | 0 | 0.0099083 | 14.9507 | 3.3198 | 0.49179 | Low | Low | High | 1087 | 1151 | 0.14814
BIG BASIN 1102CB | BIG BASIN 1102 | CENTRAL COAST | 6.2676 | 51.463 | 36.35% | 17 | 4 | 100% | 100% | 0 | 0.19295 | 1 | 2.5476 | 0.49156 | High | High | Medium | 1088 | 1076 | 0.19295
CALISTOGA 110266730 | CALISTOGA 1102 | NORTH BAY | 1.1709 | 73.9432 | 93.25% | 0 | 0 | 100% | 100% | 0 | 0.17987 | 1 | 2.7269 | 0.49048 | High | High | Medium | 1089 | 1093 | 0.17987
PARADISE 11032534 | PARADISE 1103 | NORTH VALLEY | 4.7177 | 10 | 61.75% | 3 | 6 | 100% | 100% | 0 | 0.12837 | 1 | 3.8138 | 0.48959 | High | High | High | 1090 | 1206 | 0.12837
PLACERVILLE 21066512 | PLACERVILLE 2106 | SIERRA | 20.9994 | 19.5513 | 83.24% | 2 | 9 | 100% | 100% | 0 | 0.25186 | 1 | 1.9426 | 0.48926 | High | High | Low | 1091 | 1000 | 0.25186
OTTER 11017611 | OTTER 1101 | CENTRAL COAST | 4.3976 | 73.491 | 75.26% | 4 | 3 | 100% | 100% | 1 | 0.3205 | 1 | 1.5238 | 0.48836 | High | High | Low | 1092 | 941 | 0.3205
OAKLAND K 1104CR204 | OAKLAND K 1104 | EAST BAY | 3.7332 | 23.8088 | 27.59% | 6 | 1 | 100% | 100% | 0 | 0.11562 | 1 | 4.1768 | 0.48293 | High | High | High | 1093 | 1236 | 0.11562
BIG BEND 1102CB | BIG BEND 1102 | NORTH VALLEY | 17.1238 | 77.0813 | 99.95% | 1 | 3 | 100% | 100% | 0 | 0.22606 | 1 | 2.1303 | 0.48158 | High | High | Low | 1094 | 1025 | 0.22606
BIG BASIN 11025066 | BIG BASIN 1102 | CENTRAL COAST | 14.538 | 30.1342 | 55.77% | 35 | 1 | 100% | 92.59% | 1 | 0.20391 | 1 | 2.3602 | 0.48127 | High | High | Medium | 1095 | 1053 | 0.20391
CALISTOGA 110189150 | CALISTOGA 1101 | NORTH BAY | 9.6361 | 72.7174 | 50.49% | 2 | 3 | 100% | 93.01% | 1 | 0.18208 | 1 | 2.6306 | 0.47897 | High | High | Medium | 1096 | 1087 | 0.18208
HORSESHOE 11011682 | HORSESHOE 1101 | SIERRA | 1.1361 | 10 | 70.68% | 0 | 0 | 11.64% | 0% | 0 | 0.010746 | 11.2183 | 3.9722 | 0.47887 | Low | Low | High | 1097 | 1224 | 0.12055
PAUL SWEET 210411074 | PAUL SWEET 2104 | CENTRAL COAST | 2.9891 | 10 | 96.78% | 2 | 0 | 97.58% | 100% | 0 | 0.12749 | 1 | 3.7533 | 0.47849 | High | High | High | 1098 | 1209 | 0.12749
LOS GATOS 1106LA42 | LOS GATOS 1106 | DE ANZA | 2.7943 | 10 | 80.03% | 3 | 2 | 100% | 100% | 1 | 0.15252 | 1 | 3.137 | 0.47846 | High | High | High | 1099 | 1143 | 0.15252
PINE GROVE 11013170 | PINE GROVE 1101 | STOCKTON | 40.3025 | 15.3788 | 88.67% | 12 | 21 | 100% | 0% | 0 | 0.18 | 1 | 2.6168 | 0.47101 | High | High | Medium | 1100 | 1092 | 0.18
SAN JOAQUIN #3 1103CB | SAN JOAQUIN #3 1103 | YOSEMITE | 28.2713 | 13.2744 | 82.63% | 4 | 63 | 100% | 35.67% | 0 | 0.37964 | 1 | 1.2383 | 0.47011 | High | High | Low | 1101 | 905 | 0.37964
SAN RAMON 2117CB | SAN RAMON 2117 | MISSION | 0.44721 | 10 | 0% | 0 | 0 | 26.74% | 0% | 0 | 0.0061326 | 19.9979 | 3.8316 | 0.46991 | Low | Low | High | 1102 | 1220 | 0.12264
SAUSALITO 1101CB | SAUSALITO 1101 | NORTH BAY | 0.084384 | 10 | 39.07% | 0 | 0 | 1.452% | 0% | 0 | 0.0074993 | 19.9979 | 3.1293 | 0.4693 | Low | Low | High | 1103 | 1146 | 0.14997
SILVERADO 210234959 | SILVERADO 2102 | NORTH BAY | 24.7275 | 77.6516 | 100% | 5 | 11 | 91.78% | 69.47% | 1 | 0.34288 | 1 | 1.3442 | 0.46089 | High | High | Low | 1104 | 924 | 0.34288
MORGAN HILL 2105XR268 | MORGAN HILL 2105 | SAN JOSE | 7.973 | 60.2912 | 70.21% | 1 | 2 | 100% | 100% | 0 | 0.14861 | 1 | 3.0893 | 0.45909 | High | High | High | 1105 | 1150 | 0.14861
OTTER 1101CB | OTTER 1101 | CENTRAL COAST | 6.5139 | 35.3423 | 0.6325% | 8 | 1 | 96.47% | 87.12% | 1 | 0.20943 | 1 | 2.1919 | 0.45904 | High | High | Low | 1106 | 1042 | 0.20943
COARSEGOLD 21025380 | COARSEGOLD 2102 | YOSEMITE | 14.1287 | 13.3143 | 99.57% | 3 | 25 | 100% | 100% | 0 | 0.23471 | 1 | 1.9542 | 0.45867 | High | High | Low | 1107 | 1016 | 0.23471
GOLDTREE 1105CB | GOLDTREE 1105 | LOS PADRES | 7.0823 | 62.297 | 33.11% | 0 | 1 | 49.12% | 0% | 0 | 0.014604 | 11.2183 | 2.7587 | 0.45198 | Low | Low | Medium | 1108 | 1125 | 0.16384
RED BLUFF 110176020 | RED BLUFF 1101 | NORTH VALLEY | 8.959 | 16.3023 | 99.96% | 0 | 1 | 62.16% | 0% | 0 | 0.020958 | 14.9507 | 1.44 | 0.45121 | Low | Low | Low | 1109 | 953 | 0.31334
CAMP EVERS 210637210 | CAMP EVERS 2106 | CENTRAL COAST | 6.3592 | 23.8928 | 45.59% | 8 | 2 | 100% | 100% | 0 | 0.15389 | 1 | 2.9227 | 0.44978 | High | High | Medium | 1110 | 1140 | 0.15389
SAN RAFAEL 11081262 | SAN RAFAEL 1108 | NORTH BAY | 4.0586 | 23.1286 | 14.29% | 3 | 8 | 91.28% | 100% | 0 | 0.094261 | 1 | 4.7701 | 0.44963 | High | High | High | 1111 | 1317 | 0.094261
CENTERVILLE 1101 | CENTERVILLE 1101 | NORTH VALLEY | 0.0017292 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 3.4526 | 0.44961 | High | High | High | 1112 | 1197 | 0.13022
WILLITS 1103964 | WILLITS 1103 | HUMBOLDT | 2.7651 | 34.3373 | 95.61% | 0 | 1 | 51.42% | 0% | 0 | 0.02055 | 11.2183 | 1.9496 | 0.44946 | Low | Low | Low | 1113 | 1023 | 0.23053
SONOMA 1102118 | SONOMA 1102 | SONOMA | 5.4359 | 22.1228 | 81.08% | 2 | 7 | 71.73% | 100% | 0 | 0.11084 | 1 | 4.0423 | 0.44806 | High | High | High | 1114 | 1256 | 0.11084
TASSAJARA 2113MR276 | TASSAJARA 2113 | DIABLO | 3.6023 | 62.8969 | 34.15% | 1 | 2 | 92.48% | 100% | 0 | 0.13782 | 1 | 3.251 | 0.44804 | High | High | High | 1115 | 1175 | 0.13782
PLACERVILLE 210619552 | PLACERVILLE 2106 | SIERRA | 21.1288 | 10.9472 | 81.54% | 2 | 6 | 100% | 88.4% | 1 | 0.17549 | 1 | 2.5401 | 0.44577 | High | High | Medium | 1116 | 1102 | 0.17549
REDBUD 11022013 | REDBUD 1102 | HUMBOLDT | 0.11285 | 35.1068 | 100% | 0 | 0 | 2.449% | 0% | 0 | 0.01294 | 11.2183 | 3.0608 | 0.44433 | Low | Low | Medium | 1117 | 1156 | 0.14517
TASSAJARA 2112CB | TASSAJARA 2112 | DIABLO | 0.3541 | 10 | 9.426% | 1 | 0 | 26.89% | 0% | 0 | 0.0076765 | 14.9507 | 3.8616 | 0.4432 | Low | Low | High | 1118 | 1238 | 0.11477
DEL MONTE 21043066 | DEL MONTE 2104 | CENTRAL COAST | 0.016196 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 11.2183 | 3.1116 | 0.44316 | Low | Low | High | 1119 | 1161 | 0.14242
NEWBURG 11323425 | NEWBURG 1132 | HUMBOLDT | 0.9717 | 21.9962 | 41.93% | 1 | 0 | 64.08% | 0% | 0 | 0.013757 | 11.2183 | 2.8658 | 0.44227 | Low | Low | Medium | 1120 | 1138 | 0.15433
BIG BASIN 110276752 | BIG BASIN 1102 | CENTRAL COAST | 2.6798 | 26.5426 | 60.49% | 5 | 8 | 100% | 100% | 0 | 0.1665 | 1 | 2.6319 | 0.43821 | High | High | Medium | 1121 | 1120 | 0.1665
WILLOW CREEK 11014904 | WILLOW CREEK 1101 | HUMBOLDT | 18.7302 | 84.4323 | 100% | 25 | 5 | 100% | 99.66% | 0 | 0.33351 | 1 | 1.3113 | 0.43732 | High | High | Low | 1122 | 933 | 0.33351
PARADISE 11032488 | PARADISE 1103 | NORTH VALLEY | 3.2215 | 10 | 53.79% | 1 | 2 | 100% | 95.34% | 0 | 0.11569 | 1 | 3.766 | 0.43568 | High | High | High | 1123 | 1234 | 0.11569
NARROWS 210248484 | NARROWS 2102 | SIERRA | 41.4937 | 26.7261 | 86.16% | 7 | 18 | 100% | 0% | 0 | 0.16958 | 1 | 2.5572 | 0.43366 | High | High | Medium | 1124 | 1112 | 0.16958
MORAGA 1101CB | MORAGA 1101 | DIABLO | 6.145 | 55.6277 | 5.196% | 2 | 13 | 81.97% | 88.05% | 0 | 0.12886 | 1 | 3.3628 | 0.43333 | High | High | High | 1125 | 1203 | 0.12886
VIEJO 22029118 | VIEJO 2202 | CENTRAL COAST | 0.57077 | 10 | 0.8969% | 1 | 0 | 19.02% | 0% | 0 | 0.0066199 | 14.9507 | 4.29 | 0.42459 | Low | Low | High | 1126 | 1298 | 0.098972
MIDDLETOWN 1101612 | MIDDLETOWN 1101 | HUMBOLDT | 3.8703 | 82.8475 | 40.87% | 13 | 3 | 100% | 100% | 1 | 0.19998 | 1 | 2.1199 | 0.42394 | High | High | Low | 1127 | 1057 | 0.19998
GIRVAN 11011636 | GIRVAN 1101 | NORTH VALLEY | 16.6216 | 29.0593 | 66.7% | 0 | 3 | 90.3% | 84.26% | 1 | 0.19797 | 1 | 2.1383 | 0.42331 | High | High | Low | 1128 | 1061 | 0.19797
TIVY VALLEY 110737522 | TIVY VALLEY 1107 | FRESNO | 0.51792 | 52.3595 | 87.8% | 0 | 0 | 16.67% | 0% | 0 | 0.017278 | 11.2183 | 2.1794 | 0.42243 | Low | Low | Low | 1129 | 1075 | 0.19383
REDBUD 11021212 | REDBUD 1102 | HUMBOLDT | 0.436 | 23.3209 | 21.35% | 0 | 1 | 11.49% | 0% | 0 | 0.0070167 | 19.9979 | 3.0081 | 0.42209 | Low | Low | Medium | 1130 | 1167 | 0.14032
GIRVAN 11029012 | GIRVAN 1102 | NORTH VALLEY | 15.986 | 25.3548 | 93.5% | 4 | 4 | 100% | 96.14% | 1 | 0.18146 | 1 | 2.3257 | 0.42202 | High | High | Medium | 1131 | 1090 | 0.18146
HALF MOON BAY 1101CB | HALF MOON BAY 1101 | PENINSULA | 8.298 | 59.005 | 12.7% | 3 | 2 | 59.24% | 75.84% | 1 | 0.11209 | 1 | 3.754 | 0.42078 | High | High | High | 1132 | 1248 | 0.11209
SANTA MARIA 1108M80 | SANTA MARIA 1108 | LOS PADRES | 58.3414 | 79.2858 | 99.51% | 1 | 8 | 100% | 61.18% | 1 | 0.20649 | 1 | 2.0334 | 0.41988 | High | High | Low | 1133 | 1049 | 0.20649
MARIPOSA 21021960 | MARIPOSA 2102 | YOSEMITE | 24.6612 | 47.7521 | 99.87% | 3 | 23 | 100% | 69.1% | 1 | 0.25188 | 1 | 1.666 | 0.41964 | High | High | Low | 1134 | 999 | 0.25188
FROGTOWN 170274648 | FROGTOWN 1702 | STOCKTON | 0.21722 | 10 | 30.03% | 0 | 0 | 4.115% | 0% | 0 | 0.0081651 | 26.5534 | 1.9245 | 0.41726 | Low | Low | Low | 1135 | 1035 | 0.21681
SILVERADO 2102636 | SILVERADO 2102 | NORTH BAY | 3.9682 | 44.4482 | 89.35% | 2 | 0 | 70.53% | 80.46% | 1 | 0.11193 | 1 | 3.6989 | 0.41401 | High | High | High | 1136 | 1249 | 0.11193
BIG BASIN 110296986 | BIG BASIN 1102 | CENTRAL COAST | 5.8731 | 33.0475 | 64.84% | 22 | 1 | 100% | 100% | 0 | 0.16999 | 1 | 2.3974 | 0.40753 | High | High | Medium | 1137 | 1110 | 0.16999
NOTRE DAME 11042028 | NOTRE DAME 1104 | NORTH VALLEY | 10.9017 | 45.9089 | 89% | 0 | 3 | 100% | 100% | 0 | 0.15694 | 1 | 2.5912 | 0.40666 | High | High | Medium | 1138 | 1135 | 0.15694
AUBERRY 1101R319 | AUBERRY 1101 | FRESNO | 21.0846 | 48.2226 | 98.48% | 8 | 8 | 100% | 93.05% | 1 | 0.30543 | 1 | 1.3298 | 0.40617 | High | High | Low | 1139 | 959 | 0.30543
BIG BASIN 11028403 | BIG BASIN 1102 | CENTRAL COAST | 4.9235 | 33.659 | 85.64% | 2 | 1 | 100% | 100% | 0 | 0.15781 | 1 | 2.5682 | 0.40531 | High | High | Medium | 1140 | 1133 | 0.15781
OREGON TRAIL 110335002 | OREGON TRAIL 1103 | NORTH VALLEY | 57.2663 | 26.028 | 93.47% | 4 | 13 | 100% | 0% | 0 | 0.19614 | 1 | 2.0644 | 0.40491 | High | High | Low | 1141 | 1066 | 0.19614
CAMP EVERS 210612840 | CAMP EVERS 2106 | CENTRAL COAST | 4.0602 | 32.5066 | 59.36% | 5 | 0 | 100% | 100% | 0 | 0.13232 | 1 | 3.057 | 0.40448 | High | High | Medium | 1142 | 1191 | 0.13232
GREEN VALLEY 21011645 | GREEN VALLEY 2101 | CENTRAL COAST | 0.48374 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 3.1056 | 0.40442 | High | High | High | 1143 | 1197 | 0.13022
CLARKSVILLE 210319572 | CLARKSVILLE 2103 | SIERRA | 33.5123 | 41.8595 | 99.97% | 3 | 7 | 77.35% | 59.23% | 1 | 0.15209 | 1 | 2.6524 | 0.40341 | High | High | Medium | 1144 | 1144 | 0.15209
CAMP EVERS 210310946 | CAMP EVERS 2103 | CENTRAL COAST | 5.6138 | 10 | 43.31% | 5 | 3 | 66.4% | 100% | 0 | 0.14518 | 1 | 2.7721 | 0.40244 | High | High | Medium | 1145 | 1155 | 0.14518
VIEJO 22019704 | VIEJO 2201 | CENTRAL COAST | 1.0374 | 10 | 50.89% | 1 | 2 | 40.52% | 0% | 0 | 0.011266 | 11.2183 | 3.1826 | 0.40224 | Low | Low | High | 1146 | 1212 | 0.12638
PARADISE 11042034 | PARADISE 1104 | NORTH VALLEY | 10.6989 | 15.2166 | 88.93% | 0 | 6 | 94.14% | 86.31% | 1 | 0.10808 | 1 | 3.7081 | 0.40077 | High | High | High | 1147 | 1265 | 0.10808
SUNOL 1101MR299 | SUNOL 1101 | MISSION | 4.988 | 63.7936 | 27.4% | 3 | 3 | 100% | 100% | 0 | 0.16428 | 1 | 2.4384 | 0.40057 | High | High | Medium | 1148 | 1122 | 0.16428
SAN RAFAEL 110839156 | SAN RAFAEL 1108 | NORTH BAY | 3.0298 | 11.0786 | 11.96% | 3 | 10 | 63.16% | 96.57% | 0 | 0.083717 | 1 | 4.762 | 0.39866 | High | High | High | 1149 | 1373 | 0.083717
LOS GATOS 110760092 | LOS GATOS 1107 | DE ANZA | 9.7412 | 27.0068 | 22.28% | 14 | 2 | 100% | 100% | 0 | 0.17816 | 1 | 2.2097 | 0.39367 | High | High | Low | 1150 | 1096 | 0.17816
DUNBAR 110147964 | DUNBAR 1101 | SONOMA | 6.3806 | 61.1795 | 83.1% | 1 | 6 | 83.19% | 93% | 0 | 0.13803 | 1 | 2.8326 | 0.39097 | High | High | Medium | 1151 | 1173 | 0.13803
PLACERVILLE 21067522 | PLACERVILLE 2106 | SIERRA | 67.5844 | 32.7125 | 84.62% | 19 | 16 | 100% | 11.4% | 0 | 0.1992 | 1 | 1.9612 | 0.39066 | High | High | Low | 1152 | 1058 | 0.1992
CLARKSVILLE 2105CB | CLARKSVILLE 2105 | SIERRA | 0.54433 | 10 | 0% | 0 | 0 | 45.8% | 0% | 0 | 0.0074141 | 14.9507 | 3.5177 | 0.38992 | Low | Low | High | 1153 | 1255 | 0.11085
ZACA 1102Y54 | ZACA 1102 | LOS PADRES | 34.3968 | 50.4695 | 82.24% | 0 | 23 | 99.37% | 51.02% | 1 | 0.23948 | 1 | 1.6279 | 0.38985 | High | High | Low | 1154 | 1013 | 0.23948
DOBBINS 11011264 | DOBBINS 1101 | SIERRA | 34.6636 | 46.9951 | 96.43% | 5 | 9 | 99.16% | 60.09% | 0 | 0.17584 | 1 | 2.216 | 0.38966 | High | High | Low | 1155 | 1100 | 0.17584
PLACERVILLE 210619732 | PLACERVILLE 2106 | SIERRA | 9.0659 | 10 | 43.47% | 3 | 13 | 100% | 82.12% | 1 | 0.12525 | 1 | 3.1037 | 0.38874 | High | High | High | 1156 | 1213 | 0.12525
MONTE RIO 11131067 | MONTE RIO 1113 | SONOMA | 0.80536 | 36.8006 | 36.57% | 2 | 0 | 100% | 100% | 0 | 0.12505 | 1 | 3.1062 | 0.38843 | High | High | High | 1157 | 1214 | 0.12505
FELTON 0401CB | FELTON 0401 | CENTRAL COAST | 2.2987 | 17.6192 | 4.577% | 5 | 0 | 89.41% | 100% | 0 | 0.093336 | 1 | 4.1567 | 0.38797 | High | High | High | 1158 | 1321 | 0.093336
MONROE 210392868 | MONROE 2103 | SONOMA | 0.69734 | 10 | 73.35% | 0 | 3 | 74% | 100% | 0 | 0.11412 | 1 | 3.3766 | 0.38534 | High | High | High | 1159 | 1242 | 0.11412
VINEYARD 2107MR332 | VINEYARD 2107 | MISSION | 0.086505 | 10 | 100% | 1 | 0 | 2.473% | 0% | 0 | 0.011067 | 11.2183 | 3.0685 | 0.38096 | Low | Low | Medium | 1160 | 1217 | 0.12415
OAKLAND K 1103CR188 | OAKLAND K 1103 | EAST BAY | 3.5811 | 10 | 48.05% | 3 | 7 | 100% | 62.42% | 0 | 0.086851 | 1 | 4.3746 | 0.37994 | High | High | High | 1161 | 1352 | 0.086851
REDBUD 1101454 | REDBUD 1101 | HUMBOLDT | 5.6455 | 80.3546 | 100% | 0 | 0 | 100% | 100% | 0 | 0.19502 | 1 | 1.9323 | 0.37684 | High | High | Low | 1162 | 1068 | 0.19502
PAUL SWEET 21068091 | PAUL SWEET 2106 | CENTRAL COAST | 6.0187 | 18.6502 | 32.26% | 14 | 1 | 100% | 100% | 0 | 0.12726 | 1 | 2.9537 | 0.37589 | High | High | Medium | 1163 | 1210 | 0.12726
ARBUCKLE 110447282 | ARBUCKLE 1104 | SACRAMENTO | 2.0417 | 83.3119 | 73.53% | 0 | 0 | 17.21% | 0% | 0 | 0.016706 | 14.9507 | 1.4871 | 0.37144 | Low | Low | Low | 1164 | 1002 | 0.24977
CLAYTON 2215CB | CLAYTON 2215 | DIABLO | 2.6028 | 67.9246 | 0.2184% | 0 | 2 | 23.77% | 0% | 0 | 0.0092153 | 11.2183 | 3.5872 | 0.37085 | Low | Low | High | 1165 | 1283 | 0.10338
CAMP EVERS 210611006 | CAMP EVERS 2106 | CENTRAL COAST | 2.073 | 10 | 22.12% | 2 | 1 | 100% | 100% | 0 | 0.086223 | 1 | 4.2738 | 0.3685 | High | High | High | 1166 | 1357 | 0.086223
ALTO 1124428 | ALTO 1124 | NORTH BAY | 4.8403 | 17.2865 | 1.418% | 0 | 4 | 81.37% | 100% | 0 | 0.075976 | 1 | 4.8386 | 0.36762 | High | High | High | 1167 | 1434 | 0.075976
PUEBLO 1104 | PUEBLO 1104 | NORTH BAY | 0.072037 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 11.2183 | 2.568 | 0.36574 | Low | Low | Medium | 1168 | 1161 | 0.14242
TAMARACK 1101CB | TAMARACK 1101 | SIERRA | 16.4477 | 32.6722 | 67.46% | 23 | 13 | 91.62% | 0% | 0 | 0.38292 | 1 | 0.95136 | 0.36429 | High | High | Low | 1169 | 903 | 0.38292
CLAYTON 2212Y504R | CLAYTON 2212 | DIABLO | 11.7508 | 28.9647 | 42.97% | 1 | 6 | 100% | 29.53% | 1 | 0.10152 | 1 | 3.5819 | 0.36362 | High | High | High | 1170 | 1289 | 0.10152
SAN LUIS OBISPO 1108V92 | SAN LUIS OBISPO 1108 | LOS PADRES | 0.46755 | 10 | 74.28% | 0 | 0 | 6.559% | 0% | 0 | 0.0092193 | 11.2183 | 3.5147 | 0.36351 | Low | Low | High | 1171 | 1282 | 0.10343
BIG BEND 1101641808 | BIG BEND 1101 | NORTH VALLEY | 24.9976 | 36.2263 | 100% | 6 | 10 | 95.85% | 52.55% | 1 | 0.15307 | 1 | 2.3707 | 0.36288 | High | High | Medium | 1172 | 1142 | 0.15307
PARADISE 11032486 | PARADISE 1103 | NORTH VALLEY | 6.2013 | 10 | 48.71% | 9 | 1 | 91.06% | 100% | 0 | 0.093491 | 1 | 3.8754 | 0.36232 | High | High | High | 1173 | 1320 | 0.093491
BIG RIVER 1101952 | BIG RIVER 1101 | HUMBOLDT | 16.8032 | 42.8498 | 13.29% | 16 | 25 | 100% | 0% | 0 | 0.19578 | 1 | 1.848 | 0.36179 | High | High | Low | 1174 | 1067 | 0.19578
MIRABEL 110257840 | MIRABEL 1102 | SONOMA | 2.5892 | 51.5846 | 26.12% | 5 | 1 | 100% | 100% | 0 | 0.11884 | 1 | 3.0442 | 0.36177 | High | High | Medium | 1175 | 1227 | 0.11884
CLARKSVILLE 2110CB | CLARKSVILLE 2110 | SIERRA | 0.17765 | 10 | 0% | 0 | 0 | 9.133% | 0% | 0 | 0.005146 | 19.9979 | 3.4965 | 0.35982 | Low | Low | High | 1176 | 1286 | 0.10291
CLOVERDALE 1102 | CLOVERDALE 1102 | SONOMA | 0.015567 | 90 | 100% | 0 | 0 | 100% | 100% | 0 | 0.20559 | 1 | 1.7488 | 0.35954 | High | High | Low | 1177 | 1050 | 0.20559
CENTERVILLE 11011243 | CENTERVILLE 1101 | NORTH VALLEY | 5.1549 | 10 | 65.95% | 0 | 5 | 100% | 100% | 0 | 0.11154 | 1 | 3.2195 | 0.35911 | High | High | High | 1178 | 1251 | 0.11154
STANISLAUS 17017144 | STANISLAUS 1701 | YOSEMITE | 4.4552 | 18.8557 | 79.41% | 0 | 8 | 100% | 0% | 0 | 0.10581 | 1 | 3.3929 | 0.359 | High | High | High | 1179 | 1271 | 0.10581
OLEMA 1101416 | OLEMA 1101 | NORTH BAY | 15.842 | 82.0626 | 5.587% | 9 | 6 | 97.77% | 72.25% | 1 | 0.13235 | 1 | 2.6915 | 0.35623 | High | High | Medium | 1180 | 1190 | 0.13235
MARIPOSA 210237282 | MARIPOSA 2102 | YOSEMITE | 48.8925 | 28.6255 | 92.59% | 4 | 51 | 82.09% | 39.78% | 0 | 0.20818 | 1 | 1.7072 | 0.35541 | High | High | Low | 1181 | 1044 | 0.20818
MONTE RIO 11135026 | MONTE RIO 1113 | SONOMA | 1.8374 | 45.7535 | 31.21% | 4 | 1 | 100% | 100% | 0 | 0.1045 | 1 | 3.3938 | 0.35465 | High | High | High | 1182 | 1277 | 0.1045
BELL 1107CB | BELL 1107 | SIERRA | 0.084936 | 10 | 100% | 0 | 1 | 2.211% | 0% | 0 | 0.011123 | 11.2183 | 2.8137 | 0.35111 | Low | Low | Medium | 1183 | 1215 | 0.12478
PUEBLO 210378504 | PUEBLO 2103 | NORTH BAY | 7.9718 | 44.4313 | 84.9% | 7 | 4 | 65.86% | 87.65% | 1 | 0.11699 | 1 | 3.0008 | 0.35106 | High | High | Medium | 1184 | 1231 | 0.11699
SANTA ROSA A 1107CB | SANTA ROSA A 1107 | SONOMA | 2.9541 | 10 | 71.96% | 6 | 3 | 60.44% | 100% | 0 | 0.095269 | 1 | 3.6663 | 0.34929 | High | High | High | 1185 | 1314 | 0.095269
DUNBAR 1101416 | DUNBAR 1101 | SONOMA | 2.8528 | 67.3035 | 61.83% | 0 | 0 | 84.79% | 100% | 0 | 0.13696 | 1 | 2.5295 | 0.34643 | High | High | Medium | 1186 | 1178 | 0.13696
DOBBINS 110169722 | DOBBINS 1101 | SIERRA | 6.6325 | 10 | 87.38% | 1 | 4 | 100% | 93.4% | 1 | 0.13241 | 1 | 2.5845 | 0.34221 | High | High | Medium | 1187 | 1189 | 0.13241
HIGGINS 11102408 | HIGGINS 1110 | SIERRA | 35.5285 | 10.5577 | 99.97% | 6 | 7 | 100% | 0% | 0 | 0.12315 | 1 | 2.7776 | 0.34207 | High | High | Medium | 1188 | 1219 | 0.12315
FULTON 1107 | FULTON 1107 | SONOMA | 0.4544 | 32.639 | 77.88% | 0 | 1 | 100% | 100% | 1 | 0.14528 | 1 | 2.3437 | 0.34049 | High | High | Medium | 1189 | 1153 | 0.14528
EL CERRITO G 111257953 | EL CERRITO G 1112 | EAST BAY | 0.7567 | 10 | 0% | 0 | 1 | 100% | 100% | 0 | 0.062783 | 1 | 5.378 | 0.33765 | High | High | High | 1190 | 1534 | 0.062783
MIRABEL 1102841 | MIRABEL 1102 | SONOMA | 0.78827 | 21.9552 | 18.73% | 8 | 3 | 100% | 100% | 0 | 0.11386 | 1 | 2.9577 | 0.33677 | High | High | Medium | 1191 | 1243 | 0.11386
BRYANT 0402CB | BRYANT 0402 | DIABLO | 1.2282 | 10 | 3.772% | 0 | 5 | 15.75% | 0% | 0 | 0.0062931 | 14.9507 | 3.572 | 0.33607 | Low | Low | High | 1192 | 1318 | 0.094086
MARIPOSA 2101439030 | MARIPOSA 2101 | YOSEMITE | 19.5499 | 36.6756 | 99.56% | 7 | 29 | 100% | 98.19% | 0 | 0.28602 | 1 | 1.1748 | 0.33603 | High | High | Low | 1193 | 967 | 0.28602
CAMP EVERS 210512590 | CAMP EVERS 2105 | CENTRAL COAST | 4.822 | 13.1146 | 60.2% | 9 | 1 | 87.03% | 85.9% | 0 | 0.091772 | 1 | 3.6609 | 0.33597 | High | High | High | 1194 | 1327 | 0.091772
ALTO 11252243 | ALTO 1125 | NORTH BAY | 2.9262 | 21.9292 | 59.4% | 1 | 4 | 100% | 22.94% | 0 | 0.085029 | 1 | 3.926 | 0.33382 | High | High | High | 1195 | 1363 | 0.085029
GABILAN 1101579969 | GABILAN 1101 | CENTRAL COAST | 4.2047 | 48.3297 | 40.21% | 0 | 0 | 62.81% | 0% | 0 | 0.01579 | 11.2183 | 1.8809 | 0.33318 | Low | Low | Low | 1196 | 1098 | 0.17714
SAN JOAQUIN #3 11035100 | SAN JOAQUIN #3 1103 | YOSEMITE | 26.246 | 20.2846 | 88.04% | 8 | 29 | 100% | 82.8% | 0 | 0.25116 | 1 | 1.3193 | 0.33134 | High | High | Low | 1197 | 1001 | 0.25116
HARTLEY 1101471 | HARTLEY 1101 | HUMBOLDT | 0.38585 | 10 | 33.51% | 0 | 1 | 31.01% | 0% | 0 | 0.0085975 | 14.9507 | 2.5669 | 0.32994 | Low | Low | Medium | 1198 | 1205 | 0.12854
SAN RAFAEL 1107CB | SAN RAFAEL 1107 | NORTH BAY | 4.2653 | 10 | 28.65% | 2 | 4 | 53.65% | 97.72% | 0 | 0.077391 | 1 | 4.2548 | 0.32928 | High | High | High | 1199 | 1419 | 0.077391
WILLITS 1103966 | WILLITS 1103 | HUMBOLDT | 1.3235 | 20.8407 | 41.93% | 0 | 1 | 57.92% | 0% | 0 | 0.012942 | 11.2183 | 2.2623 | 0.32845 | Low | Low | Medium | 1200 | 1154 | 0.14519
SHINGLE SPRINGS 211051790 | SHINGLE SPRINGS 2110 | SIERRA | 8.0868 | 16.0955 | 60.72% | 1 | 8 | 93.48% | 72.08% | 0 | 0.10718 | 1 | 3.0513 | 0.32703 | High | High | Medium | 1201 | 1268 | 0.10718
PENNGROVE 1101554 | PENNGROVE 1101 | SONOMA | 0.80578 | 23.6637 | 31.41% | 1 | 1 | 6.241% | 0% | 0 | 0.0073444 | 14.9507 | 2.9765 | 0.32683 | Low | Low | Medium | 1202 | 1260 | 0.1098
HALF MOON BAY 11018902 | HALF MOON BAY 1101 | PENINSULA | 14.8934 | 73.1287 | 41.51% | 11 | 3 | 82.58% | 40.17% | 0 | 0.097706 | 1 | 3.3332 | 0.32568 | High | High | High | 1203 | 1302 | 0.097706
CALPINE 1146CB | CALPINE 1146 | SONOMA | 3.8475 | 90.2876 | 70.72% | 0 | 0 | 100% | 100% | 0 | 0.16919 | 1 | 1.9173 | 0.32438 | High | High | Low | 1204 | 1113 | 0.16919
CENTERVILLE 11012592 | CENTERVILLE 1101 | NORTH VALLEY | 6.3933 | 51.1304 | 7.659% | 2 | 0 | 100% | 100% | 0 | 0.098005 | 1 | 3.2954 | 0.32296 | High | High | High | 1205 | 1301 | 0.098005
DIAMOND SPRINGS 110519910 | DIAMOND SPRINGS 1105 | SIERRA | 20.7681 | 27.6002 | 62.16% | 0 | 7 | 100% | 83.55% | 0 | 0.1574 | 1 | 2.0452 | 0.32192 | High | High | Low | 1206 | 1134 | 0.1574
PASO ROBLES 1104P02 | PASO ROBLES 1104 | LOS PADRES | 0.077403 | 10 | 100% | 0 | 0 | 1.071% | 0% | 0 | 0.010772 | 14.9507 | 1.9918 | 0.32079 | Low | Low | Low | 1207 | 1127 | 0.16105
CLARK ROAD 11022068 | CLARK ROAD 1102 | NORTH VALLEY | 10.7164 | 15.0462 | 99.79% | 0 | 2 | 100% | 90.22% | 1 | 0.13587 | 1 | 2.3575 | 0.32031 | High | High | Medium | 1208 | 1180 | 0.13587
BERKELEY F 1105BR100 | BERKELEY F 1105 | EAST BAY | 0.38346 | 10 | 26.17% | 0 | 2 | 14.66% | 0% | 0 | 0.0070264 | 11.2183 | 4.0468 | 0.31898 | Low | Low | High | 1209 | 1408 | 0.078824
PUEBLO 1105696 | PUEBLO 1105 | NORTH BAY | 20.5418 | 62.3545 | 78.14% | 5 | 4 | 69.81% | 0% | 0 | 0.11569 | 1 | 2.755 | 0.31872 | High | High | Medium | 1210 | 1235 | 0.11569
VACAVILLE 111112342 | VACAVILLE 1111 | SACRAMENTO | 0.015645 | 10 | 0% | 0 | 0 | 1.482% | 0% | 0 | 0.004768 | 19.9979 | 3.3367 | 0.31815 | Low | Low | High | 1211 | 1313 | 0.095349
PARADISE 110317711 | PARADISE 1103 | NORTH VALLEY | 6.5808 | 11.9806 | 85.8% | 3 | 1 | 100% | 51.08% | 0 | 0.087993 | 1 | 3.594 | 0.31625 | High | High | High | 1212 | 1344 | 0.087993
HARRIS 1109700 | HARRIS 1109 | HUMBOLDT | 13.0569 | 19.3799 | 29.7% | 17 | 20 | 44.54% | 0% | 0 | 0.086853 | 1 | 3.6202 | 0.31443 | High | High | High | 1213 | 1351 | 0.086853
PARADISE 110439216 | PARADISE 1104 | NORTH VALLEY | 2.1396 | 10 | 44.98% | 1 | 0 | 59.38% | 100% | 0 | 0.07729 | 1 | 4.0674 | 0.31437 | High | High | High | 1214 | 1420 | 0.07729
LAYTONVILLE 1101518 | LAYTONVILLE 1101 | HUMBOLDT | 1.7269 | 84.7584 | 100% | 0 | 1 | 7.655% | 0% | 0 | 0.02214 | 26.5534 | 0.53271 | 0.31317 | Medium | Medium | Low | 1215 | 827 | 0.58789
MARIPOSA 210110240 | MARIPOSA 2101 | YOSEMITE | 21.4769 | 25.894 | 68.07% | 2 | 22 | 100% | 66.83% | 0 | 0.13718 | 1 | 2.2737 | 0.3119 | High | High | Medium | 1216 | 1177 | 0.13718
SHINGLE SPRINGS 210913322 | SHINGLE SPRINGS 2109 | SIERRA | 41.4342 | 33.754 | 99.99% | 7 | 13 | 100% | 26.15% | 1 | 0.22465 | 1 | 1.3879 | 0.3118 | High | High | Low | 1217 | 1026 | 0.22465
CURTIS 17026008 | CURTIS 1702 | YOSEMITE | 17.4763 | 49.3908 | 89.43% | 4 | 7 | 100% | 47.18% | 0 | 0.095869 | 1 | 3.2494 | 0.31152 | High | High | High | 1218 | 1309 | 0.095869
COARSEGOLD 210210330 | COARSEGOLD 2102 | YOSEMITE | 9.5583 | 29.5023 | 99.75% | 4 | 3 | 100% | 94.16% | 0 | 0.20649 | 1 | 1.5084 | 0.31146 | High | High | Low | 1219 | 1048 | 0.20649
RED BLUFF 1104CB | RED BLUFF 1104 | NORTH VALLEY | 2.0518 | 10 | 96.16% | 0 | 0 | 19.48% | 0% | 0 | 0.012529 | 11.2183 | 2.2135 | 0.31112 | Low | Low | Low | 1220 | 1166 | 0.14056
CLARK ROAD 11022582 | CLARK ROAD 1102 | NORTH VALLEY | 20.3761 | 33.4275 | 100% | 2 | 6 | 97.24% | 8.705% | 1 | 0.10279 | 1 | 3.0257 | 0.311 | High | High | Medium | 1221 | 1287 | 0.10279
CURTIS 17039210 | CURTIS 1703 | YOSEMITE | 23.0078 | 62.9555 | 99.96% | 11 | 7 | 100% | 0% | 0 | 0.11179 | 1 | 2.775 | 0.3102 | High | High | Medium | 1222 | 1250 | 0.11179
LLAGAS 210740407 | LLAGAS 2107 | SAN JOSE | 4.4461 | 62.3794 | 79.11% | 0 | 0 | 69.99% | 65.8% | 1 | 0.080349 | 1 | 3.8574 | 0.30994 | High | High | High | 1223 | 1394 | 0.080349
GRASS VALLEY 11032180 | GRASS VALLEY 1103 | SIERRA | 44.2075 | 22.3739 | 98.77% | 3 | 16 | 100% | 0% | 0 | 0.11816 | 1 | 2.6203 | 0.30961 | High | High | Medium | 1224 | 1228 | 0.11816
BEAR VALLEY 21059560 | BEAR VALLEY 2105 | YOSEMITE | 36.2873 | 45.8774 | 99.97% | 7 | 2 | 100% | 13.33% | 1 | 0.13437 | 1 | 2.3028 | 0.30942 | High | High | Medium | 1225 | 1184 | 0.13437
HALF MOON BAY 110148868 | HALF MOON BAY 1101 | PENINSULA | 1.1515 | 26.9273 | 98.35% | 0 | 1 | 38.91% | 72.96% | 0 | 0.06326 | 1 | 4.8763 | 0.30847 | High | High | High | 1226 | 1529 | 0.06326
SWIFT 2110XR254 | SWIFT 2110 | SAN JOSE | 24.8145 | 55.7178 | 60.2% | 2 | 3 | 100% | 0% | 0 | 0.084233 | 1 | 3.6541 | 0.30779 | High | High | High | 1227 | 1369 | 0.084233
CALPINE 1146400 | CALPINE 1146 | SONOMA | 3.1435 | 89.9771 | 73.48% | 0 | 0 | 100% | 100% | 0 | 0.17211 | 1 | 1.7847 | 0.30717 | High | High | Low | 1228 | 1108 | 0.17211
PARADISE 11032558 | PARADISE 1103 | NORTH VALLEY | 2.3505 | 10 | 33.28% | 3 | 2 | 78.43% | 100% | 0 | 0.079398 | 1 | 3.8466 | 0.30541 | High | High | High | 1229 | 1405 | 0.079398
BOLINAS 110137034 | BOLINAS 1101 | NORTH BAY | 4.5303 | 84.6023 | 6.363% | 1 | 1 | 100% | 94.68% | 0 | 0.098509 | 1 | 3.0991 | 0.30529 | High | High | High | 1230 | 1300 | 0.098509
SANTA ROSA A 110464565 | SANTA ROSA A 1104 | SONOMA | 0.80928 | 10 | 22.53% | 1 | 2 | 100% | 100% | 0 | 0.087105 | 1 | 3.4851 | 0.30357 | High | High | High | 1231 | 1350 | 0.087105
SEACLIFF 040112946 | SEACLIFF 0401 | CENTRAL COAST | 2.6944 | 41.521 | 88.42% | 0 | 1 | 83.31% | 77.78% | 0 | 0.092179 | 1 | 3.282 | 0.30253 | High | High | High | 1232 | 1326 | 0.092179
PARADISE 11042470 | PARADISE 1104 | NORTH VALLEY | 5.1264 | 10.5174 | 41.48% | 3 | 8 | 44.97% | 100% | 0 | 0.069868 | 1 | 4.3221 | 0.30197 | High | High | High | 1233 | 1472 | 0.069868
BANGOR 110182350 | BANGOR 1101 | NORTH VALLEY | 20.6431 | 13.6369 | 91.07% | 2 | 31 | 93.75% | 0% | 0 | 0.091535 | 1 | 3.298 | 0.30188 | High | High | High | 1234 | 1329 | 0.091535
SAN RAFAEL 11079532 | SAN RAFAEL 1107 | NORTH BAY | 0.83024 | 10 | 59.24% | 0 | 0 | 45.34% | 100% | 0 | 0.066016 | 1 | 4.5265 | 0.29882 | High | High | High | 1235 | 1507 | 0.066016
WOODACRE 1101CB | WOODACRE 1101 | NORTH BAY | 2.7386 | 31.1084 | 27.17% | 14 | 8 | 96.75% | 56.15% | 0 | 0.068112 | 1 | 4.3841 | 0.29861 | High | High | High | 1236 | 1484 | 0.068112
CAMP EVERS 210311056 | CAMP EVERS 2103 | CENTRAL COAST | 1.8179 | 16.722 | 18.6% | 7 | 3 | 97.69% | 100% | 0 | 0.083758 | 1 | 3.5617 | 0.29832 | High | High | High | 1237 | 1372 | 0.083758
COARSEGOLD 210210610 | COARSEGOLD 2102 | YOSEMITE | 1.3639 | 10 | 100% | 0 | 1 | 100% | 100% | 0 | 0.13262 | 1 | 2.2478 | 0.29809 | High | High | Medium | 1238 | 1188 | 0.13262
OAKHURST 110110090 | OAKHURST 1101 | YOSEMITE | 44.1093 | 32.6301 | 93.91% | 4 | 19 | 100% | 7.446% | 0 | 0.12831 | 1 | 2.3192 | 0.29759 | High | High | Medium | 1239 | 1208 | 0.12831
SILVERADO 2105616 | SILVERADO 2105 | NORTH BAY | 7.7876 | 45.8077 | 54.02% | 4 | 6 | 42.79% | 95.93% | 0 | 0.097353 | 1 | 3.0537 | 0.29728 | High | High | Medium | 1240 | 1304 | 0.097353
PETALUMA C 1109128 | PETALUMA C 1109 | SONOMA | 20.216 | 67.8419 | 37.87% | 1 | 18 | 85.88% | 0% | 0 | 0.1003 | 1 | 2.9612 | 0.29701 | High | High | Medium | 1241 | 1295 | 0.1003
MORGAN HILL 2105XR176 | MORGAN HILL 2105 | SAN JOSE | 18.5618 | 37.9512 | 61.14% | 2 | 13 | 67.38% | 10.57% | 0 | 0.11466 | 1 | 2.5892 | 0.29688 | High | High | Medium | 1242 | 1240 | 0.11466
BEN LOMOND 040116010 | BEN LOMOND 0401 | CENTRAL COAST | 1.6971 | 10 | 15.35% | 1 | 2 | 100% | 100% | 0 | 0.072945 | 1 | 4.0662 | 0.29661 | High | High | High | 1243 | 1449 | 0.072945
SPRING GAP 1702693441 | SPRING GAP 1702 | YOSEMITE | 4.1995 | 35.8935 | 98.37% | 5 | 2 | 100% | 100% | 0 | 0.27702 | 1 | 1.0588 | 0.2933 | High | High | Low | 1244 | 971 | 0.27702
PUEBLO 11041304 | PUEBLO 1104 | NORTH BAY | 19.9743 | 65.3191 | 45.92% | 2 | 4 | 100% | 0% | 0 | 0.10431 | 1 | 2.809 | 0.29302 | High | High | Medium | 1245 | 1280 | 0.10431
CAMP EVERS 210410442 | CAMP EVERS 2104 | CENTRAL COAST | 5.2532 | 33.0345 | 51.92% | 6 | 3 | 50.36% | 93.05% | 0 | 0.099232 | 1 | 2.9332 | 0.29106 | High | High | Medium | 1246 | 1297 | 0.099232
SAN RAFAEL 11081210 | SAN RAFAEL 1108 | NORTH BAY | 3.0269 | 13.7905 | 14.91% | 3 | 2 | 55.23% | 100% | 0 | 0.064455 | 1 | 4.5091 | 0.29063 | High | High | High | 1247 | 1521 | 0.064455
GREENBRAE 11032371 | GREENBRAE 1103 | NORTH BAY | 0.40055 | 47.8608 | 0% | 1 | 4 | 90.05% | 100% | 0 | 0.078151 | 1 | 3.7079 | 0.28978 | High | High | High | 1248 | 1412 | 0.078151
OAKLAND K 1101CR178 | OAKLAND K 1101 | EAST BAY | 0.32942 | 10 | 9.622% | 0 | 2 | 100% | 100% | 0 | 0.068955 | 1 | 4.1976 | 0.28945 | High | High | High | 1249 | 1478 | 0.068955
SAN LUIS OBISPO 1107V02 | SAN LUIS OBISPO 1107 | LOS PADRES | 17.85 | 46.8397 | 49.77% | 4 | 7 | 97.96% | 39.87% | 0 | 0.12708 | 1 | 2.273 | 0.28886 | High | High | Medium | 1250 | 1211 | 0.12708
SAN LUIS OBISPO 1107V62 | SAN LUIS OBISPO 1107 | LOS PADRES | 6.9341 | 31.5234 | 48.48% | 0 | 11 | 100% | 70.79% | 1 | 0.1315 | 1 | 2.1877 | 0.28768 | High | High | Low | 1251 | 1195 | 0.1315
BIG BASIN 110210254 | BIG BASIN 1102 | CENTRAL COAST | 2.1303 | 79.74 | 23.5% | 0 | 1 | 100% | 100% | 1 | 0.11586 | 1 | 2.4798 | 0.28731 | High | High | Medium | 1252 | 1233 | 0.11586
MIDDLETOWN 1103CB | MIDDLETOWN 1103 | HUMBOLDT | 0.052982 | 70.6148 | 0% | 0 | 0 | 32.86% | 0% | 0 | 0.009835 | 11.2183 | 2.601 | 0.28698 | Low | Low | Medium | 1253 | 1259 | 0.11033
BANGOR 11011958 | BANGOR 1101 | NORTH VALLEY | 33.6731 | 10.1792 | 87.16% | 3 | 30 | 100% | 0% | 0 | 0.10317 | 1 | 2.7724 | 0.28603 | High | High | Medium | 1254 | 1284 | 0.10317
COARSEGOLD 21025722 | COARSEGOLD 2102 | YOSEMITE | 1.9829 | 10 | 100% | 0 | 5 | 100% | 100% | 0 | 0.14258 | 1 | 2.0056 | 0.28595 | High | High | Low | 1255 | 1160 | 0.14258
FITCH MOUNTAIN 1111CB | FITCH MOUNTAIN 1111 | SONOMA | 0.55902 | 10 | 52% | 0 | 0 | 3.182% | 0% | 0 | 0.0074291 | 14.9507 | 2.5563 | 0.28393 | Low | Low | Medium | 1256 | 1254 | 0.11107
OAKLAND K 1104CR206 | OAKLAND K 1104 | EAST BAY | 1.7925 | 10 | 7.751% | 0 | 1 | 100% | 100% | 0 | 0.066653 | 1 | 4.2537 | 0.28352 | High | High | High | 1257 | 1500 | 0.066653
BRUNSWICK 11067099 | BRUNSWICK 1106 | SIERRA | 7.5715 | 32.7231 | 90.35% | 0 | 3 | 100% | 52.26% | 0 | 0.1055 | 1 | 2.6802 | 0.28277 | High | High | Medium | 1258 | 1272 | 0.1055
JESSUP 1103CB | JESSUP 1103 | NORTH VALLEY | 0.3876 | 22.4131 | 79.44% | 0 | 0 | 2.712% | 0% | 0 | 0.010068 | 11.2183 | 2.4954 | 0.28184 | Low | Low | Medium | 1259 | 1246 | 0.11295
PAUL SWEET 21025291 | PAUL SWEET 2102 | CENTRAL COAST | 3.3045 | 10 | 22.71% | 10 | 3 | 77.46% | 100% | 0 | 0.091104 | 1 | 3.0809 | 0.28068 | High | High | High | 1260 | 1334 | 0.091104
MARIPOSA 21029590 | MARIPOSA 2102 | YOSEMITE | 36.36 | 19.6403 | 97.41% | 1 | 52 | 100% | 0% | 0 | 0.13645 | 1 | 2.0449 | 0.27902 | High | High | Low | 1261 | 1179 | 0.13645
BIG BASIN 110212124 | BIG BASIN 1102 | CENTRAL COAST | 4.2617 | 10 | 33.1% | 2 | 2 | 100% | 100% | 0 | 0.1076 | 1 | 2.589 | 0.27858 | High | High | Medium | 1262 | 1267 | 0.1076
OAKHURST 110310570 | OAKHURST 1103 | YOSEMITE | 9.7802 | 19.5863 | 100% | 0 | 5 | 100% | 83.62% | 0 | 0.13448 | 1 | 2.0684 | 0.27817 | High | High | Low | 1263 | 1183 | 0.13448
NARROWS 21022220 | NARROWS 2102 | SIERRA | 27.523 | 12.681 | 87.5% | 7 | 17 | 97.87% | 0% | 0 | 0.084411 | 1 | 3.2946 | 0.2781 | High | High | High | 1264 | 1367 | 0.084411
WEST POINT 1101CB | WEST POINT 1101 | STOCKTON | 4.7054 | 80.5028 | 15.54% | 1 | 1 | 100% | 100% | 0 | 0.11111 | 1 | 2.5021 | 0.27801 | High | High | Medium | 1265 | 1253 | 0.11111
TASSAJARA 2104CB | TASSAJARA 2104 | DIABLO | 0.10747 | 10 | 0% | 0 | 1 | 9.092% | 0% | 0 | 0.0059985 | 11.2183 | 4.1264 | 0.27768 | Low | Low | High | 1266 | 1494 | 0.067293
CURTIS 170510590 | CURTIS 1705 | YOSEMITE | 9.8062 | 25.1511 | 99.51% | 1 | 1 | 100% | 47.11% | 0 | 0.086282 | 1 | 3.2172 | 0.27758 | High | High | High | 1267 | 1355 | 0.086282
PAUL SWEET 2109CB | PAUL SWEET 2109 | CENTRAL COAST | 4.2704 | 10 | 67.66% | 4 | 1 | 34.14% | 43.22% | 0 | 0.068584 | 1 | 4.0374 | 0.2769 | High | High | High | 1268 | 1480 | 0.068584
RIO DELL 1102CB | RIO DELL 1102 | HUMBOLDT | 0.14635 | 60 | 0% | 0 | 0 | 2.061% | 0% | 0 | 0.0067382 | 14.9507 | 2.7458 | 0.27662 | Low | Low | Medium | 1269 | 1292 | 0.10074
CALISTOGA 1102769230 | CALISTOGA 1102 | NORTH BAY | 9.3152 | 56.0979 | 70.25% | 3 | 0 | 54.25% | 96.26% | 0 | 0.10199 | 1 | 2.7108 | 0.27647 | High | High | Medium | 1270 | 1288 | 0.10199
DIAMOND SPRINGS 1103 | DIAMOND SPRINGS 1103 | SIERRA | 0.10469 | 10 | 100% | 0 | 0 | 70.96% | 100% | 0 | 0.10065 | 1 | 2.7444 | 0.27622 | High | High | Medium | 1271 | 1293 | 0.10065
BELLEVUE 1102392 | BELLEVUE 1102 | SONOMA | 0.13708 | 10 | 0% | 0 | 0 | 2.019% | 0% | 0 | 0.0047936 | 19.9979 | 2.8755 | 0.27565 | Low | Low | Medium | 1272 | 1310 | 0.095862
DRUM 11011602 | DRUM 1101 | SIERRA | 16.7313 | 80.5912 | 98.54% | 5 | 3 | 100% | 100% | 0 | 0.44264 | 1 | 0.6215 | 0.2751 | High | High | Low | 1273 | 875 | 0.44264
CURTIS 17039330 | CURTIS 1703 | YOSEMITE | 41.1713 | 48.6933 | 100% | 9 | 13 | 100% | 41.49% | 1 | 0.1783 | 1 | 1.542 | 0.27494 | High | High | Low | 1274 | 1095 | 0.1783
BEN LOMOND 04015400 | BEN LOMOND 0401 | CENTRAL COAST | 0.44316 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 4.4652 | 0.27487 | High | High | High | 1275 | 1542 | 0.061559
OAKLAND X 1104CR101 | OAKLAND X 1104 | EAST BAY | 0.017651 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 4.4296 | 0.27268 | High | High | High | 1276 | 1542 | 0.061559
CAMP EVERS 210694770 | CAMP EVERS 2106 | CENTRAL COAST | 2.6769 | 10 | 36.19% | 10 | 8 | 66.11% | 100% | 0 | 0.09995 | 1 | 2.7268 | 0.27255 | High | High | Medium | 1277 | 1296 | 0.09995
LOS GATOS 1106CB | LOS GATOS 1106 | DE ANZA | 6.7095 | 14.253 | 23.95% | 2 | 3 | 87.56% | 91.62% | 0 | 0.083012 | 1 | 3.283 | 0.27253 | High | High | High | 1278 | 1374 | 0.083012
CAMP EVERS 21067603 | CAMP EVERS 2106 | CENTRAL COAST | 0.9357 | 10 | 57.8% | 0 | 0 | 100% | 100% | 0 | 0.095589 | 1 | 2.8433 | 0.27179 | High | High | Medium | 1279 | 1311 | 0.095589
SAN RAFAEL 11073323 | SAN RAFAEL 1107 | NORTH BAY | 0.13349 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 4.4049 | 0.27117 | High | High | High | 1280 | 1545 | 0.061559
HIGHLANDS 110439458 | HIGHLANDS 1104 | HUMBOLDT | 0.83315 | 10 | 36.61% | 0 | 0 | 15.6% | 0% | 0 | 0.0084597 | 11.2183 | 2.8556 | 0.271 | Low | Low | Medium | 1281 | 1315 | 0.094904
SAN RAFAEL 11081457 | SAN RAFAEL 1108 | NORTH BAY | 0.58979 | 10 | 0% | 0 | 0 | 77.17% | 100% | 0 | 0.056282 | 1 | 4.8134 | 0.27091 | Medium | Medium | High | 1282 | 1611 | 0.056282
OAKLAND K 1101CR346 | OAKLAND K 1101 | EAST BAY | 0.18736 | 10 | 0% | 1 | 2 | 100% | 100% | 0 | 0.064827 | 1 | 4.1726 | 0.2705 | High | High | High | 1283 | 1515 | 0.064827
SCE VEGAS 1701CB | SCE VEGAS 1701 | LOS PADRES | 0.17032 | 10 | 100% | 0 | 0 | 100% | 100% | 0 | 0.13022 | 1 | 2.0729 | 0.26993 | High | High | Low | 1284 | 1197 | 0.13022
CORRAL 11012128 | CORRAL 1101 | STOCKTON | 0.10849 | 55.3351 | 0% | 0 | 0 | 0.5187% | 0% | 0 | 0.0064285 | 14.9507 | 2.8084 | 0.26992 | Low | Low | Medium | 1285 | 1307 | 0.09611
ELECTRA 11022646 | ELECTRA 1102 | STOCKTON | 25.2162 | 27.1707 | 98.11% | 7 | 13 | 100% | 22.04% | 1 | 0.14592 | 1 | 1.8392 | 0.26838 | High | High | Low | 1286 | 1152 | 0.14592
CAMP EVERS 210355638 | CAMP EVERS 2103 | CENTRAL COAST | 1.9801 | 10 | 57.05% | 1 | 0 | 56.59% | 100% | 0 | 0.082558 | 1 | 3.2291 | 0.26659 | High | High | High | 1287 | 1377 | 0.082558
SAN RAFAEL 1107714160 | SAN RAFAEL 1107 | NORTH BAY | 2.7558 | 15.5208 | 10.99% | 0 | 10 | 98.34% | 63.23% | 0 | 0.060966 | 1 | 4.37 | 0.26642 | Medium | Medium | High | 1288 | 1558 | 0.060966
TEMPLETON 2111A66 | TEMPLETON 2111 | LOS PADRES | 33.7371 | 15.0206 | 78.96% | 12 | 6 | 100% | 0.9159% | 0 | 0.091159 | 1 | 2.9193 | 0.26612 | High | High | Medium | 1289 | 1333 | 0.091159
MIRABEL 1102CB | MIRABEL 1102 | SONOMA | 4.5501 | 24.245 | 39.21% | 4 | 11 | 40.5% | 94.81% | 0 | 0.080685 | 1 | 3.2843 | 0.26499 | High | High | High | 1290 | 1392 | 0.080685
GARBERVILLE 11026084 | GARBERVILLE 1102 | HUMBOLDT | 15.3135 | 81.9421 | 99.24% | 23 | 2 | 100% | 0% | 0 | 0.18331 | 1 | 1.4373 | 0.26347 | High | High | Low | 1291 | 1086 | 0.18331
NARROWS 2105CB | NARROWS 2105 | SIERRA | 35.605 | 11.8579 | 78.33% | 4 | 9 | 98.55% | 0% | 0 | 0.094041 | 1 | 2.7962 | 0.26296 | High | High | Medium | 1292 | 1319 | 0.094041
MOUNTAIN QUARRIES 210192474 | MOUNTAIN QUARRIES 2101 | SIERRA | 14.6687 | 46.984 | 70.43% | 1 | 2 | 94.19% | 51.74% | 0 | 0.10478 | 1 | 2.4996 | 0.2619 | High | High | Medium | 1293 | 1276 | 0.10478
CABRILLO 1104Y24 | CABRILLO 1104 | LOS PADRES | 18.0747 | 69.8881 | 25.08% | 0 | 8 | 92.92% | 0% | 0 | 0.080321 | 1 | 3.2604 | 0.26188 | High | High | High | 1294 | 1396 | 0.080321
CAMP EVERS 210611044 | CAMP EVERS 2106 | CENTRAL COAST | 6.5538 | 10.6438 | 23.66% | 12 | 2 | 52.73% | 81.08% | 0 | 0.062668 | 1 | 4.1597 | 0.26068 | High | High | High | 1295 | 1536 | 0.062668
CURTIS 170539256 | CURTIS 1705 | YOSEMITE | 26.4541 | 14.8561 | 72.89% | 2 | 39 | 100% | 0% | 0 | 0.087881 | 1 | 2.9559 | 0.25976 | High | High | Medium | 1296 | 1346 | 0.087881
SUNOL 1101MR298 | SUNOL 1101 | MISSION | 5.4024 | 53.1471 | 44.07% | 1 | 5 | 100% | 100% | 0 | 0.1402 | 1 | 1.8521 | 0.25967 | High | High | Low | 1297 | 1168 | 0.1402
MENLO 1102W80 | MENLO 1102 | PENINSULA | 17.326 | 69.2206 | 62.7% | 1 | 9 | 91.54% | 1.485% | 1 | 0.076689 | 1 | 3.3813 | 0.2593 | High | High | High | 1298 | 1427 | 0.076689
BOLINAS 1101504 | BOLINAS 1101 | NORTH BAY | 6.5349 | 26.1981 | 0% | 2 | 2 | 100% | 100% | 0 | 0.082308 | 1 | 3.1479 | 0.2591 | High | High | High | 1299 | 1380 | 0.082308
ORO FINO 11022236 | ORO FINO 1102 | NORTH VALLEY | 2.5402 | 88.3654 | 18.46% | 0 | 3 | 100% | 100% | 0 | 0.12209 | 1 | 2.1142 | 0.25812 | High | High | Low | 1300 | 1222 | 0.12209
HALSEY 110239104 | HALSEY 1102 | SIERRA | 30.6401 | 10.3566 | 73.57% | 9 | 18 | 100% | 0% | 0 | 0.1288 | 1 | 2.0038 | 0.25809 | High | High | Low | 1301 | 1204 | 0.1288
POINT ARENA 110137426 | POINT ARENA 1101 | HUMBOLDT | 0.081405 | 10 | 0% | 2 | 1 | 1.62% | 0% | 0 | 0.0057167 | 14.9507 | 2.9781 | 0.25453 | Low | Low | Medium | 1302 | 1362 | 0.085468
DIAMOND SPRINGS 11039432 | DIAMOND SPRINGS 1103 | SIERRA | 17.0625 | 19.7634 | 81.43% | 3 | 12 | 84.57% | 8.24% | 1 | 0.093192 | 1 | 2.7267 | 0.2541 | High | High | Medium | 1303 | 1323 | 0.093192
PENRYN 110651674 | PENRYN 1106 | SIERRA | 0.99996 | 10 | 36.11% | 0 | 0 | 8.247% | 0% | 0 | 0.0068595 | 11.2183 | 3.3008 | 0.254 | Low | Low | High | 1304 | 1423 | 0.076952
SAN RAMON 2107CB | SAN RAMON 2107 | MISSION | 0.08762 | 60 | 100% | 0 | 0 | 0.9683% | 100% | 0 | 0.072467 | 1 | 3.5047 | 0.25397 | High | High | High | 1305 | 1455 | 0.072467
HIGGINS 1103CB | HIGGINS 1103 | SIERRA | 27.5586 | 18.1402 | 77.71% | 6 | 7 | 99.3% | 0% | 0 | 0.085581 | 1 | 2.9579 | 0.25314 | High | High | Medium | 1306 | 1361 | 0.085581
MARTELL 110191216 | MARTELL 1101 | STOCKTON | 41.3413 | 10.8803 | 100% | 3 | 13 | 100% | 0% | 0 | 0.10514 | 1 | 2.4019 | 0.25253 | High | High | Medium | 1307 | 1275 | 0.10514
NEWBURG 11322074 | NEWBURG 1132 | HUMBOLDT | 1.2262 | 10 | 0% | 0 | 0 | 11.58% | 0% | 0 | 0.0060224 | 14.9507 | 2.7999 | 0.2521 | Low | Low | Medium | 1308 | 1337 | 0.090039
HOOPA 110182542 | HOOPA 1101 | HUMBOLDT | 9.9783 | 60.316 | 90.42% | 13 | 6 | 65.67% | 0% | 0 | 0.10839 | 1 | 2.3143 | 0.25085 | High | High | Medium | 1309 | 1264 | 0.10839
BIG BASIN 110211062 | BIG BASIN 1102 | CENTRAL COAST | 9.0842 | 63.1207 | 47.86% | 15 | 1 | 100% | 69.62% | 1 | 0.096095 | 1 | 2.6104 | 0.25085 | High | High | Medium | 1310 | 1308 | 0.096095
DIAMOND SPRINGS 11057722 | DIAMOND SPRINGS 1105 | SIERRA | 59.1027 | 30.4266 | 87.61% | 10 | 7 | 94.99% | 35.49% | 0 | 0.11755 | 1 | 2.1264 | 0.24995 | High | High | Low | 1311 | 1230 | 0.11755
ELK 11011272 | ELK 1101 | HUMBOLDT | 22.2131 | 39.0938 | 18.17% | 28 | 27 | 99.76% | 0% | 0 | 0.15006 | 1 | 1.6636 | 0.24963 | High | High | Low | 1312 | 1145 | 0.15006
GOLDTREE 1107CB | GOLDTREE 1107 | LOS PADRES | 1.1277 | 39.1961 | 5.234% | 0 | 0 | 30.84% | 0% | 0 | 0.008131 | 11.2183 | 2.7356 | 0.24953 | Low | Low | Medium | 1313 | 1332 | 0.091216
CALPINE 1144CB | CALPINE 1144 | SONOMA | 26.2964 | 85.7305 | 55.05% | 0 | 0 | 100% | 92.09% | 0 | 0.1323 | 1 | 1.8843 | 0.24929 | High | High | Low | 1314 | 1192 | 0.1323
MARIPOSA 210210880 | MARIPOSA 2102 | YOSEMITE | 39.106 | 24.6164 | 88.93% | 0 | 41 | 98.36% | 24.49% | 0 | 0.13284 | 1 | 1.875 | 0.24909 | High | High | Low | 1315 | 1187 | 0.13284
MORRO BAY 110247584 | MORRO BAY 1102 | LOS PADRES | 8.6089 | 11.2458 | 21.08% | 1 | 2 | 89.3% | 46.55% | 1 | 0.073801 | 1 | 3.3695 | 0.24868 | High | High | High | 1316 | 1447 | 0.073801
SHINGLE SPRINGS 210819762 | SHINGLE SPRINGS 2108 | SIERRA | 4.2221 | 28.8991 | 60.1% | 3 | 6 | 78.12% | 39.2% | 0 | 0.077593 | 1 | 3.1989 | 0.24821 | High | High | High | 1317 | 1416 | 0.077593
SAN RAFAEL 1101CB | SAN RAFAEL 1101 | NORTH BAY | 1.7156 | 10 | 28.81% | 3 | 3 | 39.77% | 100% | 1 | 0.061788 | 1 | 4.0124 | 0.24792 | High | High | High | 1318 | 1541 | 0.061788
PAUL SWEET 210610424 | PAUL SWEET 2106 | CENTRAL COAST | 5.7029 | 19.0788 | 48.59% | 2 | 1 | 80% | 79.15% | 0 | 0.067843 | 1 | 3.6484 | 0.24751 | High | High | High | 1319 | 1489 | 0.067843
PASO ROBLES 11032731 | PASO ROBLES 1103 | LOS PADRES | 1.1994 | 24.9201 | 47.66% | 0 | 0 | 73.66% | 0% | 0 | 0.015948 | 11.2183 | 1.3825 | 0.24735 | Low | Low | Low | 1320 | 1094 | 0.17891
SAN LUIS OBISPO 1107V58 | SAN LUIS OBISPO 1107 | LOS PADRES | 0.84617 | 10 | 0% | 0 | 0 | 37.96% | 0% | 0 | 0.006858 | 11.2183 | 3.2113 | 0.24706 | Low | Low | High | 1321 | 1424 | 0.076935
SANTA ROSA A 110432180 | SANTA ROSA A 1104 | SONOMA | 2.5189 | 19.7323 | 62.59% | 0 | 1 | 99.89% | 67.69% | 0 | 0.074867 | 1 | 3.2925 | 0.2465 | High | High | High | 1322 | 1440 | 0.074867
MONTE RIO 111159046 | MONTE RIO 1111 | SONOMA | 2.6767 | 61.8101 | 0% | 1 | 1 | 70.69% | 0% | 0 | 0.013942 | 11.2183 | 1.5755 | 0.24642 | Low | Low | Low | 1323 | 1136 | 0.15641
PARADISE 11031231 | PARADISE 1103 | NORTH VALLEY | 2.541 | 10 | 17.59% | 3 | 2 | 90.53% | 96.98% | 0 | 0.066519 | 1 | 3.6926 | 0.24563 | High | High | High | 1324 | 1501 | 0.066519
SAN JOAQUIN #3 110110060 | SAN JOAQUIN #3 1101 | YOSEMITE | 6.5306 | 43.2657 | 65.2% | 0 | 4 | 100% | 100% | 0 | 0.133 | 1 | 1.8456 | 0.24547 | High | High | Low | 1325 | 1186 | 0.133
CAMP EVERS 210595050 | CAMP EVERS 2105 | CENTRAL COAST | 0.13882 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.9779 | 0.24488 | High | High | High | 1326 | 1545 | 0.061559
EL CERRITO G 1105BR160 | EL CERRITO G 1105 | EAST BAY | 7.9453 | 33.1195 | 38.34% | 5 | 6 | 69.23% | 42.93% | 0 | 0.059441 | 1 | 4.1032 | 0.2439 | Medium | Medium | High | 1327 | 1571 | 0.059441
SHINGLE SPRINGS 2108CB | SHINGLE SPRINGS 2108 | SIERRA | 1.2634 | 35.9265 | 24.64% | 0 | 1 | 85.58% | 100% | 1 | 0.078196 | 1 | 3.1135 | 0.24347 | High | High | High | 1328 | 1411 | 0.078196
OCEANO 1102CB | OCEANO 1102 | LOS PADRES | 20.8775 | 11.5809 | 41.43% | 7 | 19 | 75.87% | 0% | 0 | 0.081976 | 1 | 2.9691 | 0.2434 | High | High | Medium | 1329 | 1382 | 0.081976
SAN LUIS OBISPO 11042293 | SAN LUIS OBISPO 1104 | LOS PADRES | 9.0237 | 83.3193 | 68.53% | 2 | 1 | 100% | 100% | 0 | 0.16663 | 1 | 1.4572 | 0.24281 | High | High | Low | 1330 | 1119 | 0.16663
NARROWS 21011202 | NARROWS 2101 | SIERRA | 45.5016 | 16.7658 | 94.84% | 2 | 35 | 100% | 0% | 0 | 0.10949 | 1 | 2.2156 | 0.24258 | High | High | Low | 1331 | 1262 | 0.10949
SHINGLE SPRINGS 1103CB | SHINGLE SPRINGS 1103 | SIERRA | 6.5783 | 25.7936 | 79.81% | 1 | 6 | 56.03% | 80.43% | 1 | 0.079857 | 1 | 3.0171 | 0.24094 | High | High | Medium | 1332 | 1400 | 0.079857
GREENBRAE 11031260 | GREENBRAE 1103 | NORTH BAY | 2.3256 | 16.3667 | 42.46% | 2 | 2 | 86.56% | 70.2% | 0 | 0.060164 | 1 | 4.0042 | 0.24091 | Medium | Medium | High | 1333 | 1563 | 0.060164
ALTO 1124CB | ALTO 1124 | NORTH BAY | 3.2561 | 10 | 7.135% | 1 | 6 | 46.3% | 100% | 0 | 0.050654 | 1 | 4.7415 | 0.24018 | Medium | Medium | High | 1334 | 1675 | 0.050654
EL CERRITO G 1112BR178 | EL CERRITO G 1112 | EAST BAY | 1.8955 | 10 | 57.49% | 2 | 1 | 23.53% | 92.74% | 0 | 0.049573 | 1 | 4.8314 | 0.23951 | Medium | Medium | High | 1335 | 1689 | 0.049573
SONOMA 1105404 | SONOMA 1105 | SONOMA | 12.3578 | 22.8821 | 50.06% | 1 | 16 | 68.86% | 37.07% | 0 | 0.072855 | 1 | 3.2835 | 0.23922 | High | High | High | 1336 | 1451 | 0.072855
KESWICK 11011586 | KESWICK 1101 | NORTH VALLEY | 7.6307 | 36.5577 | 16.39% | 0 | 2 | 100% | 100% | 1 | 0.085854 | 1 | 2.7857 | 0.23916 | High | High | Medium | 1337 | 1359 | 0.085854
SAN LUIS OBISPO 1101V12 | SAN LUIS OBISPO 1101 | LOS PADRES | 21.0121 | 75.506 | 48.74% | 1 | 1 | 99.72% | 49% | 1 | 0.10534 | 1 | 2.27 | 0.23913 | High | High | Medium | 1338 | 1273 | 0.10534
MC KEE 1111711900 | MC KEE 1111 | SAN JOSE | 8.3733 | 57.1059 | 68.22% | 0 | 5 | 66.5% | 0% | 0 | 0.059287 | 1 | 4.0165 | 0.23813 | Medium | Medium | High | 1339 | 1575 | 0.059287
PINE GROVE 11023168 | PINE GROVE 1102 | STOCKTON | 30.4079 | 52.9502 | 87.84% | 3 | 16 | 100% | 16.23% | 0 | 0.091596 | 1 | 2.5997 | 0.23812 | High | High | Medium | 1340 | 1328 | 0.091596
CURTIS 17058170 | CURTIS 1705 | YOSEMITE | 7.5122 | 10 | 100% | 1 | 19 | 95.23% | 28.76% | 0 | 0.063226 | 1 | 3.7646 | 0.23802 | High | High | High | 1341 | 1530 | 0.063226
OCEANO 1104Q06 | OCEANO 1104 | LOS PADRES | 12.4604 | 18.1576 | 68.47% | 10 | 12 | 100% | 0% | 0 | 0.07261 | 1 | 3.274 | 0.23772 | High | High | High | 1342 | 1453 | 0.07261
APPLE HILL 11038412 | APPLE HILL 1103 | SIERRA | 20.0804 | 56.3777 | 98.03% | 4 | 10 | 100% | 56.18% | 1 | 0.12834 | 1 | 1.8505 | 0.23749 | High | High | Low | 1343 | 1207 | 0.12834
STELLING 111060080 | STELLING 1110 | DE ANZA | 9.1723 | 64.142 | 26.3% | 6 | 3 | 90.37% | 0% | 0 | 0.074583 | 1 | 3.1821 | 0.23733 | High | High | High | 1344 | 1442 | 0.074583
PAUL SWEET 2106CB | PAUL SWEET 2106 | CENTRAL COAST | 5.2267 | 14.0145 | 33.08% | 1 | 5 | 37.05% | 92.49% | 0 | 0.057775 | 1 | 4.0611 | 0.23463 | Medium | Medium | High | 1345 | 1597 | 0.057775
SAN JOAQUIN #3 110210342 | SAN JOAQUIN #3 1102 | YOSEMITE | 1.8206 | 16.0634 | 100% | 0 | 4 | 100% | 100% | 0 | 0.16247 | 1 | 1.436 | 0.2333 | High | High | Low | 1346 | 1126 | 0.16247
SAN JOAQUIN #3 1101CB | SAN JOAQUIN #3 1101 | YOSEMITE | 5.4085 | 45.9214 | 90.84% | 2 | 3 | 100% | 98.42% | 0 | 0.15907 | 1 | 1.4628 | 0.23269 | High | High | Low | 1347 | 1132 | 0.15907
MONROE 210765424 | MONROE 2107 | SONOMA | 0.75479 | 10 | 100% | 0 | 0 | 14.79% | 100% | 0 | 0.067899 | 1 | 3.4252 | 0.23257 | High | High | High | 1348 | 1486 | 0.067899
BOLINAS 1101CB | BOLINAS 1101 | NORTH BAY | 2.176 | 69.2661 | 1.123% | 3 | 1 | 100% | 77.9% | 0 | 0.077604 | 1 | 2.9867 | 0.23178 | High | High | Medium | 1349 | 1415 | 0.077604
MARIPOSA 210110990 | MARIPOSA 2101 | YOSEMITE | 39.8367 | 17.0819 | 99.94% | 3 | 69 | 100% | 0% | 0 | 0.16909 | 1 | 1.36 | 0.22996 | High | High | Low | 1350 | 1114 | 0.16909
MORGAN HILL 2111XR186 | MORGAN HILL 2111 | SAN JOSE | 0.89677 | 65 | 0% | 0 | 0 | 5.591% | 0% | 0 | 0.0072203 | 11.2183 | 2.834 | 0.22955 | Low | Low | Medium | 1351 | 1390 | 0.080999
SAN RAFAEL 1101494 | SAN RAFAEL 1101 | NORTH BAY | 4.1663 | 10 | 20.21% | 1 | 4 | 47.93% | 100% | 0 | 0.062096 | 1 | 3.6785 | 0.22842 | High | High | High | 1352 | 1538 | 0.062096
FORT BRAGG A 110231304 | FORT BRAGG A 1102 | HUMBOLDT | 21.5206 | 61.6048 | 34.35% | 17 | 8 | 100% | 0% | 0 | 0.094856 | 1 | 2.3985 | 0.22751 | High | High | Medium | 1353 | 1316 | 0.094856
LAKEWOOD 210964992 | LAKEWOOD 2109 | DIABLO | 0.21818 | 10 | 100% | 0 | 0 | 8.548% | 100% | 0 | 0.056493 | 1 | 4.016 | 0.22688 | Medium | Medium | High | 1354 | 1607 | 0.056493
HIGGINS 110332120 | HIGGINS 1103 | SIERRA | 40.5815 | 16.4911 | 85.22% | 7 | 11 | 99.04% | 0% | 0 | 0.076505 | 1 | 2.9612 | 0.22655 | High | High | Medium | 1355 | 1429 | 0.076505
NEWBURG 11313446 | NEWBURG 1131 | HUMBOLDT | 0.24063 | 10 | 0% | 0 | 0 | 2.893% | 0% | 0 | 0.0048356 | 19.9979 | 2.3426 | 0.22653 | Low | Low | Medium | 1356 | 1306 | 0.096701
ALLEGHANY 1101808 | ALLEGHANY 1101 | SIERRA | 6.1403 | 95.663 | 12.49% | 0 | 2 | 100% | 100% | 0 | 0.13475 | 1 | 1.679 | 0.22625 | High | High | Low | 1357 | 1182 | 0.13475
CALAVERAS CEMENT 11014786 | CALAVERAS CEMENT 1101 | STOCKTON | 18.0051 | 18.3515 | 89.75% | 0 | 8 | 100% | 55.25% | 1 | 0.076728 | 1 | 2.9429 | 0.22581 | High | High | Medium | 1358 | 1426 | 0.076728
GREEN VALLEY 210190860 | GREEN VALLEY 2101 | CENTRAL COAST | 3.8052 | 10 | 95.69% | 0 | 0 | 20.73% | 93.04% | 0 | 0.070746 | 1 | 3.19 | 0.22568 | High | High | High | 1359 | 1468 | 0.070746
CASTRO VALLEY 1108 | CASTRO VALLEY 1108 | MISSION | 0.019583 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.6623 | 0.22545 | High | High | High | 1360 | 1545 | 0.061559
LAURELES 11112020 | LAURELES 1111 | CENTRAL COAST | 33.1343 | 48.734 | 70.7% | 2 | 9 | 100% | 9.9% | 1 | 0.11304 | 1 | 1.9922 | 0.2252 | High | High | Low | 1361 | 1245 | 0.11304
KANAKA 1101CB | KANAKA 1101 | NORTH VALLEY | 4.6774 | 55.1611 | 80.24% | 0 | 1 | 100% | 79.67% | 1 | 0.11271 | 1 | 1.9968 | 0.22505 | High | High | Low | 1362 | 1247 | 0.11271
GANSNER 11012006 | GANSNER 1101 | NORTH VALLEY | 17.1959 | 52.9981 | 98.77% | 5 | 5 | 100% | 2.795% | 0 | 0.086274 | 1 | 2.5916 | 0.22359 | High | High | Medium | 1363 | 1356 | 0.086274
SANTA YNEZ 1101Y52 | SANTA YNEZ 1101 | LOS PADRES | 18.8234 | 75.9887 | 74.53% | 0 | 5 | 76.28% | 53.44% | 1 | 0.10447 | 1 | 2.1391 | 0.22348 | High | High | Low | 1364 | 1278 | 0.10447
CENTERVILLE 1101CB | CENTERVILLE 1101 | NORTH VALLEY | 0.015747 | 10 | 0% | 0 | 1 | 100% | 100% | 0 | 0.071117 | 1 | 3.1314 | 0.2227 | High | High | High | 1365 | 1465 | 0.071117
PENRYN 1105CB | PENRYN 1105 | SIERRA | 0.038025 | 10 | 0% | 0 | 0 | 3.678% | 0% | 0 | 0.0048736 | 14.9507 | 3.0534 | 0.22248 | Low | Low | Medium | 1366 | 1450 | 0.072863
HALF MOON BAY 11028848 | HALF MOON BAY 1102 | PENINSULA | 3.8931 | 27.5705 | 29.99% | 4 | 3 | 38.64% | 80.42% | 0 | 0.051782 | 1 | 4.2924 | 0.22227 | Medium | Medium | High | 1367 | 1664 | 0.051782
LUCERNE 110638632 | LUCERNE 1106 | HUMBOLDT | 4.4543 | 54.342 | 100% | 6 | 8 | 95.13% | 0% | 0 | 0.076393 | 1 | 2.9038 | 0.22183 | High | High | Medium | 1368 | 1431 | 0.076393
CASTRO VALLEY 1109MR334 | CASTRO VALLEY 1109 | MISSION | 5.7287 | 41.5825 | 24.73% | 0 | 3 | 90.6% | 49.57% | 0 | 0.052651 | 1 | 4.2098 | 0.22165 | Medium | Medium | High | 1369 | 1653 | 0.052651
CORNING 11021900 | CORNING 1102 | NORTH VALLEY | 0.99921 | 77.9025 | 2.304% | 0 | 2 | 5.388% | 0% | 0 | 0.0083558 | 19.9979 | 1.3171 | 0.22009 | Low | Low | Low | 1370 | 1118 | 0.1671
MORGAN HILL 2111CB | MORGAN HILL 2111 | SAN JOSE | 0.34374 | 10 | 12.74% | 0 | 0 | 12.6% | 0% | 0 | 0.0059141 | 11.2183 | 3.3152 | 0.21995 | Low | Low | High | 1371 | 1504 | 0.066347
ROSSMOOR 1106CB | ROSSMOOR 1106 | DIABLO | 1.4865 | 10 | 68.08% | 0 | 8 | 30.91% | 92.75% | 0 | 0.057048 | 1 | 3.8412 | 0.21913 | Medium | Medium | High | 1372 | 1605 | 0.057048
ATASCADERO 1101A50 | ATASCADERO 1101 | LOS PADRES | 19.8065 | 10 | 78.19% | 4 | 9 | 94.43% | 5.217% | 1 | 0.066857 | 1 | 3.2682 | 0.2185 | High | High | High | 1373 | 1497 | 0.066857
SISQUOC 1103M14 | SISQUOC 1103 | LOS PADRES | 21.2959 | 68.8259 | 69.24% | 0 | 10 | 65.02% | 94.4% | 0 | 0.21174 | 1 | 1.0317 | 0.21846 | High | High | Low | 1374 | 1039 | 0.21174
CALAVERAS CEMENT 110180930 | CALAVERAS CEMENT 1101 | STOCKTON | 18.4785 | 30.1878 | 99.81% | 1 | 6 | 100% | 0% | 0 | 0.089656 | 1 | 2.4362 | 0.21842 | High | High | Medium | 1375 | 1338 | 0.089656
PAUL SWEET 2105CB | PAUL SWEET 2105 | CENTRAL COAST | 8.1216 | 24.934 | 34.71% | 10 | 1 | 52.4% | 90.68% | 0 | 0.064304 | 1 | 3.3844 | 0.21763 | High | High | High | 1376 | 1522 | 0.064304
CLOVERDALE 1102570 | CLOVERDALE 1102 | SONOMA | 17.3117 | 48.3271 | 69.88% | 1 | 6 | 81.35% | 95.94% | 0 | 0.11928 | 1 | 1.824 | 0.21757 | High | High | Low | 1377 | 1226 | 0.11928
CAMP EVERS 210411048 | CAMP EVERS 2104 | CENTRAL COAST | 0.87487 | 10 | 18.94% | 3 | 1 | 63.94% | 100% | 0 | 0.053728 | 1 | 4.0099 | 0.21544 | Medium | Medium | High | 1378 | 1640 | 0.053728
SONOMA 1106CB | SONOMA 1106 | SONOMA | 0.46405 | 10 | 100% | 0 | 0 | 11.88% | 100% | 0 | 0.058298 | 1 | 3.6884 | 0.21503 | Medium | Medium | High | 1379 | 1590 | 0.058298
OAKLAND K 1101CR170 | OAKLAND K 1101 | EAST BAY | 1.2514 | 10 | 10.22% | 0 | 3 | 100% | 84.34% | 0 | 0.055611 | 1 | 3.8581 | 0.21455 | Medium | Medium | High | 1380 | 1616 | 0.055611
SANTA ROSA A 110439786 | SANTA ROSA A 1104 | SONOMA | 1.14 | 10 | 49.93% | 0 | 3 | 16.83% | 100% | 0 | 0.056488 | 1 | 3.7971 | 0.21449 | Medium | Medium | High | 1381 | 1608 | 0.056488
MOUNTAIN QUARRIES 21011102 | MOUNTAIN QUARRIES 2101 | SIERRA | 44.4218 | 34.6112 | 86.6% | 0 | 15 | 100% | 0% | 0 | 0.11033 | 1 | 1.9411 | 0.21417 | High | High | Low | 1382 | 1258 | 0.11033
OREGON TRAIL 11031500 | OREGON TRAIL 1103 | NORTH VALLEY | 24.8639 | 16.6581 | 98.22% | 2 | 4 | 96.57% | 0% | 0 | 0.076799 | 1 | 2.7865 | 0.214 | High | High | Medium | 1383 | 1425 | 0.076799
SOBRANTE 1102L510R | SOBRANTE 1102 | DIABLO | 9.7593 | 10 | 23.81% | 5 | 6 | 100% | 0% | 0 | 0.067265 | 1 | 3.176 | 0.21364 | High | High | High | 1384 | 1495 | 0.067265
ROB ROY 210571630 | ROB ROY 2105 | CENTRAL COAST | 1.807 | 10 | 61.71% | 5 | 2 | 96.47% | 60.73% | 0 | 0.066075 | 1 | 3.2318 | 0.21354 | High | High | High | 1385 | 1506 | 0.066075
SAN RAFAEL 1108CB | SAN RAFAEL 1108 | NORTH BAY | 3.0131 | 10 | 10.73% | 6 | 1 | 40.8% | 100% | 0 | 0.047654 | 1 | 4.4645 | 0.21275 | Medium | Medium | High | 1386 | 1711 | 0.047654
DIAMOND SPRINGS 1103CB | DIAMOND SPRINGS 1103 | SIERRA | 16.7869 | 10 | 71.13% | 6 | 16 | 54.37% | 47.43% | 1 | 0.08564 | 1 | 2.4835 | 0.21268 | High | High | Medium | 1387 | 1360 | 0.08564
OAKLAND D 1112CR192 | OAKLAND D 1112 | EAST BAY | 2.6688 | 25.8444 | 29.93% | 2 | 4 | 64.82% | 77.45% | 0 | 0.054951 | 1 | 3.8636 | 0.21231 | Medium | Medium | High | 1388 | 1626 | 0.054951
AUBERRY 1101R2838 | AUBERRY 1101 | FRESNO | 20.2113 | 19.1577 | 100% | 5 | 21 | 100% | 0% | 0 | 0.10363 | 1 | 2.0481 | 0.21224 | High | High | Low | 1389 | 1281 | 0.10363
PARADISE 1102CB | PARADISE 1102 | NORTH VALLEY | 0.74465 | 10 | 6.716% | 2 | 0 | 53.22% | 100% | 0 | 0.048451 | 1 | 4.3681 | 0.21164 | Medium | Medium | High | 1390 | 1701 | 0.048451
PUEBLO 2102656 | PUEBLO 2102 | NORTH BAY | 0.064775 | 10 | 100% | 0 | 0 | 0.3672% | 100% | 0 | 0.059306 | 1 | 3.5617 | 0.21123 | Medium | Medium | High | 1391 | 1574 | 0.059306
SWIFT 2110XR366 | SWIFT 2110 | SAN JOSE | 8.8402 | 27.8534 | 70.07% | 1 | 1 | 80.04% | 0% | 0 | 0.04663 | 1 | 4.5152 | 0.21055 | Medium | Medium | High | 1392 | 1728 | 0.04663
GRASS VALLEY 11032110 | GRASS VALLEY 1103 | SIERRA | 19.6542 | 17.5047 | 70.11% | 3 | 10 | 97.43% | 0% | 0 | 0.080807 | 1 | 2.6029 | 0.21033 | High | High | Medium | 1393 | 1391 | 0.080807
APPLE HILL 21028372 | APPLE HILL 2102 | SIERRA | 56.1866 | 51.1532 | 100% | 7 | 2 | 89.5% | 31.4% | 1 | 0.11526 | 1 | 1.8245 | 0.2103 | High | High | Low | 1394 | 1237 | 0.11526
BOLINAS 1101528 | BOLINAS 1101 | NORTH BAY | 2.2652 | 10 | 0% | 1 | 5 | 74.53% | 100% | 0 | 0.061356 | 1 | 3.4025 | 0.20876 | Medium | Medium | High | 1395 | 1553 | 0.061356
CLOVERDALE 1102156 | CLOVERDALE 1102 | SONOMA | 6.0801 | 52.6986 | 63.14% | 2 | 11 | 52.14% | 81.66% | 0 | 0.091237 | 1 | 2.2861 | 0.20858 | High | High | Medium | 1396 | 1331 | 0.091237
MILPITAS 1109XR082 | MILPITAS 1109 | SAN JOSE | 19.1832 | 53.2607 | 99.6% | 3 | 3 | 94.55% | 0% | 0 | 0.058023 | 1 | 3.5906 | 0.20834 | Medium | Medium | High | 1397 | 1596 | 0.058023
HICKS 2103LB50 | HICKS 2103 | SAN JOSE | 10.8958 | 72.4633 | 80.45% | 3 | 2 | 82.11% | 27.73% | 0 | 0.058713 | 1 | 3.5349 | 0.20754 | Medium | Medium | High | 1398 | 1583 | 0.058713
CALAVERAS CEMENT 1101502 | CALAVERAS CEMENT 1101 | STOCKTON | 38.3009 | 27.6645 | 90.32% | 2 | 8 | 92.84% | 0% | 0 | 0.10314 | 1 | 2.0117 | 0.20748 | High | High | Low | 1399 | 1285 | 0.10314
STILLWATER 11011320 | STILLWATER 1101 | NORTH VALLEY | 18.8372 | 23.2893 | 80.24% | 9 | 10 | 93.78% | 0% | 0 | 0.10603 | 1 | 1.956 | 0.2074 | High | High | Low | 1400 | 1269 | 0.10603
HALSEY 1101CB | HALSEY 1101 | SIERRA | 17.1561 | 10.5573 | 71.81% | 7 | 24 | 100% | 0% | 0 | 0.08631 | 1 | 2.3966 | 0.20685 | High | High | Medium | 1401 | 1354 | 0.08631
AUBERRY 1102CB | AUBERRY 1102 | FRESNO | 34.5018 | 23.0923 | 82.62% | 0 | 22 | 100% | 0% | 0 | 0.089542 | 1 | 2.3016 | 0.20609 | High | High | Medium | 1402 | 1340 | 0.089542
WILLITS 11032500 | WILLITS 1103 | HUMBOLDT | 29.9853 | 83.8453 | 100% | 11 | 13 | 100% | 0% | 0 | 0.14143 | 1 | 1.453 | 0.20549 | High | High | Low | 1403 | 1164 | 0.14143
SAN BENITO 210488772 | SAN BENITO 2104 | CENTRAL COAST | 23.9825 | 25.5059 | 54.82% | 18 | 5 | 55.63% | 0% | 0 | 0.071687 | 1 | 2.854 | 0.2046 | High | High | Medium | 1404 | 1462 | 0.071687
ALHAMBRA 110582622 | ALHAMBRA 1105 | DIABLO | 25.9018 | 63.5576 | 53.56% | 4 | 18 | 100% | 1.973% | 1 | 0.072547 | 1 | 2.8047 | 0.20347 | High | High | Medium | 1405 | 1454 | 0.072547
PLACERVILLE 111019582 | PLACERVILLE 1110 | SIERRA | 22.4014 | 26.1615 | 63.31% | 2 | 22 | 100% | 0% | 0 | 0.091322 | 1 | 2.2123 | 0.20203 | High | High | Low | 1406 | 1330 | 0.091322
COARSEGOLD 2102383092 | COARSEGOLD 2102 | YOSEMITE | 0.3809 | 10 | 73.97% | 0 | 0 | 100% | 100% | 0 | 0.10776 | 1 | 1.874 | 0.20194 | High | High | Low | 1407 | 1266 | 0.10776
WEST POINT 11021369 | WEST POINT 1102 | STOCKTON | 10.5051 | 72.1066 | 100% | 1 | 0 | 98.44% | 18.78% | 0 | 0.073587 | 1 | 2.7416 | 0.20175 | High | High | Medium | 1408 | 1448 | 0.073587
FROGTOWN 17011623 | FROGTOWN 1701 | STOCKTON | 15.2549 | 27.6688 | 92.79% | 0 | 7 | 100% | 0% | 0 | 0.065843 | 1 | 3.0596 | 0.20145 | High | High | Medium | 1409 | 1508 | 0.065843
CLARKSVILLE 210951744 | CLARKSVILLE 2109 | SIERRA | 0.69986 | 10 | 100% | 0 | 1 | 39% | 87.04% | 0 | 0.062946 | 1 | 3.1987 | 0.20135 | High | High | High | 1410 | 1533 | 0.062946
BOLINAS 1101 | BOLINAS 1101 | NORTH BAY | 0.01843 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.2701 | 0.2013 | High | High | High | 1411 | 1545 | 0.061559
CURTIS 170511790 | CURTIS 1705 | YOSEMITE | 0.014226 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.2679 | 0.20117 | High | High | High | 1412 | 1542 | 0.061559
BIG BASIN 110212779 | BIG BASIN 1102 | CENTRAL COAST | 0.25335 | 10 | 27.94% | 0 | 0 | 100% | 100% | 0 | 0.076303 | 1 | 2.6324 | 0.20086 | High | High | Medium | 1413 | 1432 | 0.076303
KESWICK 1101CB | KESWICK 1101 | NORTH VALLEY | 0.016582 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 3.2562 | 0.20045 | High | High | High | 1414 | 1545 | 0.061559
NOTRE DAME 11042537 | NOTRE DAME 1104 | NORTH VALLEY | 5.2925 | 55.6781 | 100% | 0 | 0 | 100% | 22.56% | 0 | 0.062104 | 1 | 3.2088 | 0.19928 | High | High | High | 1415 | 1537 | 0.062104
SYCAMORE CREEK 11112014 | SYCAMORE CREEK 1111 | NORTH VALLEY | 22.6561 | 53.0217 | 99.04% | 1 | 4 | 99.97% | 25.97% | 0 | 0.069882 | 1 | 2.8512 | 0.19925 | High | High | Medium | 1416 | 1471 | 0.069882
COARSEGOLD 21045300 | COARSEGOLD 2104 | YOSEMITE | 37.3624 | 19.4525 | 89.47% | 1 | 28 | 100% | 0% | 0 | 0.10447 | 1 | 1.9069 | 0.19922 | High | High | Low | 1417 | 1279 | 0.10447
OCEANO 1103221092 | OCEANO 1103 | LOS PADRES | 1.2243 | 45.1389 | 92.5% | 0 | 2 | 95.43% | 0% | 0 | 0.049591 | 1 | 3.9902 | 0.19788 | Medium | Medium | High | 1418 | 1688 | 0.049591
ROB ROY 210410714 | ROB ROY 2104 | CENTRAL COAST | 15.4812 | 20.2777 | 49.42% | 12 | 6 | 79.24% | 0% | 0 | 0.069343 | 1 | 2.8504 | 0.19765 | High | High | Medium | 1419 | 1475 | 0.069343
CURTIS 170234426 | CURTIS 1702 | YOSEMITE | 4.917 | 10 | 82.09% | 0 | 4 | 71.87% | 67.24% | 1 | 0.058493 | 1 | 3.3748 | 0.1974 | Medium | Medium | High | 1420 | 1587 | 0.058493
CURTIS 17036064 | CURTIS 1703 | YOSEMITE | 19.198 | 23.357 | 96.92% | 3 | 15 | 97.54% | 0% | 0 | 0.069239 | 1 | 2.8169 | 0.19504 | High | High | Medium | 1421 | 1476 | 0.069239
AUBERRY 1101R2845 | AUBERRY 1101 | FRESNO | 17.7605 | 28.7565 | 100% | 4 | 13 | 100% | 0% | 0 | 0.10532 | 1 | 1.8477 | 0.19461 | High | High | Low | 1422 | 1274 | 0.10532
VASCO 1102MR176 | VASCO 1102 | MISSION | 38.5569 | 70.5523 | 85.5% | 0 | 7 | 89.92% | 0% | 0 | 0.084198 | 1 | 2.3104 | 0.19454 | High | High | Medium | 1423 | 1370 | 0.084198
NARROWS 21057203 | NARROWS 2105 | SIERRA | 17.8971 | 13.4012 | 99.97% | 2 | 5 | 95.78% | 0% | 0 | 0.077172 | 1 | 2.5133 | 0.19395 | High | High | Medium | 1424 | 1422 | 0.077172
OTTER 1102CB | OTTER 1102 | CENTRAL COAST | 6.6866 | 58.389 | 0% | 3 | 0 | 98.35% | 55.62% | 1 | 0.11663 | 1 | 1.6628 | 0.19393 | High | High | Low | 1425 | 1232 | 0.11663
CASTRO VALLEY 1108MR243 | CASTRO VALLEY 1108 | MISSION | 5.5308 | 36.4789 | 12.29% | 0 | 3 | 99.61% | 62.99% | 0 | 0.054568 | 1 | 3.5499 | 0.19371 | Medium | Medium | High | 1426 | 1632 | 0.054568
SOBRANTE 1103N510R | SOBRANTE 1103 | DIABLO | 0.050894 | 10 | 0% | 1 | 0 | 5.822% | 0% | 0 | 0.0050449 | 11.2183 | 3.422 | 0.19367 | Low | Low | High | 1427 | 1606 | 0.056595
SOBRANTE 1102L520R | SOBRANTE 1102 | DIABLO | 7.4675 | 10 | 48.68% | 1 | 16 | 100% | 8.05% | 0 | 0.05711 | 1 | 3.39 | 0.19361 | Medium | Medium | High | 1428 | 1604 | 0.05711
MOUNTAIN QUARRIES 21011130 | MOUNTAIN QUARRIES 2101 | SIERRA | 20.0304 | 57.0085 | 99.98% | 8 | 6 | 100% | 22.7% | 1 | 0.088009 | 1 | 2.1946 | 0.19314 | High | High | Low | 1429 | 1343 | 0.088009
APPLE HILL 210277546 | APPLE HILL 2102 | SIERRA | 43.2651 | 10.0567 | 100% | 8 | 8 | 100% | 3.986% | 0 | 0.084095 | 1 | 2.293 | 0.19283 | High | High | Medium | 1430 | 1371 | 0.084095
EL CERRITO G 1105CB | EL CERRITO G 1105 | EAST BAY | 7.4165 | 22.6789 | 12.34% | 2 | 5 | 100% | 20.23% | 0 | 0.040319 | 1 | 4.7752 | 0.19253 | Medium | Medium | High | 1431 | 1846 | 0.040319
NARROWS 21052228 | NARROWS 2105 | SIERRA | 20.4861 | 37.6865 | 94.14% | 3 | 11 | 96.44% | 0% | 0 | 0.06797 | 1 | 2.8311 | 0.19243 | High | High | Medium | 1432 | 1485 | 0.06797
COARSEGOLD 210310820 | COARSEGOLD 2103 | YOSEMITE | 28.8124 | 11.1753 | 93.73% | 0 | 47 | 100% | 0% | 0 | 0.07927 | 1 | 2.4251 | 0.19224 | High | High | Medium | 1433 | 1406 | 0.07927
GREEN VALLEY 210112824 | GREEN VALLEY 2101 | CENTRAL COAST | 0.066956 | 70 | 0% | 0 | 0 | 0.5469% | 0% | 0 | 0.007104 | 11.2183 | 2.3989 | 0.19118 | Low | Low | Medium | 1434 | 1401 | 0.079695
CURTIS 170247488 | CURTIS 1702 | YOSEMITE | 18.0809 | 16.9513 | 84.37% | 2 | 17 | 87.6% | 0% | 0 | 0.05643 | 1 | 3.3854 | 0.19104 | Medium | Medium | High | 1435 | 1609 | 0.05643
HOOPA 1101CB | HOOPA 1101 | HUMBOLDT | 15.2475 | 59.0191 | 97.73% | 17 | 6 | 56.28% | 0% | 0 | 0.085954 | 1 | 2.2215 | 0.19095 | High | High | Low | 1436 | 1358 | 0.085954
OAKLAND K 1104CR208 | OAKLAND K 1104 | EAST BAY | 2.4051 | 10 | 34.97% | 0 | 3 | 100% | 39.7% | 0 | 0.0436 | 1 | 4.378 | 0.19088 | Medium | Medium | High | 1437 | 1785 | 0.0436
PAUL SWEET 210710986 | PAUL SWEET 2107 | CENTRAL COAST | 10.6088 | 30.4341 | 52.14% | 3 | 2 | 53.14% | 44.56% | 0 | 0.066361 | 1 | 2.8689 | 0.19038 | High | High | Medium | 1438 | 1503 | 0.066361
ROB ROY 210538430 | ROB ROY 2105 | CENTRAL COAST | 4.0485 | 27.4617 | 42.48% | 11 | 1 | 61.21% | 68.36% | 0 | 0.05425 | 1 | 3.498 | 0.18976 | Medium | Medium | High | 1439 | 1636 | 0.05425
PERRY 1101V78 | PERRY 1101 | LOS PADRES | 29.478 | 56.2687 | 60.85% | 2 | 3 | 100% | 21.68% | 1 | 0.081321 | 1 | 2.3311 | 0.18957 | High | High | Medium | 1440 | 1387 | 0.081321
GREEN VALLEY 210136820 | GREEN VALLEY 2101 | CENTRAL COAST | 6.5982 | 36.5973 | 46.31% | 12 | 2 | 35.52% | 88.5% | 0 | 0.057708 | 1 | 3.2834 | 0.18948 | Medium | Medium | High | 1441 | 1598 | 0.057708
OILFIELDS 1103N44 | OILFIELDS 1103 | CENTRAL COAST | 18.7718 | 55.8541 | 96.36% | 0 | 0 | 100% | 0% | 0 | 0.079917 | 1 | 2.3613 | 0.18871 | High | High | Medium | 1442 | 1399 | 0.079917
MORAGA 1104CB | MORAGA 1104 | DIABLO | 12.3977 | 11.1682 | 54.34% | 6 | 17 | 72.33% | 3.443% | 1 | 0.053103 | 1 | 3.5454 | 0.18827 | Medium | Medium | High | 1443 | 1646 | 0.053103
LAURELES 1111432 | LAURELES 1111 | CENTRAL COAST | 49.1946 | 74.7913 | 100% | 10 | 10 | 100% | 0% | 0 | 0.11153 | 1 | 1.687 | 0.18815 | High | High | Low | 1444 | 1252 | 0.11153
KESWICK 11011588 | KESWICK 1101 | NORTH VALLEY | 6.9485 | 28.4638 | 99.9% | 2 | 4 | 79.32% | 55.95% | 0 | 0.089394 | 1 | 2.1029 | 0.18799 | High | High | Low | 1445 | 1341 | 0.089394
GIRVAN 11011330 | GIRVAN 1101 | NORTH VALLEY | 31.2468 | 42.7568 | 99.67% | 0 | 4 | 100% | 24.65% | 1 | 0.13164 | 1 | 1.4253 | 0.18763 | High | High | Low | 1446 | 1194 | 0.13164
CASTRO VALLEY 1106MR337 | CASTRO VALLEY 1106 | MISSION | 10.471 | 41.4878 | 74.2% | 2 | 2 | 55.31% | 63.23% | 0 | 0.053395 | 1 | 3.5101 | 0.18742 | Medium | Medium | High | 1447 | 1642 | 0.053395
CAMP EVERS 21035402 | CAMP EVERS 2103 | CENTRAL COAST | 2.8538 | 10 | 29.07% | 11 | 2 | 42.31% | 90.21% | 0 | 0.05912 | 1 | 3.1651 | 0.18712 | Medium | Medium | High | 1448 | 1580 | 0.05912
DIAMOND SPRINGS 1104CB | DIAMOND SPRINGS 1104 | SIERRA | 6.9541 | 10 | 49.56% | 0 | 3 | 69.41% | 79.56% | 0 | 0.059614 | 1 | 3.1336 | 0.18681 | Medium | Medium | High | 1449 | 1570 | 0.059614
VOLTA 110297816 | VOLTA 1102 | NORTH VALLEY | 5.2578 | 25.9131 | 100% | 2 | 2 | 100% | 80.28% | 1 | 0.11476 | 1 | 1.6244 | 0.18643 | High | High | Low | 1450 | 1239 | 0.11476
CURTIS 17029220 | CURTIS 1702 | YOSEMITE | 11.0663 | 17.9965 | 77.35% | 2 | 13 | 99.21% | 0.02567% | 0 | 0.05548 | 1 | 3.3526 | 0.186 | Medium | Medium | High | 1451 | 1618 | 0.05548
HALF MOON BAY 11038920 | HALF MOON BAY 1103 | PENINSULA | 8.6186 | 37.4312 | 39.37% | 7 | 11 | 100% | 0% | 0 | 0.054692 | 1 | 3.3955 | 0.1857 | Medium | Medium | High | 1452 | 1629 | 0.054692
CURTIS 170411300 | CURTIS 1704 | YOSEMITE | 3.6591 | 33.4299 | 41.14% | 0 | 2 | 100% | 62.71% | 0 | 0.065584 | 1 | 2.8287 | 0.18552 | High | High | Medium | 1453 | 1511 | 0.065584
DEL MONTE 21042624 | DEL MONTE 2104 | CENTRAL COAST | 18.1708 | 31.8719 | 33.21% | 2 | 17 | 94.85% | 0% | 0 | 0.05749 | 1 | 3.2193 | 0.18508 | Medium | Medium | High | 1454 | 1599 | 0.05749
CAYUCOS 1102CB | CAYUCOS 1102 | LOS PADRES | 11.9239 | 72.3136 | 83.3% | 3 | 2 | 41.34% | 71.02% | 0 | 0.079048 | 1 | 2.3364 | 0.18468 | High | High | Medium | 1455 | 1407 | 0.079048
WYANDOTTE 11071510 | WYANDOTTE 1107 | NORTH VALLEY | 25.4968 | 11.1229 | 100% | 1 | 4 | 100% | 0% | 0 | 0.05976 | 1 | 3.0899 | 0.18465 | Medium | Medium | High | 1456 | 1567 | 0.05976
SAN JUSTO 11014002 | SAN JUSTO 1101 | CENTRAL COAST | 18.1183 | 71.0394 | 96.75% | 4 | 7 | 95.15% | 0% | 0 | 0.089593 | 1 | 2.061 | 0.18465 | High | High | Low | 1457 | 1339 | 0.089593
CAMP EVERS 2104CB | CAMP EVERS 2104 | CENTRAL COAST | 1.0591 | 10 | 55.62% | 0 | 2 | 23.71% | 100% | 0 | 0.05446 | 1 | 3.3876 | 0.18449 | Medium | Medium | High | 1458 | 1634 | 0.05446
KANAKA 11011406 | KANAKA 1101 | NORTH VALLEY | 26.9635 | 16.7709 | 74.27% | 2 | 6 | 97.41% | 16.93% | 0 | 0.097652 | 1 | 1.8891 | 0.18448 | High | High | Low | 1459 | 1303 | 0.097652
BRUNSWICK 11062790 | BRUNSWICK 1106 | SIERRA | 8.9258 | 13.4181 | 98.75% | 0 | 3 | 81.13% | 52.78% | 0 | 0.084645 | 1 | 2.178 | 0.18435 | High | High | Low | 1460 | 1364 | 0.084645
APPLE HILL 2102186912 | APPLE HILL 2102 | SIERRA | 48.9257 | 16.1646 | 100% | 9 | 3 | 96.19% | 0% | 0 | 0.093311 | 1 | 1.9754 | 0.18433 | High | High | Low | 1461 | 1322 | 0.093311
ALTO 1122CB | ALTO 1122 | NORTH BAY | 2.386 | 10 | 11.27% | 0 | 1 | 68.83% | 100% | 0 | 0.05105 | 1 | 3.5941 | 0.18348 | Medium | Medium | High | 1462 | 1671 | 0.05105
CALPINE 1144304 | CALPINE 1144 | SONOMA | 0.046375 | 85 | 0% | 0 | 0 | 100% | 100% | 0 | 0.098754 | 1 | 1.8471 | 0.18241 | High | High | Low | 1463 | 1299 | 0.098754
ANNAPOLIS 1101608 | ANNAPOLIS 1101 | HUMBOLDT | 17.8008 | 87.1454 | 94.8% | 10 | 5 | 100% | 0% | 0 | 0.13339 | 1 | 1.3674 | 0.1824 | High | High | Low | 1464 | 1185 | 0.13339
ORINDA 0401CB | ORINDA 0401 | DIABLO | 0.11326 | 10 | 23.54% | 0 | 0 | 63.88% | 100% | 0 | 0.052555 | 1 | 3.4681 | 0.18227 | Medium | Medium | High | 1465 | 1656 | 0.052555
OREGON TRAIL 11041634 | OREGON TRAIL 1104 | NORTH VALLEY | 17.7143 | 33.9199 | 93.56% | 1 | 0 | 97.56% | 0% | 0 | 0.067366 | 1 | 2.7053 | 0.18225 | High | High | Medium | 1466 | 1493 | 0.067366
APPLE HILL 1103CB | APPLE HILL 1103 | SIERRA | 27.6878 | 21.3856 | 62.7% | 5 | 24 | 82.6% | 2.955% | 0 | 0.074928 | 1 | 2.43 | 0.18207 | High | High | Medium | 1467 | 1439 | 0.074928
BANGOR 11017446 | BANGOR 1101 | NORTH VALLEY | 43.441 | 11.2625 | 85.83% | 3 | 18 | 100% | 0% | 0 | 0.081818 | 1 | 2.2193 | 0.18158 | High | High | Low | 1468 | 1384 | 0.081818
ARCATA 11225384 | ARCATA 1122 | HUMBOLDT | 15.2841 | 39.9172 | 40.09% | 14 | 5 | 87.62% | 0% | 0 | 0.061973 | 1 | 2.9263 | 0.18135 | High | High | Medium | 1469 | 1540 | 0.061973
FROGTOWN 170275252 | FROGTOWN 1702 | STOCKTON | 57.5264 | 53.766 | 80.82% | 0 | 20 | 95.14% | 0% | 0 | 0.087181 | 1 | 2.07 | 0.18046 | High | High | Low | 1470 | 1349 | 0.087181
MONTICELLO 1101718 | MONTICELLO 1101 | NORTH BAY | 26.9011 | 60.1825 | 63.96% | 4 | 11 | 90.43% | 0% | 0 | 0.067428 | 1 | 2.6725 | 0.1802 | High | High | Medium | 1471 | 1491 | 0.067428
CURTIS 1702CB | CURTIS 1702 | YOSEMITE | 21.952 | 21.1187 | 82.49% | 5 | 14 | 95.73% | 0% | 0 | 0.0532 | 1 | 3.3587 | 0.17868 | Medium | Medium | High | 1472 | 1644 | 0.0532
HALSEY 11011704 | HALSEY 1101 | SIERRA | 12.7864 | 10 | 79.44% | 4 | 15 | 96.8% | 0% | 0 | 0.071684 | 1 | 2.4891 | 0.17843 | High | High | Medium | 1473 | 1463 | 0.071684
VIEJO 22029104 | VIEJO 2202 | CENTRAL COAST | 5.9155 | 10 | 5.95% | 8 | 7 | 99.2% | 0% | 0 | 0.054282 | 1 | 3.2793 | 0.17801 | Medium | Medium | High | 1474 | 1635 | 0.054282
FROGTOWN 170212282 | FROGTOWN 1702 | STOCKTON | 36.3191 | 39.3074 | 54.5% | 2 | 7 | 100% | 0% | 0 | 0.069451 | 1 | 2.557 | 0.17759 | High | High | Medium | 1475 | 1474 | 0.069451
SONOMA 110478372 | SONOMA 1104 | SONOMA | 16.4405 | 56.415 | 74.14% | 3 | 12 | 96.01% | 0% | 0 | 0.051874 | 1 | 3.4088 | 0.17683 | Medium | Medium | High | 1476 | 1663 | 0.051874
ECHO SUMMIT 11018922 | ECHO SUMMIT 1101 | (blank) | 2.2784 | 12.8457 | 99.62% | 6 | 2 | 64% | 0% | 0 | 0.13221 | 1 | 1.3369 | 0.17676 | High | High | Low | 1477 | 1193 | 0.13221
RED BLUFF 11011556 | RED BLUFF 1101 | NORTH VALLEY | 35.2007 | 32.6588 | 100% | 1 | 11 | 88.02% | 0% | 0 | 0.10148 | 1 | 1.7409 | 0.17666 | High | High | Low | 1478 | 1290 | 0.10148
SAN JOAQUIN #3 1102CB | SAN JOAQUIN #3 1102 | YOSEMITE | 9.6989 | 12.3012 | 62.24% | 3 | 14 | 100% | 56.8% | 0 | 0.1304 | 1 | 1.3465 | 0.17559 | High | High | Low | 1479 | 1196 | 0.1304
HIGGINS 110950078 | HIGGINS 1109 | SIERRA | 48.4681 | 37.033 | 99.96% | 1 | 15 | 100% | 0% | 0 | 0.068168 | 1 | 2.5691 | 0.17513 | High | High | Medium | 1480 | 1483 | 0.068168
SANTA YNEZ 1101Y16 | SANTA YNEZ 1101 | LOS PADRES | 7.1745 | 86.5871 | 96.55% | 0 | 1 | 49.62% | 51.9% | 0 | 0.082863 | 1 | 2.1114 | 0.17496 | High | High | Low | 1481 | 1375 | 0.082863
HIGGINS 110950072 | HIGGINS 1109 | SIERRA | 42.3856 | 25.4799 | 92.02% | 2 | 15 | 100% | 0% | 0 | 0.068313 | 1 | 2.5573 | 0.1747 | High | High | Medium | 1482 | 1482 | 0.068313
TASSAJARA 210419042 | TASSAJARA 2104 | DIABLO | 7.0796 | 47.3825 | 57.65% | 1 | 2 | 83.81% | 25.74% | 0 | 0.045532 | 1 | 3.832 | 0.17448 | Medium | Medium | High | 1483 | 1755 | 0.045532
OAKLAND X 1106CR006 | OAKLAND X 1106 | EAST BAY | 3.6093 | 38.5923 | 23.16% | 2 | 2 | 100% | 56.08% | 0 | 0.054619 | 1 | 3.186 | 0.17401 | Medium | Medium | High | 1484 | 1630 | 0.054619
COARSEGOLD 21045525 | COARSEGOLD 2104 | YOSEMITE | 13.0444 | 10.8034 | 99.82% | 2 | 45 | 100% | 0% | 0 | 0.072179 | 1 | 2.4095 | 0.17392 | High | High | Medium | 1485 | 1460 | 0.072179
SAN RAMON 2107MR287 | SAN RAMON 2107 | MISSION | 0.029952 | 10 | 100% | 0 | 0 | 0.9859% | 100% | 0 | 0.052586 | 1 | 3.3036 | 0.17373 | Medium | Medium | High | 1486 | 1654 | 0.052586
BIG RIVER 110179628 | BIG RIVER 1101 | HUMBOLDT | 14.7546 | 28.3298 | 27.17% | 16 | 19 | 100% | 0% | 0 | 0.06147 | 1 | 2.8171 | 0.17317 | Medium | Medium | Medium | 1487 | 1551 | 0.06147
OAKLAND X 1106CR008 | OAKLAND X 1106 | EAST BAY | 4.2343 | 10.8634 | 21.85% | 11 | 17 | 100% | 13.39% | 0 | 0.051531 | 1 | 3.3497 | 0.17261 | Medium | Medium | High | 1488 | 1667 | 0.051531
PACIFICA 1102CB | PACIFICA 1102 | PENINSULA | 2.2873 | 19.4 | 0% | 0 | 1 | 33.56% | 100% | 0 | 0.040266 | 1 | 4.2842 | 0.17251 | Medium | Medium | High | 1489 | 1849 | 0.040266
CALAVERAS CEMENT 11011419 | CALAVERAS CEMENT 1101 | STOCKTON | 15.0795 | 14.8417 | 100% | 2 | 7 | 100% | 0% | 0 | 0.074427 | 1 | 2.3142 | 0.17224 | High | High | Medium | 1490 | 1443 | 0.074427
PINE GROVE 11026080 | PINE GROVE 1102 | STOCKTON | 34.785 | 21.8457 | 100% | 6 | 11 | 100% | 0.6625% | 0 | 0.089074 | 1 | 1.9325 | 0.17213 | High | High | Low | 1491 | 1342 | 0.089074
AUBERRY 1102R2850 | AUBERRY 1102 | FRESNO | 25.8464 | 30.8369 | 100% | 0 | 16 | 100% | 0% | 0 | 0.095456 | 1 | 1.8012 | 0.17193 | High | High | Low | 1492 | 1312 | 0.095456
MOUNTAIN QUARRIES 21011346 | MOUNTAIN QUARRIES 2101 | SIERRA | 30.7365 | 10.3256 | 98.49% | 5 | 12 | 100% | 0% | 0 | 0.072232 | 1 | 2.3792 | 0.17186 | High | High | Medium | 1493 | 1458 | 0.072232
CAMP EVERS 2103CB | CAMP EVERS 2103 | CENTRAL COAST | 0.092755 | 10 | 13.07% | 0 | 0 | 75.74% | 100% | 0 | 0.061458 | 1 | 2.7937 | 0.17169 | Medium | Medium | Medium | 1494 | 1552 | 0.061458
PEORIA 17051834 | PEORIA 1705 | YOSEMITE | 22.9121 | 21.3201 | 69.84% | 0 | 15 | 96.15% | 0% | 0 | 0.076648 | 1 | 2.2374 | 0.17149 | High | High | Medium | 1495 | 1428 | 0.076648
ALTO 11251158 | ALTO 1125 | NORTH BAY | 2.2748 | 24.9991 | 11.61% | 1 | 1 | 41.4% | 88.18% | 0 | 0.041574 | 1 | 4.1164 | 0.17113 | Medium | Medium | High | 1496 | 1826 | 0.041574
FORT BRAGG A 1102418 | FORT BRAGG A 1102 | HUMBOLDT | 13.7424 | 13.0618 | 15.86% | 29 | 14 | 98.4% | 0% | 0 | 0.053533 | 1 | 3.1937 | 0.17097 | Medium | Medium | High | 1497 | 1641 | 0.053533
GEYSERVILLE 1102484 | GEYSERVILLE 1102 | SONOMA | 33.3601 | 63.5348 | 83.52% | 3 | 7 | 68.39% | 43.97% | 0 | 0.12892 | 1 | 1.3254 | 0.17087 | High | High | Low | 1498 | 1202 | 0.12892
PLACERVILLE 2106CB | PLACERVILLE 2106 | SIERRA | 6.6569 | 17.5661 | 15.58% | 1 | 6 | 100% | 71.65% | 0 | 0.069168 | 1 | 2.4573 | 0.16996 | High | High | Medium | 1499 | 1477 | 0.069168
TEMPLETON 2113CB | TEMPLETON 2113 | LOS PADRES | 0.49234 | 10 | 22.58% | 0 | 0 | 1.889% | 0% | 0 | 0.0057624 | 11.2183 | 2.6278 | 0.16987 | Low | Low | Medium | 1500 | 1517 | 0.064645
DUNBAR 1103440 | DUNBAR 1103 | SONOMA | 3.5573 | 21.3081 | 50.04% | 0 | 2 | 25.85% | 93.78% | 0 | 0.045809 | 1 | 3.7008 | 0.16953 | Medium | Medium | High | 1501 | 1751 | 0.045809
BIG BASIN 11022253 | BIG BASIN 1102 | CENTRAL COAST | 1.463 | 10 | 16.17% | 0 | 0 | 100% | 100% | 0 | 0.069736 | 1 | 2.4273 | 0.16927 | High | High | Medium | 1502 | 1473 | 0.069736
BRUNSWICK 110651484 | BRUNSWICK 1106 | SIERRA | 20.7709 | 48.7311 | 68.62% | 4 | 3 | 82.69% | 37.09% | 0 | 0.070762 | 1 | 2.3766 | 0.16817 | High | High | Medium | 1503 | 1467 | 0.070762
SILVERADO 2105CB | SILVERADO 2105 | NORTH BAY | 0.47706 | 10 | 63.84% | 0 | 1 | 10.39% | 100% | 0 | 0.044175 | 1 | 3.805 | 0.16809 | Medium | Medium | High | 1504 | 1773 | 0.044175
VIEJO 22019114 | VIEJO 2201 | CENTRAL COAST | 6.3385 | 10 | 15.64% | 12 | 5 | 93.11% | 0% | 0 | 0.043315 | 1 | 3.8689 | 0.16758 | Medium | Medium | High | 1505 | 1789 | 0.043315
CLAYTON 221355668 | CLAYTON 2213 | DIABLO | 3.8789 | 27.0823 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041308 | 1 | 4.0479 | 0.16721 | Medium | Medium | High | 1506 | 1829 | 0.041308
GANSNER 11012424 | GANSNER 1101 | NORTH VALLEY | 18.9007 | 82.3071 | 77.09% | 4 | 10 | 100% | 0% | 0 | 0.081226 | 1 | 2.0492 | 0.16645 | High | High | Low | 1507 | 1389 | 0.081226
OCEANO 1104V38 | OCEANO 1104 | LOS PADRES | 12.9054 | 24.0827 | 46.82% | 5 | 8 | 68.56% | 8.41% | 1 | 0.053152 | 1 | 3.1233 | 0.16601 | Medium | Medium | High | 1508 | 1645 | 0.053152
SARATOGA 1103LC16 | SARATOGA 1103 | DE ANZA | 4.0893 | 10 | 47.33% | 3 | 10 | 80.63% | 0% | 0 | 0.042849 | 1 | 3.8592 | 0.16536 | Medium | Medium | High | 1509 | 1802 | 0.042849
LUCERNE 110638436 | LUCERNE 1106 | HUMBOLDT | 4.6279 | 61.4353 | 100% | 0 | 7 | 96.43% | 0% | 0 | 0.044553 | 1 | 3.7075 | 0.16518 | Medium | Medium | High | 1510 | 1768 | 0.044553
CALPINE 1144276-G | CALPINE 1144 | SONOMA | 0.014761 | 75 | 0% | 0 | 0 | 100% | 100% | 0 | 0.092831 | 1 | 1.7759 | 0.16486 | High | High | Low | 1511 | 1324 | 0.092831
WOODSIDE 110411555 | WOODSIDE 1104 | PENINSULA | 0.85806 | 10 | 96.59% | 0 | 1 | 100% | 0% | 0 | 0.032229 | 1 | 5.0953 | 0.16422 | Medium | Medium | High | 1512 | 2037 | 0.032229
MARIPOSA 21014410 | MARIPOSA 2101 | YOSEMITE | 22.8041 | 16.019 | 99.74% | 6 | 25 | 100% | 48.37% | 1 | 0.13823 | 1 | 1.1854 | 0.16386 | High | High | Low | 1513 | 1172 | 0.13823
TIVY VALLEY 1107584840 | TIVY VALLEY 1107 | FRESNO | 44.9458 | 14.7533 | 99.99% | 0 | 18 | 100% | 0% | 0 | 0.079403 | 1 | 2.0582 | 0.16342 | High | High | Low | 1514 | 1404 | 0.079403
ROSSMOOR 1108CB | ROSSMOOR 1108 | DIABLO | 3.0229 | 50.0663 | 2.294% | 0 | 11 | 53.4% | 61.71% | 0 | 0.040788 | 1 | 3.9971 | 0.16304 | Medium | Medium | High | 1515 | 1836 | 0.040788
MARIPOSA 210110070 | MARIPOSA 2101 | YOSEMITE | 25.9306 | 26.9034 | 96.01% | 1 | 27 | 100% | 0% | 0 | 0.078332 | 1 | 2.0789 | 0.16285 | High | High | Low | 1516 | 1410 | 0.078332
NORTH TOWER 2101CB | NORTH TOWER 2101 | NORTH BAY | 0.18972 | 10 | 0% | 0 | 0 | 4.663% | 0% | 0 | 0.0049217 | 11.2183 | 2.9474 | 0.16274 | Low | Low | Medium | 1517 | 1623 | 0.055213
CLAY 110113442 | CLAY 1101 | STOCKTON | 25.1981 | 33.4611 | 98.28% | 1 | 6 | 81.01% | 0% | 0 | 0.059218 | 1 | 2.7463 | 0.16263 | Medium | Medium | Medium | 1518 | 1577 | 0.059218
TEMPLETON 2110R90 | TEMPLETON 2110 | LOS PADRES | 27.6614 | 57.9463 | 69.12% | 2 | 5 | 77.95% | 0% | 0 | 0.077528 | 1 | 2.0934 | 0.1623 | High | High | Low | 1519 | 1417 | 0.077528
BELL 11082202 | BELL 1108 | SIERRA | 31.9475 | 20.6823 | 70.59% | 0 | 8 | 96.19% | 0% | 0 | 0.059129 | 1 | 2.7384 | 0.16192 | Medium | Medium | Medium | 1520 | 1579 | 0.059129
RACETRACK 1703CB | RACETRACK 1703 | YOSEMITE | 15.5569 | 10 | 47.8% | 4 | 26 | 86.61% | 0% | 0 | 0.05588 | 1 | 2.884 | 0.16116 | Medium | Medium | Medium | 1521 | 1613 | 0.05588
RINCON 1104CB | RINCON 1104 | SONOMA | 2.6764 | 10 | 22.48% | 3 | 5 | 47.86% | 77.17% | 0 | 0.046471 | 1 | 3.464 | 0.16098 | Medium | Medium | High | 1522 | 1731 | 0.046471
KONOCTI 1102596 | KONOCTI 1102 | HUMBOLDT | 8.591 | 44.5897 | 35.58% | 1 | 10 | 63.73% | 0% | 0 | 0.046139 | 1 | 3.4882 | 0.16094 | Medium | Medium | High | 1523 | 1738 | 0.046139
VOLTA 110293418 | VOLTA 1102 | NORTH VALLEY | 2.6513 | 65.9048 | 100% | 5 | 0 | 100% | 44.92% | 0 | 0.087226 | 1 | 1.8377 | 0.1603 | High | High | Low | 1524 | 1348 | 0.087226
SANTA ROSA A 1104CB | SANTA ROSA A 1104 | SONOMA | 1.1731 | 10 | 48.07% | 0 | 1 | 19.25% | 100% | 0 | 0.042461 | 1 | 3.7672 | 0.15996 | Medium | Medium | High | 1525 | 1808 | 0.042461
NORTH DUBLIN 2103CB | NORTH DUBLIN 2103 | MISSION | 12.6489 | 55.8047 | 31.35% | 1 | 2 | 83.95% | 0% | 0 | 0.043695 | 1 | 3.6462 | 0.15932 | Medium | Medium | High | 1526 | 1783 | 0.043695
GUALALA 111135562 | GUALALA 1111 | HUMBOLDT | 14.2585 | 63.006 | 19.44% | 12 | 36 | 100% | 0% | 0 | 0.084547 | 1 | 1.8822 | 0.15913 | High | High | Low | 1527 | 1366 | 0.084547
CURTIS 170463502 | CURTIS 1704 | YOSEMITE | 10.4605 | 25.8863 | 57.75% | 1 | 16 | 100% | 0% | 0 | 0.052892 | 1 | 3.0037 | 0.15887 | Medium | Medium | Medium | 1528 | 1650 | 0.052892
ALTO 1125CB | ALTO 1125 | NORTH BAY | 0.27217 | 10 | 45.49% | 2 | 1 | 11.73% | 100% | 0 | 0.039699 | 1 | 3.9974 | 0.15869 | Medium | Medium | High | 1529 | 1865 | 0.039699
HIGHLANDS 110448262 | HIGHLANDS 1104 | HUMBOLDT | 5.8216 | 10 | 84.42% | 0 | 6 | 100% | 0% | 0 | 0.047568 | 1 | 3.314 | 0.15764 | Medium | Medium | High | 1530 | 1716 | 0.047568
ROSSMOOR 110168920 | ROSSMOOR 1101 | DIABLO | 5.9925 | 29.5829 | 31.67% | 8 | 11 | 82.31% | 24.74% | 0 | 0.047645 | 1 | 3.3031 | 0.15738 | Medium | Medium | High | 1531 | 1712 | 0.047645
ROB ROY 210410954 | ROB ROY 2104 | CENTRAL COAST | 7.1077 | 10 | 88.57% | 7 | 3 | 100% | 0% | 0 | 0.050548 | 1 | 3.1113 | 0.15727 | Medium | Medium | High | 1532 | 1676 | 0.050548
HIGGINS 1109594 | HIGGINS 1109 | SIERRA | 14.2898 | 11.2028 | 80.24% | 1 | 11 | 100% | 0% | 0 | 0.051909 | 1 | 3.0273 | 0.15715 | Medium | Medium | Medium | 1533 | 1662 | 0.051909
UKIAH 1114408 | UKIAH 1114 | HUMBOLDT | 37.0058 | 66.3521 | 67.33% | 5 | 13 | 97.48% | 0% | 0 | 0.071452 | 1 | 2.1941 | 0.15678 | High | High | Low | 1534 | 1464 | 0.071452
FORT BRAGG A 11044690 | FORT BRAGG A 1104 | HUMBOLDT | 12.2439 | 49.0226 | 37.04% | 15 | 12 | 85.93% | 0% | 0 | 0.050332 | 1 | 3.1146 | 0.15677 | Medium | Medium | High | 1535 | 1680 | 0.050332
PALO SECO 0401CB | PALO SECO 0401 | EAST BAY | 4.7078 | 10 | 0% | 4 | 1 | 100% | 18.75% | 0 | 0.035354 | 1 | 4.4285 | 0.15657 | Medium | Medium | High | 1536 | 1951 | 0.035354
SHINGLE SPRINGS 2110CB | SHINGLE SPRINGS 2110 | SIERRA | 0.10881 | 10 | 92.58% | 0 | 0 | 8.524% | 92.58% | 0 | 0.047519 | 1 | 3.2729 | 0.15553 | Medium | Medium | High | 1537 | 1717 | 0.047519
PACIFICA 11033907 | PACIFICA 1103 | PENINSULA | 3.5027 | 51.2022 | 0% | 4 | 0 | 72.69% | 71.75% | 0 | 0.042148 | 1 | 3.6814 | 0.15517 | Medium | Medium | High | 1538 | 1815 | 0.042148
ECHO SUMMIT 11012500 | ECHO SUMMIT 1101 | (blank) | 2.8817 | 10 | 100% | 2 | 2 | 100% | 0% | 0 | 0.074119 | 1 | 2.0914 | 0.15501 | High | High | Low | 1539 | 1445 | 0.074119
BIG RIVER 11013002 | BIG RIVER 1101 | HUMBOLDT | 6.8985 | 10 | 4.337% | 11 | 17 | 83.84% | 0% | 0 | 0.058669 | 1 | 2.6346 | 0.15457 | Medium | Medium | Medium | 1540 | 1584 | 0.058669
CAMP EVERS 21035404 | CAMP EVERS 2103 | CENTRAL COAST | 2.6779 | 10 | 26.91% | 3 | 0 | 57.99% | 100% | 0 | 0.052978 | 1 | 2.9173 | 0.15455 | Medium | Medium | Medium | 1541 | 1649 | 0.052978
BANGOR 11011804 | BANGOR 1101 | NORTH VALLEY | 42.8631 | 13.9127 | 93.17% | 8 | 9 | 100% | 3.48% | 0 | 0.064625 | 1 | 2.3914 | 0.15455 | High | High | Medium | 1542 | 1518 | 0.064625
MORGAN HILL 2105XR070 | MORGAN HILL 2105 | SAN JOSE | 6.67 | 37.7183 | 68.61% | 0 | 0 | 76.77% | 50.18% | 1 | 0.046839 | 1 | 3.2954 | 0.15435 | Medium | Medium | High | 1543 | 1726 | 0.046839
SHINGLE SPRINGS 210981390 | SHINGLE SPRINGS 2109 | SIERRA | 18.7493 | 21.0161 | 63.9% | 1 | 8 | 100% | 0% | 0 | 0.075764 | 1 | 2.0292 | 0.15374 | High | High | Low | 1544 | 1436 | 0.075764
JARVIS 1111MR121 | JARVIS 1111 | MISSION | 1.1185 | 70.124 | 6.252% | 0 | 0 | 20.83% | 100% | 0 | 0.045013 | 1 | 3.4072 | 0.15337 | Medium | Medium | High | 1545 | 1765 | 0.045013
ALTO 112278672 | ALTO 1122 | NORTH BAY | 2.7277 | 18.1694 | 27.03% | 6 | 9 | 33.13% | 66.64% | 0 | 0.042144 | 1 | 3.6273 | 0.15287 | Medium | Medium | High | 1546 | 1816 | 0.042144
CORNING 11021622 | CORNING 1102 | NORTH VALLEY | 34.031 | 83.6384 | 99.67% | 1 | 6 | 100% | 0% | 0 | 0.11037 | 1 | 1.3788 | 0.15218 | High | High | Low | 1547 | 1257 | 0.11037
PHILO 1101CB | PHILO 1101 | HUMBOLDT | 30.1647 | 49.3506 | 76.4% | 12 | 16 | 60.92% | 0% | 0 | 0.072449 | 1 | 2.0932 | 0.15165 | High | High | Low | 1548 | 1456 | 0.072449
CLOVERDALE 1102674 | CLOVERDALE 1102 | SONOMA | 17.0598 | 62.482 | 68.42% | 4 | 8 | 84.92% | 25.35% | 0 | 0.082178 | 1 | 1.8325 | 0.15059 | High | High | Low | 1549 | 1381 | 0.082178
DOBBINS 110191464 | DOBBINS 1101 | SIERRA | 7.0765 | 18.3456 | 88.34% | 2 | 2 | 100% | 2.371% | 0 | 0.050871 | 1 | 2.9545 | 0.1503 | Medium | Medium | Medium | 1550 | 1674 | 0.050871
STANISLAUS 170179826 | STANISLAUS 1701 | YOSEMITE | 10.1928 | 54.2786 | 66.14% | 1 | 7 | 100% | 0% | 0 | 0.044036 | 1 | 3.4104 | 0.15018 | Medium | Medium | High | 1551 | 1777 | 0.044036
SAND CREEK 110345190 | SAND CREEK 1103 | FRESNO | 36.6214 | 13.3834 | 99.51% | 0 | 5 | 100% | 0% | 0 | 0.078024 | 1 | 1.9196 | 0.14977 | High | High | Low | 1552 | 1413 | 0.078024
MONTICELLO 1101630 | MONTICELLO 1101 | NORTH BAY | 17.6986 | 68.0589 | 26.54% | 2 | 4 | 90.07% | 0% | 0 | 0.065491 | 1 | 2.2846 | 0.14962 | High | High | Medium | 1553 | 1513 | 0.065491
SPRING GAP 1702CB | SPRING GAP 1702 | YOSEMITE | 7.418 | 94.1072 | 60.1% | 3 | 1 | 100% | 85.76% | 0 | 0.17407 | 1 | 0.85687 | 0.14916 | High | High | Low | 1554 | 1105 | 0.17407
NOTRE DAME 11042408 | NOTRE DAME 1104 | NORTH VALLEY | 11.2331 | 23.0626 | 36.02% | 1 | 3 | 81.2% | 47.16% | 1 | 0.051652 | 1 | 2.8875 | 0.14914 | Medium | Medium | Medium | 1555 | 1665 | 0.051652
TASSAJARA 2112D514R | TASSAJARA 2112 | DIABLO | 3.458 | 10.5192 | 20.09% | 0 | 5 | 72.43% | 34.87% | 0 | 0.03721 | 1 | 4.003 | 0.14895 | Medium | Medium | High | 1556 | 1913 | 0.03721
GRASS VALLEY 11012208 | GRASS VALLEY 1101 | SIERRA | 12.2835 | 20.913 | 70.74% | 4 | 7 | 96.31% | 0% | 0 | 0.053929 | 1 | 2.7592 | 0.1488 | Medium | Medium | Medium | 1557 | 1638 | 0.053929
SAN LEANDRO U 1109CR182 | SAN LEANDRO U 1109 | MISSION | 4.81 | 10 | 62.88% | 5 | 1 | 100% | 19.48% | 0 | 0.046108 | 1 | 3.2168 | 0.14832 | Medium | Medium | High | 1558 | 1740 | 0.046108
INDIAN FLAT 1104CB | INDIAN FLAT 1104 | YOSEMITE | 12.7115 | 39.8985 | 69.22% | 2 | 12 | 100% | 0% | 0 | 0.075983 | 1 | 1.9513 | 0.14826 | High | High | Low | 1559 | 1433 | 0.075983
GREENBRAE 11036083 | GREENBRAE 1103 | NORTH BAY | 0.34152 | 10 | 10.92% | 0 | 0 | 100% | 67.56% | 0 | 0.040594 | 1 | 3.6438 | 0.14792 | Medium | Medium | High | 1560 | 1839 | 0.040594
CALISTOGA 1101 | CALISTOGA 1101 | NORTH BAY | 0.0027683 | 10 | 0% | 0 | 0 | 100% | 100% | 0 | 0.061559 | 1 | 2.3953 | 0.14745 | High | High | Medium | 1561 | 1545 | 0.061559
CALPELLA 1101600 | CALPELLA 1101 | HUMBOLDT | 20.3203 | 63.0301 | 92.94% | 2 | 3 | 76.37% | 16.27% | 1 | 0.080296 | 1 | 1.8322 | 0.14712 | High | High | Low | 1562 | 1397 | 0.080296
MORGAN HILL 2111XR292 | MORGAN HILL 2111 | SAN JOSE | 10.8242 | 23.3354 | 98.35% | 1 | 8 | 89.12% | 0% | 0 | 0.048423 | 1 | 3.0382 | 0.14712 | Medium | Medium | Medium | 1563 | 1702 | 0.048423
FORT BRAGG A 1102956 | FORT BRAGG A 1102 | HUMBOLDT | 10.8506 | 10 | 43.99% | 19 | 14 | 88.12% | 0% | 0 | 0.067263 | 1 | 2.1825 | 0.1468 | High | High | Low | 1564 | 1496 | 0.067263
CURTIS 17058110 | CURTIS 1705 | YOSEMITE | 8.154 | 12.6611 | 71.8% | 0 | 7 | 100% | 22.12% | 0 | 0.043018 | 1 | 3.3987 | 0.14621 | Medium | Medium | High | 1565 | 1796 | 0.043018
SARATOGA 1105LC14 | SARATOGA 1105 | DE ANZA | 9.6151 | 10 | 69.49% | 2 | 9 | 86.08% | 0% | 0 | 0.040305 | 1 | 3.6261 | 0.14615 | Medium | Medium | High | 1566 | 1847 | 0.040305
LOS GATOS 1101LB40 | LOS GATOS 1101 | DE ANZA | 7.214 | 10 | 65.42% | 2 | 3 | 77.51% | 0% | 0 | 0.041155 | 1 | 3.5497 | 0.14609 | Medium | Medium | High | 1567 | 1832 | 0.041155
SILVERADO 2104806 | SILVERADO 2104 | NORTH BAY | 20.224 | 80.8764 | 82.09% | 0 | 5 | 59.08% | 2.927% | 0 | 0.051436 | 1 | 2.8358 | 0.14586 | Medium | Medium | Medium | 1568 | 1668 | 0.051436
RINCON 1101576 | RINCON 1101 | SONOMA | 2.0608 | 10 | 77.6% | 0 | 6 | 19.69% | 79.16% | 0 | 0.055451 | 1 | 2.6301 | 0.14585 | Medium | Medium | Medium | 1569 | 1619 | 0.055451
GRASS VALLEY 11031700 | GRASS VALLEY 1103 | SIERRA | 21.5982 | 19.8547 | 93.5% | 3 | 7 | 99.55% | 0% | 0 | 0.057412 | 1 | 2.5384 | 0.14573 | Medium | Medium | Medium | 1570 | 1601 | 0.057412
FROGTOWN 1702290609 | FROGTOWN 1702 | STOCKTON | 18.0385 | 28.1983 | 98.5% | 3 | 10 | 100% | 0% | 0 | 0.059181 | 1 | 2.4612 | 0.14566 | Medium | Medium | Medium | 1571 | 1578 | 0.059181
WILLOW CREEK 110129362 | WILLOW CREEK 1101 | HUMBOLDT | 6.8106 | 67.3887 | 96.73% | 8 | 5 | 58.77% | 100% | 1 | 0.16769 | 1 | 0.86685 | 0.14536 | High | High | Low | 1572 | 1116 | 0.16769
PAUL SWEET 2102CB | PAUL SWEET 2102 | CENTRAL COAST | 0.80988 | 10 | 58.15% | 0 | 0 | 13.51% | 100% | 0 | 0.042651 | 1 | 3.4078 | 0.14534 | Medium | Medium | High | 1573 | 1805 | 0.042651
WILLOW CREEK 11032936 | WILLOW CREEK 1103 | HUMBOLDT | 32.9597 | 79.3849 | 82.84% | 19 | 24 | 100% | 0% | 0 | 0.12943 | 1 | 1.1228 | 0.14532 | High | High | Low | 1574 | 1201 | 0.12943
MIDDLETOWN 11021312 | MIDDLETOWN 1102 | HUMBOLDT | 9.8496 | 13.9462 | 100% | 1 | 10 | 100% | 0% | 0 | 0.046919 | 1 | 3.0951 | 0.14522 | Medium | Medium | High | 1575 | 1725 | 0.046919
MOUNTAIN QUARRIES 21011350 | MOUNTAIN QUARRIES 2101 | SIERRA | 21.7386 | 30.8372 | 63.86% | 7 | 7 | 100% | 0% | 0 | 0.058591 | 1 | 2.4681 | 0.14461 | Medium | Medium | Medium | 1576 | 1585 | 0.058591
RED BLUFF 11031702 | RED BLUFF 1103 | NORTH VALLEY | 15.929 | 23.8535 | 100% | 1 | 4 | 87.44% | 0% | 0 | 0.073954 | 1 | 1.9176 | 0.14181 | High | High | Low | 1577 | 1446 | 0.073954
OAKHURST 11035732 | OAKHURST 1103 | YOSEMITE | 3.391 | 10.7516 | 100% | 0 | 1 | 100% | 54.98% | 0 | 0.087919 | 1 | 1.6062 | 0.14122 | High | High | Low | 1578 | 1345 | 0.087919
TEMPLETON 2110N32 | TEMPLETON 2110 | LOS PADRES | 28.0596 | 53.4927 | 95.78% | 1 | 9 | 94.62% | 0% | 0 | 0.061984 | 1 | 2.2723 | 0.14084 | High | High | Medium | 1579 | 1539 | 0.061984
LAURELES 111268454 | LAURELES 1112 | CENTRAL COAST | 8.3342 | 11.1816 | 20.6% | 3 | 7 | 75.56% | 0% | 0 | 0.059265 | 1 | 2.3713 | 0.14054 | Medium | Medium | Medium | 1580 | 1576 | 0.059265
WYANDOTTE 110777578 | WYANDOTTE 1107 | NORTH VALLEY | 21.5731 | 10.2179 | 61.38% | 5 | 2 | 66.83% | 0% | 0 | 0.036666 | 1 | 3.8294 | 0.14041 | Medium | Medium | High | 1581 | 1925 | 0.036666
HOOPA 11013304 | HOOPA 1101 | HUMBOLDT | 16.9885 | 82.5702 | 98.71% | 15 | 4 | 100% | 0% | 0 | 0.086315 | 1 | 1.6263 | 0.14037 | High | High | Low | 1582 | 1353 | 0.086315
OAKLAND K 1104CR210 | OAKLAND K 1104 | EAST BAY | 2.8215 | 10 | 11.97% | 1 | 0 | 100% | 42.91% | 0 | 0.032016 | 1 | 4.383 | 0.14033 | Medium | Medium | High | 1583 | 2047 | 0.032016
MIDDLETOWN 1103830 | MIDDLETOWN 1103 | HUMBOLDT | 23.5041 | 79 | 88.01% | 1 | 2 | 60.51% | 36.87% | 0 | 0.059437 | 1 | 2.354 | 0.13991 | Medium | Medium | Medium | 1584 | 1572 | 0.059437
CURTIS 1704803 | CURTIS 1704 | YOSEMITE | 9.5141 | 57.4155 | 65.91% | 1 | 6 | 100% | 27.61% | 0 | 0.05233 | 1 | 2.6661 | 0.13952 | Medium | Medium | Medium | 1585 | 1658 | 0.05233
OREGON TRAIL 11021584 | OREGON TRAIL 1102 | NORTH VALLEY | 13.0863 | 23.8771 | 100% | 1 | 4 | 100% | 0% | 0 | 0.050417 | 1 | 2.7558 | 0.13894 | Medium | Medium | Medium | 1586 | 1677 | 0.050417
CURTIS 1705CB | CURTIS 1705 | YOSEMITE | 13.2215 | 11.2937 | 56.4% | 2 | 15 | 96.23% | 0% | 0 | 0.040107 | 1 | 3.4615 | 0.13883 | Medium | Medium | High | 1587 | 1854 | 0.040107
HIGGINS 1104324510 | HIGGINS 1104 | SIERRA | 12.4769 | 10 | 100% | 3 | 3 | 100% | 0% | 0 | 0.046303 | 1 | 2.9958 | 0.13872 | Medium | Medium | Medium | 1588 | 1735 | 0.046303
HALF MOON BAY 11022032 | HALF MOON BAY 1102 | PENINSULA | 3.27 | 24.2985 | 27.09% | 1 | 0 | 29.71% | 73.93% | 0 | 0.032761 | 1 | 4.2337 | 0.1387 | Medium | Medium | High | 1589 | 2017 | 0.032761
LAURELES 11116421 | LAURELES 1111 | CENTRAL COAST | 1.7279 | 54.1809 | 100% | 1 | 1 | 100% | 0% | 0 | 0.065512 | 1 | 2.115 | 0.13856 | High | High | Low | 1590 | 1512 | 0.065512
BUELLTON 1101Y06 | BUELLTON 1101 | LOS PADRES | 29.0172 | 49.4932 | 60.5% | 0 | 10 | 72.26% | 0% | 0 | 0.079416 | 1 | 1.7409 | 0.13826 | High | High | Low | 1591 | 1403 | 0.079416
SHINGLE SPRINGS 11038752 | SHINGLE SPRINGS 1103 | SIERRA | 1.8752 | 10 | 77.05% | 0 | 1 | 100% | 7.72% | 0 | 0.040295 | 1 | 3.4298 | 0.1382 | Medium | Medium | High | 1592 | 1848 | 0.040295
STILLWATER 1102CB | STILLWATER 1102 | NORTH VALLEY | 25.0709 | 15.0844 | 83.36% | 3 | 7 | 99.96% | 0% | 0 | 0.066396 | 1 | 2.0763 | 0.13786 | High | High | Low | 1593 | 1502 | 0.066396
BUELLTON 1101Y36 | BUELLTON 1101 | LOS PADRES | 33.0581 | 70.2256 | 71.54% | 1 | 11 | 92.67% | 5.931% | 1 | 0.081946 | 1 | 1.6819 | 0.13782 | High | High | Low | 1594 | 1383 | 0.081946
DIAMOND SPRINGS 11062100 | DIAMOND SPRINGS 1106 | SIERRA | 38.9747 | 13.5244 | 95.18% | 3 | 8 | 100% | 0% | 0 | 0.064847 | 1 | 2.1227 | 0.13765 | High | High | Low | 1595 | 1514 | 0.064847
WOODACRE 11021280 | WOODACRE 1102 | NORTH BAY | 10.5964 | 14.7487 | 31.13% | 2 | 14 | 100% | 0% | 0 | 0.034114 | 1 | 4.0304 | 0.1375 | Medium | Medium | High | 1596 | 1973 | 0.034114
WEIMAR 11012740 | WEIMAR 1101 | SIERRA | 19.1962 | 52.0643 | 71.74% | 1 | 4 | 100% | 0% | 0 | 0.080042 | 1 | 1.7168 | 0.13742 | High | High | Low | 1597 | 1398 | 0.080042
OAKLAND K 1104CB | OAKLAND K 1104 | EAST BAY | 2.7076 | 10 | 13.99% | 1 | 4 | 100% | 34.6% | 0 | 0.030956 | 1 | 4.4174 | 0.13675 | Medium | Medium | High | 1598 | 2071 | 0.030956
SHINGLE SPRINGS 210911092 | SHINGLE SPRINGS 2109 | SIERRA | 22.1149 | 21.1094 | 82.77% | 7 | 7 | 100% | 0% | 0 | 0.081649 | 1 | 1.6738 | 0.13667 | High | High | Low | 1599 | 1386 | 0.081649
FORT BRAGG A 110235592 | FORT BRAGG A 1102 | HUMBOLDT | 13.0568 | 10.5094 | 9.263% | 19 | 29 | 100% | 0% | 0 | 0.068352 | 1 | 1.999 | 0.13663 | High | High | Low | 1600 | 1481 | 0.068352
FULTON 110746958 | FULTON 1107 | SONOMA | 0.032131 | 10 | 100% | 0 | 0 | 6.208% | 100% | 0 | 0.055255 | 1 | 2.4591 | 0.13588 | Medium | Medium | Medium | 1601 | 1622 | 0.055255
LOS GATOS 1107CB | LOS GATOS 1107 | DE ANZA | 13.6639 | 15.4902 | 38.19% | 1 | 13 | 86.42% | 10.54% | 0 | 0.041286 | 1 | 3.2819 | 0.1355 | Medium | Medium | High | 1602 | 1831 | 0.041286
BELL 11082226 | BELL 1108 | SIERRA | 24.7638 | 11.2765 | 87.34% | 1 | 8 | 97.2% | 0% | 0 | 0.057141 | 1 | 2.363 | 0.13503 | Medium | Medium | Medium | 1603 | 1603 | 0.057141
GARBERVILLE 11011750 | GARBERVILLE 1101 | HUMBOLDT | 14.3678 | 85.1825 | 100% | 14 | 8 | 96.86% | 0% | 0 | 0.081262 | 1 | 1.6609 | 0.13497 | High | High | Low | 1604 | 1388 | 0.081262
BUCKS CREEK 1101CB | BUCKS CREEK 1101 | NORTH VALLEY | 20.005 | 83.6146 | 6.119% | 5 | 12 | 100% | 23.08% | 0 | 0.080342 | 1 | 1.6795 | 0.13494 | High | High | Low | 1605 | 1395 | 0.080342
PARADISE 110343008 | PARADISE 1103 | NORTH VALLEY | 12.9696 | 10 | 78.07% | 7 | 5 | 99.92% | 17.25% | 1 | 0.037995 | 1 | 3.5408 | 0.13453 | Medium | Medium | High | 1606 | 1898 | 0.037995
STANISLAUS 1702CB | STANISLAUS 1702 | YOSEMITE | 7.977 | 43.3363 | 28.21% | 1 | 3 | 100% | 19.55% | 0 | 0.043216 | 1 | 3.112 | 0.13449 | Medium | Medium | High | 1607 | 1791 | 0.043216
CORRAL 1102CB | CORRAL 1102 | STOCKTON | 17.6005 | 19.3826 | 70.6% | 2 | 10 | 83.31% | 0% | 0 | 0.04296 | 1 | 3.1263 | 0.13431 | Medium | Medium | High | 1608 | 1799 | 0.04296
PINE GROVE 11013166 | PINE GROVE 1101 | STOCKTON | 12.5063 | 11.3177 | 79.03% | 1 | 18 | 100% | 0% | 0 | 0.045896 | 1 | 2.919 | 0.13397 | Medium | Medium | Medium | 1609 | 1747 | 0.045896
SAN LEANDRO U 1109CR002 | SAN LEANDRO U 1109 | MISSION | 7.0761 | 10 | 24.57% | 6 | 16 | 90.45% | 0% | 0 | 0.040555 | 1 | 3.3026 | 0.13394 | Medium | Medium | High | 1610 | 1840 | 0.040555
WILLOW CREEK 110347966 | WILLOW CREEK 1103 | HUMBOLDT | 17.0216 | 48.5214 | 76.15% | 20 | 19 | 100% | 0% | 0 | 0.11952 | 1 | 1.1197 | 0.13384 | High | High | Low | 1611 | 1225 | 0.11952
SALMON CREEK 1101194 | SALMON CREEK 1101 | SONOMA | 6.5546 | 49.1883 | 4.108% | 3 | 3 | 77.1% | 22.41% | 0 | 0.053234 | 1 | 2.5104 | 0.13364 | Medium | Medium | Medium | 1612 | 1643 | 0.053234
MONTICELLO 110137384 | MONTICELLO 1101 | NORTH BAY | 9.3433 | 47.0333 | 65.93% | 7 | 4 | 99.86% | 0% | 0 | 0.054846 | 1 | 2.4323 | 0.1334 | Medium | Medium | Medium | 1613 | 1627 | 0.054846
PACIFICA 110311153 | PACIFICA 1103 | PENINSULA | 0.48816 | 27.9974 | 36.15% | 0 | 1 | 5.373% | 100% | 0 | 0.038047 | 1 | 3.4976 | 0.13307 | Medium | Medium | High | 1614 | 1897 | 0.038047
CURTIS 170210940 | CURTIS 1702 | YOSEMITE | 9.3161 | 16.9626 | 82.71% | 2 | 8 | 88.08% | 0% | 0 | 0.036211 | 1 | 3.6749 | 0.13307 | Medium | Medium | High | 1615 | 1929 | 0.036211
OAKHURST 110210100 | OAKHURST 1102 | YOSEMITE | 9.1816 | 28.1335 | 94.5% | 4 | 24 | 77.46% | 0% | 0 | 0.054576 | 1 | 2.4338 | 0.13282 | Medium | Medium | Medium | 1616 | 1631 | 0.054576
COTATI 1103148 | COTATI 1103 | SONOMA | 14.0913 | 49.2874 | 1.408% | 9 | 10 | 90.64% | 0% | 0 | 0.066855 | 1 | 1.9842 | 0.13266 | High | High | Low | 1617 | 1498 | 0.066855
WOODSIDE 1104555372 | WOODSIDE 1104 | PENINSULA | 4.1602 | 10 | 35.51% | 2 | 3 | 100% | 0% | 0 | 0.02737 | 1 | 4.8418 | 0.13252 | Medium | Medium | High | 1618 | 2182 | 0.02737
MILPITAS 1109XR524 | MILPITAS 1109 | SAN JOSE | 7.8802 | 65.8723 | 90.15% | 0 | 1 | 82.17% | 0% | 0 | 0.042366 | 1 | 3.1206 | 0.13221 | Medium | Medium | High | 1619 | 1810 | 0.042366
HOOPA 11013174 | HOOPA 1101 | HUMBOLDT | 17.6485 | 69.5085 | 99.93% | 19 | 10 | 80.04% | 0% | 0 | 0.11313 | 1 | 1.1672 | 0.13204 | High | High | Low | 1620 | 1244 | 0.11313
LUCERNE 1103630 | LUCERNE 1103 | HUMBOLDT | 12.5736 | 13.6837 | 90.26% | 2 | 19 | 92.62% | 0% | 0 | 0.043155 | 1 | 3.0456 | 0.13143 | Medium | Medium | Medium | 1621 | 1794 | 0.043155
STAFFORD 11021048 | STAFFORD 1102 | NORTH BAY | 4.9722 | 28.2651 | 55.55% | 1 | 7 | 93.63% | 17.79% | 1 | 0.042409 | 1 | 3.0962 | 0.13131 | Medium | Medium | High | 1622 | 1809 | 0.042409
LOS GATOS 1108LB86 | LOS GATOS 1108 | DE ANZA | 4.2689 | 10 | 37.07% | 3 | 5 | 80.57% | 12.91% | 0 | 0.033788 | 1 | 3.8848 | 0.13126 | Medium | Medium | High | 1623 | 1982 | 0.033788
DUNBAR 110297160 | DUNBAR 1102 | SONOMA | 0.058569 | 82.8928 | 100% | 0 | 0 | 100% | 0% | 0 | 0.046095 | 1 | 2.8466 | 0.13122 | Medium | Medium | Medium | 1624 | 1741 | 0.046095
WISHON 1101CB | WISHON 1101 | YOSEMITE | 7.7822 | 34.1369 | 78.45% | 1 | 2 | 100% | 51.22% | 1 | 0.074616 | 1 | 1.7546 | 0.13092 | High | High | Low | 1625 | 1441 | 0.074616
EL CERRITO G 1112CB | EL CERRITO G 1112 | EAST BAY | 0.64797 | 10 | 0% | 0 | 0 | 9.809% | 100% | 0 | 0.02588 | 1 | 4.9956 | 0.12929 | Medium | Medium | High | 1626 | 2217 | 0.02588
SILVERADO 2102CB | SILVERADO 2102 | NORTH BAY | 0.45935 | 10 | 0% | 0 | 0 | 26.76% | 100% | 0 | 0.034737 | 1 | 3.7165 | 0.1291 | Medium | Medium | High | 1627 | 1957 | 0.034737
DIAMOND SPRINGS 11042093 | DIAMOND SPRINGS 1104 | SIERRA | 7.2925 | 22.8545 | 79.86% | 0 | 2 | 83.65% | 44.87% | 0 | 0.053967 | 1 | 2.3806 | 0.12847 | Medium | Medium | Medium | 1628 | 1637 | 0.053967
HALSEY 110176178 | HALSEY 1101 | SIERRA | 19.4389 | 10 | 66.26% | 6 | 14 | 96.3% | 0% | 0 | 0.050379 | 1 | 2.5491 | 0.12842 | Medium | Medium | Medium | 1629 | 1679 | 0.050379
GARBERVILLE 11021510 | GARBERVILLE 1102 | HUMBOLDT | 13.0211 | 67.6864 | 30.88% | 5 | 7 | 100% | 0% | 0 | 0.063582 | 1 | 2.0147 | 0.1281 | High | High | Low | 1630 | 1527 | 0.063582
CLARK ROAD 110247006 | CLARK ROAD 1102 | NORTH VALLEY | 4.5495 | 10 | 42.4% | 2 | 3 | 100% | 41.72% | 0 | 0.037887 | 1 | 3.3709 | 0.12771 | Medium | Medium | High | 1631 | 1899 | 0.037887
ORINDA 0401N545R | ORINDA 0401 | DIABLO | 4.3157 | 10 | 9.802% | 1 | 11 | 83.77% | 52.25% | 0 | 0.038927 | 1 | 3.2801 | 0.12768 | Medium | Medium | High | 1632 | 1882 | 0.038927
OILFIELDS 1103N62 | OILFIELDS 1103 | CENTRAL COAST | 5.5689 | 75.4181 | 98.3% | 0 | 2 | 100% | 0% | 0 | 0.05809 | 1 | 2.1974 | 0.12764 | Medium | Medium | Low | 1633 | 1594 | 0.05809
SOBRANTE 1102CB | SOBRANTE 1102 | DIABLO | 10.2599 | 28.2629 | 22.78% | 2 | 15 | 98.33% | 12.04% | 0 | 0.042314 | 1 | 3.0143 | 0.12755 | Medium | Medium | Medium | 1634 | 1812 | 0.042314
TYLER 110585132 | TYLER 1105 | NORTH VALLEY | 30.9692 | 56.9117 | 100% | 0 | 21 | 100% | 0% | 0 | 0.075876 | 1 | 1.6764 | 0.1272 | High | High | Low | 1635 | 1435 | 0.075876
CEDAR CREEK 11011710 | CEDAR CREEK 1101 | NORTH VALLEY | 0.076338 | 70.3009 | 100% | 0 | 0 | 100% | 100% | 0 | 0.18445 | 1 | 0.68738 | 0.12679 | High | High | Low | 1636 | 1083 | 0.18445
CABRILLO 1103Y46 | CABRILLO 1103 | LOS PADRES | 20.218 | 55.531 | 56.98% | 1 | 5 | 42.55% | 0% | 0 | 0.043329 | 1 | 2.9259 | 0.12678 | Medium | Medium | Medium | 1637 | 1788 | 0.043329
COTTONWOOD 11011610 | COTTONWOOD 1101 | NORTH VALLEY | 38.431 | 59.7392 | 100% | 4 | 5 | 100% | 0% | 0 | 0.097181 | 1 | 1.3016 | 0.12649 | High | High | Low | 1638 | 1305 | 0.097181
EL DORADO PH 210163464 | EL DORADO PH 2101 | SIERRA | 13.6531 | 63.9369 | 100% | 0 | 2 | 100% | 36.69% | 1 | 0.084238 | 1 | 1.4999 | 0.12635 | High | High | Low | 1639 | 1368 | 0.084238
DIAMOND SPRINGS 110610587 | DIAMOND SPRINGS 1106 | SIERRA | 21.9902 | 32.7231 | 99.97% | 4 | 2 | 100% | 0% | 0 | 0.060422 | 1 | 2.0865 | 0.12607 | Medium | Medium | Low | 1640 | 1562 | 0.060422
BROWNS VALLEY 11011268 | BROWNS VALLEY 1101 | SIERRA | 10.9063 | 24.7365 | 96.96% | 1 | 7 | 100% | 0% | 0 | 0.046288 | 1 | 2.7133 | 0.12559 | Medium | Medium | Medium | 1641 | 1736 | 0.046288
CLEAR LAKE 1101406 | CLEAR LAKE 1101 | HUMBOLDT | 10.6464 | 76.543 | 93.36% | 0 | 1 | 32.19% | 54.28% | 0 | 0.052045 | 1 | 2.4044 | 0.12514 | Medium | Medium | Medium | 1642 | 1660 | 0.052045
MILPITAS 110987800 | MILPITAS 1109 | SAN JOSE | 1.61 | 77.3424 | 100% | 0 | 0 | 100% | 0% | 0 | 0.044454 | 1 | 2.8069 | 0.12478 | Medium | Medium | Medium | 1643 | 1769 | 0.044454
DEL MONTE 21043088 | DEL MONTE 2104 | CENTRAL COAST | 15.4442 | 31.6262 | 48.83% | 2 | 7 | 100% | 0% | 0 | 0.063303 | 1 | 1.9688 | 0.12463 | High | High | Low | 1644 | 1528 | 0.063303
KING CITY 11037038 | KING CITY 1103 | CENTRAL COAST | 17.5881 | 72.8479 | 99.95% | 0 | 5 | 81.26% | 0% | 0 | 0.058354 | 1 | 2.1255 | 0.12403 | Medium | Medium | Low | 1645 | 1589 | 0.058354
MARTELL 110111244 | MARTELL 1101 | STOCKTON | 21.6798 | 10 | 87.92% | 5 | 3 | 99.45% | 0% | 0 | 0.048788 | 1 | 2.5388 | 0.12386 | Medium | Medium | Medium | 1646 | 1698 | 0.048788
WHITMORE 11011594 | WHITMORE 1101 | NORTH VALLEY | 24.2582 | 53.3221 | 84.24% | 2 | 1 | 100% | 29.39% | 0 | 0.09099 | 1 | 1.3571 | 0.12348 | High | High | Low | 1647 | 1335 | 0.09099
WYANDOTTE 11031504 | WYANDOTTE 1103 | NORTH VALLEY | 11.3639 | 10 | 55.8% | 3 | 8 | 77.24% | 0% | 0 | 0.032944 | 1 | 3.7481 | 0.12348 | Medium | Medium | High | 1648 | 2011 | 0.032944
WYANDOTTE 110796390 | WYANDOTTE 1107 | NORTH VALLEY | 8.1841 | 10 | 71.02% | 4 | 1 | 80.42% | 0% | 0 | 0.033709 | 1 | 3.6617 | 0.12343 | Medium | Medium | High | 1649 | 1987 | 0.033709
CLOVERDALE 11024646 | CLOVERDALE 1102 | SONOMA | 14.4526 | 74.9071 | 80.61% | 2 | 4 | 97.6% | 0% | 0 | 0.059667 | 1 | 2.0674 | 0.12335 | Medium | Medium | Low | 1650 | 1569 | 0.059667
OCEANO 1104Q12 | OCEANO 1104 | LOS PADRES | 9.3393 | 55.4094 | 73.47% | 0 | 5 | 57.92% | 27.55% | 0 | 0.051953 | 1 | 2.3715 | 0.12321 | Medium | Medium | Medium | 1651 | 1661 | 0.051953
LOW GAP 11014086 | LOW GAP 1101 | HUMBOLDT | 11.4979 | 83.0021 | 100% | 1 | 2 | 100% | 0% | 0 | 0.090624 | 1 | 1.3559 | 0.12288 | High | High | Low | 1652 | 1336 | 0.090624
SWIFT 2110XR332 | SWIFT 2110 | SAN JOSE | 49.6657 | 79.4868 | 80.03% | 0 | 0 | 100% | 0% | 0 | 0.049698 | 1 | 2.4667 | 0.12259 | Medium | Medium | Medium | 1653 | 1686 | 0.049698
DEL MONTE 210436720 | DEL MONTE 2104 | CENTRAL COAST | 6.1198 | 15.0991 | 78.82% | 1 | 2 | 76.61% | 0% | 0 | 0.039935 | 1 | 3.0657 | 0.12243 | Medium | Medium | Medium | 1654 | 1860 | 0.039935
GUALALA 111223444 | GUALALA 1112 | HUMBOLDT | 14.5206 | 71.4539 | 16.53% | 7 | 15 | 100% | 0% | 0 | 0.069914 | 1 | 1.7456 | 0.12204 | High | High | Low | 1655 | 1470 | 0.069914
ROB ROY 210410960 | ROB ROY 2104 | CENTRAL COAST | 17.8204 | 13.6401 | 49.6% | 26 | 6 | 63.39% | 0% | 0 | 0.03619 | 1 | 3.3702 | 0.12197 | Medium | Medium | High | 1656 | 1930 | 0.03619
APPLE HILL 110313312 | APPLE HILL 1103 | SIERRA | 11.1165 | 24.9201 | 69.91% | 1 | 7 | 61.36% | 40.78% | 0 | 0.055379 | 1 | 2.1929 | 0.12144 | Medium | Medium | Low | 1657 | 1621 | 0.055379
SAN RAFAEL 110991742 | SAN RAFAEL 1109 | NORTH BAY | 5.7363 | 10 | 72.58% | 2 | 1 | 66.36% | 0% | 0 | 0.033036 | 1 | 3.657 | 0.12081 | Medium | Medium | High | 1658 | 2009 | 0.033036
VALLEY VIEW 1106 | VALLEY VIEW 1106 | EAST BAY | 0.037566 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 4.232 | 0.12066 | Medium | Medium | High | 1659 | 2136 | 0.028512
OAKHURST 11016220 | OAKHURST 1101 | YOSEMITE | 20.9199 | 34.4609 | 88.69% | 0 | 15 | 100% | 0% | 0 | 0.060711 | 1 | 1.9872 | 0.12065 | Medium | Medium | Low | 1660 | 1559 | 0.060711
EDES 1112CR312 | EDES 1112 | EAST BAY | 3.6853 | 22.7087 | 18.65% | 2 | 11 | 99.92% | 20.18% | 0 | 0.036955 | 1 | 3.2611 | 0.12051 | Medium | Medium | High | 1661 | 1919 | 0.036955
WYANDOTTE 110366146 | WYANDOTTE 1103 | NORTH VALLEY | 0.1568 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.032454 | 1 | 3.7133 | 0.12051 | Medium | Medium | High | 1662 | 2029 | 0.032454
LAKEWOOD 2224D522R | LAKEWOOD 2224 | DIABLO | 0.67815 | 10 | 23.16% | 0 | 1 | 25.38% | 100% | 0 | 0.036972 | 1 | 3.2556 | 0.12036 | Medium | Medium | High | 1663 | 1918 | 0.036972
CURTIS 1704CB | CURTIS 1704 | YOSEMITE | 13.7734 | 18.3001 | 79.09% | 1 | 5 | 96.53% | 0% | 0 | 0.035785 | 1 | 3.3627 | 0.12033 | Medium | Medium | High | 1664 | 1939 | 0.035785
VIEJO 2203CB | VIEJO 2203 | CENTRAL COAST | 3.0922 | 10 | 21.75% | 26 | 9 | 92.05% | 0% | 0 | 0.039672 | 1 | 3.0156 | 0.11963 | Medium | Medium | Medium | 1665 | 1866 | 0.039672
HAMILTON BRANCH 110187784 | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.4473 | 18.1172 | 99.8% | 0 | 3 | 100% | 0% | 0 | 0.031933 | 1 | 3.7387 | 0.11939 | Medium | Medium | High | 1666 | 2049 | 0.031933
GEYSERVILLE 110179788 | GEYSERVILLE 1101 | SONOMA | 36.3345 | 85.553 | 97.66% | 5 | 7 | 86.55% | 0% | 0 | 0.081783 | 1 | 1.4593 | 0.11934 | High | High | Low | 1667 | 1385 | 0.081783
MIRABEL 1102334 | MIRABEL 1102 | SONOMA | 5.6083 | 39.7869 | 41.25% | 2 | 2 | 61.12% | 47.7% | 0 | 0.038421 | 1 | 3.0999 | 0.1191 | Medium | Medium | High | 1668 | 1890 | 0.038421
WYANDOTTE 110913052 | WYANDOTTE 1109 | NORTH VALLEY | 19.6896 | 23.3384 | 63.11% | 1 | 2 | 99.03% | 0% | 0 | 0.035725 | 1 | 3.319 | 0.11857 | Medium | Medium | High | 1669 | 1941 | 0.035725
EL CERRITO G 1105BR194 | EL CERRITO G 1105 | EAST BAY | 3.0539 | 15.352 | 23.01% | 1 | 2 | 58.3% | 30.42% | 0 | 0.026764 | 1 | 4.423 | 0.11838 | Medium | Medium | High | 1670 | 2196 | 0.026764
DOBBINS 11015202 | DOBBINS 1101 | SIERRA | 15.7094 | 33.0821 | 86.66% | 1 | 6 | 92.01% | 0% | 0 | 0.059877 | 1 | 1.9749 | 0.11825 | Medium | Medium | Low | 1671 | 1565 | 0.059877
RACETRACK 17038120 | RACETRACK 1703 | YOSEMITE | 8.8205 | 16.6525 | 57.46% | 3 | 10 | 100% | 16.02% | 1 | 0.03955 | 1 | 2.9886 | 0.1182 | Medium | Medium | Medium | 1672 | 1871 | 0.03955
CAROLANDS 04049024 | CAROLANDS 0404 | PENINSULA | 3.5964 | 10 | 16.66% | 1 | 9 | 99.05% | 0% | 0 | 0.033705 | 1 | 3.5061 | 0.11817 | Medium | Medium | High | 1673 | 1988 | 0.033705
MENLO 11031721 | MENLO 1103 | PENINSULA | 6.795 | 58.431 | 89.52% | 4 | 2 | 100% | 0% | 0 | 0.044995 | 1 | 2.626 | 0.11816 | Medium | Medium | Medium | 1674 | 1766 | 0.044995
VOLTA 11021650 | VOLTA 1102 | NORTH VALLEY | 21.7066 | 54.4838 | 100% | 4 | 9 | 100% | 0% | 0 | 0.079578 | 1 | 1.4837 | 0.11807 | High | High | Low | 1675 | 1402 | 0.079578
BRIDGEVILLE 110255612 | BRIDGEVILLE 1102 | HUMBOLDT | 22.2453 | 91.4485 | 100% | 11 | 10 | 100% | 97.29% | 1 | 0.34757 | 1 | 0.33885 | 0.11777 | High | High | Low | 1676 | 921 | 0.34757
SARATOGA 1107LC26 | SARATOGA 1107 | DE ANZA | 5.6494 | 10 | 35.72% | 5 | 4 | 100% | 14.43% | 1 | 0.032092 | 1 | 3.6662 | 0.11766 | Medium | Medium | High | 1677 | 2043 | 0.032092
FROGTOWN 170291134 | FROGTOWN 1702 | STOCKTON | 14.7309 | 23.5525 | 81.54% | 0 | 12 | 92.7% | 0% | 0 | 0.060562 | 1 | 1.9356 | 0.11722 | Medium | Medium | Low | 1678 | 1561 | 0.060562
VACAVILLE 11088762 | VACAVILLE 1108 | SACRAMENTO | 13.206 | 54.7168 | 79.67% | 1 | 3 | 78.91% | 0% | 0 | 0.042096 | 1 | 2.7832 | 0.11716 | Medium | Medium | Medium | 1679 | 1817 | 0.042096
LUCERNE 1106664 | LUCERNE 1106 | HUMBOLDT | 6.0536 | 25.8226 | 47.99% | 4 | 24 | 54.26% | 0% | 0 | 0.038531 | 1 | 3.0381 | 0.11706 | Medium | Medium | Medium | 1680 | 1889 | 0.038531
PLACERVILLE 111219712 | PLACERVILLE 1112 | SIERRA | 12.7698 | 10 | 100% | 3 | 10 | 97.13% | 0% | 0 | 0.045629 | 1 | 2.5586 | 0.11675 | Medium | Medium | Medium | 1681 | 1753 | 0.045629
UKIAH 1111534 | UKIAH 1111 | HUMBOLDT | 18.7979 | 74.5032 | 100% | 2 | 4 | 89.62% | 0% | 0 | 0.064153 | 1 | 1.8196 | 0.11673 | High | High | Low | 1682 | 1525 | 0.064153
SPRUCE 0401BR316 | SPRUCE 0401 | EAST BAY | 4.123 | 16.22 | 7.456% | 3 | 5 | 100% | 23.86% | 0 | 0.02375 | 1 | 4.8945 | 0.11624 | Medium | Medium | High | 1683 | 2286 | 0.02375
WILLITS 11032506 | WILLITS 1103 | HUMBOLDT | 12.7779 | 67.5224 | 88.76% | 15 | 4 | 100% | 16.88% | 0 | 0.06476 | 1 | 1.7937 | 0.11616 | High | High | Low | 1684 | 1516 | 0.06476
AUBERRY 1101R2578 | AUBERRY 1101 | FRESNO | 46.349 | 12.9087 | 87.94% | 4 | 13 | 100% | 0% | 0 | 0.077203 | 1 | 1.5016 | 0.11593 | High | High | Low | 1685 | 1421 | 0.077203
HIGGINS 11041374 | HIGGINS 1104 | SIERRA | 7.2163 | 10 | 85.17% | 5 | 6 | 86.29% | 0% | 0 | 0.030394 | 1 | 3.8118 | 0.11586 | Medium | Medium | High | 1686 | 2080 | 0.030394
CALAVERAS CEMENT 110147968 | CALAVERAS CEMENT 1101 | STOCKTON | 17.4467 | 25.9867 | 99.97% | 0 | 4 | 100% | 6.1% | 1 | 0.055443 | 1 | 2.0882 | 0.11578 | Medium | Medium | Low | 1687 | 1620 | 0.055443
DEL MONTE 21032000 | DEL MONTE 2103 | CENTRAL COAST | 8.9713 | 10 | 21.71% | 13 | 11 | 98.79% | 0% | 0 | 0.037343 | 1 | 3.097 | 0.11565 | Medium | Medium | High | 1688 | 1909 | 0.037343
FORT BRAGG A 11041316 | FORT BRAGG A 1104 | HUMBOLDT | 13.2223 | 12.9501 | 11.54% | 9 | 10 | 96.48% | 0% | 0 | 0.036376 | 1 | 3.1775 | 0.11559 | Medium | Medium | High | 1689 | 1927 | 0.036376
RACETRACK 17039190 | RACETRACK 1703 | YOSEMITE | 8.9165 | 23.5588 | 27.68% | 2 | 6 | 100% | 0% | 0 | 0.034029 | 1 | 3.3879 | 0.11529 | Medium | Medium | High | 1690 | 1974 | 0.034029
AUBERRY 1101R314 | AUBERRY 1101 | FRESNO | 42.3727 | 21.0608 | 99.17% | 0 | 7 | 96.03% | 0% | 0 | 0.072346 | 1 | 1.5793 | 0.11426 | High | High | Low | 1691 | 1457 | 0.072346
HATTON 11022010 | HATTON 1102 | CENTRAL COAST | 4.0217 | 30.548 | 30.01% | 17 | 5 | 100% | 0% | 0 | 0.043055 | 1 | 2.6454 | 0.1139 | Medium | Medium | Medium | 1692 | 1795 | 0.043055
CORRAL 110236666 | CORRAL 1102 | STOCKTON | 17.3526 | 23.3821 | 99.95% | 1 | 2 | 96.21% | 0% | 0 | 0.046553 | 1 | 2.4463 | 0.11388 | Medium | Medium | Medium | 1693 | 1730 | 0.046553
HIGHLANDS 1102CB | HIGHLANDS 1102 | HUMBOLDT | 7.3244 | 28.1149 | 80.17% | 1 | 6 | 100% | 0% | 0 | 0.035726 | 1 | 3.1836 | 0.11374 | Medium | Medium | High | 1694 | 1940 | 0.035726
DUNBAR 1101CB | DUNBAR 1101 | SONOMA | 2.1801 | 23.6947 | 93.6% | 0 | 2 | 14.87% | 59.74% | 0 | 0.034709 | 1 | 3.2741 | 0.11364 | Medium | Medium | High | 1695 | 1958 | 0.034709
WISE 1102CB | WISE 1102 | SIERRA | 18.631 | 17.4842 | 45.37% | 6 | 22 | 98.52% | 0% | 0 | 0.0417 | 1 | 2.7235 | 0.11357 | Medium | Medium | Medium | 1696 | 1821 | 0.0417
HIGGINS 1104842642 | HIGGINS 1104 | SIERRA | 5.4882 | 10 | 100% | 3 | 1 | 94.43% | 0% | 0 | 0.032606 | 1 | 3.4791 | 0.11344 | Medium | Medium | High | 1697 | 2022 | 0.032606
MORGAN HILL 2104XR018 | MORGAN HILL 2104 | SAN JOSE | 4.9492 | 19.6923 | 100% | 0 | 3 | 46.16% | 0% | 0 | 0.03658 | 1 | 3.0953 | 0.11323 | Medium | Medium | High | 1698 | 1926 | 0.03658
SAND CREEK 11037420 | SAND CREEK 1103 | FRESNO | 23.394 | 10 | 99.98% | 4 | 4 | 100% | 0% | 0 | 0.04783 | 1 | 2.3612 | 0.11293 | Medium | Medium | Medium | 1699 | 1708 | 0.04783
LOS OSITOS 21033010 | LOS OSITOS 2103 | CENTRAL COAST | 30.8565 | 64.7553 | 97.74% | 3 | 10 | 99.12% | 0% | 0 | 0.057419 | 1 | 1.9613 | 0.11262 | Medium | Medium | Low | 1700 | 1600 | 0.057419
SCE TEHACHAPI 1101CB | SCE TEHACHAPI 1101 | KERN | 1.4276 | 82.1535 | 100% | 0 | 0 | 100% | 0% | 0 | 0.045873 | 1 | 2.4463 | 0.11222 | Medium | Medium | Medium | 1701 | 1748 | 0.045873
DESCHUTES 11011580 | DESCHUTES 1101 | NORTH VALLEY | 44.5215 | 20.6467 | 99.77% | 3 | 12 | 90.01% | 10.49% | 0 | 0.071696 | 1 | 1.5632 | 0.11207 | High | High | Low | 1702 | 1461 | 0.071696
SARATOGA 11075696 | SARATOGA 1107 | DE ANZA | 4.0107 | 10 | 57.71% | 6 | 9 | 65.93% | 4.474% | 0 | 0.029972 | 1 | 3.7269 | 0.1117 | Medium | Medium | High | 1703 | 2100 | 0.029972
HIGGINS 1104533648 | HIGGINS 1104 | SIERRA | 6.7529 | 10 | 96.99% | 2 | 3 | 100% | 0% | 0 | 0.034544 | 1 | 3.2267 | 0.11146 | Medium | Medium | High | 1704 | 1961 | 0.034544
SHINGLE SPRINGS 210511172 | SHINGLE SPRINGS 2105 | SIERRA | 2.0141 | 10 | 66.76% | 1 | 3 | 82.66% | 0% | 0 | 0.029323 | 1 | 3.7968 | 0.11133 | Medium | Medium | High | 1705 | 2116 | 0.029323
WOODSIDE 11018522 | WOODSIDE 1101 | PENINSULA | 0.74695 | 65.2984 | 0% | 1 | 0 | 7.949% | 85.4% | 0 | 0.029511 | 1 | 3.7573 | 0.11088 | Medium | Medium | High | 1706 | 2110 | 0.029511
POSO MOUNTAIN 21014456 | POSO MOUNTAIN 2101 | KERN | 23.5359 | 61.9546 | 91.99% | 0 | 4 | 100% | 0% | 0 | 0.052745 | 1 | 2.0977 | 0.11064 | Medium | Medium | Low | 1707 | 1652 | 0.052745
AUBERRY 1101CB | AUBERRY 1101 | FRESNO | 18.1441 | 19.2243 | 60.88% | 0 | 19 | 100% | 0% | 0 | 0.042195 | 1 | 2.6192 | 0.11052 | Medium | Medium | Medium | 1708 | 1813 | 0.042195
OILFIELDS 1103N48 | OILFIELDS 1103 | CENTRAL COAST | 47.0468 | 56.1397 | 99.69% | 2 | 26 | 100% | 0% | 0 | 0.075176 | 1 | 1.4634 | 0.11001 | High | High | Low | 1709 | 1437 | 0.075176
WEIMAR 11012084 | WEIMAR 1101 | SIERRA | 18.471 | 37.3973 | 99.11% | 2 | 13 | 100% | 0% | 0 | 0.066085 | 1 | 1.6608 | 0.10976 | High | High | Low | 1710 | 1505 | 0.066085
HIGHLANDS 1103482 | HIGHLANDS 1103 | HUMBOLDT | 23.7709 | 84.3418 | 64.96% | 1 | 10 | 92.07% | 0% | 0 | 0.046005 | 1 | 2.3829 | 0.10963 | Medium | Medium | Medium | 1711 | 1744 | 0.046005
SALT SPRINGS 21028442 | SALT SPRINGS 2102 | STOCKTON | 12.1299 | 48.4336 | 100% | 5 | 7 | 100% | 9.936% | 1 | 0.13919 | 1 | 0.78756 | 0.10962 | High | High | Low | 1712 | 1170 | 0.13919
STANISLAUS 1701CB | STANISLAUS 1701 | YOSEMITE | 6.8255 | 50.7734 | 38.45% | 1 | 4 | 100% | 0.8907% | 0 | 0.032969 | 1 | 3.3185 | 0.10941 | Medium | Medium | High | 1713 | 2010 | 0.032969
HIGHLANDS 1103CB | HIGHLANDS 1103 | HUMBOLDT | 10.5045 | 18.0278 | 65.06% | 2 | 6 | 87.07% | 0% | 0 | 0.034275 | 1 | 3.1863 | 0.10921 | Medium | Medium | High | 1714 | 1965 | 0.034275
HIGGINS 1107746082 | HIGGINS 1107 | SIERRA | 0.84187 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.032454 | 1 | 3.3644 | 0.10919 | Medium | Medium | High | 1715 | 2029 | 0.032454
FRUITLAND 114263170 | FRUITLAND 1142 | HUMBOLDT | 12.2406 | 74.2009 | 74.01% | 12 | 5 | 90.64% | 0% | 0 | 0.061047 | 1 | 1.7809 | 0.10872 | Medium | Medium | Low | 1716 | 1557 | 0.061047
HIGGINS 1109CB | HIGGINS 1109 | SIERRA | 22.2012 | 22.658 | 81.89% | 2 | 4 | 95.77% | 0% | 0 | 0.037105 | 1 | 2.9246 | 0.10852 | Medium | Medium | Medium | 1717 | 1914 | 0.037105
GREENBRAE 1103CB | GREENBRAE 1103 | NORTH BAY | 0.06411 | 10 | 0% | 0 | 0 | 1.278% | 100% | 0 | 0.02712 | 1 | 3.9968 | 0.10839 | Medium | Medium | High | 1718 | 2190 | 0.02712
MENDOCINO 1101CB | MENDOCINO 1101 | HUMBOLDT | 11.0353 | 11.0346 | 86.58% | 0 | 6 | 81.55% | 0% | 0 | 0.046385 | 1 | 2.3319 | 0.10817 | Medium | Medium | Medium | 1719 | 1734 | 0.046385
TEMPLETON 2113A12 | TEMPLETON 2113 | LOS PADRES | 40.4505 | 77.6946 | 67.36% | 2 | 5 | 100% | 23.89% | 1 | 0.092809 | 1 | 1.1655 | 0.10817 | High | High | Low | 1720 | 1325 | 0.092809
CURTIS 17029111 | CURTIS 1702 | YOSEMITE | 5.6752 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.032454 | 1 | 3.3314 | 0.10812 | Medium | Medium | High | 1721 | 2029 | 0.032454
HATTON 11019220 | HATTON 1101 | CENTRAL COAST | 2.6965 | 89.4573 | 0% | 1 | 3 | 100% | 51.79% | 0 | 0.059721 | 1 | 1.81 | 0.10809 | Medium | Medium | Low | 1722 | 1568 | 0.059721
MOUNTAIN QUARRIES 21011180 | MOUNTAIN QUARRIES 2101 | SIERRA | 12.8441 | 30.3787 | 92.22% | 1 | 2 | 100% | 9.293% | 0 | 0.048359 | 1 | 2.2311 | 0.10789 | Medium | Medium | Medium | 1723 | 1705 | 0.048359
OCEANO 1102V50 | OCEANO 1102 | LOS PADRES | 5.8788 | 10 | 32.53% | 6 | 4 | 56.2% | 0% | 0 | 0.031497 | 1 | 3.4105 | 0.10742 | Medium | Medium | High | 1724 | 2060 | 0.031497
LOW GAP 11014160 | LOW GAP 1101 | HUMBOLDT | 21.5735 | 61.654 | 100% | 10 | 5 | 99.51% | 0% | 0 | 0.082527 | 1 | 1.298 | 0.10712 | High | High | Low | 1725 | 1378 | 0.082527
MARIPOSA 21029490 | MARIPOSA 2102 | YOSEMITE | 4.2707 | 19.9086 | 45.43% | 0 | 1 | 100% | 49.91% | 0 | 0.044074 | 1 | 2.4205 | 0.10668 | Medium | Medium | Medium | 1726 | 1776 | 0.044074
FITCH MOUNTAIN 11134566 | FITCH MOUNTAIN 1113 | SONOMA | 10.4618 | 71.5628 | 83.49% | 1 | 5 | 60.29% | 0% | 0 | 0.042183 | 1 | 2.5279 | 0.10663 | Medium | Medium | Medium | 1727 | 1814 | 0.042183
RACETRACK 17036014 | RACETRACK 1703 | YOSEMITE | 6.8384 | 27.2462 | 64.22% | 2 | 1 | 100% | 0% | 0 | 0.037053 | 1 | 2.8715 | 0.1064 | Medium | Medium | Medium | 1728 | 1916 | 0.037053
CURTIS 170565908 | CURTIS 1705 | YOSEMITE | 12.8972 | 32.2499 | 79.87% | 2 | 10 | 77.15% | 0% | 0 | 0.036689 | 1 | 2.8987 | 0.10635 | Medium | Medium | Medium | 1729 | 1924 | 0.036689
MAPLE CREEK 1101CB | MAPLE CREEK 1101 | HUMBOLDT | 9.8748 | 78.7819 | 78.72% | 13 | 5 | 66.88% | 0% | 0 | 0.059846 | 1 | 1.7771 | 0.10635 | Medium | Medium | Low | 1730 | 1566 | 0.059846
POTTER VALLEY P H 11051904 | POTTER VALLEY P H 1105 | HUMBOLDT | 28.466 | 59.7756 | 95.28% | 1 | 23 | 70.74% | 17.93% | 1 | 0.078348 | 1 | 1.3548 | 0.10615 | High | High | Low | 1731 | 1409 | 0.078348
CALISTOGA 1101CB | CALISTOGA 1101 | NORTH BAY | 2.6498 | 39.1806 | 43.07% | 2 | 0 | 27.62% | 49.7% | 0 | 0.036018 | 1 | 2.9421 | 0.10597 | Medium | Medium | Medium | 1732 | 1934 | 0.036018
RACETRACK 170311270 | RACETRACK 1703 | YOSEMITE | 12.3885 | 27.441 | 56.51% | 3 | 6 | 100% | 0% | 0 | 0.03438 | 1 | 3.0786 | 0.10584 | Medium | Medium | High | 1733 | 1964 | 0.03438
BURNEY 11019042 | BURNEY 1101 | NORTH VALLEY | 3.0554 | 28.762 | 87.06% | 1 | 1 | 96.72% | 0% | 0 | 0.048736 | 1 | 2.1708 | 0.1058 | Medium | Medium | Low | 1734 | 1699 | 0.048736
FULTON 1102287172 | FULTON 1102 | SONOMA | 17.3701 | 47.5802 | 77.47% | 4 | 10 | 64.9% | 11.1% | 0 | 0.043179 | 1 | 2.4495 | 0.10577 | Medium | Medium | Medium | 1735 | 1793 | 0.043179
RINCON 1102CB | RINCON 1102 | SONOMA | 3.4953 | 21.5241 | 28.33% | 2 | 6 | 98.07% | 7.215% | 1 | 0.032618 | 1 | 3.2363 | 0.10556 | Medium | Medium | High | 1736 | 2021 | 0.032618
BUCKS CREEK 1103CB | BUCKS CREEK 1103 | NORTH VALLEY | 2.2994 | 96.1203 | 100% | 2 | 1 | 100% | 100% | 0 | 0.24438 | 1 | 0.43068 | 0.10525 | High | High | Low | 1737 | 1009 | 0.24438
COARSEGOLD 2103CB | COARSEGOLD 2103 | YOSEMITE | 38.4222 | 32.3373 | 83.55% | 1 | 26 | 100% | 0% | 0 | 0.056308 | 1 | 1.858 | 0.10462 | Medium | Medium | Low | 1738 | 1610 | 0.056308
BIG MEADOWS 21012246 | BIG MEADOWS 2101 | NORTH VALLEY | 1.3711 | 10 | 100% | 1 | 20 | 75.1% | 0% | 0 | 0.082406 | 1 | 1.2663 | 0.10435 | High | High | Low | 1739 | 1379 | 0.082406
ELECTRA 1101CB | ELECTRA 1101 | STOCKTON | 26.464 | 31.8119 | 57.82% | 4 | 8 | 100% | 0% | 0 | 0.042866 | 1 | 2.4294 | 0.10414 | Medium | Medium | Medium | 1740 | 1801 | 0.042866
VOLTA 11011568 | VOLTA 1101 | NORTH VALLEY | 23.0081 | 45.5317 | 55% | 0 | 5 | 100% | 29.05% | 0 | 0.072817 | 1 | 1.4267 | 0.10388 | High | High | Low | 1741 | 1452 | 0.072817
LAS GALLINAS A 1106CB | LAS GALLINAS A 1106 | NORTH BAY | 4.998 | 10 | 78.22% | 0 | 1 | 31.7% | 39.74% | 0 | 0.026841 | 1 | 3.8683 | 0.10383 | Medium | Medium | High | 1742 | 2195 | 0.026841
SHINGLE SPRINGS 210985766 | SHINGLE SPRINGS 2109 | SIERRA | 18.4459 | 50.1321 | 99.71% | 3 | 4 | 100% | 0% | 0 | 0.06111 | 1 | 1.6977 | 0.10374 | Medium | Medium | Low | 1743 | 1556 | 0.06111
SHADY GLEN 110132726 | SHADY GLEN 1101 | SIERRA | 12.4872 | 23.3088 | 84.95% | 3 | 6 | 100% | 0% | 0 | 0.047638 | 1 | 2.1742 | 0.10357 | Medium | Medium | Low | 1744 | 1713 | 0.047638
CHESTER 11022564 | CHESTER 1102 | NORTH VALLEY | 2.0894 | 10 | 100% | 0 | 3 | 93.3% | 0% | 0 | 0.047498 | 1 | 2.1797 | 0.10353 | Medium | Medium | Low | 1745 | 1718 | 0.047498
GREENBRAE 1103434 | GREENBRAE 1103 | NORTH BAY | 0.79973 | 10 | 68.06% | 2 | 1 | 55.44% | 2.889% | 0 | 0.020293 | 1 | 5.0736 | 0.10296 | Low | Low | High | 1746 | 2394 | 0.020293
BRUNSWICK 1103CB | BRUNSWICK 1103 | SIERRA | 6.0294 | 52.8154 | 37.6% | 9 | 3 | 59.53% | 34.21% | 0 | 0.031778 | 1 | 3.2375 | 0.10288 | Medium | Medium | High | 1747 | 2051 | 0.031778
NARROWS 2102CB | NARROWS 2102 | SIERRA | 22.8974 | 13.8368 | 78.07% | 2 | 5 | 93.68% | 0% | 0 | 0.029841 | 1 | 3.4435 | 0.10276 | Medium | Medium | High | 1748 | 2103 | 0.029841
VACAVILLE 11046542 | VACAVILLE 1104 | SACRAMENTO | 14.768 | 37.9322 | 37.99% | 1 | 5 | 100% | 0% | 0 | 0.034546 | 1 | 2.9717 | 0.10266 | Medium | Medium | Medium | 1749 | 1960 | 0.034546
HALSEY 11012414 | HALSEY 1101 | SIERRA | 14.7964 | 13.1515 | 76.48% | 3 | 9 | 100% | 0% | 0 | 0.050299 | 1 | 2.0384 | 0.10253 | Medium | Medium | Low | 1750 | 1681 | 0.050299
POSO MOUNTAIN 21033988 | POSO MOUNTAIN 2103 | KERN | 17.2368 | 49.5955 | 64.44% | 0 | 0 | 92.36% | 0% | 0 | 0.038161 | 1 | 2.6824 | 0.10236 | Medium | Medium | Medium | 1751 | 1895 | 0.038161
WEIMAR 11012058 | WEIMAR 1101 | SIERRA | 21.2651 | 19.5754 | 79.75% | 4 | 16 | 100% | 0% | 0 | 0.055164 | 1 | 1.8526 | 0.1022 | Medium | Medium | Low | 1752 | 1625 | 0.055164
PASO ROBLES 1104R12 | PASO ROBLES 1104 | LOS PADRES | 26.4117 | 63.4802 | 89.23% | 0 | 7 | 66.23% | 0% | 0 | 0.045549 | 1 | 2.2416 | 0.1021 | Medium | Medium | Medium | 1753 | 1754 | 0.045549
OREGON TRAIL 11041574 | OREGON TRAIL 1104 | NORTH VALLEY | 16.4858 | 16.0641 | 94.5% | 2 | 4 | 88.21% | 0% | 0 | 0.04716 | 1 | 2.1636 | 0.10204 | Medium | Medium | Low | 1754 | 1723 | 0.04716
HIGGINS 11077559 | HIGGINS 1107 | SIERRA | 4.3177 | 10 | 100% | 0 | 6 | 97.65% | 0% | 0 | 0.031488 | 1 | 3.2282 | 0.10165 | Medium | Medium | High | 1755 | 2061 | 0.031488
PLACERVILLE 1111CB | PLACERVILLE 1111 | SIERRA | 5.5179 | 10 | 61.74% | 2 | 10 | 83.46% | 0% | 0 | 0.033153 | 1 | 3.064 | 0.10158 | Medium | Medium | Medium | 1756 | 2003 | 0.033153
FORT BRAGG A 11014622 | FORT BRAGG A 1101 | HUMBOLDT | 13.4572 | 19.3216 | 4.804% | 12 | 12 | 100% | 0% | 0 | 0.066763 | 1 | 1.5197 | 0.10146 | High | High | Low | 1757 | 1499 | 0.066763
ELECTRA 110161816 | ELECTRA 1101 | STOCKTON | 12.191 | 16.1858 | 89% | 5 | 6 | 100% | 0% | 0 | 0.03728 | 1 | 2.7215 | 0.10146 | Medium | Medium | Medium | 1758 | 1910 | 0.03728
BRENTWOOD 2105B504R | BRENTWOOD 2105 | DIABLO | 7.4348 | 10 | 79.77% | 0 | 6 | 65.97% | 0% | 0 | 0.042733 | 1 | 2.3715 | 0.10134 | Medium | Medium | Medium | 1759 | 1804 | 0.042733
COTTONWOOD 11031348 | COTTONWOOD 1103 | NORTH VALLEY | 25.9721 | 33.8083 | 99.17% | 2 | 10 | 81.37% | 0% | 0 | 0.065681 | 1 | 1.5413 | 0.10123 | High | High | Low | 1760 | 1510 | 0.065681
HIGHLANDS 1103568 | HIGHLANDS 1103 | HUMBOLDT | 7.7314 | 14.5235 | 84.3% | 1 | 2 | 84.45% | 0% | 0 | 0.034657 | 1 | 2.9157 | 0.10105 | Medium | Medium | Medium | 1761 | 1959 | 0.034657
HAMILTON BRANCH 110137436 | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.0486 | 10 | 99.62% | 2 | 5 | 51.07% | 0% | 0 | 0.025995 | 1 | 3.8843 | 0.10097 | Medium | Medium | High | 1762 | 2215 | 0.025995
MORRO BAY 1102W22 | MORRO BAY 1102 | LOS PADRES | 4.8943 | 10 | 4.74% | 0 | 3 | 47.35% | 0% | 0 | 0.023875 | 1 | 4.2269 | 0.10092 | Medium | Medium | High | 1763 | 2280 | 0.023875
CALAVERAS CEMENT 1101585 | CALAVERAS CEMENT 1101 | STOCKTON | 14.1114 | 60.1241 | 100% | 0 | 9 | 100% | 0% | 0 | 0.061249 | 1 | 1.6439 | 0.10069 | Medium | Medium | Low | 1764 | 1554 | 0.061249
BIG RIVER 11015065 | BIG RIVER 1101 | HUMBOLDT | 2.2025 | 10 | 42.78% | 5 | 11 | 100% | 0% | 0 | 0.035469 | 1 | 2.8348 | 0.10055 | Medium | Medium | Medium | 1765 | 1947 | 0.035469
ELECTRA 11026014 | ELECTRA 1102 | STOCKTON | 28.5875 | 15.0573 | 83.7% | 1 | 14 | 100% | 0% | 0 | 0.051142 | 1 | 1.9639 | 0.10044 | Medium | Medium | Low | 1766 | 1670 | 0.051142
WYANDOTTE 110979932 | WYANDOTTE 1109 | NORTH VALLEY | 19.2875 | 10.6134 | 90.79% | 1 | 2 | 59.11% | 0% | 0 | 0.036019 | 1 | 2.7826 | 0.10022 | Medium | Medium | Medium | 1767 | 1933 | 0.036019
CALISTOGA 1102CB | CALISTOGA 1102 | NORTH BAY | 1.4649 | 10 | 27.88% | 0 | 0 | 51.57% | 53.48% | 0 | 0.030163 | 1 | 3.3194 | 0.10012 | Medium | Medium | High | 1768 | 2094 | 0.030163
MONTICELLO 11014360 | MONTICELLO 1101 | NORTH BAY | 7.4298 | 66.0263 | 57.84% | 4 | 3 | 80.69% | 0% | 0 | 0.035448 | 1 | 2.8213 | 0.10001 | Medium | Medium | Medium | 1769 | 1948 | 0.035448
VACAVILLE 1111CB | VACAVILLE 1111 | SACRAMENTO | 7.7902 | 19.0495 | 34.16% | 0 | 5 | 64.21% | 0% | 0 | 0.030405 | 1 | 3.282 | 0.099788 | Medium | Medium | High | 1770 | 2079 | 0.030405
MONTE RIO 1111292 | MONTE RIO 1111 | SONOMA | 14.6924 | 53.0276 | 14.56% | 3 | 9 | 74.19% | 33.55% | 0 | 0.046445 | 1 | 2.1476 | 0.099746 | Medium | Medium | Low | 1771 | 1733 | 0.046445
LUCERNE 1103CB | LUCERNE 1103 | HUMBOLDT | 4.1876 | 10 | 56.07% | 0 | 12 | 95.22% | 0% | 0 | 0.036043 | 1 | 2.7667 | 0.09972 | Medium | Medium | Medium | 1772 | 1932 | 0.036043
WOODSIDE 11049030 | WOODSIDE 1104 | PENINSULA | 2.2354 | 10 | 77.85% | 0 | 2 | 86.64% | 0% | 0 | 0.021812 | 1 | 4.57 | 0.099682 | Medium | Medium | High | 1773 | 2342 | 0.021812
MARIPOSA 210135244 | MARIPOSA 2101 | YOSEMITE | 17.3356 | 16.4968 | 77.7% | 2 | 10 | 100% | 23.66% | 0 | 0.045381 | 1 | 2.1925 | 0.099495 | Medium | Medium | Low | 1774 | 1758 | 0.045381
PURISIMA 1101Y44 | PURISIMA 1101 | LOS PADRES | 10.0257 | 87.5542 | 33.95% | 0 | 2 | 86.13% | 0% | 0 | 0.029127 | 1 | 3.4151 | 0.099473 | Medium | Medium | High | 1775 | 2118 | 0.029127
NARROWS 21052748 | NARROWS 2105 | SIERRA | 11.8577 | 19.7377 | 85.36% | 3 | 6 | 60.51% | 0% | 0 | 0.02804 | 1 | 3.5416 | 0.099307 | Medium | Medium | High | 1776 | 2163 | 0.02804
FOOTHILL 1102CB | FOOTHILL 1102 | LOS PADRES | 8.141 | 51.8091 | 56.43% | 3 | 6 | 82.95% | 0% | 0 | 0.034219 | 1 | 2.9019 | 0.099302 | Medium | Medium | Medium | 1777 | 1968 | 0.034219
HICKS 111660050 | HICKS 1116 | SAN JOSE | 7.9799 | 10 | 69.56% | 2 | 6 | 100% | 0% | 0 | 0.02949 | 1 | 3.3545 | 0.098924 | Medium | Medium | High | 1778 | 2111 | 0.02949
OCEANO 1102V56 | OCEANO 1102 | LOS PADRES | 9.7421 | 10 | 68.41% | 1 | 15 | 98.35% | 0% | 0 | 0.03877 | 1 | 2.5506 | 0.098886 | Medium | Medium | Medium | 1779 | 1885 | 0.03877
CURTIS 170390320 | CURTIS 1703 | YOSEMITE | 27.855 | 17.0394 | 100% | 4 | 21 | 100% | 0% | 0 | 0.10108 | 1 | 0.97587 | 0.098641 | High | High | Low | 1780 | 1291 | 0.10108
DESCHUTES 11011654 | DESCHUTES 1101 | NORTH VALLEY | 17.3592 | 41.2096 | 100% | 1 | 5 | 100% | 6.956% | 0 | 0.063997 | 1 | 1.5357 | 0.098281 | High | High | Low | 1781 | 1526 | 0.063997
PEORIA 170587222 | PEORIA 1705 | YOSEMITE | 5.2686 | 10 | 76.37% | 0 | 4 | 100% | 0% | 0 | 0.03317 | 1 | 2.9599 | 0.098179 | Medium | Medium | Medium | 1782 | 2002 | 0.03317
OAKLAND X 11066669 | OAKLAND X 1106 | EAST BAY | 0.23409 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.4389 | 0.098048 | Medium | Medium | High | 1783 | 2136 | 0.028512
CASTRO VALLEY 1108MR379 | CASTRO VALLEY 1108 | MISSION | 1.2345 | 10 | 98.65% | 0 | 0 | 78.3% | 9.302% | 0 | 0.026453 | 1 | 3.7001 | 0.09788 | Medium | Medium | High | 1784 | 2205 | 0.026453
LOS OSITOS 21037062 | LOS OSITOS 2103 | CENTRAL COAST | 12.2332 | 84.1604 | 73.22% | 2 | 3 | 100% | 0% | 0 | 0.046568 | 1 | 2.1004 | 0.097814 | Medium | Medium | Low | 1785 | 1729 | 0.046568
CLOVERDALE 110112719 | CLOVERDALE 1101 | SONOMA | 4.9181 | 80.6066 | 85.19% | 0 | 3 | 67.33% | 0% | 0 | 0.040502 | 1 | 2.4017 | 0.097273 | Medium | Medium | Medium | 1786 | 1842 | 0.040502
COARSEGOLD 21035020 | COARSEGOLD 2103 | YOSEMITE | 16.1848 | 19.8956 | 69.91% | 1 | 23 | 97.69% | 0% | 0 | 0.048835 | 1 | 1.987 | 0.097036 | Medium | Medium | Low | 1787 | 1697 | 0.048835
OCEANO 1104CB | OCEANO 1104 | LOS PADRES | 8.0054 | 24.7481 | 22.23% | 2 | 9 | 52.54% | 10.2% | 1 | 0.025849 | 1 | 3.7493 | 0.096918 | Medium | Medium | High | 1788 | 2218 | 0.025849
TEMPLETON 2110R06 | TEMPLETON 2110 | LOS PADRES | 5.1326 | 51.0168 | 86.51% | 3 | 1 | 19.81% | 33.5% | 0 | 0.040874 | 1 | 2.3652 | 0.096678 | Medium | Medium | Medium | 1789 | 1835 | 0.040874
PEORIA 17056697 | PEORIA 1705 | YOSEMITE | 4.1363 | 14.6236 | 100% | 1 | 4 | 100% | 0% | 0 | 0.036751 | 1 | 2.6171 | 0.096184 | Medium | Medium | Medium | 1790 | 1923 | 0.036751
SOBRANTE 1103CB | SOBRANTE 1103 | DIABLO | 3.6739 | 50.7835 | 26.28% | 3 | 6 | 85.25% | 16.11% | 0 | 0.030947 | 1 | 3.0955 | 0.095796 | Medium | Medium | High | 1791 | 2072 | 0.030947
EMERALD LAKE 0402CB | EMERALD LAKE 0402 | PENINSULA | 1.9157 | 10 | 14.69% | 2 | 3 | 100% | 0% | 0 | 0.017819 | 1 | 5.3744 | 0.095764 | Low | Low | High | 1792 | 2498 | 0.017819
SAN CARLOS 11049052 | SAN CARLOS 1104 | PENINSULA | 4.4833 | 10 | 33.62% | 0 | 5 | 90.23% | 0% | 0 | 0.021835 | 1 | 4.3823 | 0.095688 | Medium | Medium | High | 1793 | 2340 | 0.021835
PETALUMA C 1109738866 | PETALUMA C 1109 | SONOMA | 2.2043 | 62.3821 | 15.29% | 1 | 1 | 81.79% | 0% | 0 | 0.029792 | 1 | 3.2084 | 0.095587 | Medium | Medium | High | 1794 | 2105 | 0.029792
CURTIS 170411290 | CURTIS 1704 | YOSEMITE | 7.9015 | 12.4604 | 83.91% | 5 | 0 | 100% | 0% | 0 | 0.030926 | 1 | 3.0902 | 0.095569 | Medium | Medium | High | 1795 | 2073 | 0.030926
HIGGINS 11097831 | HIGGINS 1109 | SIERRA | 5.5525 | 26.5829 | 100% | 4 | 1 | 100% | 0% | 0 | 0.038882 | 1 | 2.4524 | 0.095352 | Medium | Medium | Medium | 1796 | 1883 | 0.038882
CALAVERAS CEMENT 1101544800 | CALAVERAS CEMENT 1101 | STOCKTON | 23.1954 | 36.7246 | 100% | 2 | 5 | 100% | 0% | 0 | 0.049871 | 1 | 1.9083 | 0.095168 | Medium | Medium | Low | 1797 | 1683 | 0.049871
CORNING 110290036 | CORNING 1102 | NORTH VALLEY | 14.194 | 60.2901 | 81.06% | 0 | 11 | 98.89% | 0% | 0 | 0.054481 | 1 | 1.7462 | 0.095135 | Medium | Medium | Low | 1798 | 1633 | 0.054481
CURTIS 17046060 | CURTIS 1704 | YOSEMITE | 4.0637 | 23.6511 | 61.76% | 0 | 3 | 100% | 0% | 0 | 0.031658 | 1 | 3.0016 | 0.095023 | Medium | Medium | Medium | 1799 | 2055 | 0.031658
HIGGINS 11044281 | HIGGINS 1104 | SIERRA | 13.3205 | 11.5983 | 77.05% | 5 | 5 | 100% | 0% | 0 | 0.032224 | 1 | 2.9395 | 0.094722 | Medium | Medium | Medium | 1800 | 2038 | 0.032224
EMERALD LAKE 04028872 | EMERALD LAKE 0402 | PENINSULA | 4.147 | 10 | 19.14% | 0 | 11 | 74.11% | 0% | 0 | 0.018758 | 1 | 5.0483 | 0.094694 | Low | Low | High | 1801 | 2458 | 0.018758
OAK 0401CB | OAK 0401 | EAST BAY | 4.3198 | 10 | 1.236% | 2 | 7 | 79.82% | 0% | 0 | 0.018493 | 1 | 5.1168 | 0.094626 | Low | Low | High | 1802 | 2466 | 0.018493
SILVERADO 2102808 | SILVERADO 2102 | NORTH BAY | 1.929 | 85.4925 | 100% | 0 | 0 | 40.02% | 25.27% | 0 | 0.039111 | 1 | 2.4149 | 0.094447 | Medium | Medium | Medium | 1803 | 1879 | 0.039111
PETALUMA C 1109848654 | PETALUMA C 1109 | SONOMA | 13.3481 | 80.6017 | 79.77% | 0 | 10 | 97.01% | 0% | 0 | 0.045978 | 1 | 2.0505 | 0.094277 | Medium | Medium | Low | 1804 | 1745 | 0.045978
SAN RAFAEL 1104802 | SAN RAFAEL 1104 | NORTH BAY | 7.826 | 10 | 18.94% | 3 | 4 | 72.62% | 0% | 0 | 0.021588 | 1 | 4.3551 | 0.094017 | Low | Low | High | 1805 | 2349 | 0.021588
PHILO 1102920 | PHILO 1102 | HUMBOLDT | 17.5582 | 57.0245 | 91.25% | 3 | 12 | 67.45% | 0% | 0 | 0.075007 | 1 | 1.2527 | 0.093958 | High | High | Low | 1806 | 1438 | 0.075007
CURTIS 17039240 | CURTIS 1703 | YOSEMITE | 10.9351 | 23.2344 | 88.01% | 0 | 12 | 100% | 3.336% | 0 | 0.063182 | 1 | 1.4789 | 0.093439 | High | High | Low | 1807 | 1531 | 0.063182
FAIRVIEW 2207P304 | FAIRVIEW 2207 | DIABLO | 5.0581 | 10 | 29.34% | 0 | 2 | 82.96% | 0% | 0 | 0.027316 | 1 | 3.4133 | 0.093239 | Medium | Medium | High | 1808 | 2185 | 0.027316
GEYSERVILLE 1102350 | GEYSERVILLE 1102 | SONOMA | 3.9586 | 50.2588 | 84.68% | 0 | 1 | 20.33% | 44.47% | 1 | 0.040497 | 1 | 2.3001 | 0.093146 | Medium | Medium | Medium | 1809 | 1843 | 0.040497
CORNING 110182846 | CORNING 1101 | NORTH VALLEY | 5.0438 | 29.0672 | 100% | 1 | 5 | 99.85% | 0% | 0 | 0.046785 | 1 | 1.9907 | 0.093136 | Medium | Medium | Low | 1810 | 1727 | 0.046785
TAR FLAT 04023144 | TAR FLAT 0402 | YOSEMITE | 4.9761 | 11.3882 | 27.07% | 0 | 3 | 96.83% | 26.03% | 1 | 0.032346 | 1 | 2.8761 | 0.093031 | Medium | Medium | Medium | 1811 | 2033 | 0.032346
OLETA 110113478 | OLETA 1101 | STOCKTON | 13.3756 | 25.4349 | 51.06% | 1 | 4 | 86.71% | 0% | 0 | 0.02671 | 1 | 3.4668 | 0.092599 | Medium | Medium | High | 1812 | 2197 | 0.02671
ELECTRA 110136816 | ELECTRA 1101 | STOCKTON | 16.3224 | 14.0317 | 85.78% | 2 | 8 | 100% | 0% | 0 | 0.035905 | 1 | 2.5788 | 0.092591 | Medium | Medium | Medium | 1813 | 1936 | 0.035905
FROGTOWN 1701L3361 | FROGTOWN 1701 | STOCKTON | 1.8736 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.2429 | 0.092461 | Medium | Medium | High | 1814 | 2132 | 0.028512
IONE 1101L3141 | IONE 1101 | STOCKTON | 13.6703 | 41.1561 | 100% | 0 | 0 | 97.4% | 0% | 0 | 0.034177 | 1 | 2.7017 | 0.092334 | Medium | Medium | Medium | 1815 | 1970 | 0.034177
DOBBINS 11011808 | DOBBINS 1101 | SIERRA | 15.539 | 16.962 | 100% | 1 | 0 | 100% | 6.412% | 0 | 0.043272 | 1 | 2.1331 | 0.092302 | Medium | Medium | Low | 1816 | 1790 | 0.043272
MORAGA 1104N532R | MORAGA 1104 | DIABLO | 4.4858 | 10 | 51.34% | 1 | 5 | 97.29% | 0% | 0 | 0.023997 | 1 | 3.8388 | 0.09212 | Medium | Medium | High | 1817 | 2277 | 0.023997
MESA 1103M72 | MESA 1103 | LOS PADRES | 9.6841 | 10 | 75.44% | 1 | 10 | 38.47% | 0% | 0 | 0.039556 | 1 | 2.326 | 0.092007 | Medium | Medium | Medium | 1818 | 1870 | 0.039556
CORNING 110185162 | CORNING 1101 | NORTH VALLEY | 5.7561 | 60.2607 | 100% | 0 | 2 | 100% | 0% | 0 | 0.047015 | 1 | 1.9543 | 0.09188 | Medium | Medium | Low | 1819 | 1724 | 0.047015
TEMPLETON 2110N30 | TEMPLETON 2110 | LOS PADRES | 20.4995 | 52.4771 | 52.2% | 1 | 3 | 100% | 0% | 0 | 0.040875 | 1 | 2.2426 | 0.091666 | Medium | Medium | Medium | 1820 | 1834 | 0.040875
POINT ARENA 1101474 | POINT ARENA 1101 | HUMBOLDT | 9.0104 | 63.6125 | 35.39% | 4 | 6 | 100% | 0% | 0 | 0.042479 | 1 | 2.1511 | 0.091377 | Medium | Medium | Low | 1821 | 1807 | 0.042479
DESCHUTES 1104CB | DESCHUTES 1104 | NORTH VALLEY | 12.32 | 22.7091 | 100% | 1 | 6 | 50.17% | 0% | 0 | 0.028343 | 1 | 3.212 | 0.091036 | Medium | Medium | High | 1822 | 2158 | 0.028343
SYCAMORE CREEK 1111 | SYCAMORE CREEK 1111 | NORTH VALLEY | 0.19166 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.1909 | 0.090978 | Medium | Medium | High | 1823 | 2136 | 0.028512
BROWNS VALLEY 110193870 | BROWNS VALLEY 1101 | SIERRA | 16.0223 | 22.1517 | 92.34% | 3 | 17 | 47.1% | 0% | 0 | 0.037632 | 1 | 2.4175 | 0.090975 | Medium | Medium | Medium | 1824 | 1903 | 0.037632
PLACERVILLE 1110CB | PLACERVILLE 1110 | SIERRA | 11.9057 | 10.8465 | 38.55% | 4 | 14 | 94.9% | 13.5% | 1 | 0.032906 | 1 | 2.7626 | 0.090907 | Medium | Medium | Medium | 1825 | 2014 | 0.032906
VOLTA 110180454 | VOLTA 1101 | NORTH VALLEY | 31.4882 | 39.839 | 95.78% | 4 | 1 | 97.71% | 0.9246% | 0 | 0.076439 | 1 | 1.1851 | 0.090591 | High | High | Low | 1826 | 1430 | 0.076439
FROGTOWN 17021573 | FROGTOWN 1702 | STOCKTON | 18.0626 | 46.2084 | 95.86% | 0 | 3 | 100% | 0% | 0 | 0.042352 | 1 | 2.1385 | 0.090571 | Medium | Medium | Low | 1827 | 1811 | 0.042352
FROGTOWN 1702L5407 | FROGTOWN 1702 | STOCKTON | 17.9809 | 33.0373 | 100% | 0 | 9 | 98.72% | 0% | 0 | 0.03936 | 1 | 2.2967 | 0.090399 | Medium | Medium | Medium | 1828 | 1875 | 0.03936
ATASCADERO 11012379 | ATASCADERO 1101 | LOS PADRES | 0.72914 | 10 | 100% | 1 | 2 | 100% | 0% | 0 | 0.030081 | 1 | 3.0039 | 0.090361 | Medium | Medium | Medium | 1829 | 2097 | 0.030081
MIDDLETOWN 1102514 | MIDDLETOWN 1102 | HUMBOLDT | 4.5797 | 10 | 100% | 1 | 1 | 86.53% | 0% | 0 | 0.025849 | 1 | 3.491 | 0.090241 | Medium | Medium | High | 1830 | 2219 | 0.025849
REEDLEY 1104 | REEDLEY 1104 | FRESNO | 0.23841 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.1623 | 0.090163 | Medium | Medium | High | 1831 | 2136 | 0.028512
FRUITLAND 11426054 | FRUITLAND 1142 | HUMBOLDT | 10.4759 | 81.7883 | 49.67% | 26 | 9 | 100% | 0% | 0 | 0.058078 | 1 | 1.5506 | 0.090055 | Medium | Medium | Low | 1832 | 1595 | 0.058078
GRAYS FLAT 0401CB | GRAYS FLAT 0401 | NORTH VALLEY | 10.7057 | 82.9815 | 68.42% | 5 | 6 | 100% | 0% | 0 | 0.063148 | 1 | 1.4254 | 0.090014 | High | High | Low | 1833 | 1532 | 0.063148
FROGTOWN 17027134 | FROGTOWN 1702 | STOCKTON | 19.267 | 44.0538 | 84.25% | 0 | 2 | 84.8% | 0% | 0 | 0.047354 | 1 | 1.8987 | 0.089911 | Medium | Medium | Low | 1834 | 1720 | 0.047354
WILLOW CREEK 11035012 | WILLOW CREEK 1103 | HUMBOLDT | 10.8623 | 35.544 | 71.11% | 10 | 12 | 100% | 0% | 0 | 0.044176 | 1 | 2.0337 | 0.08984 | Medium | Medium | Low | 1835 | 1772 | 0.044176
DIAMOND SPRINGS 110650324 | DIAMOND SPRINGS 1106 | SIERRA | 17.7246 | 10 | 70.6% | 6 | 3 | 87.05% | 0% | 0 | 0.038264 | 1 | 2.3467 | 0.089792 | Medium | Medium | Medium | 1836 | 1892 | 0.038264
KONOCTI 1102716 | KONOCTI 1102 | HUMBOLDT | 12.6002 | 59.2136 | 49.34% | 2 | 6 | 73.82% | 22.04% | 1 | 0.033546 | 1 | 2.6664 | 0.089449 | Medium | Medium | Medium | 1837 | 1992 | 0.033546
TEMPLETON 2113A20 | TEMPLETON 2113 | LOS PADRES | 7.0532 | 26.1549 | 66.41% | 2 | 0 | 89.65% | 0% | 0 | 0.033191 | 1 | 2.6768 | 0.088847 | Medium | Medium | Medium | 1838 | 2001 | 0.033191
LAKEVILLE 110287432 | LAKEVILLE 1102 | SONOMA | 8.9371 | 82.9673 | 68.1% | 1 | 4 | 65.45% | 0% | 0 | 0.032044 | 1 | 2.7702 | 0.088771 | Medium | Medium | Medium | 1839 | 2045 | 0.032044
ROSSMOOR 1101L503R | ROSSMOOR 1101 | DIABLO | 4.2657 | 11.5666 | 6.541% | 0 | 11 | 100% | 15.14% | 0 | 0.024651 | 1 | 3.5968 | 0.088666 | Medium | Medium | High | 1840 | 2252 | 0.024651
FRUITLAND 11422006 | FRUITLAND 1142 | HUMBOLDT | 8.3587 | 77.2327 | 73.06% | 6 | 2 | 90.12% | 0% | 0 | 0.041689 | 1 | 2.1223 | 0.088478 | Medium | Medium | Low | 1841 | 1824 | 0.041689
ARCATA 11224218 | ARCATA 1122 | HUMBOLDT | 4.9191 | 35.3774 | 67.92% | 2 | 3 | 99.74% | 0% | 0 | 0.032319 | 1 | 2.7359 | 0.088422 | Medium | Medium | Medium | 1842 | 2035 | 0.032319
GARBERVILLE 1101CB | GARBERVILLE 1101 | HUMBOLDT | 6.497 | 63.3643 | 74.83% | 4 | 3 | 74.77% | 0% | 0 | 0.037653 | 1 | 2.3445 | 0.088278 | Medium | Medium | Medium | 1843 | 1902 | 0.037653
CEDAR CREEK 11011664 | CEDAR CREEK 1101 | NORTH VALLEY | 29.6947 | 28.7537 | 98.78% | 0 | 12 | 100% | 0% | 0 | 0.067598 | 1 | 1.3051 | 0.088223 | High | High | Low | 1844 | 1490 | 0.067598
UKIAH 11143606 | UKIAH 1114 | HUMBOLDT | 9.6068 | 79.0327 | 97.2% | 3 | 5 | 58.23% | 0% | 0 | 0.033786 | 1 | 2.6108 | 0.088208 | Medium | Medium | Medium | 1845 | 1983 | 0.033786
REDBUD 1101CB | REDBUD 1101 | HUMBOLDT | 4.9191 | 32.5631 | 40.27% | 2 | 12 | 69.43% | 0% | 0 | 0.033542 | 1 | 2.6297 | 0.088206 | Medium | Medium | Medium | 1846 | 1993 | 0.033542
PHILO 11021308 | PHILO 1102 | HUMBOLDT | 31.8312 | 64.2643 | 100% | 9 | 11 | 100% | 0% | 0 | 0.06454 | 1 | 1.3663 | 0.088181 | High | High | Low | 1847 | 1519 | 0.06454
PEORIA 1705999 | PEORIA 1705 | YOSEMITE | 2.3082 | 18.7547 | 99.88% | 0 | 0 | 100% | 0% | 0 | 0.030188 | 1 | 2.9134 | 0.087952 | Medium | Medium | Medium | 1848 | 2093 | 0.030188
PLACERVILLE 210623190 | PLACERVILLE 2106 | SIERRA | 3.6751 | 24.4138 | 66.27% | 0 | 8 | 100% | 2.399% | 0 | 0.033321 | 1 | 2.6363 | 0.087845 | Medium | Medium | Medium | 1849 | 1998 | 0.033321
OLETA 11021204 | OLETA 1102 | STOCKTON | 24.7673 | 19.1315 | 95.37% | 0 | 4 | 83.58% | 2.402% | 0 | 0.036314 | 1 | 2.4177 | 0.087794 | Medium | Medium | Medium | 1850 | 1928 | 0.036314
HIGGINS 1109 | HIGGINS 1109 | SIERRA | 0.056072 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.0741 | 0.087647 | Medium | Medium | Medium | 1851 | 2132 | 0.028512
LAS POSITAS 2108MR182 | LAS POSITAS 2108 | MISSION | 6.1551 | 52.1024 | 25.77% | 0 | 0 | 85.34% | 0% | 0 | 0.030304 | 1 | 2.8822 | 0.087344 | Medium | Medium | Medium | 1852 | 2086 | 0.030304
BIG MEADOWS 21012586 | BIG MEADOWS 2101 | NORTH VALLEY | 9.5691 | 78.6746 | 93% | 0 | 0 | 87.41% | 0% | 0 | 0.037594 | 1 | 2.3215 | 0.087275 | Medium | Medium | Medium | 1853 | 1904 | 0.037594
NARROWS 210534069 | NARROWS 2105 | SIERRA | 15.7398 | 14.9961 | 98.66% | 0 | 6 | 100% | 0% | 0 | 0.048393 | 1 | 1.8027 | 0.087238 | Medium | Medium | Low | 1854 | 1704 | 0.048393
DEL MONTE 21032654 | DEL MONTE 2103 | CENTRAL COAST | 1.8437 | 10 | 36.65% | 2 | 2 | 100% | 0% | 0 | 0.027064 | 1 | 3.2195 | 0.087132 | Medium | Medium | High | 1855 | 2191 | 0.027064
WILLOW CREEK 1103CB | WILLOW CREEK 1103 | HUMBOLDT | 3.9217 | 18.1592 | 58.12% | 1 | 8 | 100% | 7.1% | 0 | 0.048009 | 1 | 1.8137 | 0.087072 | Medium | Medium | Low | 1856 | 1707 | 0.048009
PERRY 1101V74 | PERRY 1101 | LOS PADRES | 2.9727 | 10 | 2.672% | 10 | 7 | 58.33% | 0% | 0 | 0.024878 | 1 | 3.4959 | 0.086972 | Medium | Medium | High | 1857 | 2247 | 0.024878
PLACERVILLE 111219742 | PLACERVILLE 1112 | SIERRA | 7.3806 | 10 | 51.29% | 2 | 12 | 99.39% | 0% | 0 | 0.032573 | 1 | 2.6661 | 0.086842 | Medium | Medium | Medium | 1858 | 2025 | 0.032573
POINT ARENA 110147952 | POINT ARENA 1101 | HUMBOLDT | 10.391 | 76.4518 | 10.32% | 20 | 9 | 100% | 0% | 0 | 0.043386 | 1 | 1.9987 | 0.086717 | Medium | Medium | Low | 1859 | 1787 | 0.043386
KONOCTI 1108950 | KONOCTI 1108 | HUMBOLDT | 6.231 | 17.4671 | 73.5% | 1 | 1 | 84.02% | 0% | 0 | 0.031636 | 1 | 2.7401 | 0.086689 | Medium | Medium | Medium | 1860 | 2056 | 0.031636
HIGGINS 1104498932 | HIGGINS 1104 | SIERRA | 3.4528 | 10 | 98.29% | 1 | 2 | 80.99% | 0% | 0 | 0.024651 | 1 | 3.516 | 0.086673 | Medium | Medium | High | 1861 | 2253 | 0.024651
ALHAMBRA 11058302 | ALHAMBRA 1105 | DIABLO | 8.2556 | 10 | 24.97% | 0 | 12 | 100% | 0% | 0 | 0.029452 | 1 | 2.9395 | 0.086573 | Medium | Medium | Medium | 1862 | 2113 | 0.029452
SAUSALITO 11021268 | SAUSALITO 1102 | NORTH BAY | 5.0112 | 23.3781 | 0.422% | 3 | 4 | 100% | 0% | 0 | 0.030259 | 1 | 2.8544 | 0.086372 | Medium | Medium | Medium | 1863 | 2088 | 0.030259
KANAKA 11011036 | KANAKA 1101 | NORTH VALLEY | 0.60846 | 67.9249 | 100% | 0 | 0 | 100% | 0% | 0 | 0.041796 | 1 | 2.0662 | 0.086358 | Medium | Medium | Low | 1864 | 1820 | 0.041796
CORRAL 110359770 | CORRAL 1103 | STOCKTON | 4.5619 | 12.4013 | 100% | 1 | 1 | 62.81% | 0% | 0 | 0.02373 | 1 | 3.6376 | 0.086321 | Medium | Medium | High | 1865 | 2288 | 0.02373
UPPER LAKE 1101CB | UPPER LAKE 1101 | HUMBOLDT | 1.1134 | 70.0562 | 95.06% | 2 | 2 | 100% | 0% | 0 | 0.049432 | 1 | 1.7447 | 0.086245 | Medium | Medium | Low | 1866 | 1690 | 0.049432
CAYETANO 2111MR444 | CAYETANO 2111 | MISSION | 0.15169 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 3.0154 | 0.085973 | Medium | Medium | Medium | 1867 | 2132 | 0.028512
PLACERVILLE 1112CB | PLACERVILLE 1112 | SIERRA | 7.6031 | 10 | 47.53% | 2 | 8 | 81.02% | 0.2042% | 0 | 0.027832 | 1 | 3.0844 | 0.085847 | Medium | Medium | High | 1868 | 2167 | 0.027832
JAMESON 1103CB | JAMESON 1103 | SACRAMENTO | 3.6313 | 55.7827 | 92.07% | 0 | 1 | 33.3% | 0% | 0 | 0.025062 | 1 | 3.4236 | 0.085801 | Medium | Medium | High | 1869 | 2240 | 0.025062
FRENCH GULCH 11011464 | FRENCH GULCH 1101 | NORTH VALLEY | 3.9608 | 72.3083 | 100% | 3 | 0 | 100% | 0% | 0 | 0.044678 | 1 | 1.9188 | 0.085727 | Medium | Medium | Low | 1870 | 1767 | 0.044678
NARROWS 21052426 | NARROWS 2105 | SIERRA | 9.7882 | 10 | 86.21% | 2 | 2 | 56.57% | 0% | 0 | 0.026381 | 1 | 3.2439 | 0.085575 | Medium | Medium | High | 1871 | 2209 | 0.026381
PENRYN 11072708 | PENRYN 1107 | SIERRA | 8.636 | 10 | 67.69% | 3 | 4 | 79.72% | 0% | 0 | 0.026402 | 1 | 3.2393 | 0.085524 | Medium | Medium | High | 1872 | 2208 | 0.026402
SISQUOC 1102M52 | SISQUOC 1102 | LOS PADRES | 31.4004 | 61.3581 | 49.81% | 0 | 2 | 87.94% | 100% | 0 | 0.18147 | 1 | 0.47061 | 0.0854 | High | High | Low | 1873 | 1089 | 0.18147
GREENBRAE 1102CB | GREENBRAE 1102 | NORTH BAY | 0.15859 | 10 | 0% | 0 | 0 | 7.352% | 100% | 0 | 0.025266 | 1 | 3.3659 | 0.085044 | Medium | Medium | High | 1874 | 2234 | 0.025266
TEJON 11022455 | TEJON 1102 | KERN | 6.4984 | 10 | 98.01% | 0 | 2 | 100% | 0% | 0 | 0.043014 | 1 | 1.9757 | 0.084983 | Medium | Medium | Low | 1875 | 1797 | 0.043014
HIGGINS 1107 | HIGGINS 1107 | SIERRA | 0.013093 | 10 | 100% | 0 | 0 | 86.65% | 0% | 0 | 0.025031 | 1 | 3.3943 | 0.084962 | Medium | Medium | High | 1876 | 2242 | 0.025031
WOODSIDE 11049116 | WOODSIDE 1104 | PENINSULA | 1.063 | 10 | 91% | 2 | 5 | 24.81% | 0% | 0 | 0.018746 | 1 | 4.5156 | 0.08465 | Low | Low | High | 1877 | 2459 | 0.018746
FROGTOWN 17016807 | FROGTOWN 1701 | STOCKTON | 4.7513 | 29.5232 | 87.38% | 0 | 3 | 100% | 0% | 0 | 0.031186 | 1 | 2.7121 | 0.084578 | Medium | Medium | Medium | 1878 | 2068 | 0.031186
HIGGINS 11071070 | HIGGINS 1107 | SIERRA | 7.012 | 12.4115 | 99.96% | 1 | 4 | 84.37% | 0% | 0 | 0.027337 | 1 | 3.0898 | 0.084465 | Medium | Medium | High | 1879 | 2184 | 0.027337
ANTLER 11011384 | ANTLER 1101 | NORTH VALLEY | 8.8576 | 10 | 98.19% | 3 | 9 | 97.22% | 0% | 0 | 0.08259 | 1 | 1.0219 | 0.084396 | High | High | Low | 1880 | 1376 | 0.08259
SOBRANTE 1101CB | SOBRANTE 1101 | DIABLO | 13.5487 | 10.8121 | 22.39% | 1 | 13 | 87.75% | 0% | 0 | 0.02661 | 1 | 3.1685 | 0.084314 | Medium | Medium | High | 1881 | 2201 | 0.02661
BRENTWOOD 21056512 | BRENTWOOD 2105 | DIABLO | 0.65133 | 10 | 96.38% | 0 | 1 | 100% | 0% | 0 | 0.032177 | 1 | 2.6202 | 0.084309 | Medium | Medium | Medium | 1882 | 2039 | 0.032177
HOPLAND 11014626 | HOPLAND 1101 | HUMBOLDT | 24.0779 | 57.1108 | 92.12% | 0 | 5 | 79.18% | 0% | 0 | 0.055167 | 1 | 1.524 | 0.084074 | Medium | Medium | Low | 1883 | 1624 | 0.055167
DIAMOND SPRINGS 110676088 | DIAMOND SPRINGS 1106 | SIERRA | 11.0713 | 10.8319 | 90.75% | 3 | 3 | 100% | 0% | 0 | 0.038075 | 1 | 2.2072 | 0.08404 | Medium | Medium | Low | 1884 | 1896 | 0.038075
POINT MORETTI 11015104 | POINT MORETTI 1101 | CENTRAL COAST | 1.8713 | 40.903 | 21.17% | 4 | 0 | 100% | 0% | 0 | 0.032915 | 1 | 2.5532 | 0.084038 | Medium | Medium | Medium | 1885 | 2013 | 0.032915
MONTICELLO 11011589 | MONTICELLO 1101 | NORTH BAY | 4.3101 | 10 | 98.73% | 0 | 3 | 100% | 0% | 0 | 0.034141 | 1 | 2.4603 | 0.083998 | Medium | Medium | Medium | 1886 | 1971 | 0.034141
CAMP EVERS 2106CB | CAMP EVERS 2106 | CENTRAL COAST | 0.018997 | 10 | 0% | 0 | 0 | 0.8166% | 100% | 0 | 0.023702 | 1 | 3.5428 | 0.083973 | Medium | Medium | High | 1887 | 2289 | 0.023702
COTTONWOOD 1102CB | COTTONWOOD 1102 | NORTH VALLEY | 16.7139 | 23.1081 | 88.08% | 1 | 4 | 71.09% | 0% | 0 | 0.039338 | 1 | 2.1337 | 0.083935 | Medium | Medium | Low | 1888 | 1876 | 0.039338
WEIMAR 1101CB | WEIMAR 1101 | SIERRA | 9.2462 | 10 | 51.97% | 4 | 11 | 100% | 0% | 0 | 0.04865 | 1 | 1.7246 | 0.083901 | Medium | Medium | Low | 1889 | 1700 | 0.04865
CASTRO VALLEY 1108CB | CASTRO VALLEY 1108 | MISSION | 1.4946 | 10 | 6.175% | 3 | 1 | 53.21% | 52.04% | 0 | 0.023442 | 1 | 3.5736 | 0.083772 | Medium | Medium | High | 1890 | 2297 | 0.023442
OREGON TRAIL 1104CB | OREGON TRAIL 1104 | NORTH VALLEY | 10.8574 | 25.7844 | 63.12% | 2 | 12 | 74.06% | 0% | 0 | 0.031086 | 1 | 2.6945 | 0.08376 | Medium | Medium | Medium | 1891 | 2069 | 0.031086
SARATOGA 1106LC22 | SARATOGA 1106 | DE ANZA | 7.1525 | 10 | 35.66% | 5 | 5 | 86.79% | 0% | 0 | 0.020092 | 1 | 4.16 | 0.083584 | Low | Low | High | 1892 | 2405 | 0.020092
SO. CAL. EDISON #2 1101CB | SO. CAL. EDISON #2 1101 | YOSEMITE | 1.1766 | 10 | 100% | 0 | 0 | 100% | 37.67% | 0 | 0.051431 | 1 | 1.6243 | 0.08354 | Medium | Medium | Low | 1893 | 1669 | 0.051431
EEL RIVER 11021902 | EEL RIVER 1102 | HUMBOLDT | 5.1093 | 87.5518 | 84.86% | 3 | 2 | 68.94% | 0% | 0 | 0.043714 | 1 | 1.9061 | 0.083323 | Medium | Medium | Low | 1894 | 1782 | 0.043714
LAURELES 11122142 | LAURELES 1112 | CENTRAL COAST | 8.368 | 31.5595 | 39.83% | 4 | 4 | 87.21% | 0% | 0 | 0.030233 | 1 | 2.7544 | 0.083276 | Medium | Medium | Medium | 1895 | 2090 | 0.030233
HIGGINS 11039753 | HIGGINS 1103 | SIERRA | 2.1041 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.918 | 0.083198 | Medium | Medium | Medium | 1896 | 2136 | 0.028512
CALPELLA 1101542 | CALPELLA 1101 | HUMBOLDT | 23.4567 | 35.4534 | 89.83% | 1 | 18 | 100% | 0% | 0 | 0.058405 | 1 | 1.4223 | 0.083068 | Medium | Medium | Low | 1897 | 1588 | 0.058405
DUNBAR 110179086 | DUNBAR 1101 | SONOMA | 6.3052 | 21.6901 | 56.75% | 1 | 5 | 90.82% | 0% | 0 | 0.02897 | 1 | 2.866 | 0.083029 | Medium | Medium | Medium | 1898 | 2124 | 0.02897
SARATOGA 1106LC24 | SARATOGA 1106 | DE ANZA | 6.2415 | 10 | 42.44% | 3 | 7 | 55.48% | 10.64% | 0 | 0.021404 | 1 | 3.8778 | 0.083 | Low | Low | High | 1899 | 2354 | 0.021404
DEL MONTE 21042762 | DEL MONTE 2104 | CENTRAL COAST | 9.4859 | 27.7626 | 17.65% | 2 | 4 | 85.79% | 0% | 0 | 0.03979 | 1 | 2.0858 | 0.082991 | Medium | Medium | Low | 1900 | 1862 | 0.03979
CALAVERAS CEMENT 110136880 | CALAVERAS CEMENT 1101 | STOCKTON | 7.22 | 30.9732 | 81.65% | 0 | 2 | 83.77% | 0% | 0 | 0.037097 | 1 | 2.235 | 0.082911 | Medium | Medium | Medium | 1901 | 1915 | 0.037097
MORGAN HILL 2105XR152 | MORGAN HILL 2105 | SAN JOSE | 8.3434 | 31.972 | 72.23% | 0 | 5 | 65.24% | 0% | 0 | 0.027024 | 1 | 3.0674 | 0.082892 | Medium | Medium | Medium | 1902 | 2192 | 0.027024
WYANDOTTE 110738438 | WYANDOTTE 1107 | NORTH VALLEY | 16.8538 | 17.2711 | 100% | 1 | 4 | 100% | 13.33% | 1 | 0.046053 | 1 | 1.7995 | 0.082871 | Medium | Medium | Low | 1903 | 1742 | 0.046053
AUBERRY 1102R1013 | AUBERRY 1102 | FRESNO | 12.3506 | 22.637 | 85.13% | 0 | 11 | 100% | 0% | 0 | 0.039152 | 1 | 2.1117 | 0.082679 | Medium | Medium | Low | 1904 | 1878 | 0.039152
AUBERRY 110237466 | AUBERRY 1102 | FRESNO | 31.5797 | 23.1987 | 95.92% | 2 | 3 | 100% | 0% | 0 | 0.048258 | 1 | 1.7115 | 0.082592 | Medium | Medium | Low | 1905 | 1706 | 0.048258
BANGOR 11011806 | BANGOR 1101 | NORTH VALLEY | 8.946 | 12.2309 | 77.62% | 0 | 5 | 97.6% | 0% | 0 | 0.033897 | 1 | 2.4358 | 0.082565 | Medium | Medium | Medium | 1906 | 1980 | 0.033897
HALF MOON BAY 11036012 | HALF MOON BAY 1103 | PENINSULA | 5.8906 | 54.5639 | 76.22% | 11 | 4 | 61.12% | 0% | 0 | 0.039954 | 1 | 2.0637 | 0.082451 | Medium | Medium | Low | 1907 | 1857 | 0.039954
RIDGE 0401CB | RIDGE 0401 | EAST BAY | 2.662 | 10 | 10.22% | 3 | 4 | 100% | 0% | 0 | 0.02026 | 1 | 4.0693 | 0.082444 | Low | Low | High | 1908 | 2397 | 0.02026
STILLWATER 11021644 | STILLWATER 1102 | NORTH VALLEY | 22.854 | 11.5095 | 100% | 1 | 6 | 100% | 0% | 0 | 0.048415 | 1 | 1.7011 | 0.08236 | Medium | Medium | Low | 1909 | 1703 | 0.048415
LAKEWOOD 210738404 | LAKEWOOD 2107 | DIABLO | 6.7961 | 30.5815 | 25.31% | 5 | 8 | 68.2% | 1.158% | 0 | 0.024865 | 1 | 3.312 | 0.082353 | Medium | Medium | High | 1910 | 2248 | 0.024865
LUCERNE 11031663 | LUCERNE 1103 | HUMBOLDT | 1.2106 | 10 | 52.73% | 0 | 6 | 100% | 0% | 0 | 0.022038 | 1 | 3.735 | 0.082313 | Medium | Medium | High | 1911 | 2335 | 0.022038
JESSUP 11019752 | JESSUP 1101 | NORTH VALLEY | 3.8979 | 33.5364 | 99.93% | 0 | 1 | 100% | 0% | 0 | 0.033991 | 1 | 2.4213 | 0.082304 | Medium | Medium | Medium | 1912 | 1976 | 0.033991
MARTELL 11033152 | MARTELL 1103 | STOCKTON | 16.8696 | 31.4572 | 87.03% | 0 | 1 | 99.4% | 0% | 0 | 0.034215 | 1 | 2.4031 | 0.082223 | Medium | Medium | Medium | 1913 | 1969 | 0.034215
OREGON TRAIL 110249144 | OREGON TRAIL 1102 | NORTH VALLEY | 16.2173 | 16.9745 | 93.48% | 1 | 0 | 76.03% | 0% | 0 | 0.029469 | 1 | 2.7862 | 0.082107 | Medium | Medium | Medium | 1914 | 2112 | 0.029469
RINCON 1103472 | RINCON 1103 | SONOMA | 3.3276 | 10 | 93.65% | 0 | 2 | 70.54% | 3.999% | 0 | 0.025694 | 1 | 3.1877 | 0.081905 | Medium | Medium | High | 1915 | 2225 | 0.025694
ANNAPOLIS 110176842 | ANNAPOLIS 1101 | HUMBOLDT | 5.647 | 81.667 | 98.52% | 2 | 3 | 100% | 0% | 0 | 0.055858 | 1 | 1.4662 | 0.0819 | Medium | Medium | Low | 1916 | 1614 | 0.055858
PEORIA 170459596 | PEORIA 1704 | YOSEMITE | 19.1476 | 35.0672 | 53.97% | 0 | 6 | 53.15% | 0% | 0 | 0.024608 | 1 | 3.3279 | 0.081892 | Medium | Medium | High | 1917 | 2255 | 0.024608
NAPA 11121302 | NAPA 1112 | NORTH BAY | 17.5904 | 30.9393 | 74.37% | 2 | 8 | 52.69% | 0% | 0 | 0.026355 | 1 | 3.0997 | 0.081693 | Medium | Medium | High | 1918 | 2210 | 0.026355
BUELLTON 1101Y26 | BUELLTON 1101 | LOS PADRES | 14.0549 | 47.3747 | 54.06% | 1 | 8 | 88.5% | 0% | 0 | 0.039723 | 1 | 2.0524 | 0.081528 | Medium | Medium | Low | 1919 | 1864 | 0.039723
RALSTON 110148936 | RALSTON 1101 | PENINSULA | 3.4057 | 10 | 32.09% | 0 | 3 | 56.99% | 0% | 0 | 0.025196 | 1 | 3.2337 | 0.081477 | Medium | Medium | High | 1920 | 2236 | 0.025196
KIRKER 2104442850 | KIRKER 2104 | DIABLO | 5.4258 | 10 | 43.23% | 0 | 4 | 95.36% | 0% | 0 | 0.024306 | 1 | 3.3502 | 0.081427 | Medium | Medium | High | 1921 | 2267 | 0.024306
BANGOR 1101CB | BANGOR 1101 | NORTH VALLEY | 18.8771 | 14.9118 | 68.16% | 4 | 2 | 88.52% | 0% | 0 | 0.029011 | 1 | 2.802 | 0.081291 | Medium | Medium | Medium | 1922 | 2123 | 0.029011
MERCED FALLS 110222772 | MERCED FALLS 1102 | YOSEMITE | 2.2922 | 12.637 | 100% | 0 | 0 | 100% | 0% | 0 | 0.029016 | 14.9507 | 0.18721 | 0.081211 | Medium | Medium | Low | 1923 | 878 | 0.4338
HIGGINS 110391052 | HIGGINS 1103 | SIERRA | 0.64834 | 10 | 100% | 0 | 0 | 84.24% | 0% | 0 | 0.024449 | 1 | 3.3175 | 0.081108 | Medium | Medium | High | 1924 | 2263 | 0.024449
SAN RAFAEL 110168970 | SAN RAFAEL 1101 | NORTH BAY | 1.3404 | 10 | 17.09% | 0 | 0 | 31.9% | 46.84% | 0 | 0.018013 | 1 | 4.4995 | 0.08105 | Low | Low | High | 1925 | 2487 | 0.018013
BIG MEADOWS 21012260 | BIG MEADOWS 2101 | NORTH VALLEY | 17.1948 | 71.2696 | 55.9% | 4 | 0 | 76.22% | 0% | 0 | 0.032561 | 1 | 2.4871 | 0.080983 | Medium | Medium | Medium | 1926 | 2026 | 0.032561
GARBERVILLE 1102CB | GARBERVILLE 1102 | HUMBOLDT | 10.6146 | 34.8511 | 30.11% | 18 | 9 | 65.56% | 0% | 0 | 0.030692 | 1 | 2.6357 | 0.080896 | Medium | Medium | Medium | 1927 | 2077 | 0.030692
HIGGINS 11094189 | HIGGINS 1109 | SIERRA | 3.326 | 25.4516 | 99.91% | 0 | 3 | 100% | 0% | 0 | 0.033551 | 1 | 2.4095 | 0.080842 | Medium | Medium | Medium | 1928 | 1991 | 0.033551
OLETA 1102CB | OLETA 1102 | STOCKTON | 12.9237 | 28.5426 | 79.87% | 0 | 5 | 85.32% | 0% | 0 | 0.038817 | 1 | 2.0783 | 0.080675 | Medium | Medium | Low | 1929 | 1884 | 0.038817
TASSAJARA 210883368 | TASSAJARA 2108 | DIABLO | 0.069317 | 10 | 0% | 0 | 0 | 1.551% | 100% | 0 | 0.023873 | 1 | 3.3752 | 0.080577 | Medium | Medium | High | 1930 | 2281 | 0.023873
MORRO BAY 110249632 | MORRO BAY 1102 | LOS PADRES | 0.66912 | 10 | 0% | 0 | 3 | 100% | 0% | 0 | 0.017573 | 1 | 4.5803 | 0.080492 | Low | Low | High | 1931 | 2506 | 0.017573
TEMPLETON 2111R86 | TEMPLETON 2111 | LOS PADRES | 10.174 | 35.046 | 79.62% | 2 | 6 | 70.64% | 0% | 0 | 0.032293 | 1 | 2.4827 | 0.080172 | Medium | Medium | Medium | 1932 | 2036 | 0.032293
STELLING 11109265 | STELLING 1110 | DE ANZA | 5.4699 | 10 | 92.07% | 0 | 1 | 100% | 0% | 0 | 0.027307 | 1 | 2.9335 | 0.080104 | Medium | Medium | Medium | 1933 | 2186 | 0.027307
MARTELL 1102CB | MARTELL 1102 | STOCKTON | 6.4004 | 24.1429 | 66.43% | 0 | 4 | 94.03% | 0% | 0 | 0.031753 | 1 | 2.5224 | 0.080095 | Medium | Medium | Medium | 1934 | 2052 | 0.031753
SAN RAFAEL 1105534 | SAN RAFAEL 1105 | NORTH BAY | 1.348 | 10 | 81.92% | 3 | 4 | 85.31% | 0% | 0 | 0.024098 | 1 | 3.3132 | 0.079842 | Medium | Medium | High | 1935 | 2276 | 0.024098
VIEJO 22012064 | VIEJO 2201 | CENTRAL COAST | 0.87679 | 10 | 42.79% | 0 | 3 | 100% | 0% | 0 | 0.021793 | 1 | 3.6566 | 0.079688 | Low | Low | High | 1936 | 2343 | 0.021793
GIRVAN 1101323094 | GIRVAN 1101 | NORTH VALLEY | 36.2683 | 55.5247 | 99.98% | 1 | 3 | 100% | 0% | 0 | 0.068706 | 1 | 1.1596 | 0.079672 | High | High | Low | 1937 | 1479 | 0.068706
WOODSIDE 11049032 | WOODSIDE 1104 | PENINSULA | 2.5921 | 10 | 76.95% | 3 | 1 | 32.76% | 43.39% | 0 | 0.029563 | 1 | 2.6884 | 0.079475 | Medium | Medium | Medium | 1938 | 2109 | 0.029563
TEMPLETON 2110R94 | TEMPLETON 2110 | LOS PADRES | 13.9551 | 53.972 | 81.64% | 0 | 3 | 66.74% | 0% | 0 | 0.037368 | 1 | 2.1258 | 0.079438 | Medium | Medium | Low | 1939 | 1908 | 0.037368
CAYETANO 2109CB | CAYETANO 2109 | MISSION | 13.0515 | 49.7043 | 30.41% | 0 | 2 | 76.33% | 3.645% | 1 | 0.024131 | 1 | 3.2891 | 0.079369 | Medium | Medium | High | 1940 | 2275 | 0.024131
BAY MEADOWS 210257886 | BAY MEADOWS 2102 | PENINSULA | 4.2245 | 10 | 28.89% | 2 | 6 | 80.67% | 0% | 0 | 0.026024 | 1 | 3.0461 | 0.079274 | Medium | Medium | Medium | 1941 | 2214 | 0.026024
SAN LUIS OBISPO 1107V18 | SAN LUIS OBISPO 1107 | LOS PADRES | 3.3731 | 28.9632 | 4.194% | 1 | 0 | 84.27% | 30.63% | 0 | 0.035557 | 1 | 2.2292 | 0.079264 | Medium | Medium | Low | 1942 | 1944 | 0.035557
MENLO 11038982 | MENLO 1103 | PENINSULA | 4.6231 | 36.5586 | 24.74% | 19 | 4 | 100% | 0% | 0 | 0.043182 | 1 | 1.8329 | 0.07915 | Medium | Medium | Low | 1943 | 1792 | 0.043182
CLAYTON 22122944 | CLAYTON 2212 | DIABLO | 14.8336 | 10 | 45.06% | 1 | 4 | 97.25% | 6.81% | 1 | 0.024898 | 1 | 3.1713 | 0.078959 | Medium | Medium | High | 1944 | 2246 | 0.024898
CLAY 11031230 | CLAY 1103 | STOCKTON | 15.7057 | 29.0509 | 99.85% | 0 | 2 | 80.49% | 0% | 0 | 0.031696 | 1 | 2.4895 | 0.078906 | Medium | Medium | Medium | 1945 | 2054 | 0.031696
VIEJO 2201CB | VIEJO 2201 | CENTRAL COAST | 4.5324 | 10 | 12.86% | 16 | 6 | 89.76% | 0% | 0 | 0.020254 | 1 | 3.8798 | 0.078583 | Low | Low | High | 1946 | 2398 | 0.020254
SMARTVILLE 1101CB | SMARTVILLE 1101 | SIERRA | 15.8868 | 12.1904 | 82.07% | 1 | 6 | 100% | 0% | 0 | 0.032648 | 1 | 2.4063 | 0.078562 | Medium | Medium | Medium | 1947 | 2020 | 0.032648
OLEMA 1101602 | OLEMA 1101 | NORTH BAY | 15.0972 | 65.987 | 1.264% | 8 | 10 | 59.79% | 0% | 0 | 0.037469 | 1 | 2.0944 | 0.078477 | Medium | Medium | Low | 1948 | 1906 | 0.037469
BIG RIVER 110169032 | BIG RIVER 1101 | HUMBOLDT | 8.4667 | 31.9768 | 17.96% | 7 | 9 | 100% | 0% | 0 | 0.033152 | 1 | 2.3622 | 0.07831 | Medium | Medium | Medium | 1949 | 2004 | 0.033152
DUNBAR 1102CB | DUNBAR 1102 | SONOMA | 8.263 | 20.9256 | 44.14% | 4 | 14 | 47.06% | 0% | 0 | 0.024179 | 1 | 3.2378 | 0.078286 | Medium | Medium | High | 1950 | 2273 | 0.024179
HOLLISTER 21054018 | HOLLISTER 2105 | CENTRAL COAST | 42.8602 | 78.3807 | 68.88% | 1 | 1 | 81.19% | 0% | 0 | 0.044317 | 1 | 1.765 | 0.078218 | Medium | Medium | Low | 1951 | 1771 | 0.044317
IGNACIO 11011300 | IGNACIO 1101 | NORTH BAY | 2.4856 | 23.8629 | 75.16% | 0 | 4 | 40.74% | 21.73% | 0 | 0.025064 | 1 | 3.1191 | 0.078176 | Medium | Medium | High | 1952 | 2239 | 0.025064
HOOPA 11013290 | HOOPA 1101 | HUMBOLDT | 13.744 | 63.8622 | 97.01% | 10 | 15 | 100% | 0% | 0 | 0.077955 | 1 | 1.0027 | 0.078163 | High | High | Low | 1953 | 1414 | 0.077955
OAKLAND J 1102CR102 | OAKLAND J 1102 | EAST BAY | 0.53101 | 10 | 70.62% | 0 | 2 | 100% | 0% | 0 | 0.023454 | 1 | 3.3241 | 0.077962 | Medium | Medium | High | 1954 | 2295 | 0.023454
DUNBAR 1102528 | DUNBAR 1102 | SONOMA | 3.4638 | 30.5853 | 54.13% | 1 | 3 | 85.5% | 0% | 0 | 0.021137 | 1 | 3.6876 | 0.077945 | Low | Low | High | 1955 | 2360 | 0.021137
STILLWATER 110148950 | STILLWATER 1101 | NORTH VALLEY | 12.4263 | 10 | 99.94% | 1 | 4 | 100% | 0% | 0 | 0.046041 | 1 | 1.6867 | 0.077656 | Medium | Medium | Low | 1956 | 1743 | 0.046041
CURTIS 170320240 | CURTIS 1703 | YOSEMITE | 0.18021 | 10 | 100% | 0 | 0 | 63.08% | 0% | 0 | 0.019869 | 1 | 3.9035 | 0.077558 | Low | Low | High | 1957 | 2415 | 0.019869
OLETA 110241396 | OLETA 1102 | STOCKTON | 7.3755 | 10 | 56.8% | 3 | 3 | 100% | 0% | 0 | 0.025362 | 1 | 3.0576 | 0.077548 | Medium | Medium | Medium | 1958 | 2233 | 0.025362
SILVERADO 2102714 | SILVERADO 2102 | NORTH BAY | 4.37 | 45.4785 | 19.37% | 4 | 5 | 38.82% | 6.698% | 0 | 0.022688 | 1 | 3.4176 | 0.077537 | Medium | Medium | High | 1959 | 2317 | 0.022688
EMERALD LAKE 04028858 | EMERALD LAKE 0402 | PENINSULA | 1.9112 | 10 | 5.775% | 0 | 4 | 100% | 0% | 0 | 0.016487 | 1 | 4.6869 | 0.077272 | Low | Low | High | 1960 | 2553 | 0.016487
CARLOTTA 11214914 | CARLOTTA 1121 | HUMBOLDT | 11.4615 | 25.5188 | 70.14% | 16 | 11 | 80.82% | 0% | 0 | 0.041044 | 1 | 1.8825 | 0.077265 | Medium | Medium | Low | 1961 | 1833 | 0.041044
LUCERNE 11062327 | LUCERNE 1106 | HUMBOLDT | 0.98526 | 10 | 100% | 0 | 1 | 77.76% | 0% | 0 | 0.02342 | 1 | 3.2861 | 0.07696 | Medium | Medium | High | 1962 | 2300 | 0.02342
CURTIS 1701CB | CURTIS 1701 | YOSEMITE | 8.5475 | 34.1417 | 57.96% | 1 | 9 | 68.5% | 0% | 0 | 0.024359 | 1 | 3.1577 | 0.076918 | Medium | Medium | High | 1963 | 2266 | 0.024359
CLAY 11031821 | CLAY 1103 | STOCKTON | 2.0901 | 61.2881 | 100% | 0 | 0 | 55.49% | 0% | 0 | 0.029593 | 1 | 2.5933 | 0.076746 | Medium | Medium | Medium | 1964 | 2108 | 0.029593
TIVY VALLEY 1107R1817 | TIVY VALLEY 1107 | FRESNO | 19.042 | 15.3654 | 99.23% | 0 | 5 | 99.01% | 0% | 0 | 0.041647 | 1 | 1.8427 | 0.076744 | Medium | Medium | Low | 1965 | 1825 | 0.041647
RALSTON 11022028 | RALSTON 1102 | PENINSULA | 2.1344 | 10 | 38.62% | 0 | 5 | 92.94% | 0% | 0 | 0.020485 | 1 | 3.746 | 0.076737 | Low | Low | High | 1966 | 2387 | 0.020485
BANGOR 110131502 | BANGOR 1101 | NORTH VALLEY | 11.8542 | 14.4917 | 60.88% | 1 | 3 | 100% | 0% | 0 | 0.026318 | 1 | 2.9147 | 0.076709 | Medium | Medium | Medium | 1967 | 2212 | 0.026318
MOUNTAIN QUARRIES 210151584 | MOUNTAIN QUARRIES 2101 | SIERRA | 21.6351 | 34.2949 | 99.29% | 0 | 1 | 100% | 0% | 0 | 0.033987 | 1 | 2.2566 | 0.076695 | Medium | Medium | Medium | 1968 | 1977 | 0.033987
HALF MOON BAY 11036065 | HALF MOON BAY 1103 | PENINSULA | 6.2488 | 59.5208 | 36.98% | 1 | 1 | 91.2% | 0% | 0 | 0.02267 | 1 | 3.3733 | 0.076472 | Medium | Medium | High | 1969 | 2318 | 0.02267
RADUM 1105MR282 | RADUM 1105 | MISSION | 2.1702 | 17.1089 | 66.03% | 0 | 5 | 34.07% | 37.28% | 0 | 0.023926 | 1 | 3.184 | 0.076183 | Medium | Medium | High | 1970 | 2278 | 0.023926
HIGGINS 1104CB | HIGGINS 1104 | SIERRA | 11.5789 | 10 | 38.55% | 1 | 4 | 99.62% | 0% | 0 | 0.024722 | 1 | 3.0793 | 0.076125 | Medium | Medium | High | 1971 | 2251 | 0.024722
BIG RIVER 11011052 | BIG RIVER 1101 | HUMBOLDT | 2.9737 | 10 | 0% | 7 | 11 | 77.62% | 0% | 0 | 0.023654 | 1 | 3.2182 | 0.076123 | Medium | Medium | High | 1972 | 2291 | 0.023654
GARBERVILLE 11022010 | GARBERVILLE 1102 | HUMBOLDT | 6.6438 | 69.4132 | 9.089% | 2 | 3 | 100% | 0% | 0 | 0.042493 | 1 | 1.7903 | 0.076076 | Medium | Medium | Low | 1973 | 1806 | 0.042493
SANTA YNEZ 1102Y18 | SANTA YNEZ 1102 | LOS PADRES | 4.6184 | 77.519 | 99.57% | 1 | 1 | 61.2% | 0% | 0 | 0.035874 | 1 | 2.1205 | 0.076069 | Medium | Medium | Low | 1974 | 1937 | 0.035874
HIGGINS 1103995672 | HIGGINS 1103 | SIERRA | 2.7769 | 10 | 100% | 1 | 1 | 48.24% | 0% | 0 | 0.02307 | 1 | 3.2961 | 0.076042 | Medium | Medium | High | 1975 | 2307 | 0.02307
CLAY 110334338 | CLAY 1103 | STOCKTON | 7.6368 | 36.5237 | 71.29% | 1 | 2 | 73.13% | 0% | 0 | 0.028445 | 1 | 2.6701 | 0.075951 | Medium | Medium | Medium | 1976 | 2156 | 0.028445
HAMILTON BRANCH 11012082 | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.6281 | 32.2338 | 100% | 1 | 0 | 53.18% | 0% | 0 | 0.021199 | 1 | 3.5753 | 0.075794 | Low | Low | High | 1977 | 2358 | 0.021199
WYANDOTTE 11071026 | WYANDOTTE 1107 | NORTH VALLEY | 21.2978 | 26.1479 | 94.57% | 0 | 2 | 76.21% | 0% | 0 | 0.032543 | 1 | 2.3229 | 0.075594 | Medium | Medium | Medium | 1978 | 2028 | 0.032543
VOLTA 110153118 | VOLTA 1101 | NORTH VALLEY | 9.6297 | 40.8133 | 100% | 0 | 1 | 100% | 0% | 0 | 0.05235 | 1 | 1.4426 | 0.075522 | Medium | Medium | Low | 1979 | 1657 | 0.05235
SPRUCE 0402BR304 | SPRUCE 0402 | EAST BAY | 1.905 | 10 | 5.593% | 0 | 5 | 53.05% | 19.04% | 0 | 0.016372 | 1 | 4.6125 | 0.075515 | Low | Low | High | 1980 | 2556 | 0.016372
WEIMAR 11026175 | WEIMAR 1102 | SIERRA | 2.7281 | 10 | 100% | 0 | 1 | 100% | 0% | 0 | 0.029099 | 1 | 2.5942 | 0.075486 | Medium | Medium | Medium | 1981 | 2119 | 0.029099
APPLE HILL 210251792 | APPLE HILL 2102 | SIERRA | 9.3607 | 11.5456 | 100% | 6 | 2 | 100% | 0% | 0 | 0.04191 | 1 | 1.7949 | 0.075224 | Medium | Medium | Low | 1982 | 1819 | 0.04191
CALPELLA 11013419 | CALPELLA 1101 | HUMBOLDT | 8.0753 | 59.7032 | 100% | 1 | 1 | 100% | 3.769% | 0 | 0.0493 | 1 | 1.5255 | 0.075207 | Medium | Medium | Low | 1983 | 1692 | 0.0493
HATTON 1101CB | HATTON 1101 | CENTRAL COAST | 1.5925 | 10 | 10.22% | 4 | 0 | 100% | 0% | 0 | 0.024551 | 1 | 3.0516 | 0.074918 | Medium | Medium | Medium | 1984 | 2260 | 0.024551
CLARK ROAD 11022070 | CLARK ROAD 1102 | NORTH VALLEY | 9.7077 | 20.9726 | 72.7% | 1 | 4 | 86.39% | 12.56% | 0 | 0.028935 | 1 | 2.5885 | 0.0749 | Medium | Medium | Medium | 1985 | 2127 | 0.028935
PIERCY 2110XR258 | PIERCY 2110 | SAN JOSE | 14.4387 | 60.8378 | 97.27% | 4 | 1 | 54.5% | 0% | 0 | 0.026979 | 1 | 2.7761 | 0.074895 | Medium | Medium | Medium | 1986 | 2193 | 0.026979
HIGHLANDS 1104CB | HIGHLANDS 1104 | HUMBOLDT | 4.6735 | 10 | 74.7% | 0 | 2 | 57.1% | 0% | 0 | 0.023554 | 1 | 3.1769 | 0.074829 | Medium | Medium | High | 1987 | 2294 | 0.023554
OREGON TRAIL 1104 | OREGON TRAIL 1104 | NORTH VALLEY | 0.063815 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.6217 | 0.074749 | Medium | Medium | Medium | 1988 | 2154 | 0.028512
DESCHUTES 11011380 | DESCHUTES 1101 | NORTH VALLEY | 17.936 | 29.5967 | 86.99% | 0 | 4 | 75.95% | 0% | 0 | 0.032554 | 1 | 2.2953 | 0.07472 | Medium | Medium | Medium | 1989 | 2027 | 0.032554
PERRY 1101CB | PERRY 1101 | LOS PADRES | 2.5037 | 27.4854 | 19.25% | 0 | 1 | 100% | 0% | 0 | 0.025246 | 1 | 2.9519 | 0.074522 | Medium | Medium | Medium | 1990 | 2235 | 0.025246
CLEAR LAKE 11011302 | CLEAR LAKE 1101 | HUMBOLDT | 6.3736 | 19.3133 | 67.28% | 0 | 7 | 36.56% | 0% | 0 | 0.024377 | 1 | 3.0552 | 0.074476 | Medium | Medium | Medium | 1991 | 2265 | 0.024377
VIEJO 22029120 | VIEJO 2202 | CENTRAL COAST | 1.9636 | 10 | 20.08% | 9 | 3 | 26.52% | 0% | 0 | 0.019059 | 1 | 3.9065 | 0.074456 | Low | Low | High | 1992 | 2444 | 0.019059
SAN CARLOS 11039148 | SAN CARLOS 1103 | PENINSULA | 3.9693 | 10 | 27.37% | 0 | 9 | 43.54% | 0% | 0 | 0.016236 | 1 | 4.5802 | 0.074366 | Low | Low | High | 1993 | 2563 | 0.016236
GUALALA 1111887180 | GUALALA 1111 | HUMBOLDT | 5.4716 | 10 | 0.3119% | 7 | 8 | 100% | 0% | 0 | 0.027751 | 1 | 2.6787 | 0.074336 | Medium | Medium | Medium | 1994 | 2169 | 0.027751
CLOVERDALE 1101112 | CLOVERDALE 1101 | SONOMA | 19.0544 | 64.0868 | 84.08% | 2 | 8 | 69.85% | 0% | 0 | 0.036824 | 1 | 2.0172 | 0.074281 | Medium | Medium | Low | 1995 | 1921 | 0.036824
ALLEGHANY 1101978 | ALLEGHANY 1101 | SIERRA | 13.0219 | 53.8471 | 100% | 3 | 4 | 44.63% | 0% | 0 | 0.037002 | 1 | 2.0065 | 0.074244 | Medium | Medium | Low | 1996 | 1917 | 0.037002
OILFIELDS 11035175 | OILFIELDS 1103 | CENTRAL COAST | 1.9738 | 10 | 100% | 0 | 3 | 89.15% | 0% | 0 | 0.027271 | 1 | 2.7162 | 0.074075 | Medium | Medium | Medium | 1997 | 2187 | 0.027271
BROWNS VALLEY 110117011 | BROWNS VALLEY 1101 | SIERRA | 1.8676 | 10 | 100% | 0 | 2 | 100% | 0% | 0 | 0.029697 | 1 | 2.4913 | 0.073986 | Medium | Medium | Medium | 1998 | 2106 | 0.029697
FRENCH GULCH 11021462 | FRENCH GULCH 1102 | NORTH VALLEY | 13.6588 | 44.7353 | 99.62% | 1 | 1 | 99.24% | 22.55% | 0 | 0.052153 | 1 | 1.4168 | 0.073891 | Medium | Medium | Low | 1999 | 1659 | 0.052153
MARIPOSA 21018030 | MARIPOSA 2101 | YOSEMITE | 18.88 | 28.5381 | 67.58% | 1 | 11 | 100% | 1.019% | 0 | 0.032029 | 1 | 2.3021 | 0.073734 | Medium | Medium | Medium | 2000 | 2046 | 0.032029
APPLE HILL 21021532 | APPLE HILL 2102 | SIERRA | 38.7437 | 26.3677 | 83.01% | 8 | 10 | 92.13% | 0.1028% | 0 | 0.045174 | 1 | 1.6238 | 0.073353 | Medium | Medium | Low | 2001 | 1761 | 0.045174
FORT SEWARD 1121CB | FORT SEWARD 1121 | HUMBOLDT | 7.2358 | 72.7632 | 100% | 3 | 3 | 100% | 0% | 0 | 0.047585 | 1 | 1.5395 | 0.073259 | Medium | Medium | Low | 2002 | 1715 | 0.047585
HALF MOON BAY 110375550 | HALF MOON BAY 1103 | PENINSULA | 1.1869 | 54.8487 | 75.08% | 0 | 0 | 53.23% | 0% | 0 | 0.019917 | 1 | 3.6734 | 0.073163 | Low | Low | High | 2003 | 2411 | 0.019917
BANGOR 110180670 | BANGOR 1101 | NORTH VALLEY | 14.7472 | 18.2405 | 76% | 0 | 1 | 89.02% | 0% | 0 | 0.02277 | 1 | 3.21 | 0.073094 | Medium | Medium | High | 2004 | 2313 | 0.02277
ELK CREEK 110137334 | ELK CREEK 1101 | NORTH VALLEY | 9.7022 | 59.8583 | 100% | 0 | 0 | 100% | 0% | 0 | 0.065795 | 1 | 1.1103 | 0.073051 | High | High | Low | 2005 | 1509 | 0.065795
SWIFT 2107XR526 | SWIFT 2107 | SAN JOSE | 2.6821 | 10 | 42.91% | 0 | 1 | 49.21% | 0% | 0 | 0.016512 | 1 | 4.4175 | 0.072944 | Low | Low | High | 2006 | 2550 | 0.016512
KERCKHOFF 1101CB | KERCKHOFF 1101 | YOSEMITE | 16.9469 | 19.3199 | 39.66% | 0 | 15 | 100% | 0% | 0 | 0.032903 | 1 | 2.2156 | 0.072899 | Medium | Medium | Low | 2007 | 2015 | 0.032903
STILLWATER 11021466 | STILLWATER 1102 | NORTH VALLEY | 19.2831 | 16.0387 | 100% | 1 | 10 | 94.09% | 0% | 0 | 0.051049 | 1 | 1.4241 | 0.0727 | Medium | Medium | Low | 2008 | 1672 | 0.051049
POSO MOUNTAIN 2101CB | POSO MOUNTAIN 2101 | KERN | 4.3131 | 10 | 10.82% | 0 | 0 | 100% | 0% | 0 | 0.026686 | 1 | 2.722 | 0.072639 | Medium | Medium | Medium | 2009 | 2198 | 0.026686
CABRILLO 110420711 | CABRILLO 1104 | LOS PADRES | 0.18254 | 10 | 100% | 0 | 0 | 58.32% | 0% | 0 | 0.01896 | 1 | 3.8254 | 0.072532 | Low | Low | High | 2010 | 2449 | 0.01896
NORTH DUBLIN 2101CB | NORTH DUBLIN 2101 | MISSION | 3.6193 | 54.6377 | 4.667% | 0 | 3 | 91.94% | 0% | 0 | 0.019955 | 1 | 3.6341 | 0.072519 | Low | Low | High | 2011 | 2410 | 0.019955
STILLWATER 1101CB | STILLWATER 1101 | NORTH VALLEY | 3.671 | 10 | 87.48% | 3 | 2 | 85.62% | 0% | 0 | 0.027635 | 1 | 2.6197 | 0.072394 | Medium | Medium | Medium | 2012 | 2173 | 0.027635
OILFIELDS 11032757 | OILFIELDS 1103 | CENTRAL COAST | 2.6282 | 37.5918 | 90.66% | 0 | 3 | 100% | 0% | 0 | 0.033768 | 1 | 2.1416 | 0.072319 | Medium | Medium | Low | 2013 | 1984 | 0.033768
CEDAR CREEK 1101CB | CEDAR CREEK 1101 | NORTH VALLEY | 15.4651 | 37.802 | 95.68% | 0 | 0 | 100% | 38.1% | 1 | 0.067896 | 1 | 1.0626 | 0.072148 | High | High | Low | 2014 | 1487 | 0.067896
LOW GAP 110137498 | LOW GAP 1101 | HUMBOLDT | 16.1307 | 72.1022 | 98.67% | 6 | 3 | 100% | 0% | 0 | 0.062673 | 1 | 1.1505 | 0.072104 | High | High | Low | 2015 | 1535 | 0.062673
DUNLAP 11037040 | DUNLAP 1103 | FRESNO | 24.7254 | 12.3243 | 100% | 0 | 2 | 100% | 0% | 0 | 0.039034 | 1 | 1.8465 | 0.072078 | Medium | Medium | Low | 2016 | 1881 | 0.039034
PETALUMA C 110948000 | PETALUMA C 1109 | SONOMA | 8.7103 | 40.2232 | 37.55% | 1 | 9 | 65.59% | 0% | 0 | 0.023831 | 1 | 3.0235 | 0.072053 | Medium | Medium | Medium | 2017 | 2284 | 0.023831
HAMILTON BRANCH 110118205 | HAMILTON BRANCH 1101 | NORTH VALLEY | 4.0384 | 59.6103 | 100% | 0 | 1 | 100% | 0% | 0 | 0.040382 | 1 | 1.7837 | 0.072028 | Medium | Medium | Low | 2018 | 1844 | 0.040382
HORSESHOE 110150140 | HORSESHOE 1101 | SIERRA | 3.7526 | 10 | 69.76% | 1 | 4 | 60.16% | 0% | 0 | 0.018953 | 1 | 3.7991 | 0.072006 | Low | Low | High | 2019 | 2450 | 0.018953
ZACA 1102Y02 | ZACA 1102 | LOS PADRES | 10.6195 | 15.4408 | 92.94% | 0 | 5 | 80.71% | 0% | 0 | 0.042959 | 1 | 1.6742 | 0.071921 | Medium | Medium | Low | 2020 | 1800 | 0.042959
PINE GROVE 110194936 | PINE GROVE 1101 | STOCKTON | 9.27 | 10 | 75.09% | 1 | 1 | 100% | 0% | 0 | 0.027484 | 1 | 2.6139 | 0.071841 | Medium | Medium | Medium | 2021 | 2177 | 0.027484
HALSEY 1102CB | HALSEY 1102 | SIERRA | 8.0128 | 10 | 41.48% | 9 | 5 | 100% | 0% | 0 | 0.032715 | 1 | 2.1959 | 0.071838 | Medium | Medium | Low | 2022 | 2019 | 0.032715
TIVY VALLEY 11077380 | TIVY VALLEY 1107 | FRESNO | 12.8078 | 20.0234 | 100% | 1 | 4 | 45.52% | 0% | 0 | 0.033102 | 1 | 2.1686 | 0.071783 | Medium | Medium | Low | 2023 | 2007 | 0.033102
SAND CREEK 1103CB | SAND CREEK 1103 | FRESNO | 12.8175 | 20.9724 | 70.85% | 0 | 3 | 100% | 0% | 0 | 0.033442 | 1 | 2.1429 | 0.071662 | Medium | Medium | Low | 2024 | 1997 | 0.033442
AUBERRY 110137536 | AUBERRY 1101 | FRESNO | 5.4818 | 31.3295 | 100% | 3 | 2 | 100% | 20.77% | 1 | 0.055781 | 1 | 1.2846 | 0.071654 | Medium | Medium | Low | 2025 | 1615 | 0.055781
AUBERRY 1102R902 | AUBERRY 1102 | FRESNO | 15.0447 | 11.5312 | 82.04% | 0 | 7 | 100% | 0% | 0 | 0.037249 | 1 | 1.9232 | 0.071637 | Medium | Medium | Low | 2026 | 1912 | 0.037249
OREGON TRAIL 1103CB | OREGON TRAIL 1103 | NORTH VALLEY | 2.7772 | 25.1322 | 81.43% | 2 | 1 | 95.03% | 0% | 0 | 0.030857 | 1 | 2.3184 | 0.071539 | Medium | Medium | Medium | 2027 | 2074 | 0.030857
APPLE HILL 21026552 | APPLE HILL 2102 | SIERRA | 12.3732 | 14.1708 | 74.28% | 2 | 0 | 100% | 6.545% | 1 | 0.045443 | 1 | 1.5727 | 0.07147 | Medium | Medium | Low | 2028 | 1756 | 0.045443
WOODSIDE 1104CB | WOODSIDE 1104 | PENINSULA | 0.34613 | 10 | 13.48% | 0 | 0 | 4.645% | 100% | 0 | 0.027423 | 1 | 2.6038 | 0.071405 | Medium | Medium | Medium | 2029 | 2179 | 0.027423
FORT SEWARD 11211602 | FORT SEWARD 1121 | HUMBOLDT | 18.3365 | 83.3472 | 100% | 8 | 9 | 80.72% | 0% | 0 | 0.074162 | 1 | 0.96205 | 0.071347 | High | High | Low | 2030 | 1444 | 0.074162
COTTONWOOD 11021578 | COTTONWOOD 1102 | NORTH VALLEY | 28.4377 | 38.0859 | 100% | 1 | 7 | 81.08% | 0% | 0 | 0.049028 | 1 | 1.4522 | 0.0712 | Medium | Medium | Low | 2031 | 1695 | 0.049028
SUMMIT 110148632 | SUMMIT 1101 | SIERRA | 2.7291 | 10 | 63.45% | 5 | 6 | 100% | 0% | 0 | 0.037786 | 1 | 1.8801 | 0.071043 | Medium | Medium | Low | 2032 | 1901 | 0.037786
COARSEGOLD 21045516 | COARSEGOLD 2104 | YOSEMITE | 18.4464 | 11.3018 | 100% | 1 | 1 | 100% | 0% | 0 | 0.043744 | 1 | 1.6156 | 0.070674 | Medium | Medium | Low | 2033 | 1781 | 0.043744
VIEJO 22019490 | VIEJO 2201 | CENTRAL COAST | 2.0007 | 10 | 0.3261% | 11 | 5 | 93.15% | 0% | 0 | 0.019802 | 1 | 3.5624 | 0.070542 | Low | Low | High | 2034 | 2420 | 0.019802
BUCKS CREEK 1102CB | BUCKS CREEK 1102 | NORTH VALLEY | 29.5609 | 73.8859 | 50.06% | 3 | 10 | 100% | 23.04% | 0 | 0.077422 | 1 | 0.91112 | 0.07054 | High | High | Low | 2035 | 1418 | 0.077422
FULTON 1102CB | FULTON 1102 | SONOMA | 1.3424 | 10 | 29.14% | 0 | 0 | 30.03% | 82.09% | 0 | 0.02998 | 1 | 2.351 | 0.070482 | Medium | Medium | Medium | 2036 | 2099 | 0.02998
OREGON TRAIL 11021382 | OREGON TRAIL 1102 | NORTH VALLEY | 5.4732 | 13.8429 | 96.06% | 0 | 1 | 100% | 0% | 0 | 0.03292 | 1 | 2.141 | 0.070481 | Medium | Medium | Low | 2037 | 2012 | 0.03292
ALTO 11251256 | ALTO 1125 | NORTH BAY | 1.3805 | 10 | 15.55% | 1 | 0 | 94.69% | 19.69% | 0 | 0.018993 | 1 | 3.7099 | 0.070461 | Low | Low | High | 2038 | 2447 | 0.018993
CEDAR CREEK 11011656 | CEDAR CREEK 1101 | NORTH VALLEY | 32.2585 | 60.8127 | 100% | 10 | 9 | 100% | 0% | 0 | 0.10049 | 1 | 0.70111 | 0.070453 | High | High | Low | 2039 | 1294 | 0.10049
LLAGAS 21011451 | LLAGAS 2101 | SAN JOSE | 5.288 | 70.7589 | 100% | 0 | 0 | 57.46% | 0% | 0 | 0.028219 | 1 | 2.4961 | 0.070438 | Medium | Medium | Medium | 2040 | 2159 | 0.028219
AUBERRY 1102R309 | AUBERRY 1102 | FRESNO | 8.5895 | 21.9499 | 78.92% | 1 | 2 | 100% | 0% | 0 | 0.04051 | 1 | 1.7362 | 0.070333 | Medium | Medium | Low | 2041 | 1841 | 0.04051
RIO DELL 110275970 | RIO DELL 1102 | HUMBOLDT | 7.0738 | 89.4562 | 39.39% | 2 | 2 | 100% | 0% | 0 | 0.05303 | 1 | 1.3258 | 0.07031 | Medium | Medium | Low | 2042 | 1648 | 0.05303
BEAR VALLEY 21014160 | BEAR VALLEY 2101 | YOSEMITE | 22.75 | 19.66 | 91.43% | 0 | 7 | 99.99% | 0% | 0 | 0.032723 | 1 | 2.1443 | 0.070169 | Medium | Medium | Low | 2043 | 2018 | 0.032723
VIEJO 22019698 | VIEJO 2201 | CENTRAL COAST | 0.90136 | 10 | 0% | 2 | 3 | 100% | 0% | 0 | 0.018036 | 1 | 3.8848 | 0.070067 | Low | Low | High | 2044 | 2486 | 0.018036
TYLER 11051536 | TYLER 1105 | NORTH VALLEY | 17.0203 | 70.2834 | 100% | 0 | 5 | 94.18% | 0% | 0 | 0.044384 | 1 | 1.5772 | 0.070005 | Medium | Medium | Low | 2045 | 1770 | 0.044384
COLUMBIA HILL 110190730 | COLUMBIA HILL 1101 | SIERRA | 8.3212 | 17.8031 | 100% | 1 | 4 | 100% | 5.083% | 1 | 0.040638 | 1 | 1.7208 | 0.069929 | Medium | Medium | Low | 2046 | 1838 | 0.040638
HARTLEY 11011306 | HARTLEY 1101 | HUMBOLDT | 8.9139 | 32.0441 | 81.66% | 1 | 4 | 70.23% | 0% | 0 | 0.026684 | 1 | 2.6078 | 0.069587 | Medium | Medium | Medium | 2047 | 2199 | 0.026684
UKIAH 11151216 | UKIAH 1115 | HUMBOLDT | 13.2203 | 25.9617 | 80.05% | 1 | 10 | 70.13% | 0% | 0 | 0.028563 | 1 | 2.4347 | 0.069541 | Medium | Medium | Medium | 2048 | 2131 | 0.028563
LAYTONVILLE 1101402 | LAYTONVILLE 1101 | HUMBOLDT | 22.8392 | 79.1892 | 99.99% | 6 | 8 | 96.88% | 0% | 0 | 0.070954 | 1 | 0.97747 | 0.069355 | High | High | Low | 2049 | 1466 | 0.070954
WILDWOOD 11011576 | WILDWOOD 1101 | NORTH VALLEY | 8.159 | 75.9447 | 99.97% | 1 | 4 | 100% | 0% | 0 | 0.070451 | 1 | 0.98125 | 0.06913 | High | High | Low | 2050 | 1469 | 0.070451
BIG RIVER 11011286 | BIG RIVER 1101 | HUMBOLDT | 4.4303 | 10 | 38.59% | 7 | 9 | 58.78% | 0% | 0 | 0.025767 | 1 | 2.6794 | 0.06904 | Medium | Medium | Medium | 2051 | 2222 | 0.025767
DESCHUTES 11049718 | DESCHUTES 1104 | NORTH VALLEY | 6.0769 | 37.0786 | 75.84% | 1 | 1 | 34.09% | 0% | 0 | 0.025713 | 1 | 2.6812 | 0.068942 | Medium | Medium | Medium | 2052 | 2224 | 0.025713
ATASCADERO 1103A14 | ATASCADERO 1103 | LOS PADRES | 25.1166 | 61.0387 | 72.56% | 0 | 2 | 99.83% | 36.1% | 0 | 0.058565 | 1 | 1.1767 | 0.068916 | Medium | Medium | Low | 2053 | 1586 | 0.058565
PERRY 1101W12 | PERRY 1101 | LOS PADRES | 4.7971 | 10 | 2.793% | 5 | 9 | 75.15% | 0% | 0 | 0.01938 | 1 | 3.5539 | 0.068874 | Low | Low | High | 2054 | 2426 | 0.01938
SOLEDAD 210242506 | SOLEDAD 2102 | CENTRAL COAST | 5.4144 | 74.2068 | 100% | 0 | 1 | 19.16% | 0% | 0 | 0.029952 | 1 | 2.2961 | 0.068774 | Medium | Medium | Medium | 2055 | 2101 | 0.029952
HOLLISTER 21054048 | HOLLISTER 2105 | CENTRAL COAST | 15.0102 | 85.5727 | 83.97% | 1 | 0 | 53.3% | 0% | 0 | 0.034508 | 1 | 1.9904 | 0.068686 | Medium | Medium | Low | 2056 | 1962 | 0.034508
ATASCADERO 1103A16 | ATASCADERO 1103 | LOS PADRES | 18.5162 | 60.2309 | 48.27% | 0 | 1 | 91.95% | 38.05% | 0 | 0.045156 | 1 | 1.5184 | 0.068565 | Medium | Medium | Low | 2057 | 1762 | 0.045156
BELL 11085703 | BELL 1108 | SIERRA | 4.5516 | 23.9501 | 96.07% | 0 | 3 | 57.44% | 0% | 0 | 0.024235 | 1 | 2.8219 | 0.068387 | Medium | Medium | Medium | 2058 | 2270 | 0.024235
WYANDOTTE 11101954 | WYANDOTTE 1110 | NORTH VALLEY | 13.197 | 10 | 59.13% | 1 | 2 | 48.67% | 0% | 0 | 0.019374 | 1 | 3.5192 | 0.068181 | Low | Low | High | 2059 | 2427 | 0.019374
OLETA 11014768 | OLETA 1101 | STOCKTON | 12.2184 | 44.115 | 100% | 0 | 5 | 89.74% | 0% | 0 | 0.040719 | 1 | 1.6733 | 0.068136 | Medium | Medium | Low | 2060 | 1837 | 0.040719
ORINDA 04013442 | ORINDA 0401 | DIABLO | 4.9574 | 14.2459 | 5.153% | 4 | 12 | 73.89% | 0% | 0 | 0.021076 | 1 | 3.2283 | 0.068041 | Low | Low | High | 2061 | 2364 | 0.021076
GARBERVILLE 11011514 | GARBERVILLE 1101 | HUMBOLDT | 14.7707 | 71.7705 | 51.17% | 15 | 7 | 100% | 0% | 0 | 0.10959 | 1 | 0.62013 | 0.067963 | High | High | Low | 2062 | 1261 | 0.10959
PENRYN 1107346 | PENRYN 1107 | SIERRA | 12.7652 | 20.7142 | 69.91% | 3 | 7 | 51.25% | 0% | 0 | 0.026474 | 1 | 2.5635 | 0.067868 | Medium | Medium | Medium | 2063 | 2204 | 0.026474
LAURELES 1111CB | LAURELES 1111 | CENTRAL COAST | 7.0885 | 26.8874 | 36.65% | 2 | 3 | 86.44% | 0% | 0 | 0.023775 | 1 | 2.8474 | 0.067697 | Medium | Medium | Medium | 2064 | 2285 | 0.023775
MOUNTAIN QUARRIES 21012422 | MOUNTAIN QUARRIES 2101 | SIERRA | 8.6685 | 16.1435 | 71.9% | 2 | 3 | 100% | 0% | 0 | 0.029445 | 1 | 2.2909 | 0.067454 | Medium | Medium | Medium | 2065 | 2114 | 0.029445
STILLWATER 110248952 | STILLWATER 1102 | NORTH VALLEY | 10.5922 | 15.961 | 100% | 1 | 3 | 100% | 0% | 0 | 0.041312 | 1 | 1.6325 | 0.067444 | Medium | Medium | Low | 2066 | 1828 | 0.041312
PEORIA 170570198 | PEORIA 1705 | YOSEMITE | 1.5831 | 45.3965 | 98.01% | 1 | 0 | 49.77% | 0% | 0 | 0.025104 | 1 | 2.6852 | 0.067408 | Medium | Medium | Medium | 2067 | 2238 | 0.025104
BEAR VALLEY 210521160 | BEAR VALLEY 2105 | YOSEMITE | 23.7351 | 48.0267 | 99.88% | 2 | 5 | 100% | 3.193% | 0 | 0.043692 | 1 | 1.5413 | 0.067341 | Medium | Medium | Low | 2068 | 1784 | 0.043692
KERCKHOFF 1101R353 | KERCKHOFF 1101 | YOSEMITE | 13.7831 | 33.1172 | 88.25% | 0 | 1 | 100% | 0% | 0 | 0.039955 | 1 | 1.6842 | 0.067293 | Medium | Medium | Low | 2069 | 1856 | 0.039955
FITCH MOUNTAIN 111324550 | FITCH MOUNTAIN 1113 | SONOMA | 9.0741 | 56.5036 | 70.47% | 3 | 1 | 41.6% | 1.605% | 0 | 0.024475 | 1 | 2.7468 | 0.067228 | Medium | Medium | Medium | 2070 | 2262 | 0.024475
CLARKSVILLE 2109CB | CLARKSVILLE 2109 | SIERRA | 1.031 | 10 | 7.581% | 0 | 1 | 91.6% | 7.913% | 0 | 0.018738 | 1 | 3.5876 | 0.067224 | Low | Low | High | 2071 | 2461 | 0.018738
SAN CARLOS 11048942 | SAN CARLOS 1104 | PENINSULA | 1.591 | 10 | 52.6% | 0 | 5 | 59.7% | 0% | 0 | 0.016545 | 1 | 4.0626 | 0.067215 | Low | Low | High | 2072 | 2547 | 0.016545
WEIMAR 1102CB | WEIMAR 1102 | SIERRA | 12.1704 | 10.9563 | 65.6% | 3 | 8 | 100% | 0% | 0 | 0.030334 | 1 | 2.2122 | 0.067104 | Medium | Medium | Low | 2073 | 2082 | 0.030334
JESSUP 11012839 | JESSUP 1101 | NORTH VALLEY | 1.47 | 10 | 100% | 0 | 3 | 100% | 0% | 0 | 0.030308 | 1 | 2.2134 | 0.067083 | Medium | Medium | Low | 2074 | 2084 | 0.030308
EDES 1112CR308 | EDES 1112 | EAST BAY | 3.5907 | 10 | 15.92% | 2 | 4 | 100% | 0% | 0 | 0.020943 | 1 | 3.1965 | 0.066942 | Low | Low | High | 2075 | 2369 | 0.020943
CLARK ROAD 110292622 | CLARK ROAD 1102 | NORTH VALLEY | 30.8948 | 14.2994 | 87.09% | 2 | 9 | 100% | 0% | 0 | 0.032599 | 1 | 2.0512 | 0.066867 | Medium | Medium | Low | 2076 | 2024 | 0.032599
CLAYTON 2215W531R | CLAYTON 2215 | DIABLO | 5.8394 | 49.6313 | 12.81% | 0 | 3 | 54.09% | 19.44% | 0 | 0.019385 | 1 | 3.4465 | 0.06681 | Low | Low | High | 2077 | 2425 | 0.019385
HATTON 11012026 | HATTON 1101 | CENTRAL COAST | 6.3396 | 38.9334 | 46.88% | 0 | 2 | 62.03% | 0% | 0 | 0.021035 | 1 | 3.1737 | 0.06676 | Low | Low | High | 2078 | 2367 | 0.021035
PAUL SWEET 210612828 | PAUL SWEET 2106 | CENTRAL COAST | 1.7112 | 10 | 38.85% | 0 | 0 | 34.49% | 21.63% | 0 | 0.014721 | 1 | 4.5319 | 0.066716 | Low | Low | High | 2079 | 2624 | 0.014721
LAYTONVILLE 110237586 | LAYTONVILLE 1102 | HUMBOLDT | 13.9719 | 83.5514 | 97.33% | 7 | 7 | 100% | 0% | 0 | 0.064508 | 1 | 1.0342 | 0.066716 | High | High | Low | 2080 | 1520 | 0.064508
ELECTRA 1101L3849 | ELECTRA 1101 | STOCKTON | 5.7652 | 16.1295 | 95.19% | 1 | 1 | 100% | 0% | 0 | 0.033619 | 1 | 1.9842 | 0.066706 | Medium | Medium | Low | 2081 | 1990 | 0.033619
GUALALA 1112662 | GUALALA 1112 | HUMBOLDT | 8.3014 | 33.9068 | 0.6489% | 13 | 22 | 98.43% | 0% | 0 | 0.031273 | 1 | 2.1271 | 0.06652 | Medium | Medium | Low | 2082 | 2067 | 0.031273
SUNOL 1101MR650 | SUNOL 1101 | MISSION | 1.0325 | 10 | 30.92% | 0 | 2 | 64.08% | 55.43% | 0 | 0.028936 | 1 | 2.294 | 0.066379 | Medium | Medium | Medium | 2083 | 2126 | 0.028936
WYANDOTTE 1110 | WYANDOTTE 1110 | NORTH VALLEY | 0.049002 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.324 | 0.066261 | Medium | Medium | Medium | 2084 | 2136 | 0.028512
FOOTHILL 110299432 | FOOTHILL 1102 | LOS PADRES | 0.73004 | 62.5798 | 100% | 0 | 3 | 16.66% | 0% | 0 | 0.021721 | 1 | 3.048 | 0.066206 | Low | Low | Medium | 2085 | 2345 | 0.021721
VOLTA 1101CB | VOLTA 1101 | NORTH VALLEY | 9.2068 | 22.5796 | 72.56% | 6 | 5 | 100% | 27.96% | 0 | 0.059425 | 1 | 1.1139 | 0.066194 | Medium | Medium | Low | 2086 | 1573 | 0.059425
SAN LUIS OBISPO 1104V14 | SAN LUIS OBISPO 1104 | LOS PADRES | 9.0673 | 22.9917 | 13.75% | 0 | 2 | 100% | 0% | 0 | 0.023923 | 1 | 2.7612 | 0.066057 | Medium | Medium | Medium | 2087 | 2279 | 0.023923
LUCERNE 1106526 | LUCERNE 1106 | HUMBOLDT | 9.9941 | 16.6965 | 53.92% | 1 | 9 | 92.11% | 0% | 0 | 0.026433 | 1 | 2.4967 | 0.065996 | Medium | Medium | Medium | 2088 | 2206 | 0.026433
SAN LUIS OBISPO 1102597518 | SAN LUIS OBISPO 1102 | LOS PADRES | 0.61698 | 17.5901 | 98.92% | 0 | 1 | 28.41% | 0% | 0 | 0.015039 | 1 | 4.3749 | 0.065794 | Low | Low | High | 2089 | 2607 | 0.015039
WILDWOOD 110185112 | WILDWOOD 1101 | NORTH VALLEY | 6.7175 | 80.7667 | 100% | 4 | 6 | 100% | 0% | 0 | 0.061113 | 1 | 1.0754 | 0.065723 | Medium | Medium | Low | 2090 | 1555 | 0.061113
STAFFORD 11021019 | STAFFORD 1102 | NORTH BAY | 0.54264 | 10 | 100% | 0 | 0 | 74.36% | 0% | 0 | 0.022194 | 1 | 2.9612 | 0.065721 | Medium | Medium | Medium | 2091 | 2325 | 0.022194
RED BLUFF 110585632 | RED BLUFF 1105 | NORTH VALLEY | 13.6331 | 10 | 81.59% | 1 | 4 | 91.86% | 0% | 0 | 0.032365 | 1 | 2.0302 | 0.065709 | Medium | Medium | Low | 2092 | 2032 | 0.032365
AUBERRY 1101R2839 | AUBERRY 1101 | FRESNO | 12.6224 | 16.271 | 63.89% | 0 | 4 | 100% | 0% | 0 | 0.035608 | 1 | 1.8413 | 0.065564 | Medium | Medium | Low | 2093 | 1943 | 0.035608
CAMP EVERS 210392582 | CAMP EVERS 2103 | CENTRAL COAST | 0.22538 | 10 | 0% | 0 | 0 | 8.037% | 100% | 0 | 0.025436 | 1 | 2.5772 | 0.065553 | Medium | Medium | Medium | 2094 | 2231 | 0.025436
HIGHLANDS 110275140 | HIGHLANDS 1102 | HUMBOLDT | 8.7915 | 33.3312 | 88.94% | 0 | 4 | 43.92% | 0% | 0 | 0.019109 | 1 | 3.4168 | 0.065291 | Low | Low | High | 2095 | 2438 | 0.019109
DIAMOND SPRINGS 110656026 | DIAMOND SPRINGS 1106 | SIERRA | 15.0808 | 21.2538 | 81.61% | 2 | 7 | 100% | 0% | 0 | 0.031374 | 1 | 2.0796 | 0.065246 | Medium | Medium | Low | 2096 | 2064 | 0.031374
INDIAN FLAT 110410270 | INDIAN FLAT 1104 | YOSEMITE | 3.8012 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.047687 | 1 | 1.3662 | 0.065148 | Medium | Medium | Low | 2097 | 1710 | 0.047687
POTTER VALLEY P H 110576498 | POTTER VALLEY P H 1105 | HUMBOLDT | 14.8769 | 81.1366 | 60.61% | 2 | 8 | 100% | 0% | 0 | 0.058866 | 1 | 1.1067 | 0.065148 | Medium | Medium | Low | 2098 | 1582 | 0.058866
HAMILTON BRANCH 1101CB | HAMILTON BRANCH 1101 | NORTH VALLEY | 4.2457 | 27.0953 | 61.17% | 1 | 2 | 74.22% | 0% | 0 | 0.019168 | 1 | 3.3969 | 0.065111 | Low | Low | High | 2099 | 2437 | 0.019168
BEAR VALLEY 210576694 | BEAR VALLEY 2105 | YOSEMITE | 4.546 | 19.6129 | 100% | 0 | 0 | 100% | 0% | 0 | 0.030391 | 1 | 2.1365 | 0.064928 | Medium | Medium | Low | 2100 | 2081 | 0.030391
PEORIA 1704877670 | PEORIA 1704 | YOSEMITE | 6.3096 | 69.9259 | 47.8% | 1 | 5 | 95.84% | 0% | 0 | 0.030095 | 1 | 2.1572 | 0.064921 | Medium | Medium | Low | 2101 | 2096 | 0.030095
COARSEGOLD 21046210 | COARSEGOLD 2104 | YOSEMITE | 10.6712 | 44.0621 | 48.52% | 0 | 11 | 100% | 0% | 0 | 0.033703 | 1 | 1.9204 | 0.064723 | Medium | Medium | Low | 2102 | 1989 | 0.033703
OAKLAND X 1104CB | OAKLAND X 1104 | EAST BAY | 1.3072 | 10 | 2.074% | 0 | 2 | 53.76% | 24.1% | 0 | 0.014319 | 1 | 4.5195 | 0.064715 | Low | Low | High | 2103 | 2639 | 0.014319
CLOVERDALE 1102801904 | CLOVERDALE 1102 | SONOMA | 0.014995 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.2691 | 0.064697 | Medium | Medium | Medium | 2104 | 2136 | 0.028512
BROWNS VALLEY 110197188 | BROWNS VALLEY 1101 | SIERRA | 6.5763 | 19.9978 | 93.03% | 2 | 3 | 95.83% | 0% | 0 | 0.03906 | 1 | 1.6554 | 0.064659 | Medium | Medium | Low | 2105 | 1880 | 0.03906
SAND CREEK 11037070 | SAND CREEK 1103 | FRESNO | 17.8283 | 24.5064 | 100% | 1 | 3 | 100% | 0% | 0 | 0.049625 | 1 | 1.3027 | 0.064648 | Medium | Medium | Low | 2106 | 1687 | 0.049625
PHILO 1102CB | PHILO 1102 | HUMBOLDT | 5.5805 | 58.9475 | 61.62% | 10 | 11 | 44.58% | 0% | 0 | 0.027409 | 1 | 2.3552 | 0.064554 | Medium | Medium | Medium | 2107 | 2180 | 0.027409
GREEN VALLEY 210112106 | GREEN VALLEY 2101 | CENTRAL COAST | 6.3447 | 10 | 54.91% | 5 | 0 | 33.81% | 31.75% | 0 | 0.018337 | 1 | 3.5176 | 0.064501 | Low | Low | High | 2108 | 2473 | 0.018337
STELLING 111060090 | STELLING 1110 | DE ANZA | 6.0088 | 10 | 51.27% | 4 | 1 | 91.55% | 0% | 0 | 0.019051 | 1 | 3.3845 | 0.064479 | Low | Low | High | 2109 | 2445 | 0.019051
DESCHUTES 11011652 | DESCHUTES 1101 | NORTH VALLEY | 22.782 | 45.1857 | 96.26% | 0 | 4 | 93.2% | 0% | 0 | 0.035474 | 1 | 1.8172 | 0.064462 | Medium | Medium | Low | 2110 | 1946 | 0.035474
JESSUP 11011496 | JESSUP 1101 | NORTH VALLEY | 14.7255 | 17.8878 | 100% | 1 | 3 | 90.72% | 1.915% | 1 | 0.030466 | 1 | 2.1149 | 0.064433 | Medium | Medium | Low | 2111 | 2078 | 0.030466
SAN LEANDRO U 1114MR545 | SAN LEANDRO U 1114 | MISSION | 2.8053 | 10 | 16.34% | 0 | 2 | 62.83% | 0% | 0 | 0.01772 | 1 | 3.623 | 0.0642 | Low | Low | High | 2112 | 2501 | 0.01772
COTTONWOOD 110168190 | COTTONWOOD 1101 | NORTH VALLEY | 22.7429 | 39.5713 | 100% | 3 | 4 | 90.15% | 0% | 0 | 0.045908 | 1 | 1.3967 | 0.064119 | Medium | Medium | Low | 2113 | 1746 | 0.045908
AUBERRY 1101R322 | AUBERRY 1101 | FRESNO | 7.483 | 34.3076 | 99.18% | 0 | 0 | 100% | 0% | 0 | 0.033278 | 1 | 1.9251 | 0.064062 | Medium | Medium | Low | 2114 | 2000 | 0.033278
SAUSALITO 1102410 | SAUSALITO 1102 | NORTH BAY | 1.0698 | 10 | 84.58% | 1 | 1 | 48.49% | 0% | 0 | 0.017913 | 1 | 3.5643 | 0.063846 | Low | Low | High | 2115 | 2493 | 0.017913
ROB ROY 210412596 | ROB ROY 2104 | CENTRAL COAST | 7.6393 | 10 | 59% | 3 | 3 | 72.22% | 0.5428% | 0 | 0.019837 | 1 | 3.2178 | 0.063833 | Low | Low | High | 2116 | 2418 | 0.019837
SAN RAFAEL 1105344 | SAN RAFAEL 1105 | NORTH BAY | 2.2778 | 10 | 70.24% | 0 | 2 | 30.4% | 0% | 0 | 0.015331 | 1 | 4.1625 | 0.063813 | Low | Low | High | 2117 | 2596 | 0.015331
APPLE HILL 210212025 | APPLE HILL 2102 | SIERRA | 9.1227 | 10 | 100% | 3 | 0 | 100% | 0% | 0 | 0.033724 | 1 | 1.8915 | 0.063789 | Medium | Medium | Low | 2118 | 1985 | 0.033724
CALPELLA 11011204 | CALPELLA 1101 | HUMBOLDT | 9.1784 | 21.5734 | 72.42% | 2 | 10 | 70.57% | 0% | 0 | 0.030223 | 1 | 2.1101 | 0.063774 | Medium | Medium | Low | 2119 | 2091 | 0.030223
FORT SEWARD 1122CB | FORT SEWARD 1122 | HUMBOLDT | 17.3427 | 75.2963 | 100% | 3 | 11 | 79.07% | 0% | 0 | 0.067846 | 1 | 0.93948 | 0.06374 | High | High | Low | 2120 | 1488 | 0.067846
CURTIS 1703CB | CURTIS 1703 | YOSEMITE | 8.4941 | 16.7987 | 53.44% | 0 | 2 | 77.88% | 0% | 0 | 0.0196 | 1 | 3.2518 | 0.063736 | Low | Low | High | 2121 | 2423 | 0.0196
SUNOL 1101MR387 | SUNOL 1101 | MISSION | 4.657 | 55.0854 | 92.88% | 0 | 1 | 93.35% | 0% | 0 | 0.03951 | 1 | 1.6108 | 0.063643 | Medium | Medium | Low | 2122 | 1872 | 0.03951
SOBRANTE 1101L534R | SOBRANTE 1101 | DIABLO | 1.5331 | 10 | 22.75% | 1 | 1 | 80.03% | 7.584% | 0 | 0.016712 | 1 | 3.8056 | 0.0636 | Low | Low | High | 2123 | 2540 | 0.016712
PHILO 11013700 | PHILO 1101 | HUMBOLDT | 18.1219 | 64.058 | 52.24% | 7 | 7 | 100% | 0% | 0 | 0.039935 | 1 | 1.5874 | 0.063395 | Medium | Medium | Low | 2124 | 1859 | 0.039935
MENLO 11037902 | MENLO 1103 | PENINSULA | 11.6802 | 47.4802 | 20.98% | 8 | 4 | 71.01% | 0% | 0 | 0.022804 | 1 | 2.779 | 0.063373 | Medium | Medium | Medium | 2125 | 2311 | 0.022804
OREGON TRAIL 11031448 | OREGON TRAIL 1103 | NORTH VALLEY | 30.932 | 14.1761 | 100% | 1 | 10 | 100% | 0% | 0 | 0.041357 | 1 | 1.5321 | 0.063365 | Medium | Medium | Low | 2126 | 1827 | 0.041357
GOLDTREE 1108CB | GOLDTREE 1108 | LOS PADRES | 2.5563 | 36.4917 | 29.18% | 2 | 3 | 52.35% | 0% | 0 | 0.022193 | 1 | 2.85 | 0.063249 | Medium | Medium | Medium | 2127 | 2326 | 0.022193
SAND CREEK 110397354 | SAND CREEK 1103 | FRESNO | 8.1104 | 10 | 100% | 0 | 1 | 80.11% | 0% | 0 | 0.035362 | 1 | 1.7829 | 0.063047 | Medium | Medium | Low | 2128 | 1950 | 0.035362
CLARK ROAD 11022584 | CLARK ROAD 1102 | NORTH VALLEY | 7.9946 | 18.0642 | 99.96% | 1 | 2 | 85.31% | 0% | 0 | 0.0275 | 1 | 2.2918 | 0.063027 | Medium | Medium | Medium | 2129 | 2175 | 0.0275
MONTICELLO 110193384 | MONTICELLO 1101 | NORTH BAY | 15.2847 | 55.7693 | 100% | 0 | 3 | 88.22% | 0% | 0 | 0.047273 | 1 | 1.3315 | 0.062941 | Medium | Medium | Low | 2130 | 1721 | 0.047273
MOUNTAIN QUARRIES 210135466 | MOUNTAIN QUARRIES 2101 | SIERRA | 7.4036 | 10 | 90.3% | 2 | 0 | 100% | 0% | 0 | 0.030814 | 1 | 2.0397 | 0.062851 | Medium | Medium | Low | 2131 | 2075 | 0.030814
CHOLAME 21025597 | CHOLAME 2102 | LOS PADRES | 5.1199 | 69.1665 | 100% | 0 | 2 | 100% | 0% | 0 | 0.049821 | 1 | 1.2615 | 0.062847 | Medium | Medium | Low | 2132 | 1684 | 0.049821
DOBBINS 1101CB | DOBBINS 1101 | SIERRA | 0.67055 | 10 | 81.76% | 0 | 0 | 100% | 0% | 0 | 0.028046 | 1 | 2.2347 | 0.062675 | Medium | Medium | Medium | 2133 | 2162 | 0.028046
REDBUD 110191960 | REDBUD 1101 | HUMBOLDT | 7.0156 | 10 | 50% | 3 | 16 | 100% | 0% | 0 | 0.0275 | 1 | 2.2782 | 0.062653 | Medium | Medium | Medium | 2134 | 2174 | 0.0275
SAND CREEK 11037823F | SAND CREEK 1103 | FRESNO | 4.6802 | 10 | 100% | 0 | 1 | 100% | 0% | 0 | 0.029099 | 1 | 2.1489 | 0.062531 | Medium | Medium | Low | 2135 | 2119 | 0.029099
CALAVERAS CEMENT 110111188 | CALAVERAS CEMENT 1101 | STOCKTON | 6.2741 | 29.7373 | 82.62% | 0 | 1 | 100% | 0% | 0 | 0.032851 | 1 | 1.9023 | 0.062494 | Medium | Medium | Low | 2136 | 2016 | 0.032851
NARROWS 210276952 | NARROWS 2102 | SIERRA | 3.581 | 10 | 96.43% | 1 | 1 | 31.95% | 0% | 0 | 0.016756 | 1 | 3.7233 | 0.062386 | Low | Low | High | 2137 | 2537 | 0.016756
BURNEY 110145984 | BURNEY 1101 | NORTH VALLEY | 4.7181 | 10 | 42.42% | 2 | 3 | 98.54% | 0% | 0 | 0.025045 | 1 | 2.4898 | 0.062355 | Medium | Medium | Medium | 2138 | 2241 | 0.025045
HALSEY 11026129 | HALSEY 1102 | SIERRA | 3.2034 | 10 | 99.84% | 0 | 1 | 100% | 0% | 0 | 0.029062 | 1 | 2.1446 | 0.062326 | Medium | Medium | Low | 2139 | 2122 | 0.029062
PUEBLO 1104640 | PUEBLO 1104 | NORTH BAY | 1.0277 | 10 | 45.71% | 1 | 4 | 32.52% | 0% | 0 | 0.02008 | 1 | 3.1015 | 0.06228 | Low | Low | High | 2140 | 2407 | 0.02008
LONE TREE 210521210 | LONE TREE 2105 | DIABLO | 9.5646 | 10 | 95.6% | 0 | 2 | 59.2% | 0% | 0 | 0.019234 | 1 | 3.2356 | 0.062233 | Low | Low | High | 2141 | 2434 | 0.019234
HALF MOON BAY 110369412 | HALF MOON BAY 1103 | PENINSULA | 16.9285 | 23.3773 | 24.92% | 11 | 5 | 79.06% | 0% | 0 | 0.038624 | 1 | 1.6101 | 0.062188 | Medium | Medium | Low | 2142 | 1887 | 0.038624
FROGTOWN 17027108 | FROGTOWN 1702 | STOCKTON | 10.0437 | 39.0873 | 66.95% | 0 | 1 | 78.26% | 0% | 0 | 0.024952 | 1 | 2.4898 | 0.062125 | Medium | Medium | Medium | 2143 | 2244 | 0.024952
RED BLUFF 11041302 | RED BLUFF 1104 | NORTH VALLEY | 14.0918 | 39.8066 | 84.84% | 0 | 4 | 98.04% | 0% | 0 | 0.03726 | 1 | 1.6666 | 0.062097 | Medium | Medium | Low | 2144 | 1911 | 0.03726
IGNACIO 1104450582 | IGNACIO 1104 | NORTH BAY | 3.8063 | 10 | 29.85% | 0 | 4 | 90.17% | 0% | 0 | 0.020738 | 1 | 2.9935 | 0.062078 | Low | Low | Medium | 2145 | 2378 | 0.020738
CAMBRIA 1102CB | CAMBRIA 1102 | LOS PADRES | 14.9946 | 41.8579 | 39.26% | 1 | 1 | 64.1% | 0% | 0 | 0.026518 | 1 | 2.3401 | 0.062055 | Medium | Medium | Medium | 2146 | 2202 | 0.026518
MENLO 110212249 | MENLO 1102 | PENINSULA | 2.4062 | 33.867 | 49.86% | 2 | 1 | 100% | 0% | 0 | 0.02665 | 1 | 2.3278 | 0.062037 | Medium | Medium | Medium | 2147 | 2200 | 0.02665
VALLEY VIEW 1105P190 | VALLEY VIEW 1105 | EAST BAY | 3.5037 | 10 | 43.53% | 0 | 2 | 59.31% | 0% | 0 | 0.014389 | 1 | 4.3115 | 0.062036 | Low | Low | High | 2148 | 2634 | 0.014389
CASTRO VALLEY 1108MR525 | CASTRO VALLEY 1108 | MISSION | 0.061081 | 10 | 0% | 0 | 3 | 100% | 0% | 0 | 0.017573 | 1 | 3.5299 | 0.062033 | Low | Low | High | 2149 | 2506 | 0.017573
WEIMAR 11022038 | WEIMAR 1102 | SIERRA | 8.1278 | 10 | 76.79% | 4 | 4 | 100% | 0% | 0 | 0.030781 | 1 | 2.0149 | 0.062021 | Medium | Medium | Low | 2150 | 2076 | 0.030781
NORTH BRANCH 110111158 | NORTH BRANCH 1101 | STOCKTON | 11.9363 | 47.5829 | 78.02% | 0 | 4 | 41.95% | 0% | 0 | 0.024519 | 1 | 2.528 | 0.061986 | Medium | Medium | Medium | 2151 | 2261 | 0.024519
MARIPOSA 2102CB | MARIPOSA 2102 | YOSEMITE | 6.6916 | 39.3684 | 36.18% | 1 | 6 | 63.39% | 0% | 0 | 0.024571 | 1 | 2.5225 | 0.061982 | Medium | Medium | Medium | 2152 | 2259 | 0.024571
WHITMORE 110145262 | WHITMORE 1101 | NORTH VALLEY | 28.7585 | 25.719 | 87.63% | 2 | 2 | 100% | 0% | 0 | 0.03964 | 1 | 1.5616 | 0.061901 | Medium | Medium | Low | 2153 | 1867 | 0.03964
MC KEE 110870535 | MC KEE 1108 | SAN JOSE | 1.0836 | 23.5844 | 100% | 0 | 0 | 32.92% | 0% | 0 | 0.016178 | 1 | 3.8247 | 0.061876 | Low | Low | High | 2154 | 2564 | 0.016178
OAKLAND X 1106CB | OAKLAND X 1106 | EAST BAY | 4.876 | 10 | 15.55% | 5 | 5 | 41.41% | 19.42% | 0 | 0.014897 | 1 | 4.146 | 0.061764 | Low | Low | High | 2155 | 2611 | 0.014897
HIGHLANDS 110484640 | HIGHLANDS 1104 | HUMBOLDT | 0.56405 | 10 | 72.8% | 1 | 1 | 76.24% | 0% | 0 | 0.021388 | 1 | 2.8868 | 0.061742 | Low | Low | Medium | 2156 | 2355 | 0.021388
GUALALA 1111445166 | GUALALA 1111 | HUMBOLDT | 7.5421 | 19.2895 | 4.143% | 11 | 12 | 79.44% | 0% | 0 | 0.036855 | 1 | 1.6737 | 0.061683 | Medium | Medium | Low | 2157 | 1920 | 0.036855
PASO ROBLES 1103N52 | PASO ROBLES 1103 | LOS PADRES | 6.5425 | 67.4375 | 22.89% | 0 | 0 | 100% | 0% | 0 | 0.025622 | 1 | 2.4074 | 0.061683 | Medium | Medium | Medium | 2158 | 2228 | 0.025622
EDES 1112CR282 | EDES 1112 | EAST BAY | 3.4204 | 10 | 46.24% | 0 | 3 | 83.7% | 0% | 0 | 0.019097 | 1 | 3.2289 | 0.061662 | Low | Low | High | 2159 | 2441 | 0.019097
GONZALES 11013094 | GONZALES 1101 | CENTRAL COAST | 3.5612 | 68.6689 | 100% | 1 | 1 | 39.42% | 0% | 0 | 0.027478 | 1 | 2.2388 | 0.061516 | Medium | Medium | Medium | 2160 | 2178 | 0.027478
OLETA 110151740 | OLETA 1101 | STOCKTON | 9.506 | 52.4452 | 97.68% | 1 | 4 | 44.88% | 0% | 0 | 0.023833 | 1 | 2.5749 | 0.061369 | Medium | Medium | Medium | 2161 | 2283 | 0.023833
SAN RAFAEL 1109418 | SAN RAFAEL 1109 | NORTH BAY | 4.3553 | 10 | 55.54% | 4 | 2 | 35.66% | 0% | 0 | 0.013234 | 1 | 4.6368 | 0.061362 | Low | Low | High | 2162 | 2702 | 0.013234
HIGGINS 11097863 | HIGGINS 1109 | SIERRA | 4.2214 | 12.2843 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028948 | 1 | 2.1193 | 0.06135 | Medium | Medium | Low | 2163 | 2125 | 0.028948
SAN LUIS OBISPO 1104V40 | SAN LUIS OBISPO 1104 | LOS PADRES | 11.8926 | 26.5582 | 47.13% | 0 | 7 | 51.44% | 0% | 0 | 0.028654 | 1 | 2.1403 | 0.061327 | Medium | Medium | Low | 2164 | 2129 | 0.028654
BURNEY 11011358 | BURNEY 1101 | NORTH VALLEY | 7.0165 | 60.5885 | 76.98% | 1 | 3 | 74.4% | 0% | 0 | 0.0317 | 1 | 1.9333 | 0.061286 | Medium | Medium | Low | 2165 | 2053 | 0.0317
NARROWS 2101CB | NARROWS 2101 | SIERRA | 15.6172 | 42.314 | 50.34% | 2 | 7 | 100% | 0% | 0 | 0.031975 | 1 | 1.9092 | 0.061047 | Medium | Medium | Low | 2166 | 2048 | 0.031975
BRUNSWICK 111061602 | BRUNSWICK 1110 | SIERRA | 9.4416 | 27.4436 | 52.21% | 4 | 4 | 73.99% | 0% | 0 | 0.022016 | 1 | 2.7653 | 0.06088 | Medium | Medium | Medium | 2167 | 2336 | 0.022016
KONOCTI 1102948 | KONOCTI 1102 | HUMBOLDT | 6.065 | 30.1749 | 46.64% | 1 | 1 | 78.59% | 0% | 0 | 0.02028 | 1 | 2.9925 | 0.060688 | Low | Low | Medium | 2168 | 2395 | 0.02028
KONOCTI 1108CB | KONOCTI 1108 | HUMBOLDT | 6.6517 | 32.6717 | 74.99% | 0 | 6 | 75.6% | 0% | 0 | 0.024164 | 1 | 2.5096 | 0.060644 | Medium | Medium | Medium | 2169 | 2274 | 0.024164
ELK CREEK 11012032 | ELK CREEK 1101 | NORTH VALLEY | 9.5675 | 53.63 | 100% | 0 | 1 | 99.9% | 0% | 0 | 0.044086 | 1 | 1.3752 | 0.060626 | Medium | Medium | Low | 2170 | 1775 | 0.044086
TIVY VALLEY 11077370 | TIVY VALLEY 1107 | FRESNO | 11.4788 | 20.0364 | 68.04% | 0 | 4 | 63.49% | 0% | 0 | 0.030142 | 1 | 2.0098 | 0.060577 | Medium | Medium | Low | 2171 | 2095 | 0.030142
BURNEY 11011340 | BURNEY 1101 | NORTH VALLEY | 18.024 | 21.8274 | 89.51% | 4 | 2 | 100% | 0% | 0 | 0.045714 | 1 | 1.3248 | 0.060564 | Medium | Medium | Low | 2172 | 1752 | 0.045714
REDBUD 1102922 | REDBUD 1102 | HUMBOLDT | 3.3 | 10 | 97% | 1 | 5 | 42.49% | 0% | 0 | 0.026319 | 1 | 2.2985 | 0.060493 | Medium | Medium | Medium | 2173 | 2211 | 0.026319
CAYETANO 2109MR572 | CAYETANO 2109 | MISSION | 8.1822 | 10 | 47.67% | 0 | 2 | 66.51% | 19.49% | 0 | 0.021821 | 1 | 2.7701 | 0.060448 | Medium | Medium | Medium | 2174 | 2341 | 0.021821
EL CERRITO G 1110BR236 | EL CERRITO G 1110 | EAST BAY | 0.52869 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.7576 | 0.0604 | Low | Low | High | 2175 | 2735 | 0.012695
SAN RAFAEL 1104CB | SAN RAFAEL 1104 | NORTH BAY | 2.4428 | 10 | 2.078% | 0 | 0 | 23.27% | 19.55% | 0 | 0.012295 | 1 | 4.9116 | 0.060389 | Low | Low | High | 2176 | 2788 | 0.012295
BELL 1109CB | BELL 1109 | SIERRA | 13.433 | 10 | 50.92% | 4 | 3 | 76.11% | 0% | 0 | 0.022099 | 1 | 2.7321 | 0.060377 | Medium | Medium | Medium | 2177 | 2331 | 0.022099
MORAGA 1103E510R | MORAGA 1103 | DIABLO | 1.3196 | 10 | 100% | 0 | 1 | 21.61% | 0% | 0 | 0.013477 | 1 | 4.475 | 0.060311 | Low | Low | High | 2178 | 2684 | 0.013477
LAS AROMAS 0401LA401R | LAS AROMAS 0401 | DIABLO | 3.6951 | 10 | 0.309% | 3 | 6 | 93.3% | 0% | 0 | 0.018243 | 1 | 3.3031 | 0.060258 | Low | Low | High | 2179 | 2480 | 0.018243
PEORIA 170590374 | PEORIA 1705 | YOSEMITE | 3.6064 | 10 | 81.75% | 0 | 1 | 81.35% | 0% | 0 | 0.020938 | 1 | 2.8737 | 0.060168 | Low | Low | Medium | 2180 | 2370 | 0.020938
PLACER 1103CB | PLACER 1103 | SIERRA | 12.2492 | 28.3994 | 44.01% | 5 | 11 | 41.67% | 0% | 0 | 0.020134 | 1 | 2.9879 | 0.060157 | Low | Low | Medium | 2181 | 2402 | 0.020134
SAN LUIS OBISPO 1103V82 | SAN LUIS OBISPO 1103 | LOS PADRES | 6.5219 | 24.8763 | 65.03% | 1 | 11 | 46.53% | 0% | 0 | 0.026432 | 1 | 2.2734 | 0.060091 | Medium | Medium | Medium | 2182 | 2207 | 0.026432
NORTH BRANCH 1101TS1115 | NORTH BRANCH 1101 | STOCKTON | 17.6104 | 17.7152 | 77.63% | 1 | 0 | 100% | 0% | 0 | 0.025404 | 1 | 2.3625 | 0.060018 | Medium | Medium | Medium | 2183 | 2232 | 0.025404
SNEATH LANE 110134438 | SNEATH LANE 1101 | PENINSULA | 1.6791 | 10 | 46% | 1 | 0 | 33.32% | 0% | 0 | 0.014366 | 1 | 4.1734 | 0.059955 | Low | Low | High | 2184 | 2636 | 0.014366
SYCAMORE CREEK 1111CB | SYCAMORE CREEK 1111 | NORTH VALLEY | 8.3942 | 56.8563 | 45.31% | 1 | 3 | 47.06% | 0% | 0 | 0.020907 | 1 | 2.8652 | 0.059903 | Low | Low | Medium | 2185 | 2372 | 0.020907
BOLINAS 11011236 | BOLINAS 1101 | NORTH BAY | 3.0037 | 58.0295 | 0% | 0 | 0 | 73.67% | 0% | 0 | 0.017604 | 1 | 3.3892 | 0.059663 | Low | Low | High | 2186 | 2504 | 0.017604
ECHO SUMMIT 110155262 | ECHO SUMMIT 1101 | (blank) | 0.16554 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 2.0866 | 0.059493 | Medium | Medium | Low | 2187 | 2136 | 0.028512
DIAMOND SPRINGS 110740353 | DIAMOND SPRINGS 1107 | SIERRA | 2.2415 | 10 | 74.48% | 1 | 0 | 87.31% | 0% | 0 | 0.023671 | 1 | 2.5112 | 0.059443 | Medium | Medium | Medium | 2188 | 2290 | 0.023671
HARTLEY 11014710 | HARTLEY 1101 | HUMBOLDT | 1.5005 | 10 | 52.07% | 1 | 0 | 100% | 0% | 0 | 0.019631 | 1 | 3.0245 | 0.059375 | Low | Low | Medium | 2189 | 2422 | 0.019631
VOLTA 11011516 | VOLTA 1101 | NORTH VALLEY | 25.7297 | 67.2634 | 100% | 4 | 8 | 100% | 0% | 0 | 0.084582 | 1 | 0.70197 | 0.059374 | High | High | Low | 2190 | 1365 | 0.084582
SAN JOAQUIN #2 110310320 | SAN JOAQUIN #2 1103 | YOSEMITE | 11.8104 | 12.4719 | 98.89% | 1 | 18 | 100% | 0% | 0 | 0.047599 | 1 | 1.2459 | 0.059305 | Medium | Medium | Low | 2191 | 1714 | 0.047599
OILFIELDS 110383158 | OILFIELDS 1103 | CENTRAL COAST | 18.1787 | 60.504 | 100% | 0 | 4 | 93.79% | 0% | 0 | 0.067417 | 1 | 0.87957 | 0.059298 | High | High | Low | 2192 | 1492 | 0.067417
PEORIA 170567898 | PEORIA 1705 | YOSEMITE | 5.0246 | 20.73 | 47.42% | 1 | 2 | 80.37% | 0% | 0 | 0.0199 | 1 | 2.9757 | 0.059217 | Low | Low | Medium | 2193 | 2414 | 0.0199
RINCON 1101CB | RINCON 1101 | SONOMA | 2.1293 | 20.6419 | 39.27% | 1 | 4 | 43.97% | 11.03% | 0 | 0.018447 | 1 | 3.2011 | 0.05905 | Low | Low | High | 2194 | 2468 | 0.018447
MIRABEL 1101CB | MIRABEL 1101 | SONOMA | 2.6279 | 19.2673 | 59.3% | 0 | 2 | 31.12% | 21.2% | 0 | 0.016241 | 1 | 3.6316 | 0.058979 | Low | Low | High | 2195 | 2562 | 0.016241
ANNAPOLIS 1101CB | ANNAPOLIS 1101 | HUMBOLDT | 0.65809 | 81.2301 | 84.52% | 1 | 1 | 100% | 0% | 0 | 0.041698 | 1 | 1.4144 | 0.058979 | Medium | Medium | Low | 2196 | 1822 | 0.041698
PALMER 110198478 | PALMER 1101 | LOS PADRES | 4.9874 | 64.4051 | 90.52% | 0 | 0 | 100% | 0% | 0 | 0.05552 | 1 | 1.0612 | 0.058918 | Medium | Medium | Low | 2197 | 1617 | 0.05552
MORGAN HILL 210940000 | MORGAN HILL 2109 | SAN JOSE | 1.7684 | 10 | 99.47% | 0 | 0 | 59.08% | 0% | 0 | 0.019023 | 1 | 3.095 | 0.058876 | Low | Low | High | 2198 | 2446 | 0.019023
GEYSERVILLE 1102522 | GEYSERVILLE 1102 | SONOMA | 8.3806 | 11.5615 | 69.84% | 1 | 7 | 78.98% | 12.25% | 0 | 0.038533 | 1 | 1.5258 | 0.058796 | Medium | Medium | Low | 2199 | 1888 | 0.038533
KONOCTI 11084039 | KONOCTI 1108 | HUMBOLDT | 1.6026 | 10 | 100% | 0 | 2 | 69.54% | 0% | 0 | 0.022058 | 1 | 2.6616 | 0.05871 | Medium | Medium | Medium | 2200 | 2333 | 0.022058
MORAGA 11017616 | MORAGA 1101 | DIABLO | 1.1725 | 14.9864 | 34.86% | 0 | 4 | 82.16% | 0% | 0 | 0.015878 | 1 | 3.6873 | 0.058547 | Low | Low | High | 2201 | 2579 | 0.015878
EL DORADO PH 210152456 | EL DORADO PH 2101 | SIERRA | 10.1963 | 62.6198 | 100% | 3 | 10 | 100% | 0% | 0 | 0.058118 | 1 | 1.007 | 0.058524 | Medium | Medium | Low | 2202 | 1593 | 0.058118
JESSUP 11021550 | JESSUP 1102 | NORTH VALLEY | 17.7067 | 29.9161 | 71.58% | 1 | 0 | 80.02% | 0% | 0 | 0.024597 | 1 | 2.3755 | 0.05843 | Medium | Medium | Medium | 2203 | 2257 | 0.024597
WILLOW CREEK 11033090 | WILLOW CREEK 1103 | HUMBOLDT | 10.7823 | 82.4459 | 100% | 5 | 3 | 100% | 0% | 0 | 0.058956 | 1 | 0.99063 | 0.058403 | Medium | Medium | Low | 2204 | 1581 | 0.058956
STAFFORD 1102908 | STAFFORD 1102 | NORTH BAY | 0.96495 | 10 | 77.17% | 0 | 3 | 21.89% | 0% | 0 | 0.01736 | 1 | 3.3591 | 0.058315 | Low | Low | High | 2205 | 2516 | 0.01736
BEAR VALLEY 21054609 | BEAR VALLEY 2105 | YOSEMITE | 4.5488 | 18.0167 | 100% | 1 | 5 | 100% | 0% | 0 | 0.033715 | 1 | 1.728 | 0.058259 | Medium | Medium | Low | 2206 | 1986 | 0.033715
VIEJO 22022606 | VIEJO 2202 | CENTRAL COAST | 0.94683 | 10 | 0% | 1 | 1 | 98.67% | 0% | 0 | 0.014784 | 1 | 3.9289 | 0.058085 | Low | Low | High | 2207 | 2620 | 0.014784
CORNING 110253184 | CORNING 1102 | NORTH VALLEY | 31.925 | 68.303 | 86.89% | 0 | 7 | 100% | 0% | 0 | 0.049388 | 1 | 1.1736 | 0.05796 | Medium | Medium | Low | 2208 | 1691 | 0.049388
MORGAN HILL 2105XR564 | MORGAN HILL 2105 | SAN JOSE | 5.4316 | 26.8638 | 49.46% | 0 | 4 | 75.02% | 0% | 0 | 0.023443 | 1 | 2.4719 | 0.057948 | Medium | Medium | Medium | 2209 | 2296 | 0.023443
CMC 1101CB | CMC 1101 | LOS PADRES | 2.0609 | 25.5297 | 52.24% | 0 | 0 | 100% | 0% | 0 | 0.021532 | 1 | 2.6866 | 0.057849 | Low | Low | Medium | 2210 | 2350 | 0.021532
RIDGE 0402CB | RIDGE 0402 | EAST BAY | 1.6674 | 10 | 31.81% | 1 | 0 | 69.66% | 0% | 0 | 0.014084 | 1 | 4.0946 | 0.05767 | Low | Low | High | 2211 | 2658 | 0.014084
LAS PULGAS 0401CB | LAS PULGAS 0401 | PENINSULA | 0.063561 | 10 | 100% | 0 | 1 | 1.053% | 0% | 0 | 0.012548 | 1 | 4.5955 | 0.057664 | Low | Low | High | 2212 | 2771 | 0.012548
FLORENCE 0401CR220 | FLORENCE 0401 | EAST BAY | 0.0014212 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.5363 | 0.057589 | Low | Low | High | 2213 | 2735 | 0.012695
LLAGAS 21011449 | LLAGAS 2101 | SAN JOSE | 7.6142 | 50.4014 | 99.39% | 2 | 1 | 54.33% | 0% | 0 | 0.024906 | 1 | 2.3109 | 0.057555 | Medium | Medium | Medium | 2214 | 2245 | 0.024906
TAR FLAT 0401CB | TAR FLAT 0401 | YOSEMITE | 3.4825 | 10 | 7.176% | 1 | 2 | 94.76% | 17.84% | 1 | 0.017966 | 1 | 3.199 | 0.057473 | Low | Low | High | 2215 | 2490 | 0.017966
SALMON CREEK 110137368 | SALMON CREEK 1101 | SONOMA | 7.013 | 10 | 3.2% | 1 | 7 | 100% | 0% | 0 | 0.029331 | 1 | 1.9591 | 0.057461 | Medium | Medium | Low | 2216 | 2115 | 0.029331
CLOVERDALE 1102CB | CLOVERDALE 1102 | SONOMA | 0.24384 | 33.3215 | 52.03% | 0 | 0 | 8.095% | 59.2% | 0 | 0.023631 | 1 | 2.4298 | 0.05742 | Medium | Medium | Medium | 2217 | 2292 | 0.023631
POINT ARENA 11012637 | POINT ARENA 1101 | HUMBOLDT | 4.0404 | 84.4232 | 59.73% | 1 | 2 | 100% | 0% | 0 | 0.046116 | 1 | 1.2415 | 0.057252 | Medium | Medium | Low | 2218 | 1739 | 0.046116
VALLEY VIEW 1106P176 | VALLEY VIEW 1106 | EAST BAY | 0.884 | 14.838 | 80.1% | 1 | 0 | 21.45% | 0% | 0 | 0.013387 | 1 | 4.2737 | 0.057211 | Low | Low | High | 2219 | 2692 | 0.013387
ROSSMOOR 110845268 | ROSSMOOR 1108 | DIABLO | 3.7726 | 24.3862 | 31.05% | 0 | 7 | 47.92% | 0% | 0 | 0.014195 | 1 | 4.0289 | 0.057189 | Low | Low | High | 2220 | 2652 | 0.014195
SAUSALITO 11021500 | SAUSALITO 1102 | NORTH BAY | 1.1513 | 69.0338 | 0% | 0 | 0 | 90.51% | 0% | 0 | 0.017208 | 1 | 3.3211 | 0.05715 | Low | Low | High | 2221 | 2522 | 0.017208
SARATOGA 11076867 | SARATOGA 1107 | DE ANZA | 0.24862 | 10 | 100% | 0 | 2 | 30.1% | 0% | 0 | 0.014963 | 1 | 3.817 | 0.057115 | Low | Low | High | 2222 | 2609 | 0.014963
MONTICELLO 1101654 | MONTICELLO 1101 | NORTH BAY | 8.1004 | 46.4584 | 35.79% | 0 | 2 | 92.66% | 0% | 0 | 0.031073 | 1 | 1.8356 | 0.057038 | Medium | Medium | Low | 2223 | 2070 | 0.031073
PURISIMA 1101CB | PURISIMA 1101 | LOS PADRES | 3.8284 | 30.5658 | 4.848% | 1 | 0 | 83.25% | 0% | 0 | 0.014861 | 1 | 3.8367 | 0.057017 | Low | Low | High | 2224 | 2615 | 0.014861
HIGGINS 1110CB | HIGGINS 1110 | SIERRA | 11.6416 | 10 | 74.55% | 3 | 1 | 64.03% | 0% | 0 | 0.01732 | 1 | 3.2906 | 0.056995 | Low | Low | High | 2225 | 2517 | 0.01732
PUEBLO 21031970 | PUEBLO 2103 | NORTH BAY | 3.678 | 37.2305 | 48.19% | 3 | 0 | 44.65% | 0% | 0 | 0.017676 | 1 | 3.2222 | 0.056955 | Low | Low | High | 2226 | 2503 | 0.017676
DUNLAP 11037220 | DUNLAP 1103 | FRESNO | 24.8173 | 17.858 | 99.97% | 1 | 5 | 100% | 0% | 0 | 0.0383 | 1 | 1.4867 | 0.056942 | Medium | Medium | Low | 2227 | 1891 | 0.0383
PINE GROVE 110152088 | PINE GROVE 1101 | STOCKTON | 2.528 | 10 | 68.63% | 1 | 3 | 100% | 0% | 0 | 0.023865 | 1 | 2.3857 | 0.056935 | Medium | Medium | Medium | 2228 | 2282 | 0.023865
REDBUD 1102510 | REDBUD 1102 | HUMBOLDT | 6.0638 | 23.833 | 59.82% | 2 | 2 | 75.22% | 0% | 0 | 0.02163 | 1 | 2.6321 | 0.056933 | Low | Low | Medium | 2229 | 2348 | 0.02163
HALSEY 11012412 | HALSEY 1101 | SIERRA | 5.321 | 10 | 60.58% | 4 | 4 | 100% | 0% | 0 | 0.023732 | 1 | 2.3931 | 0.056792 | Medium | Medium | Medium | 2230 | 2287 | 0.023732
MORAGA 1103CB | MORAGA 1103 | DIABLO | 1.341 | 16.5323 | 0% | 6 | 3 | 21.01% | 11.54% | 0 | 0.01426 | 1 | 3.9729 | 0.056652 | Low | Low | High | 2231 | 2643 | 0.01426
COARSEGOLD 2103 | COARSEGOLD 2103 | YOSEMITE | 0.14838 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.9847 | 0.056588 | Medium | Medium | Low | 2232 | 2136 | 0.028512
OAKLAND K 1103CR422 | OAKLAND K 1103 | EAST BAY | 1.8547 | 10 | 4.055% | 0 | 3 | 90.41% | 0% | 0 | 0.0127 | 1 | 4.4523 | 0.056544 | Low | Low | High | 2233 | 2731 | 0.0127
POINT ARENA 11014923 | POINT ARENA 1101 | HUMBOLDT | 2.8662 | 57.1036 | 19.76% | 5 | 5 | 100% | 0% | 0 | 0.031366 | 1 | 1.8015 | 0.056505 | Medium | Medium | Low | 2234 | 2065 | 0.031366
NEWBURG 1133CB | NEWBURG 1133 | HUMBOLDT | 3.7712 | 37.8079 | 38.51% | 2 | 0 | 41.21% | 0% | 0 | 0.020349 | 1 | 2.7759 | 0.056485 | Low | Low | Medium | 2235 | 2391 | 0.020349
VALLEY VIEW 1106CB | VALLEY VIEW 1106 | EAST BAY | 3.4767 | 45.2583 | 0.9386% | 0 | 1 | 68.92% | 0% | 0 | 0.013903 | 1 | 4.0593 | 0.056436 | Low | Low | High | 2236 | 2667 | 0.013903
FRENCH GULCH 11011892 | FRENCH GULCH 1101 | NORTH VALLEY | 2.9079 | 75.8107 | 100% | 0 | 0 | 100% | 0% | 0 | 0.044011 | 1 | 1.2823 | 0.056435 | Medium | Medium | Low | 2237 | 1778 | 0.044011
SAN CARLOS 11049048 | SAN CARLOS 1104 | PENINSULA | 0.01529 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.4369 | 0.056328 | Low | Low | High | 2238 | 2735 | 0.012695
HARTLEY 1101698 | HARTLEY 1101 | HUMBOLDT | 6.3129 | 57.2881 | 69.42% | 1 | 7 | 61.15% | 0% | 0 | 0.027842 | 1 | 2.0226 | 0.056312 | Medium | Medium | Low | 2239 | 2166 | 0.027842
VACAVILLE 1104CB | VACAVILLE 1104 | SACRAMENTO | 0.88859 | 38.1521 | 69.79% | 0 | 1 | 28.2% | 0% | 0 | 0.017694 | 1 | 3.1813 | 0.056289 | Low | Low | High | 2240 | 2502 | 0.017694
OAKLAND K 1104468 | OAKLAND K 1104 | EAST BAY | 0.0028424 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.4321 | 0.056268 | Low | Low | High | 2241 | 2735 | 0.012695
FROGTOWN 170211212 | FROGTOWN 1702 | STOCKTON | 22.4074 | 27.4478 | 70.17% | 2 | 7 | 100% | 0% | 0 | 0.033949 | 1 | 1.6518 | 0.056076 | Medium | Medium | Low | 2242 | 1979 | 0.033949
PIT NO 1 110170952 | PIT NO 1 1101 | NORTH VALLEY | 1.5383 | 10 | 71.41% | 1 | 1 | 89.97% | 0% | 0 | 0.024193 | 1 | 2.3158 | 0.056027 | Medium | Medium | Medium | 2243 | 2272 | 0.024193
SAND CREEK 1103 | SAND CREEK 1103 | FRESNO | 0.037983 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.9649 | 0.056022 | Medium | Medium | Low | 2244 | 2136 | 0.028512
UKIAH 111129452 | UKIAH 1111 | HUMBOLDT | 3.6752 | 77.2683 | 100% | 0 | 0 | 30.05% | 0% | 0 | 0.022547 | 1 | 2.4814 | 0.055947 | Medium | Medium | Medium | 2245 | 2320 | 0.022547
ELK CREEK 110193504 | ELK CREEK 1101 | NORTH VALLEY | 2.2601 | 54.3949 | 100% | 0 | 0 | 90.07% | 0% | 0 | 0.034745 | 1 | 1.6101 | 0.055942 | Medium | Medium | Low | 2246 | 1956 | 0.034745
SO. CAL. EDISON #3 1101CB | SO. CAL. EDISON #3 1101 | FRESNO | 6.4255 | 72.2284 | 15.88% | 0 | 1 | 100% | 34.58% | 0 | 0.038701 | 1 | 1.4452 | 0.055932 | Medium | Medium | Low | 2247 | 1886 | 0.038701
FORT BRAGG A 11013100 | FORT BRAGG A 1101 | HUMBOLDT | 12.9058 | 10 | 7.343% | 8 | 11 | 88.01% | 0% | 0 | 0.021681 | 1 | 2.5776 | 0.055885 | Low | Low | Medium | 2248 | 2346 | 0.021681
SAN LEANDRO U 1114MR218 | SAN LEANDRO U 1114 | MISSION | 6.9334 | 10 | 55.46% | 3 | 0 | 61.53% | 0% | 0 | 0.01617 | 1 | 3.4495 | 0.055778 | Low | Low | High | 2249 | 2565 | 0.01617
LUCERNE 11062355 | LUCERNE 1106 | HUMBOLDT | 0.92313 | 10 | 100% | 1 | 0 | 88.59% | 0% | 0 | 0.02584 | 1 | 2.1572 | 0.055742 | Medium | Medium | Low | 2250 | 2220 | 0.02584
EL CERRITO G 1113CB | EL CERRITO G 1113 | EAST BAY | 0.20892 | 10 | 100% | 0 | 0 | 4.98% | 0% | 0 | 0.011198 | 1 | 4.968 | 0.055631 | Low | Low | High | 2251 | 2856 | 0.011198
HAMILTON BRANCH 11012436 | HAMILTON BRANCH 1101 | NORTH VALLEY | 1.2668 | 10 | 100% | 0 | 1 | 100% | 0% | 0 | 0.029099 | 1 | 1.9087 | 0.055542 | Medium | Medium | Low | 2252 | 2119 | 0.029099
RESERVATION ROAD 11023030 | RESERVATION ROAD 1102 | CENTRAL COAST | 4.2831 | 56.4796 | 100% | 0 | 1 | 16.48% | 0% | 0 | 0.038229 | 1 | 1.4511 | 0.055473 | Medium | Medium | Low | 2253 | 1894 | 0.038229
CORRAL 110213498 | CORRAL 1102 | STOCKTON | 0.99648 | 10 | 14.99% | 0 | 1 | 100% | 0% | 0 | 0.0167 | 1 | 3.3092 | 0.055263 | Low | Low | High | 2254 | 2541 | 0.0167
OLETA 11011208 | OLETA 1101 | STOCKTON | 32.4243 | 51.211 | 80.1% | 0 | 12 | 85.11% | 0% | 0 | 0.040132 | 1 | 1.3763 | 0.055235 | Medium | Medium | Low | 2255 | 1852 | 0.040132
CEDAR CREEK 11011608 | CEDAR CREEK 1101 | NORTH VALLEY | 33.3899 | 31.7775 | 100% | 3 | 12 | 100% | 36.09% | 1 | 0.10917 | 1 | 0.50558 | 0.055196 | High | High | Low | 2256 | 1263 | 0.10917
SISQUOC 1103M98 | SISQUOC 1103 | LOS PADRES | 6.4595 | 29.4274 | 100% | 0 | 1 | 65.51% | 60.21% | 1 | 0.060705 | 1 | 0.90853 | 0.055153 | Medium | Medium | Low | 2257 | 1560 | 0.060705
SUNOL 1101MR297 | SUNOL 1101 | MISSION | 6.0465 | 17.8817 | 28.91% | 0 | 2 | 100% | 17.46% | 0 | 0.023322 | 1 | 2.3616 | 0.055077 | Medium | Medium | Medium | 2258 | 2302 | 0.023322
BIG RIVER 1101CB | BIG RIVER 1101 | HUMBOLDT | 1.8594 | 10 | 0.4258% | 5 | 2 | 94.21% | 0% | 0 | 0.01527 | 1 | 3.6 | 0.054971 | Low | Low | High | 2259 | 2599 | 0.01527
MORRO BAY 110248384 | MORRO BAY 1102 | LOS PADRES | 0.22159 | 10 | 0% | 1 | 1 | 100% | 0% | 0 | 0.013132 | 1 | 4.1848 | 0.054953 | Low | Low | High | 2260 | 2709 | 0.013132
FORT BRAGG A 1102816 | FORT BRAGG A 1102 | HUMBOLDT | 2.5631 | 10 | 6.097% | 3 | 2 | 100% | 0% | 0 | 0.018806 | 1 | 2.916 | 0.054838 | Low | Low | Medium | 2261 | 2456 | 0.018806
MORRO BAY 110298906 | MORRO BAY 1102 | LOS PADRES | 0.034162 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.3164 | 0.054798 | Low | Low | High | 2262 | 2735 | 0.012695
ARCATA 11211206 | ARCATA 1121 | HUMBOLDT | 6.629 | 50.041 | 6.756% | 12 | 6 | 42.25% | 0% | 0 | 0.022231 | 1 | 2.4644 | 0.054786 | Medium | Medium | Medium | 2263 | 2323 | 0.022231
HOPLAND 110194006 | HOPLAND 1101 | HUMBOLDT | 13.3558 | 51.6995 | 99.02% | 0 | 1 | 84.05% | 0% | 0 | 0.032603 | 1 | 1.676 | 0.054643 | Medium | Medium | Low | 2264 | 2023 | 0.032603
BEAR VALLEY 21059480 | BEAR VALLEY 2105 | YOSEMITE | 12.4081 | 50.2702 | 94.93% | 2 | 0 | 100% | 0% | 0 | 0.041692 | 1 | 1.3091 | 0.054581 | Medium | Medium | Low | 2265 | 1823 | 0.041692
PETALUMA C 1108632 | PETALUMA C 1108 | SONOMA | 14.7325 | 83.7221 | 19.94% | 0 | 2 | 100% | 0% | 0 | 0.033063 | 1 | 1.6482 | 0.054496 | Medium | Medium | Low | 2266 | 2008 | 0.033063
OAKLAND J 1102CR184 | OAKLAND J 1102 | EAST BAY | 3.4622 | 10 | 2.127% | 3 | 2 | 100% | 0% | 0 | 0.01597 | 1 | 3.4089 | 0.054442 | Low | Low | High | 2267 | 2572 | 0.01597
FORT SEWARD 11211663 | FORT SEWARD 1121 | HUMBOLDT | 1.9431 | 10 | 100% | 1 | 4 | 100% | 0% | 0 | 0.03133 | 1 | 1.7358 | 0.054383 | Medium | Medium | Low | 2268 | 2066 | 0.03133
WISE 1101CB | WISE 1101 | SIERRA | 5.8467 | 15.7551 | 45.1% | 2 | 5 | 65.21% | 0% | 0 | 0.01999 | 1 | 2.7196 | 0.054364 | Low | Low | Medium | 2269 | 2408 | 0.01999
PHILO 110137222 | PHILO 1101 | HUMBOLDT | 25.4322 | 53.3862 | 64.87% | 9 | 12 | 100% | 0% | 0 | 0.060092 | 1 | 0.9025 | 0.054233 | Medium | Medium | Low | 2270 | 1564 | 0.060092
FROGTOWN 17028482 | FROGTOWN 1702 | STOCKTON | 14.6236 | 52.3445 | 57.04% | 0 | 2 | 100% | 0% | 0 | 0.027885 | 1 | 1.9388 | 0.054064 | Medium | Medium | Low | 2271 | 2165 | 0.027885
SAN CARLOS 110475210 | SAN CARLOS 1104 | PENINSULA | 0.38485 | 10 | 11.56% | 0 | 1 | 100% | 0% | 0 | 0.01424 | 1 | 3.7871 | 0.053927 | Low | Low | High | 2272 | 2648 | 0.01424
CRESCENT MILLS 21012562 | CRESCENT MILLS 2101 | NORTH VALLEY | 17.3839 | 76.7012 | 88.81% | 4 | 1 | 50.76% | 0% | 0 | 0.034993 | 1 | 1.5371 | 0.053789 | Medium | Medium | Low | 2273 | 1953 | 0.034993
MORRO BAY 110242062 | MORRO BAY 1102 | LOS PADRES | 0.13997 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.236 | 0.053777 | Low | Low | High | 2274 | 2735 | 0.012695
CASTRO VALLEY 1101MR204 | CASTRO VALLEY 1101 | MISSION | 2.1197 | 29.3697 | 13.12% | 0 | 1 | 73.48% | 0% | 0 | 0.012645 | 1 | 4.251 | 0.053753 | Low | Low | High | 2275 | 2769 | 0.012645
OTTER 1101440 | OTTER 1101 | CENTRAL COAST | 8.556 | 21.3917 | 0.8557% | 24 | 4 | 77.84% | 0% | 0 | 0.021414 | 1 | 2.508 | 0.053708 | Low | Low | Medium | 2276 | 2353 | 0.021414
ANTLER 1101CB | ANTLER 1101 | NORTH VALLEY | 1.601 | 30.2969 | 97.79% | 1 | 1 | 100% | 0% | 0 | 0.042837 | 1 | 1.2522 | 0.053641 | Medium | Medium | Low | 2277 | 1803 | 0.042837
WEIMAR 11012764 | WEIMAR 1101 | SIERRA | 6.0658 | 10 | 51% | 1 | 6 | 100% | 0% | 0 | 0.028566 | 1 | 1.8747 | 0.053554 | Medium | Medium | Low | 2278 | 2130 | 0.028566
LOS GATOS 1102CB | LOS GATOS 1102 | DE ANZA | 1.1034 | 10 | 59.61% | 1 | 4 | 18.46% | 0% | 0 | 0.013194 | 1 | 4.0562 | 0.053517 | Low | Low | High | 2279 | 2705 | 0.013194
GARBERVILLE 11011604 | GARBERVILLE 1101 | HUMBOLDT | 4.3333 | 50.687 | 100% | 0 | 3 | 25.13% | 0% | 0 | 0.024833 | 1 | 2.1532 | 0.053469 | Medium | Medium | Low | 2280 | 2249 | 0.024833
SARATOGA 1115LC20 | SARATOGA 1115 | DE ANZA | 2.7261 | 10 | 38.53% | 0 | 1 | 56.79% | 0% | 0 | 0.015057 | 1 | 3.5487 | 0.053432 | Low | Low | High | 2281 | 2605 | 0.015057
TEMPLETON 2113A08 | TEMPLETON 2113 | LOS PADRES | 9.9198 | 65.213 | 45.79% | 1 | 2 | 40.4% | 37.28% | 0 | 0.032324 | 1 | 1.6527 | 0.053421 | Medium | Medium | Low | 2282 | 2034 | 0.032324
LUCERNE 11034200 | LUCERNE 1103 | HUMBOLDT | 4.2514 | 45.4735 | 81.38% | 0 | 1 | 86.14% | 0% | 0 | 0.027721 | 1 | 1.9269 | 0.053416 | Medium | Medium | Low | 2283 | 2170 | 0.027721
REDBUD 1101400 | REDBUD 1101 | HUMBOLDT | 1.0177 | 10 | 44.91% | 0 | 5 | 100% | 0% | 0 | 0.020268 | 1 | 2.632 | 0.053346 | Low | Low | Medium | 2284 | 2396 | 0.020268
PEORIA 170169124 | PEORIA 1701 | YOSEMITE | 2.706 | 13.7023 | 100% | 0 | 2 | 100% | 0% | 0 | 0.039389 | 1 | 1.3543 | 0.053345 | Medium | Medium | Low | 2285 | 1874 | 0.039389
FORT BRAGG A 110195294 | FORT BRAGG A 1101 | HUMBOLDT | 25.9363 | 28.0829 | 8.119% | 33 | 16 | 99.05% | 0% | 0 | 0.053875 | 1 | 0.98845 | 0.053253 | Medium | Medium | Low | 2286 | 1639 | 0.053875
RIO DELL 11028852 | RIO DELL 1102 | HUMBOLDT | 3.7546 | 61.6723 | 39.96% | 1 | 3 | 79.33% | 0% | 0 | 0.021849 | 1 | 2.4325 | 0.053146 | Medium | Medium | Medium | 2287 | 2339 | 0.021849
NEWBURG 113190242 | NEWBURG 1131 | HUMBOLDT | 3.4074 | 35.576 | 50.59% | 5 | 2 | 78.12% | 0% | 0 | 0.020383 | 1 | 2.6054 | 0.053106 | Low | Low | Medium | 2288 | 2388 | 0.020383
VOLTA 110149742 | VOLTA 1101 | NORTH VALLEY | 3.4776 | 49.9174 | 84.98% | 0 | 1 | 100% | 0% | 0 | 0.038241 | 1 | 1.3857 | 0.05299 | Medium | Medium | Low | 2289 | 1893 | 0.038241
HIGGINS 111051794 | HIGGINS 1110 | SIERRA | 3.8902 | 22.6443 | 10.14% | 0 | 1 | 100% | 0% | 0 | 0.017481 | 1 | 3.0277 | 0.052927 | Low | Low | Medium | 2290 | 2513 | 0.017481
HIGGINS 11041006 | HIGGINS 1104 | SIERRA | 9.9734 | 10.2486 | 72.09% | 2 | 7 | 49.68% | 0% | 0 | 0.016495 | 1 | 3.2059 | 0.052881 | Low | Low | High | 2291 | 2552 | 0.016495
FORT BRAGG A 11013113 | FORT BRAGG A 1101 | HUMBOLDT | 10.0167 | 23.3659 | 35.03% | 10 | 7 | 100% | 0% | 0 | 0.031469 | 1 | 1.6795 | 0.052853 | Medium | Medium | Low | 2292 | 2062 | 0.031469
WEIMAR 1101 | WEIMAR 1101 | SIERRA | 0.067365 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.8525 | 0.052817 | Medium | Medium | Low | 2293 | 2136 | 0.028512
PHILO 1102928 | PHILO 1102 | HUMBOLDT | 13.0575 | 61.4578 | 77.17% | 8 | 4 | 85.6% | 0% | 0 | 0.058135 | 1 | 0.90846 | 0.052813 | Medium | Medium | Low | 2294 | 1592 | 0.058135
LOS GATOS 110160052 | LOS GATOS 1101 | DE ANZA | 1.8727 | 10 | 24.39% | 0 | 1 | 100% | 0% | 0 | 0.015806 | 1 | 3.3394 | 0.052781 | Low | Low | High | 2295 | 2583 | 0.015806
SHINGLE SPRINGS 210819622 | SHINGLE SPRINGS 2108 | SIERRA | 4.5627 | 12.9837 | 69.35% | 2 | 3 | 39.08% | 0% | 0 | 0.015541 | 1 | 3.3954 | 0.052766 | Low | Low | High | 2296 | 2590 | 0.015541
SAN RAFAEL 11042651 | SAN RAFAEL 1104 | NORTH BAY | 0.79099 | 10 | 0% | 1 | 1 | 96.62% | 0% | 0 | 0.0127 | 1 | 4.1495 | 0.0527 | Low | Low | High | 2297 | 2730 | 0.0127
PERRY 1101V72 | PERRY 1101 | LOS PADRES | 5.7537 | 10 | 2.358% | 4 | 2 | 65.46% | 0% | 0 | 0.013146 | 1 | 4.0035 | 0.052631 | Low | Low | High | 2298 | 2708 | 0.013146
HIGHLANDS 11034630 | HIGHLANDS 1103 | HUMBOLDT | 1.4567 | 24.8899 | 80.52% | 0 | 2 | 42.07% | 0% | 0 | 0.015892 | 1 | 3.3089 | 0.052584 | Low | Low | High | 2299 | 2578 | 0.015892
HOLLISTER 21044403 | HOLLISTER 2104 | CENTRAL COAST | 5.3706 | 82.3816 | 100% | 0 | 0 | 28.45% | 0% | 0 | 0.022969 | 1 | 2.2884 | 0.052563 | Medium | Medium | Medium | 2300 | 2308 | 0.022969
BIG RIVER 1101954 | BIG RIVER 1101 | HUMBOLDT | 7.7476 | 11.9193 | 13.02% | 4 | 10 | 95.19% | 0% | 0 | 0.020135 | 1 | 2.6074 | 0.0525 | Low | Low | Medium | 2301 | 2401 | 0.020135
EDENVALE 2107D80 | EDENVALE 2107 | SAN JOSE | 0.032033 | 71.8938 | 0% | 0 | 0 | 100% | 0% | 0 | 0.019259 | 1 | 2.7189 | 0.052363 | Low | Low | Medium | 2302 | 2431 | 0.019259
CLAY 11037124 | CLAY 1103 | STOCKTON | 8.9452 | 50.0578 | 97.24% | 0 | 1 | 27.91% | 0% | 0 | 0.020936 | 1 | 2.4969 | 0.052275 | Low | Low | Medium | 2303 | 2371 | 0.020936
SAN JOAQUIN #2 1103157026 | SAN JOAQUIN #2 1103 | YOSEMITE | 3.2012 | 10 | 100% | 2 | 9 | 100% | 0% | 0 | 0.039941 | 1 | 1.3059 | 0.052157 | Medium | Medium | Low | 2304 | 1858 | 0.039941
AUBURN 11028611 | AUBURN 1102 | SIERRA | 1.8383 | 10 | 16.6% | 1 | 2 | 100% | 0% | 0 | 0.017498 | 1 | 2.9798 | 0.05214 | Low | Low | Medium | 2305 | 2512 | 0.017498
CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 1101 | STOCKTON | 0.0029886 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.8278 | 0.052113 | Medium | Medium | Low | 2306 | 2136 | 0.028512
CALAVERAS CEMENT 110111236 | CALAVERAS CEMENT 1101 | STOCKTON | 20.1179 | 16.0826 | 47.9% | 0 | 4 | 100% | 0% | 0 | 0.027497 | 1 | 1.8952 | 0.052111 | Medium | Medium | Low | 2307 | 2176 | 0.027497
TASSAJARA 2104 | TASSAJARA 2104 | DIABLO | 0.070201 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.0947 | 0.051984 | Low | Low | High | 2308 | 2735 | 0.012695
POINT ARENA 110183354 | POINT ARENA 1101 | HUMBOLDT | 5.1346 | 37.1787 | 0% | 2 | 5 | 100% | 0% | 0 | 0.025688 | 1 | 2.0227 | 0.051961 | Medium | Medium | Low | 2309 | 2227 | 0.025688
DESCHUTES 11041370 | DESCHUTES 1104 | NORTH VALLEY | 12.2362 | 19.7367 | 98.52% | 1 | 1 | 55.17% | 0% | 0 | 0.022854 | 1 | 2.271 | 0.051901 | Medium | Medium | Medium | 2310 | 2310 | 0.022854
POSO MOUNTAIN 21012181 | POSO MOUNTAIN 2101 | KERN | 17.1051 | 10 | 29.81% | 0 | 0 | 71.06% | 0% | 0 | 0.023433 | 1 | 2.214 | 0.051879 | Medium | Medium | Low | 2311 | 2298 | 0.023433
SALT SPRINGS 21011232 | SALT SPRINGS 2101 | STOCKTON | 6.1779 | 10 | 100% | 4 | 2 | 68.77% | 0% | 0 | 0.064284 | 1 | 0.80663 | 0.051853 | High | High | Low | 2312 | 1523 | 0.064284
ALTO 112265474 | ALTO 1122 | NORTH BAY | 2.1481 | 10 | 21.89% | 2 | 1 | 58.84% | 6.137% | 0 | 0.013328 | 1 | 3.89 | 0.051845 | Low | Low | High | 2313 | 2697 | 0.013328
PERRY 1101W52 | PERRY 1101 | LOS PADRES | 2.9028 | 10 | 12.36% | 3 | 2 | 69.83% | 0% | 0 | 0.014698 | 1 | 3.5249 | 0.051807 | Low | Low | High | 2314 | 2627 | 0.014698
PENRYN 11072410 | PENRYN 1107 | SIERRA | 2.4145 | 10 | 87.13% | 0 | 1 | 32.14% | 0% | 0 | 0.015364 | 1 | 3.3713 | 0.051797 | Low | Low | High | 2315 | 2594 | 0.015364
TIDEWATER 210614072 | TIDEWATER 2106 | DIABLO | 3.6661 | 10 | 16.78% | 0 | 0 | 95.56% | 0% | 0 | 0.013929 | 1 | 3.718 | 0.051789 | Low | Low | High | 2316 | 2665 | 0.013929
PEORIA 170190090 | PEORIA 1701 | YOSEMITE | 29.5241 | 42.6688 | 45.08% | 1 | 8 | 98.45% | 0% | 0 | 0.050945 | 1 | 1.0149 | 0.051705 | Medium | Medium | Low | 2317 | 1673 | 0.050945
COARSEGOLD 2102CB | COARSEGOLD 2102 | YOSEMITE | 14.0621 | 38.5067 | 44.35% | 2 | 1 | 100% | 4.748% | 0 | 0.028352 | 1 | 1.8189 | 0.051569 | Medium | Medium | Low | 2318 | 2157 | 0.028352
PERRY 110185870 | PERRY 1101 | LOS PADRES | 13.2734 | 34.8685 | 24.59% | 0 | 0 | 72.93% | 0% | 0 | 0.018257 | 1 | 2.8229 | 0.051539 | Low | Low | Medium | 2319 | 2477 | 0.018257
PEORIA 170510580 | PEORIA 1705 | YOSEMITE | 6.4351 | 24.7232 | 93.54% | 1 | 4 | 54.9% | 0% | 0 | 0.021125 | 1 | 2.4388 | 0.051522 | Low | Low | Medium | 2320 | 2361 | 0.021125
WALDO 0402CB | WALDO 0402 | EAST BAY | 3.0716 | 10 | 16.14% | 2 | 4 | 59.8% | 0% | 0 | 0.010847 | 1 | 4.7456 | 0.051476 | Low | Low | High | 2321 | 2878 | 0.010847
PEORIA 170184318 | PEORIA 1701 | YOSEMITE | 9.9103 | 10 | 99.97% | 1 | 8 | 100% | 0% | 0 | 0.049883 | 1 | 1.0313 | 0.051441 | Medium | Medium | Low | 2322 | 1682 | 0.049883
MENDOCINO 110131322 | MENDOCINO 1101 | HUMBOLDT | 4.4175 | 35.3153 | 77.6% | 2 | 7 | 15.42% | 0% | 0 | 0.01894 | 1 | 2.7133 | 0.05139 | Low | Low | Medium | 2323 | 2452 | 0.01894
HOOPA 110137202 | HOOPA 1101 | HUMBOLDT | 23.7883 | 81.2571 | 100% | 8 | 3 | 82.1% | 0% | 0 | 0.045151 | 1 | 1.1358 | 0.051283 | Medium | Medium | Low | 2324 | 1763 | 0.045151
HOLLISTER 21064004 | HOLLISTER 2106 | CENTRAL COAST | 7.4093 | 64.8641 | 59.97% | 2 | 1 | 36.51% | 0% | 0 | 0.019101 | 1 | 2.6827 | 0.051242 | Low | Low | Medium | 2325 | 2439 | 0.019101
RACETRACK 17032553 | RACETRACK 1703 | YOSEMITE | 1.2971 | 10 | 100% | 0 | 1 | 52.29% | 0% | 0 | 0.018242 | 1 | 2.8066 | 0.051198 | Low | Low | Medium | 2326 | 2481 | 0.018242
SOLEDAD 21027048 | SOLEDAD 2102 | CENTRAL COAST | 16.945 | 59.8739 | 88.98% | 0 | 0 | 48.94% | 0% | 0 | 0.022097 | 1 | 2.316 | 0.051176 | Medium | Medium | Medium | 2327 | 2332 | 0.022097
UKIAH 1115CB | UKIAH 1115 | HUMBOLDT | 4.3061 | 10 | 64.92% | 0 | 1 | 67.93% | 0% | 0 | 0.018255 | 1 | 2.8014 | 0.051141 | Low | Low | Medium | 2328 | 2479 | 0.018255
PIT NO 1 11013312 | PIT NO 1 1101 | NORTH VALLEY | 7.449 | 11.3541 | 100% | 0 | 1 | 82.66% | 0% | 0 | 0.032143 | 1 | 1.5906 | 0.051127 | Medium | Medium | Low | 2329 | 2041 | 0.032143
CAL WATER 1102920714 | CAL WATER 1102 | KERN | 2.9688 | 76.5947 | 100% | 0 | 0 | 34.42% | 0% | 0 | 0.023426 | 1 | 2.1754 | 0.05096 | Medium | Medium | Low | 2330 | 2299 | 0.023426
BIG RIVER 11012183 | BIG RIVER 1101 | HUMBOLDT | 2.6396 | 37.6233 | 33.84% | 1 | 4 | 100% | 0% | 0 | 0.022133 | 1 | 2.3018 | 0.050945 | Medium | Medium | Medium | 2331 | 2330 | 0.022133
PURISIMA 1101Y80 | PURISIMA 1101 | LOS PADRES | 1.0399 | 27.8619 | 91.46% | 0 | 0 | 17.5% | 0% | 0 | 0.01334 | 1 | 3.819 | 0.050944 | Low | Low | High | 2332 | 2695 | 0.01334
COTATI 110361736 | COTATI 1103 | SONOMA | 9.9372 | 78.8786 | 12.09% | 0 | 11 | 59.74% | 0% | 0 | 0.02142 | 1 | 2.3776 | 0.050928 | Low | Low | Medium | 2333 | 2352 | 0.02142
MC KEE 1107XR010 | MC KEE 1107 | SAN JOSE | 2.6945 | 34.7956 | 81.62% | 0 | 0 | 19.75% | 0% | 0 | 0.013193 | 1 | 3.8599 | 0.050922 | Low | Low | High | 2334 | 2706 | 0.013193
SAN JUSTO 110136902 | SAN JUSTO 1101 | CENTRAL COAST | 12.1218 | 14.481 | 44.84% | 5 | 5 | 82.09% | 0% | 0 | 0.024262 | 1 | 2.0985 | 0.050914 | Medium | Medium | Low | 2335 | 2269 | 0.024262
LUCERNE 110693293 | LUCERNE 1106 | HUMBOLDT | 0.10086 | 10 | 100% | 0 | 0 | 83.34% | 0% | 0 | 0.024233 | 1 | 2.1005 | 0.050903 | Medium | Medium | Low | 2336 | 2271 | 0.024233
BERKELEY F 1105BR166 | BERKELEY F 1105 | EAST BAY | 0.038193 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 4.0059 | 0.050857 | Low | Low | High | 2337 | 2735 | 0.012695
ALTO 11201214 | ALTO 1120 | NORTH BAY | 2.1973 | 49.1379 | 3.101% | 3 | 5 | 48.69% | 0% | 0 | 0.017477 | 1 | 2.904 | 0.050753 | Low | Low | Medium | 2338 | 2514 | 0.017477
HALSEY 11025739 | HALSEY 1102 | SIERRA | 6.6683 | 10 | 67.05% | 2 | 3 | 100% | 0% | 0 | 0.027187 | 1 | 1.8652 | 0.050708 | Medium | Medium | Low | 2339 | 2188 | 0.027187
EL CERRITO G 1105BR164 | EL CERRITO G 1105 | EAST BAY | 0.056936 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.9936 | 0.0507 | Low | Low | High | 2340 | 2735 | 0.012695
ZACA 1101Y72 | ZACA 1101 | LOS PADRES | 6.264 | 51.6717 | 31.17% | 0 | 0 | 97.2% | 23.49% | 0 | 0.039557 | 1 | 1.2802 | 0.050641 | Medium | Medium | Low | 2341 | 1869 | 0.039557
FORT ROSS 1121CB | FORT ROSS 1121 | SONOMA | 13.6368 | 88.1189 | 22.5% | 13 | 2 | 100% | 0% | 0 | 0.036054 | 1 | 1.4046 | 0.050641 | Medium | Medium | Low | 2342 | 1931 | 0.036054
SAN RAMON 21077742 | SAN RAMON 2107 | MISSION | 0.0028424 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.9835 | 0.050572 | Low | Low | High | 2343 | 2735 | 0.012695
HOLLISTER 2102855412 | HOLLISTER 2102 | CENTRAL COAST | 25.5091 | 59.8315 | 42.36% | 0 | 0 | 81.28% | 0% | 0 | 0.020819 | 1 | 2.4248 | 0.050482 | Low | Low | Medium | 2344 | 2377 | 0.020819
DIAMOND SPRINGS 110699658 | DIAMOND SPRINGS 1106 | SIERRA | 5.0702 | 10 | 100% | 3 | 3 | 39.71% | 0% | 0 | 0.019909 | 1 | 2.5296 | 0.050364 | Low | Low | Medium | 2345 | 2413 | 0.019909
MARTELL 110368192 | MARTELL 1103 | STOCKTON | 2.6279 | 35.8454 | 65.85% | 0 | 2 | 40.93% | 0% | 0 | 0.017124 | 1 | 2.9408 | 0.05036 | Low | Low | Medium | 2346 | 2524 | 0.017124
CASTRO VALLEY 1101MR359 | CASTRO VALLEY 1101 | MISSION | 0.81851 | 10 | 96.11% | 0 | 0 | 9.323% | 0% | 0 | 0.011325 | 1 | 4.4348 | 0.050223 | Low | Low | High | 2347 | 2846 | 0.011325
DUNLAP 11027060 | DUNLAP 1102 | FRESNO | 17.8164 | 21.4268 | 100% | 3 | 11 | 100% | 0% | 0 | 0.045381 | 1 | 1.1057 | 0.050176 | Medium | Medium | Low | 2348 | 1757 | 0.045381
JOLON 11027068 | JOLON 1102 | CENTRAL COAST | 3.8301 | 72.2303 | 100% | 0 | 0 | 100% | 0% | 0 | 0.042992 | 1 | 1.1665 | 0.05015 | Medium | Medium | Low | 2349 | 1798 | 0.042992
TULUCAY 1101628 | TULUCAY 1101 | NORTH BAY | 4.4167 | 65.2777 | 26.9% | 0 | 1 | 50.38% | 0% | 0 | 0.014345 | 1 | 3.4912 | 0.050083 | Low | Low | High | 2350 | 2637 | 0.014345
FROGTOWN 170232556 | FROGTOWN 1702 | STOCKTON | 4.3373 | 25.6533 | 79.39% | 0 | 0 | 69.35% | 0% | 0 | 0.025794 | 1 | 1.9369 | 0.049959 | Medium | Medium | Low | 2351 | 2221 | 0.025794
LAURELES 11112028 | LAURELES 1111 | CENTRAL COAST | 8.3353 | 36.2004 | 23.71% | 6 | 1 | 95.28% | 0% | 0 | 0.019345 | 1 | 2.5818 | 0.049946 | Low | Low | Medium | 2352 | 2428 | 0.019345
PERRY 1101W26 | PERRY 1101 | LOS PADRES | 2.7324 | 25.8267 | 23.85% | 3 | 0 | 100% | 0% | 0 | 0.017829 | 1 | 2.8 | 0.049922 | Low | Low | Medium | 2353 | 2497 | 0.017829
HALF MOON BAY 11036018 | HALF MOON BAY 1103 | PENINSULA | 14.4915 | 43.0242 | 18.48% | 5 | 3 | 79.35% | 0% | 0 | 0.022185 | 1 | 2.2501 | 0.049917 | Medium | Medium | Medium | 2354 | 2328 | 0.022185
PALMER 1101M84 | PALMER 1101 | LOS PADRES | 19.4244 | 65.3938 | 31.64% | 0 | 6 | 79.33% | 0% | 0 | 0.042007 | 1 | 1.1845 | 0.049756 | Medium | Medium | Low | 2355 | 1818 | 0.042007
ROB ROY 21045304 | ROB ROY 2104 | CENTRAL COAST | 2.975 | 10 | 39.67% | 0 | 0 | 59.8% | 0% | 0 | 0.015337 | 1 | 3.2417 | 0.049718 | Low | Low | High | 2356 | 2595 | 0.015337
MARTELL 1101CB | MARTELL 1101 | STOCKTON | 6.3498 | 10 | 65.48% | 1 | 2 | 48.33% | 0% | 0 | 0.01783 | 1 | 2.7857 | 0.049671 | Low | Low | Medium | 2357 | 2496 | 0.01783
WYANDOTTE 110737472 | WYANDOTTE 1107 | NORTH VALLEY | 6.2847 | 13.7184 | 63.51% | 2 | 3 | 42.06% | 0% | 0 | 0.013447 | 1 | 3.6893 | 0.049612 | Low | Low | High | 2358 | 2687 | 0.013447
LLAGAS 2101XR586 | LLAGAS 2101 | SAN JOSE | 4.744 | 52.8351 | 95.8% | 0 | 1 | 35.43% | 0% | 0 | 0.019912 | 1 | 2.4913 | 0.049608 | Low | Low | Medium | 2359 | 2412 | 0.019912
ELK CREEK 11012212 | ELK CREEK 1101 | NORTH VALLEY | 10.0272 | 85.6358 | 100% | 0 | 1 | 29.79% | 0% | 0 | 0.02765 | 1 | 1.7915 | 0.049534 | Medium | Medium | Low | 2360 | 2172 | 0.02765
SUNOL 110148180 | SUNOL 1101 | MISSION | 0.015663 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.7365 | 0.049509 | Medium | Medium | Low | 2361 | 2136 | 0.028512
WYANDOTTE 11095607 | WYANDOTTE 1109 | NORTH VALLEY | 3.9588 | 10 | 93.75% | 0 | 0 | 59.06% | 0% | 0 | 0.018157 | 1 | 2.7246 | 0.049471 | Low | Low | Medium | 2362 | 2483 | 0.018157
POSO MOUNTAIN 2103CB | POSO MOUNTAIN 2103 | KERN | 2.3192 | 10 | 26.74% | 0 | 0 | 100% | 0% | 0 | 0.017995 | 1 | 2.7452 | 0.0494 | Low | Low | Medium | 2363 | 2488 | 0.017995
FRANKLIN 1104P146 | FRANKLIN 1104 | EAST BAY | 1.1753 | 10 | 98.96% | 0 | 2 | 31.88% | 0% | 0 | 0.015101 | 1 | 3.2686 | 0.049359 | Low | Low | High | 2364 | 2604 | 0.015101
ANDERSON 1101CB | ANDERSON 1101 | NORTH VALLEY | 1.7524 | 42.6703 | 99.35% | 0 | 2 | 19.42% | 0% | 0 | 0.016693 | 1 | 2.9503 | 0.049249 | Low | Low | Medium | 2365 | 2544 | 0.016693
LINCOLN 11012310 | LINCOLN 1101 | SIERRA | 10.0776 | 10 | 72.42% | 0 | 6 | 56.39% | 0% | 0 | 0.016835 | 1 | 2.9232 | 0.049213 | Low | Low | Medium | 2366 | 2535 | 0.016835
ELK CREEK 11012002 | ELK CREEK 1101 | NORTH VALLEY | 17.647 | 82.0427 | 100% | 0 | 0 | 58.67% | 0% | 0 | 0.045253 | 1 | 1.0865 | 0.049167 | Medium | Medium | Low | 2367 | 1760 | 0.045253
RALSTON 1102CB | RALSTON 1102 | PENINSULA | 1.0812 | 10 | 71.25% | 0 | 0 | 25.36% | 0% | 0 | 0.014111 | 1 | 3.4704 | 0.04897 | Low | Low | High | 2368 | 2657 | 0.014111
CALAVERAS CEMENT 1101CB | CALAVERAS CEMENT 1101 | STOCKTON | 11.1338 | 14.2948 | 43.85% | 0 | 4 | 60.61% | 0% | 0 | 0.02038 | 1 | 2.3984 | 0.048881 | Low | Low | Medium | 2369 | 2389 | 0.02038
GUALALA 1111498 | GUALALA 1111 | HUMBOLDT | 2.9971 | 32.4304 | 1.089% | 0 | 12 | 100% | 0% | 0 | 0.024787 | 1 | 1.9715 | 0.048867 | Medium | Medium | Low | 2370 | 2250 | 0.024787
ELECTRA 11024756 | ELECTRA 1102 | STOCKTON | 8.9008 | 26.6489 | 52.03% | 0 | 4 | 75.65% | 0% | 0 | 0.018513 | 1 | 2.637 | 0.048818 | Low | Low | Medium | 2371 | 2465 | 0.018513
JESSUP 11013383 | JESSUP 1101 | NORTH VALLEY | 1.283 | 10 | 88.48% | 0 | 0 | 68.06% | 0% | 0 | 0.021667 | 1 | 2.2493 | 0.048737 | Low | Low | Medium | 2372 | 2347 | 0.021667
ANTLER 11011378 | ANTLER 1101 | NORTH VALLEY | 23.3437 | 22.2502 | 87.11% | 6 | 14 | 92.94% | 12.19% | 1 | 0.058255 | 1 | 0.83529 | 0.04866 | Medium | Medium | Low | 2373 | 1591 | 0.058255
CABRILLO 1104CB | CABRILLO 1104 | LOS PADRES | 4.9085 | 16.6076 | 47.38% | 0 | 1 | 28.73% | 0% | 0 | 0.012822 | 1 | 3.7934 | 0.048641 | Low | Low | High | 2374 | 2723 | 0.012822
CLOVERDALE 1102262 | CLOVERDALE 1102 | SONOMA | 1.062 | 28.5735 | 25.58% | 2 | 0 | 19.75% | 47.85% | 0 | 0.020231 | 1 | 2.3861 | 0.048274 | Low | Low | Medium | 2375 | 2399 | 0.020231
HOLLYWOOD 0401CB | HOLLYWOOD 0401 | EAST BAY | 2.9599 | 10 | 0% | 0 | 1 | 55.84% | 0% | 0 | 0.010899 | 1 | 4.4177 | 0.048147 | Low | Low | High | 2376 | 2875 | 0.010899
DESCHUTES 11041582 | DESCHUTES 1104 | NORTH VALLEY | 6.3252 | 21.3729 | 99.66% | 0 | 1 | 41.84% | 0% | 0 | 0.020198 | 1 | 2.3806 | 0.048084 | Low | Low | Medium | 2377 | 2400 | 0.020198
GIRVAN 110280726 | GIRVAN 1102 | NORTH VALLEY | 5.9722 | 10 | 96.6% | 0 | 5 | 31.79% | 0% | 0 | 0.017957 | 1 | 2.6748 | 0.048032 | Low | Low | Medium | 2378 | 2491 | 0.017957
PANORAMA 11021632 | PANORAMA 1102 | NORTH VALLEY | 8.5492 | 81.3182 | 43.52% | 0 | 3 | 100% | 0% | 0 | 0.040056 | 1 | 1.1987 | 0.048014 | Medium | Medium | Low | 2379 | 1855 | 0.040056
SAN RAFAEL 1109CB | SAN RAFAEL 1109 | NORTH BAY | 0.026389 | 10 | 100% | 0 | 0 | 0.5374% | 0% | 0 | 0.013951 | 1 | 3.4403 | 0.047995 | Low | Low | High | 2380 | 2664 | 0.013951
PEORIA 17019250 | PEORIA 1701 | YOSEMITE | 8.3271 | 28.832 | 87.97% | 0 | 3 | 100% | 0% | 0 | 0.035488 | 1 | 1.35 | 0.047908 | Medium | Medium | Low | 2381 | 1945 | 0.035488
STAFFORD 1101CB | STAFFORD 1101 | NORTH BAY | 2.6576 | 10 | 64.37% | 5 | 3 | 21.89% | 0% | 0 | 0.016699 | 1 | 2.8654 | 0.047849 | Low | Low | Medium | 2382 | 2542 | 0.016699
HOPLAND 1101768 | HOPLAND 1101 | HUMBOLDT | 16.1128 | 49.9055 | 90.85% | 1 | 4 | 80.79% | 0% | 0 | 0.03582 | 1 | 1.3347 | 0.047808 | Medium | Medium | Low | 2383 | 1938 | 0.03582
HALSEY 11015731 | HALSEY 1101 | SIERRA | 3.1252 | 10 | 52.17% | 0 | 1 | 100% | 0% | 0 | 0.019797 | 1 | 2.4133 | 0.047777 | Low | Low | Medium | 2384 | 2421 | 0.019797
PEORIA 170413490 | PEORIA 1704 | YOSEMITE | 4.0441 | 23.9004 | 44.53% | 0 | 0 | 76.49% | 0% | 0 | 0.018107 | 1 | 2.6351 | 0.047714 | Low | Low | Medium | 2385 | 2484 | 0.018107
OAKLAND J 1105CR256 | OAKLAND J 1105 | EAST BAY | 1.5352 | 10 | 0.8551% | 1 | 0 | 83.22% | 0% | 0 | 0.014281 | 1 | 3.3396 | 0.047692 | Low | Low | High | 2386 | 2641 | 0.014281
CABRILLO 1103Y10 | CABRILLO 1103 | LOS PADRES | 4.0955 | 68.6545 | 11.89% | 0 | 1 | 43.98% | 0% | 0 | 0.012191 | 1 | 3.9107 | 0.047675 | Low | Low | High | 2387 | 2795 | 0.012191
STAFFORD 11011298 | STAFFORD 1101 | NORTH BAY | 2.4249 | 10 | 52.95% | 1 | 0 | 36.21% | 0% | 0 | 0.015641 | 1 | 3.0475 | 0.047666 | Low | Low | Medium | 2388 | 2587 | 0.015641
HICKS 2101XR162 | HICKS 2101 | SAN JOSE | 2.3563 | 22.9213 | 92.08% | 0 | 3 | 24.69% | 0% | 0 | 0.014813 | 1 | 3.2145 | 0.047617 | Low | Low | High | 2389 | 2616 | 0.014813
TASSAJARA 2103CB | TASSAJARA 2103 | DIABLO | 1.7119 | 10 | 14.73% | 0 | 4 | 9.614% | 35.07% | 0 | 0.011177 | 1 | 4.2565 | 0.047577 | Low | Low | High | 2390 | 2857 | 0.011177
REEDLEY 1104274990 | REEDLEY 1104 | FRESNO | 1.6643 | 56.3701 | 98.08% | 0 | 0 | 3.167% | 0% | 0 | 0.014809 | 1 | 3.2104 | 0.047544 | Low | Low | High | 2391 | 2617 | 0.014809
MARIPOSA 210197142 | MARIPOSA 2101 | YOSEMITE | 4.6012 | 28.8872 | 53.68% | 0 | 6 | 100% | 0% | 0 | 0.025194 | 1 | 1.8808 | 0.047384 | Medium | Medium | Low | 2392 | 2237 | 0.025194
GARBERVILLE 1103CB | GARBERVILLE 1103 | HUMBOLDT | 1.3711 | 26.7284 | 20.19% | 10 | 1 | 61.39% | 0% | 0 | 0.017309 | 1 | 2.7282 | 0.04722 | Low | Low | Medium | 2393 | 2518 | 0.017309
NOVATO 110455398 | NOVATO 1104 | NORTH BAY | 2.9149 | 74.0149 | 52.93% | 0 | 1 | 25.83% | 0% | 0 | 0.016828 | 1 | 2.8041 | 0.047187 | Low | Low | Medium | 2394 | 2536 | 0.016828
GUALALA 1112CB | GUALALA 1112 | HUMBOLDT | 2.0288 | 40.2405 | 4.36% | 2 | 4 | 94.33% | 0% | 0 | 0.028665 | 1 | 1.6458 | 0.047177 | Medium | Medium | Low | 2395 | 2128 | 0.028665
MONTICELLO 1101CB | MONTICELLO 1101 | NORTH BAY | 0.56293 | 10 | 41.7% | 0 | 0 | 100% | 0% | 0 | 0.020311 | 1 | 2.3219 | 0.047161 | Low | Low | Medium | 2396 | 2393 | 0.020311
SNEATH LANE 110796530 | SNEATH LANE 1107 | PENINSULA | 0.71298 | 10 | 94.87% | 0 | 0 | 32.23% | 0% | 0 | 0.014063 | 1 | 3.3534 | 0.047158 | Low | Low | High | 2397 | 2663 | 0.014063
OILFIELDS 1103N64 | OILFIELDS 1103 | CENTRAL COAST | 9.7922 | 31.0491 | 50.23% | 0 | 4 | 78.14% | 0% | 0 | 0.019257 | 1 | 2.4471 | 0.047124 | Low | Low | Medium | 2398 | 2432 | 0.019257
LAURELES 11122768 | LAURELES 1112 | CENTRAL COAST | 6.6363 | 20.652 | 26.91% | 3 | 3 | 82.17% | 0% | 0 | 0.023337 | 1 | 2.0172 | 0.047076 | Medium | Medium | Low | 2399 | 2301 | 0.023337
GREENBRAE 110388832 | GREENBRAE 1103 | NORTH BAY | 1.2167 | 10 | 6.453% | 0 | 0 | 88.72% | 0% | 0 | 0.011967 | 1 | 3.9315 | 0.047049 | Low | Low | High | 2400 | 2811 | 0.011967
FLINT 1102CB | FLINT 1102 | SIERRA | 0.092844 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.014483 | 1 | 3.2339 | 0.046837 | Low | Low | High | 2401 | 2630 | 0.014483
DIAMOND SPRINGS 1107CB | DIAMOND SPRINGS 1107 | SIERRA | 7.4424 | 10 | 84.55% | 2 | 3 | 62.03% | 0.42% | 0 | 0.019073 | 1 | 2.4518 | 0.046763 | Low | Low | Medium | 2402 | 2443 | 0.019073
EL CERRITO G 1112BR196 | EL CERRITO G 1112 | EAST BAY | 0.02286 | 10 | 100% | 0 | 0 | 0.6321% | 0% | 0 | 0.010725 | 1 | 4.3473 | 0.046627 | Low | Low | High | 2403 | 2892 | 0.010725
VIEJO 220255787 | VIEJO 2202 | CENTRAL COAST | 0.036656 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.6721 | 0.046619 | Low | Low | High | 2404 | 2735 | 0.012695
SARATOGA 110413314 | SARATOGA 1104 | DE ANZA | 1.7714 | 10 | 52.47% | 2 | 5 | 15.54% | 0% | 0 | 0.010963 | 1 | 4.2395 | 0.046476 | Low | Low | High | 2405 | 2869 | 0.010963
OAKLAND K 1101CR172 | OAKLAND K 1101 | EAST BAY | 0.63886 | 10 | 27.9% | 0 | 1 | 30.68% | 23.7% | 0 | 0.011998 | 1 | 3.8735 | 0.046474 | Low | Low | High | 2406 | 2808 | 0.011998
PLACERVILLE 11118582 | PLACERVILLE 1111 | SIERRA | 7.7771 | 10 | 58.12% | 5 | 4 | 64.88% | 0% | 0 | 0.016693 | 1 | 2.7827 | 0.046451 | Low | Low | Medium | 2407 | 2543 | 0.016693
LAURELES 1112438 | LAURELES 1112 | CENTRAL COAST | 5.2403 | 57.3236 | 0.9038% | 0 | 0 | 91.32% | 0% | 0 | 0.020992 | 1 | 2.2111 | 0.046416 | Low | Low | Low | 2408 | 2368 | 0.020992
ROB ROY 210512586 | ROB ROY 2105 | CENTRAL COAST | 3.2869 | 10 | 13.9% | 3 | 2 | 50.3% | 0% | 0 | 0.015967 | 1 | 2.9067 | 0.046412 | Low | Low | Medium | 2409 | 2574 | 0.015967
CLARK ROAD 110281296 | CLARK ROAD 1102 | NORTH VALLEY | 8.8512 | 53.0547 | 65.11% | 1 | 2 | 64.96% | 2.959% | 0 | 0.029241 | 1 | 1.5871 | 0.046408 | Medium | Medium | Low | 2410 | 2117 | 0.029241
FAIRVIEW 220799096 | FAIRVIEW 2207 | DIABLO | 9.9116 | 14.1017 | 19.38% | 0 | 2 | 100% | 0% | 0 | 0.015926 | 1 | 2.9135 | 0.046399 | Low | Low | Medium | 2411 | 2575 | 0.015926
CLAY 110184572 | CLAY 1101 | STOCKTON | 1.3752 | 10 | 53.62% | 0 | 0 | 60.97% | 0% | 0 | 0.013356 | 1 | 3.473 | 0.046384 | Low | Low | High | 2412 | 2693 | 0.013356
RIO DELL 11027124 | RIO DELL 1102 | HUMBOLDT | 0.67226 | 75.6649 | 100% | 0 | 0 | 100% | 0% | 0 | 0.043969 | 1 | 1.0549 | 0.046383 | Medium | Medium | Low | 2413 | 1779 | 0.043969
ELK 11018779 | ELK 1101 | HUMBOLDT | 4.2672 | 21.5207 | 21.57% | 6 | 10 | 100% | 0% | 0 | 0.032081 | 1 | 1.4446 | 0.046343 | Medium | Medium | Low | 2414 | 2044 | 0.032081
RALSTON 1101CB | RALSTON 1101 | PENINSULA | 5.2354 | 10 | 67.13% | 0 | 1 | 62.97% | 0% | 0 | 0.015521 | 1 | 2.985 | 0.04633 | Low | Low | Medium | 2415 | 2591 | 0.015521
FORT BRAGG A 11014698 | FORT BRAGG A 1101 | HUMBOLDT | 7.9299 | 10 | 15.57% | 8 | 8 | 100% | 0% | 0 | 0.018863 | 1 | 2.4544 | 0.046298 | Low | Low | Medium | 2416 | 2454 | 0.018863
CAMBRIA 1101V76 | CAMBRIA 1101 | LOS PADRES | 20.0895 | 13.7459 | 1.828% | 1 | 2 | 100% | 0% | 0 | 0.039572 | 1 | 1.1661 | 0.046144 | Medium | Medium | Low | 2417 | 1868 | 0.039572
LLAGAS 2104XR294 | LLAGAS 2104 | SAN JOSE | 1.6348 | 49.1137 | 100% | 0 | 0 | 15.4% | 0% | 0 | 0.016162 | 1 | 2.8487 | 0.046041 | Low | Low | Medium | 2418 | 2566 | 0.016162
KONOCTI 11081278 | KONOCTI 1108 | HUMBOLDT | 3.9864 | 24.8046 | 63% | 1 | 3 | 49.95% | 0% | 0 | 0.017559 | 1 | 2.6217 | 0.046036 | Low | Low | Medium | 2419 | 2508 | 0.017559
SAN CARLOS 110479774 | SAN CARLOS 1104 | PENINSULA | 0.48017 | 10 | 65.63% | 1 | 1 | 30.37% | 0% | 0 | 0.011253 | 1 | 4.0855 | 0.045976 | Low | Low | High | 2420 | 2850 | 0.011253
IGNACIO 1101CB | IGNACIO 1101 | NORTH BAY | 1.394 | 10 | 18.69% | 0 | 2 | 76.2% | 0% | 0 | 0.013891 | 1 | 3.3089 | 0.045965 | Low | Low | High | 2421 | 2668 | 0.013891
OAKLAND J 1105CR150 | OAKLAND J 1105 | EAST BAY | 0.4695 | 10 | 10.02% | 0 | 1 | 100% | 0% | 0 | 0.014063 | 1 | 3.265 | 0.045915 | Low | Low | High | 2422 | 2662 | 0.014063
AUBURN 1101CB | AUBURN 1101 | SIERRA | 3.1166 | 10 | 26.2% | 0 | 7 | 63.53% | 0% | 0 | 0.014449 | 1 | 3.1752 | 0.045877 | Low | Low | High | 2423 | 2632 | 0.014449
FRUITLAND 114195324 | FRUITLAND 1141 | HUMBOLDT | 9.0462 | 63.96 | 12.78% | 11 | 1 | 100% | 0% | 0 | 0.027146 | 1 | 1.6852 | 0.045746 | Medium | Medium | Low | 2424 | 2189 | 0.027146
FRENCH GULCH 1101CB | FRENCH GULCH 1101 | NORTH VALLEY | 2.2975 | 10 | 100% | 0 | 3 | 100% | 0% | 0 | 0.030308 | 1 | 1.5093 | 0.045746 | Medium | Medium | Low | 2425 | 2085 | 0.030308
FITCH MOUNTAIN 1113583202 | FITCH MOUNTAIN 1113 | SONOMA | 3.5047 | 64.5439 | 56.95% | 1 | 2 | 36.51% | 0% | 0 | 0.018742 | 1 | 2.4393 | 0.045717 | Low | Low | Medium | 2426 | 2460 | 0.018742
BIG MEADOWS 21012248 | BIG MEADOWS 2101 | NORTH VALLEY | 9.1467 | 42.3693 | 7.268% | 0 | 1 | 100% | 0% | 0 | 0.022222 | 1 | 2.056 | 0.045688 | Medium | Medium | Low | 2427 | 2324 | 0.022222
UPPER LAKE 11011276 | UPPER LAKE 1101 | HUMBOLDT | 12.9332 | 76.2596 | 54.71% | 3 | 4 | 100% | 0% | 0 | 0.039478 | 1 | 1.1564 | 0.045653 | Medium | Medium | Low | 2428 | 1873 | 0.039478
RED BLUFF 11041566 | RED BLUFF 1104 | NORTH VALLEY | 11.3669 | 45.5787 | 76.5% | 0 | 1 | 74.23% | 0% | 0 | 0.03504 | 1 | 1.3025 | 0.045641 | Medium | Medium | Low | 2429 | 1952 | 0.03504
CLARKSVILLE 210955666 | CLARKSVILLE 2109 | SIERRA | 0.61278 | 10 | 100% | 0 | 0 | 32.55% | 0% | 0 | 0.014709 | 1 | 3.1023 | 0.04563 | Low | Low | High | 2430 | 2626 | 0.014709
POSO MOUNTAIN 21013990 | POSO MOUNTAIN 2101 | KERN | 4.4819 | 10 | 34.01% | 0 | 1 | 80.62% | 0% | 0 | 0.0161 | 1 | 2.8327 | 0.045606 | Low | Low | Medium | 2431 | 2568 | 0.0161
CASTRO VALLEY 1106MR205 | CASTRO VALLEY 1106 | MISSION | 0.6704 | 10 | 69.55% | 0 | 0 | 12.34% | 11.35% | 0 | 0.01128 | 1 | 4.0306 | 0.045466 | Low | Low | High | 2432 | 2848 | 0.01128
WYANDOTTE 110213044 | WYANDOTTE 1102 | NORTH VALLEY | 3.9523 | 10 | 53.49% | 0 | 6 | 66.87% | 0% | 0 | 0.018256 | 1 | 2.4807 | 0.045288 | Low | Low | Medium | 2433 | 2478 | 0.018256
LLAGAS 2107XR188 | LLAGAS 2107 | SAN JOSE | 2.7329 | 20.244 | 46.06% | 0 | 0 | 43.36% | 5.395% | 0 | 0.014067 | 1 | 3.2148 | 0.045223 | Low | Low | High | 2434 | 2660 | 0.014067
UPPER LAKE 110175370 | UPPER LAKE 1101 | HUMBOLDT | 11.9492 | 35.1291 | 70.43% | 2 | 8 | 80.82% | 6.214% | 1 | 0.033449 | 1 | 1.3516 | 0.04521 | Medium | Medium | Low | 2435 | 1996 | 0.033449
WOODWARD 210878448 | WOODWARD 2108 | FRESNO | 18.5469 | 31.6388 | 94.91% | 1 | 5 | 62.76% | 0% | 0 | 0.028087 | 1 | 1.6079 | 0.045161 | Medium | Medium | Low | 2436 | 2161 | 0.028087
AUBERRY 1101R2579 | AUBERRY 1101 | FRESNO | 34.5067 | 14.4508 | 99.64% | 2 | 14 | 100% | 0% | 0 | 0.045338 | 1 | 0.99472 | 0.045098 | Medium | Medium | Low | 2437 | 1759 | 0.045338
AUBURN 1102 | AUBURN 1102 | SIERRA | 0.025464 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.014483 | 1 | 3.1021 | 0.044929 | Low | Low | High | 2438 | 2631 | 0.014483
MILPITAS 1109XR374 | MILPITAS 1109 | SAN JOSE | 0.65242 | 10 | 100% | 0 | 1 | 21.62% | 0% | 0 | 0.013479 | 1 | 3.3325 | 0.044919 | Low | Low | High | 2439 | 2683 | 0.013479
RALSTON 11029126 | RALSTON 1102 | PENINSULA | 0.049841 | 10 | 100% | 0 | 1 | 2.638% | 0% | 0 | 0.012746 | 1 | 3.5205 | 0.044873 | Low | Low | High | 2440 | 2728 | 0.012746
BIG MEADOWS 2101CB | BIG MEADOWS 2101 | NORTH VALLEY | 2.1059 | 66.4943 | 39.01% | 1 | 2 | 100% | 0% | 0 | 0.026855 | 1 | 1.6697 | 0.04484 | Medium | Medium | Low | 2441 | 2194 | 0.026855
GARBERVILLE 110237054 | GARBERVILLE 1102 | HUMBOLDT | 8.8244 | 78.2726 | 22.8% | 0 | 2 | 95.32% | 0% | 0 | 0.04584 | 1 | 0.97592 | 0.044736 | Medium | Medium | Low | 2442 | 1750 | 0.04584
MORRO BAY 110280174 | MORRO BAY 1102 | LOS PADRES | 3.4488 | 10 | 0% | 1 | 0 | 76.14% | 0% | 0 | 0.011588 | 1 | 3.8574 | 0.044702 | Low | Low | High | 2443 | 2831 | 0.011588
DUNBAR 1101234 | DUNBAR 1101 | SONOMA | 3.2653 | 13.7421 | 32.63% | 2 | 8 | 50.44% | 15.33% | 0 | 0.01612 | 1 | 2.7726 | 0.044694 | Low | Low | Medium | 2444 | 2567 | 0.01612
CLAY 110359714 | CLAY 1103 | STOCKTON | 4.4126 | 25.7757 | 4.31% | 0 | 1 | 95.22% | 0% | 0 | 0.014243 | 1 | 3.1342 | 0.044639 | Low | Low | High | 2445 | 2647 | 0.014243
OTTER 110298036 | OTTER 1102 | CENTRAL COAST | 9.353 | 32.3159 | 7.526% | 0 | 13 | 100% | 0% | 0 | 0.034494 | 1 | 1.2921 | 0.04457 | Medium | Medium | Low | 2446 | 1963 | 0.034494
VIEJO 220292792 | VIEJO 2202 | CENTRAL COAST | 0.01896 | 10 | 100% | 0 | 0 | 1.272% | 0% | 0 | 0.010794 | 1 | 4.1247 | 0.044521 | Low | Low | High | 2447 | 2883 | 0.010794
CURTIS 17019230 | CURTIS 1701 | YOSEMITE | 2.2694 | 10 | 15.95% | 1 | 2 | 72.76% | 0% | 0 | 0.013303 | 1 | 3.3462 | 0.044513 | Low | Low | High | 2448 | 2699 | 0.013303
MARIPOSA 2101CB | MARIPOSA 2101 | YOSEMITE | 6.8371 | 18.7213 | 60.25% | 1 | 4 | 63.95% | 0% | 0 | 0.019315 | 1 | 2.3032 | 0.044486 | Low | Low | Medium | 2449 | 2429 | 0.019315
WHITMORE 1101002 | WHITMORE 1101 | NORTH VALLEY | 0.0042201 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.5578 | 0.044415 | Medium | Medium | Low | 2450 | 2136 | 0.028512
COTATI 1102462 | COTATI 1102 | SONOMA | 3.3153 | 11.8938 | 22% | 1 | 2 | 84.56% | 0% | 0 | 0.015902 | 1 | 2.7902 | 0.044371 | Low | Low | Medium | 2451 | 2577 | 0.015902
SAN MIGUEL 1104N60 | SAN MIGUEL 1104 | LOS PADRES | 7.3672 | 40.8154 | 100% | 0 | 1 | 83.22% | 0% | 0 | 0.030327 | 1 | 1.4627 | 0.044359 | Medium | Medium | Low | 2452 | 2083 | 0.030327
HUMBOLDT BAY 11024724 | HUMBOLDT BAY 1102 | HUMBOLDT | 7.0458 | 41.454 | 0.8967% | 10 | 0 | 45.74% | 0% | 0 | 0.012021 | 1 | 3.6836 | 0.044279 | Low | Low | High | 2453 | 2807 | 0.012021
ROSSMOOR 11018132 | ROSSMOOR 1101 | DIABLO | 2.3517 | 13.1594 | 38.14% | 0 | 7 | 64.04% | 0% | 0 | 0.014331 | 1 | 3.0841 | 0.044197 | Low | Low | High | 2454 | 2638 | 0.014331
VINEYARD 2110CB | VINEYARD 2110 | MISSION | 5.8656 | 49.5436 | 17.49% | 1 | 0 | 52.96% | 0% | 0 | 0.013877 | 1 | 3.1806 | 0.044138 | Low | Low | High | 2455 | 2670 | 0.013877
BELMONT 11038958 | BELMONT 1103 | PENINSULA | 0.46477 | 10 | 49.35% | 0 | 4 | 26.9% | 0% | 0 | 0.011413 | 1 | 3.8671 | 0.044135 | Low | Low | High | 2456 | 2842 | 0.011413
LAS AROMAS 04013342 | LAS AROMAS 0401 | DIABLO | 2.2911 | 10 | 3.001% | 3 | 0 | 100% | 0% | 0 | 0.013529 | 1 | 3.2617 | 0.044129 | Low | Low | High | 2457 | 2680 | 0.013529
WYANDOTTE 11102590 | WYANDOTTE 1110 | NORTH VALLEY | 0.10676 | 10 | 95.21% | 0 | 0 | 17.59% | 0% | 0 | 0.012201 | 1 | 3.6162 | 0.044121 | Low | Low | High | 2458 | 2794 | 0.012201
OAKLAND X 1101CR224 | OAKLAND X 1101 | EAST BAY | 0.53647 | 10 | 23.35% | 2 | 2 | 46.33% | 0% | 0 | 0.0096559 | 1 | 4.5636 | 0.044066 | Low | Low | High | 2459 | 2944 | 0.0096559
SHINGLE SPRINGS 1104CB | SHINGLE SPRINGS 1104 | SIERRA | 0.43321 | 10 | 56.49% | 2 | 0 | 18.41% | 23.01% | 0 | 0.013336 | 1 | 3.3035 | 0.044055 | Low | Low | High | 2460 | 2696 | 0.013336
FITCH MOUNTAIN 1113352 | FITCH MOUNTAIN 1113 | SONOMA | 7.3048 | 34.6273 | 40.22% | 1 | 0 | 61.07% | 0% | 0 | 0.016355 | 1 | 2.6925 | 0.044035 | Low | Low | Medium | 2461 | 2557 | 0.016355
KERCKHOFF 1101R308 | KERCKHOFF 1101 | YOSEMITE | 3.8623 | 40.5798 | 35.11% | 0 | 3 | 100% | 0% | 0 | 0.022056 | 1 | 1.9946 | 0.043992 | Medium | Medium | Low | 2462 | 2334 | 0.022056
TYLER 11051704 | TYLER 1105 | NORTH VALLEY | 12.5832 | 29.6218 | 100% | 0 | 8 | 27.35% | 0% | 0 | 0.024427 | 1 | 1.7997 | 0.043962 | Medium | Medium | Low | 2463 | 2264 | 0.024427
OLETA 11021228 | OLETA 1102 | STOCKTON | 8.954 | 36.1723 | 96.93% | 0 | 0 | 20.75% | 0% | 0 | 0.019803 | 1 | 2.2184 | 0.043932 | Low | Low | Low | 2464 | 2419 | 0.019803
ALHAMBRA 110581514 | ALHAMBRA 1105 | DIABLO | 2.5203 | 17.3445 | 21.67% | 2 | 3 | 52.7% | 0% | 0 | 0.014173 | 1 | 3.0995 | 0.043928 | Low | Low | High | 2465 | 2654 | 0.014173
APPLE HILL 210289934 | APPLE HILL 2102 | SIERRA | 5.6225 | 10 | 91.39% | 0 | 0 | 100% | 0% | 0 | 0.030296 | 1 | 1.4475 | 0.043854 | Medium | Medium | Low | 2466 | 2087 | 0.030296
EL CERRITO G 1110CB | EL CERRITO G 1110 | EAST BAY | 1.4466 | 10 | 13.89% | 0 | 3 | 52.88% | 0% | 0 | 0.0094866 | 1 | 4.6174 | 0.043803 | Low | Low | High | 2467 | 2952 | 0.0094866
HIGGINS 1107CB | HIGGINS 1107 | SIERRA | 4.6439 | 10 | 81.31% | 3 | 3 | 24.48% | 0% | 0 | 0.012908 | 1 | 3.3796 | 0.043625 | Low | Low | High | 2468 | 2718 | 0.012908
BASALT 11065030 | BASALT 1106 | NORTH BAY | 3.3103 | 53.7565 | 71.04% | 0 | 0 | 20.61% | 0% | 0 | 0.013874 | 1 | 3.1305 | 0.043433 | Low | Low | High | 2469 | 2671 | 0.013874
DEL MONTE 21049096 | DEL MONTE 2104 | CENTRAL COAST | 2.1074 | 10 | 10.71% | 2 | 5 | 31.81% | 0% | 0 | 0.011931 | 1 | 3.6328 | 0.043344 | Low | Low | High | 2470 | 2813 | 0.011931
EDES 1112CR306 | EDES 1112 | EAST BAY | 1.0069 | 10 | 0% | 3 | 0 | 100% | 0% | 0 | 0.013203 | 1 | 3.2812 | 0.043321 | Low | Low | High | 2471 | 2704 | 0.013203
LOS OSITOS 21037468 | LOS OSITOS 2103 | CENTRAL COAST | 1.0746 | 71.3986 | 100% | 0 | 0 | 13.23% | 0% | 0 | 0.018377 | 1 | 2.3508 | 0.043201 | Low | Low | Medium | 2472 | 2472 | 0.018377
CALPELLA 1101CB | CALPELLA 1101 | HUMBOLDT | 10.9748 | 13.9128 | 62.49% | 0 | 11 | 53.93% | 0% | 0 | 0.025545 | 1 | 1.6899 | 0.043167 | Medium | Medium | Low | 2473 | 2229 | 0.025545
SAN LEANDRO U 1109CR284 | SAN LEANDRO U 1109 | MISSION | 0.93355 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.3989 | 0.043151 | Low | Low | High | 2474 | 2735 | 0.012695
VALLEY VIEW 1105CB | VALLEY VIEW 1105 | EAST BAY | 0.87089 | 10 | 56.45% | 0 | 0 | 18.73% | 0% | 0 | 0.0089925 | 1 | 4.7951 | 0.04312 | Low | Low | High | 2475 | 2976 | 0.0089925
BIG MEADOWS 21012016 | BIG MEADOWS 2101 | NORTH VALLEY | 0.0028416 | 10 | 100% | 0 | 0 | 0.06646% | 0% | 0 | 0.010666 | 1 | 4.0333 | 0.043017 | Low | Low | High | 2476 | 2897 | 0.010666
FROGTOWN 1701CB | FROGTOWN 1701 | STOCKTON | 9.8066 | 35.2796 | 29.68% | 0 | 4 | 86.99% | 0% | 0 | 0.018301 | 1 | 2.3489 | 0.042988 | Low | Low | Medium | 2477 | 2475 | 0.018301
CAROLANDS 0404 | CAROLANDS 0404 | PENINSULA | 0.066741 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.3793 | 0.042901 | Low | Low | High | 2478 | 2732 | 0.012695
FRUITLAND 114137410 | FRUITLAND 1141 | HUMBOLDT | 3.8197 | 75.1023 | 57.88% | 10 | 0 | 69.23% | 0% | 0 | 0.034236 | 1 | 1.2527 | 0.042886 | Medium | Medium | Low | 2479 | 1967 | 0.034236
SNEATH LANE 11071277 | SNEATH LANE 1107 | PENINSULA | 0.25243 | 10 | 100% | 0 | 1 | 11.7% | 0% | 0 | 0.012219 | 1 | 3.504 | 0.042815 | Low | Low | High | 2480 | 2792 | 0.012219
PEORIA 1704CB | PEORIA 1704 | YOSEMITE | 8.3627 | 39.95 | 39.21% | 0 | 3 | 93.61% | 0% | 0 | 0.021324 | 1 | 2.0061 | 0.042779 | Low | Low | Low | 2481 | 2356 | 0.021324
BELL 1108CB | BELL 1108 | SIERRA | 4.1507 | 10 | 64.56% | 0 | 6 | 33.13% | 0% | 0 | 0.016334 | 1 | 2.6182 | 0.042766 | Low | Low | Medium | 2482 | 2558 | 0.016334
WHITMORE 1101CB | WHITMORE 1101 | NORTH VALLEY | 5.8976 | 20.259 | 68.5% | 1 | 0 | 100% | 0% | 0 | 0.027347 | 1 | 1.5637 | 0.042762 | Medium | Medium | Low | 2483 | 2183 | 0.027347
UKIAH 1114822 | UKIAH 1114 | HUMBOLDT | 1.3145 | 67.0871 | 100% | 0 | 3 | 9.397% | 0% | 0 | 0.018289 | 1 | 2.3374 | 0.042749 | Low | Low | Medium | 2484 | 2476 | 0.018289
WILLITS 110434006 | WILLITS 1104 | HUMBOLDT | 3.7731 | 21.9583 | 31.14% | 0 | 7 | 66.96% | 0% | 0 | 0.016864 | 1 | 2.5304 | 0.042672 | Low | Low | Medium | 2485 | 2533 | 0.016864
CASTRO VALLEY 1108MR341 | CASTRO VALLEY 1108 | MISSION | 2.4534 | 10 | 13.13% | 0 | 1 | 77.41% | 2.031% | 0 | 0.011918 | 1 | 3.5792 | 0.042656 | Low | Low | High | 2486 | 2814 | 0.011918
WYANDOTTE 110313018 | WYANDOTTE 1103 | NORTH VALLEY | 0.12548 | 10 | 100% | 0 | 0 | 7.599% | 0% | 0 | 0.011492 | 1 | 3.697 | 0.042487 | Low | Low | High | 2487 | 2835 | 0.011492
SWIFT 2109XR300 | SWIFT 2109 | SAN JOSE | 0.30955 | 10 | 37.52% | 0 | 0 | 37.32% | 0% | 0 | 0.0092647 | 1 | 4.5685 | 0.042326 | Low | Low | High | 2488 | 2967 | 0.0092647
HARRIS 11082062 | HARRIS 1108 | HUMBOLDT | 2.3961 | 14.4145 | 20.24% | 1 | 5 | 45.88% | 0% | 0 | 0.010144 | 1 | 4.1719 | 0.042318 | Low | Low | High | 2489 | 2922 | 0.010144
VIEJO 2204CB | VIEJO 2204 | CENTRAL COAST | 2.2166 | 10 | 31.01% | 10 | 1 | 54.6% | 0% | 0 | 0.013845 | 1 | 3.0559 | 0.04231 | Low | Low | Medium | 2490 | 2673 | 0.013845
PANOCHE 11034008 | PANOCHE 1103 | YOSEMITE | 35.3708 | 69.547 | 99.82% | 0 | 2 | 100% | 0% | 0 | 0.064167 | 1 | 0.65772 | 0.042204 | High | High | Low | 2491 | 1524 | 0.064167
JAMESON 11059472 | JAMESON 1105 | SACRAMENTO | 2.8377 | 36.7552 | 61.91% | 0 | 2 | 38.64% | 0% | 0 | 0.016315 | 1 | 2.585 | 0.042175 | Low | Low | Medium | 2492 | 2559 | 0.016315
HATTON 1102CB | HATTON 1102 | CENTRAL COAST | 2.1206 | 10 | 0.1341% | 1 | 3 | 45.47% | 0% | 0 | 0.013538 | 1 | 3.1114 | 0.042121 | Low | Low | High | 2493 | 2679 | 0.013538
MESA 1103M68 | MESA 1103 | LOS PADRES | 0.22844 | 10 | 100% | 0 | 0 | 7.509% | 0% | 0 | 0.013101 | 1 | 3.2134 | 0.042099 | Low | Low | High | 2494 | 2712 | 0.013101
CURTIS 170349746 | CURTIS 1703 | YOSEMITE | 0.37395 | 10 | 15.4% | 0 | 1 | 100% | 0% | 0 | 0.014691 | 1 | 2.8626 | 0.042055 | Low | Low | Medium | 2495 | 2628 | 0.014691
FRENCH GULCH 11012905 | FRENCH GULCH 1101 | NORTH VALLEY | 9.7071 | 49.4271 | 100% | 1 | 0 | 100% | 0% | 0 | 0.037487 | 1 | 1.1218 | 0.042053 | Medium | Medium | Low | 2496 | 1905 | 0.037487
BELL 110880680 | BELL 1108 | SIERRA | 1.2687 | 10 | 46.62% | 0 | 0 | 71.23% | 0% | 0 | 0.015926 | 1 | 2.6403 | 0.042048 | Low | Low | Medium | 2497 | 2576 | 0.015926
MARTELL 110299214 | MARTELL 1102 | STOCKTON | 0.5909 | 10 | 69.1% | 1 | 4 | 29.13% | 0% | 0 | 0.013885 | 1 | 3.016 | 0.041876 | Low | Low | Medium | 2498 | 2669 | 0.013885
WYANDOTTE 1105CB | WYANDOTTE 1105 | NORTH VALLEY | 12.987 | 37.2024 | 0% | 0 | 0 | 96.35% | 0.5289% | 1 | 0.016922 | 1 | 2.4689 | 0.041778 | Low | Low | Medium | 2499 | 2531 | 0.016922
FRENCH GULCH 11022902 | FRENCH GULCH 1102 | NORTH VALLEY | 6.9875 | 84.5854 | 100% | 0 | 4 | 100% | 0% | 0 | 0.057283 | 1 | 0.72881 | 0.041748 | Medium | Medium | Low | 2500 | 1602 | 0.057283
PERRY 1101W10 | PERRY 1101 | LOS PADRES | 1.7167 | 22.2223 | 1.272% | 0 | 2 | 91.87% | 0% | 0 | 0.013398 | 1 | 3.1157 | 0.041744 | Low | Low | High | 2501 | 2690 | 0.013398
FORT ROSS 112137326 | FORT ROSS 1121 | SONOMA | 5.1708 | 13.0882 | 4.203% | 4 | 1 | 100% | 0% | 0 | 0.031597 | 1 | 1.3203 | 0.04172 | Medium | Medium | Low | 2502 | 2058 | 0.031597
MORRO BAY 1101 | MORRO BAY 1101 | LOS PADRES | 0.0056924 | 70 | 100% | 0 | 0 | 9.555% | 0% | 0 | 0.017559 | 1 | 2.3749 | 0.041701 | Low | Low | Medium | 2503 | 2509 | 0.017559
CAYETANO 2111CB | CAYETANO 2111 | MISSION | 5.2576 | 70.3707 | 27.25% | 0 | 1 | 45% | 0% | 0 | 0.014119 | 1 | 2.9536 | 0.041701 | Low | Low | Medium | 2504 | 2656 | 0.014119
EDES 1112CR100 | EDES 1112 | EAST BAY | 3.3566 | 10 | 0% | 1 | 0 | 100% | 0% | 0 | 0.012862 | 1 | 3.2337 | 0.041593 | Low | Low | High | 2505 | 2721 | 0.012862
HALF MOON BAY 11039112 | HALF MOON BAY 1103 | PENINSULA | 3.4704 | 36.5949 | 39.16% | 3 | 0 | 43.21% | 0% | 0 | 0.012394 | 1 | 3.3557 | 0.041589 | Low | Low | High | 2506 | 2777 | 0.012394
DOLAN ROAD 11013012 | DOLAN ROAD 1101 | CENTRAL COAST | 2.5496 | 10 | 65.12% | 1 | 1 | 12.08% | 0% | 0 | 0.010669 | 1 | 3.8845 | 0.041444 | Low | Low | High | 2507 | 2896 | 0.010669
LAYTONVILLE 11022502 | LAYTONVILLE 1102 | HUMBOLDT | 17.8026 | 72.9803 | 99.59% | 0 | 9 | 100% | 0% | 0 | 0.051556 | 1 | 0.80349 | 0.041424 | Medium | Medium | Low | 2508 | 1666 | 0.051556
PUTAH CREEK 11028352 | PUTAH CREEK 1102 | SACRAMENTO | 4.7179 | 43.9192 | 97.12% | 0 | 4 | 40.06% | 0% | 0 | 0.021102 | 1 | 1.961 | 0.041381 | Low | Low | Low | 2509 | 2363 | 0.021102
OTTER 110263868 | OTTER 1102 | CENTRAL COAST | 15.8742 | 30.1739 | 15.67% | 12 | 5 | 100% | 0% | 0 | 0.031617 | 1 | 1.3086 | 0.041374 | Medium | Medium | Low | 2510 | 2057 | 0.031617
OLEMA 110175686 | OLEMA 1101 | NORTH BAY | 3.5949 | 80.3245 | 25.14% | 0 | 0 | 69.82% | 0% | 0 | 0.021165 | 1 | 1.9507 | 0.041286 | Low | Low | Low | 2511 | 2359 | 0.021165
KONOCTI 1102CB | KONOCTI 1102 | HUMBOLDT | 6.3926 | 38.5127 | 58.33% | 0 | 0 | 42.97% | 1.842% | 0 | 0.01654 | 1 | 2.4961 | 0.041284 | Low | Low | Medium | 2512 | 2548 | 0.01654
RACETRACK 170310850 | RACETRACK 1703 | YOSEMITE | 0.060314 | 10 | 0% | 0 | 0 | 95.5% | 0% | 0 | 0.012143 | 1 | 3.3993 | 0.041276 | Low | Low | High | 2513 | 2798 | 0.012143
POINT ARENA 1101CB | POINT ARENA 1101 | HUMBOLDT | 2.4683 | 40.0153 | 0% | 3 | 1 | 100% | 0% | 0 | 0.016501 | 1 | 2.4898 | 0.041084 | Low | Low | Medium | 2514 | 2551 | 0.016501
LAS GALLINAS A 1105904 | LAS GALLINAS A 1105 | NORTH BAY | 2.5108 | 10 | 36.59% | 0 | 1 | 34.95% | 0% | 0 | 0.010466 | 1 | 3.9244 | 0.041073 | Low | Low | High | 2515 | 2906 | 0.010466
LUCERNE 110647198 | LUCERNE 1106 | HUMBOLDT | 3.6836 | 20.6629 | 59.47% | 1 | 7 | 65.28% | 0% | 0 | 0.018382 | 1 | 2.2339 | 0.041063 | Low | Low | Medium | 2516 | 2471 | 0.018382
SAN RAFAEL 1106910 | SAN RAFAEL 1106 | NORTH BAY | 1.5306 | 10 | 41.18% | 0 | 1 | 20.8% | 0% | 0 | 0.010777 | 1 | 3.8096 | 0.041054 | Low | Low | High | 2517 | 2885 | 0.010777
MESA 1101M86 | MESA 1101 | LOS PADRES | 10.0922 | 14.4649 | 78% | 0 | 7 | 48.4% | 0% | 0 | 0.019529 | 1 | 2.0981 | 0.040973 | Low | Low | Low | 2518 | 2424 | 0.019529
CALPELLA 1101 | CALPELLA 1101 | HUMBOLDT | 0.0052324 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.4352 | 0.040921 | Medium | Medium | Low | 2519 | 2136 | 0.028512
HATTON 110137088 | HATTON 1101 | CENTRAL COAST | 4.1243 | 13.8122 | 55.58% | 4 | 4 | 48.38% | 0% | 0 | 0.014072 | 1 | 2.9011 | 0.040823 | Low | Low | Medium | 2520 | 2659 | 0.014072
TOCALOMA 0241CB | TOCALOMA 0241 | NORTH BAY | 0.031239 | 60 | 0% | 0 | 0 | 100% | 0% | 0 | 0.017781 | 1 | 2.2908 | 0.040732 | Low | Low | Medium | 2521 | 2499 | 0.017781
POINT MORETTI 1101CB | POINT MORETTI 1101 | CENTRAL COAST | 0.028582 | 13.6525 | 6.641% | 0 | 0 | 100% | 6.641% | 0 | 0.015281 | 1 | 2.6605 | 0.040655 | Low | Low | Medium | 2522 | 2598 | 0.015281
ROB ROY 210512474 | ROB ROY 2105 | CENTRAL COAST | 2.374 | 10 | 59.61% | 0 | 1 | 28.06% | 0% | 0 | 0.013458 | 1 | 3.02 | 0.040644 | Low | Low | Medium | 2523 | 2685 | 0.013458
PEORIA 17046090 | PEORIA 1704 | YOSEMITE | 0.79834 | 10 | 4.922% | 0 | 1 | 100% | 0% | 0 | 0.01755 | 1 | 2.3134 | 0.0406 | Low | Low | Medium | 2524 | 2510 | 0.01755
SAN LEANDRO U 1107MR560 | SAN LEANDRO U 1107 | MISSION | 0.061986 | 10 | 100% | 0 | 0 | 0.7828% | 0% | 0 | 0.010742 | 1 | 3.7725 | 0.040522 | Low | Low | High | 2525 | 2888 | 0.010742
HIGGINS 1108CB | HIGGINS 1108 | SIERRA | 0.020411 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.189 | 0.040485 | Low | Low | High | 2526 | 2766 | 0.012695
REDBUD 110244119 | REDBUD 1102 | HUMBOLDT | 0.66752 | 10 | 86.82% | 0 | 0 | 23.81% | 0% | 0 | 0.012119 | 1 | 3.3402 | 0.040479 | Low | Low | High | 2527 | 2801 | 0.012119
SPENCE 11223078 | SPENCE 1122 | CENTRAL COAST | 9.9861 | 56.9194 | 40.99% | 1 | 2 | 62.29% | 0% | 0 | 0.0298 | 1 | 1.3582 | 0.040476 | Medium | Medium | Low | 2528 | 2104 | 0.0298
BAY MEADOWS 2102 | BAY MEADOWS 2102 | PENINSULA | 0.027395 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.1881 | 0.040474 | Low | Low | High | 2529 | 2735 | 0.012695
CAMPHORA 110177978 | CAMPHORA 1101 | CENTRAL COAST | 1.4665 | 83.8291 | 100% | 0 | 0 | 5.721% | 0% | 0 | 0.018555 | 1 | 2.1797 | 0.040444 | Low | Low | Low | 2530 | 2463 | 0.018555
CABRILLO 1104Y22 | CABRILLO 1104 | LOS PADRES | 7.1091 | 12.8346 | 36.03% | 1 | 10 | 27.87% | 0% | 0 | 0.012091 | 1 | 3.3316 | 0.040283 | Low | Low | High | 2531 | 2803 | 0.012091
PANORAMA 11021342 | PANORAMA 1102 | NORTH VALLEY | 11.6409 | 39.043 | 100% | 0 | 1 | 45.41% | 0% | 0 | 0.020716 | 1 | 1.9444 | 0.04028 | Low | Low | Low | 2532 | 2379 | 0.020716
UPPER LAKE 1101412 | UPPER LAKE 1101 | HUMBOLDT | 11.536 | 63.7276 | 55.28% | 0 | 4 | 61.85% | 0% | 0 | 0.031441 | 1 | 1.2806 | 0.040263 | Medium | Medium | Low | 2533 | 2063 | 0.031441
WOODWARD 2108R2860 | WOODWARD 2108 | FRESNO | 11.5924 | 40.5433 | 94.73% | 0 | 1 | 52.86% | 0% | 0 | 0.024579 | 1 | 1.6377 | 0.040253 | Medium | Medium | Low | 2534 | 2258 | 0.024579
COTATI 1102CB | COTATI 1102 | SONOMA | 1.3007 | 52.8482 | 0.4591% | 0 | 0 | 64.8% | 0% | 0 | 0.013707 | 1 | 2.9311 | 0.040175 | Low | Low | Medium | 2535 | 2677 | 0.013707
WILDWOOD 110198896 | WILDWOOD 1101 | NORTH VALLEY | 9.9251 | 71.2641 | 100% | 1 | 1 | 100% | 0% | 0 | 0.044142 | 1 | 0.90896 | 0.040124 | Medium | Medium | Low | 2536 | 1774 | 0.044142
FLORENCE 0401CB | FLORENCE 0401 | EAST BAY | 1.7144 | 10 | 2.295% | 5 | 1 | 39.92% | 0% | 0 | 0.00887 | 1 | 4.5207 | 0.040099 | Low | Low | High | 2537 | 2983 | 0.00887
MADISON 21017702 | MADISON 2101 | SACRAMENTO | 2.3216 | 70.1745 | 98.98% | 0 | 0 | 10.42% | 0% | 0 | 0.017585 | 1 | 2.2784 | 0.040066 | Low | Low | Medium | 2538 | 2505 | 0.017585
OAKLAND K 1101CB | OAKLAND K 1101 | EAST BAY | 0.35314 | 10 | 0% | 1 | 1 | 14.81% | 24.18% | 0 | 0.0095124 | 1 | 4.2078 | 0.040027 | Low | Low | High | 2539 | 2950 | 0.0095124
LLAGAS 2106XR146 | LLAGAS 2106 | SAN JOSE | 1.5959 | 59.0705 | 100% | 0 | 0 | 7.634% | 0% | 0 | 0.016009 | 1 | 2.4996 | 0.040015 | Low | Low | Medium | 2540 | 2569 | 0.016009
HOPLAND 1101960 | HOPLAND 1101 | HUMBOLDT | 16.1295 | 41.2103 | 77.4% | 2 | 9 | 74.6% | 0% | 0 | 0.028177 | 1 | 1.4185 | 0.039967 | Medium | Medium | Low | 2541 | 2160 | 0.028177
PACIFICA 110266732 | PACIFICA 1102 | PENINSULA | 1.1315 | 10 | 0% | 1 | 0 | 38.02% | 24.53% | 0 | 0.010334 | 1 | 3.8564 | 0.039854 | Low | Low | High | 2542 | 2913 | 0.010334
HATTON 1102648928 | HATTON 1102 | CENTRAL COAST | 2.8842 | 29.9397 | 0% | 2 | 4 | 59.99% | 0% | 0 | 0.014193 | 1 | 2.8013 | 0.039758 | Low | Low | Medium | 2543 | 2653 | 0.014193
FRANKLIN 1101P138 | FRANKLIN 1101 | EAST BAY | 1.4993 | 10 | 0% | 0 | 0 | 97.65% | 0% | 0 | 0.012403 | 1 | 3.2 | 0.03969 | Low | Low | High | 2544 | 2776 | 0.012403
SOLEDAD 21017056 | SOLEDAD 2101 | CENTRAL COAST | 1.1515 | 59.0572 | 100% | 0 | 0 | 11.67% | 0% | 0 | 0.016656 | 1 | 2.3825 | 0.039684 | Low | Low | Medium | 2545 | 2545 | 0.016656
MORGAN HILL 2105XR494 | MORGAN HILL 2105 | SAN JOSE | 0.23352 | 25.7168 | 100% | 0 | 0 | 3.179% | 0% | 0 | 0.012233 | 1 | 3.2406 | 0.039642 | Low | Low | High | 2546 | 2791 | 0.012233
COTATI 1104426 | COTATI 1104 | SONOMA | 2.1239 | 10 | 43.82% | 0 | 2 | 54.27% | 0% | 0 | 0.012029 | 1 | 3.2883 | 0.039554 | Low | Low | High | 2547 | 2806 | 0.012029
GARBERVILLE 110256048 | GARBERVILLE 1102 | HUMBOLDT | 4.9695 | 84.598 | 7.194% | 2 | 1 | 100% | 0% | 0 | 0.030194 | 1 | 1.3096 | 0.039543 | Medium | Medium | Low | 2548 | 2092 | 0.030194
KONOCTI 11084041 | KONOCTI 1108 | HUMBOLDT | 1.9081 | 10 | 99.47% | 0 | 0 | 40.69% | 0% | 0 | 0.015871 | 1 | 2.4887 | 0.039499 | Low | Low | Medium | 2549 | 2580 | 0.015871
ROSSMOOR 1101L501R | ROSSMOOR 1101 | DIABLO | 0.055455 | 10 | 100% | 0 | 0 | 2.751% | 0% | 0 | 0.010953 | 1 | 3.5964 | 0.039392 | Low | Low | High | 2550 | 2871 | 0.010953
SONOMA 1104914376 | SONOMA 1104 | SONOMA | 0.42319 | 32.6662 | 64.75% | 0 | 0 | 6.07% | 0% | 0 | 0.0098958 | 1 | 3.98 | 0.039385 | Low | Low | High | 2551 | 2934 | 0.0098958
ANTLER 11011520 | ANTLER 1101 | NORTH VALLEY | 8.8735 | 30.8958 | 71.85% | 2 | 4 | 100% | 0% | 0 | 0.033121 | 1 | 1.188 | 0.039347 | Medium | Medium | Low | 2552 | 2006 | 0.033121
MENDOCINO 1101450 | MENDOCINO 1101 | HUMBOLDT | 5.6815 | 36.3951 | 100% | 0 | 2 | 30.28% | 3.061% | 1 | 0.021431 | 1 | 1.8346 | 0.039318 | Low | Low | Low | 2553 | 2351 | 0.021431
SAN LUIS OBISPO 110742048 | SAN LUIS OBISPO 1107 | LOS PADRES | 0.025219 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0883 | 0.039207 | Low | Low | High | 2554 | 2735 | 0.012695
DOLAN ROAD 110122158 | DOLAN ROAD 1101 | CENTRAL COAST | 1.2712 | 10 | 84.22% | 0 | 1 | 10.85% | 0% | 0 | 0.010653 | 1 | 3.6785 | 0.039186 | Low | Low | High | 2555 | 2899 | 0.010653
SAN LUIS OBISPO 1107V08 | SAN LUIS OBISPO 1107 | LOS PADRES | 0.024874 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0856 | 0.039173 | Low | Low | High | 2556 | 2735 | 0.012695
SAN LEANDRO U 11149838 | SAN LEANDRO U 1114 | MISSION | 1.9933 | 10 | 1.408% | 0 | 0 | 80.56% | 0% | 0 | 0.010593 | 1 | 3.6901 | 0.039087 | Low | Low | High | 2557 | 2902 | 0.010593
NEWBURG 1131CB | NEWBURG 1131 | HUMBOLDT | 3.0239 | 26.9176 | 14.49% | 0 | 2 | 24.41% | 0% | 0 | 0.013392 | 1 | 2.916 | 0.03905 | Low | Low | Medium | 2558 | 2691 | 0.013392
PALMER 1101M82 | PALMER 1101 | LOS PADRES | 10.3483 | 48.0186 | 61.68% | 0 | 5 | 69.3% | 0% | 0 | 0.022153 | 1 | 1.7614 | 0.03902 | Medium | Medium | Low | 2559 | 2329 | 0.022153
DEL MONTE 21032204 | DEL MONTE 2103 | CENTRAL COAST | 0.36868 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0732 | 0.039015 | Low | Low | Medium | 2560 | 2735 | 0.012695
LOS OSITOS 21037082 | LOS OSITOS 2103 | CENTRAL COAST | 0.3792 | 71.4337 | 96.62% | 0 | 0 | 1.843% | 0% | 0 | 0.015988 | 1 | 2.4399 | 0.03901 | Low | Low | Medium | 2561 | 2571 | 0.015988
FAIRMOUNT 0401CB | FAIRMOUNT 0401 | EAST BAY | 1.4849 | 10 | 0% | 0 | 2 | 25.81% | 0% | 0 | 0.0082593 | 1 | 4.7218 | 0.038999 | Low | Low | High | 2562 | 3005 | 0.0082593
JESSUP 11031540 | JESSUP 1103 | NORTH VALLEY | 2.7435 | 22.0778 | 100% | 1 | 1 | 18.03% | 0% | 0 | 0.01631 | 1 | 2.3847 | 0.038895 | Low | Low | Medium | 2563 | 2560 | 0.01631
ROB ROY 2105CB | ROB ROY 2105 | CENTRAL COAST | 0.78923 | 10 | 41.07% | 2 | 0 | 55.78% | 0% | 0 | 0.013414 | 1 | 2.895 | 0.038833 | Low | Low | Medium | 2564 | 2689 | 0.013414
PEABODY 210818182 | PEABODY 2108 | SACRAMENTO | 0.013085 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0555 | 0.03879 | Low | Low | Medium | 2565 | 2735 | 0.012695
PUEBLO 2103694 | PUEBLO 2103 | NORTH BAY | 0.4502 | 10 | 100% | 0 | 0 | 9.445% | 0% | 0 | 0.011704 | 1 | 3.3141 | 0.038789 | Low | Low | High | 2566 | 2822 | 0.011704
SAN LUIS OBISPO 1105CB | SAN LUIS OBISPO 1105 | LOS PADRES | 1.9887 | 39.9951 | 43.06% | 3 | 3 | 16.92% | 0% | 0 | 0.012254 | 1 | 3.1619 | 0.038746 | Low | Low | High | 2567 | 2790 | 0.012254
POINT MORETTI 11015076 | POINT MORETTI 1101 | CENTRAL COAST | 7.1634 | 15.8606 | 16.59% | 11 | 1 | 79.19% | 0% | 0 | 0.018862 | 1 | 2.0481 | 0.03863 | Low | Low | Low | 2568 | 2455 | 0.018862
NORTH BRANCH 110113496 | NORTH BRANCH 1101 | STOCKTON | 2.2189 | 10 | 62.08% | 0 | 0 | 44.24% | 0% | 0 | 0.012126 | 1 | 3.1825 | 0.03859 | Low | Low | High | 2569 | 2799 | 0.012126
SOLEDAD 21013720 | SOLEDAD 2101 | CENTRAL COAST | 2.3505 | 51.9589 | 88.77% | 0 | 0 | 12.85% | 0% | 0 | 0.016725 | 1 | 2.3054 | 0.038559 | Low | Low | Medium | 2570 | 2539 | 0.016725
BURNEY 11012402 | BURNEY 1101 | NORTH VALLEY | 1.4308 | 10 | 91.1% | 2 | 2 | 38.13% | 0% | 0 | 0.020105 | 1 | 1.914 | 0.038481 | Low | Low | Low | 2571 | 2404 | 0.020105
BEAR VALLEY 2101CB | BEAR VALLEY 2101 | YOSEMITE | 18.7199 | 23.9906 | 55.73% | 0 | 6 | 100% | 0% | 0 | 0.047229 | 1 | 0.81463 | 0.038474 | Medium | Medium | Low | 2572 | 1722 | 0.047229
DUNLAP 11027849F | DUNLAP 1102 | FRESNO | 8.6653 | 17.4771 | 100% | 3 | 9 | 100% | 0% | 0 | 0.037371 | 1 | 1.0288 | 0.038447 | Medium | Medium | Low | 2573 | 1907 | 0.037371
SAN LEANDRO U 1114MR544 | SAN LEANDRO U 1114 | MISSION | 2.1618 | 10 | 45.25% | 0 | 0 | 34.37% | 0% | 0 | 0.010938 | 1 | 3.5146 | 0.038442 | Low | Low | High | 2574 | 2874 | 0.010938
CAYUCOS 1102W18 | CAYUCOS 1102 | LOS PADRES | 1.9754 | 67.8899 | 46.98% | 0 | 0 | 8.859% | 14.04% | 0 | 0.015968 | 1 | 2.4056 | 0.038413 | Low | Low | Medium | 2575 | 2573 | 0.015968
HIGGINS 1110 | HIGGINS 1110 | SIERRA | 0.035539 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 3.0246 | 0.038398 | Low | Low | Medium | 2576 | 2735 | 0.012695
PETALUMA C 1109270 | PETALUMA C 1109 | SONOMA | 1.61 | 25.9839 | 62.25% | 0 | 3 | 21.02% | 0% | 0 | 0.011438 | 1 | 3.35 | 0.038318 | Low | Low | High | 2577 | 2840 | 0.011438
WILLOW CREEK 110191926 | WILLOW CREEK 1101 | HUMBOLDT | 5.6211 | 81.2548 | 100% | 2 | 0 | 52.92% | 0% | 0 | 0.033802 | 1 | 1.1327 | 0.038287 | Medium | Medium | Low | 2578 | 1981 | 0.033802
TEMPLETON 2112R98 | TEMPLETON 2112 | LOS PADRES | 2.5848 | 57.8675 | 88.32% | 0 | 0 | 11.06% | 0% | 0 | 0.017037 | 1 | 2.2449 | 0.038247 | Low | Low | Medium | 2579 | 2527 | 0.017037
WYANDOTTE 11091520 | WYANDOTTE 1109 | NORTH VALLEY | 4.1645 | 10 | 80.53% | 0 | 0 | 21.24% | 0% | 0 | 0.011222 | 1 | 3.4039 | 0.038199 | Low | Low | High | 2580 | 2852 | 0.011222
ANDERSON 11011752 | ANDERSON 1101 | NORTH VALLEY | 3.4624 | 22.5175 | 29.42% | 0 | 0 | 74.73% | 0% | 0 | 0.015595 | 1 | 2.4433 | 0.038104 | Low | Low | Medium | 2581 | 2589 | 0.015595
SUNOL 110111587 | SUNOL 1101 | MISSION | 0.25848 | 10 | 100% | 0 | 1 | 24.35% | 0% | 0 | 0.013849 | 1 | 2.7479 | 0.038054 | Low | Low | Medium | 2582 | 2672 | 0.013849
LAYTONVILLE 1102220946 | LAYTONVILLE 1102 | HUMBOLDT | 0.040461 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.3334 | 0.038016 | Medium | Medium | Low | 2583 | 2136 | 0.028512
SUNOL 11018721 | SUNOL 1101 | MISSION | 2.3818 | 51.7237 | 49.03% | 0 | 1 | 76.51% | 0% | 0 | 0.0231 | 1 | 1.6423 | 0.037937 | Medium | Medium | Low | 2584 | 2306 | 0.0231
JESSUP 11019002 | JESSUP 1101 | NORTH VALLEY | 6.7893 | 16.4426 | 68.96% | 0 | 5 | 44.76% | 0% | 0 | 0.017028 | 1 | 2.2277 | 0.037935 | Low | Low | Low | 2585 | 2528 | 0.017028
SOLEDAD 21027562 | SOLEDAD 2102 | CENTRAL COAST | 1.9641 | 22.7828 | 92.71% | 0 | 0 | 25.93% | 0% | 0 | 0.014154 | 1 | 2.6794 | 0.037924 | Low | Low | Medium | 2586 | 2655 | 0.014154
FROGTOWN 170236870 | FROGTOWN 1702 | STOCKTON | 2.2467 | 10 | 88.34% | 0 | 2 | 72.13% | 0% | 0 | 0.020592 | 1 | 1.8354 | 0.037794 | Low | Low | Low | 2587 | 2383 | 0.020592
SAN LUIS OBISPO 110788962 | SAN LUIS OBISPO 1107 | LOS PADRES | 1.6209 | 48.7477 | 22.43% | 0 | 1 | 40.61% | 0% | 0 | 0.012815 | 1 | 2.9485 | 0.037786 | Low | Low | Medium | 2588 | 2724 | 0.012815
WOOD 0401CB | WOOD 0401 | EAST BAY | 0.4018 | 10 | 54.38% | 0 | 0 | 12.06% | 0% | 0 | 0.0082741 | 1 | 4.5612 | 0.037739 | Low | Low | High | 2589 | 3004 | 0.0082741
RED BLUFF 1101 | RED BLUFF 1101 | NORTH VALLEY | 0.18711 | 22.4749 | 100% | 0 | 0 | 61.69% | 0% | 0 | 0.021308 | 1 | 1.7689 | 0.037691 | Low | Low | Low | 2590 | 2357 | 0.021308
WYANDOTTE 110942650 | WYANDOTTE 1109 | NORTH VALLEY | 0.71686 | 10 | 44.77% | 0 | 0 | 27.21% | 0% | 0 | 0.0088907 | 1 | 4.2335 | 0.037638 | Low | Low | High | 2591 | 2982 | 0.0088907
CARLOTTA 112142896 | CARLOTTA 1121 | HUMBOLDT | 2.183 | 31.2732 | 37.15% | 2 | 2 | 39.92% | 0% | 0 | 0.015245 | 1 | 2.4688 | 0.037636 | Low | Low | Medium | 2592 | 2601 | 0.015245
CORONA 11034446 | CORONA 1103 | SONOMA | 0.968 | 50.7747 | 83.54% | 0 | 0 | 7.888% | 0% | 0 | 0.013274 | 1 | 2.8291 | 0.037555 | Low | Low | Medium | 2593 | 2700 | 0.013274
CLOVERDALE 1102429006 | CLOVERDALE 1102 | SONOMA | 2.0089 | 22.4739 | 19.1% | 0 | 1 | 100% | 0% | 0 | 0.016467 | 1 | 2.2766 | 0.037488 | Low | Low | Medium | 2594 | 2554 | 0.016467
MILPITAS 110962157 | MILPITAS 1109 | SAN JOSE | 0.044828 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.9508 | 0.037462 | Low | Low | Medium | 2595 | 2735 | 0.012695
NARROWS 21022718 | NARROWS 2102 | SIERRA | 0.45209 | 10 | 82.65% | 0 | 1 | 6.234% | 0% | 0 | 0.010047 | 1 | 3.7245 | 0.037421 | Low | Low | High | 2596 | 2926 | 0.010047
ANDERSON 11031600 | ANDERSON 1103 | NORTH VALLEY | 2.5631 | 13.0676 | 100% | 0 | 0 | 23.83% | 0% | 0 | 0.015715 | 1 | 2.3807 | 0.037413 | Low | Low | Medium | 2597 | 2585 | 0.015715
OTTER 11022166 | OTTER 1102 | CENTRAL COAST | 4.0812 | 30.3358 | 3.172% | 4 | 2 | 100% | 0% | 0 | 0.027673 | 1 | 1.3506 | 0.037374 | Medium | Medium | Low | 2598 | 2171 | 0.027673
GRASS VALLEY 1103 | GRASS VALLEY 1103 | SIERRA | 0.021115 | 10 | 19.87% | 0 | 0 | 100% | 0% | 0 | 0.014923 | 1 | 2.5027 | 0.037349 | Low | Low | Medium | 2599 | 2610 | 0.014923
SAUSALITO 11011270 | SAUSALITO 1101 | NORTH BAY | 0.49678 | 64.5423 | 0% | 0 | 0 | 50.41% | 0% | 0 | 0.011233 | 1 | 3.3242 | 0.037341 | Low | Low | High | 2600 | 2851 | 0.011233
MENLO 11029110 | MENLO 1102 | PENINSULA | 0.16148 | 10 | 87.04% | 1 | 0 | 1.751% | 0% | 0 | 0.0098849 | 1 | 3.7774 | 0.037339 | Low | Low | High | 2601 | 2935 | 0.0098849
HICKS 2101XR548 | HICKS 2101 | SAN JOSE | 1.763 | 53.1133 | 61.37% | 0 | 0 | 20.35% | 0% | 0 | 0.012735 | 1 | 2.9304 | 0.037318 | Low | Low | Medium | 2602 | 2729 | 0.012735
CORRAL 110214028 | CORRAL 1102 | STOCKTON | 3.2845 | 10 | 84.85% | 0 | 2 | 41.18% | 0% | 0 | 0.01476 | 1 | 2.5258 | 0.03728 | Low | Low | Medium | 2603 | 2621 | 0.01476
WILLOW PASS 1101CB | WILLOW PASS 1101 | DIABLO | 0.46926 | 10 | 100% | 0 | 1 | 6.681% | 0% | 0 | 0.011627 | 1 | 3.2051 | 0.037265 | Low | Low | High | 2604 | 2828 | 0.011627
NARROWS 210551582 | NARROWS 2105 | SIERRA | 9.5263 | 10 | 48.26% | 0 | 1 | 100% | 0% | 0 | 0.019181 | 1 | 1.9413 | 0.037237 | Low | Low | Low | 2605 | 2436 | 0.019181
COTTONWOOD 11029026 | COTTONWOOD 1102 | NORTH VALLEY | 14.1835 | 17.7686 | 84.41% | 1 | 2 | 58.01% | 0% | 0 | 0.021122 | 1 | 1.7609 | 0.037192 | Low | Low | Low | 2606 | 2362 | 0.021122
FORT ROSS 1121134 | FORT ROSS 1121 | SONOMA | 7.7066 | 23.2401 | 8.01% | 16 | 1 | 95.15% | 0% | 0 | 0.029926 | 1 | 1.2427 | 0.037189 | Medium | Medium | Low | 2607 | 2102 | 0.029926
KONOCTI 11022293 | KONOCTI 1102 | HUMBOLDT | 0.16556 | 10 | 100% | 0 | 0 | 9.444% | 0% | 0 | 0.011704 | 1 | 3.1767 | 0.03718 | Low | Low | High | 2608 | 2823 | 0.011704
JESSUP 1101CB | JESSUP 1101 | NORTH VALLEY | 1.1327 | 30.8343 | 100% | 0 | 0 | 19.43% | 0% | 0 | 0.01487 | 1 | 2.5003 | 0.037179 | Low | Low | Medium | 2609 | 2614 | 0.01487
POSO MOUNTAIN 2104CB | POSO MOUNTAIN 2104 | KERN | 5.3916 | 10 | 6.227% | 0 | 6 | 72.59% | 0% | 0 | 0.013157 | 1 | 2.8181 | 0.037076 | Low | Low | Medium | 2610 | 2707 | 0.013157
LUCERNE 110676850 | LUCERNE 1106 | HUMBOLDT | 2.0465 | 10 | 61.3% | 0 | 3 | 55.89% | 0% | 0 | 0.014386 | 1 | 2.5722 | 0.037005 | Low | Low | Medium | 2611 | 2635 | 0.014386
COTATI 1102464 | COTATI 1102 | SONOMA | 1.2747 | 26.0788 | 66.97% | 0 | 1 | 15.73% | 0% | 0 | 0.012358 | 1 | 2.9928 | 0.036986 | Low | Low | Medium | 2612 | 2780 | 0.012358
SYCAMORE CREEK 1109CB | SYCAMORE CREEK 1109 | NORTH VALLEY | 0.58228 | 10 | 100% | 0 | 0 | 6.6% | 0% | 0 | 0.011379 | 1 | 3.2447 | 0.036922 | Low | Low | High | 2613 | 2843 | 0.011379
MORRO BAY 1102CB | MORRO BAY 1102 | LOS PADRES | 3.3958 | 10 | 1.002% | 0 | 0 | 71.82% | 0% | 0 | 0.011049 | 1 | 3.3405 | 0.036911 | Low | Low | High | 2614 | 2861 | 0.011049
PEABODY 2106CB | PEABODY 2106 | SACRAMENTO | 0.58049 | 10 | 53.14% | 0 | 0 | 53.74% | 0% | 0 | 0.012385 | 1 | 2.9801 | 0.036907 | Low | Low | Medium | 2615 | 2778 | 0.012385
NORTH BRANCH 1101CB | NORTH BRANCH 1101 | STOCKTON | 10.7662 | 27.7002 | 39.92% | 0 | 5 | 56% | 0% | 0 | 0.014214 | 1 | 2.5951 | 0.036887 | Low | Low | Medium | 2616 | 2650 | 0.014214
JARVIS 1108MR368 | JARVIS 1108 | MISSION | 0.80128 | 10 | 39.98% | 0 | 0 | 23.87% | 0% | 0 | 0.0094416 | 1 | 3.9056 | 0.036875 | Low | Low | High | 2617 | 2958 | 0.0094416
COARSEGOLD 210410030 | COARSEGOLD 2104 | YOSEMITE | 15.7445 | 10.7109 | 33.01% | 0 | 3 | 88.51% | 0% | 0 | 0.020603 | 1 | 1.786 | 0.036797 | Low | Low | Low | 2618 | 2382 | 0.020603
RIO DEL MAR 0401CB | RIO DEL MAR 0401 | CENTRAL COAST | 1.702 | 10 | 16.67% | 5 | 1 | 48.18% | 0% | 0 | 0.010828 | 1 | 3.3814 | 0.036613 | Low | Low | High | 2619 | 2882 | 0.010828
HATTON 11029642 | HATTON 1102 | CENTRAL COAST | 1.1982 | 10 | 4.477% | 2 | 1 | 100% | 0% | 0 | 0.013798 | 1 | 2.6508 | 0.036576 | Low | Low | Medium | 2620 | 2674 | 0.013798
RACETRACK 170310870 | RACETRACK 1703 | YOSEMITE | 1.0803 | 10 | 45.22% | 0 | 3 | 41.49% | 0% | 0 | 0.010943 | 1 | 3.3367 | 0.036514 | Low | Low | High | 2621 | 2873 | 0.010943
FITCH MOUNTAIN 11115060 | FITCH MOUNTAIN 1111 | SONOMA | 2.1624 | 43.6089 | 39.41% | 0 | 3 | 35.19% | 0% | 0 | 0.012308 | 1 | 2.9515 | 0.036326 | Low | Low | Medium | 2622 | 2784 | 0.012308
KONOCTI 11084037 | KONOCTI 1108 | HUMBOLDT | 0.3878 | 10 | 100% | 0 | 0 | 22.52% | 0% | 0 | 0.013321 | 1 | 2.7262 | 0.036316 | Low | Low | Medium | 2623 | 2698 | 0.013321
ELK 110191336 | ELK 1101 | HUMBOLDT | 7.8266 | 12.5917 | 0% | 14 | 5 | 92.25% | 0% | 0 | 0.020708 | 1 | 1.7508 | 0.036255 | Low | Low | Low | 2624 | 2380 | 0.020708
OAKHURST 110311900 | OAKHURST 1103 | YOSEMITE | 0.064919 | 10 | 100% | 0 | 0 | 7.722% | 0% | 0 | 0.011506 | 1 | 3.147 | 0.03621 | Low | Low | High | 2625 | 2834 | 0.011506
WISE 110163199 | WISE 1101 | SIERRA | 0.5708 | 42.4087 | 13.05% | 0 | 0 | 61.18% | 0% | 0 | 0.01197 | 1 | 3.0242 | 0.036199 | Low | Low | Medium | 2626 | 2810 | 0.01197
WILLITS 1103696 | WILLITS 1103 | HUMBOLDT | 6.5774 | 41.2479 | 62.23% | 0 | 3 | 69.69% | 0% | 0 | 0.020487 | 1 | 1.7628 | 0.036115 | Low | Low | Low | 2627 | 2386 | 0.020487
CHESTER 1102CB | CHESTER 1102 | NORTH VALLEY | 0.32002 | 10 | 100% | 0 | 0 | 10.17% | 0% | 0 | 0.01345 | 1 | 2.6792 | 0.036036 | Low | Low | Medium | 2628 | 2686 | 0.01345
OILFIELDS 1103 | OILFIELDS 1103 | CENTRAL COAST | 0.020981 | 19.5696 | 17.4% | 0 | 0 | 100% | 0% | 0 | 0.015601 | 1 | 2.3018 | 0.035911 | Low | Low | Medium | 2629 | 2588 | 0.015601
EDENVALE 2107CB | EDENVALE 2107 | SAN JOSE | 0.73661 | 33.423 | 98.26% | 0 | 0 | 2.254% | 0% | 0 | 0.01259 | 1 | 2.8521 | 0.035908 | Low | Low | Medium | 2630 | 2770 | 0.01259
SAN CARLOS 11048846 | SAN CARLOS 1104 | PENINSULA | 1.1188 | 10 | 42.43% | 0 | 1 | 25.48% | 0% | 0 | 0.0087545 | 1 | 4.0972 | 0.035869 | Low | Low | High | 2631 | 2986 | 0.0087545
HALSEY 11022514 | HALSEY 1102 | SIERRA | 9.2843 | 10 | 42.43% | 1 | 2 | 47.49% | 0% | 0 | 0.012855 | 1 | 2.7818 | 0.035761 | Low | Low | Medium | 2632 | 2722 | 0.012855
CLAY 1102CB | CLAY 1102 | STOCKTON | 1.1664 | 10 | 0% | 0 | 0 | 60.02% | 0% | 0 | 0.011126 | 1 | 3.2104 | 0.035721 | Low | Low | High | 2633 | 2860 | 0.011126
MENDOCINO 110137462 | MENDOCINO 1101 | HUMBOLDT | 2.449 | 10 | 46.73% | 0 | 2 | 50.22% | 0% | 0 | 0.0135 | 1 | 2.6397 | 0.035636 | Low | Low | Medium | 2634 | 2682 | 0.0135
HICKS 1116CB | HICKS 1116 | SAN JOSE | 1.3112 | 10 | 43.95% | 1 | 3 | 7.743% | 0% | 0 | 0.0089608 | 1 | 3.9753 | 0.035622 | Low | Low | High | 2635 | 2979 | 0.0089608
CURTIS 170190120 | CURTIS 1701 | YOSEMITE | 2.5983 | 10 | 28.78% | 0 | 1 | 50.57% | 0% | 0 | 0.010044 | 1 | 3.5453 | 0.035611 | Low | Low | High | 2636 | 2927 | 0.010044
DESCHUTES 1101CB | DESCHUTES 1101 | NORTH VALLEY | 4.1985 | 15.36 | 72.74% | 0 | 0 | 36.89% | 0% | 0 | 0.012752 | 1 | 2.792 | 0.035602 | Low | Low | Medium | 2637 | 2727 | 0.012752
TIDEWATER 210665866 | TIDEWATER 2106 | DIABLO | 4.2405 | 36.2821 | 12.3% | 0 | 0 | 47.54% | 0% | 0 | 0.0099699 | 1 | 3.5683 | 0.035576 | Low | Low | High | 2638 | 2929 | 0.0099699
MORGAN HILL 2110XR326 | MORGAN HILL 2110 | SAN JOSE | 2.054 | 29.8956 | 63.47% | 0 | 2 | 9.633% | 0% | 0 | 0.013515 | 1 | 2.63 | 0.035544 | Low | Low | Medium | 2639 | 2681 | 0.013515
BANGOR 110155206 | BANGOR 1101 | NORTH VALLEY | 2.9326 | 34.2156 | 61.32% | 1 | 0 | 28.49% | 0% | 0 | 0.012304 | 1 | 2.8829 | 0.03547 | Low | Low | Medium | 2640 | 2785 | 0.012304
CEDAR CREEK 11011362 | CEDAR CREEK 1101 | NORTH VALLEY | 0.015515 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 1.2439 | 0.035466 | Medium | Medium | Low | 2641 | 2136 | 0.028512
DUNBAR 1101160 | DUNBAR 1101 | SONOMA | 4.1387 | 21.8951 | 29.76% | 0 | 0 | 62.23% | 10.35% | 0 | 0.01425 | 1 | 2.486 | 0.035427 | Low | Low | Medium | 2642 | 2644 | 0.01425
PEORIA 17013186 | PEORIA 1701 | YOSEMITE | 10.0751 | 10 | 99.94% | 1 | 2 | 100% | 0% | 0 | 0.030068 | 1 | 1.1773 | 0.035399 | Medium | Medium | Low | 2643 | 2098 | 0.030068
FORT ORD 21069658 | FORT ORD 2106 | CENTRAL COAST | 0.097044 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.7847 | 0.035353 | Low | Low | Medium | 2644 | 2735 | 0.012695
CHESTER 1101CB | CHESTER 1101 | NORTH VALLEY | 2.5695 | 10 | 96.88% | 0 | 0 | 31.91% | 0% | 0 | 0.01425 | 1 | 2.4772 | 0.035299 | Low | Low | Medium | 2645 | 2645 | 0.01425
HATTON 11022070 | HATTON 1102 | CENTRAL COAST | 0.49418 | 10 | 29.42% | 0 | 3 | 25.81% | 0% | 0 | 0.010726 | 1 | 3.2805 | 0.035187 | Low | Low | High | 2646 | 2891 | 0.010726
LUCERNE 1106CB | LUCERNE 1106 | HUMBOLDT | 2.483 | 10 | 34.76% | 1 | 7 | 68.8% | 0% | 0 | 0.01653 | 1 | 2.1266 | 0.035153 | Low | Low | Low | 2647 | 2549 | 0.01653
CURTIS 170356972 | CURTIS 1703 | YOSEMITE | 8.4449 | 49.5291 | 11.99% | 0 | 2 | 100% | 0.5389% | 1 | 0.02188 | 1 | 1.6045 | 0.035106 | Medium | Medium | Low | 2648 | 2338 | 0.02188
ELK 11011260 | ELK 1101 | HUMBOLDT | 15.6745 | 74.4455 | 25.71% | 10 | 4 | 100% | 0% | 0 | 0.043784 | 1 | 0.80153 | 0.035094 | Medium | Medium | Low | 2649 | 1780 | 0.043784
PLACERVILLE 1109CB | PLACERVILLE 1109 | SIERRA | 0.020146 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.012961 | 1 | 2.6978 | 0.034966 | Low | Low | Medium | 2650 | 2716 | 0.012961
ROSSMOOR 110192164 | ROSSMOOR 1101 | DIABLO | 0.25455 | 10 | 51.39% | 0 | 0 | 26.2% | 0% | 0 | 0.0092923 | 1 | 3.7629 | 0.034966 | Low | Low | High | 2651 | 2963 | 0.0092923
ROSSMOOR 110676468 | ROSSMOOR 1106 | DIABLO | 1.5034 | 10 | 14.83% | 1 | 2 | 51.08% | 0% | 0 | 0.0093177 | 1 | 3.7505 | 0.034946 | Low | Low | High | 2652 | 2962 | 0.0093177
FAIRVIEW 2207P150 | FAIRVIEW 2207 | DIABLO | 1.7182 | 19.1624 | 0% | 0 | 0 | 75.67% | 0% | 0 | 0.010614 | 1 | 3.2893 | 0.034913 | Low | Low | High | 2653 | 2900 | 0.010614
GEYSERVILLE 110135492 | GEYSERVILLE 1101 | SONOMA | 8.4529 | 69.0353 | 85.9% | 0 | 0 | 39.22% | 0% | 0 | 0.020833 | 1 | 1.6734 | 0.034862 | Low | Low | Low | 2654 | 2376 | 0.020833
WILLOW PASS 2107P500R | WILLOW PASS 2107 | DIABLO | 0.15832 | 10 | 100% | 0 | 0 | 4.986% | 0% | 0 | 0.011198 | 1 | 3.1106 | 0.034834 | Low | Low | High | 2655 | 2855 | 0.011198
BERKELEY F 0402CB | BERKELEY F 0402 | EAST BAY | 0.47631 | 10 | 26.87% | 0 | 0 | 22.4% | 0% | 0 | 0.0083588 | 1 | 4.1661 | 0.034823 | Low | Low | High | 2656 | 3002 | 0.0083588
SAND CREEK 11037110 | SAND CREEK 1103 | FRESNO | 19.4155 | 27.8259 | 94.86% | 5 | 7 | 100% | 0% | 0 | 0.080582 | 1 | 0.43197 | 0.034809 | High | High | Low | 2657 | 1393 | 0.080582
POSO MOUNTAIN 210448268 | POSO MOUNTAIN 2104 | KERN | 4.774 | 10 | 10.21% | 0 | 0 | 90.31% | 0% | 0 | 0.012535 | 1 | 2.7681 | 0.034699 | Low | Low | Medium | 2658 | 2772 | 0.012535
BELMONT 1103415994 | BELMONT 1103 | PENINSULA | 1.0684 | 10 | 38.18% | 0 | 2 | 26.01% | 0% | 0 | 0.0086782 | 1 | 3.9933 | 0.034655 | Low | Low | High | 2659 | 2991 | 0.0086782
BUTTE 11052410 | BUTTE 1105 | NORTH VALLEY | 1.8432 | 10 | 92.92% | 0 | 0 | 16.76% | 0% | 0 | 0.011878 | 1 | 2.9154 | 0.034628 | Low | Low | Medium | 2660 | 2815 | 0.011878
VALLEY VIEW 1105P126 | VALLEY VIEW 1105 | EAST BAY | 0.94179 | 10 | 5.099% | 0 | 0 | 45.94% | 0% | 0 | 0.008838 | 1 | 3.9116 | 0.034571 | Low | Low | High | 2661 | 2984 | 0.008838
TEJON 11023751 | TEJON 1102 | KERN | 20.1546 | 14.4086 | 57.09% | 0 | 4 | 78.15% | 0% | 0 | 0.034903 | 1 | 0.99037 | 0.034567 | Medium | Medium | Low | 2662 | 1954 | 0.034903
MESA 1101CB | MESA 1101 | LOS PADRES | 13.1474 | 48.8211 | 12.29% | 0 | 3 | 51.32% | 0% | 0 | 0.013679 | 1 | 2.5227 | 0.034509 | Low | Low | Medium | 2663 | 2678 | 0.013679
CMC 1102CB | CMC 1102 | LOS PADRES | 0.46264 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.714 | 0.034455 | Low | Low | Medium | 2664 | 2766 | 0.012695
SNEATH LANE 1106CB | SNEATH LANE 1106 | PENINSULA | 1.101 | 10 | 47.15% | 3 | 3 | 17.83% | 0% | 0 | 0.0091441 | 1 | 3.7667 | 0.034443 | Low | Low | High | 2665 | 2973 | 0.0091441
HARTLEY 110194178 | HARTLEY 1101 | HUMBOLDT | 1.6171 | 10 | 47.04% | 0 | 1 | 41.48% | 0% | 0 | 0.012159 | 1 | 2.8315 | 0.034428 | Low | Low | Medium | 2666 | 2797 | 0.012159
KERN OIL 11063301 | KERN OIL 1106 | KERN | 0.36257 | 10 | 100% | 0 | 0 | 1.116% | 0% | 0 | 0.012298 | 1 | 2.7994 | 0.034427 | Low | Low | Medium | 2667 | 2786 | 0.012298
SAN LUIS OBISPO 1103CB | SAN LUIS OBISPO 1103 | LOS PADRES | 2.8352 | 59.393 | 72.07% | 0 | 1 | 20.37% | 0% | 0 | 0.014802 | 1 | 2.3239 | 0.034398 | Low | Low | Medium | 2668 | 2618 | 0.014802
LOS MOLINOS 11011308 | LOS MOLINOS 1101 | NORTH VALLEY | 0.1275 | 79.8468 | 100% | 0 | 0 | 1.055% | 0% | 0 | 0.017254 | 1 | 1.9923 | 0.034377 | Low | Low | Low | 2669 | 2519 | 0.017254
CLAY 1103CB | CLAY 1103 | STOCKTON | 5.7506 | 36.571 | 11.82% | 0 | 1 | 42.68% | 0% | 0 | 0.011049 | 1 | 3.1111 | 0.034376 | Low | Low | High | 2670 | 2862 | 0.011049
CABRILLO 11031437 | CABRILLO 1103 | LOS PADRES | 3.2446 | 37.9706 | 72.77% | 0 | 0 | 66.31% | 0% | 0 | 0.019849 | 1 | 1.7318 | 0.034374 | Low | Low | Low | 2671 | 2417 | 0.019849
SONOMA 11054456 | SONOMA 1105 | SONOMA | 1.6486 | 23.1811 | 52.93% | 0 | 1 | 22.31% | 0% | 0 | 0.010106 | 1 | 3.401 | 0.034372 | Low | Low | High | 2672 | 2923 | 0.010106
STELLING 110913228 | STELLING 1109 | DE ANZA | 0.52786 | 10 | 79.39% | 0 | 0 | 6.214% | 0% | 0 | 0.0095798 | 1 | 3.5877 | 0.034369 | Low | Low | High | 2673 | 2947 | 0.0095798
TEJON 11023760 | TEJON 1102 | KERN | 5.5529 | 84.6891 | 100% | 0 | 0 | 84.6% | 0% | 0 | 0.040235 | 1 | 0.85149 | 0.03426 | Medium | Medium | Low | 2674 | 1850 | 0.040235
WILLITS 11044650 | WILLITS 1104 | HUMBOLDT | 2.8566 | 16.3398 | 61.51% | 0 | 4 | 48.68% | 0% | 0 | 0.014299 | 1 | 2.3934 | 0.034224 | Low | Low | Medium | 2675 | 2640 | 0.014299
MORGAN HILL 2105XR602 | MORGAN HILL 2105 | SAN JOSE | 0.59187 | 10 | 11.22% | 0 | 0 | 69.56% | 0% | 0 | 0.010291 | 1 | 3.3208 | 0.034174 | Low | Low | High | 2676 | 2916 | 0.010291
BURNEY 1101CB | BURNEY 1101 | NORTH VALLEY | 0.91927 | 10 | 59.07% | 1 | 0 | 46.14% | 0% | 0 | 0.012215 | 1 | 2.7975 | 0.034171 | Low | Low | Medium | 2677 | 2793 | 0.012215
BURNEY 110297318 | BURNEY 1102 | NORTH VALLEY | 0.71383 | 14.6507 | 68.47% | 0 | 0 | 50.51% | 0% | 0 | 0.015997 | 1 | 2.1361 | 0.034171 | Low | Low | Low | 2678 | 2570 | 0.015997
TEMPLETON 2108A40 | TEMPLETON 2108 | LOS PADRES | 1.2118 | 10 | 85.64% | 0 | 0 | 9.425% | 0% | 0 | 0.010408 | 1 | 3.2792 | 0.03413 | Low | Low | High | 2679 | 2909 | 0.010408
PIT NO 1 1101CB | PIT NO 1 1101 | NORTH VALLEY | 6.4361 | 10 | 29.8% | 1 | 2 | 98.02% | 0% | 0 | 0.019097 | 1 | 1.7847 | 0.034083 | Low | Low | Low | 2680 | 2440 | 0.019097
OREGON TRAIL 110346860 | OREGON TRAIL 1103 | NORTH VALLEY | 0.53541 | 10 | 100% | 0 | 0 | 16.12% | 0% | 0 | 0.012504 | 1 | 2.7222 | 0.034039 | Low | Low | Medium | 2681 | 2774 | 0.012504
HIGHLANDS 1101CB | HIGHLANDS 1101 | HUMBOLDT | 0.026418 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.6761 | 0.033974 | Low | Low | Medium | 2682 | 2766 | 0.012695
LAS GALLINAS A 11051218 | LAS GALLINAS A 1105 | NORTH BAY | 0.13008 | 10 | 100% | 0 | 0 | 5.571% | 0% | 0 | 0.011264 | 1 | 3.0158 | 0.033969 | Low | Low | Medium | 2683 | 2849 | 0.011264
WISE 11011404 | WISE 1101 | SIERRA | 2.2264 | 13.0264 | 54.75% | 0 | 1 | 62.41% | 0% | 0 | 0.014247 | 1 | 2.3816 | 0.03393 | Low | Low | Medium | 2684 | 2646 | 0.014247
RACETRACK 1703332820 | RACETRACK 1703 | YOSEMITE | 1.3085 | 10 | 3.686% | 0 | 0 | 71.54% | 0% | 0 | 0.0098677 | 1 | 3.4356 | 0.033901 | Low | Low | High | 2685 | 2936 | 0.0098677
GONZALES 110422420 | GONZALES 1104 | CENTRAL COAST | 0.060363 | 60 | 100% | 0 | 0 | 0.7167% | 0% | 0 | 0.015047 | 1 | 2.2459 | 0.033793 | Low | Low | Medium | 2686 | 2606 | 0.015047
SANTA YNEZ 1104CB | SANTA YNEZ 1104 | LOS PADRES | 0.81728 | 10 | 74.93% | 2 | 0 | 9.437% | 0% | 0 | 0.00979 | 1 | 3.444 | 0.033717 | Low | Low | High | 2687 | 2941 | 0.00979
GEYSERVILLE 1101166 | GEYSERVILLE 1101 | SONOMA | 11.044 | 32.5571 | 62.6% | 3 | 3 | 68.81% | 0% | 0 | 0.022773 | 1 | 1.478 | 0.033658 | Medium | Medium | Low | 2688 | 2312 | 0.022773
WYANDOTTE 1105329930 | WYANDOTTE 1105 | NORTH VALLEY | 7.9312 | 11.1268 | 28.89% | 0 | 1 | 75.51% | 0% | 0 | 0.01297 | 1 | 2.5915 | 0.033613 | Low | Low | Medium | 2689 | 2715 | 0.01297
MONTEREY 04022644 | MONTEREY 0402 | CENTRAL COAST | 0.7655 | 10 | 0% | 1 | 1 | 53.52% | 0% | 0 | 0.010791 | 1 | 3.0937 | 0.033385 | Low | Low | High | 2690 | 2884 | 0.010791
PIT NO 3 2101CB | PIT NO 3 2101 | NORTH VALLEY | 4.5423 | 34.7965 | 2.145% | 10 | 3 | 100% | 0% | 0 | 0.027375 | 1 | 1.2188 | 0.033365 | Medium | Medium | Low | 2691 | 2181 | 0.027375
ZACA 1102Y48 | ZACA 1102 | LOS PADRES | 4.0585 | 10 | 41.4% | 0 | 6 | 34.23% | 0% | 0 | 0.011989 | 1 | 2.7812 | 0.033343 | Low | Low | Medium | 2692 | 2809 | 0.011989
BEAR VALLEY 21014500 | BEAR VALLEY 2101 | YOSEMITE | 27.333 | 23.9548 | 99.26% | 0 | 3 | 33.35% | 0% | 0 | 0.017222 | 1 | 1.9324 | 0.03328 | Low | Low | Low | 2693 | 2521 | 0.017222
SAN BERNARD 1101CB | SAN BERNARD 1101 | KERN | 0.91753 | 10 | 100% | 0 | 0 | 2.928% | 0% | 0 | 0.010972 | 1 | 3.031 | 0.033257 | Low | Low | Medium | 2694 | 2867 | 0.010972
GEYSERVILLE 110137454 | GEYSERVILLE 1101 | SONOMA | 7.5123 | 58.2774 | 62.29% | 0 | 0 | 62.62% | 0% | 0 | 0.022967 | 1 | 1.4474 | 0.033242 | Medium | Medium | Low | 2695 | 2309 | 0.022967
JESSUP 1102CB | JESSUP 1102 | NORTH VALLEY | 0.20781 | 10 | 69.42% | 4 | 1 | 3.869% | 0% | 0 | 0.01209 | 1 | 2.7419 | 0.033151 | Low | Low | Medium | 2696 | 2804 | 0.01209
LLAGAS 2105XR234 | LLAGAS 2105 | SAN JOSE | 0.40589 | 10 | 70.52% | 0 | 1 | 18.63% | 0% | 0 | 0.01029 | 1 | 3.2175 | 0.033108 | Low | Low | High | 2697 | 2917 | 0.01029
COVELO 110196896 | COVELO 1101 | HUMBOLDT | 3.6958 | 52.7111 | 100% | 5 | 0 | 24.03% | 0% | 0 | 0.024981 | 1 | 1.3246 | 0.033091 | Medium | Medium | Low | 2698 | 2243 | 0.024981
SILVERADO 21023010 | SILVERADO 2102 | NORTH BAY | 3.5284 | 66.7535 | 84.82% | 0 | 1 | 27.23% | 0% | 0 | 0.018454 | 1 | 1.79 | 0.033032 | Low | Low | Low | 2699 | 2467 | 0.018454
STONE CORRAL 11107784F | STONE CORRAL 1110 | FRESNO | 0.37155 | 63.2273 | 64.55% | 0 | 0 | 7.804% | 0% | 0 | 0.012359 | 1 | 2.6713 | 0.033015 | Low | Low | Medium | 2700 | 2779 | 0.012359
LAS POSITAS 2108MR190 | LAS POSITAS 2108 | MISSION | 1.1924 | 39.2847 | 52.56% | 0 | 0 | 10.54% | 0% | 0 | 0.011177 | 1 | 2.9514 | 0.032988 | Low | Low | Medium | 2701 | 2858 | 0.011177
EDES 1112CB | EDES 1112 | EAST BAY | 0.77646 | 10 | 11.31% | 0 | 0 | 52.35% | 0% | 0 | 0.0099087 | 1 | 3.3253 | 0.032949 | Low | Low | High | 2702 | 2933 | 0.0099087
SAN MIGUEL 1106CB | SAN MIGUEL 1106 | LOS PADRES | 36.8861 | 40.1614 | 99.45% | 1 | 6 | 63.1% | 0% | 0 | 0.035909 | 1 | 0.91469 | 0.032845 | Medium | Medium | Low | 2703 | 1935 | 0.035909
WALDO 0401CB | WALDO 0401 | EAST BAY | 1.6612 | 10 | 12.79% | 0 | 1 | 29.42% | 0% | 0 | 0.0071421 | 1 | 4.5981 | 0.03284 | Low | Low | High | 2704 | 3050 | 0.0071421
BURNEY 11011322 | BURNEY 1101 | NORTH VALLEY | 16.3381 | 29.8396 | 61.19% | 0 | 0 | 87.48% | 0% | 0 | 0.021071 | 1 | 1.5564 | 0.032794 | Low | Low | Low | 2705 | 2365 | 0.021071
BIG MEADOWS 21012476 | BIG MEADOWS 2101 | NORTH VALLEY | 4.675 | 24.1427 | 65.6% | 4 | 4 | 53.74% | 0% | 0 | 0.017254 | 1 | 1.8966 | 0.032724 | Low | Low | Low | 2706 | 2520 | 0.017254
POINT MORETTI 110112122 | POINT MORETTI 1101 | CENTRAL COAST | 6.8941 | 11.1834 | 26.23% | 14 | 1 | 86.19% | 0% | 0 | 0.019307 | 1 | 1.689 | 0.03261 | Low | Low | Low | 2707 | 2430 | 0.019307
SAN RAFAEL 11042235 | SAN RAFAEL 1104 | NORTH BAY | 0.29854 | 10 | 0% | 0 | 1 | 34.56% | 0% | 0 | 0.0067695 | 1 | 4.8094 | 0.032557 | Low | Low | High | 2708 | 3065 | 0.0067695
LINCOLN 11042072 | LINCOLN 1104 | SIERRA | 0.13391 | 10 | 100% | 0 | 0 | 0.7885% | 0% | 0 | 0.010742 | 1 | 3.0303 | 0.032552 | Low | Low | Medium | 2709 | 2887 | 0.010742
TASSAJARA 2109CB | TASSAJARA 2109 | DIABLO | 0.80761 | 10 | 0% | 0 | 4 | 46.43% | 0% | 0 | 0.0081085 | 1 | 4.0127 | 0.032537 | Low | Low | High | 2710 | 3009 | 0.0081085
OCEANO 1105V44 | OCEANO 1105 | LOS PADRES | 0.92167 | 10 | 6.253% | 0 | 2 | 80.43% | 0% | 0 | 0.011472 | 1 | 2.8318 | 0.032488 | Low | Low | Medium | 2711 | 2837 | 0.011472
POINT ARENA 11013702 | POINT ARENA 1101 | HUMBOLDT | 4.3225 | 19.0711 | 4.681% | 4 | 1 | 86.66% | 0% | 0 | 0.013218 | 1 | 2.4572 | 0.03248 | Low | Low | Medium | 2712 | 2703 | 0.013218
PURISIMA 110149394 | PURISIMA 1101 | LOS PADRES | 0.38618 | 10 | 25.81% | 1 | 0 | 4.395% | 0% | 0 | 0.0070193 | 1 | 4.6217 | 0.032441 | Low | Low | High | 2713 | 3054 | 0.0070193
LAKEVILLE 1102530 | LAKEVILLE 1102 | SONOMA | 0.62549 | 57.7371 | 40.72% | 0 | 0 | 12.01% | 0% | 0 | 0.010222 | 1 | 3.1695 | 0.032397 | Low | Low | High | 2714 | 2919 | 0.010222
BALCH NO 1 1101CB | BALCH NO 1 1101 | FRESNO | 8.601 | 30.315 | 65.14% | 0 | 10 | 100% | 0% | 0 | 0.030256 | 1 | 1.07 | 0.032375 | Medium | Medium | Low | 2715 | 2089 | 0.030256
MC KEE 1103XR028 | MC KEE 1103 | SAN JOSE | 2.8083 | 15.9921 | 15.4% | 0 | 2 | 26.81% | 0% | 0 | 0.007561 | 1 | 4.2746 | 0.032321 | Low | Low | High | 2716 | 3027 | 0.007561
ELK CREEK 11012228 | ELK CREEK 1101 | NORTH VALLEY | 3.1012 | 51.6707 | 100% | 0 | 0 | 29.46% | 0% | 0 | 0.018884 | 1 | 1.7101 | 0.032292 | Low | Low | Low | 2717 | 2453 | 0.018884
BERKELEY F 1105CB | BERKELEY F 1105 | EAST BAY | 1.3653 | 10 | 33.54% | 1 | 1 | 21.32% | 0% | 0 | 0.0079134 | 1 | 4.0804 | 0.03229 | Low | Low | High | 2718 | 3014 | 0.0079134
FRENCH GULCH 1102CB | FRENCH GULCH 1102 | NORTH VALLEY | 1.6951 | 33.4949 | 100% | 0 | 1 | 100% | 0% | 0 | 0.034 | 1 | 0.94898 | 0.032265 | Medium | Medium | Low | 2719 | 1975 | 0.034
DUNBAR 110113481 | DUNBAR 1101 | SONOMA | 0.13904 | 10 | 89.93% | 1 | 0 | 12.88% | 0% | 0 | 0.011301 | 1 | 2.8533 | 0.032246 | Low | Low | Medium | 2720 | 2847 | 0.011301
UKIAH 1114528 | UKIAH 1114 | HUMBOLDT | 2.0763 | 22.6279 | 79.13% | 0 | 2 | 16.87% | 0% | 0 | 0.013763 | 1 | 2.3375 | 0.032173 | Low | Low | Medium | 2721 | 2676 | 0.013763
VOLTA 110165764 | VOLTA 1101 | NORTH VALLEY | 10.3627 | 58.9136 | 100% | 1 | 0 | 100% | 0% | 0 | 0.0399 | 1 | 0.80592 | 0.032156 | Medium | Medium | Low | 2722 | 1861 | 0.0399
CLEAR LAKE 11024708 | CLEAR LAKE 1102 | HUMBOLDT | 0.26472 | 10 | 85.61% | 0 | 0 | 9.354% | 0% | 0 | 0.010398 | 1 | 3.0898 | 0.032127 | Low | Low | High | 2723 | 2911 | 0.010398
SNEATH LANE 11015311 | SNEATH LANE 1101 | PENINSULA | 0.49818 | 10 | 0% | 0 | 0 | 44.61% | 0% | 0 | 0.0073269 | 1 | 4.3756 | 0.032059 | Low | Low | High | 2724 | 3039 | 0.0073269
RISING RIVER 1101CB | RISING RIVER 1101 | NORTH VALLEY | 9.43 | 10 | 88.75% | 1 | 2 | 70.58% | 0% | 0 | 0.020612 | 1 | 1.5535 | 0.03202 | Low | Low | Low | 2725 | 2381 | 0.020612
GRASS VALLEY 1103CB | GRASS VALLEY 1103 | SIERRA | 0.095866 | 10 | 0% | 0 | 0 | 80.7% | 0% | 0 | 0.010486 | 1 | 3.0497 | 0.03198 | Low | Low | Medium | 2726 | 2904 | 0.010486
OAKLAND J 1102CR254 | OAKLAND J 1102 | EAST BAY | 1.0198 | 10 | 0% | 1 | 0 | 66.21% | 0% | 0 | 0.0092017 | 1 | 3.4742 | 0.031969 | Low | Low | High | 2727 | 2968 | 0.0092017
OTTER 11022002 | OTTER 1102 | CENTRAL COAST | 8.6285 | 34.3246 | 5.086% | 6 | 1 | 100% | 0% | 0 | 0.025475 | 1 | 1.2546 | 0.03196 | Medium | Medium | Low | 2728 | 2230 | 0.025475
JOLON 11027040 | JOLON 1102 | CENTRAL COAST | 20.3578 | 63.5106 | 29.02% | 0 | 1 | 88.79% | 0% | 0 | 0.02105 | 1 | 1.5142 | 0.031874 | Low | Low | Low | 2729 | 2366 | 0.02105
CAMBRIA 1102W50 | CAMBRIA 1102 | LOS PADRES | 2.1309 | 10 | 10.45% | 0 | 0 | 58.83% | 0% | 0 | 0.010493 | 1 | 3.0352 | 0.031848 | Low | Low | Medium | 2730 | 2903 | 0.010493
PUEBLO 2102CB | PUEBLO 2102 | NORTH BAY | 0.216 | 10 | 100% | 0 | 1 | 1.423% | 0% | 0 | 0.011037 | 1 | 2.8708 | 0.031684 | Low | Low | Medium | 2731 | 2864 | 0.011037
JESSUP 110338864 | JESSUP 1103 | NORTH VALLEY | 0.59204 | 10 | 100% | 1 | 3 | 7.85% | 0% | 0 | 0.012422 | 1 | 2.5473 | 0.031642 | Low | Low | Medium | 2732 | 2775 | 0.012422
GIRVAN 1102CB | GIRVAN 1102 | NORTH VALLEY | 4.7326 | 13.9144 | 68.55% | 4 | 1 | 22.51% | 1.048% | 1 | 0.01158 | 1 | 2.7229 | 0.031532 | Low | Low | Medium | 2733 | 2832 | 0.01158
RESERVATION ROAD 1102CB | RESERVATION ROAD 1102 | CENTRAL COAST | 6.8792 | 54.6073 | 43.73% | 1 | 5 | 38.43% | 0% | 0 | 0.017073 | 1 | 1.8467 | 0.031528 | Low | Low | Low | 2734 | 2525 | 0.017073
SAN RAFAEL 110969860 | SAN RAFAEL 1109 | NORTH BAY | 0.67004 | 10 | 27.57% | 0 | 0 | 26.27% | 0% | 0 | 0.0076522 | 1 | 4.1175 | 0.031508 | Low | Low | High | 2735 | 3024 | 0.0076522
PANORAMA 11021526 | PANORAMA 1102 | NORTH VALLEY | 11.8848 | 23.1923 | 53.04% | 0 | 7 | 67.25% | 0% | 0 | 0.020361 | 1 | 1.5446 | 0.03145 | Low | Low | Low | 2736 | 2390 | 0.020361
FLINT 110140666 | FLINT 1101 | SIERRA | 0.79305 | 10 | 48.92% | 0 | 1 | 27.77% | 0% | 0 | 0.009443 | 1 | 3.3257 | 0.031404 | Low | Low | High | 2737 | 2957 | 0.009443
OLETA 11022642 | OLETA 1102 | STOCKTON | 4.6588 | 10 | 54.08% | 0 | 0 | 100% | 0.8976% | 1 | 0.01998 | 1 | 1.5701 | 0.031371 | Low | Low | Low | 2738 | 2409 | 0.01998
CLAY 11037142 | CLAY 1103 | STOCKTON | 4.4879 | 10 | 67.68% | 2 | 0 | 29.1% | 0% | 0 | 0.012796 | 1 | 2.4498 | 0.031348 | Low | Low | Medium | 2739 | 2726 | 0.012796
FRANKLIN 1104P136 | FRANKLIN 1104 | EAST BAY | 3.8457 | 10 | 0% | 0 | 1 | 65.24% | 0% | 0 | 0.009184 | 1 | 3.4131 | 0.031346 | Low | Low | High | 2740 | 2969 | 0.009184
DIVIDE 110348160 | DIVIDE 1103 | LOS PADRES | 2.2423 | 10 | 32.11% | 0 | 0 | 17.66% | 0% | 0 | 0.010844 | 1 | 2.8904 | 0.031344 | Low | Low | Medium | 2741 | 2879 | 0.010844
JOLON 11027070 | JOLON 1102 | CENTRAL COAST | 4.9443 | 33.893 | 99.18% | 0 | 3 | 30.01% | 0% | 0 | 0.023132 | 1 | 1.3548 | 0.031339 | Medium | Medium | Low | 2742 | 2305 | 0.023132
SANTA YNEZ 1102320270 | SANTA YNEZ 1102 | LOS PADRES | 0.55315 | 10 | 90.55% | 0 | 2 | 19.74% | 0% | 0 | 0.012507 | 1 | 2.5016 | 0.031288 | Low | Low | Medium | 2743 | 2773 | 0.012507
OLEMA 110137074 | OLEMA 1101 | NORTH BAY | 0.013643 | 10 | 100% | 0 | 0 | 4.337% | 0% | 0 | 0.011127 | 1 | 2.8085 | 0.03125 | Low | Low | Medium | 2744 | 2859 | 0.011127
PUTAH CREEK 11058812 | PUTAH CREEK 1105 | SACRAMENTO | 0.75773 | 78.0828 | 100% | 0 | 0 | 1.163% | 0% | 0 | 0.017069 | 1 | 1.8258 | 0.031165 | Low | Low | Low | 2745 | 2526 | 0.017069
PACIFIC GROVE 04222614 | PACIFIC GROVE 0422 | CENTRAL COAST | 0.61996 | 10 | 0% | 1 | 0 | 28.91% | 0% | 0 | 0.007251 | 1 | 4.276 | 0.031005 | Low | Low | High | 2746 | 3044 | 0.007251
WILLITS 1102CB | WILLITS 1102 | HUMBOLDT | 5.2584 | 15.1568 | 26.36% | 0 | 4 | 54.45% | 0% | 0 | 0.01287 | 1 | 2.3959 | 0.030834 | Low | Low | Medium | 2747 | 2719 | 0.01287
SOBRANTE 110142914 | SOBRANTE 1101 | DIABLO | 0.83179 | 10 | 55.86% | 0 | 1 | 20.13% | 0% | 0 | 0.0092648 | 1 | 3.3242 | 0.030798 | Low | Low | High | 2748 | 2966 | 0.0092648
OAKLAND X 1105CB | OAKLAND X 1105 | EAST BAY | 3.475 | 10 | 21.39% | 0 | 3 | 23.79% | 0% | 0 | 0.0086247 | 1 | 3.5708 | 0.030797 | Low | Low | High | 2749 | 2993 | 0.0086247
SAN CARLOS 110436864 | SAN CARLOS 1104 | PENINSULA | 0.3154 | 10 | 0% | 0 | 1 | 37.17% | 0% | 0 | 0.0069476 | 1 | 4.4226 | 0.030727 | Low | Low | High | 2750 | 3056 | 0.0069476
POINT MORETTI 110135874 | POINT MORETTI 1101 | CENTRAL COAST | 0.27376 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.4196 | 0.030718 | Low | Low | Medium | 2751 | 2735 | 0.012695
ROB ROY 210512584 | ROB ROY 2105 | CENTRAL COAST | 3.0913 | 10 | 22.02% | 2 | 1 | 25.72% | 0% | 0 | 0.011337 | 1 | 2.7064 | 0.030682 | Low | Low | Medium | 2752 | 2845 | 0.011337
CHOLAME 2102X06 | CHOLAME 2102 | LOS PADRES | 33.5233 | 47.8201 | 99.99% | 1 | 7 | 63.4% | 0% | 0 | 0.034127 | 1 | 0.89797 | 0.030645 | Medium | Medium | Low | 2753 | 1972 | 0.034127
ZACA 1101CB | ZACA 1101 | LOS PADRES | 7.3177 | 63.5153 | 26.01% | 0 | 1 | 67.25% | 0% | 0 | 0.024613 | 1 | 1.2436 | 0.030608 | Medium | Medium | Low | 2754 | 2254 | 0.024613
BEAR VALLEY 21059570 | BEAR VALLEY 2105 | YOSEMITE | 8.0469 | 57.8177 | 84.85% | 0 | 1 | 100% | 0% | 0 | 0.035385 | 1 | 0.86453 | 0.030591 | Medium | Medium | Low | 2755 | 1949 | 0.035385
VIEJO 220146068 | VIEJO 2201 | CENTRAL COAST | 0.073762 | 10 | 0% | 0 | 0 | 53.15% | 0% | 0 | 0.0079762 | 1 | 3.8343 | 0.030583 | Low | Low | High | 2756 | 3011 | 0.0079762
UPPER LAKE 1101472084 | UPPER LAKE 1101 | HUMBOLDT | 4.5266 | 10 | 55.47% | 0 | 3 | 61.59% | 0% | 0 | 0.016554 | 1 | 1.8437 | 0.030521 | Low | Low | Low | 2757 | 2546 | 0.016554
LOS OSITOS 21027470 | LOS OSITOS 2102 | CENTRAL COAST | 2.5834 | 65.4453 | 76.6% | 0 | 0 | 9.453% | 0% | 0 | 0.014067 | 1 | 2.1688 | 0.030509 | Low | Low | Low | 2758 | 2661 | 0.014067
SANTA YNEZ 1102CB | SANTA YNEZ 1102 | LOS PADRES | 1.3864 | 10 | 42.97% | 0 | 2 | 15.51% | 0% | 0 | 0.010594 | 1 | 2.8741 | 0.030449 | Low | Low | Medium | 2759 | 2901 | 0.010594
BERESFORD 04039154 | BERESFORD 0403 | PENINSULA | 3.1988 | 10 | 17.34% | 4 | 1 | 48.83% | 0% | 0 | 0.0094751 | 1 | 3.2128 | 0.030442 | Low | Low | High | 2760 | 2953 | 0.0094751
SAN BENITO 2104CB | SAN BENITO 2104 | CENTRAL COAST | 4.8064 | 10 | 7.992% | 0 | 0 | 52.81% | 0% | 0 | 0.014395 | 1 | 2.1147 | 0.030441 | Low | Low | Low | 2761 | 2633 | 0.014395
ELECTRA 1102CB | ELECTRA 1102 | STOCKTON | 2.62 | 68.1508 | 1.119% | 0 | 0 | 100% | 0% | 0 | 0.018952 | 1 | 1.606 | 0.030437 | Low | Low | Low | 2762 | 2451 | 0.018952
CARLOTTA 11214045 | CARLOTTA 1121 | HUMBOLDT | 0.14338 | 10 | 100% | 0 | 0 | 7.252% | 0% | 0 | 0.011453 | 1 | 2.6575 | 0.030436 | Low | Low | Medium | 2763 | 2839 | 0.011453
HOPLAND 11011100 | HOPLAND 1101 | HUMBOLDT | 2.6093 | 13.3851 | 100% | 0 | 1 | 39.2% | 0% | 0 | 0.016404 | 1 | 1.8539 | 0.030412 | Low | Low | Low | 2764 | 2555 | 0.016404
REDBUD 1102432 | REDBUD 1102 | HUMBOLDT | 1.3051 | 10 | 69.46% | 0 | 1 | 11.62% | 0% | 0 | 0.0095157 | 1 | 3.1897 | 0.030352 | Low | Low | High | 2765 | 2949 | 0.0095157
WILLITS 1103CB | WILLITS 1103 | HUMBOLDT | 1.4734 | 28.6497 | 64.03% | 0 | 1 | 37.49% | 0% | 0 | 0.015222 | 1 | 1.9923 | 0.030328 | Low | Low | Low | 2766 | 2602 | 0.015222
JOLON 11027002 | JOLON 1102 | CENTRAL COAST | 7.9112 | 56.9708 | 100% | 0 | 0 | 43.93% | 0% | 0 | 0.025691 | 1 | 1.1804 | 0.030327 | Medium | Medium | Low | 2767 | 2226 | 0.025691
CLARK ROAD 11022044 | CLARK ROAD 1102 | NORTH VALLEY | 5.5376 | 29.0224 | 29.16% | 0 | 3 | 44.24% | 0% | 0 | 0.018991 | 1 | 1.5914 | 0.030222 | Low | Low | Low | 2768 | 2448 | 0.018991
PEORIA 1704 | PEORIA 1704 | YOSEMITE | 0.12912 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.3748 | 0.030148 | Low | Low | Medium | 2769 | 2735 | 0.012695
OAKLAND J 1102CR252 | OAKLAND J 1102 | EAST BAY | 1.1914 | 10 | 48.94% | 0 | 1 | 19.56% | 0% | 0 | 0.0087055 | 1 | 3.4603 | 0.030124 | Low | Low | High | 2770 | 2990 | 0.0087055
RIO DEL MAR 0402CB | RIO DEL MAR 0402 | CENTRAL COAST | 1.6949 | 10 | 6.344% | 2 | 0 | 47.04% | 0% | 0 | 0.0081166 | 1 | 3.7099 | 0.030112 | Low | Low | High | 2771 | 3008 | 0.0081166
HARTLEY 1101738 | HARTLEY 1101 | HUMBOLDT | 3.053 | 10 | 42.13% | 1 | 2 | 37.87% | 0% | 0 | 0.011659 | 1 | 2.581 | 0.030092 | Low | Low | Medium | 2772 | 2824 | 0.011659
ANTLER 11011612 | ANTLER 1101 | NORTH VALLEY | 8.3928 | 10 | 100% | 2 | 6 | 90.86% | 15.08% | 1 | 0.043586 | 1 | 0.69008 | 0.030078 | Medium | Medium | Low | 2773 | 1786 | 0.043586
VALLEY VIEW 1106P128 | VALLEY VIEW 1106 | EAST BAY | 0.72514 | 10 | 44.15% | 0 | 0 | 28.68% | 0% | 0 | 0.0089763 | 1 | 3.3463 | 0.030037 | Low | Low | High | 2774 | 2978 | 0.0089763
FORT ORD 210637286 | FORT ORD 2106 | CENTRAL COAST | 1.5847 | 10 | 0% | 0 | 4 | 43% | 0% | 0 | 0.010213 | 1 | 2.936 | 0.029984 | Low | Low | Medium | 2775 | 2920 | 0.010213
SAN MIGUEL 1104R58 | SAN MIGUEL 1104 | LOS PADRES | 9.7655 | 26.7568 | 99.18% | 0 | 1 | 40.61% | 0% | 0 | 0.018077 | 1 | 1.6551 | 0.029918 | Low | Low | Low | 2776 | 2485 | 0.018077
MORAGA 110381146 | MORAGA 1103 | DIABLO | 0.81099 | 10 | 24.05% | 0 | 0 | 14.46% | 0% | 0 | 0.00661 | 1 | 4.5238 | 0.029902 | Low | Low | High | 2777 | 3072 | 0.00661
UKIAH 111472990 | UKIAH 1114 | HUMBOLDT | 0.7336 | 10 | 33.42% | 1 | 5 | 22.74% | 0% | 0 | 0.0099473 | 1 | 3.0013 | 0.029855 | Low | Low | Medium | 2778 | 2930 | 0.0099473
MORRO BAY 1101V66 | MORRO BAY 1101 | LOS PADRES | 3.6398 | 32.9293 | 34.81% | 0 | 0 | 22.6% | 18.48% | 0 | 0.01232 | 1 | 2.4197 | 0.029811 | Low | Low | Medium | 2779 | 2783 | 0.01232
SAN CARLOS 1103 | SAN CARLOS 1103 | PENINSULA | 0.013694 | 10 | 0% | 0 | 0 | 32.32% | 0% | 0 | 0.0064833 | 1 | 4.5959 | 0.029797 | Low | Low | High | 2780 | 3080 | 0.0064833
FORT ORD 210736596 | FORT ORD 2107 | CENTRAL COAST | 2.9621 | 10 | 1.434% | 0 | 3 | 23.77% | 0% | 0 | 0.0095449 | 1 | 3.1211 | 0.029791 | Low | Low | High | 2781 | 2948 | 0.0095449
LAS GALLINAS A 11041220 | LAS GALLINAS A 1104 | NORTH BAY | 1.0215 | 10 | 17.87% | 0 | 0 | 20.99% | 0% | 0 | 0.0076561 | 1 | 3.869 | 0.029621 | Low | Low | High | 2782 | 3023 | 0.0076561
CALAVERAS CEMENT 110113424 | CALAVERAS CEMENT 1101 | STOCKTON | 1.1628 | 27.7873 | 54.51% | 0 | 1 | 32.26% | 0% | 0 | 0.011657 | 1 | 2.5395 | 0.029604 | Low | Low | Medium | 2783 | 2825 | 0.011657
LOYOLA 1102LL12 | LOYOLA 1102 | DE ANZA | 0.10967 | 10 | 100% | 0 | 0 | 1.811% | 0% | 0 | 0.010852 | 1 | 2.7206 | 0.029523 | Low | Low | Medium | 2784 | 2877 | 0.010852
VIEJO 220285904 | VIEJO 2202 | CENTRAL COAST | 0.44182 | 10 | 5.103% | 1 | 0 | 22.34% | 0% | 0 | 0.007082 | 1 | 4.1688 | 0.029523 | Low | Low | High | 2785 | 3051 | 0.007082
ANDERSON 1103CB | ANDERSON 1103 | NORTH VALLEY | 3.2551 | 15.9196 | 80.29% | 1 | 2 | 15.59% | 0% | 0 | 0.011642 | 1 | 2.5308 | 0.029465 | Low | Low | Medium | 2786 | 2826 | 0.011642
MIRABEL 1102206 | MIRABEL 1102 | SONOMA | 1.6804 | 10 | 37.83% | 0 | 1 | 13.09% | 0% | 0 | 0.0097141 | 1 | 3.0324 | 0.029457 | Low | Low | Medium | 2787 | 2943 | 0.0097141
PASO ROBLES 110355374 | PASO ROBLES 1103 | LOS PADRES | 2.104 | 28.3586 | 87.29% | 0 | 2 | 19.75% | 0% | 0 | 0.013788 | 1 | 2.1323 | 0.0294 | Low | Low | Low | 2788 | 2675 | 0.013788
ECHO SUMMIT 1101344250 | ECHO SUMMIT 1101 | (blank) | 0.80694 | 10 | 100% | 1 | 0 | 14.32% | 0% | 0 | 0.014197 | 1 | 2.0707 | 0.029398 | Low | Low | Low | 2789 | 2651 | 0.014197
DEL MONTE 210332886 | DEL MONTE 2103 | CENTRAL COAST | 1.2598 | 10 | 0% | 5 | 1 | 31.74% | 0% | 0 | 0.0091616 | 1 | 3.2009 | 0.029325 | Low | Low | High | 2790 | 2970 | 0.0091616
BIG RIVER 11012989 | BIG RIVER 1101 | HUMBOLDT | 0.072968 | 10 | 100% | 0 | 0 | 6.918% | 0% | 0 | 0.011415 | 1 | 2.5683 | 0.029316 | Low | Low | Medium | 2791 | 2841 | 0.011415
PETALUMA C 1108630 | PETALUMA C 1108 | SONOMA | 1.2522 | 54.3048 | 11.61% | 0 | 2 | 29.56% | 0% | 0 | 0.0097687 | 1 | 3 | 0.029306 | Low | Low | Medium | 2792 | 2942 | 0.0097687
WILLITS 1104CB | WILLITS 1104 | HUMBOLDT | 2.2442 | 16.2086 | 22.49% | 1 | 7 | 29.86% | 0% | 0 | 0.012113 | 1 | 2.4118 | 0.029214 | Low | Low | Medium | 2793 | 2802 | 0.012113
SOLEDAD 2101CB | SOLEDAD 2101 | CENTRAL COAST | 1.1091 | 10 | 100% | 0 | 0 | 7.451% | 0% | 0 | 0.011475 | 1 | 2.5437 | 0.02919 | Low | Low | Medium | 2794 | 2836 | 0.011475
OAKLAND J 1106CR330 | OAKLAND J 1106 | EAST BAY | 0.49535 | 10 | 40.09% | 0 | 0 | 20.57% | 0% | 0 | 0.0091449 | 1 | 3.1852 | 0.029128 | Low | Low | High | 2795 | 2972 | 0.0091449
POINT MORETTI 11015074 | POINT MORETTI 1101 | CENTRAL COAST | 1.726 | 19.9026 | 1.553% | 2 | 1 | 56.7% | 0% | 0 | 0.009381 | 1 | 3.1003 | 0.029084 | Low | Low | High | 2796 | 2961 | 0.009381
BUELLTON 1101753644 | BUELLTON 1101 | LOS PADRES | 0.0028488 | 10 | 100% | 0 | 0 | 0.4009% | 0% | 0 | 0.010701 | 1 | 2.7101 | 0.029001 | Low | Low | Medium | 2797 | 2894 | 0.010701
SAN LUIS OBISPO 1107CB | SAN LUIS OBISPO 1107 | LOS PADRES | 0.84728 | 10 | 25.92% | 0 | 0 | 48.86% | 0% | 0 | 0.0094493 | 1 | 3.0675 | 0.028986 | Low | Low | Medium | 2798 | 2955 | 0.0094493
OAKLAND J 1106CR164 | OAKLAND J 1106 | EAST BAY | 1.4865 | 10 | 46.08% | 2 | 1 | 22.66% | 0% | 0 | 0.0090035 | 1 | 3.2151 | 0.028947 | Low | Low | High | 2799 | 2975 | 0.0090035
WILDWOOD 11011454 | WILDWOOD 1101 | NORTH VALLEY | 7.7462 | 36.802 | 100% | 0 | 1 | 100% | 0% | 0 | 0.034751 | 1 | 0.83154 | 0.028897 | Medium | Medium | Low | 2800 | 1955 | 0.034751
GARBERVILLE 11024744 | GARBERVILLE 1102 | HUMBOLDT | 16.8626 | 50.888 | 35.22% | 7 | 3 | 83.26% | 0% | 0 | 0.047692 | 1 | 0.60586 | 0.028895 | Medium | Medium | Low | 2801 | 1709 | 0.047692
ATASCADERO 1101CB | ATASCADERO 1101 | LOS PADRES | 0.44126 | 10 | 57.34% | 0 | 0 | 21.26% | 0% | 0 | 0.0092885 | 1 | 3.1059 | 0.028849 | Low | Low | High | 2802 | 2964 | 0.0092885
LAS GALLINAS A 1104304 | LAS GALLINAS A 1104 | NORTH BAY | 0.14237 | 10 | 35.52% | 0 | 1 | 5.697% | 0% | 0 | 0.0067954 | 1 | 4.2336 | 0.028769 | Low | Low | High | 2803 | 3062 | 0.0067954
HOLLISTER 210441808 | HOLLISTER 2104 | CENTRAL COAST | 0.1888 | 10 | 100% | 0 | 0 | 1.735% | 0% | 0 | 0.010843 | 1 | 2.6518 | 0.028755 | Low | Low | Medium | 2804 | 2880 | 0.010843
RAWSON 110385334 | RAWSON 1103 | NORTH VALLEY | 2.3781 | 53.7562 | 78.76% | 0 | 1 | 24.97% | 0% | 0 | 0.017954 | 1 | 1.5952 | 0.028642 | Low | Low | Low | 2805 | 2492 | 0.017954
WYANDOTTE 11101952 | WYANDOTTE 1110 | NORTH VALLEY | 0.44853 | 10 | 100% | 0 | 0 | 5.144% | 0% | 0 | 0.011216 | 1 | 2.5511 | 0.028613 | Low | Low | Medium | 2806 | 2853 | 0.011216
HOLLISTER 21024780 | HOLLISTER 2102 | CENTRAL COAST | 2.8684 | 10 | 66.05% | 0 | 1 | 19.03% | 0% | 0 | 0.011367 | 1 | 2.5162 | 0.028602 | Low | Low | Medium | 2807 | 2844 | 0.011367
VIEJO 22029089 | VIEJO 2202 | CENTRAL COAST | 0.44699 | 10 | 0% | 1 | 3 | 26.75% | 0% | 0 | 0.0075545 | 1 | 3.7807 | 0.028562 | Low | Low | High | 2808 | 3028 | 0.0075545
HOOPA 110193038 | HOOPA 1101 | HUMBOLDT | 0.1684 | 40.7085 | 100% | 0 | 1 | 6.029% | 0% | 0 | 0.014214 | 1 | 2.0078 | 0.028539 | Low | Low | Low | 2809 | 2649 | 0.014214
ATASCADERO 1101A22 | ATASCADERO 1101 | LOS PADRES | 0.48233 | 10 | 88.74% | 0 | 1 | 3.681% | 0% | 0 | 0.010296 | 1 | 2.761 | 0.028426 | Low | Low | Medium | 2810 | 2915 | 0.010296
VIEJO 22049110 | VIEJO 2204 | CENTRAL COAST | 0.89252 | 10 | 16.91% | 0 | 0 | 20.66% | 0% | 0 | 0.0066316 | 1 | 4.2831 | 0.028404 | Low | Low | High | 2811 | 3071 | 0.0066316
ROB ROY 210410930 | ROB ROY 2104 | CENTRAL COAST | 1.4484 | 10 | 54.81% | 0 | 0 | 12.82% | 0% | 0 | 0.0083664 | 1 | 3.3859 | 0.028328 | Low | Low | High | 2812 | 3000 | 0.0083664
GREEN VALLEY 210112130 | GREEN VALLEY 2101 | CENTRAL COAST | 1.2937 | 17.054 | 59.16% | 0 | 0 | 7.411% | 0% | 0 | 0.0086186 | 1 | 3.2862 | 0.028323 | Low | Low | High | 2813 | 2995 | 0.0086186
HARTLEY 110186876 | HARTLEY 1101 | HUMBOLDT | 2.3866 | 10 | 49.85% | 0 | 0 | 28.66% | 0% | 0 | 0.0094023 | 1 | 2.9982 | 0.02819 | Low | Low | Medium | 2814 | 2960 | 0.0094023
EL CERRITO G 1111CB | EL CERRITO G 1111 | EAST BAY | 0.94606 | 10 | 6.246% | 0 | 0 | 7.497% | 0% | 0 | 0.0053291 | 1 | 5.2654 | 0.028059 | Low | Low | High | 2815 | 3131 | 0.0053291
VINEYARD 2107CB | VINEYARD 2107 | MISSION | 1.6942 | 13.0214 | 48.11% | 0 | 2 | 16.67% | 0% | 0 | 0.0087566 | 1 | 3.1976 | 0.028 | Low | Low | High | 2816 | 2985 | 0.0087566
TEMPLETON 2113R82 | TEMPLETON 2113 | LOS PADRES | 34.6176 | 62.3861 | 93.76% | 0 | 4 | 50.19% | 6.458% | 0 | 0.03681 | 1 | 0.75794 | 0.0279 | Medium | Medium | Low | 2817 | 1922 | 0.03681
MERCED FALLS 110287352 | MERCED FALLS 1102 | YOSEMITE | 26.2614 | 32.8974 | 99.99% | 0 | 0 | 98.93% | 0% | 0 | 0.054765 | 1 | 0.50877 | 0.027863 | Medium | Medium | Low | 2818 | 1628 | 0.054765
GUALALA 1111CB | GUALALA 1111 | HUMBOLDT | 3.8671 | 10 | 20.51% | 4 | 5 | 100% | 0% | 0 | 0.017522 | 1 | 1.59 | 0.02786 | Low | Low | Low | 2819 | 2511 | 0.017522
BRENTWOOD 2105502672 | BRENTWOOD 2105 | DIABLO | 1.383 | 10 | 100% | 0 | 0 | 7.371% | 0% | 0 | 0.011466 | 1 | 2.4116 | 0.027652 | Low | Low | Medium | 2820 | 2838 | 0.011466
PEORIA 17019811 | PEORIA 1701 | YOSEMITE | 5.5301 | 39.6322 | 92.09% | 0 | 0 | 62.43% | 0% | 0 | 0.022586 | 1 | 1.223 | 0.027623 | Medium | Medium | Low | 2821 | 2319 | 0.022586
MESA 1103M92 | MESA 1103 | LOS PADRES | 1.0274 | 49.2008 | 44.21% | 0 | 0 | 12.96% | 0% | 0 | 0.010021 | 1 | 2.7565 | 0.027622 | Low | Low | Medium | 2822 | 2928 | 0.010021
STAFFORD 110242542 | STAFFORD 1102 | NORTH BAY | 0.92749 | 10 | 53.57% | 0 | 0 | 26.56% | 0% | 0 | 0.0094932 | 1 | 2.9041 | 0.027569 | Low | Low | Medium | 2823 | 2951 | 0.0094932
PURISIMA 1101Y42 | PURISIMA 1101 | LOS PADRES | 0.33998 | 72.2951 | 27.05% | 0 | 0 | 2.02% | 0% | 0 | 0.010429 | 1 | 2.6418 | 0.02755 | Low | Low | Medium | 2824 | 2908 | 0.010429
FLINT 1101CB | FLINT 1101 | SIERRA | 0.81732 | 10 | 11.07% | 0 | 2 | 31.46% | 0% | 0 | 0.008378 | 1 | 3.2795 | 0.027475 | Low | Low | High | 2825 | 2998 | 0.008378
GRASS VALLEY 110358498 | GRASS VALLEY 1103 | SIERRA | 0.54343 | 10 | 37.4% | 0 | 2 | 23.91% | 0% | 0 | 0.0096407 | 1 | 2.8446 | 0.027424 | Low | Low | Medium | 2826 | 2945 | 0.0096407
CAYUCOS 11014701 | CAYUCOS 1101 | LOS PADRES | 2.0826 | 72.227 | 28.46% | 1 | 0 | 23.77% | 0% | 0 | 0.011613 | 1 | 2.3562 | 0.027363 | Low | Low | Medium | 2827 | 2829 | 0.011613
ELK CREEK 11012106 | ELK CREEK 1101 | NORTH VALLEY | 13.2055 | 80.5547 | 100% | 0 | 1 | 100% | 0% | 0 | 0.052586 | 1 | 0.52019 | 0.027355 | Medium | Medium | Low | 2828 | 1655 | 0.052586
LUCERNE 11031280 | LUCERNE 1103 | HUMBOLDT | 8.886 | 18.4647 | 53.77% | 0 | 7 | 37.48% | 0% | 0 | 0.012974 | 1 | 2.1053 | 0.027314 | Low | Low | Low | 2829 | 2714 | 0.012974
SAN RAFAEL 1106837 | SAN RAFAEL 1106 | NORTH BAY | 0.43527 | 10 | 0% | 0 | 2 | 28.12% | 0% | 0 | 0.0074019 | 1 | 3.69 | 0.027313 | Low | Low | High | 2830 | 3035 | 0.0074019
RESERVATION ROAD 11023032 | RESERVATION ROAD 1102 | CENTRAL COAST | 1.7351 | 10 | 40.39% | 0 | 1 | 17.91% | 0% | 0 | 0.010406 | 1 | 2.6242 | 0.027307 | Low | Low | Medium | 2831 | 2910 | 0.010406
CORNING 110135974 | CORNING 1101 | NORTH VALLEY | 0.83179 | 10 | 47.68% | 0 | 0 | 100% | 0% | 0 | 0.02429 | 1 | 1.1214 | 0.027239 | Medium | Medium | Low | 2832 | 2268 | 0.02429
GEYSERVILLE 1101122 | GEYSERVILLE 1101 | SONOMA | 3.5712 | 48.4332 | 60.55% | 0 | 3 | 18.96% | 0% | 0 | 0.012864 | 1 | 2.1153 | 0.027211 | Low | Low | Low | 2833 | 2720 | 0.012864
SOLEDAD 21027008 | SOLEDAD 2102 | CENTRAL COAST | 1.2631 | 69.0048 | 38.01% | 0 | 0 | 6.974% | 0% | 0 | 0.011715 | 1 | 2.322 | 0.027202 | Low | Low | Medium | 2834 | 2820 | 0.011715
COARSEGOLD 21036110 | COARSEGOLD 2103 | YOSEMITE | 9.9772 | 20.6713 | 95.13% | 0 | 5 | 33.47% | 0% | 0 | 0.016997 | 1 | 1.5993 | 0.027183 | Low | Low | Low | 2835 | 2529 | 0.016997
FRUITLAND 11418860 | FRUITLAND 1141 | HUMBOLDT | 2.4992 | 72.7282 | 25.93% | 4 | 0 | 65.81% | 0% | 0 | 0.01798 | 1 | 1.5096 | 0.027143 | Low | Low | Low | 2836 | 2489 | 0.01798
JOLON 1102CB | JOLON 1102 | CENTRAL COAST | 23.7338 | 63.1412 | 51.5% | 0 | 1 | 99.01% | 0% | 0 | 0.02781 | 1 | 0.97488 | 0.027111 | Medium | Medium | Low | 2837 | 2168 | 0.02781
SUMMIT 1101CB | SUMMIT 1101 | SIERRA | 0.12475 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.016863 | 1 | 1.5975 | 0.026939 | Low | Low | Low | 2838 | 2534 | 0.016863
CAROLANDS 04049026 | CAROLANDS 0404 | PENINSULA | 0.27754 | 10 | 28.62% | 0 | 0 | 5.507% | 0% | 0 | 0.0071679 | 1 | 3.7571 | 0.026931 | Low | Low | High | 2839 | 3049 | 0.0071679
SUMMIT 11016627 | SUMMIT 1101 | SIERRA | 0.56142 | 10 | 45.61% | 0 | 0 | 100% | 0% | 0 | 0.01839 | 1 | 1.4632 | 0.026909 | Low | Low | Low | 2840 | 2470 | 0.01839
MARIPOSA 210210250 | MARIPOSA 2102 | YOSEMITE | 0.04003 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.119 | 0.026901 | Low | Low | Low | 2841 | 2735 | 0.012695
FRANKLIN 1104CB | FRANKLIN 1104 | EAST BAY | 0.64777 | 10 | 0% | 0 | 2 | 12.31% | 0% | 0 | 0.0072216 | 1 | 3.7113 | 0.026802 | Low | Low | High | 2842 | 3046 | 0.0072216
PRUNEDALE 11103716 | PRUNEDALE 1110 | CENTRAL COAST | 0.046537 | 10 | 100% | 0 | 0 | 0.3534% | 0% | 0 | 0.010696 | 1 | 2.4997 | 0.026736 | Low | Low | Medium | 2843 | 2895 | 0.010696
TEMPLETON 2113A32 | TEMPLETON 2113 | LOS PADRES | 0.77097 | 10 | 66.93% | 0 | 0 | 13.18% | 0% | 0 | 0.0092713 | 1 | 2.8821 | 0.026721 | Low | Low | Medium | 2844 | 2965 | 0.0092713
SNEATH LANE 1107CB | SNEATH LANE 1107 | PENINSULA | 0.3748 | 10 | 41.65% | 0 | 1 | 9.682% | 0% | 0 | 0.0074343 | 1 | 3.594 | 0.026719 | Low | Low | High | 2845 | 3034 | 0.0074343
WYANDOTTE 1107CB | WYANDOTTE 1107 | NORTH VALLEY | 1.0691 | 10 | 31.7% | 0 | 1 | 7.068% | 0% | 0 | 0.0066762 | 1 | 3.9827 | 0.026589 | Low | Low | High | 2846 | 3067 | 0.0066762
BEAR VALLEY 21054170 | BEAR VALLEY 2105 | YOSEMITE | 9.5178 | 57.2029 | 100% | 3 | 1 | 100% | 0% | 0 | 0.041292 | 1 | 0.64305 | 0.026553 | Medium | Medium | Low | 2847 | 1830 | 0.041292
PEORIA 170488630 | PEORIA 1704 | YOSEMITE | 0.77831 | 38.0661 | 100% | 0 | 0 | 100% | 0% | 0 | 0.050412 | 1 | 0.52663 | 0.026548 | Medium | Medium | Low | 2848 | 1678 | 0.050412
TRES PINOS 11114032 | TRES PINOS 1111 | CENTRAL COAST | 0.10269 | 70 | 100% | 0 | 0 | 0.5446% | 0% | 0 | 0.018321 | 1 | 1.4487 | 0.026542 | Low | Low | Low | 2849 | 2474 | 0.018321
BRENTWOOD 210596324 | BRENTWOOD 2105 | DIABLO | 0.37122 | 10 | 0% | 0 | 0 | 76.98% | 0% | 0 | 0.010106 | 1 | 2.6232 | 0.02651 | Low | Low | Medium | 2850 | 2924 | 0.010106
PEORIA 1701CB | PEORIA 1701 | YOSEMITE | 8.8374 | 31.1758 | 54.24% | 0 | 6 | 100% | 0% | 0 | 0.037882 | 1 | 0.69967 | 0.026505 | Medium | Medium | Low | 2851 | 1900 | 0.037882
SONOMA 1107126 | SONOMA 1107 | SONOMA | 2.2583 | 59.5559 | 29.29% | 0 | 1 | 10.13% | 0% | 0 | 0.009446 | 1 | 2.8041 | 0.026487 | Low | Low | Medium | 2852 | 2956 | 0.009446
JOLON 11027004 | JOLON 1102 | CENTRAL COAST | 5.4816 | 47.887 | 100% | 0 | 0 | 27.2% | 0% | 0 | 0.020525 | 1 | 1.2884 | 0.026445 | Low | Low | Low | 2853 | 2385 | 0.020525
ELK 11014628 | ELK 1101 | HUMBOLDT | 2.8486 | 10 | 0% | 0 | 7 | 69.22% | 0% | 0 | 0.012349 | 1 | 2.1397 | 0.026424 | Low | Low | Low | 2854 | 2781 | 0.012349
CLOVERDALE 1102670 | CLOVERDALE 1102 | SONOMA | 0.27521 | 10 | 95.35% | 0 | 0 | 6.733% | 0% | 0 | 0.01097 | 1 | 2.3989 | 0.026316 | Low | Low | Medium | 2855 | 2868 | 0.01097
NOVATO 11041282 | NOVATO 1104 | NORTH BAY | 1.3064 | 10 | 9.821% | 0 | 6 | 28.52% | 0% | 0 | 0.008753 | 1 | 3.0035 | 0.026289 | Low | Low | Medium | 2856 | 2987 | 0.008753
HICKS 1116LB16 | HICKS 1116 | SAN JOSE | 1.4512 | 10 | 12.53% | 1 | 1 | 15.83% | 0% | 0 | 0.0072028 | 1 | 3.6384 | 0.026207 | Low | Low | High | 2857 | 3048 | 0.0072028
LOS GATOS 1101CB | LOS GATOS 1101 | DE ANZA | 0.83125 | 10 | 32.44% | 0 | 1 | 21.19% | 0% | 0 | 0.0077301 | 1 | 3.3892 | 0.026199 | Low | Low | High | 2858 | 3020 | 0.0077301
POTTER VALLEY P H 110537476 | POTTER VALLEY P H 1105 | HUMBOLDT | 0.5064 | 62.972 | 86.61% | 0 | 3 | 5.941% | 0% | 0 | 0.015424 | 1 | 1.6964 | 0.026166 | Low | Low | Low | 2859 | 2592 | 0.015424
LINCOLN 110195756 | LINCOLN 1101 | SIERRA | 3.5302 | 10.7023 | 65.54% | 2 | 0 | 19.54% | 0% | 0 | 0.010072 | 1 | 2.5936 | 0.026122 | Low | Low | Medium | 2860 | 2925 | 0.010072
FAIRVIEW 2207M501R | FAIRVIEW 2207 | DIABLO | 1.376 | 10 | 11.91% | 1 | 2 | 29.22% | 0% | 0 | 0.0083598 | 1 | 3.1246 | 0.026121 | Low | Low | High | 2861 | 3001 | 0.0083598
COAST RD 0401CB | COAST RD 0401 | CENTRAL COAST | 0.04709 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 2.0553 | 0.026093 | Low | Low | Low | 2862 | 2735 | 0.012695
GONZALES 11033096 | GONZALES 1103 | CENTRAL COAST | 1.0413 | 57.173 | 49.23% | 0 | 0 | 5.766% | 0% | 0 | 0.011709 | 1 | 2.2241 | 0.026042 | Low | Low | Low | 2863 | 2821 | 0.011709
CASTRO VALLEY 1106MR233 | CASTRO VALLEY 1106 | MISSION | 0.14387 | 10 | 11.99% | 0 | 0 | 22.61% | 0% | 0 | 0.0064943 | 1 | 3.9938 | 0.025937 | Low | Low | High | 2864 | 3079 | 0.0064943
CARLOTTA 1121CB | CARLOTTA 1121 | HUMBOLDT | 3.8375 | 25.0692 | 63.58% | 0 | 0 | 16.59% | 0% | 0 | 0.010334 | 1 | 2.4931 | 0.025765 | Low | Low | Medium | 2865 | 2914 | 0.010334
PETALUMA C 1109CB | PETALUMA C 1109 | SONOMA | 0.77473 | 10 | 39.24% | 0 | 1 | 15.77% | 0% | 0 | 0.007744 | 1 | 3.3257 | 0.025754 | Low | Low | High | 2866 | 3019 | 0.007744
PAUL SWEET 210510290 | PAUL SWEET 2105 | CENTRAL COAST | 0.48079 | 10 | 22.97% | 0 | 0 | 8.329% | 0% | 0 | 0.0061637 | 1 | 4.1772 | 0.025747 | Low | Low | High | 2867 | 3097 | 0.0061637
FORT BRAGG A 1102CB | FORT BRAGG A 1102 | HUMBOLDT | 1.663 | 13.8095 | 19.07% | 2 | 1 | 29% | 0% | 0 | 0.0078888 | 1 | 3.2475 | 0.025619 | Low | Low | High | 2868 | 3015 | 0.0078888
SNEATH LANE 110748338 | SNEATH LANE 1107 | PENINSULA | 0.48719 | 10 | 2.1% | 0 | 0 | 45.41% | 0% | 0 | 0.0075134 | 1 | 3.4081 | 0.025607 | Low | Low | High | 2869 | 3030 | 0.0075134
PANORAMA 1102CB | PANORAMA 1102 | NORTH VALLEY | 0.071747 | 10 | 100% | 0 | 0 | 0.6421% | 0% | 0 | 0.010727 | 1 | 2.3856 | 0.025589 | Low | Low | Medium | 2870 | 2890 | 0.010727
STONE CORRAL 11107320 | STONE CORRAL 1110 | FRESNO | 1.9474 | 22.4898 | 48.09% | 0 | 0 | 8.248% | 0% | 0 | 0.010731 | 1 | 2.3816 | 0.025558 | Low | Low | Medium | 2871 | 2889 | 0.010731
ALTO 1123CB | ALTO 1123 | NORTH BAY | 2.3955 | 10 | 3.352% | 0 | 0 | 39.61% | 4.121% | 0 | 0.0076595 | 1 | 3.3336 | 0.025533 | Low | Low | High | 2872 | 3022 | 0.0076595
ELK 11011298 | ELK 1101 | HUMBOLDT | 13.5042 | 33.0971 | 18.55% | 6 | 11 | 83.72% | 0% | 0 | 0.022711 | 1 | 1.1193 | 0.025419 | Medium | Medium | Low | 2873 | 2316 | 0.022711
TRIDAM POWERHOUSE 2101CB | TRIDAM POWERHOUSE 2101 | YOSEMITE | 0.050313 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.89044 | 0.025388 | Medium | Medium | Low | 2874 | 2132 | 0.028512
OTTER 11022012 | OTTER 1102 | CENTRAL COAST | 9.1781 | 41.691 | 0% | 3 | 4 | 91.18% | 0% | 0 | 0.018558 | 1 | 1.3664 | 0.025359 | Low | Low | Low | 2875 | 2462 | 0.018558
ARLINGTON 0401CB | ARLINGTON 0401 | EAST BAY | 0.76473 | 10 | 0% | 0 | 1 | 19.15% | 0% | 0 | 0.005806 | 1 | 4.3631 | 0.025332 | Low | Low | High | 2876 | 3112 | 0.005806
FITCH MOUNTAIN 1113154 | FITCH MOUNTAIN 1113 | SONOMA | 2.1793 | 18.0666 | 70.63% | 0 | 0 | 11.51% | 0% | 0 | 0.0099274 | 1 | 2.5363 | 0.025179 | Low | Low | Medium | 2877 | 2931 | 0.0099274
OCEANO 1106V28 | OCEANO 1106 | LOS PADRES | 1.0201 | 10 | 22.73% | 0 | 0 | 11.28% | 0% | 0 | 0.006335 | 1 | 3.973 | 0.025169 | Low | Low | High | 2878 | 3087 | 0.006335
FAIRVIEW 2207CB | FAIRVIEW 2207 | DIABLO | 0.060291 | 10 | 69.19% | 0 | 0 | 1.178% | 0% | 0 | 0.0083828 | 1 | 2.9891 | 0.025057 | Low | Low | Medium | 2879 | 2997 | 0.0083828
RESERVATION ROAD 1101CB | RESERVATION ROAD 1101 | CENTRAL COAST | 3.6814 | 10 | 45.32% | 0 | 3 | 39.08% | 0% | 0 | 0.013924 | 1 | 1.799 | 0.025049 | Low | Low | Low | 2880 | 2666 | 0.013924
COVELO 110137328 | COVELO 1101 | HUMBOLDT | 3.9213 | 85.1621 | 100% | 0 | 0 | 16.63% | 0% | 0 | 0.020839 | 1 | 1.2015 | 0.025038 | Low | Low | Low | 2881 | 2374 | 0.020839
IGNACIO 1104316 | IGNACIO 1104 | NORTH BAY | 0.5655 | 10 | 40.98% | 0 | 2 | 6.524% | 0% | 0 | 0.0073158 | 1 | 3.4198 | 0.025018 | Low | Low | High | 2882 | 3040 | 0.0073158
GARBERVILLE 110139524 | GARBERVILLE 1101 | HUMBOLDT | 5.5428 | 59.5329 | 86.83% | 1 | 2 | 35.93% | 0% | 0 | 0.020129 | 1 | 1.2425 | 0.02501 | Low | Low | Low | 2883 | 2403 | 0.020129
OLEMA 1101320 | OLEMA 1101 | NORTH BAY | 0.033859 | 54.8898 | 25.18% | 0 | 1 | 0.2531% | 0% | 0 | 0.0091583 | 1 | 2.7217 | 0.024926 | Low | Low | Medium | 2884 | 2971 | 0.0091583
OAKLAND J 1118CR198 | OAKLAND J 1118 | EAST BAY | 0.38627 | 10 | 34.69% | 0 | 0 | 7.348% | 0% | 0 | 0.0076722 | 1 | 3.2489 | 0.024926 | Low | Low | High | 2885 | 3021 | 0.0076722
UKIAH 1114CB | UKIAH 1114 | HUMBOLDT | 1.2249 | 10 | 45.97% | 1 | 2 | 14.08% | 0% | 0 | 0.0083238 | 1 | 2.9939 | 0.024921 | Low | Low | Medium | 2886 | 3003 | 0.0083238
UPPER LAKE 1101660 | UPPER LAKE 1101 | HUMBOLDT | 7.1376 | 10 | 50.04% | 0 | 2 | 74.17% | 0% | 0 | 0.015402 | 1 | 1.6171 | 0.024907 | Low | Low | Low | 2887 | 2593 | 0.015402
CASTRO VALLEY 1104MR201 | CASTRO VALLEY 1104 | MISSION | 1.8766 | 10 | 10.28% | 0 | 1 | 19.54% | 0% | 0 | 0.007241 | 1 | 3.4354 | 0.024876 | Low | Low | High | 2888 | 3045 | 0.007241
HOPLAND 1101770 | HOPLAND 1101 | HUMBOLDT | 8.7193 | 58.1602 | 26.75% | 1 | 4 | 57.45% | 0% | 0 | 0.015784 | 1 | 1.5698 | 0.024778 | Low | Low | Low | 2889 | 2584 | 0.015784
POTTER VALLEY P H 110495878 | POTTER VALLEY P H 1104 | HUMBOLDT | 6.3973 | 36.9398 | 60.01% | 0 | 4 | 34.83% | 8.674% | 0 | 0.01627 | 1 | 1.5212 | 0.024749 | Low | Low | Low | 2890 | 2561 | 0.01627
WILLITS 110337504 | WILLITS 1103 | HUMBOLDT | 0.81372 | 28.0694 | 47.51% | 0 | 2 | 22.82% | 0% | 0 | 0.010255 | 1 | 2.412 | 0.024736 | Low | Low | Medium | 2891 | 2918 | 0.010255
SPENCE 1123CB | SPENCE 1123 | CENTRAL COAST | 2.0801 | 71.6022 | 100% | 0 | 0 | 6.177% | 0% | 0 | 0.017169 | 1 | 1.4373 | 0.024677 | Low | Low | Low | 2892 | 2523 | 0.017169
BOLINAS 11011064 | BOLINAS 1101 | NORTH BAY | 0.79432 | 10 | 14.47% | 2 | 1 | 17.88% | 0% | 0 | 0.0075676 | 1 | 3.2571 | 0.024648 | Low | Low | High | 2893 | 3026 | 0.0075676
HARTLEY 1101CB | HARTLEY 1101 | HUMBOLDT | 1.2777 | 10 | 19.8% | 0 | 1 | 42.25% | 0% | 0 | 0.0098099 | 1 | 2.5013 | 0.024537 | Low | Low | Medium | 2894 | 2939 | 0.0098099
HALF MOON BAY 110265568 | HALF MOON BAY 1102 | PENINSULA | 0.079124 | 10 | 0% | 0 | 0 | 2.534% | 0% | 0 | 0.0062845 | 1 | 3.8984 | 0.0245 | Low | Low | High | 2895 | 3089 | 0.0062845
OAKLAND K 1103CB | OAKLAND K 1103 | EAST BAY | 0.65834 | 10 | 0% | 1 | 2 | 13.28% | 0% | 0 | 0.0056661 | 1 | 4.3233 | 0.024496 | Low | Low | High | 2896 | 3120 | 0.0056661
OCEANO 110376678 | OCEANO 1103 | LOS PADRES | 0.055262 | 10 | 22.91% | 0 | 2 | 14.84% | 0% | 0 | 0.0068538 | 1 | 3.5692 | 0.024463 | Low | Low | High | 2897 | 3061 | 0.0068538
COTTONWOOD 110131500 | COTTONWOOD 1101 | NORTH VALLEY | 3.2216 | 22.5046 | 96% | 0 | 0 | 27.31% | 0% | 0 | 0.01471 | 1 | 1.6607 | 0.024428 | Low | Low | Low | 2898 | 2625 | 0.01471
WYANDOTTE 110213914 | WYANDOTTE 1102 | NORTH VALLEY | 0.60739 | 10 | 33.65% | 0 | 0 | 34.43% | 0% | 0 | 0.0087222 | 1 | 2.7969 | 0.024396 | Low | Low | Medium | 2899 | 2989 | 0.0087222
ALHAMBRA 1105CB | ALHAMBRA 1105 | DIABLO | 0.38371 | 10 | 15.25% | 0 | 0 | 20.22% | 0% | 0 | 0.0074366 | 1 | 3.2796 | 0.02439 | Low | Low | High | 2900 | 3033 | 0.0074366
HARRIS 11084674 | HARRIS 1108 | HUMBOLDT | 0.15936 | 10 | 0% | 0 | 0 | 1.98% | 0% | 0 | 0.0047917 | 1 | 5.073 | 0.024308 | Low | Low | High | 2901 | 3164 | 0.0047917
POTTER VALLEY P H 110564118 | POTTER VALLEY P H 1105 | HUMBOLDT | 1.7203 | 30.1363 | 62.86% | 2 | 1 | 18.17% | 0% | 0 | 0.014734 | 1 | 1.6469 | 0.024265 | Low | Low | Low | 2902 | 2623 | 0.014734
KONOCTI 110264464 | KONOCTI 1102 | HUMBOLDT | 0.53615 | 10 | 9.05% | 1 | 0 | 19.93% | 0% | 0 | 0.0081536 | 1 | 2.9706 | 0.024221 | Low | Low | Medium | 2903 | 3007 | 0.0081536
MORRO BAY 1101W20 | MORRO BAY 1101 | LOS PADRES | 1.8981 | 10 | 0% | 0 | 1 | 48.29% | 0% | 0 | 0.0077601 | 1 | 3.1154 | 0.024176 | Low | Low | High | 2904 | 3018 | 0.0077601
EEL RIVER 110249130 | EEL RIVER 1102 | HUMBOLDT | 1.458 | 43.0989 | 47.28% | 0 | 1 | 10.5% | 0% | 0 | 0.0098241 | 1 | 2.4567 | 0.024135 | Low | Low | Medium | 2905 | 2937 | 0.0098241
PEORIA 170176030 | PEORIA 1701 | YOSEMITE | 5.4729 | 32.855 | 62.69% | 0 | 1 | 88.26% | 0% | 0 | 0.022385 | 1 | 1.0774 | 0.024117 | Medium | Medium | Low | 2906 | 2321 | 0.022385
PAUL SWEET 210212850 | PAUL SWEET 2102 | CENTRAL COAST | 0.99852 | 10 | 0% | 0 | 0 | 24.38% | 0% | 0 | 0.0059903 | 1 | 4.0239 | 0.024104 | Low | Low | High | 2907 | 3108 | 0.0059903
KERN OIL 110646960 | KERN OIL 1106 | KERN | 1.1498 | 10 | 1.744% | 0 | 0 | 59.65% | 0% | 0 | 0.0086311 | 1 | 2.7916 | 0.024095 | Low | Low | Medium | 2908 | 2992 | 0.0086311
PANORAMA 1101CB | PANORAMA 1101 | NORTH VALLEY | 1.9355 | 10 | 100% | 0 | 2 | 10.24% | 0% | 0 | 0.012297 | 1 | 1.9576 | 0.024072 | Low | Low | Low | 2909 | 2787 | 0.012297
SILVERADO 210298998 | SILVERADO 2102 | NORTH BAY | 4.5559 | 48.6012 | 79.99% | 0 | 0 | 16.02% | 0% | 0 | 0.015709 | 1 | 1.5297 | 0.024031 | Low | Low | Low | 2910 | 2586 | 0.015709
TEMPLETON 2113A30 | TEMPLETON 2113 | LOS PADRES | 0.53596 | 10 | 10.42% | 0 | 0 | 34.36% | 0% | 0 | 0.0082271 | 1 | 2.9117 | 0.023955 | Low | Low | Medium | 2911 | 3006 | 0.0082271
ALHAMBRA 110213333 | ALHAMBRA 1102 | DIABLO | 0.074793 | 10 | 23.29% | 0 | 0 | 25.18% | 0% | 0 | 0.007309 | 1 | 3.2612 | 0.023836 | Low | Low | High | 2912 | 3041 | 0.007309
IONE 1101CB | IONE 1101 | STOCKTON | 1.9633 | 49.7739 | 2.974% | 1 | 0 | 13.95% | 0% | 0 | 0.007346 | 1 | 3.2391 | 0.023794 | Low | Low | High | 2913 | 3038 | 0.007346
TEJON 11032280 | TEJON 1103 | KERN | 2.7582 | 10 | 100% | 0 | 0 | 9.965% | 0% | 0 | 0.011765 | 1 | 2.0211 | 0.023777 | Low | Low | Low | 2914 | 2817 | 0.011765
EL CERRITO G 1108CB | EL CERRITO G 1108 | EAST BAY | 0.47538 | 10 | 0% | 0 | 0 | 6.483% | 0% | 0 | 0.0050118 | 1 | 4.7287 | 0.023699 | Low | Low | High | 2915 | 3145 | 0.0050118
EAST MARYSVILLE 11081706 | EAST MARYSVILLE 1108 | SIERRA | 0.35809 | 10 | 100% | 0 | 0 | 0.5923% | 0% | 0 | 0.010721 | 1 | 2.2096 | 0.02369 | Low | Low | Low | 2916 | 2893 | 0.010721
MADISON 21011943 | MADISON 2101 | SACRAMENTO | 0.028904 | 10 | 100% | 0 | 0 | 0.9967% | 0% | 0 | 0.010764 | 1 | 2.1991 | 0.023671 | Low | Low | Low | 2917 | 2886 | 0.010764
LAKEWOOD 210769586 | LAKEWOOD 2107 | DIABLO | 0.5706 | 16.4781 | 12.07% | 0 | 2 | 6.994% | 0% | 0 | 0.0069201 | 1 | 3.4182 | 0.023654 | Low | Low | High | 2918 | 3057 | 0.0069201
GARBERVILLE 11011770 | GARBERVILLE 1101 | HUMBOLDT | 8.6092 | 87.0246 | 95.86% | 7 | 3 | 100% | 0% | 0 | 0.087398 | 1 | 0.26991 | 0.02359 | High | High | Low | 2919 | 1347 | 0.087398
MORGAN HILL 2105XR578 | MORGAN HILL 2105 | SAN JOSE | 0.218 | 10 | 8.67% | 0 | 0 | 31.62% | 0% | 0 | 0.0069127 | 1 | 3.4108 | 0.023578 | Low | Low | High | 2920 | 3058 | 0.0069127
MC ARTHUR 11011546 | MC ARTHUR 1101 | NORTH VALLEY | 13.3497 | 54.7981 | 96.53% | 1 | 1 | 58.43% | 0% | 0 | 0.025754 | 1 | 0.91531 | 0.023572 | Medium | Medium | Low | 2921 | 2223 | 0.025754
HOLLISTER 210491424 | HOLLISTER 2104 | CENTRAL COAST | 0.19482 | 10 | 75.59% | 0 | 0 | 2.224% | 0% | 0 | 0.0089256 | 1 | 2.6389 | 0.023554 | Low | Low | Medium | 2922 | 2981 | 0.0089256
COTATI 1105893 | COTATI 1105 | SONOMA | 0.50896 | 59.1092 | 51.41% | 0 | 0 | 4.828% | 0% | 0 | 0.010484 | 1 | 2.2464 | 0.023552 | Low | Low | Medium | 2923 | 2905 | 0.010484
HALF MOON BAY 1102CB | HALF MOON BAY 1102 | PENINSULA | 0.43987 | 10 | 9.941% | 0 | 1 | 10.85% | 0% | 0 | 0.0057997 | 1 | 4.0421 | 0.023443 | Low | Low | High | 2924 | 3114 | 0.0057997
DEL MAR 2109CB | DEL MAR 2109 | SIERRA | 1.7939 | 12.1972 | 19.79% | 0 | 1 | 27.43% | 0% | 0 | 0.0075272 | 1 | 3.1113 | 0.023419 | Low | Low | High | 2925 | 3029 | 0.0075272
ESTUDILLO 0401CB | ESTUDILLO 0401 | MISSION | 0.69789 | 10 | 26.72% | 0 | 0 | 14.78% | 0% | 0 | 0.0067781 | 1 | 3.4546 | 0.023416 | Low | Low | High | 2926 | 3064 | 0.0067781
TAR FLAT 0402CB | TAR FLAT 0402 | YOSEMITE | 0.52249 | 10 | 7.104% | 0 | 0 | 35.32% | 0% | 0 | 0.0070807 | 1 | 3.3002 | 0.023368 | Low | Low | High | 2927 | 3052 | 0.0070807
ELK CREEK 11012004 | ELK CREEK 1101 | NORTH VALLEY | 14.9707 | 82.0149 | 100% | 0 | 1 | 27.7% | 0% | 0 | 0.034268 | 1 | 0.68104 | 0.023338 | Medium | Medium | Low | 2928 | 1966 | 0.034268
PIT NO 1 11011552 | PIT NO 1 1101 | NORTH VALLEY | 9.8425 | 12.4749 | 95.95% | 1 | 1 | 37.18% | 0% | 0 | 0.023212 | 1 | 1.0048 | 0.023324 | Medium | Medium | Low | 2929 | 2303 | 0.023212
AUBURN 1102CB | AUBURN 1102 | SIERRA | 0.41789 | 10 | 46.75% | 0 | 2 | 6.005% | 0% | 0 | 0.0076302 | 1 | 3.055 | 0.02331 | Low | Low | Medium | 2930 | 3025 | 0.0076302
EEL RIVER 1102530 | EEL RIVER 1102 | HUMBOLDT | 5.0874 | 49.3959 | 37.23% | 9 | 0 | 15.69% | 0% | 0 | 0.010956 | 1 | 2.1273 | 0.023307 | Low | Low | Low | 2931 | 2870 | 0.010956
TULE POWER HOUSE 1101CB | TULE POWER HOUSE 1101 | FRESNO | 4.0927 | 57.029 | 3.215% | 0 | 0 | 100% | 0% | 0 | 0.01789 | 1 | 1.3019 | 0.023291 | Low | Low | Low | 2932 | 2494 | 0.01789
EL CERRITO G 1108BR346 | EL CERRITO G 1108 | EAST BAY | 0.1038 | 10 | 0% | 0 | 0 | 1.483% | 0% | 0 | 0.004768 | 1 | 4.878 | 0.023259 | Low | Low | High | 2933 | 3168 | 0.004768
OCEANO 1105V16 | OCEANO 1105 | LOS PADRES | 1.6064 | 10 | 0% | 0 | 0 | 44.18% | 0% | 0 | 0.0072956 | 1 | 3.1854 | 0.023239 | Low | Low | High | 2934 | 3042 | 0.0072956
ALHAMBRA 110595016 | ALHAMBRA 1105 | DIABLO | 0.37201 | 51.8878 | 0% | 0 | 0 | 9.208% | 0% | 0 | 0.0078178 | 1 | 2.9552 | 0.023103 | Low | Low | Medium | 2935 | 3017 | 0.0078178
BEAR VALLEY 210110000 | BEAR VALLEY 2101 | YOSEMITE | 29.476 | 56.7898 | 61.86% | 4 | 0 | 88.5% | 0% | 0 | 0.039743 | 1 | 0.58061 | 0.023075 | Medium | Medium | Low | 2936 | 1863 | 0.039743
IGNACIO 11041290 | IGNACIO 1104 | NORTH BAY | 1.6542 | 10 | 24.98% | 1 | 1 | 15.64% | 0% | 0 | 0.0079604 | 1 | 2.8977 | 0.023067 | Low | Low | Medium | 2937 | 3013 | 0.0079604
TIDEWATER 210695842 | TIDEWATER 2106 | DIABLO | 0.21866 | 10 | 7.343% | 0 | 0 | 20.55% | 0% | 0 | 0.0061241 | 1 | 3.7665 | 0.023066 | Low | Low | High | 2938 | 3100 | 0.0061241
GEYSERVILLE 110289714 | GEYSERVILLE 1102 | SONOMA | 1.4773 | 46.3035 | 100% | 0 | 0 | 11.51% | 0% | 0 | 0.015262 | 1 | 1.5055 | 0.022977 | Low | Low | Low | 2939 | 2600 | 0.015262
SNEATH LANE 1101CB | SNEATH LANE 1101 | PENINSULA | 0.21236 | 10 | 2.867% | 0 | 1 | 21.58% | 0% | 0 | 0.0060901 | 1 | 3.7657 | 0.022933 | Low | Low | High | 2940 | 3102 | 0.0060901
HARTLEY 1102CB | HARTLEY 1102 | HUMBOLDT | 2.7707 | 10 | 40.84% | 0 | 2 | 23.94% | 0% | 0 | 0.0099181 | 1 | 2.3095 | 0.022906 | Low | Low | Medium | 2941 | 2932 | 0.0099181
OROSI 11027948F | OROSI 1102 | FRESNO | 0.26307 | 10 | 100% | 0 | 0 | 3.077% | 0% | 0 | 0.010989 | 1 | 2.0809 | 0.022866 | Low | Low | Low | 2942 | 2865 | 0.010989
POINT MORETTI 110183716 | POINT MORETTI 1101 | CENTRAL COAST | 2.5672 | 18.0705 | 6.579% | 5 | 0 | 94.36% | 0% | 0 | 0.014279 | 1 | 1.6002 | 0.022849 | Low | Low | Low | 2943 | 2642 | 0.014279
SARATOGA 1105CB | SARATOGA 1105 | DE ANZA | 0.26967 | 10 | 28.45% | 0 | 0 | 4.984% | 0% | 0 | 0.0062358 | 1 | 3.6613 | 0.022831 | Low | Low | High | 2944 | 3094 | 0.0062358
PACIFICA 1104CB | PACIFICA 1104 | PENINSULA | 0.50255 | 42.4378 | 0% | 0 | 0 | 11.92% | 0% | 0 | 0.006597 | 1 | 3.4551 | 0.022793 | Low | Low | High | 2945 | 3073 | 0.006597
CASTRO VALLEY 1104MR236 | CASTRO VALLEY 1104 | MISSION | 1.7251 | 10 | 10.02% | 0 | 1 | 20.44% | 0% | 0 | 0.0063847 | 1 | 3.5607 | 0.022734 | Low | Low | High | 2946 | 3086 | 0.0063847
PENRYN 11051378 | PENRYN 1105 | SIERRA | 0.3076 | 10 | 15.69% | 2 | 1 | 16.27% | 0% | 0 | 0.0065875 | 1 | 3.4493 | 0.022722 | Low | Low | High | 2947 | 3076 | 0.0065875
MORRO BAY 1101CB | MORRO BAY 1101 | LOS PADRES | 0.64776 | 10 | 6.384% | 0 | 0 | 29.39% | 0% | 0 | 0.0066355 | 1 | 3.4209 | 0.0227 | Low | Low | High | 2948 | 3070 | 0.0066355
COTTONWOOD 1103CB | COTTONWOOD 1103 | NORTH VALLEY | 0.091321 | 14.0615 | 100% | 0 | 0 | 0.8116% | 0% | 0 | 0.011044 | 1 | 2.0553 | 0.022699 | Low | Low | Low | 2949 | 2863 | 0.011044
BAYWOOD 1101CB | BAYWOOD 1101 | LOS PADRES | 1.4233 | 43.3041 | 38.16% | 0 | 0 | 4.9% | 0% | 0 | 0.008459 | 1 | 2.6765 | 0.022641 | Low | Low | Medium | 2950 | 2996 | 0.008459
SAN LUIS OBISPO 1104645976 | SAN LUIS OBISPO 1104 | LOS PADRES | 2.1274 | 42.6681 | 27.62% | 0 | 0 | 32.32% | 0% | 0 | 0.010145 | 1 | 2.231 | 0.022633 | Low | Low | Medium | 2951 | 2921 | 0.010145
SISQUOC 1102M54 | SISQUOC 1102 | LOS PADRES | 17.0931 | 11.3388 | 62.6% | 1 | 3 | 56.95% | 1.375% | 0 | 0.022753 | 1 | 0.99426 | 0.022622 | Medium | Medium | Low | 2952 | 2315 | 0.022753
SUNOL 1101MR169 | SUNOL 1101 | MISSION | 3.8873 | 57.3439 | 37.68% | 0 | 0 | 41.76% | 0% | 0 | 0.013353 | 1 | 1.6919 | 0.022592 | Low | Low | Low | 2953 | 2694 | 0.013353
TASSAJARA 211238868 | TASSAJARA 2112 | DIABLO | 0.17353 | 10 | 11.26% | 2 | 2 | 4.039% | 0% | 0 | 0.0057426 | 1 | 3.9277 | 0.022555 | Low | Low | High | 2954 | 3117 | 0.0057426
COARSEGOLD 210490356 | COARSEGOLD 2104 | YOSEMITE | 4.6415 | 10 | 96.81% | 0 | 4 | 27.05% | 0% | 0 | 0.014744 | 1 | 1.5262 | 0.022503 | Low | Low | Low | 2955 | 2622 | 0.014744
VIEJO 22049540 | VIEJO 2204 | CENTRAL COAST | 0.84933 | 10 | 0% | 3 | 2 | 38.01% | 0% | 0 | 0.0074407 | 1 | 3.0127 | 0.022417 | Low | Low | Medium | 2956 | 3032 | 0.0074407
SUMMIT 110158642 | SUMMIT 1101 | SIERRA | 1.9126 | 10 | 32.51% | 0 | 1 | 100% | 0% | 0 | 0.019248 | 1 | 1.1597 | 0.022322 | Low | Low | Low | 2957 | 2433 | 0.019248
RED BLUFF 11041630 | RED BLUFF 1104 | NORTH VALLEY | 2.5495 | 10 | 100% | 0 | 1 | 18.04% | 0% | 0 | 0.01301 | 1 | 1.715 | 0.022313 | Low | Low | Low | 2958 | 2713 | 0.01301
VASONA 1102CB | VASONA 1102 | DE ANZA | 0.06716 | 10 | 0% | 0 | 0 | 0.4408% | 0% | 0 | 0.0047187 | 1 | 4.7083 | 0.022217 | Low | Low | High | 2959 | 3176 | 0.0047187
FORT BRAGG A 1102 | FORT BRAGG A 1102 | HUMBOLDT | 0.10961 | 10 | 0% | 0 | 0 | 85.38% | 0% | 0 | 0.010984 | 1 | 2.0184 | 0.02217 | Low | Low | Low | 2960 | 2866 | 0.010984
FAIRVIEW 2207P142 | FAIRVIEW 2207 | DIABLO | 0.64407 | 10 | 4.931% | 0 | 0 | 20.76% | 0% | 0 | 0.0060169 | 1 | 3.6784 | 0.022132 | Low | Low | High | 2961 | 3107 | 0.0060169
SAN MIGUEL 1104R66 | SAN MIGUEL 1104 | LOS PADRES | 8.3967 | 54.4532 | 99.05% | 0 | 3 | 18.97% | 0% | 0 | 0.020883 | 1 | 1.0549 | 0.02203 | Low | Low | Low | 2962 | 2373 | 0.020883
COTATI 1105616 | COTATI 1105 | SONOMA | 0.88156 | 51.5142 | 16.32% | 0 | 0 | 2.877% | 0% | 0 | 0.0083693 | 1 | 2.6305 | 0.022015 | Low | Low | Medium | 2963 | 2999 | 0.0083693
SUNOL 1101CB | SUNOL 1101 | MISSION | 3.3865 | 29.3526 | 12.99% | 0 | 0 | 58.39% | 0% | 0 | 0.010654 | 1 | 2.0615 | 0.021963 | Low | Low | Low | 2964 | 2898 | 0.010654
BEAR VALLEY 210511210 | BEAR VALLEY 2105 | YOSEMITE | 17.0195 | 54.7309 | 100% | 0 | 6 | 100% | 0% | 0 | 0.049124 | 1 | 0.44607 | 0.021913 | Medium | Medium | Low | 2965 | 1693 | 0.049124
OCEANO 1106CB | OCEANO 1106 | LOS PADRES | 0.86306 | 10 | 5.571% | 1 | 4 | 19.68% | 0% | 0 | 0.0065904 | 1 | 3.3208 | 0.021885 | Low | Low | High | 2966 | 3075 | 0.0065904
CLARKSVILLE 2106CB | CLARKSVILLE 2106 | SIERRA | 0.13957 | 10 | 0% | 0 | 0 | 27.21% | 0% | 0 | 0.0061619 | 1 | 3.5511 | 0.021882 | Low | Low | High | 2967 | 3098 | 0.0061619
SAN RAFAEL 110648752 | SAN RAFAEL 1106 | NORTH BAY | 0.61983 | 10 | 0% | 0 | 1 | 26.76% | 0% | 0 | 0.0062637 | 1 | 3.4892 | 0.021855 | Low | Low | High | 2968 | 3090 | 0.0062637
OAKLAND J 1105CR132 | OAKLAND J 1105 | EAST BAY | 0.28914 | 10 | 34.84% | 0 | 0 | 6.37% | 0% | 0 | 0.0066625 | 1 | 3.2608 | 0.021725 | Low | Low | High | 2969 | 3068 | 0.0066625
ATASCADERO 1103A46 | ATASCADERO 1103 | LOS PADRES | 0.63104 | 65.2454 | 33.62% | 0 | 0 | 6.794% | 0% | 0 | 0.0096376 | 1 | 2.251 | 0.021694 | Low | Low | Medium | 2970 | 2946 | 0.0096376
PACIFICA 1103CB | PACIFICA 1103 | PENINSULA | 0.044512 | 50.42 | 0% | 0 | 0 | 0.9046% | 0% | 0 | 0.0062412 | 1 | 3.4634 | 0.021616 | Low | Low | High | 2971 | 3093 | 0.0062412
SAN RAFAEL 11092213 | SAN RAFAEL 1109 | NORTH BAY | 0.014561 | 10 | 0% | 0 | 0 | 3.395% | 0% | 0 | 0.0048598 | 1 | 4.438 | 0.021568 | Low | Low | High | 2972 | 3156 | 0.0048598
VIEJO 22029488 | VIEJO 2202 | CENTRAL COAST | 0.18548 | 10 | 0% | 0 | 0 | 14.19% | 0% | 0 | 0.0054123 | 1 | 3.9833 | 0.021559 | Low | Low | High | 2973 | 3128 | 0.0054123
BERESFORD 0403CB | BERESFORD 0403 | PENINSULA | 0.94707 | 10 | 19.89% | 1 | 1 | 17.08% | 0% | 0 | 0.0067843 | 1 | 3.1734 | 0.02153 | Low | Low | High | 2974 | 3063 | 0.0067843
WOODSIDE 11028862 | WOODSIDE 1102 | PENINSULA | 0.10582 | 10 | 0% | 0 | 0 | 2.762% | 0% | 0 | 0.0048292 | 1 | 4.4266 | 0.021377 | Low | Low | High | 2975 | 3161 | 0.0048292
MORRO BAY 1101V70 | MORRO BAY 1101 | LOS PADRES | 0.13653 | 10 | 0% | 0 | 0 | 22.43% | 0% | 0 | 0.0058754 | 1 | 3.6321 | 0.02134 | Low | Low | High | 2976 | 3111 | 0.0058754
LAS GALLINAS A 1105CB | LAS GALLINAS A 1105 | NORTH BAY | 0.31033 | 10 | 12.89% | 0 | 0 | 14.92% | 0% | 0 | 0.0060597 | 1 | 3.5062 | 0.021246 | Low | Low | High | 2977 | 3104 | 0.0060597
SALT SPRINGS 21014913 | SALT SPRINGS 2101 | STOCKTON | 3.8651 | 10 | 100% | 0 | 2 | 100% | 0% | 0 | 0.029697 | 1 | 0.71504 | 0.021235 | Medium | Medium | Low | 2978 | 2107 | 0.029697
COTTONWOOD 1101CB | COTTONWOOD 1101 | NORTH VALLEY | 5.2937 | 10 | 60.95% | 2 | 2 | 23.27% | 0% | 0 | 0.010444 | 1 | 2.0305 | 0.021206 | Low | Low | Low | 2979 | 2907 | 0.010444
OCEANO 1104Q04 | OCEANO 1104 | LOS PADRES | 0.015582 | 10 | 0% | 0 | 0 | 0.5987% | 0% | 0 | 0.0047262 | 1 | 4.4629 | 0.021092 | Low | Low | High | 2980 | 3175 | 0.0047262
SAUSALITO 11021224 | SAUSALITO 1102 | NORTH BAY | 0.046722 | 10 | 29.73% | 0 | 0 | 1.494% | 0% | 0 | 0.0060863 | 1 | 3.4619 | 0.02107 | Low | Low | High | 2981 | 3103 | 0.0060863
NARROWS 2104CB | NARROWS 2104 | SIERRA | 0.002841 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.6515 | 0.020967 | Low | Low | Low | 2982 | 2735 | 0.012695
ZACA 1101Y70 | ZACA 1101 | LOS PADRES | 5.1032 | 39.0808 | 69.39% | 0 | 1 | 58.75% | 0% | 0 | 0.018441 | 1 | 1.1363 | 0.020954 | Low | Low | Low | 2983 | 2469 | 0.018441
FRUITLAND 11413902 | FRUITLAND 1141 | HUMBOLDT | 5.0988 | 85.765 | 7.833% | 1 | 0 | 99.69% | 0% | 0 | 0.025906 | 1 | 0.80512 | 0.020857 | Medium | Medium | Low | 2984 | 2216 | 0.025906
SUMMIT 110186658 | SUMMIT 1101 | SIERRA | 0.66943 | 10 | 1.926% | 3 | 0 | 100% | 0% | 0 | 0.015299 | 1 | 1.3569 | 0.020759 | Low | Low | Low | 2985 | 2597 | 0.015299
MARIPOSA 210190180 | MARIPOSA 2101 | YOSEMITE | 4.7841 | 52.2474 | 63.07% | 0 | 2 | 100% | 0% | 0 | 0.033288 | 1 | 0.62236 | 0.020717 | Medium | Medium | Low | 2986 | 1999 | 0.033288
CALPELLA 1102496 | CALPELLA 1102 | HUMBOLDT | 4.1652 | 16.4846 | 91.99% | 0 | 2 | 24.91% | 0% | 0 | 0.015871 | 1 | 1.3046 | 0.020706 | Low | Low | Low | 2987 | 2581 | 0.015871
BANCROFT 0402CB | BANCROFT 0402 | EAST BAY | 1.0716 | 10 | 1.687% | 0 | 0 | 23.45% | 0% | 0 | 0.0060178 | 1 | 3.4396 | 0.020699 | Low | Low | High | 2988 | 3106 | 0.0060178
OAKLAND J 1105CR130 | OAKLAND J 1105 | EAST BAY | 0.95094 | 10 | 5.238% | 0 | 0 | 19.42% | 0% | 0 | 0.0059522 | 1 | 3.464 | 0.020619 | Low | Low | High | 2989 | 3110 | 0.0059522
MADISON 210137082 | MADISON 2101 | SACRAMENTO | 0.85819 | 87.1383 | 100% | 0 | 0 | 4.662% | 0% | 0 | 0.018775 | 1 | 1.0976 | 0.020608 | Low | Low | Low | 2990 | 2457 | 0.018775
CLEAR LAKE 1102CB | CLEAR LAKE 1102 | HUMBOLDT | 0.13095 | 10 | 54.49% | 0 | 0 | 0.5805% | 0% | 0 | 0.0073882 | 1 | 2.7821 | 0.020555 | Low | Low | Medium | 2991 | 3036 | 0.0073882
GARBERVILLE 11028189 | GARBERVILLE 1102 | HUMBOLDT | 1.0385 | 78.4457 | 65.35% | 2 | 1 | 100% | 0% | 0 | 0.035613 | 1 | 0.5748 | 0.02047 | Medium | Medium | Low | 2992 | 1942 | 0.035613
GUALALA 1111402866 | GUALALA 1111 | HUMBOLDT | 1.5915 | 10 | 0% | 1 | 1 | 100% | 0% | 0 | 0.013132 | 1 | 1.557 | 0.020445 | Low | Low | Low | 2993 | 2709 | 0.013132
SUMMIT 1102CB | SUMMIT 1102 | SIERRA | 1.0104 | 10 | 73.24% | 1 | 3 | 100% | 0% | 0 | 0.032108 | 1 | 0.63651 | 0.020437 | Medium | Medium | Low | 2994 | 2042 | 0.032108
SNEATH LANE 110168070 | SNEATH LANE 1101 | PENINSULA | 0.099639 | 10 | 0% | 0 | 2 | 4.651% | 0% | 0 | 0.0051309 | 1 | 3.9783 | 0.020412 | Low | Low | High | 2995 | 3138 | 0.0051309
BUELLTON 11016621 | BUELLTON 1101 | LOS PADRES | 1.6446 | 36.7928 | 44.49% | 0 | 1 | 16.9% | 0% | 0 | 0.0098043 | 1 | 2.0776 | 0.020369 | Low | Low | Low | 2996 | 2940 | 0.0098043
COPPERMINE 1104R755 | COPPERMINE 1104 | FRESNO | 8.1519 | 17.5841 | 96.77% | 0 | 3 | 13.19% | 0% | 0 | 0.013252 | 1 | 1.537 | 0.020367 | Low | Low | Low | 2997 | 2701 | 0.013252
PLACER 110451732 | PLACER 1104 | SIERRA | 1.3434 | 10 | 21.69% | 0 | 0 | 16.14% | 0% | 0 | 0.0065925 | 1 | 3.0863 | 0.020346 | Low | Low | High | 2998 | 3074 | 0.0065925
PLACER 1101CB | PLACER 1101 | SIERRA | 0.77573 | 10 | 3.906% | 0 | 0 | 10.24% | 0% | 0 | 0.0061355 | 1 | 3.3142 | 0.020334 | Low | Low | High | 2999 | 3099 | 0.0061355
GABILAN 11013034 | GABILAN 1101 | CENTRAL COAST | 0.41092 | 10 | 76.33% | 0 | 0 | 1.978% | 0% | 0 | 0.0089581 | 1 | 2.2622 | 0.020265 | Low | Low | Medium | 3000 | 2980 | 0.0089581
OCEANO 1105V48 | OCEANO 1105 | LOS PADRES | 0.76105 | 10 | 0% | 0 | 1 | 30.2% | 0% | 0 | 0.0064819 | 1 | 3.124 | 0.020249 | Low | Low | High | 3001 | 3081 | 0.0064819
BRUNSWICK 111094368 | BRUNSWICK 1110 | SIERRA | 0.16855 | 10 | 0% | 0 | 0 | 35.28% | 0% | 0 | 0.0066771 | 1 | 3.0325 | 0.020249 | Low | Low | Medium | 3002 | 3066 | 0.0066771
PIT NO 7 1101CB | PIT NO 7 1101 | NORTH VALLEY | 2.7098 | 77.1247 | 100% | 0 | 2 | 100% | 0% | 0 | 0.046206 | 1 | 0.4374 | 0.02021 | Medium | Medium | Low | 3003 | 1737 | 0.046206
MADISON 21011606 | MADISON 2101 | SACRAMENTO | 0.66018 | 28.3427 | 86.09% | 0 | 0 | 3.933% | 0% | 0 | 0.0112 | 1 | 1.8042 | 0.020206 | Low | Low | Low | 3004 | 2854 | 0.0112
LOS COCHES 1101CB | LOS COCHES 1101 | CENTRAL COAST | 2.6219 | 75.2391 | 12.86% | 0 | 1 | 13.12% | 0% | 0 | 0.009461 | 1 | 2.1351 | 0.020201 | Low | Low | Low | 3005 | 2954 | 0.009461
CALPELLA 1102CB | CALPELLA 1102 | HUMBOLDT | 1.6769 | 10 | 88.62% | 0 | 2 | 18.53% | 0% | 0 | 0.012165 | 1 | 1.6553 | 0.020137 | Low | Low | Low | 3006 | 2796 | 0.012165
VIEJO 22022014 | VIEJO 2202 | CENTRAL COAST | 0.34884 | 10 | 0% | 0 | 0 | 8.641% | 0% | 0 | 0.0051208 | 1 | 3.9267 | 0.020108 | Low | Low | High | 3007 | 3139 | 0.0051208
MARTELL 110198374 | MARTELL 1101 | STOCKTON | 0.48931 | 10 | 16.23% | 0 | 0 | 12.89% | 0% | 0 | 0.0061034 | 1 | 3.2848 | 0.020049 | Low | Low | High | 3008 | 3101 | 0.0061034
BOSTON 0401CR242 | BOSTON 0401 | EAST BAY | 0.44969 | 10 | 0% | 0 | 0 | 9.847% | 0% | 0 | 0.0051828 | 1 | 3.8356 | 0.019879 | Low | Low | High | 3009 | 3135 | 0.0051828
SAN RAFAEL 1105CB | SAN RAFAEL 1105 | NORTH BAY | 0.49095 | 10 | 6.778% | 3 | 1 | 5.07% | 0% | 0 | 0.0055495 | 1 | 3.5772 | 0.019852 | Low | Low | High | 3010 | 3122 | 0.0055495
VIEJO 22032634 | VIEJO 2203 | CENTRAL COAST | 0.37273 | 10 | 10.45% | 0 | 0 | 22.39% | 0% | 0 | 0.0063984 | 1 | 3.0948 | 0.019802 | Low | Low | High | 3011 | 3083 | 0.0063984
SAN LUIS OBISPO 1104CB | SAN LUIS OBISPO 1104 | LOS PADRES | 0.36018 | 63.441 | 2.835% | 0 | 0 | 5.218% | 0% | 0 | 0.007285 | 1 | 2.718 | 0.019801 | Low | Low | Medium | 3012 | 3043 | 0.007285
SARATOGA 1103LC40 | SARATOGA 1103 | DE ANZA | 0.12637 | 10 | 0% | 0 | 0 | 6.576% | 0% | 0 | 0.0050164 | 1 | 3.9395 | 0.019762 | Low | Low | High | 3013 | 3144 | 0.0050164
POTTER VALLEY P H 1105CB | POTTER VALLEY P H 1105 | HUMBOLDT | 0.024417 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.014786 | 1 | 1.3325 | 0.019702 | Low | Low | Low | 3014 | 2619 | 0.014786
CASTRO VALLEY 1101MR518 | CASTRO VALLEY 1101 | MISSION | 0.037775 | 10 | 0% | 0 | 0 | 1.912% | 0% | 0 | 0.0047885 | 1 | 4.111 | 0.019686 | Low | Low | High | 3015 | 3165 | 0.0047885
SNEATH LANE 1102CB | SNEATH LANE 1102 | PENINSULA | 0.28247 | 10 | 3.955% | 0 | 1 | 11.21% | 0% | 0 | 0.0055412 | 1 | 3.5434 | 0.019634 | Low | Low | High | 3016 | 3123 | 0.0055412
HORSESHOE 1104CB | HORSESHOE 1104 | SIERRA | 0.063337 | 10 | 0% | 0 | 0 | 2.137% | 0% | 0 | 0.0047992 | 1 | 4.0681 | 0.019524 | Low | Low | High | 3017 | 3163 | 0.0047992
VOLTA 110185234 | VOLTA 1101 | NORTH VALLEY | 7.9136 | 44.4652 | 95.46% | 10 | 12 | 100% | 0% | 0 | 0.11805 | 1 | 0.16495 | 0.019472 | High | High | Low | 3018 | 1229 | 0.11805
CARMEL 0402CB | CARMEL 0402 | CENTRAL COAST | 0.30828 | 10 | 0% | 0 | 0 | 21.19% | 0% | 0 | 0.0058032 | 1 | 3.3503 | 0.019442 | Low | Low | High | 3019 | 3113 | 0.0058032
HOLLISTER 2104855412 | HOLLISTER 2104 | CENTRAL COAST | 0.30314 | 60 | 0% | 1 | 0 | 11.12% | 0% | 0 | 0.007471 | 1 | 2.599 | 0.019417 | Low | Low | Medium | 3020 | 3031 | 0.007471
PUEBLO 11053022 | PUEBLO 1105 | NORTH BAY | 0.42768 | 10 | 42.51% | 0 | 0 | 4.687% | 0% | 0 | 0.0069771 | 1 | 2.7525 | 0.019205 | Low | Low | Medium | 3021 | 3055 | 0.0069771
HALF MOON BAY 11019014 | HALF MOON BAY 1101 | PENINSULA | 0.031423 | 10 | 0% | 0 | 0 | 1.737% | 0% | 0 | 0.0047801 | 1 | 4.0077 | 0.019157 | Low | Low | High | 3022 | 3166 | 0.0047801
POINT ARENA 11011296 | POINT ARENA 1101 | HUMBOLDT | 2.101 | 59.6296 | 9.522% | 3 | 3 | 37.92% | 0% | 0 | 0.013105 | 1 | 1.4612 | 0.019149 | Low | Low | Low | 3023 | 2711 | 0.013105
PIT NO 5 11011658 | PIT NO 5 1101 | NORTH VALLEY | 4.5542 | 60.6461 | 59.05% | 1 | 2 | 100% | 0% | 0 | 0.039255 | 1 | 0.48755 | 0.019139 | Medium | Medium | Low | 3024 | 1877 | 0.039255
WILLOW PASS 210821196 | WILLOW PASS 2108 | DIABLO | 0.047227 | 10 | 0% | 0 | 0 | 23.89% | 0% | 0 | 0.005961 | 1 | 3.2102 | 0.019136 | Low | Low | High | 3025 | 3109 | 0.005961
HOOPA 1101 | HOOPA 1101 | HUMBOLDT | 0.098699 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.5065 | 0.019125 | Low | Low | Low | 3026 | 2735 | 0.012695
COAST RD 04015134 | COAST RD 0401 | CENTRAL COAST | 1.6146 | 10 | 0% | 0 | 0 | 53.13% | 0% | 0 | 0.007975 | 1 | 2.3974 | 0.019119 | Low | Low | Medium | 3027 | 3012 | 0.007975
SAN RAFAEL 11061230 | SAN RAFAEL 1106 | NORTH BAY | 0.27095 | 10 | 0% | 0 | 1 | 5.214% | 0% | 0 | 0.0050532 | 1 | 3.7783 | 0.019092 | Low | Low | High | 3028 | 3142 | 0.0050532
ANTLER 11011376 | ANTLER 1101 | NORTH VALLEY | 9.003 | 26.8195 | 100% | 0 | 3 | 100% | 0% | 0 | 0.049747 | 1 | 0.38247 | 0.019027 | Medium | Medium | Low | 3029 | 1685 | 0.049747
FORT BRAGG A 1103588 | FORT BRAGG A 1103 | HUMBOLDT | 0.37656 | 10 | 0% | 0 | 0 | 20.3% | 0% | 0 | 0.0057518 | 1 | 3.299 | 0.018975 | Low | Low | High | 3030 | 3116 | 0.0057518
LAKEWOOD 1102CB | LAKEWOOD 1102 | DIABLO | 0.47236 | 10 | 18.19% | 0 | 0 | 4.922% | 0% | 0 | 0.0057291 | 1 | 3.3099 | 0.018962 | Low | Low | High | 3031 | 3119 | 0.0057291
SARATOGA 1107CB | SARATOGA 1107 | DE ANZA | 0.16938 | 10 | 0% | 0 | 1 | 1.739% | 0% | 0 | 0.0048811 | 1 | 3.8453 | 0.018769 | Low | Low | High | 3032 | 3155 | 0.0048811
CAMBRIA 1101CB | CAMBRIA 1101 | LOS PADRES | 7.5504 | 30.2261 | 1.521% | 0 | 1 | 62.43% | 0% | 0 | 0.010371 | 1 | 1.7969 | 0.018636 | Low | Low | Low | 3033 | 2912 | 0.010371
CARMEL 0405CB | CARMEL 0405 | CENTRAL COAST | 0.33684 | 10 | 0% | 0 | 1 | 10.77% | 0% | 0 | 0.0053408 | 1 | 3.4633 | 0.018497 | Low | Low | High | 3034 | 3130 | 0.0053408
ROSSMOOR 110479146 | ROSSMOOR 1104 | DIABLO | 0.24893 | 10 | 0% | 0 | 0 | 11.42% | 0% | 0 | 0.0052646 | 1 | 3.5101 | 0.018479 | Low | Low | High | 3035 | 3133 | 0.0052646
WYANDOTTE 1103CB | WYANDOTTE 1103 | NORTH VALLEY | 0.060864 | 10 | 0% | 0 | 0 | 0.8345% | 0% | 0 | 0.0047373 | 1 | 3.8992 | 0.018471 | Low | Low | High | 3036 | 3172 | 0.0047373
FORT BRAGG A 110436526 | FORT BRAGG A 1104 | HUMBOLDT | 0.39885 | 10 | 0% | 0 | 0 | 6.124% | 0% | 0 | 0.0049939 | 1 | 3.6762 | 0.018359 | Low | Low | High | 3037 | 3146 | 0.0049939
DEL MONTE 210386496 | DEL MONTE 2103 | CENTRAL COAST | 0.39145 | 10 | 0% | 3 | 0 | 5.331% | 0% | 0 | 0.0051542 | 1 | 3.545 | 0.018272 | Low | Low | High | 3038 | 3136 | 0.0051542
LAMONT 11024222 | LAMONT 1102 | KERN | 0.50063 | 85 | 100% | 0 | 0 | 3.081% | 0% | 0 | 0.018222 | 1 | 1.0005 | 0.01823 | Low | Low | Low | 3039 | 2482 | 0.018222
SOLEDAD 111435306 | SOLEDAD 1114 | CENTRAL COAST | 0.90872 | 10 | 9.031% | 0 | 0 | 12.56% | 0% | 0 | 0.0065483 | 1 | 2.7745 | 0.018169 | Low | Low | Medium | 3040 | 3077 | 0.0065483
CAYETANO 2109MR186 | CAYETANO 2109 | MISSION | 0.10978 | 10 | 0% | 0 | 0 | 4.27% | 0% | 0 | 0.0063941 | 1 | 2.8337 | 0.018119 | Low | Low | Medium | 3041 | 3084 | 0.0063941
VALLEY VIEW 1105P124 | VALLEY VIEW 1105 | EAST BAY | 0.092976 | 10 | 0% | 0 | 0 | 2.939% | 0% | 0 | 0.0048377 | 1 | 3.7353 | 0.01807 | Low | Low | High | 3042 | 3160 | 0.0048377
SUMMIT 110249484 | SUMMIT 1102 | SIERRA | 2.6877 | 10 | 54.68% | 1 | 0 | 100% | 0% | 0 | 0.026029 | 1 | 0.69298 | 0.018038 | Medium | Medium | Low | 3043 | 2213 | 0.026029
EEL RIVER 11033820 | EEL RIVER 1103 | HUMBOLDT | 2.3658 | 10 | 0% | 0 | 1 | 11.93% | 0% | 0 | 0.0080448 | 1 | 2.2417 | 0.018034 | Low | Low | Medium | 3044 | 3010 | 0.0080448
OAKLAND J 1105153228 | OAKLAND J 1105 | EAST BAY | 0.47385 | 10 | 4.597% | 0 | 0 | 11.41% | 0% | 0 | 0.0054665 | 1 | 3.2905 | 0.017988 | Low | Low | High | 3045 | 3125 | 0.0054665
CLARKSVILLE 2103CB | CLARKSVILLE 2103 | SIERRA | 0.11367 | 10 | 0% | 0 | 0 | 7.91% | 0% | 0 | 0.0050836 | 1 | 3.5358 | 0.017975 | Low | Low | High | 3046 | 3140 | 0.0050836
FLINT 110138570 | FLINT 1101 | SIERRA | 0.12622 | 10 | 17.37% | 0 | 0 | 3.673% | 0% | 0 | 0.0056203 | 1 | 3.1886 | 0.017921 | Low | Low | High | 3047 | 3121 | 0.0056203
HALF MOON BAY 11036014 | HALF MOON BAY 1103 | PENINSULA | 5.273 | 14.6725 | 1.871% | 0 | 0 | 42.92% | 0% | 0 | 0.0086216 | 1 | 2.0756 | 0.017895 | Low | Low | Low | 3048 | 2994 | 0.0086216
RISING RIVER 11019032 | RISING RIVER 1101 | NORTH VALLEY | 23.4901 | 16.8815 | 99.94% | 5 | 2 | 100% | 0% | 0 | 0.033124 | 1 | 0.53301 | 0.017655 | Medium | Medium | Low | 3049 | 2005 | 0.033124
GREENBRAE 1104751 | GREENBRAE 1104 | NORTH BAY | 0.079918 | 10 | 0% | 0 | 1 | 2.532% | 0% | 0 | 0.0049198 | 1 | 3.5848 | 0.017636 | Low | Low | High | 3050 | 3151 | 0.0049198
PIT NO 3 21011480 | PIT NO 3 2101 | NORTH VALLEY | 2.2265 | 10 | 27.11% | 1 | 1 | 90.29% | 0% | 0 | 0.016964 | 1 | 1.0365 | 0.017582 | Low | Low | Low | 3051 | 2530 | 0.016964
FROGTOWN 1702CB | FROGTOWN 1702 | STOCKTON | 2.2987 | 10 | 21.1% | 0 | 2 | 44.33% | 0% | 0 | 0.0090529 | 1 | 1.9418 | 0.017579 | Low | Low | Low | 3052 | 2974 | 0.0090529
BIG RIVER 110155402 | BIG RIVER 1101 | HUMBOLDT | 2.6094 | 10 | 0.156% | 5 | 5 | 28.18% | 0% | 0 | 0.0073839 | 1 | 2.3739 | 0.017528 | Low | Low | Medium | 3053 | 3037 | 0.0073839
LUCERNE 11034624 | LUCERNE 1103 | HUMBOLDT | 0.73972 | 10 | 26.07% | 0 | 0 | 19.5% | 0% | 0 | 0.0070666 | 1 | 2.4759 | 0.017496 | Low | Low | Medium | 3054 | 3053 | 0.0070666
GEYSERVILLE 1101CB | GEYSERVILLE 1101 | SONOMA | 0.2847 | 40.3314 | 82.04% | 0 | 1 | 3.457% | 0% | 0 | 0.011941 | 1 | 1.4595 | 0.017428 | Low | Low | Low | 3055 | 2812 | 0.011941
FORT BRAGG A 1104CB | FORT BRAGG A 1104 | HUMBOLDT | 0.049503 | 10 | 0% | 1 | 0 | 1.775% | 0% | 0 | 0.0048453 | 1 | 3.575 | 0.017322 | Low | Low | High | 3056 | 3157 | 0.0048453
OROVILLE 11042588 | OROVILLE 1104 | NORTH VALLEY | 0.2392 | 13.5731 | 31.06% | 1 | 0 | 2.673% | 0% | 0 | 0.0064634 | 1 | 2.6797 | 0.01732 | Low | Low | Medium | 3057 | 3082 | 0.0064634
SALT SPRINGS 21011216 | SALT SPRINGS 2101 | STOCKTON | 5.4385 | 73.7435 | 99.91% | 0 | 1 | 98.38% | 0% | 0 | 0.056184 | 1 | 0.30767 | 0.017286 | Medium | Medium | Low | 3058 | 1612 | 0.056184
HOLLISTER 21054724 | HOLLISTER 2105 | CENTRAL COAST | 3.4016 | 78.2881 | 100% | 0 | 0 | 12.91% | 0% | 0 | 0.019187 | 1 | 0.89991 | 0.017267 | Low | Low | Low | 3059 | 2435 | 0.019187
FORT BRAGG A 1101CB | FORT BRAGG A 1101 | HUMBOLDT | 0.22122 | 10 | 0% | 0 | 1 | 2.86% | 0% | 0 | 0.0049359 | 1 | 3.4946 | 0.017249 | Low | Low | High | 3060 | 3148 | 0.0049359
COVELO 1101562360 | COVELO 1101 | HUMBOLDT | 2.2904 | 16.1283 | 100% | 0 | 1 | 6.052% | 0% | 0 | 0.012043 | 1 | 1.4309 | 0.017233 | Low | Low | Low | 3061 | 2805 | 0.012043
BEAR VALLEY 210190550 | BEAR VALLEY 2101 | YOSEMITE | 8.0073 | 10 | 99.83% | 0 | 6 | 100% | 0% | 0 | 0.032169 | 1 | 0.53108 | 0.017084 | Medium | Medium | Low | 3062 | 2040 | 0.032169
POINT ARENA 1101476 | POINT ARENA 1101 | HUMBOLDT | 2.7213 | 21.4527 | 0% | 6 | 2 | 18.23% | 0% | 0 | 0.0068718 | 1 | 2.4696 | 0.01697 | Low | Low | Medium | 3063 | 3060 | 0.0068718
IGNACIO 1104 | IGNACIO 1104 | NORTH BAY | 0.012266 | 10 | 0% | 0 | 0 | 20.53% | 0% | 0 | 0.005765 | 1 | 2.9425 | 0.016964 | Low | Low | Medium | 3064 | 3115 | 0.005765
POTTER VALLEY P H 1105990354 | POTTER VALLEY P H 1105 | HUMBOLDT | 0.0040482 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.331 | 0.016897 | Low | Low | Low | 3065 | 2732 | 0.012695
PIT NO 5 11011660 | PIT NO 5 1101 | NORTH VALLEY | 4.8851 | 10 | 71.19% | 4 | 4 | 100% | 0% | 0 | 0.033496 | 1 | 0.50439 | 0.016895 | Medium | Medium | Low | 3066 | 1995 | 0.033496
POTTER VALLEY PH 11054634 | POTTER VALLEY PH 1105 | HUMBOLDT | 0.0052407 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.3294 | 0.016878 | Low | Low | Low | 3067 | 2732 | 0.012695
POTTER VALLEY P H 1104CB | POTTER VALLEY P H 1104 | HUMBOLDT | 0.077279 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.3279 | 0.016858 | Low | Low | Low | 3068 | 2735 | 0.012695
POTTER VALLEY P H 11054634 | POTTER VALLEY P H 1105 | HUMBOLDT | 0.13813 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.3268 | 0.016844 | Low | Low | Low | 3069 | 2735 | 0.012695
SAN LEANDRO U 1109CR344 | SAN LEANDRO U 1109 | MISSION | 0.097411 | 10 | 0% | 0 | 0 | 3.929% | 0% | 0 | 0.0048858 | 1 | 3.393 | 0.016577 | Low | Low | High | 3070 | 3154 | 0.0048858
OAKLAND J 1116CR420 | OAKLAND J 1116 | EAST BAY | 0.031861 | 10 | 0% | 0 | 0 | 0.2787% | 0% | 0 | 0.0047111 | 1 | 3.508 | 0.016527 | Low | Low | High | 3071 | 3177 | 0.0047111
PANOCHE 11034036 | PANOCHE 1103 | YOSEMITE | 8.0979 | 77.6294 | 100% | 0 | 1 | 32.26% | 0% | 0 | 0.023574 | 1 | 0.7002 | 0.016507 | Medium | Medium | Low | 3072 | 2293 | 0.023574
TEMPLETON 2108A64 | TEMPLETON 2108 | LOS PADRES | 1.3676 | 10 | 21.6% | 0 | 0 | 11.56% | 0% | 0 | 0.0062941 | 1 | 2.6112 | 0.016435 | Low | Low | Medium | 3073 | 3088 | 0.0062941
DEL MAR 210938684 | DEL MAR 2109 | SIERRA | 0.062211 | 10 | 0% | 0 | 0 | 6.669% | 0% | 0 | 0.0050211 | 1 | 3.2725 | 0.016432 | Low | Low | High | 3074 | 3143 | 0.0050211
JOLON 1103CB | JOLON 1103 | CENTRAL COAST | 14.8367 | 53.4685 | 41.31% | 0 | 2 | 82.37% | 0% | 0 | 0.020833 | 1 | 0.78084 | 0.016268 | Low | Low | Low | 3075 | 2375 | 0.020833
SHINGLE SPRINGS 210851474 | SHINGLE SPRINGS 2108 | SIERRA | 0.24496 | 10 | 0% | 0 | 0 | 5.255% | 0% | 0 | 0.0049508 | 1 | 3.2752 | 0.016215 | Low | Low | High | 3076 | 3147 | 0.0049508
SUMMIT 1101742 | SUMMIT 1101 | SIERRA | 0.86692 | 10 | 60.19% | 0 | 1 | 66.72% | 0% | 0 | 0.017361 | 1 | 0.93316 | 0.016201 | Low | Low | Low | 3077 | 2515 | 0.017361
GEYSERVILLE 1102756 | GEYSERVILLE 1102 | SONOMA | 0.58953 | 10 | 0% | 0 | 1 | 100% | 0% | 0 | 0.012961 | 1 | 1.2459 | 0.016148 | Low | Low | Low | 3078 | 2716 | 0.012961
SNEATH LANE 110275844 | SNEATH LANE 1102 | PENINSULA | 0.025403 | 10 | 0% | 0 | 0 | 4.723% | 0% | 0 | 0.0049246 | 1 | 3.2777 | 0.016141 | Low | Low | High | 3079 | 3150 | 0.0049246
MC ARTHUR 11021324 | MC ARTHUR 1102 | NORTH VALLEY | 0.91154 | 54.3228 | 100% | 0 | 0 | 3.568% | 0% | 0 | 0.014895 | 1 | 1.0821 | 0.016117 | Low | Low | Low | 3080 | 2612 | 0.014895
FORT ROSS 1121560 | FORT ROSS 1121 | SONOMA | 5.3342 | 23.1043 | 0.06425% | 1 | 0 | 90.51% | 0% | 0 | 0.0128 | 1 | 1.2567 | 0.016087 | Low | Low | Low | 3081 | 2725 | 0.0128
SALT SPRINGS 210110416 | SALT SPRINGS 2101 | STOCKTON | 0.57657 | 81.6052 | 94.63% | 2 | 1 | 100% | 0% | 0 | 0.045848 | 1 | 0.35085 | 0.016086 | Medium | Medium | Low | 3082 | 1749 | 0.045848
GARBERVILLE 1102 | GARBERVILLE 1102 | HUMBOLDT | 0.096479 | 11.5575 | 97.17% | 0 | 0 | 86.15% | 0% | 0 | 0.024601 | 1 | 0.65244 | 0.016051 | Medium | Medium | Low | 3083 | 2256 | 0.024601
MILPITAS 1109XR044 | MILPITAS 1109 | SAN JOSE | 0.07893 | 10 | 0% | 0 | 0 | 4.212% | 0% | 0 | 0.0048996 | 1 | 3.2735 | 0.016039 | Low | Low | High | 3084 | 3153 | 0.0048996
MONTEREY 04012642 | MONTEREY 0401 | CENTRAL COAST | 0.26645 | 10 | 0% | 0 | 0 | 10.11% | 0% | 0 | 0.0051963 | 1 | 3.0669 | 0.015936 | Low | Low | Medium | 3085 | 3134 | 0.0051963
ALHAMBRA 1102CB | ALHAMBRA 1102 | DIABLO | 0.16935 | 10 | 0% | 0 | 0 | 2.96% | 0% | 0 | 0.0048388 | 1 | 3.2866 | 0.015903 | Low | Low | High | 3086 | 3159 | 0.0048388
VIEJO 22039094 | VIEJO 2203 | CENTRAL COAST | 0.038317 | 10 | 0% | 0 | 0 | 1.572% | 0% | 0 | 0.0047723 | 1 | 3.3195 | 0.015842 | Low | Low | High | 3087 | 3167 | 0.0047723
RIO DELL 11024230 | RIO DELL 1102 | HUMBOLDT | 22.9435 | 79.495 | 27.47% | 20 | 5 | 99.94% | 0% | 0 | 0.05306 | 1 | 0.29839 | 0.015832 | Medium | Medium | Low | 3088 | 1647 | 0.05306
COVELO 1101536 | COVELO 1101 | HUMBOLDT | 0.011418 | 10 | 100% | 1 | 0 | 0.05103% | 0% | 0 | 0.012329 | 1 | 1.2835 | 0.015825 | Low | Low | Low | 3089 | 2782 | 0.012329
FRANKLIN 1101P132 | FRANKLIN 1101 | EAST BAY | 0.033203 | 10 | 0% | 0 | 0 | 2.185% | 0% | 0 | 0.0048015 | 1 | 3.2929 | 0.015811 | Low | Low | High | 3090 | 3162 | 0.0048015
RINCON 1102640 | RINCON 1102 | SONOMA | 0.04813 | 10 | 0% | 0 | 0 | 1.143% | 0% | 0 | 0.0047519 | 1 | 3.3054 | 0.015707 | Low | Low | High | 3091 | 3170 | 0.0047519
SALT SPRINGS 21023118 | SALT SPRINGS 2102 | STOCKTON | 0.07196 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.54869 | 0.015644 | Medium | Medium | Low | 3092 | 2154 | 0.028512
VACAVILLE 110847860 | VACAVILLE 1108 | SACRAMENTO | 0.28908 | 10 | 0% | 0 | 0 | 7.334% | 0% | 0 | 0.0050545 | 1 | 3.0859 | 0.015598 | Low | Low | High | 3093 | 3141 | 0.0050545
CAROLANDS 040484797 | CAROLANDS 0404 | PENINSULA | 0.013784 | 10 | 0% | 0 | 0 | 1.034% | 0% | 0 | 0.0047467 | 1 | 3.2801 | 0.01557 | Low | Low | High | 3094 | 3171 | 0.0047467
GARBERVILLE 11022540 | GARBERVILLE 1102 | HUMBOLDT | 15.3454 | 59.7556 | 6.792% | 13 | 5 | 85.73% | 0% | 0 | 0.046446 | 1 | 0.33411 | 0.015518 | Medium | Medium | Low | 3095 | 1732 | 0.046446
ARCATA 112233060 | ARCATA 1122 | HUMBOLDT | 0.34235 | 10 | 0% | 0 | 1 | 7.017% | 0% | 0 | 0.0051448 | 1 | 3.0094 | 0.015483 | Low | Low | Medium | 3096 | 3137 | 0.0051448
HOPLAND 1101CB | HOPLAND 1101 | HUMBOLDT | 0.39955 | 10 | 100% | 0 | 1 | 6.5% | 0% | 0 | 0.011606 | 1 | 1.3337 | 0.015479 | Low | Low | Low | 3097 | 2830 | 0.011606
BIG MEADOWS 21012510 | BIG MEADOWS 2101 | NORTH VALLEY | 5.0492 | 32.6868 | 6.505% | 7 | 2 | 57.3% | 0% | 0 | 0.015201 | 1 | 1.0173 | 0.015464 | Low | Low | Low | 3098 | 2603 | 0.015201
RED BLUFF 1105161818 | RED BLUFF 1105 | NORTH VALLEY | 0.38337 | 10 | 100% | 0 | 0 | 8.045% | 0% | 0 | 0.011543 | 1 | 1.3232 | 0.015274 | Low | Low | Low | 3099 | 2833 | 0.011543
BRUNSWICK 111095576 | BRUNSWICK 1110 | SIERRA | 0.15603 | 10 | 0% | 0 | 0 | 4.385% | 0% | 0 | 0.004908 | 1 | 3.0967 | 0.015199 | Low | Low | High | 3100 | 3152 | 0.004908
REEDLEY 11127240 | REEDLEY 1112 | FRESNO | 0.0028032 | 10 | 0% | 0 | 0 | 0.01029% | 0% | 0 | 0.0046985 | 1 | 3.2223 | 0.01514 | Low | Low | High | 3101 | 3181 | 0.0046985
MAXWELL 11053008 | MAXWELL 1105 | SACRAMENTO | 1.6684 | 73.9154 | 100% | 0 | 0 | 12.26% | 0% | 0 | 0.018513 | 1 | 0.80874 | 0.014972 | Low | Low | Low | 3102 | 2464 | 0.018513
POSO MOUNTAIN 21011703 | POSO MOUNTAIN 2101 | KERN | 0.0074631 | 10 | 0% | 0 | 0 | 0.304% | 0% | 0 | 0.0053821 | 1 | 2.7786 | 0.014955 | Low | Low | Medium | 3103 | 3129 | 0.0053821
RISING RIVER 11011532 | RISING RIVER 1101 | NORTH VALLEY | 3.0653 | 21.21 | 32.28% | 0 | 0 | 62.2% | 0% | 0 | 0.012255 | 1 | 1.2187 | 0.014936 | Low | Low | Low | 3104 | 2789 | 0.012255
CORRAL 110175204 | CORRAL 1101 | STOCKTON | 1.1128 | 10 | 10.09% | 0 | 0 | 5.993% | 0% | 0 | 0.0054182 | 1 | 2.7419 | 0.014856 | Low | Low | Medium | 3105 | 3127 | 0.0054182
ALTO 1121CB | ALTO 1121 | NORTH BAY | 0.013093 | 10 | 0% | 0 | 0 | 0.2456% | 0% | 0 | 0.0047095 | 1 | 3.1177 | 0.014683 | Low | Low | High | 3106 | 3178 | 0.0047095
ALTO 112088190 | ALTO 1120 | NORTH BAY | 0.01959 | 10 | 0% | 0 | 0 | 0.6244% | 0% | 0 | 0.0047274 | 1 | 3.0907 | 0.014611 | Low | Low | High | 3107 | 3174 | 0.0047274
WESTLEY 11039010 | WESTLEY 1103 | YOSEMITE | 0.92376 | 10 | 100% | 0 | 0 | 2.686% | 0% | 0 | 0.010946 | 1 | 1.3317 | 0.014577 | Low | Low | Low | 3108 | 2872 | 0.010946
BEAR VALLEY 210110019 | BEAR VALLEY 2101 | YOSEMITE | 1.9804 | 23.7531 | 100% | 0 | 6 | 100% | 0% | 0 | 0.04012 | 1 | 0.35957 | 0.014426 | Medium | Medium | Low | 3109 | 1853 | 0.04012
FORT BRAGG A 11021226 | FORT BRAGG A 1102 | HUMBOLDT | 1.1335 | 10 | 21.46% | 0 | 3 | 14.45% | 0% | 0 | 0.0068882 | 1 | 2.0906 | 0.0144 | Low | Low | Low | 3110 | 3059 | 0.0068882
GEYSERVILLE 1101480 | GEYSERVILLE 1101 | SONOMA | 1.4699 | 10 | 99.61% | 0 | 0 | 9.197% | 0% | 0 | 0.011639 | 1 | 1.237 | 0.014397 | Low | Low | Low | 3111 | 2827 | 0.011639
RISING RIVER 11011530 | RISING RIVER 1101 | NORTH VALLEY | 10.3786 | 10.5372 | 70.85% | 4 | 0 | 58.6% | 0% | 0 | 0.01587 | 1 | 0.8986 | 0.014261 | Low | Low | Low | 3112 | 2582 | 0.01587
BRUNSWICK 110765574 | BRUNSWICK 1107 | SIERRA | 0.053599 | 10 | 0% | 0 | 0 | 3.058% | 0% | 0 | 0.0048435 | 1 | 2.9407 | 0.014243 | Low | Low | Medium | 3113 | 3158 | 0.0048435
OCEANO 1105V42 | OCEANO 1105 | LOS PADRES | 0.34173 | 10 | 0% | 0 | 0 | 14.57% | 0% | 0 | 0.0054323 | 1 | 2.6024 | 0.014137 | Low | Low | Medium | 3114 | 3126 | 0.0054323
BRUNSWICK 1110CB | BRUNSWICK 1110 | SIERRA | 0.0037878 | 10 | 0% | 0 | 0 | 0.2212% | 0% | 0 | 0.0047084 | 1 | 2.9563 | 0.01392 | Low | Low | Medium | 3115 | 3179 | 0.0047084
CLARK ROAD 11022094 | CLARK ROAD 1102 | NORTH VALLEY | 0.57902 | 10 | 17.05% | 0 | 0 | 16.85% | 0% | 0 | 0.0063918 | 1 | 2.1553 | 0.013776 | Low | Low | Low | 3116 | 3085 | 0.0063918
PALMER 1101M88 | PALMER 1101 | LOS PADRES | 2.2617 | 68.2305 | 27.53% | 0 | 1 | 14.75% | 0% | 0 | 0.011798 | 1 | 1.1586 | 0.013669 | Low | Low | Low | 3117 | 2816 | 0.011798
RESERVATION ROAD 110222136 | RESERVATION ROAD 1102 | CENTRAL COAST | 1.1023 | 40.7641 | 13.41% | 0 | 0 | 19.9% | 0% | 0 | 0.0078815 | 1 | 1.7282 | 0.013621 | Low | Low | Low | 3118 | 3016 | 0.0078815
ELK 1101900 | ELK 1101 | HUMBOLDT | 6.0335 | 22.7757 | 2.097% | 2 | 3 | 29.53% | 0% | 0 | 0.0087294 | 1 | 1.5553 | 0.013577 | Low | Low | Low | 3119 | 2988 | 0.0087294
VOLTA 11011596 | VOLTA 1101 | NORTH VALLEY | 21.7972 | 45.4978 | 99.98% | 1 | 12 | 100% | 0% | 0 | 0.052789 | 1 | 0.25608 | 0.013518 | Medium | Medium | Low | 3120 | 1651 | 0.052789
SUMMIT 11022302 | SUMMIT 1102 | SIERRA | 1.4575 | 10 | 25.54% | 1 | 4 | 100% | 0% | 0 | 0.022343 | 1 | 0.59618 | 0.01332 | Medium | Medium | Low | 3121 | 2322 | 0.022343
PEORIA 17048040 | PEORIA 1704 | YOSEMITE | 8.9787 | 41.627 | 97.88% | 2 | 3 | 34.87% | 0% | 0 | 0.02277 | 1 | 0.58079 | 0.013225 | Medium | Medium | Low | 3122 | 2314 | 0.02277
GIRVAN 1101CB | GIRVAN 1101 | NORTH VALLEY | 0.35544 | 10 | 1.64% | 0 | 0 | 10.78% | 0% | 0 | 0.0053021 | 1 | 2.487 | 0.013186 | Low | Low | Medium | 3123 | 3132 | 0.0053021
CORNING 110193362 | CORNING 1101 | NORTH VALLEY | 0.36788 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 1.0353 | 0.013144 | Low | Low | Low | 3124 | 2735 | 0.012695
MERCED FALLS 1102CB | MERCED FALLS 1102 | YOSEMITE | 8.7968 | 48.2872 | 48.16% | 0 | 1 | 34.84% | 0% | 0 | 0.014879 | 1 | 0.87183 | 0.012972 | Low | Low | Low | 3125 | 2613 | 0.014879
RIO DELL 11021504 | RIO DELL 1102 | HUMBOLDT | 8.4162 | 77.8437 | 6.428% | 4 | 1 | 69.81% | 0% | 0 | 0.016871 | 1 | 0.76309 | 0.012874 | Low | Low | Low | 3126 | 2532 | 0.016871
CAYUCOS 1101W14 | CAYUCOS 1101 | LOS PADRES | 0.012808 | 10 | 0% | 0 | 0 | 0.1056% | 0% | 0 | 0.004703 | 1 | 2.7337 | 0.012857 | Low | Low | Medium | 3127 | 3180 | 0.004703
HOPLAND 1101558 | HOPLAND 1101 | HUMBOLDT | 0.37929 | 10 | 97.04% | 0 | 0 | 4.114% | 0% | 0 | 0.010837 | 1 | 1.1824 | 0.012815 | Low | Low | Low | 3128 | 2881 | 0.010837
BROWNS VALLEY 110136622 | BROWNS VALLEY 1101 | SIERRA | 2.3766 | 10 | 8.927% | 0 | 1 | 25.35% | 0% | 0 | 0.0066455 | 1 | 1.9026 | 0.012644 | Low | Low | Low | 3129 | 3069 | 0.0066455
PIT NO 1 11019702 | PIT NO 1 1101 | NORTH VALLEY | 0.44484 | 10 | 24.55% | 0 | 0 | 4.849% | 0% | 0 | 0.0060315 | 1 | 2.0734 | 0.012506 | Low | Low | Low | 3130 | 3105 | 0.0060315
MC ARTHUR 11011492 | MC ARTHUR 1101 | NORTH VALLEY | 9.6647 | 34.9258 | 100% | 1 | 0 | 31.38% | 0% | 0 | 0.019862 | 1 | 0.62862 | 0.012486 | Low | Low | Low | 3131 | 2416 | 0.019862
MC ARTHUR 110138998 | MC ARTHUR 1101 | NORTH VALLEY | 11.0305 | 56.1464 | 63.76% | 0 | 2 | 67.61% | 0% | 0 | 0.021999 | 1 | 0.56625 | 0.012457 | Medium | Medium | Low | 3132 | 2337 | 0.021999
PIT NO 5 11011606 | PIT NO 5 1101 | NORTH VALLEY | 5.5302 | 10 | 89.8% | 1 | 2 | 100% | 0% | 0 | 0.031556 | 1 | 0.39242 | 0.012383 | Medium | Medium | Low | 3133 | 2059 | 0.031556
SUMMIT 110147786 | SUMMIT 1101 | SIERRA | 1.7732 | 10 | 6.416% | 0 | 1 | 100% | 0% | 0 | 0.017764 | 1 | 0.69667 | 0.012376 | Low | Low | Low | 3134 | 2500 | 0.017764
SALT SPRINGS 21013116 | SALT SPRINGS 2101 | STOCKTON | 0.70592 | 10 | 100% | 0 | 1 | 70.33% | 0% | 0 | 0.021776 | 1 | 0.56292 | 0.012258 | Low | Low | Low | 3135 | 2344 | 0.021776
SUMMIT 110148636 | SUMMIT 1101 | SIERRA | 0.057422 | 10 | 100% | 0 | 0 | 2.116% | 0% | 0 | 0.010884 | 1 | 1.1135 | 0.01212 | Low | Low | Low | 3136 | 2876 | 0.010884
LAURELES 1112CB | LAURELES 1112 | CENTRAL COAST | 0.015644 | 10 | 0% | 0 | 0 | 0.6574% | 0% | 0 | 0.0047289 | 1 | 2.5304 | 0.011966 | Low | Low | Medium | 3137 | 3173 | 0.0047289
MARTELL 1103CB | MARTELL 1103 | STOCKTON | 0.8745 | 10 | 17.84% | 0 | 0 | 13.95% | 0% | 0 | 0.0062499 | 1 | 1.9128 | 0.011955 | Low | Low | Low | 3138 | 3091 | 0.0062499
MC ARTHUR 11011490 | MC ARTHUR 1101 | NORTH VALLEY | 9.1248 | 10 | 79.7% | 0 | 4 | 60.48% | 0% | 0 | 0.02318 | 1 | 0.49873 | 0.01156 | Medium | Medium | Low | 3139 | 2304 | 0.02318
GLENN 11012012 | GLENN 1101 | NORTH VALLEY | 2.3498 | 85 | 100% | 0 | 0 | 7.814% | 0% | 0 | 0.01909 | 1 | 0.59338 | 0.011328 | Low | Low | Low | 3140 | 2442 | 0.01909
OLEMA 110149756 | OLEMA 1101 | NORTH BAY | 0.14983 | 10 | 0% | 0 | 2 | 2.553% | 0% | 0 | 0.0057386 | 1 | 1.9687 | 0.011298 | Low | Low | Low | 3141 | 3118 | 0.0057386
ANTELOPE 11011631 | ANTELOPE 1101 | KERN | 0.75322 | 47.1276 | 100% | 0 | 0 | 6.682% | 0% | 0 | 0.014633 | 1 | 0.73269 | 0.010722 | Low | Low | Low | 3142 | 2629 | 0.014633
MC ARTHUR 110137344 | MC ARTHUR 1101 | NORTH VALLEY | 0.26567 | 10 | 48.66% | 0 | 0 | 2.972% | 0% | 0 | 0.0072135 | 1 | 1.4849 | 0.010712 | Low | Low | Low | 3143 | 3047 | 0.0072135
STONE CORRAL 11087100 | STONE CORRAL 1108 | FRESNO | 2.9159 | 10 | 14.41% | 0 | 0 | 15.91% | 0% | 0 | 0.0061962 | 1 | 1.7025 | 0.010549 | Low | Low | Low | 3144 | 3095 | 0.0061962
FREMONT 1104MR707 | FREMONT 1104 | MISSION | 1.4479 | 10 | 0% | 0 | 0 | 16.1% | 0% | 0 | 0.0055159 | 1 | 1.8893 | 0.010421 | Low | Low | Low | 3145 | 3124 | 0.0055159
CUYAMA 1103622728 | CUYAMA 1103 | KERN | 2.3769 | 95 | 100% | 0 | 0 | 6.184% | 0% | 0 | 0.02009 | 1 | 0.49944 | 0.010034 | Low | Low | Low | 3146 | 2406 | 0.02009
MERCED FALLS 11029460 | MERCED FALLS 1102 | YOSEMITE | 8.5158 | 30.9683 | 53.31% | 0 | 0 | 95.4% | 0% | 0 | 0.031807 | 1 | 0.30868 | 0.009818 | Medium | Medium | Low | 3147 | 2050 | 0.031807
ELK 1101CB | ELK 1101 | HUMBOLDT | 0.88673 | 10 | 0% | 1 | 0 | 90.98% | 0% | 0 | 0.011764 | 1 | 0.82427 | 0.0096969 | Low | Low | Low | 3148 | 2818 | 0.011764
PANOCHE 11034016 | PANOCHE 1103 | YOSEMITE | 2.3488 | 61.1971 | 100% | 0 | 0 | 18.31% | 0% | 0 | 0.020566 | 1 | 0.46613 | 0.0095864 | Low | Low | Low | 3149 | 2384 | 0.020566
RIO DELL 11028768 | RIO DELL 1102 | HUMBOLDT | 0.28084 | 10 | 0% | 0 | 0 | 4.757% | 0% | 0 | 0.0049263 | 1 | 1.9394 | 0.0095539 | Low | Low | Low | 3150 | 3149 | 0.0049263
MERCED FALLS 11029470 | MERCED FALLS 1102 | YOSEMITE | 22.9864 | 12.6287 | 82.62% | 0 | 4 | 100% | 0% | 0 | 0.040338 | 1 | 0.22626 | 0.0091268 | Medium | Medium | Low | 3151 | 1845 | 0.040338
JOLON 110268034 | JOLON 1102 | CENTRAL COAST | 0.019914 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.71712 | 0.0091041 | Low | Low | Low | 3152 | 2735 | 0.012695
BEAR VALLEY 2105CB | BEAR VALLEY 2105 | YOSEMITE | 3.852 | 80.717 | 62.63% | 2 | 1 | 100% | 0% | 0 | 0.040229 | 1 | 0.22311 | 0.0089755 | Medium | Medium | Low | 3153 | 1851 | 0.040229
PIT NO 5 110190846 | PIT NO 5 1101 | NORTH VALLEY | 0.092785 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 1 | 0.31428 | 0.0089606 | Medium | Medium | Low | 3154 | 2136 | 0.028512
PEORIA 170492888 | PEORIA 1704 | YOSEMITE | 0.24891 | 10 | 100% | 0 | 0 | 52.34% | 0% | 0 | 0.017878 | 1 | 0.4954 | 0.0088569 | Low | Low | Low | 3155 | 2495 | 0.017878
PEORIA 1701 | PEORIA 1701 | YOSEMITE | 0.00281 | 10 | 0% | 0 | 0 | 100% | 0% | 0 | 0.012695 | 1 | 0.6973 | 0.0088524 | Low | Low | Low | 3156 | 2735 | 0.012695
CLARK ROAD 1102CB | CLARK ROAD 1102 | NORTH VALLEY | 0.16153 | 10 | 1.759% | 0 | 1 | 10.59% | 0% | 0 | 0.006177 | 1 | 1.3847 | 0.0085535 | Low | Low | Low | 3157 | 3096 | 0.006177
PIT NO 3 21011360 | PIT NO 3 2101 | NORTH VALLEY | 21.8208 | 46.6037 | 72.84% | 2 | 7 | 96.78% | 0% | 0 | 0.033534 | 1 | 0.24766 | 0.0083049 | Medium | Medium | Low | 3158 | 1994 | 0.033534
PIT NO 5 11011614 | PIT NO 5 1101 | NORTH VALLEY | 1.8659 | 92.5056 | 100% | 0 | 0 | 100% | 0% | 0 | 0.049074 | 1 | 0.16422 | 0.0080592 | Medium | Medium | Low | 3159 | 1694 | 0.049074
SAN ARDO 11017094 | SAN ARDO 1101 | CENTRAL COAST | 1.1437 | 50.6148 | 100% | 0 | 0 | 6.71% | 0% | 0 | 0.014985 | 1 | 0.52695 | 0.0078965 | Low | Low | Low | 3160 | 2608 | 0.014985
ELK 11011300 | ELK 1101 | HUMBOLDT | 3.0348 | 10 | 21.85% | 10 | 1 | 31.85% | 0% | 0 | 0.0089861 | 1 | 0.83981 | 0.0075467 | Low | Low | Low | 3161 | 2977 | 0.0089861
PIT NO 3 21011386 | PIT NO 3 2101 | NORTH VALLEY | 5.8084 | 10 | 93.45% | 4 | 0 | 84.51% | 0% | 0 | 0.027889 | 1 | 0.24957 | 0.0069602 | Medium | Medium | Low | 3162 | 2164 | 0.027889
VOLTA 11011640 | VOLTA 1101 | NORTH VALLEY | 10.4338 | 80.2423 | 83.4% | 1 | 4 | 100% | 0% | 0 | 0.072189 | 1 | 0.092106 | 0.006649 | High | High | Low | 3163 | 1459 | 0.072189
MERCED FALLS 110238748 | MERCED FALLS 1102 | YOSEMITE | 15.288 | 16.9529 | 100% | 0 | 0 | 100% | 0% | 0 | 0.033981 | 1 | 0.19224 | 0.0065325 | Medium | Medium | Low | 3164 | 1978 | 0.033981
MC ARTHUR 11011488 | MC ARTHUR 1101 | NORTH VALLEY | 2.4985 | 10 | 70.57% | 0 | 2 | 7.462% | 0% | 0 | 0.0094078 | 1 | 0.63499 | 0.0059739 | Low | Low | Low | 3165 | 2959 | 0.0094078
MERCED FALLS 110222774 | MERCED FALLS 1102 | YOSEMITE | 1.0091 | 37.0223 | 100% | 0 | 0 | 27.2% | 0% | 0 | 0.016738 | 1 | 0.33771 | 0.0056526 | Low | Low | Low | 3166 | 2538 | 0.016738
SAN ARDO 11017632 | SAN ARDO 1101 | CENTRAL COAST | 0.79963 | 10 | 100% | 0 | 0 | 9.729% | 0% | 0 | 0.011737 | 1 | 0.481 | 0.0056455 | Low | Low | Low | 3167 | 2819 | 0.011737
CORNING 110187304 | CORNING 1101 | NORTH VALLEY | 1.5372 | 10 | 14.41% | 0 | 3 | 10.47% | 0% | 0 | 0.0062491 | 1 | 0.88021 | 0.0055005 | Low | Low | Low | 3168 | 3092 | 0.0062491
SAN ARDO 110193072 | SAN ARDO 1101 | CENTRAL COAST | 0.72134 | 10 | 63.38% | 0 | 0 | 8.566% | 0% | 0 | 0.0098197 | 1 | 0.54117 | 0.0053141 | Low | Low | Low | 3169 | 2938 | 0.0098197
LOGAN CREEK 21022226 | LOGAN CREEK 2102 | NORTH VALLEY | 3.7103 | 86.8404 | 100% | 0 | 1 | 10.78% | 0% | 0 | 0.020313 | 1 | 0.2575 | 0.0052305 | Low | Low | Low | 3170 | 2392 | 0.020313
PIT NO 5 1101CB | PIT NO 5 1101 | NORTH VALLEY | 0.72275 | 65.782 | 100% | 4 | 2 | 100% | 0% | 0 | 0.045131 | 1 | 0.11458 | 0.0051713 | Medium | Medium | Low | 3171 | 1764 | 0.045131
PIT NO 3 21011482 | PIT NO 3 2101 | NORTH VALLEY | 12.042 | 25.2752 | 56.98% | 0 | 2 | 100% | 0% | 0 | 0.026507 | 1 | 0.19495 | 0.0051676 | Medium | Medium | Low | 3172 | 2203 | 0.026507
SUMMIT 110168706 | SUMMIT 1101 | SIERRA | 0.058904 | 10 | 0% | 0 | 0 | 1.149% | 0% | 0 | 0.0047522 | 1 | 1.0375 | 0.0049304 | Low | Low | Low | 3173 | 3169 | 0.0047522
DUNLAP 11027360 | DUNLAP 1102 | FRESNO | 8.5319 | 14.1381 | 99.93% | 0 | 0 | 100% | 0% | 0 | 0.048964 | 1 | 0.093748 | 0.0045903 | Medium | Medium | Low | 3174 | 1696 | 0.048964
MC ARTHUR 11011544 | MC ARTHUR 1101 | NORTH VALLEY | 14.33 | 61.0373 | 66.86% | 0 | 1 | 51.35% | 0% | 0 | 0.022186 | 1 | 0.18317 | 0.0040638 | Medium | Medium | Low | 3175 | 2327 | 0.022186
RIO DELL 110270960 | RIO DELL 1102 | HUMBOLDT | 3.7354 | 51.8564 | 33.96% | 2 | 2 | 31.94% | 0% | 0 | 0.012119 | 1 | 0.29794 | 0.0036108 | Low | Low | Low | 3176 | 2800 | 0.012119
SPAULDING 1101578852 | SPAULDING 1101 | SIERRA | 20.1063 | 56.8104 | 73.09% | 2 | 12 | 82.23% | 8.84% | 1 | 0.13582 | 1 | 0.021523 | 0.0029234 | High | High | Low | 3177 | 1181 | 0.13582
GARBERVILLE 110197300 | GARBERVILLE 1101 | HUMBOLDT | 14.1538 | 63.6884 | 85.32% | 13 | 2 | 100% | 0% | 0 | 0.1059 | 1 | 0.026166 | 0.0027709 | High | High | Low | 3178 | 1270 | 0.1059
PIT NO 5 11011618 | PIT NO 5 1101 | NORTH VALLEY | 6.0991 | 69.0036 | 93.71% | 0 | 2 | 100% | 0% | 0 | 0.047368 | 1 | 0.028548 | 0.0013523 | Medium | Medium | Low | 3179 | 1719 | 0.047368
OILFIELDS 1103N42 | OILFIELDS 1103 | CENTRAL COAST | 2.2461 | 52.6729 | 47.6% | 0 | 0 | 37.49% | 0% | 0 | 0.013447 | 1 | 0.061363 | 0.00082516 | Low | Low | Low | 3180 | 2688 | 0.013447
SAN MIGUEL 1106N34 | SAN MIGUEL 1106 | LOS PADRES | 0.29269 | 10 | 21.51% | 0 | 0 | 2.142% | 0% | 0 | 0.0065395 | 1 | 0.080486 | 0.00052634 | Low | Low | Low | 3181 | 3078 | 0.0065395
OCEANO 1105V20 | OCEANO 1105 | LOS PADRES | 0.031809 | 10 | 0% | 0 | 0 | 0.5465% | 0% | 0 | 0.0047237 | 0 | 0 | 0 | Low | Low | Low | 3182 | 3182 | 0
ECHO SUMMIT 1101CB | ECHO SUMMIT 1101 | (blank) | 0.03514 | 10 | 100% | 0 | 0 | 100% | 0% | 0 | 0.028512 | 0 | 0 | 0 | Medium | Medium | Low | 3182 | 3182 | 0
MC ARTHUR 110137388 | MC ARTHUR 1101 | NORTH VALLEY | 8.6734 | 54.6058 | 74.62% | 0 | 2 | 69.39% | 0% | 0 | 0.024182 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
CHOLAME 2102X10 | CHOLAME 2102 | LOS PADRES | 19.7574 | 72.3337 | 100% | 0 | 0 | 44.78% | 0% | 0 | 0.028694 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
DUNLAP 110239190 | DUNLAP 1102 | FRESNO | 1.8032 | 10 | 99.73% | 0 | 0 | 100% | 0% | 0 | 0.02845 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
LAYTONVILLE 11011760 | LAYTONVILLE 1101 | HUMBOLDT | 8.2141 | 83.102 | 88.6% | 5 | 4 | 64.9% | 0% | 0 | 0.039524 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
OILFIELDS 11037006 | OILFIELDS 1103 | CENTRAL COAST | 2.4385 | 10 | 100% | 0 | 0 | 16.07% | 0% | 0 | 0.016263 | 0 | 0 | -0.00036352 | Low | Low | Low | 3184 | 3182 | 0
CARLOTTA 112144150 | CARLOTTA 1121 | HUMBOLDT | 3.5728 | 56.6428 | 100% | 0 | 1 | 100% | 0% | 0 | 0.039603 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
DUNLAP 11027050 | DUNLAP 1102 | FRESNO | 9.1044 | 57.339 | 92.11% | 4 | 10 | 100% | 0% | 0 | 0.15825 | 0 | 0 | -0.00036352 | High | High | Low | 3184 | 3182 | 0
PIT NO 5 11013308 | PIT NO 5 1101 | NORTH VALLEY | 0.044135 | 85 | 100% | 0 | 0 | 100% | 0% | 0 | 0.046733 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
EL DORADO PH 210113532 | EL DORADO PH 2101 | SIERRA | 5.3271 | 64.1847 | 100% | 5 | 1 | 100% | 0% | 0 | 0.082958 | 0 | 0 | -0.00036352 | High | High | Low | 3184 | 3182 | 0
BRIDGEVILLE 1102 | BRIDGEVILLE 1102 | HUMBOLDT | 0.0078479 | 90 | 100% | 0 | 0 | 100% | 0% | 0 | 0.048281 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
BRIDGEVILLE 110237486 | BRIDGEVILLE 1102 | HUMBOLDT | 10.3672 | 71.0468 | 99.35% | 4 | 7 | 92.24% | 0% | 0 | 0.054132 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
DUNLAP 11037170 | DUNLAP 1103 | FRESNO | 5.3633 | 51.4528 | 91.12% | 7 | 8 | 100% | 0% | 0 | 0.057836 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
DUNLAP 1102778286 | DUNLAP 1102 | FRESNO | 2.6016 | 93.4441 | 63.93% | 0 | 0 | 100% | 0% | 0 | 0.042218 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
DUNLAP 1102CB | DUNLAP 1102 | FRESNO | 6.506 | 11.6092 | 99.83% | 1 | 2 | 100% | 0% | 0 | 0.034553 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
BOGARD 1101CB | BOGARD 1101 | NORTH VALLEY | 0.51623 | 20.4818 | 100% | 1 | 0 | 100% | 0% | 0 | 0.03523 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
DUNLAP 11037080 | DUNLAP 1103 | FRESNO | 7.9166 | 53.1398 | 56.92% | 4 | 5 | 100% | 0% | 0 | 0.052315 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
DUNLAP 11027290 | DUNLAP 1102 | FRESNO | 0.73169 | 39.1465 | 99.26% | 0 | 9 | 100% | 0% | 0 | 0.04685 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
DUNLAP 1103CB | DUNLAP 1103 | FRESNO | 5.3266 | 46.6515 | 99.77% | 2 | 1 | 100% | 0% | 0 | 0.043161 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
BALCH NO 1 1101R372 | BALCH NO 1 1101 | FRESNO | 6.0973 | 42.1008 | 100% | 0 | 0 | 100% | 0% | 0 | 0.035267 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0
EL DORADO PH 210136764 | EL DORADO PH 2101 | SIERRA | 3.1646 | 79.8685 | 100% | 3 | 0 | 72.39% | 0% | 0 | 0.12435 | 0 | 0 | -0.00036352 | High | High | Low | 3184 | 3182 | 0
BRIDGEVILLE 1102CB | BRIDGEVILLE 1102 | HUMBOLDT | 0.72529 | 72.3371 | 88.58% | 0 | 0 | 5.257% | 0% | 0 | 0.020259 | 0 | 0 | -0.00036352 | Low | Low | Low | 3184 | 3182 | 0
DUNLAP 11037991F | DUNLAP 1103 | FRESNO | 2.6521 | 79.9208 | 100% | 1 | 4 | 100% | 0% | 0 | 0.056283 | 0 | 0 | -0.00036352 | Medium | Medium | Low | 3184 | 3182 | 0

## Dx - Inspection
Dx Prioritization Output - Inspection
Circuit Information |  |  |  |  | Independent Variables | [29 empty] | Dependent Variable | Risk Scoring |  |  |  | Risk Tiers
Feeder Name | Circuit ID | Region Name | Division Name | Tier 2/3 OH Miles | 3-year Average Summer Load | Average Pole Height | Loading Percent - Mile-weighted Average | Conductor Size 2 - % of Miles | Conductor Size 4 - % of Miles | Conductor Size 6 - % of Miles | Conductor_Broken_Damaged | Conductor_Clearance_Impaired | Total Fuses | Material AR - % of Miles | Material C - % of Miles | Pole Species - % Western Red Cedar | Pole Height >45 | Poles Original Treatment: Cellon_Gas | Poles Original Treatment: Copper_Napthenate__CNI_ | Poles Original Treatment: Methane_Propane | Poles Original Treatment: Penta | Poles Original Treatment: Penta_in_Petroleum | Total Splice Count | Switch Type: 14 | Total Switches | Total Poles | Transformers: Avg SummerPCT | Transformers: RatedKVA - 15 | Transformers: RatedKVA - 25 | Transformers: RatedKVA - 50 | Total Transformers | Transformers Version: A3P7 | VoltageRegulators Version: M2C9 | Number of Fuses Per Phase: 1 | Above Average Outage Indicator | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Consolidated Risk Score | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Consolidated Risk Score | Rank Cons Risk | Rank P*C | P*C
WOODACRE 1101 | 043021101 | BAY AREA | NORTH BAY | 37.9171 | 273416.3333 | 43.81 | 20.15% | 5.073% | 33.09% | 36.66% | 32 | 6 | 79 | 29.85% | 45.04% | 9.908% | 250 | 387 | 11 | 7 | 313 | 262 | 0 | 20 | 36 | 1090 | 35.8159 | 113 | 108 | 20 | 359 | 0 | 0 | 79 | 1 | 0.86687 | 49.5253 | 7.3343 | 314.8735 | High | High | High | Top | 1 | 6 | 363.2322
DOWNIEVILLE DIESEL 1101 | 158001101 | NORTHERN | SIERRA | 0.032712 | 0 | 45 | 0% | 100% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.51842 | 102.1389 | 5.2688 | 278.9877 | Medium | High | Medium | Top | 2 | 2 | 538.1461
MONTE RIO 1113 | 042811113 | NORTHERN | SONOMA | 61.2941 | 888801.3333 | 42.5277 | 24.79% | 5.339% | 50.76% | 32.68% | 51 | 13 | 90 | 47.74% | 42.26% | 11.85% | 299 | 593 | 1 | 9 | 644 | 305 | 101 | 24 | 48 | 1806 | 39.267 | 208 | 169 | 92 | 702 | 0 | 0 | 90 | 1 | 0.89768 | 48.4702 | 5.9889 | 260.5828 | High | High | High | Top | 3 | 14 | 290.2846
MORAGA 1105 | 013801105 | BAY AREA | DIABLO | 9.5389 | 587971.3333 | 45.9444 | 37.45% | 0% | 29.87% | 23.07% | 3 | 2 | 13 | 24.38% | 66.25% | 21.95% | 49 | 69 | 0 | 0 | 20 | 13 | 3 | 5 | 6 | 164 | 24.8462 | 19 | 17 | 5 | 54 | 0 | 0 | 12 | 1 | 0.76456 | 47.5187 | 6.7041 | 243.5644 | High | High | High | Top | 4 | 9 | 318.568
MONTE RIO 1112 | 042811112 | NORTHERN | SONOMA | 20.2317 | 364345.6667 | 42.1563 | 33.13% | 13.3% | 28.64% | 27.75% | 26 | 9 | 48 | 43.13% | 41.53% | 7.236% | 112 | 226 | 0 | 12 | 256 | 126 | 11 | 11 | 20 | 691 | 41.4675 | 76 | 53 | 27 | 240 | 0 | 2 | 48 | 1 | 0.82845 | 41.2665 | 5.8415 | 199.7026 | High | High | High | Top | 5 | 25 | 241.057
HALF MOON BAY 1101 | 024101101 | CENTRAL COAST | PENINSULA | 32.9103 | 1062793.6667 | 41.5213 | 27.97% | 0.2214% | 40.67% | 32.07% | 12 | 4 | 45 | 44.44% | 48.11% | 6.897% | 38 | 186 | 0 | 2 | 229 | 27 | 38 | 4 | 8 | 493 | 30.4785 | 57 | 33 | 5 | 169 | 1 | 0 | 45 | 1 | 0.80716 | 36.9629 | 6.6522 | 198.469 | High | High | High | Top | 6 | 21 | 245.8857
WOODSIDE 1101 | 024251101 | CENTRAL COAST | PENINSULA | 42.3143 | 731429.6667 | 42.484 | 26.09% | 0.1141% | 34.56% | 43.73% | 70 | 2 | 106 | 47.82% | 48.88% | 12.26% | 139 | 482 | 0 | 6 | 559 | 67 | 1 | 12 | 22 | 1248 | 20.9813 | 135 | 157 | 23 | 443 | 4 | 1 | 105 | 1 | 0.80161 | 32.5504 | 6.6282 | 172.9485 | High | High | High | Top | 7 | 37 | 215.7519
PIKE CITY 1101 | 152201101 | NORTHERN | SIERRA | 34.5379 | 89793.3333 | 40.9752 | 25.31% | 99.84% | 0% | 0% | 6 | 2 | 37 | 99.84% | 0.1367% | 13.65% | 54 | 324 | 9 | 0 | 87 | 95 | 10 | 4 | 10 | 806 | 38.1636 | 69 | 25 | 6 | 226 | 0 | 0 | 37 | 1 | 0.62309 | 85.7553 | 3.2113 | 171.5898 | Medium | High | Low | Top | 8 | 17 | 275.3846
MONTE RIO 1111 | 042811111 | NORTHERN | SONOMA | 59.7678 | 340795 | 41.9722 | 32.33% | 1.776% | 42.07% | 47.48% | 42 | 28 | 95 | 32.57% | 59.3% | 12.46% | 158 | 426 | 1 | 5 | 563 | 164 | 40 | 24 | 47 | 1372 | 33.6364 | 181 | 77 | 33 | 524 | 0 | 5 | 95 | 1 | 0.84976 | 36.3844 | 5.4039 | 167.0779 | High | High | High | Top | 9 | 47 | 196.6188
TASSAJARA 2108 | 014662108 | BAY AREA | DIABLO | 1.5457 | 1333879 | 44.4186 | 18.89% | 0% | 33.34% | 66.66% | 0 | 0 | 3 | 33.34% | 66.66% | 18.6% | 10 | 13 | 0 | 0 | 15 | 4 | 0 | 1 | 1 | 43 | 54.96 | 9 | 10 | 0 | 25 | 0 | 0 | 3 | 1 | 0.66045 | 41.5134 | 6.0558 | 166.0359 | High | High | High | Top | 10 | 20 | 251.3971
SPANISH CREEK 4401 | 103104401 | NORTHERN | NORTH VALLEY | 7.9163 | 4545.3333 | 47.0543 | 179% | 96.68% | 0% | 3.324% | 1 | 0 | 2 | 10.89% | 89.11% | 37.21% | 54 | 33 | 0 | 0 | 59 | 14 | 0 | 0 | 2 | 129 | 16 | 5 | 5 | 1 | 14 | 0 | 1 | 2 | 1 | 0.56086 | 69.1856 | 4.1141 | 159.6402 | Medium | High | Medium | Top | 11 | 16 | 284.6368
MIRABEL 1101 | 042091101 | NORTHERN | SONOMA | 30.224 | 547280.3333 | 43.036 | 23.83% | 19.53% | 54.19% | 20.9% | 27 | 2 | 49 | 55.16% | 39.46% | 7.376% | 106 | 313 | 0 | 2 | 142 | 58 | 0 | 7 | 11 | 583 | 28.2218 | 87 | 42 | 11 | 252 | 0 | 0 | 49 | 1 | 0.72695 | 39.009 | 5.3754 | 152.4327 | High | High | Medium | Top | 12 | 39 | 209.6888
SIERRA CITY GEN 1101 | 158011101 | NORTHERN | SIERRA | 0.018511 | 0 | 40 | 0% | 100% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 100% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.46796 | 85.4511 | 3.6603 | 146.3655 | Medium | High | Low | Top | 13 | 11 | 312.7725
SILVERADO 2105 | 043432105 | BAY AREA | NORTH BAY | 39.6838 | 1206104.6667 | 42.9808 | 18.97% | 0.5537% | 84.96% | 11.55% | 11 | 5 | 61 | 78.81% | 21.17% | 8.075% | 129 | 311 | 0 | 3 | 114 | 140 | 12 | 24 | 26 | 743 | 53.0083 | 59 | 53 | 20 | 246 | 0 | 0 | 60 | 1 | 0.61045 | 41.9515 | 5.4951 | 140.7273 | Medium | High | High | Top | 14 | 30 | 230.5296
VINEYARD 2108 | 014502108 | CENTRAL COAST | MISSION | 4.6061 | 1483072.6667 | 43.2524 | 10.74% | 0% | 71.39% | 28.55% | 0 | 0 | 15 | 37.6% | 62.34% | 17.31% | 20 | 33 | 0 | 3 | 22 | 11 | 0 | 1 | 3 | 104 | 40.3103 | 11 | 14 | 0 | 33 | 0 | 0 | 15 | 1 | 0.66651 | 35.5506 | 5.877 | 139.2542 | High | High | High | Top | 15 | 40 | 208.9307
MOLINO 1102 | 042571102 | NORTHERN | SONOMA | 113.1393 | 1494417.6667 | 43.6669 | 26.83% | 0.09873% | 58.93% | 35.46% | 38 | 12 | 205 | 55.31% | 39.9% | 7.03% | 582 | 1241 | 3 | 40 | 684 | 353 | 48 | 45 | 59 | 2717 | 31.1546 | 428 | 183 | 42 | 1093 | 0 | 3 | 205 | 1 | 0.71054 | 36.3102 | 4.8722 | 125.7032 | High | High | Medium | Top | 16 | 57 | 176.912
SILVERADO 2104 | 043432104 | BAY AREA | NORTH BAY | 126.0115 | 1582484 | 42.671 | 56.62% | 2.81% | 70.69% | 16.2% | 28 | 8 | 181 | 69.19% | 21.13% | 8.469% | 307 | 997 | 3 | 35 | 670 | 483 | 5 | 39 | 69 | 2633 | 51.0611 | 248 | 201 | 42 | 889 | 0 | 6 | 180 | 1 | 0.64794 | 31.2142 | 6.206 | 125.5164 | Medium | High | High | Top | 17 | 48 | 193.7149
SAN RAFAEL 1108 | 042011108 | BAY AREA | NORTH BAY | 38.5753 | 1208223.3333 | 44.7083 | 17.5% | 3.798% | 18.92% | 56.56% | 59 | 2 | 96 | 19.21% | 63.02% | 10.94% | 519 | 550 | 22 | 13 | 637 | 437 | 46 | 22 | 39 | 1856 | 39.1417 | 150 | 195 | 89 | 616 | 0 | 0 | 96 | 1 | 0.85709 | 15.8796 | 8.7878 | 119.6041 | High | High | High | Top | 18 | 85 | 139.5474
CASTRO VALLEY 1108 | 014091108 | CENTRAL COAST | MISSION | 23.8731 | 633879.3333 | 43.8625 | 25.09% | 1.618% | 53.21% | 31.18% | 14 | 5 | 49 | 18.59% | 68.72% | 12.72% | 93 | 216 | 0 | 9 | 237 | 33 | 0 | 10 | 21 | 613 | 8.2542 | 75 | 76 | 17 | 247 | 1 | 0 | 49 | 1 | 0.82415 | 22.6481 | 6.3834 | 119.1487 | High | High | High | Top | 19 | 80 | 144.572
FITCH MOUNTAIN 1113 | 042751113 | NORTHERN | SONOMA | 76.7611 | 881431 | 42.8272 | 26.89% | 3.271% | 63.28% | 31.49% | 33 | 1 | 77 | 63.56% | 35.4% | 8.406% | 201 | 488 | 0 | 25 | 273 | 195 | 10 | 16 | 21 | 1154 | 29.4603 | 160 | 80 | 8 | 435 | 0 | 1 | 77 | 0 | 0.6378 | 44.6104 | 4.1614 | 118.4028 | Medium | High | Medium | Top | 20 | 52 | 185.6419
ROSSMOOR 1108 | 014161108 | BAY AREA | DIABLO | 13.4853 | 1018341.3333 | 44.9576 | 79.53% | 1.278% | 20.16% | 50.27% | 4 | 0 | 34 | 21.2% | 50.57% | 8.017% | 47 | 87 | 0 | 0 | 68 | 13 | 0 | 6 | 11 | 237 | 20.6591 | 26 | 37 | 4 | 93 | 0 | 0 | 34 | 1 | 0.69505 | 24.5636 | 6.9013 | 117.8266 | High | High | High | Top | 21 | 62 | 169.5214
OLEMA 1101 | 042291101 | BAY AREA | NORTH BAY | 66.1086 | 448317.6667 | 44.1264 | 25.78% | 7.557% | 31.32% | 49.59% | 53 | 7 | 85 | 12.34% | 76.2% | 6.101% | 360 | 527 | 7 | 16 | 499 | 201 | 37 | 19 | 28 | 1557 | 29.0694 | 157 | 117 | 14 | 457 | 0 | 4 | 84 | 1 | 0.77859 | 27.9587 | 5.3446 | 116.3441 | High | High | Medium | Top | 22 | 75 | 149.4287
ALTO 1124 | 042031124 | BAY AREA | NORTH BAY | 30.9272 | 748572.6667 | 44.3557 | 10.74% | 11.84% | 15.43% | 64.15% | 24 | 4 | 70 | 20.63% | 72.31% | 9.419% | 309 | 427 | 12 | 6 | 460 | 168 | 29 | 9 | 18 | 1274 | 36.3527 | 130 | 115 | 43 | 460 | 0 | 0 | 70 | 1 | 0.88167 | 16.3831 | 7.9503 | 114.8378 | High | High | High | Top | 23 | 96 | 130.2498
MORAGA 1101 | 013801101 | BAY AREA | DIABLO | 19.0142 | 238194.3333 | 45.5655 | 51.54% | 0.2943% | 28.08% | 26.07% | 12 | 7 | 26 | 11.36% | 48.52% | 15.48% | 136 | 93 | 0 | 0 | 200 | 34 | 22 | 11 | 30 | 504 | 23.5492 | 62 | 69 | 17 | 198 | 0 | 0 | 26 | 1 | 0.77846 | 20.5225 | 6.8809 | 109.9299 | High | High | High | Top | 24 | 81 | 141.2139
BONNIE NOOK 1102 | 152301102 | NORTHERN | SIERRA | 34.3352 | 96245 | 42.2368 | 13.33% | 82.61% | 12.88% | 4.503% | 4 | 7 | 51 | 85.18% | 14.81% | 14.47% | 86 | 399 | 7 | 0 | 125 | 106 | 3 | 17 | 17 | 919 | 34.8528 | 121 | 44 | 2 | 279 | 0 | 0 | 51 | 1 | 0.51672 | 79.0787 | 2.6595 | 108.6697 | Medium | High | Low | Top | 25 | 38 | 210.3079
BOLINAS 1101 | 042261101 | BAY AREA | NORTH BAY | 36.998 | 354120 | 45.8392 | 71.21% | 6.313% | 30.38% | 16.61% | 5 | 1 | 43 | 15.42% | 45.77% | 10.19% | 169 | 183 | 8 | 10 | 199 | 89 | 9 | 13 | 35 | 569 | 23.6196 | 28 | 27 | 10 | 95 | 0 | 5 | 43 | 0 | 0.48819 | 29.7958 | 6.927 | 100.7604 | Medium | High | High | Top | 26 | 42 | 206.3957
FORT ROSS 1121 | 042851121 | NORTHERN | SONOMA | 94.05 | 141625.6667 | 41.9432 | 26.12% | 13.3% | 55.06% | 26.25% | 25 | 3 | 96 | 60.65% | 37.35% | 4.676% | 121 | 275 | 0 | 7 | 510 | 240 | 2 | 24 | 40 | 1326 | 27.0773 | 158 | 43 | 10 | 396 | 0 | 2 | 96 | 0 | 0.55429 | 46.7686 | 3.8784 | 100.5414 | Medium | High | Medium | Top | 27 | 56 | 181.3878
SANTA ROSA A 1111 | 042151111 | NORTHERN | SONOMA | 5.9664 | 1044190.3333 | 43.6641 | 10.27% | 0% | 60.18% | 39.82% | 1 | 0 | 14 | 60.18% | 39.82% | 12.21% | 32 | 62 | 0 | 0 | 37 | 24 | 0 | 1 | 1 | 131 | 38.7321 | 23 | 9 | 1 | 59 | 0 | 0 | 14 | 1 | 0.6526 | 40.33 | 3.7553 | 98.8371 | Medium | High | Medium | Top | 28 | 73 | 151.4506
DUNBAR 1102 | 043071102 | NORTHERN | SONOMA | 49.625 | 1055070 | 44.5079 | 35.25% | 1.251% | 57.69% | 35.79% | 9 | 8 | 92 | 56.29% | 38.6% | 7.402% | 343 | 548 | 2 | 13 | 290 | 153 | 25 | 22 | 31 | 1270 | 40.5804 | 172 | 107 | 24 | 483 | 0 | 0 | 92 | 1 | 0.6997 | 26.194 | 5.3908 | 98.8029 | High | High | High | Top | 29 | 82 | 141.2073
WOODACRE 1102 | 043021102 | BAY AREA | NORTH BAY | 32.9746 | 735161.3333 | 44.5506 | 29.78% | 3.241% | 26.83% | 45.01% | 20 | 8 | 71 | 24.33% | 50.83% | 6.682% | 321 | 307 | 7 | 22 | 501 | 294 | 8 | 12 | 23 | 1317 | 37.9609 | 115 | 124 | 55 | 413 | 0 | 0 | 71 | 1 | 0.79914 | 13.9926 | 8.807 | 98.4806 | High | High | High | Top | 30 | 106 | 123.2328
PUEBLO 2102 | 043292102 | BAY AREA | NORTH BAY | 24.0288 | 2021001 | 42.1375 | 22.76% | 0% | 93.89% | 6.111% | 4 | 2 | 18 | 93.79% | 6.207% | 5% | 46 | 83 | 1 | 2 | 107 | 108 | 0 | 7 | 8 | 400 | 38.5968 | 45 | 28 | 6 | 131 | 0 | 0 | 18 | 1 | 0.43521 | 49.0597 | 4.583 | 97.8539 | Medium | High | Medium | Top | 31 | 32 | 224.8421
CAMP EVERS 2106 | 083622106 | CENTRAL COAST | CENTRAL COAST | 130.0354 | 1461187.3333 | 44.2214 | 0% | 0.3016% | 58.29% | 19.37% | 95 | 21 | 247 | 63.6% | 21.78% | 9.994% | 729 | 1439 | 2 | 25 | 884 | 315 | 109 | 62 | 91 | 3292 | 32.3605 | 505 | 316 | 41 | 1321 | 7 | 0 | 245 | 1 | 0.8005 | 17.3477 | 6.977 | 96.8882 | High | High | High | Top | 32 | 108 | 121.0343
STAFFORD 1102 | 043201102 | BAY AREA | NORTH BAY | 23.9883 | 1147106 | 44.7403 | 41.86% | 2.538% | 46.07% | 47.89% | 10 | 1 | 36 | 45.01% | 51.48% | 5.34% | 159 | 309 | 2 | 3 | 183 | 63 | 0 | 16 | 26 | 618 | 28.0064 | 53 | 40 | 4 | 161 | 0 | 0 | 36 | 1 | 0.68685 | 24.2775 | 5.8053 | 96.8023 | High | High | High | Top | 33 | 83 | 140.9373
TASSAJARA 2113 | 014662113 | BAY AREA | DIABLO | 3.7253 | 1442201.6667 | 47 | 34.59% | 2.73% | 47.87% | 28.5% | 0 | 0 | 11 | 33.02% | 49.38% | 17.57% | 34 | 24 | 0 | 0 | 22 | 5 | 0 | 5 | 5 | 74 | 31.75 | 7 | 3 | 1 | 18 | 0 | 0 | 11 | 1 | 0.68513 | 19.1639 | 7.1048 | 93.2843 | High | High | High | Top | 34 | 88 | 136.1559
MIWUK 1701 | 163661701 | CENTRAL VALLEY | YOSEMITE | 77.1453 | 519456 | 43.0016 | 35.1% | 79.89% | 1.633% | 2.682% | 18 | 1 | 135 | 86.77% | 6.286% | 5.964% | 330 | 999 | 1 | 0 | 852 | 155 | 57 | 10 | 39 | 2448 | 17.2147 | 478 | 310 | 48 | 1179 | 0 | 0 | 135 | 0 | 0.2456 | 58.7054 | 6.395 | 92.2031 | Low | High | High | Top | 35 | 5 | 375.4194
SOBRANTE 1103 | 014671103 | BAY AREA | DIABLO | 3.9569 | 359945 | 44.5755 | 23.68% | 0% | 17.29% | 17.27% | 2 | 1 | 9 | 24.4% | 30.11% | 31.13% | 17 | 41 | 0 | 0 | 24 | 12 | 0 | 5 | 15 | 106 | 23.0811 | 13 | 13 | 2 | 39 | 0 | 0 | 9 | 1 | 0.66178 | 19.8226 | 6.8661 | 90.0701 | High | High | High | Top | 36 | 89 | 136.1034
MIRABEL 1102 | 042091102 | NORTHERN | SONOMA | 37.7507 | 657529.3333 | 43.2312 | 21.57% | 4.553% | 39.93% | 39.36% | 28 | 17 | 70 | 39.85% | 45.53% | 6.683% | 252 | 413 | 1 | 6 | 399 | 179 | 51 | 17 | 26 | 1212 | 36.788 | 120 | 90 | 37 | 374 | 0 | 0 | 70 | 1 | 0.90476 | 19.1361 | 5.195 | 89.9435 | High | High | Medium | Top | 37 | 131 | 99.4115
BRUNSWICK 1105 | 152481105 | NORTHERN | SIERRA | 121.439 | 1156546 | 41.8642 | 38.42% | 92.06% | 2.166% | 0.7665% | 19 | 5 | 296 | 93.3% | 2.918% | 12.71% | 219 | 1949 | 11 | 0 | 579 | 305 | 1 | 59 | 101 | 3375 | 40.1125 | 591 | 409 | 47 | 1422 | 0 | 7 | 296 | 1 | 0.30112 | 82.3318 | 3.5748 | 88.6249 | Low | High | Low | Top | 38 | 13 | 294.3166
ALTO 1125 | 042031125 | BAY AREA | NORTH BAY | 37.5324 | 671150 | 43.3888 | 20.73% | 17.34% | 22% | 51.19% | 47 | 13 | 90 | 18.53% | 72.43% | 7.861% | 237 | 417 | 15 | 9 | 435 | 245 | 65 | 16 | 40 | 1323 | 29.7205 | 127 | 139 | 48 | 438 | 0 | 2 | 90 | 1 | 0.84635 | 13.5659 | 7.4405 | 85.4285 | High | High | High | Top | 39 | 130 | 100.9377
PUEBLO 2103 | 043292103 | BAY AREA | NORTH BAY | 47.7491 | 1373463.3333 | 42.5493 | 34.46% | 1.582% | 78.95% | 19.46% | 25 | 1 | 61 | 56.76% | 43.24% | 6.771% | 131 | 363 | 0 | 11 | 284 | 170 | 6 | 12 | 18 | 1019 | 40.3447 | 130 | 48 | 7 | 331 | 0 | 0 | 61 | 1 | 0.52269 | 33.3329 | 4.8731 | 84.9015 | Medium | High | Medium | Top | 40 | 66 | 162.4333
MENLO 1102 | 024131102 | CENTRAL COAST | PENINSULA | 28.7936 | 829244.3333 | 42.4303 | 41.92% | 13.21% | 64.33% | 7.693% | 10 | 0 | 50 | 62.16% | 37.46% | 11.65% | 59 | 241 | 2 | 11 | 200 | 31 | 10 | 8 | 12 | 575 | 23.0058 | 61 | 50 | 9 | 177 | 1 | 0 | 50 | 1 | 0.64574 | 23.9405 | 5.4737 | 84.6193 | Medium | High | High | Top | 41 | 95 | 131.0429
PARADISE 1105 | 102831105 | NORTHERN | NORTH VALLEY | 14.2966 | 586838.6667 | 42.7788 | 31.82% | 35.13% | 6.272% | 28.06% | 10 | 0 | 20 | 43.08% | 30.07% | 4.031% | 95 | 220 | 3 | 0 | 151 | 33 | 0 | 4 | 17 | 521 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 20 | 1 | 0.5487 | 22.8948 | 6.6999 | 84.1666 | Medium | High | High | Top | 42 | 71 | 153.3931
ALLEGHANY 1102 | 152101102 | NORTHERN | SIERRA | 18.0939 | 31926.6667 | 45 | 47.86% | 91.29% | 8.479% | 0% | 1 | 1 | 21 | 39.16% | 60.61% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 5 | 15 | 1 | 38.7324 | 22 | 14 | 3 | 75 | 0 | 0 | 21 | 0 | 0.43406 | 85.5381 | 2.1807 | 80.9689 | Medium | High | Low | Top | 43 | 51 | 186.5369
RINCON 1103 | 043321103 | NORTHERN | SONOMA | 45.8675 | 513395 | 42.8019 | 90.78% | 0% | 74.98% | 18.96% | 22 | 0 | 53 | 75.63% | 18.96% | 11.4% | 90 | 271 | 0 | 10 | 247 | 129 | 9 | 10 | 19 | 737 | 33.9135 | 117 | 55 | 16 | 319 | 0 | 5 | 53 | 1 | 0.60151 | 33.225 | 4.0312 | 80.5653 | Medium | High | Medium | Top | 44 | 93 | 133.9381
PARADISE 1101 | 102831101 | NORTHERN | NORTH VALLEY | 24.3296 | 775325.6667 | 41.9196 | 10.24% | 20.18% | 20.33% | 39.86% | 41 | 1 | 0 | 34.11% | 47.09% | 6.853% | 156 | 411 | 4 | 0 | 387 | 42 | 116 | 0 | 0 | 1109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.65652 | 18.0935 | 6.7536 | 80.2249 | Medium | High | High | Top | 45 | 107 | 122.1965
SAN RAMON 2108 | 014232108 | CENTRAL COAST | MISSION | 16.6213 | 1249108 | 44.2447 | 49.12% | 10.21% | 65.3% | 24.46% | 1 | 3 | 44 | 50.08% | 49.89% | 7.463% | 52 | 146 | 2 | 3 | 113 | 10 | 0 | 7 | 10 | 335 | 46.7524 | 31 | 30 | 5 | 112 | 1 | 0 | 43 | 0 | 0.45199 | 27.2942 | 6.4811 | 79.9552 | Medium | High | High | Top | 46 | 58 | 176.8971
STELLING 1110 | 083481110 | CENTRAL COAST | DE ANZA | 37.1918 | 1044813.3333 | 45.1508 | 117.2% | 0.01493% | 67.34% | 16.04% | 16 | 0 | 42 | 65.01% | 21.39% | 7.899% | 180 | 294 | 0 | 6 | 132 | 72 | 0 | 12 | 21 | 633 | 3.3481 | 50 | 36 | 9 | 166 | 0 | 0 | 42 | 1 | 0.6158 | 26.0714 | 4.98 | 79.9516 | Medium | High | Medium | Top | 47 | 97 | 129.8347
CALISTOGA 1101 | 042711101 | BAY AREA | NORTH BAY | 95.7332 | 589307.3333 | 42.0721 | 42.65% | 7.025% | 68.84% | 23.35% | 20 | 8 | 139 | 64.3% | 34.95% | 10.92% | 184 | 690 | 3 | 12 | 541 | 301 | 16 | 36 | 50 | 1895 | 35.0987 | 205 | 115 | 12 | 655 | 0 | 3 | 139 | 1 | 0.70389 | 26.144 | 4.3442 | 79.9442 | High | High | Medium | Top | 48 | 118 | 113.5747
PARADISE 1106 | 102831106 | NORTHERN | NORTH VALLEY | 24.5474 | 711555.3333 | 45.3904 | 76.96% | 59.18% | 0.2597% | 0% | 2 | 4 | 29 | 82.84% | 0% | 4.075% | 234 | 638 | 0 | 0 | 10 | 69 | 0 | 3 | 14 | 859 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 29 | 0 | 0.24182 | 43.2819 | 7.4641 | 78.1235 | Low | High | High | Top | 49 | 7 | 323.059
BUCKS CREEK 1103 | 102211103 | NORTHERN | NORTH VALLEY | 10.5199 | 37208 | 42.0381 | 44.83% | 82.75% | 2.62% | 0% | 10 | 0 | 18 | 99.97% | 0% | 10.82% | 12 | 115 | 0 | 0 | 84 | 33 | 41 | 12 | 15 | 342 | 43.6 | 59 | 13 | 3 | 119 | 0 | 1 | 18 | 1 | 0.68568 | 65.0189 | 1.7474 | 77.9036 | High | High | Low | Top | 50 | 117 | 113.6148
ORO FINO 1101 | 103031101 | NORTHERN | NORTH VALLEY | 46.3606 | 646807.6667 | 42.8923 | 21.1% | 79.62% | 2.308% | 0% | 13 | 3 | 150 | 90.41% | 2.501% | 5.505% | 173 | 1023 | 9 | 0 | 184 | 68 | 10 | 26 | 59 | 1544 | 68.3964 | 344 | 321 | 145 | 967 | 0 | 4 | 149 | 0 | 0.19375 | 60.5421 | 6.6109 | 77.546 | Low | High | High | Top | 51 | 4 | 400.238
TIGER CREEK 0201 | 161380201 | CENTRAL VALLEY | STOCKTON | 3.8998 | 887 | 40.0543 | 0% | 22.85% | 77.15% | 0% | 0 | 0 | 2 | 100% | 0% | 4.348% | 8 | 69 | 0 | 0 | 10 | 3 | 0 | 0 | 1 | 92 | 16.1667 | 1 | 4 | 1 | 10 | 0 | 0 | 1 | 0 | 0.22906 | 71.5175 | 4.4647 | 73.1388 | Low | High | Medium | Top | 52 | 8 | 319.3026
SARATOGA 1107 | 083371107 | CENTRAL COAST | DE ANZA | 33.4836 | 875523.3333 | 43.8562 | 23.19% | 1.918% | 71.25% | 22.52% | 28 | 7 | 85 | 70.63% | 25.15% | 7.91% | 173 | 280 | 2 | 10 | 361 | 68 | 5 | 30 | 40 | 885 | 4.1008 | 104 | 117 | 41 | 373 | 0 | 1 | 85 | 1 | 0.71571 | 16.8903 | 6.0226 | 72.8047 | High | High | High | Top | 53 | 129 | 101.7235
GARCIA 0401 | 043040401 | NORTHERN | HUMBOLDT | 2.4735 | 4533.6667 | 39.7059 | 0% | 75.56% | 24.44% | 0% | 1 | 1 | 1 | 100% | 0% | 0% | 2 | 19 | 0 | 0 | 9 | 0 | 0 | 1 | 2 | 34 | 57.5714 | 3 | 2 | 0 | 8 | 0 | 0 | 1 | 0 | 0.33591 | 93.5007 | 2.3124 | 72.6268 | Medium | High | Low | Top | 54 | 36 | 216.2094
SILVERADO 2103 | 043432103 | BAY AREA | NORTH BAY | 11.51 | 1588607 | 42.7387 | 6.913% | 3.441% | 86.31% | 10.2% | 2 | 0 | 9 | 88.77% | 11.18% | 12.06% | 27 | 50 | 0 | 1 | 47 | 41 | 0 | 5 | 5 | 199 | 47.7167 | 10 | 13 | 3 | 61 | 0 | 0 | 9 | 0 | 0.28458 | 52.7974 | 4.7886 | 71.95 | Low | High | Medium | Top | 55 | 19 | 252.8263
GARBERVILLE 1102 | 192221102 | NORTHERN | HUMBOLDT | 127.6889 | 692058.6667 | 40.5965 | 87.09% | 13.66% | 30.68% | 20.71% | 65 | 5 | 140 | 42.93% | 22.78% | 39.63% | 172 | 103 | 0 | 5 | 1525 | 152 | 2 | 28 | 51 | 2339 | 33.5908 | 170 | 82 | 45 | 648 | 0 | 11 | 140 | 1 | 0.66354 | 37.7728 | 2.8479 | 71.3775 | High | High | Low | Top | 56 | 122 | 107.5715
HALF MOON BAY 1103 | 024101103 | CENTRAL COAST | PENINSULA | 144.5672 | 1311801 | 41.2361 | 45.7% | 2.707% | 43.84% | 28.56% | 62 | 6 | 181 | 35.72% | 60.32% | 5.516% | 117 | 1383 | 1 | 10 | 1225 | 127 | 30 | 29 | 58 | 2973 | 24.4918 | 228 | 144 | 26 | 780 | 1 | 0 | 181 | 1 | 0.82543 | 15.2282 | 5.5362 | 69.5888 | High | High | High | Top | 57 | 157 | 84.3065
GRAYS FLAT 0401 | 102530401 | NORTHERN | NORTH VALLEY | 10.7057 | 15420.6667 | 44.4889 | 76.07% | 74.47% | 0.1799% | 21.84% | 1 | 0 | 13 | 68.42% | 28.08% | 21.68% | 76 | 87 | 3 | 0 | 48 | 27 | 0 | 0 | 0 | 226 | 16.1429 | 13 | 22 | 1 | 53 | 0 | 0 | 13 | 0 | 0.45263 | 54.5771 | 2.8156 | 69.5542 | Medium | High | Low | Top | 58 | 70 | 153.6677
MAPLE CREEK 1101 | 192101101 | NORTHERN | HUMBOLDT | 10.4152 | 110830.6667 | 43.2515 | 127.8% | 20.72% | 61.54% | 11.06% | 6 | 0 | 7 | 74.63% | 18.69% | 44.71% | 44 | 2 | 0 | 2 | 108 | 9 | 16 | 2 | 3 | 170 | 23 | 7 | 3 | 0 | 18 | 0 | 0 | 7 | 1 | 0.59034 | 25.9034 | 4.5175 | 69.0803 | Medium | High | Medium | Top | 59 | 111 | 117.0176
VALLEY VIEW 1106 | 014341106 | BAY AREA | EAST BAY | 9.8122 | 799970.6667 | 44.5192 | 0% | 0.5291% | 19.36% | 13.87% | 1 | 0 | 8 | 14.66% | 21.58% | 7.051% | 35 | 39 | 0 | 1 | 89 | 17 | 0 | 5 | 7 | 156 | 11.2121 | 8 | 8 | 5 | 38 | 0 | 0 | 8 | 0 | 0.51791 | 17.9636 | 7.3446 | 68.3312 | Medium | High | High | Top | 60 | 94 | 131.9359
BIG BEND 1102 | 103751102 | NORTHERN | NORTH VALLEY | 38.1787 | 0 | 41.5415 | 0% | 26.13% | 69.74% | 2.151% | 2 | 0 | 23 | 97.83% | 2.151% | 11.87% | 42 | 414 | 24 | 0 | 139 | 82 | 0 | 9 | 12 | 893 | 39.7652 | 113 | 28 | 0 | 258 | 0 | 4 | 23 | 0 | 0.21549 | 67.4098 | 4.7008 | 68.2843 | Low | High | Medium | Top | 61 | 10 | 316.8776
FRUITLAND 1142 | 192311142 | NORTHERN | HUMBOLDT | 59.9112 | 294852.3333 | 40.6435 | 45.61% | 3.332% | 77.32% | 5.909% | 31 | 0 | 56 | 75.23% | 11.94% | 39.01% | 96 | 72 | 0 | 0 | 690 | 57 | 5 | 13 | 24 | 1156 | 30.0948 | 96 | 41 | 18 | 321 | 0 | 2 | 56 | 1 | 0.52745 | 46.1007 | 2.797 | 68.0119 | Medium | High | Low | Top | 62 | 99 | 128.9442
MEADOW LANE 2106 | 014302106 | BAY AREA | DIABLO | 0.84595 | 1211425.3333 | 41.6667 | 0% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 16.67% | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6 | 46.6667 | 0 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.12434 | 85.4511 | 6.3861 | 67.8537 | Low | High | High | Top | 63 | 1 | 545.7029
CASTRO VALLEY 1109 | 014091109 | CENTRAL COAST | MISSION | 5.9691 | 477156 | 43.1818 | 28.05% | 0.1603% | 26.28% | 36.61% | 2 | 2 | 14 | 23.73% | 39.29% | 3.788% | 20 | 33 | 0 | 0 | 68 | 7 | 0 | 2 | 4 | 132 | 20.1571 | 17 | 20 | 13 | 75 | 0 | 1 | 14 | 0 | 0.63046 | 16.8148 | 6.3721 | 67.5504 | Medium | High | High | Top | 64 | 124 | 107.1452
CHALLENGE 1101 | 103201101 | NORTHERN | NORTH VALLEY | 48.4283 | 111396.6667 | 41.2851 | 70.45% | 93.19% | 6.727% | 0% | 21 | 0 | 53 | 99.91% | 0.09182% | 5.085% | 47 | 581 | 13 | 0 | 189 | 74 | 7 | 19 | 27 | 1180 | 40.4863 | 131 | 29 | 5 | 345 | 0 | 6 | 53 | 0 | 0.29117 | 73.9452 | 3.1368 | 67.5371 | Low | High | Low | Top | 65 | 29 | 231.9531
CAMP EVERS 2104 | 083622104 | CENTRAL COAST | CENTRAL COAST | 28.9403 | 1715943.6667 | 44.8958 | 16.2% | 1.513% | 64.32% | 25.03% | 20 | 9 | 33 | 59.21% | 31.79% | 6.935% | 202 | 337 | 0 | 16 | 172 | 58 | 11 | 14 | 22 | 721 | 46.0478 | 111 | 64 | 9 | 302 | 2 | 0 | 33 | 1 | 0.74064 | 12.2665 | 7.4164 | 67.3779 | High | High | High | Top | 66 | 144 | 90.9728
BONNIE NOOK 1101 | 152301101 | NORTHERN | SIERRA | 24.4427 | 118202 | 43.2057 | 19.81% | 63.3% | 32.61% | 0.4943% | 0 | 0 | 52 | 58.93% | 41.04% | 13.11% | 138 | 239 | 6 | 0 | 177 | 73 | 0 | 8 | 14 | 671 | 40.1806 | 91 | 46 | 4 | 225 | 0 | 2 | 52 | 0 | 0.33611 | 71.1778 | 2.8122 | 67.2784 | Medium | High | Low | Top | 67 | 46 | 200.1696
CASTRO VALLEY 1106 | 014091106 | CENTRAL COAST | MISSION | 20.1929 | 1020298.3333 | 43.1944 | 30.74% | 0% | 51.18% | 46.16% | 2 | 0 | 29 | 48.72% | 48.62% | 5.627% | 20 | 192 | 1 | 0 | 111 | 7 | 6 | 0 | 1 | 391 | 12.0248 | 27 | 34 | 18 | 126 | 0 | 1 | 29 | 0 | 0.47754 | 22.5872 | 6.233 | 67.2308 | Medium | High | High | Top | 68 | 84 | 140.7869
HICKS 2103 | 083432103 | CENTRAL COAST | SAN JOSE | 12.878 | 1050230 | 45.2812 | 32.31% | 0% | 80.23% | 19.77% | 1 | 2 | 12 | 80.23% | 19.77% | 17.5% | 40 | 83 | 0 | 3 | 33 | 2 | 0 | 3 | 3 | 160 | 46.1071 | 8 | 10 | 0 | 33 | 0 | 0 | 12 | 0 | 0.36574 | 36.537 | 4.9968 | 66.7726 | Medium | High | Medium | Top | 69 | 55 | 182.5692
TASSAJARA 2112 | 014662112 | BAY AREA | DIABLO | 10.8205 | 1218166.3333 | 44.3694 | 34.53% | 38.7% | 14.54% | 23.77% | 1 | 0 | 28 | 14.54% | 62.47% | 14.35% | 64 | 84 | 0 | 0 | 63 | 18 | 0 | 18 | 26 | 223 | 51.5753 | 17 | 29 | 15 | 81 | 0 | 0 | 28 | 1 | 0.71198 | 14.5909 | 6.4193 | 66.687 | High | High | High | Top | 70 | 141 | 93.6636
WASHINGTON CITY GEN. 1101 | 158041101 | NORTHERN | SIERRA | 0.016194 | 0 | 45 | 0% | 100% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0.51587 | 65.3912 | 1.8983 | 64.0372 | Medium | High | Low | Top | 71 | 103 | 124.1349
FRUITLAND 1141 | 192311141 | NORTHERN | HUMBOLDT | 25.2358 | 143637.6667 | 40.4961 | 69.09% | 1.516% | 24.99% | 17.04% | 13 | 0 | 30 | 25.8% | 17.75% | 31.09% | 35 | 19 | 0 | 0 | 377 | 15 | 15 | 7 | 19 | 521 | 20.6947 | 27 | 15 | 12 | 102 | 0 | 1 | 30 | 1 | 0.71072 | 43.5287 | 2.057 | 63.6351 | High | High | Low | Top | 72 | 146 | 89.5367
CALPINE 1146 | 048011146 | NORTHERN | SONOMA | 7.0108 | 0 | 54.5 | 0% | 12.38% | 29.09% | 11.85% | 0 | 0 | 12 | 72.04% | 11.85% | 0% | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 13 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 12 | 0 | 0.33574 | 49.4557 | 3.8156 | 63.3541 | Medium | High | Medium | Top | 73 | 49 | 188.7025
KONOCTI 1102 | 043311102 | NORTHERN | HUMBOLDT | 125.5875 | 939842 | 43.4403 | 68.51% | 28.03% | 51.57% | 14.79% | 47 | 10 | 156 | 65.6% | 30.38% | 11.08% | 490 | 1204 | 0 | 30 | 736 | 313 | 0 | 26 | 59 | 2806 | 38.5626 | 417 | 199 | 44 | 966 | 0 | 7 | 143 | 0 | 0.53781 | 22.8305 | 5.0794 | 62.3678 | Medium | High | Medium | Top | 74 | 113 | 115.9654
GARBERVILLE 1101 | 192221101 | NORTHERN | HUMBOLDT | 86.6908 | 480627.3333 | 41.7085 | 34.66% | 19.32% | 55.03% | 0.6503% | 36 | 3 | 108 | 83.68% | 0.7413% | 35.26% | 213 | 106 | 0 | 1 | 810 | 69 | 21 | 25 | 40 | 1520 | 29.0128 | 122 | 65 | 23 | 421 | 0 | 0 | 107 | 1 | 0.5911 | 38.006 | 2.7692 | 62.2114 | Medium | High | Low | Top | 75 | 126 | 105.2467
BIG BASIN 1101 | 082841101 | CENTRAL COAST | CENTRAL COAST | 56.1051 | 568121.3333 | 43.4029 | 18.97% | 0.5049% | 47.45% | 28.29% | 74 | 13 | 128 | 51.44% | 33.93% | 9.023% | 226 | 384 | 0 | 18 | 730 | 186 | 94 | 25 | 42 | 1751 | 24.8837 | 217 | 183 | 38 | 667 | 3 | 0 | 128 | 1 | 0.89531 | 9.9669 | 6.9512 | 62.0292 | High | Medium | High | Top | 76 | 192 | 69.282
BURNS 2101 | 183582101 | CENTRAL COAST | CENTRAL COAST | 1.6694 | 0 | 43.8662 | 34.99% | 1.805% | 42.28% | 25.56% | 35 | 3 | 104 | 37.72% | 51.73% | 9.719% | 239 | 376 | 0 | 9 | 458 | 156 | 46 | 34 | 52 | 1317 | 32.416 | 188 | 99 | 14 | 522 | 4 | 0 | 103 | 1 | 0.854 | 10.0722 | 7.1684 | 61.6602 | High | Medium | High | Top | 77 | 180 | 72.2019
PETALUMA C 1108 | 042631108 | NORTHERN | SONOMA | 74.2809 | 1293574.3333 | 42.6589 | 32.65% | 0.1844% | 49.58% | 46.86% | 21 | 3 | 121 | 29.01% | 68.63% | 5.274% | 290 | 785 | 0 | 4 | 529 | 214 | 34 | 21 | 37 | 1858 | 26.6996 | 194 | 63 | 6 | 495 | 0 | 0 | 121 | 0 | 0.6193 | 33.2388 | 2.9732 | 61.2016 | Medium | High | Low | Top | 78 | 135 | 98.8243
PIKE CITY 1102 | 152201102 | NORTHERN | SIERRA | 9.4149 | 3190 | 40.4831 | 16.19% | 62.21% | 37.34% | 0% | 2 | 0 | 8 | 75.24% | 24.76% | 35.27% | 7 | 31 | 1 | 1 | 80 | 72 | 0 | 0 | 3 | 207 | 27.4706 | 7 | 1 | 0 | 17 | 0 | 0 | 8 | 0 | 0.30098 | 90.6538 | 2.225 | 60.7099 | Low | High | Low | Top | 79 | 44 | 201.7078
CAMP EVERS 2105 | 083622105 | CENTRAL COAST | CENTRAL COAST | 89.301 | 917398.3333 | 44.0145 | 0% | 0.564% | 53.59% | 22.8% | 92 | 33 | 210 | 54.81% | 27.43% | 7.444% | 490 | 816 | 0 | 26 | 1049 | 203 | 115 | 65 | 95 | 2633 | 36.9282 | 333 | 262 | 50 | 990 | 14 | 0 | 209 | 1 | 0.84514 | 8.9754 | 8.0024 | 60.7015 | High | Medium | High | Top | 80 | 182 | 71.8241
BERKELEY F 1103 | 012061103 | BAY AREA | EAST BAY | 2.1377 | 1054702.3333 | 44.1026 | 3.803% | 24.57% | 59.11% | 16.33% | 1 | 0 | 5 | 44.5% | 55.5% | 26.92% | 10 | 15 | 0 | 6 | 31 | 5 | 0 | 1 | 2 | 78 | 22.1429 | 8 | 6 | 7 | 28 | 0 | 0 | 5 | 0 | 0.48197 | 17.5559 | 7.1543 | 60.5365 | Medium | High | High | Top | 81 | 102 | 125.6011
BUCKS CREEK 1101 | 102211101 | NORTHERN | NORTH VALLEY | 20.005 | 4541.3333 | 43.9709 | 29.47% | 86.51% | 3.485% | 7.184% | 2 | 1 | 11 | 6.119% | 91.51% | 33.06% | 80 | 115 | 2 | 0 | 154 | 38 | 0 | 1 | 11 | 484 | 32.1765 | 9 | 2 | 0 | 23 | 0 | 0 | 11 | 0 | 0.47328 | 26.2124 | 4.8176 | 59.7668 | Medium | High | Medium | Top | 82 | 101 | 126.2809
ALHAMBRA 1105 | 014101105 | BAY AREA | DIABLO | 37.7253 | 497618.3333 | 44.5342 | 7.539% | 3.137% | 77.85% | 12.85% | 7 | 3 | 75 | 43.84% | 49.99% | 12.42% | 123 | 355 | 1 | 0 | 202 | 50 | 8 | 21 | 30 | 805 | 26.3074 | 110 | 119 | 14 | 340 | 0 | 1 | 75 | 0 | 0.40998 | 24.356 | 5.9383 | 59.2964 | Medium | High | High | Top | 83 | 79 | 144.6337
ANNAPOLIS 1101 | 042861101 | NORTHERN | HUMBOLDT | 51.2424 | 73654.6667 | 43.1562 | 22.7% | 10.09% | 71.98% | 1.626% | 15 | 0 | 49 | 97.83% | 2.115% | 3.201% | 150 | 188 | 0 | 4 | 446 | 34 | 2 | 10 | 16 | 781 | 36.44 | 38 | 11 | 2 | 161 | 0 | 0 | 48 | 1 | 0.55712 | 44.643 | 2.3285 | 57.9138 | Medium | High | Low | Top | 84 | 127 | 103.9519
WOODSIDE 1104 | 024251104 | CENTRAL COAST | PENINSULA | 14.8672 | 883355.3333 | 42.9964 | 25.38% | 1.23% | 67.34% | 22.58% | 9 | 4 | 39 | 69.83% | 23.26% | 8.587% | 60 | 189 | 0 | 1 | 294 | 20 | 0 | 7 | 11 | 559 | 17.3192 | 65 | 71 | 25 | 217 | 0 | 0 | 39 | 1 | 0.65918 | 9.7107 | 8.9719 | 57.4295 | Medium | Medium | High | Top | 85 | 150 | 87.1233
OAKLAND K 1102 | 012101102 | BAY AREA | EAST BAY | 15.6371 | 511025 | 46.4153 | 34.6% | 0% | 37.32% | 19.08% | 13 | 1 | 40 | 18.81% | 47.36% | 23.61% | 159 | 113 | 0 | 1 | 191 | 52 | 36 | 26 | 45 | 487 | 18.3043 | 31 | 80 | 28 | 170 | 0 | 0 | 39 | 0 | 0.64899 | 13.1282 | 6.5755 | 56.0234 | Medium | High | High | Top | 86 | 155 | 86.3243
CALPINE 1144 | 048011144 | NORTHERN | SONOMA | 30.4155 | 14794.6667 | 0 | 0% | 17.18% | 39.68% | 6.755% | 0 | 0 | 35 | 56.23% | 9.093% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 19 | 0 | 5 | 2 | 5 | 2 | 44 | 0 | 0 | 35 | 0 | 0.33222 | 44.753 | 3.7313 | 55.4765 | Medium | High | Low | Top | 87 | 65 | 166.9886
BIG BASIN 1102 | 082841102 | CENTRAL COAST | CENTRAL COAST | 73.4523 | 445922 | 44.4454 | 19.22% | 2.324% | 57.19% | 16.45% | 83 | 15 | 125 | 55.68% | 24.43% | 11.65% | 349 | 696 | 0 | 17 | 524 | 228 | 58 | 21 | 44 | 1777 | 24.2091 | 213 | 117 | 29 | 619 | 2 | 0 | 123 | 1 | 0.85269 | 10.5824 | 6.1282 | 55.2976 | High | Medium | High | Top | 88 | 206 | 64.8512
FOOTHILL 1101 | 182951101 | CENTRAL COAST | LOS PADRES | 19.8573 | 161535.3333 | 41.6914 | 10.46% | 0% | 50.37% | 40.15% | 4 | 0 | 12 | 50.37% | 40.15% | 7.09% | 36 | 27 | 0 | 106 | 141 | 35 | 0 | 2 | 4 | 409 | 28.3333 | 40 | 9 | 4 | 103 | 0 | 0 | 12 | 1 | 0.64347 | 14.7358 | 5.7639 | 54.6534 | Medium | High | High | Top | 89 | 156 | 84.935
MIDDLETOWN 1101 | 043141101 | NORTHERN | HUMBOLDT | 96.9667 | 760831.3333 | 42.8966 | 35.12% | 25.16% | 58.37% | 9% | 21 | 9 | 122 | 80.4% | 14.96% | 9.066% | 388 | 870 | 1 | 18 | 694 | 173 | 14 | 18 | 31 | 2217 | 38.0723 | 307 | 142 | 32 | 732 | 0 | 2 | 122 | 0 | 0.28996 | 42.6631 | 4.373 | 54.0978 | Low | High | Medium | Top | 90 | 50 | 186.5677
LAS GALLINAS A 1105 | 042991105 | BAY AREA | NORTH BAY | 13.3067 | 815852.6667 | 47.0429 | 54.58% | 4.201% | 51.94% | 3.297% | 0 | 0 | 17 | 52.88% | 6.559% | 1.709% | 114 | 135 | 0 | 1 | 46 | 38 | 0 | 6 | 13 | 234 | 33.3333 | 15 | 20 | 3 | 58 | 0 | 2 | 17 | 0 | 0.25962 | 27.6546 | 7.5185 | 53.9799 | Low | High | High | Top | 91 | 41 | 207.9219
MIWUK 1702 | 163661702 | CENTRAL VALLEY | YOSEMITE | 75.7688 | 700089.6667 | 43.5587 | 51.21% | 80.48% | 8.501% | 3.03% | 14 | 1 | 124 | 83.29% | 8.9% | 5.685% | 437 | 1281 | 0 | 0 | 549 | 187 | 15 | 14 | 36 | 2410 | 20.1794 | 574 | 370 | 29 | 1281 | 0 | 0 | 123 | 0 | 0.17901 | 42.6734 | 7.0209 | 53.6334 | Low | High | High | Top | 92 | 12 | 299.604
ORO FINO 1102 | 103031102 | NORTHERN | NORTH VALLEY | 109.5969 | 444513.6667 | 41.5442 | 15.84% | 67.73% | 17.24% | 3.447% | 14 | 3 | 125 | 92.19% | 3.587% | 5.444% | 143 | 1245 | 41 | 0 | 643 | 97 | 1 | 37 | 57 | 2700 | 45.6659 | 376 | 190 | 26 | 881 | 0 | 4 | 122 | 0 | 0.12196 | 76.0455 | 5.7587 | 53.4088 | Low | High | High | Top | 93 | 3 | 437.9241
EL DORADO PH 2102 | 152762102 | NORTHERN | SIERRA | 34.253 | 447460.6667 | 42.0764 | 22.92% | 82.78% | 4.398% | 0% | 13 | 2 | 59 | 88.76% | 11.02% | 0.9658% | 146 | 609 | 16 | 0 | 268 | 70 | 12 | 13 | 22 | 1139 | 45.3724 | 279 | 123 | 24 | 527 | 0 | 1 | 59 | 0 | 0.22067 | 63.9055 | 3.7472 | 52.8413 | Low | High | Medium | Top | 94 | 26 | 239.4637
PARADISE 1102 | 102831102 | NORTHERN | NORTH VALLEY | 15.5735 | 1127377 | 42.2321 | 18.64% | 19.44% | 26.09% | 38.88% | 1 | 3 | 0 | 45.45% | 39.14% | 5.179% | 76 | 226 | 3 | 0 | 183 | 25 | 71 | 0 | 0 | 560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38818 | 19.4771 | 6.9671 | 52.6759 | Medium | High | High | Top | 95 | 90 | 135.6986
EL DORADO PH 2101 | 152762101 | NORTHERN | SIERRA | 156.326 | 892577.3333 | 42.4752 | 40.66% | 91.79% | 3.443% | 0.1415% | 20 | 6 | 210 | 93.29% | 3.482% | 2.047% | 428 | 2233 | 36 | 0 | 801 | 247 | 55 | 45 | 77 | 4347 | 47.9521 | 858 | 340 | 34 | 1844 | 0 | 5 | 209 | 0 | 0.25422 | 60.6839 | 3.3481 | 51.6505 | Low | High | Low | Top | 96 | 43 | 203.1751
MENLO 1103 | 024131103 | CENTRAL COAST | PENINSULA | 40.483 | 542020.6667 | 41.4118 | 30.72% | 0.6489% | 60.17% | 13.68% | 34 | 3 | 58 | 52.2% | 47.8% | 7.451% | 56 | 378 | 1 | 9 | 267 | 34 | 20 | 11 | 21 | 765 | 20.4041 | 79 | 30 | 2 | 200 | 0 | 0 | 58 | 0 | 0.59311 | 18.4464 | 4.6883 | 51.2938 | Medium | High | Medium | Top | 97 | 153 | 86.4832
CALISTOGA 1102 | 042711102 | BAY AREA | NORTH BAY | 25.8439 | 1209225.6667 | 42.9894 | 78.86% | 1.451% | 64.1% | 21.01% | 9 | 0 | 33 | 64.28% | 31.22% | 7.544% | 94 | 224 | 3 | 5 | 127 | 122 | 0 | 17 | 21 | 570 | 37.8608 | 50 | 46 | 11 | 207 | 0 | 0 | 33 | 1 | 0.54883 | 17.2654 | 5.3093 | 50.3095 | Medium | High | Medium | Top | 98 | 142 | 91.6664
ALLEGHANY 1101 | 152101101 | NORTHERN | SIERRA | 63.6568 | 172093.6667 | 38.5274 | 61.05% | 85.42% | 1.736% | 1.002% | 9 | 3 | 93 | 85.96% | 2.267% | 14.33% | 106 | 759 | 9 | 58 | 427 | 166 | 0 | 20 | 69 | 2156 | 37.914 | 96 | 59 | 11 | 301 | 0 | 6 | 93 | 0 | 0.22658 | 65.1726 | 3.4063 | 50.3011 | Low | High | Low | Top | 99 | 34 | 222.0006
LAKEVILLE 1102 | 043371102 | NORTHERN | SONOMA | 22.8278 | 324491 | 44.2947 | 40.97% | 7.7% | 54.72% | 36.61% | 1 | 1 | 10 | 52.92% | 46.12% | 9.091% | 75 | 125 | 0 | 14 | 80 | 59 | 0 | 5 | 5 | 319 | 35.662 | 22 | 15 | 2 | 72 | 0 | 0 | 10 | 0 | 0.41298 | 30.9464 | 3.8583 | 49.3101 | Medium | High | Medium | Top | 100 | 109 | 119.401
BELL 1110 | 152701110 | NORTHERN | SIERRA | 0.36763 | 1090418.3333 | 41.875 | 14.41% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 1 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 33.2 | 1 | 3 | 0 | 5 | 0 | 0 | 0 | 0 | 0.21636 | 47.6367 | 4.7034 | 48.4765 | Low | High | Medium | Top | 101 | 33 | 224.0565
STANISLAUS 1702 | 162821702 | CENTRAL VALLEY | YOSEMITE | 85.5755 | 713366.3333 | 43.3785 | 19.57% | 89.52% | 1.995% | 1.119% | 7 | 2 | 187 | 89.99% | 3.239% | 2.18% | 651 | 1571 | 1 | 1 | 834 | 112 | 58 | 33 | 71 | 2936 | 26.0683 | 879 | 402 | 13 | 1757 | 0 | 0 | 187 | 1 | 0.18553 | 45.2841 | 5.7429 | 48.2501 | Low | High | High | Top | 102 | 18 | 260.062
LOS GATOS 1107 | 082021107 | CENTRAL COAST | DE ANZA | 94.6764 | 820307 | 43.3633 | 45.31% | 7.429% | 67.97% | 9.819% | 45 | 8 | 175 | 76.39% | 10.72% | 10.78% | 351 | 1073 | 1 | 10 | 674 | 173 | 12 | 29 | 51 | 2282 | 3.4667 | 320 | 211 | 40 | 911 | 0 | 0 | 172 | 1 | 0.35698 | 24.1189 | 5.5723 | 47.9779 | Medium | High | High | Top | 103 | 91 | 134.3986
SAN RAMON 2107 | 014232107 | CENTRAL COAST | MISSION | 13.9149 | 1508724.3333 | 45.4089 | 13.88% | 0.5199% | 72.21% | 25.32% | 1 | 0 | 34 | 72.18% | 25.87% | 7.011% | 87 | 130 | 1 | 0 | 60 | 14 | 0 | 10 | 12 | 271 | 28.7 | 21 | 19 | 5 | 78 | 0 | 0 | 33 | 0 | 0.38737 | 18.9553 | 6.5285 | 47.9372 | Medium | High | High | Top | 104 | 105 | 123.7494
PURISIMA 1101 | 182971101 | CENTRAL COAST | LOS PADRES | 19.2204 | 1576262.6667 | 41.0931 | 135.2% | 0% | 36.93% | 11.68% | 2 | 0 | 7 | 36.93% | 11.68% | 0.8032% | 13 | 11 | 0 | 23 | 124 | 30 | 0 | 10 | 18 | 249 | 25.1875 | 4 | 7 | 1 | 36 | 0 | 0 | 7 | 0 | 0.29858 | 23.0277 | 6.8643 | 47.1964 | Low | High | High | Top | 105 | 67 | 158.0695
CLAYTON 2215 | 012022215 | BAY AREA | DIABLO | 8.9607 | 1585359 | 44.6471 | 0% | 2.854% | 11.4% | 24.63% | 3 | 0 | 7 | 11.4% | 30.35% | 14.71% | 33 | 86 | 0 | 0 | 21 | 6 | 0 | 3 | 5 | 170 | 48.475 | 10 | 16 | 4 | 46 | 0 | 0 | 7 | 0 | 0.62031 | 11.0942 | 6.8386 | 47.0622 | Medium | Medium | High | Top | 106 | 174 | 75.869
BRUNSWICK 1107 | 152481107 | NORTHERN | SIERRA | 8.871 | 757448.3333 | 41.9088 | 11.04% | 38.53% | 51.17% | 2.63% | 2 | 0 | 31 | 46.46% | 46.65% | 12.82% | 34 | 171 | 3 | 0 | 88 | 26 | 11 | 7 | 10 | 351 | 38.2028 | 35 | 50 | 12 | 147 | 0 | 0 | 31 | 1 | 0.63707 | 14.2839 | 5.0141 | 45.6282 | Medium | High | Medium | Top | 107 | 183 | 71.6216
GUALALA 1112 | 042841112 | NORTHERN | HUMBOLDT | 46.2448 | 283978.6667 | 42.2627 | 37.35% | 0.2584% | 28.02% | 67.98% | 35 | 2 | 96 | 10.58% | 86.13% | 3.661% | 106 | 308 | 0 | 3 | 307 | 49 | 44 | 13 | 20 | 956 | 36.3333 | 120 | 35 | 10 | 427 | 0 | 1 | 96 | 1 | 0.69981 | 19.1758 | 3.3433 | 44.8652 | High | High | Low | Top | 108 | 207 | 64.1103
GOLDTREE 1105 | 182581105 | CENTRAL COAST | LOS PADRES | 7.1045 | 856916.3333 | 42.3504 | 118% | 0% | 33.32% | 40.83% | 0 | 0 | 8 | 33.32% | 40.83% | 2.564% | 8 | 1 | 0 | 15 | 55 | 12 | 0 | 2 | 5 | 117 | 19.4286 | 5 | 2 | 0 | 18 | 0 | 0 | 8 | 0 | 0.45177 | 20.1837 | 4.9002 | 44.6824 | Medium | High | Medium | Top | 109 | 134 | 98.9051
SPRING GAP 1702 | 162831702 | CENTRAL VALLEY | YOSEMITE | 41.0705 | 0 | 42.5719 | 143.6% | 84.92% | 3.058% | 0% | 9 | 1 | 53 | 83.26% | 4.717% | 8.784% | 171 | 335 | 0 | 0 | 526 | 59 | 0 | 11 | 29 | 1184 | 25.0833 | 160 | 108 | 8 | 449 | 0 | 0 | 52 | 0 | 0.23994 | 50.1342 | 3.6805 | 44.2745 | Low | High | Low | Top | 110 | 54 | 184.5213
OTTER 1101 | 182941101 | CENTRAL COAST | CENTRAL COAST | 25.0962 | 123757 | 40.0704 | 32.22% | 4.226% | 24.73% | 37.01% | 16 | 4 | 31 | 17.53% | 62.62% | 13.25% | 20 | 188 | 0 | 9 | 190 | 42 | 2 | 10 | 16 | 498 | 13.2086 | 50 | 36 | 4 | 169 | 0 | 0 | 31 | 1 | 0.74861 | 13.9573 | 4.2298 | 44.195 | High | High | Medium | Top | 111 | 222 | 59.0362
PUEBLO 1104 | 043291104 | BAY AREA | NORTH BAY | 31.2032 | 723874 | 41.893 | 33.25% | 1.253% | 57.25% | 39.6% | 5 | 0 | 36 | 46.1% | 52% | 8.453% | 44 | 266 | 0 | 15 | 157 | 97 | 8 | 11 | 13 | 627 | 42.2246 | 78 | 41 | 5 | 190 | 0 | 1 | 36 | 0 | 0.48292 | 18.8717 | 4.8451 | 44.1556 | Medium | High | Medium | Top | 112 | 143 | 91.4353
BIG MEADOWS 2101 | 102812101 | NORTHERN | NORTH VALLEY | 63.4393 | 493664.3333 | 43.7034 | 52.57% | 88.47% | 0.6282% | 3.3% | 12 | 0 | 69 | 54.98% | 40.51% | 14.39% | 299 | 560 | 4 | 0 | 423 | 89 | 0 | 14 | 34 | 1724 | 41.9714 | 126 | 72 | 11 | 329 | 0 | 2 | 69 | 0 | 0.3795 | 26.4346 | 4.3997 | 44.1376 | Medium | High | Medium | Top | 113 | 112 | 116.3033
LAKEWOOD 2107 | 013532107 | BAY AREA | DIABLO | 9.3294 | 1395105 | 45 | 0% | 0% | 22.34% | 41.19% | 2 | 0 | 31 | 19.17% | 78.97% | 13.58% | 71 | 73 | 0 | 0 | 94 | 14 | 9 | 6 | 8 | 243 | 49.6636 | 27 | 45 | 12 | 108 | 0 | 0 | 31 | 1 | 0.74167 | 8.9554 | 6.6182 | 43.958 | High | Medium | High | Top | 114 | 221 | 59.2689
COTATI 1103 | 042271103 | NORTHERN | SONOMA | 85.8821 | 571225.3333 | 42.0299 | 100.3% | 0.8466% | 42.44% | 45.86% | 21 | 2 | 107 | 22.08% | 72.47% | 4.327% | 212 | 753 | 0 | 5 | 507 | 201 | 35 | 18 | 39 | 1710 | 31.7867 | 138 | 60 | 9 | 384 | 0 | 1 | 107 | 0 | 0.59061 | 24.6428 | 3.0163 | 43.8998 | Medium | High | Low | Top | 115 | 177 | 74.3298
BURNS 2101 | 183582101 | CENTRAL COAST | CENTRAL COAST | 1.6694 | 0 | 43.5294 | 0% | 0% | 8.944% | 22.02% | 2 | 0 | 3 | 25.87% | 24.07% | 5.556% | 8 | 8 | 0 | 0 | 19 | 3 | 0 | 3 | 4 | 36 | 32.0714 | 6 | 2 | 0 | 14 | 1 | 0 | 3 | 1 | 0.60685 | 10.0722 | 7.1684 | 43.8155 | Medium | Medium | High | Top | 116 | 180 | 72.2019
FORT SEWARD 1121 | 192321121 | NORTHERN | HUMBOLDT | 39.059 | 73000 | 39.7697 | 75.37% | 49.12% | 29.4% | 0% | 6 | 3 | 20 | 100% | 0% | 34.85% | 35 | 12 | 0 | 0 | 287 | 53 | 0 | 8 | 13 | 614 | 35.6535 | 34 | 11 | 4 | 134 | 0 | 1 | 20 | 0 | 0.43329 | 38.5389 | 2.5731 | 42.9664 | Medium | High | Low | Top | 117 | 132 | 99.1637
DUNBAR 1101 | 043071101 | NORTHERN | SONOMA | 43.5849 | 843643 | 43.9917 | 24.41% | 1.622% | 60.47% | 30.58% | 14 | 1 | 65 | 60.85% | 32.35% | 8.245% | 210 | 418 | 1 | 12 | 211 | 124 | 20 | 22 | 26 | 849 | 37.2642 | 120 | 91 | 17 | 359 | 0 | 0 | 65 | 1 | 0.76795 | 11.9565 | 4.6754 | 42.9292 | High | Medium | Medium | Top | 118 | 236 | 55.9009
SONOMA 1104 | 042721104 | NORTHERN | SONOMA | 20.5139 | 741589.3333 | 44.6264 | 41.13% | 4.224% | 69.12% | 26.66% | 7 | 0 | 33 | 71.34% | 28.66% | 7.473% | 134 | 208 | 0 | 4 | 94 | 81 | 2 | 9 | 9 | 455 | 35.7857 | 73 | 46 | 8 | 186 | 0 | 1 | 33 | 0 | 0.39279 | 21.5406 | 5.0643 | 42.8485 | Medium | High | Medium | Top | 119 | 120 | 109.0873
BIG BEND 1101 | 103751101 | NORTHERN | NORTH VALLEY | 57.4664 | 0 | 42.1363 | 0% | 38.12% | 57.61% | 1.166% | 22 | 1 | 49 | 87.75% | 9.141% | 12.87% | 63 | 585 | 27 | 0 | 203 | 174 | 9 | 11 | 19 | 1375 | 41.0997 | 175 | 38 | 1 | 355 | 0 | 2 | 49 | 0 | 0.31114 | 24.5458 | 5.5674 | 42.5183 | Low | High | High | Top | 120 | 87 | 136.6551
CAYUCOS 1102 | 182551102 | CENTRAL COAST | LOS PADRES | 14.9742 | 532008.6667 | 41.8956 | 10.74% | 13.99% | 50.24% | 23.97% | 3 | 0 | 6 | 76.03% | 23.97% | 10.38% | 24 | 2 | 0 | 8 | 85 | 29 | 0 | 3 | 3 | 183 | 32.4231 | 20 | 2 | 1 | 54 | 0 | 0 | 6 | 0 | 0.43451 | 22.5077 | 4.2742 | 41.8006 | Medium | High | Medium | Top | 121 | 138 | 96.2022
SILVERADO 2102 | 043432102 | BAY AREA | NORTH BAY | 61.4862 | 1297278.3333 | 43.148 | 89.13% | 0.5129% | 89.11% | 3.798% | 17 | 1 | 75 | 88.65% | 5.534% | 9.625% | 167 | 315 | 1 | 17 | 258 | 241 | 0 | 33 | 47 | 987 | 45.3902 | 60 | 57 | 11 | 282 | 0 | 1 | 75 | 0 | 0.30025 | 27.6603 | 5.016 | 41.6584 | Low | High | Medium | Top | 122 | 86 | 138.7436
BEN LOMOND 0401 | 083040401 | CENTRAL COAST | CENTRAL COAST | 21.1277 | 173524.6667 | 44.4801 | 0% | 1.251% | 40.32% | 34.47% | 26 | 1 | 36 | 41.81% | 41.66% | 7.107% | 122 | 165 | 0 | 1 | 221 | 66 | 28 | 17 | 23 | 605 | 20.2422 | 57 | 88 | 15 | 231 | 1 | 0 | 36 | 0 | 0.78936 | 6.6101 | 7.9288 | 41.3705 | High | Medium | High | Top | 123 | 256 | 52.4105
CABRILLO 1104 | 183101104 | CENTRAL COAST | LOS PADRES | 34.4425 | 615165 | 41.762 | 48.45% | 9.532% | 25.85% | 30.82% | 9 | 2 | 21 | 30.75% | 45% | 2.762% | 65 | 34 | 0 | 69 | 236 | 59 | 20 | 2 | 8 | 543 | 23.41 | 36 | 8 | 1 | 113 | 0 | 0 | 20 | 0 | 0.59436 | 11.348 | 6.1259 | 41.3185 | Medium | Medium | High | Top | 124 | 191 | 69.517
KANAKA 1101 | 103221101 | NORTHERN | NORTH VALLEY | 93.2538 | 157764.3333 | 41.4647 | 24.57% | 19.68% | 69.64% | 3.536% | 17 | 4 | 56 | 81.77% | 13.86% | 5.938% | 101 | 1074 | 43 | 0 | 326 | 111 | 4 | 29 | 39 | 2004 | 42.3043 | 217 | 44 | 1 | 551 | 0 | 2 | 56 | 0 | 0.1712 | 50.17 | 4.744 | 40.7468 | Low | High | Medium | Top | 125 | 27 | 238.0071
CHALLENGE 1102 | 103201102 | NORTHERN | NORTH VALLEY | 63.9131 | 200478.6667 | 40.6424 | 26.02% | 28.96% | 67.3% | 0% | 21 | 5 | 54 | 97.76% | 0.003964% | 3.731% | 51 | 848 | 23 | 0 | 214 | 52 | 0 | 14 | 21 | 1474 | 45.2548 | 211 | 53 | 4 | 551 | 0 | 4 | 53 | 0 | 0.1784 | 54.9878 | 4.1301 | 40.5158 | Low | High | Medium | Top | 126 | 31 | 227.1058
NORTH DUBLIN 2103 | 014052103 | CENTRAL COAST | MISSION | 19.5175 | 1418542.3333 | 43.3628 | 87.41% | 1.211% | 48.44% | 39.07% | 0 | 1 | 28 | 40% | 50.81% | 7.375% | 16 | 198 | 0 | 4 | 69 | 11 | 0 | 13 | 15 | 339 | 46.9619 | 23 | 46 | 10 | 114 | 0 | 0 | 28 | 0 | 0.50016 | 12.8108 | 6.3181 | 40.4827 | Medium | High | High | Top | 127 | 163 | 80.9395
HAMILTON BRANCH 1101 | 102361101 | NORTHERN | NORTH VALLEY | 27.1542 | 424216.3333 | 43.8696 | 38.36% | 81.53% | 0% | 3.465% | 8 | 3 | 51 | 76.62% | 16.34% | 3.586% | 196 | 307 | 3 | 0 | 233 | 45 | 0 | 20 | 30 | 725 | 38.2857 | 87 | 66 | 13 | 207 | 0 | 0 | 50 | 0 | 0.35316 | 19.9897 | 5.6969 | 40.217 | Medium | High | High | Top | 128 | 116 | 113.8792
MIDDLETOWN 1103 | 043141103 | NORTHERN | HUMBOLDT | 27.8272 | 89806 | 43.6236 | 68.25% | 9.431% | 76.29% | 0.7473% | 0 | 0 | 12 | 85.72% | 0.7473% | 17.22% | 90 | 130 | 0 | 3 | 94 | 70 | 2 | 4 | 6 | 360 | 37.5278 | 34 | 13 | 3 | 78 | 0 | 0 | 12 | 0 | 0.23524 | 39.0448 | 4.3749 | 40.1831 | Low | High | Medium | Top | 129 | 61 | 170.8184
OAKLAND X 1106 | 012541106 | BAY AREA | EAST BAY | 16.5816 | 765290.3333 | 44.2004 | 34.31% | 4.536% | 56% | 18.4% | 18 | 1 | 52 | 24.92% | 54.1% | 18.45% | 107 | 111 | 0 | 6 | 346 | 19 | 5 | 21 | 36 | 569 | 19.8299 | 38 | 64 | 20 | 149 | 0 | 0 | 52 | 0 | 0.62186 | 9.9434 | 6.4265 | 39.7379 | Medium | Medium | High | Top | 130 | 209 | 63.9013
CRESCENT MILLS 2101 | 103132101 | NORTHERN | NORTH VALLEY | 49.7398 | 187120.6667 | 42.6676 | 11.47% | 88.75% | 1.613% | 3.972% | 1 | 1 | 46 | 89.85% | 6.575% | 19.91% | 144 | 469 | 12 | 0 | 251 | 123 | 0 | 10 | 14 | 1105 | 42.9088 | 95 | 29 | 2 | 279 | 0 | 1 | 46 | 0 | 0.23089 | 48.487 | 3.5488 | 39.7293 | Low | High | Low | Top | 131 | 60 | 172.07
EAST QUINCY 1101 | 102551101 | NORTHERN | NORTH VALLEY | 3.9217 | 430641 | 42.5194 | 20.26% | 70.89% | 0.07478% | 2.009% | 0 | 0 | 2 | 85.68% | 7.367% | 7.752% | 18 | 88 | 2 | 0 | 11 | 6 | 0 | 1 | 2 | 129 | 37.5532 | 20 | 12 | 2 | 48 | 0 | 0 | 2 | 0 | 0.31432 | 25.4904 | 4.9573 | 39.7179 | Low | High | Medium | Top | 132 | 100 | 126.3633
RESEARCH 2102 | 014692102 | BAY AREA | DIABLO | 1.8257 | 1648770 | 44.918 | 11.42% | 0% | 24.38% | 75.46% | 1 | 0 | 9 | 24.38% | 75.46% | 11.29% | 18 | 15 | 0 | 0 | 25 | 1 | 0 | 3 | 3 | 62 | 50.0303 | 9 | 17 | 2 | 33 | 0 | 0 | 9 | 0 | 0.57996 | 11.4244 | 5.9634 | 39.5118 | Medium | Medium | High | Top | 133 | 194 | 68.1286
BRIDGEVILLE 1101 | 192461101 | NORTHERN | HUMBOLDT | 22.6718 | 41572 | 41.2399 | 18.92% | 28.24% | 12.88% | 0% | 10 | 3 | 28 | 99.69% | 0% | 28.3% | 35 | 7 | 0 | 1 | 221 | 24 | 3 | 6 | 13 | 371 | 31.6471 | 22 | 8 | 3 | 70 | 0 | 0 | 28 | 1 | 0.67759 | 74.0616 | 0.78727 | 39.5078 | High | High | Low | Top | 134 | 227 | 58.3068
PUEBLO 1105 | 043291105 | BAY AREA | NORTH BAY | 26.5646 | 658552.3333 | 43.1205 | 54% | 0% | 82.91% | 17.08% | 4 | 0 | 25 | 76.18% | 23.81% | 16.87% | 53 | 145 | 0 | 5 | 91 | 129 | 0 | 11 | 14 | 415 | 34.4031 | 38 | 24 | 10 | 133 | 0 | 0 | 25 | 1 | 0.51355 | 17.3535 | 4.39 | 39.1225 | Medium | High | Medium | Top | 135 | 173 | 76.1812
WILLOW CREEK 1102 | 192171102 | NORTHERN | HUMBOLDT | 9.6275 | 37994.3333 | 44.2767 | 16.2% | 8.232% | 31.81% | 0.04622% | 2 | 0 | 21 | 99.31% | 0.1192% | 57.14% | 41 | 6 | 0 | 0 | 105 | 6 | 0 | 3 | 6 | 161 | 33.76 | 16 | 14 | 2 | 51 | 0 | 0 | 21 | 1 | 0.53644 | 41.1814 | 1.7321 | 38.2656 | Medium | High | Low | Top | 136 | 184 | 71.3323
LOS GATOS 1106 | 082021106 | CENTRAL COAST | DE ANZA | 70.8424 | 529466.6667 | 44.0876 | 26.26% | 1.726% | 66.18% | 15.87% | 51 | 6 | 143 | 67.75% | 17.31% | 10.52% | 398 | 841 | 1 | 15 | 556 | 175 | 23 | 25 | 51 | 1930 | 3.4031 | 248 | 173 | 32 | 693 | 0 | 0 | 142 | 1 | 0.72921 | 8.9217 | 5.867 | 38.1692 | High | Medium | High | Top | 137 | 257 | 52.3432
FORESTHILL 1102 | 152181102 | NORTHERN | SIERRA | 29.7452 | 122980.6667 | 40.8218 | 78.51% | 55.95% | 43.8% | 0% | 2 | 0 | 38 | 99.72% | 0.01595% | 10.24% | 60 | 290 | 1 | 0 | 130 | 45 | 0 | 9 | 11 | 586 | 36.7281 | 104 | 55 | 4 | 223 | 0 | 0 | 38 | 0 | 0.25527 | 39.6063 | 3.7424 | 37.8357 | Low | High | Medium | Top | 138 | 76 | 148.2206
TASSAJARA 2104 | 014662104 | BAY AREA | DIABLO | 7.4925 | 934894.3333 | 45.6034 | 42.88% | 0% | 60.47% | 26.97% | 2 | 0 | 10 | 57.62% | 31.83% | 17.09% | 33 | 51 | 0 | 0 | 19 | 9 | 0 | 4 | 5 | 117 | 45.7381 | 15 | 17 | 3 | 42 | 0 | 0 | 10 | 1 | 0.67001 | 8.4601 | 6.6681 | 37.7974 | High | Medium | High | Top | 139 | 235 | 56.4128
DRUM 1101 | 152321101 | NORTHERN | SIERRA | 18.8373 | 38852.3333 | 40.9494 | 12.54% | 91.97% | 8.034% | 0% | 3 | 1 | 18 | 98.7% | 1.3% | 18.88% | 29 | 168 | 9 | 0 | 180 | 49 | 0 | 9 | 17 | 482 | 35.4483 | 32 | 16 | 3 | 104 | 0 | 0 | 18 | 1 | 0.5977 | 59.9623 | 1.0505 | 37.6487 | Medium | High | Low | Top | 140 | 213 | 62.9897
PINE GROVE 1102 | 163751102 | CENTRAL VALLEY | STOCKTON | 177.6802 | 1059080.6667 | 41.5789 | 39.49% | 69.29% | 21.95% | 0.3204% | 17 | 4 | 227 | 90.53% | 2.333% | 4.474% | 473 | 2499 | 7 | 0 | 1385 | 286 | 5 | 44 | 72 | 4806 | 34.2066 | 889 | 448 | 29 | 1913 | 0 | 3 | 224 | 0 | 0.18246 | 35.5813 | 5.6368 | 36.5942 | Low | High | High | Top | 141 | 45 | 200.5632
BEN LOMOND 1101 | 083041101 | CENTRAL COAST | CENTRAL COAST | 15.4019 | 131737.3333 | 43.9722 | 0% | 0% | 55.72% | 26.65% | 25 | 4 | 26 | 56.43% | 43.22% | 9.392% | 118 | 134 | 0 | 5 | 189 | 57 | 28 | 8 | 13 | 543 | 21.4279 | 78 | 47 | 7 | 205 | 0 | 0 | 26 | 0 | 0.7062 | 6.4203 | 8.0629 | 36.5574 | High | Medium | High | Top | 142 | 261 | 51.7663
POINT ARENA 1101 | 043381101 | NORTHERN | HUMBOLDT | 44.7075 | 253041 | 41.7775 | 32.83% | 7.617% | 22.77% | 69.01% | 28 | 1 | 59 | 17.1% | 82.26% | 4.4% | 69 | 185 | 0 | 5 | 254 | 33 | 2 | 10 | 15 | 750 | 37.9359 | 64 | 21 | 11 | 240 | 0 | 0 | 59 | 1 | 0.73932 | 19.1632 | 2.5157 | 35.6415 | High | High | Low | Top | 143 | 274 | 48.2086
MOLINO 1101 | 042571101 | NORTHERN | SONOMA | 34.3752 | 1326137.6667 | 43.9088 | 17.04% | 0.03488% | 68.7% | 29.48% | 6 | 0 | 88 | 64% | 34.21% | 6.519% | 190 | 472 | 0 | 13 | 198 | 64 | 13 | 6 | 9 | 813 | 35.8114 | 172 | 78 | 20 | 391 | 0 | 0 | 88 | 1 | 0.4493 | 19.5174 | 4.0205 | 35.257 | Medium | High | Medium | Top | 144 | 169 | 78.4703
BRUNSWICK 1103 | 152481103 | NORTHERN | SIERRA | 56.4048 | 1067549.3333 | 41.3644 | 13.51% | 62.41% | 31.22% | 5.069% | 4 | 1 | 169 | 81.85% | 16.84% | 11.68% | 126 | 1045 | 10 | 0 | 335 | 138 | 3 | 26 | 46 | 1849 | 37.0174 | 279 | 171 | 27 | 704 | 0 | 2 | 169 | 1 | 0.14531 | 56.0528 | 4.315 | 35.1465 | Low | High | Medium | Top | 145 | 24 | 241.8683
FULTON 1107 | 042561107 | NORTHERN | SONOMA | 38.1815 | 1355819.3333 | 43.9477 | 44.27% | 0.1011% | 63.83% | 27.3% | 6 | 3 | 51 | 66.33% | 27.73% | 8.235% | 186 | 378 | 0 | 6 | 209 | 95 | 15 | 8 | 18 | 765 | 34.733 | 140 | 74 | 14 | 373 | 0 | 2 | 49 | 1 | 0.45784 | 16.6839 | 4.5961 | 35.1072 | Medium | High | Medium | Top | 146 | 171 | 76.6806
WEST POINT 1102 | 163201102 | CENTRAL VALLEY | STOCKTON | 230.9017 | 563721.6667 | 41.661 | 28.27% | 88% | 7.589% | 0% | 20 | 9 | 289 | 93.01% | 3.954% | 3.801% | 434 | 2599 | 5 | 1 | 1348 | 396 | 13 | 36 | 71 | 5340 | 28.6072 | 923 | 305 | 7 | 2081 | 0 | 6 | 289 | 0 | 0.20713 | 35.6819 | 4.7401 | 35.0326 | Low | High | Medium | Top | 147 | 63 | 169.1346
BIG TREES 0402 | 083050402 | CENTRAL COAST | CENTRAL COAST | 16.2451 | 179748.6667 | 42.7589 | 0% | 0.849% | 40.88% | 45.19% | 30 | 1 | 28 | 37.02% | 49.89% | 8.659% | 86 | 131 | 0 | 6 | 256 | 66 | 56 | 8 | 11 | 589 | 33.5945 | 60 | 66 | 13 | 221 | 3 | 0 | 28 | 1 | 0.8653 | 5.1328 | 7.8809 | 35.0022 | High | Medium | High | Top | 148 | 302 | 40.4508
JARVIS 1111 | 013501111 | CENTRAL COAST | MISSION | 1.7872 | 1285978.3333 | 46.875 | 10.08% | 0% | 3.913% | 96.09% | 1 | 2 | 2 | 3.913% | 96.09% | 0% | 10 | 18 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 24 | 0.8 | 1 | 3 | 0 | 9 | 0 | 0 | 1 | 0 | 0.2221 | 27.9901 | 5.6278 | 34.9862 | Low | High | High | Top | 149 | 68 | 157.5226
CURTIS 1704 | 163351704 | CENTRAL VALLEY | YOSEMITE | 75.7369 | 1032983.3333 | 42.7292 | 0% | 21.67% | 51.52% | 12.63% | 12 | 1 | 89 | 71.24% | 21.97% | 4.389% | 317 | 1069 | 2 | 0 | 384 | 138 | 0 | 17 | 37 | 1914 | 21.6413 | 285 | 172 | 18 | 787 | 0 | 0 | 88 | 0 | 0.29832 | 20.5941 | 5.6887 | 34.9487 | Low | High | High | Top | 150 | 110 | 117.1534
NORTH DUBLIN 2101 | 014052101 | CENTRAL COAST | MISSION | 3.8203 | 1705733.6667 | 54.8485 | 111.3% | 0.4186% | 4.003% | 0.4585% | 0 | 0 | 2 | 4.422% | 0.4585% | 34.34% | 93 | 4 | 0 | 0 | 16 | 4 | 0 | 3 | 5 | 99 | 75.2 | 3 | 1 | 1 | 5 | 0 | 0 | 2 | 1 | 0.50495 | 10.8414 | 6.3623 | 34.8295 | Medium | Medium | High | Top | 151 | 193 | 68.9766
WILLITS 1104 | 042661104 | NORTHERN | HUMBOLDT | 86.9073 | 978692.3333 | 45.1893 | 29.96% | 52.92% | 34.17% | 6.231% | 9 | 1 | 119 | 86.82% | 6.51% | 6.631% | 812 | 1269 | 13 | 10 | 260 | 288 | 15 | 11 | 20 | 2247 | 42.7252 | 287 | 105 | 39 | 881 | 0 | 2 | 118 | 1 | 0.3021 | 37.5818 | 3.0623 | 34.7685 | Low | High | Low | Top | 152 | 115 | 115.0884
WILLOW CREEK 1101 | 192171101 | NORTHERN | HUMBOLDT | 48.6376 | 236976.6667 | 42.5683 | 41.37% | 27.06% | 48.46% | 0.005846% | 21 | 0 | 51 | 97.41% | 0.005846% | 50.27% | 152 | 43 | 0 | 0 | 524 | 73 | 27 | 15 | 21 | 923 | 34.2955 | 90 | 36 | 12 | 274 | 0 | 0 | 51 | 1 | 0.64034 | 35.5089 | 1.5081 | 34.2916 | Medium | High | Low | Top | 153 | 247 | 53.5525
SUNOL 1101 | 014241101 | CENTRAL COAST | MISSION | 38.3328 | 675538 | 44.5115 | 69.23% | 3.622% | 60.17% | 13.02% | 11 | 4 | 44 | 41.1% | 39.98% | 9.909% | 133 | 283 | 7 | 7 | 178 | 41 | 0 | 9 | 16 | 656 | 10.6432 | 59 | 56 | 5 | 199 | 0 | 2 | 44 | 0 | 0.48925 | 13.785 | 5.0808 | 34.2669 | Medium | High | Medium | Top | 154 | 188 | 70.0393
VINEYARD 2110 | 014502110 | CENTRAL COAST | MISSION | 6.8528 | 1350053.6667 | 42.7679 | 128.2% | 0% | 15.62% | 56.42% | 2 | 0 | 5 | 15.62% | 56.42% | 8.85% | 14 | 36 | 0 | 0 | 45 | 2 | 0 | 2 | 3 | 113 | 44.08 | 10 | 4 | 1 | 27 | 0 | 0 | 5 | 0 | 0.53485 | 11.3495 | 5.5876 | 33.9185 | Medium | Medium | High | Top | 155 | 211 | 63.4164
ROB ROY 2105 | 083692105 | CENTRAL COAST | CENTRAL COAST | 43.7417 | 1421678 | 44.4507 | 8.058% | 0.4349% | 68.03% | 18.71% | 30 | 7 | 94 | 65.28% | 22.25% | 6.667% | 139 | 493 | 0 | 12 | 288 | 91 | 17 | 38 | 48 | 1065 | 47.523 | 118 | 94 | 12 | 486 | 0 | 0 | 94 | 1 | 0.72299 | 7.8598 | 5.9669 | 33.9072 | High | Medium | High | Top | 156 | 281 | 46.8986
TULUCAY 1101 | 042301101 | BAY AREA | NORTH BAY | 5.2142 | 1477437 | 42.2222 | 8.963% | 0% | 30.47% | 69.45% | 0 | 1 | 3 | 30.47% | 69.45% | 8.333% | 4 | 12 | 0 | 0 | 9 | 5 | 12 | 1 | 3 | 36 | 4.5556 | 2 | 2 | 0 | 10 | 0 | 0 | 3 | 0 | 0.47375 | 16.6451 | 4.2652 | 33.6344 | Medium | High | Medium | Top | 157 | 186 | 70.9956
SAN LUIS OBISPO 1101 | 182631101 | CENTRAL COAST | LOS PADRES | 28.243 | 691252 | 41.6046 | 120.7% | 8.695% | 44.57% | 21.48% | 2 | 0 | 24 | 42.08% | 43.85% | 3.893% | 58 | 16 | 2 | 35 | 208 | 82 | 0 | 4 | 8 | 488 | 31.4885 | 43 | 32 | 5 | 138 | 0 | 0 | 24 | 0 | 0.29372 | 25.4113 | 4.4635 | 33.3146 | Low | High | Medium | Top | 158 | 119 | 113.4241
FOOTHILL 1102 | 182951102 | CENTRAL COAST | LOS PADRES | 11.5966 | 1015329 | 42.2917 | 51.79% | 0% | 53.14% | 5.519% | 4 | 0 | 16 | 53.14% | 14.94% | 17.13% | 22 | 12 | 0 | 11 | 122 | 23 | 0 | 3 | 9 | 216 | 33.3898 | 23 | 4 | 2 | 62 | 0 | 0 | 16 | 0 | 0.41901 | 14.7557 | 5.3882 | 33.314 | Medium | High | High | Top | 159 | 165 | 79.507
CAMP EVERS 2103 | 083622103 | CENTRAL COAST | CENTRAL COAST | 48.9903 | 837752 | 43.9178 | 13.65% | 0.3207% | 42.76% | 25.74% | 49 | 18 | 117 | 51.78% | 36.46% | 8.049% | 222 | 411 | 0 | 6 | 420 | 98 | 36 | 25 | 36 | 1230 | 50.4239 | 170 | 115 | 24 | 531 | 5 | 0 | 117 | 1 | 0.90961 | 5.454 | 6.6958 | 33.218 | High | Medium | High | Top | 160 | 324 | 36.5191
SAN LUIS OBISPO 1104 | 182631104 | CENTRAL COAST | LOS PADRES | 55.0451 | 846517.6667 | 42.6227 | 45.22% | 5.14% | 64.99% | 25.28% | 14 | 0 | 78 | 58.52% | 37.71% | 3.181% | 111 | 193 | 1 | 79 | 245 | 56 | 0 | 13 | 21 | 943 | 31.6207 | 62 | 33 | 10 | 248 | 0 | 1 | 78 | 0 | 0.46928 | 15.2773 | 4.6252 | 33.1594 | Medium | High | Medium | Top | 161 | 187 | 70.6602
CLEAR LAKE 1101 | 042141101 | NORTHERN | HUMBOLDT | 20.6199 | 835264 | 44.0314 | 33.73% | 1.064% | 84.1% | 14.84% | 5 | 0 | 20 | 85.16% | 14.84% | 6.545% | 84 | 127 | 0 | 4 | 134 | 44 | 10 | 1 | 2 | 382 | 38.3719 | 41 | 35 | 5 | 128 | 0 | 0 | 20 | 0 | 0.31052 | 21.5331 | 4.9446 | 33.0616 | Low | High | Medium | Top | 162 | 125 | 106.4727
SAN LUIS OBISPO 1105 | 182631105 | CENTRAL COAST | LOS PADRES | 2.3718 | 922696.6667 | 41.0484 | 35.1% | 1.227% | 36.65% | 38.53% | 0 | 0 | 6 | 37.87% | 38.53% | 3.226% | 4 | 1 | 0 | 1 | 35 | 4 | 0 | 1 | 2 | 62 | 15.3571 | 3 | 5 | 1 | 14 | 0 | 0 | 6 | 1 | 0.53568 | 12.2002 | 5.0535 | 33.0265 | Medium | Medium | Medium | Top | 163 | 219 | 61.6537
BRUNSWICK 1106 | 152481106 | NORTHERN | SIERRA | 174.0097 | 1283831.3333 | 42.2812 | 29.73% | 59.28% | 30.38% | 0.9753% | 19 | 11 | 272 | 78.86% | 12.16% | 11.24% | 375 | 2818 | 19 | 0 | 831 | 434 | 7 | 36 | 61 | 4820 | 39.1351 | 961 | 501 | 36 | 2088 | 0 | 5 | 272 | 0 | 0.26639 | 29.8946 | 4.1467 | 33.0222 | Low | High | Medium | Top | 164 | 104 | 123.9631
FORESTHILL 1101 | 152181101 | NORTHERN | SIERRA | 65.2463 | 717203.6667 | 39.6521 | 32.8% | 90.26% | 3.167% | 0.1137% | 6 | 7 | 140 | 93.37% | 0.5195% | 5.618% | 57 | 963 | 8 | 0 | 365 | 128 | 0 | 31 | 46 | 1780 | 42.6561 | 326 | 226 | 26 | 744 | 0 | 0 | 140 | 0 | 0.13101 | 62.8764 | 3.8926 | 32.0653 | Low | High | Medium | Top | 165 | 22 | 244.7513
NOVATO 1104 | 042211104 | BAY AREA | NORTH BAY | 4.7025 | 1065059 | 51.5714 | 22.56% | 15.79% | 37.33% | 29.34% | 0 | 0 | 5 | 35.54% | 46.92% | 3.077% | 35 | 10 | 0 | 0 | 25 | 8 | 0 | 2 | 4 | 65 | 12.3 | 5 | 2 | 0 | 13 | 0 | 0 | 5 | 0 | 0.47286 | 11.8674 | 5.5799 | 31.3125 | Medium | Medium | High | Top | 166 | 199 | 66.2189
SALMON CREEK 1101 | 043161101 | NORTHERN | SONOMA | 29.8535 | 493241 | 43.3764 | 38.45% | 0.007616% | 17.98% | 73.9% | 20 | 0 | 36 | 12.08% | 79.81% | 4.31% | 50 | 174 | 0 | 1 | 97 | 34 | 6 | 10 | 13 | 348 | 24.8256 | 33 | 21 | 8 | 88 | 0 | 3 | 36 | 0 | 0.60581 | 12.2083 | 4.2284 | 31.273 | Medium | Medium | Medium | Top | 167 | 262 | 51.6218
SAN RAFAEL 1107 | 042011107 | BAY AREA | NORTH BAY | 21.024 | 904257 | 44.2947 | 29.24% | 2.146% | 28.21% | 65.05% | 18 | 4 | 54 | 27.54% | 69.51% | 6.667% | 222 | 230 | 8 | 5 | 271 | 244 | 18 | 22 | 30 | 885 | 41.8753 | 105 | 134 | 45 | 367 | 0 | 0 | 54 | 1 | 0.84623 | 4.2874 | 8.5737 | 31.1065 | High | Medium | High | Top | 168 | 321 | 36.7589
HALF MOON BAY 1102 | 024101102 | CENTRAL COAST | PENINSULA | 9.0112 | 1004665.6667 | 42.2449 | 20.25% | 0% | 32.97% | 57.61% | 3 | 0 | 10 | 28.62% | 61.96% | 5.442% | 1 | 93 | 0 | 0 | 40 | 10 | 0 | 1 | 1 | 147 | 26.2885 | 14 | 11 | 3 | 52 | 4 | 0 | 10 | 0 | 0.60755 | 6.693 | 7.4146 | 30.1504 | Medium | Medium | High | Top | 169 | 270 | 49.626
EEL RIVER 1102 | 192381102 | NORTHERN | HUMBOLDT | 40.3143 | 853283.3333 | 41.3694 | 27.77% | 39.69% | 30.43% | 29.88% | 18 | 0 | 15 | 61.68% | 38.32% | 44.69% | 57 | 11 | 0 | 0 | 321 | 73 | 33 | 9 | 11 | 631 | 22.6667 | 29 | 9 | 3 | 99 | 1 | 0 | 15 | 0 | 0.67847 | 26.3681 | 1.6609 | 29.713 | High | High | Low | Top | 170 | 290 | 43.7943
COLUMBIA HILL 1101 | 152471101 | NORTHERN | SIERRA | 90.9452 | 320210 | 41.9552 | 37.57% | 51.19% | 48.58% | 0% | 16 | 3 | 99 | 99.88% | 0% | 12.86% | 188 | 1157 | 18 | 0 | 199 | 251 | 2 | 15 | 28 | 2076 | 40.6647 | 245 | 102 | 15 | 706 | 0 | 3 | 99 | 1 | 0.19573 | 39.5629 | 3.742 | 28.9769 | Low | High | Medium | Top | 171 | 77 | 148.0432
CAYETANO 2111 | 014422111 | CENTRAL COAST | MISSION | 5.6926 | 1694873 | 42.1084 | 18.37% | 1.868% | 58.97% | 39.17% | 0 | 0 | 1 | 27.84% | 72.16% | 9.639% | 0 | 20 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 83 | 24.1481 | 15 | 2 | 0 | 31 | 0 | 0 | 1 | 0 | 0.32508 | 16.3151 | 5.4631 | 28.9751 | Low | High | High | Top | 172 | 147 | 89.1313
GUALALA 1111 | 042841111 | NORTHERN | HUMBOLDT | 37.4475 | 390200 | 43.257 | 39.15% | 0.4% | 15.42% | 58.55% | 19 | 4 | 73 | 10.49% | 73.81% | 0.9646% | 120 | 178 | 0 | 5 | 296 | 9 | 10 | 27 | 44 | 622 | 33.2212 | 74 | 26 | 9 | 235 | 0 | 0 | 72 | 1 | 0.74923 | 11.7966 | 3.2724 | 28.9232 | High | Medium | Low | Top | 173 | 311 | 38.6037
SALT SPRINGS 2102 | 163692102 | CENTRAL VALLEY | STOCKTON | 52.0669 | 174733.6667 | 45.2358 | 15.15% | 63.02% | 1.348% | 0% | 4 | 0 | 49 | 97.67% | 2.329% | 4.379% | 625 | 933 | 0 | 0 | 268 | 88 | 45 | 16 | 32 | 1553 | 26.9377 | 413 | 125 | 6 | 766 | 0 | 2 | 48 | 1 | 0.155 | 45.6414 | 4.0669 | 28.7703 | Low | High | Medium | Top | 174 | 53 | 185.6202
HOOPA 1101 | 192401101 | NORTHERN | HUMBOLDT | 109.0104 | 374716 | 42.2778 | 76.54% | 36.54% | 52.94% | 1.34% | 66 | 4 | 109 | 97.73% | 1.856% | 38.68% | 244 | 47 | 0 | 0 | 1037 | 217 | 11 | 35 | 43 | 1988 | 29.7526 | 260 | 72 | 11 | 643 | 2 | 3 | 107 | 1 | 0.54358 | 28.7619 | 1.8223 | 28.4902 | Medium | High | Low | Top | 175 | 255 | 52.4119
SAN LUIS OBISPO 1107 | 182631107 | CENTRAL COAST | LOS PADRES | 48.8854 | 1313335.6667 | 41.8043 | 63.41% | 3.533% | 48.4% | 29.04% | 12 | 0 | 82 | 47.4% | 40.63% | 7.056% | 94 | 74 | 1 | 134 | 432 | 130 | 0 | 25 | 35 | 992 | 32.1584 | 103 | 34 | 3 | 323 | 0 | 0 | 81 | 1 | 0.52312 | 10.881 | 4.9523 | 28.1892 | Medium | Medium | Medium | Top | 176 | 245 | 53.8862
CAYUCOS 1101 | 182551101 | CENTRAL COAST | LOS PADRES | 2.5426 | 221217 | 38.9655 | 9.713% | 0% | 26.38% | 68.26% | 0 | 0 | 1 | 26.38% | 71.91% | 3.448% | 0 | 14 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 29 | 116.6 | 4 | 2 | 0 | 10 | 0 | 0 | 1 | 1 | 0.38046 | 22.1068 | 3.317 | 27.8987 | Medium | High | Low | Top | 177 | 178 | 73.3284
MC KEE 1111 | 083531111 | CENTRAL COAST | SAN JOSE | 8.9106 | 1066791.3333 | 44.0446 | 42.57% | 0% | 67.12% | 32.88% | 0 | 0 | 13 | 67.12% | 32.88% | 10.83% | 23 | 73 | 0 | 1 | 50 | 9 | 0 | 4 | 5 | 157 | 12.5556 | 21 | 12 | 2 | 54 | 0 | 0 | 13 | 1 | 0.53022 | 17.8967 | 2.8981 | 27.5012 | Medium | High | Low | Top | 178 | 259 | 51.8673
ARCATA 1122 | 192021122 | NORTHERN | HUMBOLDT | 20.6796 | 707240 | 41.8762 | 45.78% | 0.3739% | 44.86% | 53.1% | 12 | 0 | 31 | 45.78% | 54.22% | 56.01% | 58 | 21 | 0 | 1 | 362 | 34 | 3 | 5 | 10 | 516 | 27.8462 | 62 | 17 | 19 | 188 | 0 | 2 | 31 | 1 | 0.77057 | 6.9454 | 5.1355 | 27.4847 | High | Medium | Medium | Top | 179 | 327 | 35.6681
PENNGROVE 1101 | 043471101 | NORTHERN | SONOMA | 20.4175 | 939644.6667 | 44.6137 | 21.7% | 1.682% | 78.69% | 19.63% | 5 | 3 | 26 | 80.37% | 19.63% | 4.846% | 136 | 247 | 0 | 7 | 71 | 66 | 0 | 8 | 8 | 454 | 27.598 | 80 | 33 | 4 | 204 | 0 | 2 | 26 | 0 | 0.30952 | 23.2872 | 3.7267 | 26.8613 | Low | High | Low | Top | 180 | 151 | 86.7834
CLAYTON 2212 | 012022212 | BAY AREA | DIABLO | 48.6411 | 1195201.6667 | 44.6242 | 0% | 14.48% | 64.81% | 12.94% | 9 | 3 | 76 | 52.57% | 40.75% | 13.93% | 175 | 495 | 1 | 1 | 169 | 42 | 0 | 17 | 18 | 919 | 45.8519 | 118 | 104 | 14 | 351 | 0 | 0 | 76 | 1 | 0.61951 | 7.6487 | 5.6075 | 26.5708 | Medium | Medium | High | Top | 181 | 294 | 42.8903
SCE TEHACHAPI 1101 | 258131101 | CENTRAL VALLEY | KERN | 1.4276 | 3303.3333 | 0 | 0% | 0% | 56.93% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.26781 | 26.8233 | 3.6719 | 26.3773 | Low | High | Low | Top | 182 | 136 | 98.4917
PETALUMA C 1109 | 042631109 | NORTHERN | SONOMA | 50.3206 | 989739.3333 | 44.5784 | 45.21% | 0.3492% | 59.26% | 26.88% | 6 | 0 | 75 | 49.58% | 37.91% | 3.507% | 211 | 458 | 0 | 1 | 207 | 113 | 0 | 11 | 19 | 941 | 22.7729 | 75 | 36 | 5 | 241 | 0 | 1 | 74 | 0 | 0.34315 | 21.485 | 3.5633 | 26.2708 | Medium | High | Low | Top | 183 | 172 | 76.5572
RESERVATION ROAD 1101 | 182731101 | CENTRAL COAST | CENTRAL COAST | 26.4979 | 367194 | 42.1029 | 27.19% | 11.7% | 54.62% | 26.37% | 4 | 1 | 64 | 38.81% | 53.79% | 9.892% | 68 | 162 | 1 | 9 | 226 | 30 | 2 | 13 | 22 | 556 | 14.1441 | 74 | 50 | 5 | 244 | 0 | 0 | 64 | 1 | 0.63189 | 11.6366 | 3.5694 | 26.2459 | Medium | Medium | Low | Top | 184 | 299 | 41.5356
EL CERRITO G 1105 | 012501105 | BAY AREA | EAST BAY | 19.526 | 595064.3333 | 44.101 | 29.33% | 3.688% | 60.19% | 15.46% | 7 | 2 | 52 | 25.97% | 64.12% | 28.91% | 107 | 166 | 0 | 4 | 289 | 17 | 34 | 6 | 26 | 768 | 19.7189 | 46 | 115 | 24 | 234 | 0 | 0 | 52 | 0 | 0.52174 | 6.0467 | 8.3184 | 26.2432 | Medium | Medium | High | Top | 185 | 267 | 50.2994
CAYETANO 2109 | 014422109 | CENTRAL COAST | MISSION | 37.0707 | 935025 | 42.8694 | 40.93% | 0% | 59.19% | 25.44% | 0 | 0 | 46 | 59.33% | 35.19% | 19.55% | 32 | 266 | 0 | 0 | 160 | 17 | 0 | 7 | 9 | 583 | 43.6142 | 42 | 30 | 6 | 137 | 0 | 0 | 46 | 0 | 0.42316 | 11.2808 | 5.4929 | 26.221 | Medium | Medium | High | Top | 186 | 217 | 61.9645
ROB ROY 2104 | 083692104 | CENTRAL COAST | CENTRAL COAST | 106.0267 | 906993 | 43.4998 | 15.78% | 0.734% | 72.55% | 14.36% | 63 | 13 | 211 | 71.7% | 20.47% | 7.288% | 334 | 1233 | 1 | 14 | 626 | 211 | 78 | 47 | 59 | 2415 | 45.1421 | 279 | 118 | 20 | 987 | 8 | 0 | 211 | 1 | 0.70868 | 6.8211 | 5.4061 | 26.133 | High | Medium | High | Top | 187 | 320 | 36.8758
FLINT 1101 | 152531101 | NORTHERN | SIERRA | 6.2972 | 697988.3333 | 44.3262 | 44.08% | 6.072% | 61.82% | 20.02% | 1 | 0 | 10 | 64.72% | 23.21% | 8.451% | 29 | 81 | 0 | 0 | 27 | 8 | 0 | 3 | 9 | 142 | 29.0364 | 23 | 22 | 0 | 55 | 0 | 0 | 10 | 0 | 0.45312 | 11.8876 | 4.8331 | 26.0333 | Medium | Medium | Medium | Top | 188 | 231 | 57.454
SAUSALITO 1101 | 042491101 | BAY AREA | NORTH BAY | 0.75125 | 757959.6667 | 44.359 | 11.8% | 0% | 18.96% | 9.827% | 3 | 0 | 3 | 12.91% | 75.95% | 2.564% | 8 | 12 | 0 | 0 | 17 | 5 | 0 | 1 | 2 | 39 | 12.8667 | 0 | 7 | 1 | 15 | 0 | 0 | 3 | 1 | 0.56512 | 7.7572 | 5.9244 | 25.971 | Medium | Medium | High | Top | 189 | 285 | 45.9569
BRUNSWICK 1110 | 152481110 | NORTHERN | SIERRA | 24.9441 | 1326975 | 41.5924 | 18.5% | 43.86% | 34% | 0% | 3 | 0 | 40 | 56.96% | 20.9% | 9.772% | 58 | 432 | 6 | 0 | 127 | 53 | 11 | 12 | 21 | 788 | 35.9049 | 106 | 75 | 19 | 287 | 0 | 0 | 40 | 1 | 0.57292 | 9.2457 | 4.8758 | 25.8271 | Medium | Medium | Medium | Top | 190 | 287 | 45.0801
WILLOW CREEK 1103 | 192171103 | NORTHERN | HUMBOLDT | 84.8219 | 402608 | 41.3286 | 24.87% | 20.3% | 58.13% | 0.366% | 46 | 3 | 96 | 79.72% | 0.4735% | 48.48% | 103 | 55 | 0 | 0 | 1004 | 89 | 30 | 16 | 27 | 1706 | 33.2074 | 225 | 98 | 20 | 646 | 1 | 2 | 96 | 1 | 0.4792 | 25.4354 | 2.1189 | 25.8269 | Medium | High | Low | Top | 191 | 244 | 53.8957
PACIFICA 1103 | 022811103 | CENTRAL COAST | PENINSULA | 5.1834 | 366741 | 44.5775 | 3.111% | 1.604% | 13.5% | 7.182% | 2 | 0 | 4 | 3.981% | 18.3% | 5.556% | 14 | 19 | 0 | 0 | 36 | 6 | 1 | 2 | 7 | 72 | 14.5263 | 3 | 5 | 3 | 20 | 1 | 0 | 4 | 0 | 0.46166 | 8.529 | 6.4696 | 25.4741 | Medium | Medium | High | Top | 192 | 238 | 55.1792
RIO DELL 1102 | 192251102 | NORTHERN | HUMBOLDT | 54.1452 | 399090 | 40.5793 | 47.48% | 29.91% | 33.88% | 13.64% | 15 | 1 | 27 | 27.95% | 50.61% | 42.76% | 60 | 27 | 0 | 0 | 656 | 33 | 0 | 16 | 28 | 898 | 27.6838 | 36 | 16 | 4 | 123 | 0 | 1 | 24 | 0 | 0.53344 | 31.657 | 1.5043 | 25.4034 | Medium | High | Low | Top | 193 | 277 | 47.6217
ELK 1101 | 042981101 | NORTHERN | HUMBOLDT | 79.6211 | 489185 | 41.2989 | 60.79% | 6.005% | 33.57% | 54.94% | 53 | 1 | 121 | 15.74% | 82.42% | 9.971% | 139 | 456 | 0 | 12 | 372 | 130 | 10 | 13 | 23 | 1364 | 37.1869 | 180 | 35 | 16 | 498 | 0 | 2 | 120 | 1 | 0.76642 | 10.6701 | 3.0792 | 25.1809 | High | Medium | Low | Top | 194 | 340 | 32.8554
FORT BRAGG A 1102 | 042761102 | NORTHERN | HUMBOLDT | 65.6344 | 694872 | 43.2274 | 26.5% | 4.471% | 24.95% | 67.01% | 78 | 3 | 111 | 24.79% | 71.64% | 4.627% | 334 | 581 | 0 | 9 | 367 | 134 | 55 | 16 | 25 | 1621 | 35.5671 | 214 | 87 | 31 | 667 | 0 | 3 | 111 | 0 | 0.69983 | 9.8268 | 3.6102 | 24.8273 | High | Medium | Low | Top | 195 | 330 | 35.4763
BRUNSWICK 1102 | 152481102 | NORTHERN | SIERRA | 51.0819 | 584357.6667 | 42.8594 | 18.57% | 88.64% | 6.798% | 0% | 7 | 1 | 80 | 81.29% | 14.15% | 15.25% | 93 | 743 | 3 | 0 | 204 | 184 | 1 | 17 | 27 | 1298 | 36.6673 | 238 | 106 | 7 | 500 | 0 | 2 | 80 | 0 | 0.11075 | 58.9898 | 3.7495 | 24.4963 | Low | High | Medium | Top | 196 | 35 | 221.181
LAS POSITAS 2108 | 014402108 | CENTRAL COAST | MISSION | 8.2317 | 1375733.6667 | 43.6667 | 67.99% | 11.23% | 50.94% | 32.08% | 0 | 0 | 15 | 34.49% | 65.23% | 14.07% | 16 | 82 | 0 | 1 | 21 | 8 | 0 | 2 | 2 | 135 | 28.2692 | 3 | 7 | 4 | 32 | 0 | 0 | 15 | 0 | 0.61383 | 8.5365 | 4.6617 | 24.4271 | Medium | Medium | Medium | Top | 197 | 306 | 39.7948
PLACERVILLE 2106 | 153082106 | NORTHERN | SIERRA | 276.5055 | 1392202.6667 | 42.4766 | 31.57% | 50.23% | 36.82% | 4.119% | 37 | 4 | 406 | 79.07% | 12.22% | 4.603% | 563 | 3741 | 123 | 4 | 940 | 630 | 19 | 55 | 104 | 6822 | 40.202 | 1185 | 542 | 59 | 2553 | 0 | 9 | 406 | 0 | 0.25289 | 25.2136 | 3.8202 | 24.358 | Low | High | Medium | Top | 198 | 137 | 96.3205
SAN LUIS OBISPO 1103 | 182631103 | CENTRAL COAST | LOS PADRES | 19.9224 | 1227529 | 42.4841 | 18.95% | 0% | 66.14% | 25.17% | 6 | 0 | 34 | 66.14% | 25.19% | 7.789% | 63 | 60 | 0 | 66 | 178 | 33 | 0 | 5 | 7 | 475 | 26.0335 | 54 | 32 | 3 | 184 | 0 | 0 | 34 | 0 | 0.36473 | 11.7829 | 5.6258 | 24.1772 | Medium | Medium | High | Top | 199 | 198 | 66.2882
REDBUD 1101 | 043191101 | NORTHERN | HUMBOLDT | 50.857 | 569887.6667 | 43.4176 | 20.08% | 15.05% | 67.27% | 3.547% | 4 | 2 | 74 | 81.76% | 4.11% | 8.186% | 266 | 406 | 1 | 5 | 307 | 93 | 3 | 10 | 22 | 1075 | 30.2011 | 158 | 77 | 26 | 369 | 0 | 3 | 74 | 0 | 0.16109 | 32.1788 | 4.6637 | 24.1748 | Low | High | Medium | Top | 200 | 74 | 150.0715
HUMBOLDT BAY 1102 | 192341102 | NORTHERN | HUMBOLDT | 7.6153 | 641347 | 39.3706 | 20.18% | 0% | 3.741% | 96.26% | 3 | 0 | 9 | 0.8297% | 99.17% | 39.86% | 3 | 7 | 0 | 0 | 115 | 1 | 0 | 0 | 0 | 143 | 21.7619 | 15 | 7 | 2 | 45 | 0 | 0 | 9 | 0 | 0.44021 | 7.9626 | 6.8887 | 24.1463 | Medium | Medium | High | Top | 201 | 239 | 54.8519
MOLINO 1104 | 042571104 | NORTHERN | SONOMA | 2.6049 | 1197726 | 43.5 | 13.33% | 0% | 36.75% | 63.25% | 1 | 0 | 1 | 36.75% | 63.25% | 0% | 11 | 27 | 0 | 0 | 12 | 6 | 0 | 1 | 1 | 50 | 36.5833 | 11 | 4 | 1 | 24 | 0 | 0 | 1 | 0 | 0.41317 | 16.3193 | 3.5606 | 24.008 | Medium | High | Low | Top | 202 | 228 | 58.1064
HIGHLANDS 1102 | 043361102 | NORTHERN | HUMBOLDT | 37.0971 | 1292006.6667 | 44.2937 | 50.91% | 1.527% | 69.43% | 1.902% | 1 | 0 | 33 | 58.28% | 14.94% | 7.011% | 167 | 317 | 2 | 13 | 283 | 74 | 0 | 4 | 13 | 813 | 40.3849 | 78 | 76 | 33 | 250 | 0 | 0 | 33 | 0 | 0.17838 | 24.8843 | 5.3908 | 23.9291 | Low | High | High | Top | 203 | 92 | 134.1456
ANITA 1106 | 102841106 | NORTHERN | NORTH VALLEY | 1.7851 | 678856 | 41.5 | 2.269% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 10% | 0 | 4 | 0 | 0 | 3 | 2 | 5 | 0 | 0 | 10 | 33 | 2 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0.22299 | 36.1193 | 2.9673 | 23.8997 | Low | High | Low | Top | 204 | 123 | 107.1758
LOW GAP 1101 | 192411101 | NORTHERN | HUMBOLDT | 71.107 | 138249.3333 | 39.9325 | 36.89% | 72.24% | 13.89% | 0% | 12 | 0 | 87 | 99.7% | 0% | 32.86% | 76 | 192 | 0 | 8 | 1002 | 111 | 0 | 15 | 27 | 1564 | 21.3201 | 112 | 28 | 14 | 423 | 0 | 0 | 87 | 0 | 0.31922 | 37.7486 | 1.9831 | 23.8968 | Low | High | Low | Top | 205 | 176 | 74.8605
HATTON 1101 | 182291101 | CENTRAL COAST | CENTRAL COAST | 16.0491 | 831835.3333 | 39.942 | 18.08% | 1.257% | 60.03% | 22.96% | 2 | 3 | 24 | 37.58% | 48.7% | 8.357% | 25 | 84 | 0 | 4 | 148 | 24 | 0 | 8 | 12 | 347 | 15.0168 | 39 | 25 | 6 | 121 | 0 | 0 | 23 | 0 | 0.46974 | 11.2329 | 4.47 | 23.5863 | Medium | Medium | Medium | Top | 206 | 268 | 50.2114
WYANDOTTE 1106 | 102911106 | NORTHERN | NORTH VALLEY | 2.1424 | 1331297.3333 | 45.8333 | 3.022% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 2 | 3 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 18 | 47.5 | 5 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 0.24462 | 18.9456 | 4.9601 | 22.9876 | Low | High | Medium | Top | 207 | 140 | 93.9729
BRIDGEVILLE 1102 | 192461102 | NORTHERN | HUMBOLDT | 35.2561 | 71499 | 45.2783 | 34.27% | 16.97% | 70.78% | 0% | 5 | 0 | 33 | 99.57% | 0% | 34.54% | 178 | 13 | 0 | 1 | 366 | 24 | 0 | 7 | 11 | 524 | 32.9725 | 31 | 14 | 7 | 114 | 0 | 2 | 33 | 0 | 0.45248 | 49.2394 | 1.0316 | 22.9841 | Medium | High | Low | Top | 208 | 264 | 50.7954
ROSSMOOR 1101 | 014161101 | BAY AREA | DIABLO | 13.7756 | 880452.6667 | 43.5049 | 35.63% | 0% | 32.74% | 48.49% | 26 | 2 | 40 | 24.8% | 56.42% | 11.17% | 73 | 90 | 0 | 0 | 193 | 19 | 9 | 5 | 12 | 412 | 17.5174 | 34 | 103 | 33 | 208 | 0 | 0 | 40 | 0 | 0.74002 | 5.1737 | 5.9514 | 22.786 | High | Medium | High | Top | 209 | 360 | 30.7909
TASSAJARA 2109 | 014662109 | BAY AREA | DIABLO | 1.2042 | 719239 | 0 | 62.8% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.34331 | 9.4155 | 6.9926 | 22.6033 | Medium | Medium | High | Top | 210 | 200 | 65.8392
PUTAH CREEK 1103 | 063681103 | NORTHERN | SACRAMENTO | 4.0778 | 820485.3333 | 42.8431 | 6.4% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 11.76% | 9 | 17 | 6 | 0 | 9 | 15 | 0 | 0 | 0 | 51 | 34.2727 | 6 | 2 | 0 | 13 | 0 | 0 | 0 | 0 | 0.20705 | 33.5773 | 3.2063 | 22.2902 | Low | High | Low | Top | 211 | 121 | 107.658
LLAGAS 2107 | 083182107 | CENTRAL COAST | SAN JOSE | 9.1355 | 1392960.3333 | 41.7939 | 40.48% | 0% | 71.27% | 18.13% | 0 | 0 | 15 | 63.4% | 28.54% | 4.58% | 24 | 83 | 0 | 1 | 25 | 3 | 0 | 1 | 1 | 131 | 16.7636 | 21 | 15 | 2 | 59 | 0 | 0 | 15 | 0 | 0.35821 | 16.1281 | 3.8499 | 22.2414 | Medium | High | Medium | Top | 212 | 216 | 62.0911
PHILO 1102 | 042601102 | NORTHERN | HUMBOLDT | 91.607 | 267821 | 42.0276 | 52.79% | 3.105% | 86.33% | 8.621% | 26 | 2 | 82 | 81.49% | 18.04% | 8.598% | 158 | 498 | 0 | 28 | 330 | 112 | 0 | 11 | 15 | 1419 | 38.444 | 190 | 54 | 13 | 533 | 0 | 5 | 81 | 0 | 0.27998 | 31.5923 | 2.4968 | 22.0846 | Low | High | Low | Top | 213 | 167 | 78.8787
FORT BRAGG A 1104 | 042761104 | NORTHERN | HUMBOLDT | 26.426 | 480870.6667 | 40.9883 | 15% | 1.766% | 23.28% | 69.39% | 11 | 0 | 69 | 22.94% | 76.2% | 7.299% | 45 | 205 | 1 | 2 | 233 | 64 | 28 | 4 | 4 | 685 | 33.2632 | 111 | 50 | 14 | 309 | 0 | 0 | 67 | 0 | 0.69322 | 8.8034 | 3.6033 | 21.9897 | High | Medium | Low | Top | 214 | 348 | 31.7212
OAKHURST 1103 | 254421103 | CENTRAL VALLEY | YOSEMITE | 129.2156 | 1392881.3333 | 40.0855 | 0% | 65.77% | 17.19% | 0.3504% | 32 | 2 | 190 | 75.05% | 11.4% | 23.1% | 122 | 546 | 0 | 0 | 1391 | 265 | 17 | 39 | 67 | 3299 | 26.6074 | 469 | 314 | 46 | 1404 | 0 | 3 | 186 | 0 | 0.27031 | 21.771 | 3.734 | 21.9744 | Low | High | Low | Top | 215 | 161 | 81.2928
SCE REFUGIO 1101 | 188071101 | CENTRAL COAST | LOS PADRES | 0.29161 | 0 | 0 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0.23266 | 47.7737 | 1.9745 | 21.9458 | Low | High | Low | Top | 216 | 139 | 94.3271
HICKS 2101 | 083432101 | CENTRAL COAST | SAN JOSE | 17.3217 | 1240974.3333 | 44.1935 | 67.8% | 0.4407% | 47.47% | 20.94% | 5 | 0 | 17 | 41.44% | 27.41% | 9.545% | 51 | 97 | 0 | 5 | 62 | 14 | 7 | 3 | 3 | 220 | 32.973 | 26 | 15 | 3 | 82 | 0 | 0 | 17 | 0 | 0.54487 | 10.2974 | 3.8628 | 21.6733 | Medium | Medium | Medium | Top | 217 | 307 | 39.7772
LAYTONVILLE 1102 | 042681102 | NORTHERN | HUMBOLDT | 114.8069 | 241083.3333 | 41.8251 | 15.8% | 43.57% | 44.21% | 0.2741% | 11 | 3 | 101 | 95.61% | 0.4488% | 7.915% | 202 | 449 | 1 | 12 | 564 | 267 | 0 | 20 | 33 | 1794 | 33.0655 | 129 | 41 | 15 | 463 | 0 | 1 | 101 | 0 | 0.27405 | 46.6879 | 1.6916 | 21.6439 | Low | High | Low | Top | 218 | 166 | 78.9784
GANSNER 1101 | 103021101 | NORTHERN | NORTH VALLEY | 39.2147 | 433695 | 43.3222 | 18.21% | 82.72% | 7.229% | 9.981% | 3 | 1 | 40 | 88.36% | 11.57% | 10.64% | 208 | 544 | 9 | 0 | 272 | 112 | 2 | 10 | 12 | 1081 | 37.7562 | 129 | 62 | 6 | 292 | 0 | 2 | 39 | 0 | 0.14642 | 35.2913 | 4.1621 | 21.5069 | Low | High | Medium | Top | 219 | 78 | 146.8844
MONTICELLO 1101 | 043051101 | BAY AREA | NORTH BAY | 114.3461 | 412528 | 43.6848 | 85.14% | 3.791% | 87.7% | 7.604% | 14 | 7 | 98 | 64.78% | 34.32% | 6.723% | 277 | 694 | 3 | 14 | 575 | 384 | 10 | 24 | 41 | 1904 | 31 | 207 | 106 | 11 | 546 | 0 | 4 | 98 | 0 | 0.39577 | 13.3474 | 4.0532 | 21.411 | Medium | High | Medium | Top | 220 | 242 | 54.1003
PERRY 1101 | 183071101 | CENTRAL COAST | LOS PADRES | 70.1245 | 547419 | 41.3534 | 16.81% | 3.192% | 45.63% | 40.66% | 13 | 1 | 103 | 34.54% | 57.69% | 3.878% | 104 | 138 | 0 | 159 | 693 | 125 | 0 | 19 | 39 | 1470 | 25.5915 | 174 | 87 | 7 | 462 | 0 | 0 | 103 | 0 | 0.54895 | 7.3713 | 5.2829 | 21.3772 | Medium | Medium | Medium | Top | 221 | 310 | 38.9417
RACETRACK 1704 | 163761704 | CENTRAL VALLEY | YOSEMITE | 45.5677 | 180126 | 43.3317 | 45.93% | 2.308% | 56.44% | 28.44% | 3 | 3 | 43 | 38.93% | 50.17% | 3.149% | 164 | 521 | 0 | 0 | 225 | 97 | 6 | 7 | 12 | 1048 | 27.5783 | 152 | 67 | 6 | 376 | 0 | 0 | 43 | 0 | 0.30415 | 14.732 | 4.7463 | 21.2671 | Low | High | Medium | Top | 222 | 189 | 69.9224
WEST POINT 1101 | 163201101 | CENTRAL VALLEY | STOCKTON | 63.0247 | 313435.6667 | 41.0194 | 44.91% | 89.98% | 0% | 0% | 1 | 3 | 72 | 90.89% | 5.997% | 1.771% | 148 | 1043 | 4 | 0 | 568 | 68 | 0 | 10 | 38 | 1863 | 32.8842 | 447 | 207 | 5 | 863 | 0 | 3 | 70 | 0 | 0.073726 | 60.3254 | 4.7757 | 21.2403 | Low | High | Medium | Top | 223 | 15 | 288.0982
LUCERNE 1106 | 043351106 | NORTHERN | HUMBOLDT | 37.8799 | 845747.6667 | 45.3434 | 57.6% | 2.469% | 62.94% | 12.15% | 11 | 1 | 51 | 65.41% | 12.15% | 8.037% | 453 | 493 | 1 | 4 | 207 | 175 | 7 | 7 | 16 | 1095 | 41.5934 | 214 | 173 | 44 | 524 | 0 | 3 | 51 | 0 | 0.31024 | 12.0284 | 5.6516 | 21.09 | Low | Medium | High | Top | 224 | 195 | 67.9795
DUNBAR 1103 | 043071103 | NORTHERN | SONOMA | 32.1454 | 645561.3333 | 44.5221 | 56.3% | 0% | 88.63% | 8.735% | 1 | 2 | 24 | 87.06% | 10.31% | 7.875% | 113 | 251 | 2 | 5 | 98 | 102 | 0 | 6 | 7 | 546 | 39.7349 | 89 | 42 | 10 | 222 | 0 | 0 | 24 | 0 | 0.13363 | 27.724 | 5.6755 | 21.0257 | Low | High | High | Top | 225 | 69 | 157.3488
GEYSERVILLE 1101 | 042891101 | NORTHERN | SONOMA | 76.3146 | 772005 | 43.9944 | 16.55% | 1.539% | 82.14% | 13.09% | 6 | 1 | 50 | 84.22% | 13.09% | 11.53% | 185 | 498 | 0 | 19 | 90 | 179 | 35 | 15 | 19 | 902 | 29.6115 | 104 | 43 | 10 | 289 | 0 | 0 | 50 | 0 | 0.28882 | 21.875 | 3.2553 | 20.5671 | Low | High | Low | Top | 226 | 185 | 71.2095
GREEN VALLEY 2101 | 083192101 | CENTRAL COAST | CENTRAL COAST | 45.9799 | 1544278.6667 | 43.1863 | 11.38% | 0.1774% | 62.85% | 31.7% | 18 | 0 | 47 | 61.69% | 34.45% | 4.878% | 100 | 383 | 0 | 3 | 245 | 45 | 0 | 11 | 12 | 820 | 47.3034 | 65 | 27 | 9 | 285 | 4 | 0 | 47 | 1 | 0.62633 | 7.1918 | 4.5628 | 20.5529 | Medium | Medium | Medium | Top | 227 | 341 | 32.8148
STANISLAUS 1701 | 162821701 | CENTRAL VALLEY | YOSEMITE | 45.3745 | 376817.6667 | 43.848 | 19.74% | 69.23% | 1.57% | 0.6919% | 1 | 2 | 72 | 63.97% | 7.656% | 4.91% | 284 | 589 | 0 | 0 | 406 | 54 | 0 | 8 | 34 | 1283 | 23.438 | 218 | 123 | 11 | 531 | 0 | 0 | 72 | 0 | 0.15783 | 21.9018 | 5.9241 | 20.4777 | Low | High | High | Top | 228 | 98 | 129.7481
EMERALD LAKE 0401 | 024080401 | CENTRAL COAST | PENINSULA | 16.2767 | 245797.3333 | 43.1377 | 58.16% | 0% | 36.54% | 38.06% | 9 | 0 | 30 | 30.34% | 69.37% | 12.19% | 40 | 187 | 0 | 2 | 178 | 21 | 17 | 1 | 10 | 443 | 41.52 | 30 | 86 | 25 | 177 | 3 | 0 | 29 | 0 | 0.71426 | 3.2162 | 8.9033 | 20.4527 | High | Medium | High | Top | 229 | 367 | 28.6349
LAYTONVILLE 1101 | 042681101 | NORTHERN | HUMBOLDT | 53.8079 | 227276.3333 | 42.2127 | 36% | 30.05% | 40.22% | 0.07462% | 7 | 7 | 52 | 97.69% | 0.07462% | 10.48% | 102 | 326 | 0 | 3 | 191 | 54 | 16 | 6 | 11 | 935 | 36.2151 | 105 | 28 | 13 | 288 | 0 | 0 | 52 | 0 | 0.38664 | 36.3313 | 1.4317 | 20.1108 | Medium | High | Low | Top | 230 | 258 | 52.0143
FELTON 0401 | 083140401 | CENTRAL COAST | CENTRAL COAST | 2.536 | 8693 | 50 | 0% | 0% | 4.149% | 13.64% | 3 | 0 | 3 | 4.149% | 95.85% | 27.12% | 41 | 12 | 0 | 1 | 23 | 15 | 3 | 2 | 4 | 59 | 22 | 5 | 4 | 2 | 13 | 0 | 0 | 3 | 1 | 0.68495 | 3.6103 | 8.0992 | 20.0282 | High | Medium | High | Top | 231 | 365 | 29.2403
FITCH MOUNTAIN 1111 | 042751111 | NORTHERN | SONOMA | 3.8443 | 985909.6667 | 43.4211 | 30.64% | 8.052% | 44.36% | 47.25% | 0 | 0 | 0 | 52.42% | 47.25% | 10.53% | 20 | 23 | 1 | 2 | 20 | 8 | 0 | 0 | 0 | 57 | 30.8 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 0.48412 | 11.4461 | 3.6063 | 19.9835 | Medium | Medium | Low | Top | 232 | 300 | 41.2776
APPLE HILL 1104 | 153661104 | NORTHERN | SIERRA | 93.3232 | 721905.3333 | 41.8187 | 25.47% | 84.35% | 7.756% | 0.5476% | 11 | 3 | 170 | 90.26% | 3.94% | 0.9738% | 169 | 1508 | 26 | 0 | 526 | 149 | 18 | 19 | 32 | 2670 | 42.4293 | 552 | 282 | 23 | 1142 | 0 | 3 | 170 | 0 | 0.11727 | 51.8866 | 3.2527 | 19.7917 | Low | High | Low | Top | 233 | 64 | 168.7734
ALTO 1122 | 042031122 | BAY AREA | NORTH BAY | 9.2369 | 541722.3333 | 43.7024 | 21.44% | 0% | 26.32% | 46.46% | 6 | 2 | 17 | 26.28% | 58.56% | 9.176% | 75 | 80 | 9 | 4 | 167 | 97 | 23 | 2 | 8 | 425 | 30.0855 | 42 | 45 | 17 | 155 | 0 | 0 | 17 | 1 | 0.78086 | 3.4502 | 7.3044 | 19.6788 | High | Medium | High | Top | 234 | 384 | 25.2014
BRUNSWICK 1104 | 152481104 | NORTHERN | SIERRA | 56.8876 | 1004879.3333 | 41.5361 | 23.73% | 63.18% | 27.21% | 2.673% | 6 | 2 | 99 | 83.29% | 9.921% | 11.92% | 122 | 845 | 9 | 1 | 364 | 179 | 19 | 10 | 31 | 1636 | 38.3063 | 248 | 169 | 19 | 632 | 0 | 3 | 99 | 0 | 0.11063 | 38.5596 | 4.5752 | 19.5179 | Low | High | Medium | Top | 235 | 59 | 176.4199
PINECREST 0401 | 163160401 | CENTRAL VALLEY | YOSEMITE | 2.308 | 17353 | 40.7692 | 123.7% | 100% | 0% | 0% | 1 | 0 | 2 | 100% | 0% | 16.92% | 1 | 7 | 0 | 0 | 70 | 2 | 0 | 1 | 2 | 130 | 8.7308 | 6 | 16 | 0 | 26 | 0 | 0 | 2 | 1 | 0.55994 | 10.7721 | 3.2114 | 19.3702 | Medium | Medium | Low | Top | 236 | 334 | 34.5934
SEACLIFF 0401 | 083500401 | CENTRAL COAST | CENTRAL COAST | 8.831 | 68383.6667 | 44.7143 | 89.29% | 0% | 69.59% | 23.45% | 3 | 0 | 11 | 69.59% | 23.45% | 6.667% | 43 | 91 | 0 | 3 | 67 | 17 | 23 | 4 | 6 | 210 | 27.716 | 17 | 25 | 2 | 84 | 0 | 0 | 11 | 0 | 0.52438 | 5.9604 | 6.131 | 19.1625 | Medium | Medium | High | Top | 237 | 323 | 36.5429
VACA DIXON 1101 | 063591101 | NORTHERN | SACRAMENTO | 0.95938 | 1369157.6667 | 44.7222 | 0.7454% | 40.21% | 59.79% | 0% | 0 | 0 | 3 | 100% | 0% | 5.556% | 5 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 18 | 17.2 | 4 | 1 | 0 | 7 | 0 | 0 | 3 | 0 | 0.23531 | 20.3765 | 3.9802 | 19.084 | Low | High | Medium | Top | 238 | 162 | 81.1016
SYCAMORE CREEK 1111 | 102971111 | NORTHERN | NORTH VALLEY | 54.4191 | 856377.3333 | 41.5149 | 121.2% | 57.08% | 32.93% | 6.766% | 4 | 2 | 61 | 90.01% | 6.766% | 7.16% | 74 | 483 | 30 | 0 | 187 | 46 | 0 | 9 | 11 | 1243 | 38.4848 | 153 | 80 | 5 | 382 | 0 | 6 | 61 | 0 | 0.078038 | 49.371 | 4.9398 | 19.0319 | Low | High | Medium | Top | 239 | 23 | 243.8816
MILPITAS 1109 | 082831109 | CENTRAL COAST | SAN JOSE | 31.7351 | 944263.6667 | 42.297 | 46.2% | 10.39% | 84% | 0.9638% | 9 | 0 | 19 | 94.39% | 0.9638% | 5.051% | 42 | 151 | 0 | 1 | 117 | 5 | 0 | 11 | 16 | 396 | 9.042 | 36 | 24 | 6 | 129 | 0 | 0 | 18 | 0 | 0.39836 | 16.4592 | 2.901 | 19.0211 | Medium | High | Low | Top | 240 | 276 | 47.7484
WILLITS 1103 | 042661103 | NORTHERN | HUMBOLDT | 145.158 | 627725.6667 | 43.3384 | 22.62% | 33.33% | 60.18% | 4.309% | 22 | 1 | 155 | 88.19% | 9.633% | 10.87% | 563 | 1124 | 4 | 39 | 761 | 357 | 21 | 36 | 52 | 2961 | 38.7011 | 389 | 132 | 33 | 1035 | 0 | 7 | 154 | 0 | 0.23888 | 34.3856 | 2.2905 | 18.8143 | Low | High | Low | Top | 241 | 168 | 78.7604
COTATI 1105 | 042271105 | NORTHERN | SONOMA | 39.2511 | 853816.3333 | 43.1749 | 51.84% | 7.026% | 56.51% | 22.56% | 7 | 1 | 72 | 51.92% | 34.18% | 3.934% | 170 | 524 | 0 | 4 | 200 | 119 | 8 | 22 | 34 | 915 | 37.1816 | 140 | 68 | 16 | 374 | 0 | 4 | 72 | 0 | 0.32337 | 19.3531 | 2.9919 | 18.7239 | Low | High | Low | Top | 242 | 229 | 57.9026
NOTRE DAME 1104 | 102041104 | NORTHERN | NORTH VALLEY | 28.6184 | 1065755.6667 | 43.1707 | 38.88% | 7.59% | 62.48% | 0% | 0 | 1 | 10 | 70.07% | 0% | 7.266% | 71 | 178 | 4 | 0 | 59 | 9 | 0 | 5 | 9 | 578 | 39.5289 | 67 | 23 | 2 | 126 | 0 | 3 | 10 | 0 | 0.28459 | 11.1999 | 5.831 | 18.5858 | Low | Medium | High | Top | 243 | 203 | 65.307
SAUSALITO 1102 | 042491102 | BAY AREA | NORTH BAY | 8.7614 | 820352.6667 | 43.0369 | 19.47% | 4.189% | 12.46% | 42.41% | 4 | 1 | 17 | 11.63% | 73.47% | 4.362% | 40 | 44 | 0 | 1 | 202 | 22 | 0 | 10 | 15 | 298 | 35.0161 | 24 | 14 | 5 | 63 | 0 | 0 | 17 | 1 | 0.73232 | 4.1671 | 5.9676 | 18.2113 | High | Medium | High | Top | 244 | 386 | 24.8678
ARCATA 1121 | 192021121 | NORTHERN | HUMBOLDT | 6.8402 | 810260 | 40.963 | 75.92% | 2.883% | 3.664% | 93.45% | 7 | 0 | 10 | 6.547% | 93.45% | 40.74% | 0 | 4 | 0 | 0 | 92 | 7 | 0 | 2 | 2 | 135 | 15.4375 | 9 | 2 | 3 | 33 | 0 | 0 | 10 | 1 | 0.5651 | 7.3201 | 4.2129 | 17.4269 | Medium | Medium | Medium | Top | 245 | 359 | 30.8384
SPRUCE 0401 | 013340401 | BAY AREA | EAST BAY | 4.123 | 83704.6667 | 44.7953 | 34.2% | 0% | 40.19% | 28.52% | 3 | 0 | 12 | 7.456% | 66% | 65.7% | 22 | 15 | 0 | 0 | 35 | 4 | 2 | 3 | 8 | 172 | 45.7818 | 6 | 24 | 14 | 55 | 0 | 0 | 12 | 1 | 0.7654 | 2.5009 | 9.038 | 17.3002 | High | Medium | High | Top | 246 | 392 | 22.6029
RINCON 1101 | 043321101 | NORTHERN | SONOMA | 22.5067 | 856789 | 43.9057 | 46.18% | 0% | 89.1% | 5.069% | 0 | 1 | 27 | 89.1% | 5.069% | 6.767% | 59 | 138 | 0 | 0 | 69 | 32 | 0 | 7 | 9 | 266 | 33.1448 | 64 | 31 | 10 | 151 | 0 | 0 | 27 | 1 | 0.20622 | 20.328 | 4.0865 | 17.1307 | Low | High | Medium | Top | 247 | 160 | 83.07
GRASS VALLEY 1101 | 152031101 | NORTHERN | SIERRA | 17.4986 | 470903 | 42.0538 | 20.32% | 47.37% | 21.93% | 1.034% | 1 | 0 | 43 | 63.29% | 7.041% | 7.312% | 48 | 268 | 2 | 0 | 81 | 29 | 0 | 3 | 14 | 465 | 33.0793 | 82 | 30 | 3 | 166 | 0 | 1 | 43 | 0 | 0.26083 | 14.2287 | 4.5855 | 17.0183 | Low | High | Medium | Top | 248 | 204 | 65.2463
GARBERVILLE 1103 | 192221103 | NORTHERN | HUMBOLDT | 1.5013 | 204302 | 42.7083 | 10.26% | 0% | 22.25% | 56.82% | 0 | 0 | 2 | 18.44% | 72.86% | 25% | 4 | 4 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 24 | 30.2222 | 3 | 3 | 1 | 9 | 0 | 0 | 2 | 1 | 0.51486 | 7.0838 | 4.657 | 16.985 | Medium | Medium | Medium | Top | 249 | 338 | 32.9893
LAURELES 1111 | 182371111 | CENTRAL COAST | CENTRAL COAST | 105.5941 | 313728.3333 | 40.507 | 34.76% | 21.84% | 71.69% | 2.14% | 20 | 2 | 111 | 80.39% | 18.12% | 12.52% | 153 | 729 | 0 | 88 | 537 | 150 | 0 | 15 | 20 | 1789 | 14.9403 | 171 | 83 | 18 | 617 | 0 | 0 | 111 | 0 | 0.23895 | 22.8849 | 3.0551 | 16.7061 | Low | High | Low | Top | 250 | 190 | 69.9159
CABRILLO 1103 | 183101103 | CENTRAL COAST | LOS PADRES | 61.5614 | 439667.3333 | 41.4516 | 44.87% | 9.704% | 52.79% | 21.84% | 1 | 1 | 50 | 56.48% | 31.3% | 2.335% | 55 | 87 | 2 | 184 | 307 | 160 | 0 | 4 | 7 | 1028 | 24.3281 | 66 | 34 | 4 | 275 | 0 | 0 | 49 | 0 | 0.19035 | 15.1342 | 5.7894 | 16.6782 | Low | High | High | Top | 251 | 148 | 87.6175
UPPER LAKE 1101 | 042871101 | NORTHERN | HUMBOLDT | 57.6996 | 410579 | 44.0754 | 58.66% | 9.214% | 53.33% | 32.16% | 4 | 1 | 25 | 61.24% | 33.46% | 7.415% | 244 | 444 | 0 | 17 | 234 | 147 | 24 | 8 | 16 | 998 | 36.4437 | 128 | 51 | 11 | 325 | 0 | 1 | 25 | 0 | 0.47303 | 13.3397 | 2.6416 | 16.6684 | Medium | High | Low | Top | 252 | 331 | 35.2378
BUELLTON 1101 | 183041101 | CENTRAL COAST | LOS PADRES | 83.6196 | 1244816.3333 | 41.788 | 38.57% | 8.091% | 58.81% | 17.29% | 6 | 2 | 68 | 62.04% | 23.75% | 2.684% | 105 | 110 | 2 | 246 | 351 | 182 | 0 | 11 | 17 | 1267 | 20.1398 | 74 | 30 | 14 | 352 | 0 | 0 | 67 | 0 | 0.2908 | 15.5306 | 3.6659 | 16.5566 | Low | High | Low | Top | 253 | 233 | 56.9339
GREENBRAE 1103 | 043091103 | BAY AREA | NORTH BAY | 5.5389 | 1089266 | 43.1922 | 9.46% | 0% | 32.68% | 65.01% | 10 | 1 | 8 | 32.68% | 66.45% | 9.091% | 43 | 79 | 5 | 1 | 113 | 79 | 9 | 1 | 1 | 308 | 26.4937 | 21 | 29 | 16 | 83 | 0 | 0 | 8 | 1 | 0.83128 | 2.375 | 8.3516 | 16.4882 | High | Low | High | Top | 254 | 418 | 19.8346
CAMBRIA 1102 | 182771102 | CENTRAL COAST | LOS PADRES | 19.7066 | 241500.3333 | 42.5837 | 17.92% | 0.2957% | 51.45% | 43.75% | 1 | 0 | 12 | 31.12% | 67.03% | 7.177% | 27 | 4 | 0 | 14 | 108 | 29 | 0 | 3 | 4 | 209 | 32.7 | 20 | 11 | 6 | 62 | 0 | 0 | 11 | 0 | 0.50187 | 7.6706 | 4.246 | 16.3457 | Medium | Medium | Medium | Top | 255 | 342 | 32.5697
PAUL SWEET 2104 | 083252104 | CENTRAL COAST | CENTRAL COAST | 17.7398 | 1907378 | 45.2185 | 8.745% | 0% | 76.87% | 11.53% | 3 | 0 | 52 | 76.1% | 12.43% | 4.37% | 91 | 203 | 0 | 5 | 108 | 27 | 0 | 10 | 10 | 389 | 57.9791 | 42 | 39 | 8 | 192 | 4 | 0 | 52 | 0 | 0.35781 | 7.4358 | 6.1387 | 16.3329 | Medium | Medium | High | Top | 256 | 286 | 45.6462
OAKLAND D 1112 | 012041112 | BAY AREA | EAST BAY | 2.7059 | 1308951.6667 | 45.1087 | 8.874% | 25.7% | 11.84% | 33.9% | 2 | 0 | 8 | 29.52% | 62.52% | 36.96% | 30 | 14 | 0 | 0 | 43 | 16 | 6 | 6 | 9 | 92 | 11.6923 | 8 | 7 | 5 | 29 | 0 | 0 | 8 | 0 | 0.66632 | 3.5155 | 6.8847 | 16.1272 | High | Medium | High | Top | 257 | 388 | 24.2033
TOCALOMA 0241 | 043150241 | BAY AREA | NORTH BAY | 0.031239 | 140551.6667 | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2517 | 11.2183 | 5.7098 | 16.1223 | Low | Medium | High | Top | 258 | 208 | 64.0548
CLAYTON 2213 | 012022213 | BAY AREA | DIABLO | 3.8789 | 1024410 | 42.1698 | 0% | 0% | 100% | 0% | 0 | 0 | 2 | 100% | 0% | 0% | 14 | 10 | 0 | 0 | 40 | 0 | 0 | 1 | 1 | 53 | 21 | 1 | 0 | 2 | 4 | 0 | 0 | 2 | 1 | 0.39159 | 6.6722 | 6.1598 | 16.094 | Medium | Medium | High | Top | 259 | 301 | 41.0996
MORGAN HILL 2111 | 083242111 | CENTRAL COAST | SAN JOSE | 51.8726 | 1641880 | 42.2732 | 50.3% | 7.74% | 72.11% | 10.01% | 11 | 0 | 88 | 79.43% | 13.6% | 7.361% | 143 | 415 | 1 | 23 | 325 | 54 | 0 | 6 | 16 | 951 | 17.2821 | 89 | 63 | 7 | 323 | 0 | 0 | 86 | 0 | 0.20331 | 18.1806 | 4.2576 | 15.7369 | Low | High | Medium | Top | 260 | 170 | 77.4054
LAURELES 1112 | 182371112 | CENTRAL COAST | CENTRAL COAST | 29.5797 | 437175.6667 | 40.7037 | 11.39% | 0.561% | 42.14% | 30.11% | 8 | 3 | 43 | 23.27% | 67.16% | 6.657% | 38 | 169 | 0 | 20 | 340 | 30 | 0 | 7 | 10 | 676 | 15.813 | 83 | 73 | 12 | 265 | 4 | 0 | 43 | 1 | 0.71132 | 5.2747 | 4.1937 | 15.7349 | High | Medium | Medium | Top | 261 | 398 | 22.1207
BAYWOOD 1101 | 182801101 | CENTRAL COAST | LOS PADRES | 4.2971 | 403333.6667 | 41.1628 | 3.693% | 0% | 74.94% | 25.06% | 0 | 0 | 1 | 74.94% | 25.06% | 4.651% | 4 | 1 | 2 | 2 | 17 | 0 | 0 | 2 | 3 | 43 | 20.1667 | 6 | 1 | 0 | 15 | 0 | 0 | 1 | 0 | 0.24583 | 12.3111 | 5.1411 | 15.5592 | Low | High | Medium | Top | 262 | 212 | 63.292
APPLE HILL 2102 | 153662102 | NORTHERN | SIERRA | 340.2385 | 1278042.6667 | 42.6618 | 39.25% | 67.52% | 27.16% | 0.0005566% | 25 | 5 | 457 | 95.5% | 0.0005566% | 1.824% | 682 | 4238 | 270 | 0 | 1183 | 707 | 25 | 44 | 74 | 8167 | 42.6252 | 1351 | 653 | 40 | 2988 | 0 | 7 | 457 | 0 | 0.24544 | 18.073 | 3.4818 | 15.4449 | Low | High | Low | Top | 263 | 214 | 62.9265
JAMESON 1102 | 063801102 | NORTHERN | SACRAMENTO | 8.9423 | 874727 | 42.0833 | 31.17% | 0.5673% | 59.84% | 37.25% | 1 | 0 | 10 | 60.41% | 37.25% | 3.226% | 31 | 94 | 4 | 0 | 59 | 10 | 0 | 5 | 5 | 217 | 33.9159 | 29 | 50 | 8 | 113 | 0 | 0 | 10 | 0 | 0.43725 | 5.3375 | 6.5491 | 15.2846 | Medium | Medium | High | Top | 264 | 333 | 34.9562
VACAVILLE 1104 | 063601104 | NORTHERN | SACRAMENTO | 15.7436 | 991004.3333 | 43.3104 | 143.9% | 1.618% | 39.26% | 27.79% | 2 | 0 | 20 | 39.57% | 33.35% | 6.831% | 60 | 116 | 1 | 0 | 109 | 20 | 0 | 3 | 11 | 366 | 33.0805 | 33 | 21 | 2 | 102 | 0 | 5 | 20 | 0 | 0.35647 | 10.7723 | 3.9792 | 15.28 | Medium | Medium | Medium | Top | 265 | 295 | 42.8647
OCEANO 1104 | 182601104 | CENTRAL COAST | LOS PADRES | 93.0178 | 1243391 | 41.8747 | 18.26% | 2.748% | 57.26% | 30.7% | 15 | 0 | 170 | 56.75% | 38.65% | 7.593% | 210 | 193 | 0 | 329 | 915 | 166 | 3 | 32 | 45 | 2173 | 27.9753 | 351 | 139 | 19 | 934 | 0 | 2 | 169 | 0 | 0.58112 | 5.4309 | 4.7955 | 15.1348 | Medium | Medium | Medium | Top | 266 | 381 | 26.0441
BELLEVUE 2103 | 043182103 | NORTHERN | SONOMA | 32.2764 | 1226044.6667 | 44.2334 | 22.47% | 0.4413% | 81.51% | 6.989% | 2 | 2 | 54 | 80.16% | 8.974% | 7.491% | 157 | 397 | 0 | 15 | 67 | 70 | 7 | 10 | 12 | 574 | 36.5889 | 112 | 78 | 9 | 272 | 0 | 0 | 54 | 0 | 0.17484 | 23.3201 | 3.7084 | 15.1202 | Low | High | Low | Top | 267 | 154 | 86.4804
GLENN 1101 | 102601101 | NORTHERN | NORTH VALLEY | 2.3498 | 784294 | 37 | 7.384% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 1 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 5 | 11.5 | 2 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0.16613 | 47.6367 | 1.9073 | 15.0944 | Low | High | Low | Top | 268 | 145 | 90.8597
SONOMA 1107 | 042721107 | NORTHERN | SONOMA | 3.8318 | 610322.6667 | 44.7887 | 31.83% | 0% | 22.48% | 51.09% | 0 | 0 | 5 | 22.48% | 73.69% | 8.333% | 26 | 25 | 0 | 0 | 4 | 13 | 0 | 0 | 0 | 72 | 25.8571 | 3 | 1 | 0 | 9 | 0 | 0 | 5 | 0 | 0.40148 | 9.6896 | 3.8449 | 14.9574 | Medium | Medium | Medium | Top | 269 | 317 | 37.2559
ALTO 1120 | 042031120 | BAY AREA | NORTH BAY | 2.732 | 1013554.6667 | 43.4375 | 5.513% | 0% | 65.93% | 34.07% | 2 | 0 | 11 | 2.494% | 97.51% | 7.692% | 24 | 34 | 2 | 1 | 49 | 18 | 0 | 2 | 7 | 130 | 31.3889 | 8 | 16 | 0 | 37 | 0 | 0 | 11 | 1 | 0.65076 | 3.266 | 7.0337 | 14.9492 | Medium | Medium | High | Top | 270 | 391 | 22.9719
BUCKS CREEK 1102 | 102211102 | NORTHERN | NORTH VALLEY | 29.5609 | 24064 | 45.1628 | 29.42% | 95.12% | 2.32% | 1.332% | 0 | 0 | 20 | 50.06% | 49.94% | 25.17% | 238 | 195 | 1 | 0 | 227 | 74 | 0 | 6 | 19 | 743 | 30.913 | 11 | 11 | 7 | 65 | 0 | 0 | 19 | 0 | 0.42203 | 30.0939 | 1.1382 | 14.4563 | Medium | High | Low | Top | 271 | 335 | 34.254
SHADY GLEN 1102 | 152431102 | NORTHERN | SIERRA | 39.9524 | 232070.3333 | 43.3918 | 21.35% | 56.21% | 23.77% | 0.9866% | 1 | 2 | 73 | 85.12% | 7.619% | 7.763% | 157 | 469 | 6 | 0 | 166 | 82 | 0 | 9 | 17 | 979 | 33.3199 | 162 | 92 | 9 | 377 | 0 | 0 | 73 | 0 | 0.095149 | 42.5798 | 3.5604 | 14.4247 | Low | High | Low | Top | 272 | 72 | 151.6013
PAUL SWEET 2107 | 083252107 | CENTRAL COAST | CENTRAL COAST | 11.6036 | 2229446.6667 | 42.5758 | 6.567% | 0.3399% | 48.7% | 19.85% | 0 | 1 | 9 | 48.7% | 43.43% | 8.333% | 20 | 32 | 0 | 3 | 53 | 8 | 0 | 5 | 5 | 132 | 26.3478 | 15 | 4 | 1 | 52 | 0 | 0 | 9 | 1 | 0.65913 | 3.567 | 6.0734 | 14.279 | Medium | Medium | High | Top | 273 | 400 | 21.6634
ELECTRA 1102 | 162161102 | CENTRAL VALLEY | STOCKTON | 83.9986 | 567923.3333 | 43.1537 | 52.38% | 44.29% | 34.7% | 4.547% | 4 | 1 | 16 | 85.67% | 8.854% | 3.815% | 283 | 813 | 0 | 0 | 504 | 134 | 24 | 5 | 11 | 1835 | 41.9552 | 26 | 12 | 0 | 69 | 0 | 2 | 16 | 0 | 0.23094 | 13.9932 | 4.4144 | 14.2655 | Low | High | Medium | Top | 274 | 218 | 61.7712
RESERVATION ROAD 1102 | 182731102 | CENTRAL COAST | CENTRAL COAST | 17.671 | 873814.3333 | 40.3351 | 7.497% | 0.4033% | 64.91% | 33.98% | 2 | 0 | 26 | 58.49% | 40.8% | 9.043% | 17 | 105 | 0 | 1 | 140 | 25 | 0 | 4 | 5 | 376 | 15.2941 | 49 | 29 | 3 | 147 | 0 | 0 | 26 | 0 | 0.3525 | 14.7217 | 2.7418 | 14.2282 | Medium | High | Low | Top | 275 | 304 | 40.3641
BIG RIVER 1101 | 043081101 | NORTHERN | HUMBOLDT | 73.6464 | 656342 | 42.0514 | 21.84% | 2.061% | 18.35% | 70.42% | 71 | 0 | 148 | 17.45% | 79.11% | 3.96% | 194 | 693 | 0 | 11 | 435 | 71 | 53 | 17 | 27 | 1717 | 36.2511 | 228 | 94 | 17 | 705 | 0 | 1 | 148 | 1 | 0.74751 | 4.0922 | 4.6289 | 14.1595 | High | Medium | Medium | Mid | 276 | 426 | 18.9422
CLOVERDALE 1102 | 042821102 | NORTHERN | SONOMA | 83.3346 | 1190946 | 42.7159 | 42.23% | 4.676% | 76.45% | 13.66% | 10 | 0 | 69 | 75.96% | 20.78% | 9.05% | 147 | 365 | 0 | 6 | 223 | 164 | 6 | 20 | 26 | 884 | 34.094 | 131 | 60 | 9 | 330 | 0 | 2 | 69 | 0 | 0.3486 | 16.796 | 2.4032 | 14.071 | Medium | High | Low | Mid | 277 | 303 | 40.3646
PHILO 1101 | 042601101 | NORTHERN | HUMBOLDT | 78.3323 | 289113.3333 | 42.4822 | 35.62% | 7.394% | 80.96% | 7.054% | 20 | 0 | 57 | 66.43% | 28.97% | 5.924% | 142 | 457 | 0 | 5 | 317 | 79 | 0 | 8 | 13 | 1131 | 32.6424 | 130 | 26 | 8 | 366 | 0 | 3 | 57 | 0 | 0.28284 | 19.2782 | 2.544 | 13.8714 | Low | High | Low | Mid | 278 | 272 | 49.0438
OTTER 1102 | 182941102 | CENTRAL COAST | CENTRAL COAST | 54.0889 | 233793.3333 | 39.8005 | 123.4% | 8.731% | 59.84% | 22.32% | 11 | 5 | 91 | 6.951% | 86.82% | 6.049% | 36 | 192 | 0 | 9 | 272 | 25 | 2 | 30 | 44 | 777 | 27.0575 | 88 | 39 | 11 | 241 | 0 | 1 | 90 | 1 | 0.67709 | 6.6789 | 3.0669 | 13.8692 | High | Medium | Low | Mid | 279 | 409 | 20.4837
VOLTA 1102 | 102541102 | NORTHERN | NORTH VALLEY | 128.9875 | 581294.6667 | 39.3776 | 0% | 95.94% | 1.1% | 0.03167% | 13 | 2 | 187 | 97.04% | 0.03167% | 6.354% | 66 | 1996 | 69 | 0 | 514 | 202 | 41 | 34 | 66 | 3352 | 39.5782 | 438 | 168 | 8 | 1116 | 0 | 10 | 187 | 0 | 0.15947 | 30.8605 | 2.8037 | 13.7976 | Low | High | Low | Mid | 280 | 152 | 86.5226
SANTA ROSA A 1108 | 042151108 | NORTHERN | SONOMA | 0.13621 | 1285152.6667 | 42.5 | 21.79% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 228 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.13174 | 26.5534 | 3.9118 | 13.6844 | Low | High | Medium | Mid | 281 | 128 | 103.8719
UKIAH 1113 | 042771113 | NORTHERN | HUMBOLDT | 7.0118 | 342503.6667 | 44.0107 | 0% | 32.53% | 55.33% | 12.06% | 0 | 0 | 8 | 86.76% | 13.16% | 8.021% | 42 | 65 | 0 | 0 | 64 | 15 | 0 | 2 | 2 | 187 | 28.8605 | 33 | 18 | 4 | 88 | 0 | 0 | 8 | 0 | 0.22946 | 19.4946 | 2.9987 | 13.4136 | Low | High | Low | Mid | 282 | 225 | 58.4583
FREMONT 1104 | 014351104 | CENTRAL COAST | MISSION | 7.4071 | 841311 | 41.4706 | 8.998% | 0% | 3.264% | 19.86% | 0 | 0 | 2 | 3.264% | 96.74% | 5.882% | 1 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 0 | 3 | 1 | 1 | 5 | 0 | 0 | 2 | 0 | 0.21027 | 12.4551 | 5.1163 | 13.3992 | Low | High | Medium | Mid | 283 | 210 | 63.7244
CURTIS 1703 | 163351703 | CENTRAL VALLEY | YOSEMITE | 195.9575 | 1283179.6667 | 43.1818 | 0% | 53.14% | 37.62% | 0.8058% | 19 | 1 | 202 | 90.47% | 1.158% | 3.02% | 712 | 2036 | 5 | 0 | 858 | 408 | 15 | 44 | 82 | 4205 | 25.3661 | 570 | 384 | 63 | 1540 | 0 | 1 | 202 | 0 | 0.26317 | 10.7025 | 4.7409 | 13.3531 | Low | Medium | Medium | Mid | 284 | 265 | 50.7395
PLACER 1103 | 152461103 | NORTHERN | SIERRA | 14.4144 | 655934 | 43.4528 | 37.12% | 0.03919% | 44.06% | 24.96% | 1 | 0 | 21 | 40.47% | 28.89% | 5.212% | 48 | 220 | 1 | 0 | 41 | 11 | 0 | 2 | 4 | 307 | 33.2034 | 49 | 36 | 0 | 120 | 0 | 0 | 21 | 0 | 0.34787 | 7.7884 | 4.9258 | 13.3454 | Medium | Medium | Medium | Mid | 285 | 313 | 38.3637
FORT SEWARD 1122 | 192321122 | NORTHERN | HUMBOLDT | 17.6582 | 29145 | 38.3943 | 42.47% | 10.48% | 67.82% | 0% | 2 | 0 | 10 | 100% | 0% | 21.77% | 13 | 4 | 0 | 0 | 158 | 8 | 0 | 1 | 2 | 248 | 36.7347 | 14 | 8 | 5 | 50 | 0 | 0 | 10 | 0 | 0.30678 | 25.8623 | 1.6724 | 13.2692 | Low | High | Low | Mid | 286 | 293 | 43.2527
JAMESON 1105 | 063801105 | NORTHERN | SACRAMENTO | 22.537 | 1153872.3333 | 43.1313 | 13.93% | 0% | 79.81% | 13.73% | 2 | 3 | 15 | 73.95% | 19.58% | 3.023% | 72 | 264 | 5 | 0 | 44 | 28 | 0 | 1 | 1 | 397 | 29.7642 | 44 | 33 | 5 | 118 | 0 | 0 | 15 | 0 | 0.2476 | 11.0603 | 4.8249 | 13.2129 | Low | Medium | Medium | Mid | 287 | 248 | 53.3644
VACA DIXON 1105 | 063591105 | NORTHERN | SACRAMENTO | 29.0754 | 747516 | 42.2837 | 22.35% | 0.1419% | 90.86% | 0.8615% | 3 | 0 | 19 | 91% | 0.8615% | 2.2% | 56 | 230 | 3 | 0 | 71 | 17 | 1 | 6 | 7 | 500 | 35.7798 | 74 | 57 | 12 | 191 | 0 | 0 | 19 | 0 | 0.20292 | 18.0837 | 3.6007 | 13.2127 | Low | High | Low | Mid | 288 | 205 | 65.1137
HIGHLANDS 1103 | 043361103 | NORTHERN | HUMBOLDT | 114.7409 | 801003 | 44.9955 | 67.57% | 12.43% | 65.75% | 1.789% | 8 | 8 | 115 | 86.52% | 2.564% | 12.58% | 642 | 1074 | 22 | 9 | 354 | 453 | 0 | 15 | 29 | 2249 | 41.8491 | 376 | 182 | 56 | 856 | 0 | 5 | 115 | 0 | 0.11397 | 22.9843 | 5.0074 | 13.1168 | Low | High | Medium | Mid | 289 | 114 | 115.0924
GOLDTREE 1108 | 182581108 | CENTRAL COAST | LOS PADRES | 2.8394 | 635317 | 44.3333 | 127% | 1.891% | 25.37% | 6.778% | 1 | 0 | 3 | 27.26% | 6.778% | 4.444% | 11 | 0 | 0 | 4 | 18 | 16 | 0 | 1 | 1 | 45 | 58.1818 | 3 | 2 | 0 | 12 | 0 | 0 | 3 | 0 | 0.36451 | 7.1986 | 4.9397 | 12.9614 | Medium | Medium | Medium | Mid | 290 | 329 | 35.5587
REDBUD 1102 | 043191102 | NORTHERN | HUMBOLDT | 29.3262 | 893934.6667 | 44.7823 | 73.97% | 3.45% | 68.7% | 8.426% | 4 | 1 | 17 | 72.15% | 8.426% | 8.484% | 216 | 285 | 3 | 10 | 176 | 83 | 0 | 6 | 9 | 719 | 35.119 | 91 | 80 | 14 | 259 | 0 | 0 | 17 | 0 | 0.19155 | 12.7704 | 5.2758 | 12.9055 | Low | High | Medium | Mid | 291 | 196 | 67.3739
SWIFT 2110 | 083392110 | CENTRAL COAST | SAN JOSE | 83.7273 | 1271083.6667 | 40.976 | 49.02% | 11.88% | 65.4% | 22.33% | 3 | 0 | 73 | 73.06% | 26.93% | 6.649% | 67 | 548 | 0 | 8 | 275 | 81 | 0 | 3 | 12 | 1128 | 9.4839 | 78 | 49 | 5 | 250 | 0 | 1 | 72 | 0 | 0.22472 | 21.4706 | 2.6679 | 12.8723 | Low | High | Low | Mid | 292 | 232 | 57.2813
KING CITY 1103 | 182031103 | CENTRAL COAST | CENTRAL COAST | 17.6652 | 567182 | 40.3876 | 20.41% | 0.04509% | 99.95% | 0% | 0 | 0 | 21 | 99.95% | 0% | 6.95% | 12 | 105 | 0 | 2 | 76 | 19 | 0 | 3 | 3 | 259 | 14.3854 | 44 | 8 | 0 | 105 | 0 | 0 | 21 | 0 | 0.12954 | 25.8045 | 3.8377 | 12.8287 | Low | High | Medium | Mid | 293 | 133 | 99.0299
NEWBURG 1133 | 192151133 | NORTHERN | HUMBOLDT | 4.5902 | 104146 | 41.5217 | 18.35% | 0% | 39.51% | 25.94% | 0 | 0 | 3 | 39.51% | 48.81% | 63.04% | 7 | 0 | 0 | 0 | 36 | 4 | 0 | 1 | 1 | 46 | 12 | 6 | 0 | 0 | 16 | 0 | 0 | 3 | 1 | 0.62446 | 7.44 | 2.7149 | 12.6134 | Medium | Medium | Low | Mid | 294 | 413 | 20.1989
PASO ROBLES 1107 | 182611107 | CENTRAL COAST | LOS PADRES | 0.27858 | 948215.3333 | 38.3333 | 9.404% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 16.67% | 0 | 0 | 0 | 2 | 2 | 2 | 0 | 0 | 0 | 6 | 34.5 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.16605 | 24.9252 | 3.038 | 12.5737 | Low | High | Low | Mid | 295 | 175 | 75.7226
SANTA MARIA 1108 | 182671108 | CENTRAL COAST | LOS PADRES | 73.6335 | 1175161.3333 | 40.9195 | 35.85% | 2.43% | 93.3% | 0.2728% | 5 | 0 | 53 | 97.28% | 1.23% | 11.01% | 64 | 139 | 0 | 125 | 483 | 97 | 0 | 8 | 13 | 1054 | 27.4301 | 96 | 32 | 8 | 307 | 0 | 0 | 53 | 0 | 0.15542 | 30.8224 | 2.6213 | 12.5573 | Low | High | Low | Mid | 296 | 164 | 80.7943
SANTA YNEZ 1101 | 182721101 | CENTRAL COAST | LOS PADRES | 34.6124 | 1199568 | 41.3793 | 113.2% | 4.532% | 74.18% | 5.897% | 1 | 0 | 27 | 78.16% | 11.69% | 3.058% | 56 | 43 | 0 | 46 | 204 | 77 | 0 | 14 | 18 | 556 | 22.3465 | 18 | 14 | 4 | 109 | 0 | 1 | 27 | 0 | 0.14889 | 33.8357 | 2.4884 | 12.5359 | Low | High | Low | Mid | 297 | 158 | 84.196
UKIAH 1114 | 042771114 | NORTHERN | HUMBOLDT | 56.1108 | 603713.3333 | 42.2371 | 0% | 46.79% | 43.87% | 4.081% | 4 | 0 | 34 | 72.94% | 21.81% | 6.452% | 101 | 344 | 0 | 9 | 282 | 54 | 0 | 1 | 2 | 899 | 32.2492 | 130 | 42 | 9 | 306 | 0 | 0 | 34 | 0 | 0.23571 | 22.8555 | 2.3246 | 12.5234 | Low | High | Low | Mid | 298 | 249 | 53.1296
SOBRANTE 1102 | 014671102 | BAY AREA | DIABLO | 27.4867 | 665912.3333 | 44.9287 | 44.98% | 1.018% | 33.4% | 36.09% | 6 | 2 | 107 | 30.18% | 40.33% | 15.56% | 198 | 196 | 1 | 1 | 310 | 33 | 0 | 11 | 20 | 771 | 25.2005 | 84 | 205 | 53 | 411 | 0 | 0 | 107 | 1 | 0.57577 | 3.4775 | 6.2088 | 12.4314 | Medium | Medium | High | Mid | 299 | 401 | 21.5911
CASTRO VALLEY 1101 | 014091101 | CENTRAL COAST | MISSION | 3.4212 | 992296.6667 | 43.9216 | 25.37% | 0% | 45.71% | 10.04% | 8 | 4 | 0 | 36.26% | 19.49% | 3.922% | 4 | 9 | 0 | 0 | 40 | 1 | 0 | 1 | 2 | 51 | 5.6667 | 0 | 6 | 0 | 12 | 0 | 0 | 0 | 0 | 0.45379 | 4.2248 | 6.38 | 12.2315 | Medium | Medium | High | Mid | 300 | 377 | 26.9542
SALT SPRINGS 2101 | 163692101 | CENTRAL VALLEY | STOCKTON | 16.0684 | 59288.6667 | 46.2035 | 33.03% | 44.28% | 3.125% | 0% | 1 | 1 | 16 | 99.78% | 0.1926% | 3.462% | 268 | 290 | 0 | 0 | 109 | 22 | 0 | 4 | 14 | 520 | 28.3106 | 68 | 15 | 2 | 137 | 0 | 2 | 16 | 1 | 0.4829 | 15.8942 | 1.5862 | 12.1744 | Medium | High | Low | Mid | 301 | 383 | 25.2111
PARADISE 1104 | 102831104 | NORTHERN | NORTH VALLEY | 38.9544 | 1065050.6667 | 42.4077 | 14.54% | 3.104% | 56.28% | 32.08% | 21 | 5 | 82 | 56.48% | 35.62% | 4.57% | 172 | 664 | 27 | 0 | 323 | 80 | 76 | 10 | 28 | 1466 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 81 | 1 | 0.73559 | 2.41 | 6.7957 | 12.047 | High | Medium | High | Mid | 302 | 448 | 16.3773
MILPITAS 1108 | 082831108 | CENTRAL COAST | SAN JOSE | 0.28331 | 934813.6667 | 40 | 0% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 100% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 44 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.13615 | 26.5534 | 3.2974 | 11.9212 | Low | High | Low | Mid | 303 | 149 | 87.557
PASO ROBLES 1103 | 182611103 | CENTRAL COAST | LOS PADRES | 40.9142 | 920890.6667 | 44.0492 | 98.09% | 0.966% | 50.6% | 15.19% | 4 | 0 | 51 | 50.48% | 16.9% | 6.831% | 177 | 84 | 0 | 88 | 149 | 66 | 0 | 16 | 30 | 732 | 37.9921 | 147 | 33 | 2 | 260 | 0 | 0 | 51 | 0 | 0.28115 | 10.6388 | 3.9743 | 11.8876 | Low | Medium | Medium | Mid | 304 | 297 | 42.2821
TEMPLETON 2112 | 183052112 | CENTRAL COAST | LOS PADRES | 3.3396 | 1058186 | 42.4194 | 22.73% | 0% | 82.75% | 17.25% | 0 | 0 | 2 | 82.75% | 17.25% | 3.226% | 9 | 0 | 0 | 3 | 11 | 2 | 0 | 0 | 0 | 31 | 25.1667 | 3 | 4 | 0 | 13 | 0 | 0 | 2 | 0 | 0.22631 | 15.8309 | 3.3114 | 11.8637 | Low | High | Low | Mid | 305 | 254 | 52.4217
FRENCH GULCH 1102 | 103381102 | NORTHERN | NORTH VALLEY | 22.423 | 40453.6667 | 40.4175 | 76.3% | 62.99% | 30.28% | 0% | 1 | 0 | 7 | 99.77% | 0% | 4.277% | 78 | 184 | 7 | 0 | 216 | 32 | 0 | 4 | 7 | 491 | 30.8 | 13 | 3 | 0 | 30 | 0 | 0 | 6 | 0 | 0.26809 | 11.8873 | 3.7098 | 11.8226 | Low | Medium | Low | Mid | 306 | 289 | 44.0996
CURTIS 1701 | 163351701 | CENTRAL VALLEY | YOSEMITE | 14.8035 | 1423665 | 43.9225 | 0% | 0% | 42.83% | 18.88% | 1 | 1 | 10 | 42.78% | 22.21% | 6.731% | 109 | 165 | 0 | 0 | 118 | 44 | 1 | 4 | 13 | 416 | 29.8258 | 47 | 51 | 10 | 168 | 0 | 0 | 10 | 0 | 0.41835 | 4.74 | 5.9345 | 11.7678 | Medium | Medium | High | Mid | 307 | 369 | 28.1292
VACAVILLE 1108 | 063601108 | NORTHERN | SACRAMENTO | 30.2656 | 956164.3333 | 42.1267 | 27.73% | 17.16% | 78.83% | 1.73% | 3 | 0 | 19 | 88.9% | 9.616% | 4.673% | 62 | 198 | 4 | 1 | 126 | 20 | 13 | 3 | 5 | 535 | 25.5682 | 59 | 59 | 9 | 201 | 0 | 0 | 19 | 0 | 0.22624 | 14.4907 | 3.5756 | 11.7221 | Low | High | Low | Mid | 308 | 260 | 51.8124
SANTA YNEZ 1102 | 182721102 | CENTRAL COAST | LOS PADRES | 7.2642 | 780186.3333 | 43.866 | 97.1% | 0.2586% | 86.15% | 1.148% | 0 | 1 | 11 | 85.39% | 2.167% | 5.102% | 17 | 4 | 0 | 11 | 35 | 10 | 0 | 3 | 3 | 98 | 34.3478 | 5 | 6 | 1 | 24 | 0 | 0 | 11 | 0 | 0.19826 | 19.492 | 3.0213 | 11.6756 | Low | High | Low | Mid | 309 | 224 | 58.8911
JARVIS 1101 | 013501101 | CENTRAL COAST | MISSION | 0.92149 | 1462003 | 42.7778 | 3.281% | 0% | 93.6% | 0% | 0 | 0 | 1 | 37.36% | 56.23% | 0% | 1 | 6 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 9 | 1.5 | 2 | 1 | 0 | 4 | 0 | 0 | 1 | 0 | 0.18332 | 9.8889 | 6.3467 | 11.5054 | Low | Medium | High | Mid | 310 | 215 | 62.7618
MORGAN HILL 2105 | 083242105 | CENTRAL COAST | SAN JOSE | 53.819 | 1235253.3333 | 42.623 | 31.12% | 0.5059% | 67.87% | 17.27% | 7 | 0 | 123 | 64.03% | 22.35% | 7.328% | 168 | 591 | 1 | 10 | 269 | 54 | 0 | 23 | 35 | 1078 | 24.7897 | 131 | 103 | 19 | 426 | 0 | 0 | 122 | 0 | 0.31888 | 8.7824 | 4.0834 | 11.4356 | Low | Medium | Medium | Mid | 311 | 325 | 35.8618
LLAGAS 2106 | 083182106 | CENTRAL COAST | SAN JOSE | 2.0521 | 1901998 | 47.5 | 0.7117% | 0% | 100% | 0% | 0 | 0 | 2 | 100% | 0% | 83.33% | 12 | 2 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 18 | 0 | 1 | 3 | 0 | 5 | 0 | 0 | 2 | 0 | 0.29163 | 13.8356 | 2.8315 | 11.4249 | Low | High | Low | Mid | 312 | 308 | 39.1756
CENTERVILLE 1101 | 102021101 | NORTHERN | NORTH VALLEY | 36.3928 | 119772.6667 | 44.4126 | 21.95% | 6.43% | 65.78% | 18.73% | 13 | 1 | 0 | 65.79% | 25.15% | 6.933% | 159 | 312 | 1 | 0 | 100 | 67 | 2 | 0 | 0 | 750 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44045 | 4.0581 | 6.3214 | 11.2989 | Medium | Medium | High | Mid | 313 | 382 | 25.6533
MESA 1101 | 182821101 | CENTRAL COAST | LOS PADRES | 51.3797 | 610527 | 42.1948 | 32.34% | 0.08203% | 61.62% | 22.63% | 7 | 0 | 55 | 64.34% | 22.8% | 5.841% | 93 | 74 | 0 | 210 | 216 | 85 | 0 | 3 | 8 | 856 | 30.3484 | 95 | 41 | 4 | 311 | 0 | 0 | 55 | 0 | 0.27505 | 11.6851 | 3.4196 | 10.9904 | Low | Medium | Low | Mid | 314 | 305 | 39.9579
PIERCY 2110 | 083912110 | CENTRAL COAST | SAN JOSE | 21.9492 | 830413 | 40.7759 | 18.46% | 0% | 91.1% | 0% | 5 | 0 | 9 | 89% | 2.102% | 5.603% | 12 | 9 | 0 | 1 | 194 | 14 | 0 | 3 | 3 | 232 | 20.6364 | 11 | 3 | 3 | 44 | 0 | 0 | 8 | 0 | 0.23788 | 15.0285 | 3.0676 | 10.9666 | Low | High | Low | Mid | 315 | 284 | 46.1014
HARRIS 1108 | 192431108 | NORTHERN | HUMBOLDT | 3.1677 | 1162559 | 42.2794 | 22.21% | 0% | 19.91% | 79.84% | 0 | 0 | 7 | 20.16% | 79.84% | 26.47% | 5 | 6 | 0 | 1 | 49 | 3 | 0 | 1 | 2 | 68 | 23.3846 | 8 | 7 | 0 | 26 | 0 | 0 | 7 | 0 | 0.55493 | 2.6375 | 7.4912 | 10.9641 | Medium | Medium | High | Mid | 316 | 419 | 19.7578
IGNACIO 1101 | 042481101 | BAY AREA | NORTH BAY | 6.5242 | 913608.6667 | 45.6085 | 64.41% | 0% | 54.92% | 0% | 3 | 0 | 19 | 54.92% | 0% | 2.105% | 46 | 29 | 0 | 1 | 98 | 31 | 0 | 8 | 13 | 190 | 27.4898 | 6 | 21 | 14 | 53 | 0 | 0 | 19 | 0 | 0.40325 | 3.9009 | 6.9266 | 10.8959 | Medium | Medium | High | Mid | 317 | 375 | 27.0201
OCEANO 1103 | 182601103 | CENTRAL COAST | LOS PADRES | 1.2899 | 1402991.3333 | 42.3333 | 10.74% | 0% | 88.78% | 11.22% | 0 | 0 | 4 | 88.78% | 11.22% | 0% | 0 | 0 | 0 | 1 | 3 | 11 | 0 | 2 | 2 | 15 | 58.25 | 0 | 1 | 0 | 7 | 0 | 0 | 4 | 1 | 0.23181 | 9.651 | 4.8193 | 10.7817 | Low | Medium | Medium | Mid | 318 | 282 | 46.511
BASALT 1106 | 042461106 | BAY AREA | NORTH BAY | 6.2402 | 1007250 | 42.7586 | 30.81% | 7.111% | 80.61% | 0.7277% | 0 | 0 | 4 | 70.63% | 20.15% | 6.897% | 4 | 15 | 0 | 0 | 6 | 1 | 0 | 0 | 0 | 29 | 36 | 1 | 0 | 0 | 5 | 0 | 0 | 4 | 0 | 0.18266 | 17.6161 | 3.3495 | 10.7778 | Low | High | Low | Mid | 319 | 223 | 59.0053
UKIAH 1111 | 042771111 | NORTHERN | HUMBOLDT | 22.9697 | 692428 | 41.4815 | 64.46% | 18.2% | 81.8% | 0% | 0 | 0 | 8 | 99.86% | 0.1414% | 16% | 20 | 46 | 0 | 1 | 153 | 96 | 0 | 0 | 0 | 325 | 43.5 | 29 | 11 | 4 | 75 | 0 | 0 | 8 | 0 | 0.16351 | 28.8186 | 2.2781 | 10.7352 | Low | High | Low | Mid | 320 | 201 | 65.6529
PENRYN 1103 | 152561103 | NORTHERN | SIERRA | 68.3912 | 559268 | 42.2959 | 34.43% | 1.345% | 64.14% | 23.75% | 9 | 0 | 139 | 65.33% | 24.08% | 5.737% | 137 | 983 | 9 | 4 | 202 | 72 | 0 | 13 | 28 | 1499 | 33.0661 | 294 | 203 | 17 | 639 | 0 | 2 | 139 | 0 | 0.34554 | 6.5132 | 4.7384 | 10.664 | Medium | Medium | Medium | Mid | 321 | 358 | 30.8624
MORAGA 1102 | 013801102 | BAY AREA | DIABLO | 4.3902 | 485517.3333 | 44.8457 | 104.1% | 0% | 27.11% | 30.91% | 0 | 0 | 11 | 13.13% | 74.88% | 20.25% | 43 | 41 | 0 | 0 | 84 | 7 | 0 | 0 | 4 | 163 | 20.55 | 12 | 32 | 7 | 60 | 0 | 0 | 11 | 0 | 0.58353 | 2.6954 | 6.6962 | 10.5322 | Medium | Medium | High | Mid | 322 | 436 | 18.049
PANORAMA 1102 | 103461102 | NORTHERN | NORTH VALLEY | 34.2527 | 976523.6667 | 43.0259 | 52.24% | 24.89% | 45.15% | 15.66% | 1 | 0 | 12 | 66.55% | 33.45% | 7.246% | 126 | 246 | 10 | 0 | 114 | 71 | 0 | 5 | 7 | 621 | 35.5055 | 31 | 19 | 1 | 106 | 0 | 0 | 12 | 0 | 0.29312 | 9.8211 | 3.6499 | 10.5071 | Low | Medium | Low | Mid | 323 | 326 | 35.8457
CLOVERDALE 1101 | 042821101 | NORTHERN | SONOMA | 24.6061 | 702582.6667 | 43.4877 | 46.47% | 7.145% | 75.67% | 12.85% | 1 | 0 | 15 | 82.63% | 13.03% | 16.92% | 62 | 129 | 0 | 3 | 64 | 74 | 0 | 4 | 5 | 325 | 35.5678 | 54 | 17 | 5 | 122 | 0 | 0 | 15 | 0 | 0.19234 | 24.723 | 2.1882 | 10.4056 | Low | High | Low | Mid | 324 | 243 | 54.0995
HARRIS 1109 | 192431109 | NORTHERN | HUMBOLDT | 13.4593 | 1050995 | 41.8673 | 6.082% | 3.296% | 43.05% | 53.66% | 5 | 0 | 21 | 29.16% | 70.84% | 41.91% | 28 | 23 | 0 | 1 | 306 | 28 | 22 | 1 | 1 | 408 | 26.7095 | 54 | 27 | 9 | 183 | 0 | 0 | 20 | 1 | 0.76709 | 2.1669 | 6.2272 | 10.3507 | High | Low | High | Mid | 325 | 478 | 13.4935
SAN BENITO 2101 | 182742101 | CENTRAL COAST | CENTRAL COAST | 3.8338 | 1306436.3333 | 39.1538 | 71.09% | 0% | 61.18% | 38.82% | 0 | 0 | 3 | 61.18% | 38.82% | 0% | 1 | 21 | 0 | 1 | 39 | 0 | 0 | 0 | 0 | 65 | 35.087 | 12 | 2 | 0 | 25 | 0 | 0 | 3 | 0 | 0.27258 | 12.0304 | 3.1507 | 10.3316 | Low | Medium | Low | Mid | 326 | 314 | 37.9037
SANTA YNEZ 1104 | 182721104 | CENTRAL COAST | LOS PADRES | 46.9293 | 971931.6667 | 41.9828 | 80.97% | 1.287% | 78.43% | 17.04% | 1 | 0 | 74 | 78.06% | 19.19% | 5.665% | 48 | 55 | 0 | 78 | 211 | 163 | 0 | 7 | 9 | 812 | 30.0575 | 50 | 40 | 3 | 234 | 0 | 0 | 73 | 0 | 0.15411 | 25.263 | 2.6431 | 10.2901 | Low | High | Low | Mid | 327 | 197 | 66.7727
FRENCH GULCH 1101 | 103381101 | NORTHERN | NORTH VALLEY | 18.8732 | 81398 | 41.7304 | 57.91% | 30.8% | 64.98% | 0% | 3 | 0 | 7 | 100% | 0% | 7.219% | 49 | 205 | 14 | 1 | 97 | 57 | 0 | 4 | 11 | 471 | 37.3176 | 36 | 13 | 0 | 90 | 0 | 1 | 7 | 0 | 0.26417 | 10.7915 | 3.5769 | 10.1971 | Low | Medium | Low | Mid | 328 | 312 | 38.6003
JOLON 1102 | 182981102 | CENTRAL COAST | CENTRAL COAST | 69.9647 | 275593 | 42.1747 | 38.06% | 7.302% | 53.86% | 0.2338% | 1 | 0 | 45 | 61.35% | 0.2094% | 15.99% | 79 | 217 | 3 | 16 | 290 | 107 | 16 | 7 | 21 | 807 | 16.48 | 95 | 17 | 1 | 242 | 0 | 0 | 43 | 0 | 0.31963 | 14.6619 | 2.1624 | 10.134 | Low | High | Low | Mid | 329 | 349 | 31.7049
MORAGA 1103 | 013801103 | BAY AREA | DIABLO | 4.0164 | 626060.6667 | 43.8889 | 34.64% | 0% | 48.32% | 34.84% | 3 | 0 | 6 | 45.28% | 40.44% | 9.524% | 7 | 10 | 0 | 0 | 37 | 2 | 0 | 0 | 2 | 63 | 23.3103 | 7 | 12 | 7 | 31 | 0 | 0 | 6 | 1 | 0.70234 | 1.9231 | 7.4024 | 9.9984 | High | Low | High | Mid | 330 | 470 | 14.2358
WILDWOOD 1101 | 103611101 | NORTHERN | NORTH VALLEY | 32.6037 | 57735.6667 | 38.9234 | 116.9% | 81.49% | 18.51% | 0% | 0 | 0 | 11 | 99.99% | 0% | 1.59% | 12 | 257 | 7 | 0 | 254 | 18 | 0 | 9 | 19 | 629 | 43.3605 | 36 | 9 | 2 | 96 | 0 | 2 | 11 | 0 | 0.27865 | 24.5337 | 1.4501 | 9.9136 | Low | High | Low | Mid | 331 | 328 | 35.5774
JOLON 1103 | 182981103 | CENTRAL COAST | CENTRAL COAST | 15.4705 | 0 | 44.0179 | 220.2% | 7.902% | 35.28% | 0.9642% | 0 | 0 | 3 | 43.18% | 0.9642% | 23.21% | 11 | 16 | 0 | 0 | 20 | 10 | 0 | 2 | 4 | 56 | 16.1667 | 2 | 0 | 0 | 8 | 0 | 0 | 3 | 0 | 0.43911 | 14.1831 | 1.5867 | 9.882 | Medium | High | Low | Mid | 332 | 396 | 22.5043
MENDOCINO 1101 | 042951101 | NORTHERN | HUMBOLDT | 44.2375 | 553806.6667 | 42.8664 | 30.44% | 22.23% | 66.86% | 7.339% | 5 | 1 | 41 | 89.5% | 7.339% | 8.363% | 116 | 381 | 0 | 8 | 181 | 140 | 0 | 5 | 10 | 849 | 38.7038 | 147 | 41 | 8 | 374 | 0 | 0 | 41 | 0 | 0.1357 | 26.2844 | 2.7636 | 9.8572 | Low | High | Low | Mid | 333 | 179 | 72.6401
OAKLAND K 1104 | 012101104 | BAY AREA | EAST BAY | 15.128 | 643588 | 45.8829 | 19.27% | 0% | 47.07% | 23.19% | 11 | 2 | 43 | 26.48% | 51% | 31.59% | 172 | 118 | 1 | 13 | 243 | 61 | 46 | 27 | 48 | 573 | 16.262 | 41 | 92 | 32 | 198 | 0 | 0 | 43 | 0 | 0.65953 | 2.2398 | 6.6719 | 9.8558 | Medium | Low | High | Mid | 334 | 463 | 14.9438
GEYSERVILLE 1102 | 042891102 | NORTHERN | SONOMA | 59.7619 | 896499.3333 | 43.4738 | 43.68% | 6.622% | 73.37% | 14.71% | 2 | 2 | 39 | 76.77% | 18.23% | 6.831% | 159 | 308 | 0 | 2 | 141 | 134 | 0 | 15 | 16 | 688 | 29.5061 | 113 | 33 | 5 | 255 | 0 | 2 | 39 | 0 | 0.19288 | 20.7752 | 2.4522 | 9.826 | Low | High | Low | Mid | 335 | 263 | 50.9445
LOS OSITOS 2103 | 182082103 | CENTRAL COAST | CENTRAL COAST | 45.0959 | 716742.3333 | 39.2462 | 71.04% | 1.849% | 90.35% | 7.449% | 4 | 0 | 20 | 90.93% | 8.504% | 15.18% | 22 | 121 | 1 | 14 | 294 | 74 | 7 | 9 | 14 | 652 | 12.5521 | 67 | 14 | 6 | 208 | 0 | 0 | 20 | 0 | 0.19223 | 30.202 | 1.6624 | 9.6512 | Low | High | Low | Mid | 336 | 269 | 50.2066
SAN JOAQUIN #3 1101 | 252531101 | CENTRAL VALLEY | YOSEMITE | 24.668 | 0 | 39.9922 | 292.2% | 69.68% | 6.734% | 0.7802% | 2 | 1 | 22 | 82.86% | 15.1% | 21.01% | 46 | 50 | 0 | 0 | 297 | 71 | 4 | 19 | 25 | 652 | 32.3179 | 35 | 44 | 18 | 160 | 0 | 0 | 22 | 0 | 0.36647 | 8.251 | 3.1698 | 9.5846 | Medium | Medium | Low | Mid | 337 | 380 | 26.1541
LINCOLN 1104 | 153701104 | NORTHERN | SIERRA | 41.2963 | 492281.3333 | 41.7903 | 30.03% | 0.6821% | 66.55% | 31.26% | 1 | 0 | 46 | 64.23% | 34.26% | 5.136% | 59 | 400 | 2 | 0 | 64 | 24 | 5 | 8 | 8 | 623 | 30.6027 | 100 | 62 | 1 | 232 | 0 | 0 | 46 | 0 | 0.27935 | 11.8636 | 2.8558 | 9.4642 | Low | Medium | Low | Mid | 338 | 336 | 33.8796
PEABODY 2113 | 063642113 | NORTHERN | SACRAMENTO | 1.6686 | 1469742 | 41.0417 | 8.551% | 2.441% | 77.59% | 19.96% | 0 | 0 | 2 | 80.04% | 19.96% | 0% | 2 | 0 | 0 | 0 | 10 | 1 | 0 | 0 | 0 | 24 | 12.6667 | 3 | 0 | 1 | 7 | 0 | 0 | 2 | 0 | 0.16237 | 13.8657 | 4.1688 | 9.3853 | Low | High | Medium | Mid | 339 | 230 | 57.8035
WYANDOTTE 1103 | 102911103 | NORTHERN | NORTH VALLEY | 85.3328 | 1309730 | 41.7952 | 68.67% | 12.09% | 73.24% | 3.693% | 6 | 1 | 67 | 91.02% | 3.693% | 4.266% | 114 | 1321 | 29 | 0 | 252 | 128 | 0 | 23 | 38 | 2063 | 43.7528 | 326 | 93 | 5 | 740 | 0 | 4 | 67 | 0 | 0.04014 | 39.8104 | 5.8477 | 9.3445 | Low | High | High | Mid | 340 | 28 | 232.7993
SONOMA 1105 | 042721105 | NORTHERN | SONOMA | 16.7065 | 977537 | 43.7416 | 30.56% | 0% | 53.56% | 45.41% | 2 | 2 | 14 | 53.56% | 45.41% | 8.638% | 46 | 143 | 0 | 0 | 59 | 43 | 14 | 6 | 6 | 301 | 34.7438 | 52 | 22 | 3 | 123 | 0 | 1 | 14 | 0 | 0.58215 | 3.4113 | 4.6018 | 9.1387 | Medium | Medium | Medium | Mid | 341 | 456 | 15.6982
BELL 1107 | 152701107 | NORTHERN | SIERRA | 43.5817 | 1149493 | 42.7907 | 21.07% | 4.099% | 59.89% | 27.58% | 3 | 1 | 32 | 62.47% | 29.1% | 4.949% | 98 | 767 | 2 | 0 | 72 | 54 | 15 | 6 | 9 | 990 | 35.4893 | 196 | 137 | 4 | 433 | 0 | 5 | 32 | 0 | 0.28902 | 7.4759 | 4.2173 | 9.1125 | Low | Medium | Medium | Mid | 342 | 350 | 31.5285
PAUL SWEET 2106 | 083252106 | CENTRAL COAST | CENTRAL COAST | 39.4262 | 710856.6667 | 43.9967 | 17.4% | 0.2284% | 57.77% | 26.71% | 19 | 3 | 78 | 51.57% | 34.93% | 7.9% | 173 | 307 | 1 | 12 | 313 | 92 | 7 | 12 | 18 | 924 | 38.9403 | 131 | 72 | 14 | 404 | 8 | 0 | 76 | 1 | 0.79157 | 1.7883 | 6.3865 | 9.0408 | High | Low | High | Mid | 343 | 498 | 11.4213
GONZALES 1103 | 182131103 | CENTRAL COAST | CENTRAL COAST | 1.7723 | 932805 | 41.4286 | 3.265% | 0% | 39.15% | 60.85% | 0 | 0 | 3 | 39.15% | 60.85% | 23.81% | 1 | 7 | 0 | 0 | 4 | 7 | 0 | 1 | 1 | 21 | 30.8 | 5 | 0 | 0 | 11 | 0 | 0 | 3 | 0 | 0.4298 | 16.4522 | 1.2676 | 8.9637 | Medium | High | Low | Mid | 344 | 406 | 20.8553
BEAR VALLEY 2105 | 252192105 | CENTRAL VALLEY | YOSEMITE | 133.2806 | 221278.6667 | 40.9388 | 0% | 66.83% | 31.03% | 0.5335% | 4 | 1 | 101 | 97.5% | 2.486% | 26.73% | 107 | 260 | 3 | 10 | 1208 | 140 | 0 | 36 | 59 | 2507 | 17.8247 | 288 | 94 | 15 | 786 | 0 | 4 | 101 | 0 | 0.16978 | 16.9472 | 3.1109 | 8.9509 | Low | High | Low | Mid | 345 | 251 | 52.721
MONROE 2103 | 043302103 | NORTHERN | SONOMA | 1.5309 | 1768564.3333 | 46.1111 | 4.176% | 0% | 87.86% | 0.1856% | 0 | 0 | 1 | 87.86% | 0.1856% | 11.11% | 2 | 3 | 0 | 0 | 3 | 3 | 0 | 3 | 3 | 9 | 24.6667 | 1 | 0 | 0 | 5 | 0 | 0 | 1 | 1 | 0.27354 | 7.2428 | 4.3373 | 8.5931 | Low | Medium | Medium | Mid | 346 | 352 | 31.414
FULTON 1102 | 042561102 | NORTHERN | SONOMA | 32.1618 | 1112538.6667 | 44.0832 | 35.57% | 0.1938% | 71.61% | 16.81% | 0 | 0 | 44 | 72.74% | 16.88% | 9.808% | 116 | 240 | 0 | 6 | 77 | 99 | 0 | 14 | 14 | 469 | 34.1714 | 69 | 28 | 4 | 179 | 0 | 0 | 44 | 0 | 0.25329 | 9.2752 | 3.6516 | 8.5787 | Low | Medium | Low | Mid | 347 | 337 | 33.869
NEWBURG 1131 | 192151131 | NORTHERN | HUMBOLDT | 8.326 | 589860.3333 | 43.0065 | 17.28% | 0% | 35.74% | 62.59% | 2 | 0 | 5 | 34.38% | 63.96% | 43.14% | 19 | 28 | 0 | 0 | 85 | 17 | 0 | 0 | 0 | 153 | 25.9474 | 14 | 7 | 4 | 58 | 0 | 0 | 5 | 1 | 0.63324 | 4.1728 | 3.2415 | 8.5651 | Medium | Medium | Low | Mid | 348 | 477 | 13.5259
MIDDLETOWN 1102 | 043141102 | NORTHERN | HUMBOLDT | 42.3893 | 840964 | 46.2448 | 73.79% | 20.19% | 67.42% | 0.2889% | 18 | 2 | 19 | 91.88% | 0.2889% | 13.08% | 424 | 602 | 0 | 2 | 97 | 131 | 17 | 15 | 23 | 963 | 52.5093 | 140 | 155 | 64 | 439 | 0 | 0 | 19 | 0 | 0.27312 | 5.8176 | 5.3484 | 8.4981 | Low | Medium | Medium | Mid | 349 | 357 | 31.1148
HATTON 1102 | 182291102 | CENTRAL COAST | CENTRAL COAST | 11.2788 | 817731.6667 | 40.4734 | 31.82% | 6.678% | 31.11% | 31.08% | 12 | 1 | 30 | 15.54% | 72.72% | 15.63% | 11 | 101 | 0 | 2 | 136 | 23 | 3 | 23 | 27 | 339 | 15.2936 | 43 | 28 | 6 | 116 | 0 | 0 | 29 | 1 | 0.70058 | 2.3868 | 5.0435 | 8.4333 | High | Low | Medium | Mid | 350 | 492 | 12.0376
COTATI 1102 | 042271102 | NORTHERN | SONOMA | 17.1258 | 1012833.6667 | 45.663 | 37.38% | 7.087% | 36.6% | 28.56% | 5 | 0 | 22 | 35.04% | 39.34% | 3.315% | 109 | 176 | 0 | 2 | 107 | 27 | 4 | 8 | 11 | 362 | 25.929 | 52 | 32 | 4 | 158 | 0 | 0 | 22 | 0 | 0.50342 | 4.551 | 3.6744 | 8.4182 | Medium | Medium | Low | Mid | 351 | 445 | 16.722
FORT BRAGG A 1101 | 042761101 | NORTHERN | HUMBOLDT | 71.2927 | 664677.3333 | 41.3017 | 37.32% | 1.35% | 21.27% | 71.76% | 44 | 8 | 128 | 11.84% | 87.73% | 4.19% | 147 | 514 | 0 | 17 | 468 | 58 | 49 | 19 | 26 | 1456 | 37.1306 | 177 | 75 | 20 | 500 | 0 | 4 | 127 | 0 | 0.69501 | 3.574 | 3.3624 | 8.3519 | High | Medium | Low | Mid | 352 | 493 | 12.0171
GABILAN 1101 | 182331101 | CENTRAL COAST | CENTRAL COAST | 7.2565 | 1406118.6667 | 39.9038 | 10.48% | 0% | 59.09% | 36.3% | 1 | 0 | 2 | 57.88% | 42.12% | 5.769% | 1 | 14 | 0 | 0 | 22 | 1 | 0 | 0 | 0 | 52 | 5.6316 | 5 | 3 | 0 | 22 | 0 | 0 | 2 | 0 | 0.28754 | 9.9013 | 2.9325 | 8.3491 | Low | Medium | Low | Mid | 353 | 366 | 29.0357
VOLTA 1101 | 102541101 | NORTHERN | NORTH VALLEY | 153.1533 | 261975 | 40.4718 | 0% | 46.76% | 42.24% | 1.944% | 41 | 5 | 114 | 89.01% | 4.004% | 12% | 220 | 1320 | 54 | 1 | 1004 | 244 | 32 | 34 | 59 | 3375 | 42.5214 | 244 | 96 | 23 | 635 | 0 | 9 | 113 | 0 | 0.28746 | 11.8539 | 2.3935 | 8.1561 | Low | Medium | Low | Mid | 354 | 368 | 28.3727
RINCON 1102 | 043321102 | NORTHERN | SONOMA | 3.7815 | 795269.6667 | 45.1587 | 51.96% | 0% | 31.56% | 28.58% | 2 | 0 | 10 | 30.29% | 29.85% | 0% | 18 | 20 | 0 | 3 | 24 | 8 | 0 | 2 | 2 | 63 | 40.3478 | 19 | 10 | 4 | 47 | 0 | 0 | 10 | 1 | 0.51752 | 3.9597 | 3.9716 | 8.1388 | Medium | Medium | Medium | Mid | 355 | 455 | 15.7264
CARLOTTA 1121 | 192291121 | NORTHERN | HUMBOLDT | 23.6581 | 315621 | 44.1397 | 25.44% | 20.75% | 46.03% | 11.31% | 8 | 0 | 17 | 68.48% | 25.21% | 33.42% | 95 | 19 | 0 | 0 | 239 | 24 | 8 | 2 | 5 | 404 | 28.6829 | 43 | 20 | 12 | 130 | 0 | 2 | 17 | 0 | 0.55115 | 5.1578 | 2.8531 | 8.1105 | Medium | Medium | Low | Mid | 356 | 466 | 14.7154
SHADY GLEN 1101 | 152431101 | NORTHERN | SIERRA | 42.3648 | 695856.6667 | 42.1893 | 17.57% | 59.28% | 27.98% | 3.447% | 5 | 1 | 66 | 85.01% | 11.4% | 8.072% | 86 | 620 | 2 | 0 | 133 | 89 | 15 | 16 | 22 | 1053 | 36.5293 | 194 | 103 | 15 | 471 | 0 | 0 | 66 | 0 | 0.17219 | 11.439 | 4.1118 | 8.0989 | Low | Medium | Medium | Mid | 357 | 280 | 47.0346
STAFFORD 1101 | 043201101 | BAY AREA | NORTH BAY | 8.5838 | 1056111 | 43.9262 | 27.29% | 0% | 66.95% | 10.79% | 1 | 0 | 13 | 66.95% | 10.79% | 4.878% | 38 | 49 | 3 | 0 | 46 | 23 | 0 | 5 | 9 | 123 | 28.2273 | 15 | 16 | 5 | 45 | 0 | 0 | 13 | 1 | 0.41419 | 3.3148 | 5.8841 | 8.0787 | Medium | Medium | High | Mid | 358 | 421 | 19.5047
TAMARACK 1101 | 152291101 | NORTHERN | SIERRA | 17.6532 | 57018.3333 | 43.6402 | 11.63% | 71.08% | 8.336% | 2.557% | 13 | 1 | 26 | 69.68% | 12.29% | 23.19% | 87 | 108 | 2 | 0 | 129 | 22 | 14 | 7 | 11 | 483 | 36.1429 | 52 | 30 | 6 | 142 | 0 | 0 | 26 | 1 | 0.73405 | 5.1641 | 2.1191 | 8.0327 | High | Medium | Low | Mid | 359 | 503 | 10.943
TEMPLETON 2110 | 183052110 | CENTRAL COAST | LOS PADRES | 136.5197 | 1004387.3333 | 41.6003 | 57.59% | 13.55% | 78.42% | 4.468% | 13 | 2 | 112 | 81.92% | 18.04% | 8.597% | 217 | 141 | 0 | 350 | 748 | 191 | 0 | 33 | 44 | 1896 | 38.1793 | 224 | 118 | 6 | 622 | 0 | 0 | 111 | 0 | 0.18446 | 12.0159 | 3.6039 | 7.988 | Low | Medium | Low | Mid | 360 | 292 | 43.3044
RADUM 1105 | 013151105 | CENTRAL COAST | MISSION | 2.3633 | 898321.6667 | 46.828 | 13.05% | 0% | 71.01% | 13.68% | 2 | 3 | 7 | 67.75% | 16.94% | 21.51% | 37 | 29 | 0 | 0 | 43 | 3 | 0 | 6 | 10 | 93 | 10.5116 | 9 | 18 | 6 | 46 | 0 | 0 | 7 | 1 | 0.5345 | 2.7701 | 5.3598 | 7.9357 | Medium | Medium | Medium | Mid | 361 | 464 | 14.8471
MOUNTAIN QUARRIES 2101 | 152282101 | NORTHERN | SIERRA | 224.836 | 1285830 | 43.5164 | 33.38% | 13.47% | 75.99% | 1.38% | 16 | 3 | 322 | 85.21% | 9.612% | 7.27% | 564 | 3178 | 32 | 3 | 342 | 415 | 14 | 37 | 76 | 4952 | 46.5909 | 1051 | 564 | 31 | 2166 | 0 | 6 | 322 | 0 | 0.16423 | 10.9288 | 4.4155 | 7.9252 | Low | Medium | Medium | Mid | 362 | 273 | 48.2566
SHINGLE SPRINGS 2108 | 153652108 | NORTHERN | SIERRA | 15.2009 | 1326514.3333 | 44.2614 | 78.45% | 7.544% | 60.05% | 0% | 1 | 0 | 33 | 67.6% | 0% | 1.989% | 46 | 207 | 0 | 0 | 78 | 27 | 8 | 10 | 20 | 352 | 52.0895 | 76 | 95 | 10 | 195 | 0 | 0 | 33 | 0 | 0.24584 | 5.9973 | 5.3365 | 7.8681 | Low | Medium | Medium | Mid | 363 | 345 | 32.0045
TEJON 1102 | 252931102 | CENTRAL VALLEY | KERN | 34.9658 | 1275225.3333 | 42.4099 | 62.49% | 81.27% | 8.228% | 1.952% | 0 | 0 | 41 | 69.41% | 30.2% | 26.76% | 44 | 41 | 0 | 38 | 314 | 55 | 0 | 2 | 10 | 751 | 9.85 | 83 | 57 | 12 | 241 | 0 | 0 | 41 | 0 | 0.27617 | 6.3453 | 4.3844 | 7.6832 | Low | Medium | Medium | Mid | 364 | 372 | 27.8208
TEMPLETON 2113 | 183052113 | CENTRAL COAST | LOS PADRES | 199.0069 | 2234642 | 40.4477 | 73.34% | 5.894% | 77.49% | 11.62% | 7 | 1 | 131 | 76.11% | 20.08% | 9.025% | 175 | 184 | 3 | 593 | 1360 | 292 | 0 | 30 | 42 | 3191 | 37.3539 | 401 | 140 | 16 | 1120 | 0 | 1 | 131 | 0 | 0.13377 | 21.458 | 2.6495 | 7.6055 | Low | High | Low | Mid | 365 | 234 | 56.8533
SAN BENITO 2104 | 182742104 | CENTRAL COAST | CENTRAL COAST | 30.1443 | 253743.6667 | 43.8982 | 22.3% | 0.2078% | 46.34% | 21.02% | 14 | 1 | 53 | 46.36% | 46.11% | 4.863% | 130 | 337 | 0 | 4 | 161 | 56 | 0 | 5 | 12 | 658 | 46.9528 | 90 | 26 | 2 | 265 | 2 | 0 | 53 | 0 | 0.61226 | 2.9223 | 4.2369 | 7.5805 | Medium | Medium | Medium | Mid | 366 | 490 | 12.3813
ORINDA 0401 | 012350401 | BAY AREA | DIABLO | 9.525 | 214002.6667 | 44.5238 | 0% | 8.848% | 49.67% | 30.24% | 11 | 2 | 27 | 7.449% | 90.73% | 27.09% | 82 | 106 | 1 | 1 | 102 | 27 | 11 | 8 | 16 | 358 | 46.0258 | 24 | 97 | 13 | 157 | 0 | 0 | 27 | 1 | 0.79195 | 1.3734 | 6.8908 | 7.4951 | High | Low | High | Mid | 367 | 519 | 9.4641
PALMER 1101 | 183031101 | CENTRAL COAST | LOS PADRES | 39.5446 | 932357 | 45.1737 | 131.3% | 5.813% | 57.29% | 12.2% | 1 | 0 | 44 | 46.65% | 30.11% | 1.625% | 115 | 56 | 1 | 93 | 144 | 110 | 5 | 11 | 20 | 554 | 26.48 | 30 | 11 | 1 | 113 | 0 | 0 | 44 | 0 | 0.19953 | 12.9258 | 2.8668 | 7.3937 | Low | High | Low | Mid | 368 | 318 | 37.0557
CURTIS 1702 | 163351702 | CENTRAL VALLEY | YOSEMITE | 112.3028 | 1209566.6667 | 42.8858 | 0% | 24.78% | 60.65% | 5.201% | 8 | 1 | 138 | 87.58% | 8.982% | 3.342% | 442 | 1710 | 0 | 0 | 568 | 239 | 5 | 30 | 62 | 3022 | 24.3476 | 598 | 377 | 42 | 1424 | 0 | 0 | 136 | 0 | 0.15508 | 7.1779 | 6.5779 | 7.3224 | Low | Medium | High | Mid | 369 | 279 | 47.2154
EDES 1112 | 013681112 | BAY AREA | EAST BAY | 16.0717 | 698923.6667 | 45.2051 | 22.63% | 0% | 45.38% | 10.27% | 4 | 2 | 40 | 19.69% | 42.92% | 30.09% | 120 | 80 | 0 | 1 | 356 | 20 | 19 | 25 | 42 | 585 | 22.5211 | 24 | 58 | 29 | 148 | 0 | 0 | 40 | 1 | 0.68701 | 1.9154 | 5.5547 | 7.3095 | High | Low | High | Mid | 370 | 506 | 10.6396
ZACA 1101 | 182681101 | CENTRAL COAST | LOS PADRES | 20.191 | 337919.3333 | 44.3945 | 56.26% | 29.52% | 40.55% | 20% | 1 | 0 | 18 | 41.83% | 48.93% | 9.966% | 62 | 17 | 1 | 56 | 100 | 47 | 0 | 6 | 8 | 291 | 31.8769 | 11 | 8 | 3 | 69 | 0 | 0 | 18 | 0 | 0.36334 | 9.9161 | 2.025 | 7.2959 | Medium | Medium | Low | Mid | 371 | 415 | 20.0798
CORNING 1102 | 103331102 | NORTHERN | NORTH VALLEY | 81.2965 | 1289581.3333 | 39.9017 | 95.68% | 11.15% | 84.86% | 0.07427% | 4 | 0 | 36 | 90.2% | 6.193% | 3.328% | 86 | 786 | 12 | 0 | 148 | 77 | 0 | 10 | 18 | 1322 | 40.104 | 89 | 32 | 3 | 208 | 0 | 2 | 36 | 0 | 0.11127 | 25.5568 | 2.5613 | 7.2837 | Low | High | Low | Mid | 372 | 202 | 65.4598
SANTA ROSA A 1104 | 042151104 | NORTHERN | SONOMA | 44.9934 | 1003317.3333 | 44.2131 | 27.46% | 0.08983% | 67.49% | 14.7% | 3 | 2 | 120 | 69.48% | 14.7% | 6.934% | 264 | 505 | 0 | 9 | 283 | 151 | 2 | 31 | 43 | 1024 | 35.1076 | 213 | 127 | 23 | 511 | 0 | 3 | 120 | 1 | 0.28997 | 5.9898 | 4.1716 | 7.2455 | Low | Medium | Medium | Mid | 373 | 385 | 24.9871
IGNACIO 1104 | 042481104 | BAY AREA | NORTH BAY | 7.7928 | 917913.6667 | 44.0407 | 32.42% | 12.03% | 36.09% | 15.62% | 4 | 2 | 12 | 33.32% | 46.51% | 10.57% | 65 | 96 | 1 | 2 | 69 | 54 | 0 | 3 | 4 | 246 | 26.4321 | 28 | 19 | 1 | 82 | 0 | 0 | 12 | 1 | 0.69028 | 1.5732 | 6.6586 | 7.231 | High | Low | High | Mid | 374 | 508 | 10.4755
DEL MONTE 2104 | 182222104 | CENTRAL COAST | CENTRAL COAST | 61.8446 | 2135572 | 43.948 | 25.97% | 0.06563% | 58.88% | 15.23% | 4 | 2 | 123 | 38.09% | 39.91% | 9.39% | 264 | 503 | 0 | 16 | 380 | 85 | 8 | 66 | 84 | 1214 | 17.1443 | 148 | 77 | 6 | 429 | 0 | 0 | 123 | 0 | 0.39261 | 4.4291 | 4.1273 | 7.1771 | Medium | Medium | Medium | Mid | 375 | 433 | 18.2804
VASCO 1102 | 013751102 | CENTRAL COAST | MISSION | 43.1032 | 566741 | 42.0938 | 99.26% | 0.3618% | 97.47% | 2.164% | 0 | 0 | 41 | 86.37% | 13.63% | 11.73% | 49 | 193 | 0 | 10 | 263 | 40 | 0 | 7 | 8 | 597 | 6.6599 | 51 | 46 | 8 | 164 | 0 | 1 | 40 | 0 | 0.13324 | 20.2954 | 2.6442 | 7.1504 | Low | High | Low | Mid | 376 | 246 | 53.6659
EMERALD LAKE 0402 | 024080402 | CENTRAL COAST | PENINSULA | 8.0268 | 214527.6667 | 45.6734 | 70.51% | 1.854% | 14.23% | 40.68% | 8 | 1 | 17 | 14.77% | 80.23% | 10.77% | 63 | 150 | 1 | 1 | 96 | 18 | 8 | 2 | 9 | 297 | 45.4621 | 22 | 71 | 18 | 151 | 0 | 0 | 17 | 0 | 0.6989 | 1 | 10.2221 | 7.1442 | High | Low | High | Mid | 377 | 509 | 10.2221
SAN JUSTO 1101 | 183181101 | CENTRAL COAST | CENTRAL COAST | 39.4357 | 320395.3333 | 40.7899 | 54.3% | 14.62% | 66.44% | 18.94% | 2 | 0 | 34 | 68.3% | 31.7% | 8.589% | 37 | 192 | 0 | 14 | 245 | 51 | 0 | 7 | 8 | 652 | 15.0843 | 95 | 34 | 2 | 269 | 0 | 0 | 34 | 0 | 0.22829 | 11.5172 | 2.7089 | 7.1225 | Low | Medium | Low | Mid | 378 | 356 | 31.1992
SHINGLE SPRINGS 2105 | 153652105 | NORTHERN | SIERRA | 32.0602 | 1266119 | 43.0414 | 43.26% | 0.0146% | 83.23% | 0.1687% | 4 | 4 | 60 | 83.25% | 0.1687% | 0.7084% | 107 | 584 | 3 | 0 | 116 | 47 | 12 | 6 | 16 | 847 | 56.5618 | 230 | 149 | 15 | 435 | 0 | 0 | 60 | 0 | 0.12831 | 10.4629 | 5.2798 | 7.0883 | Low | Medium | Medium | Mid | 379 | 237 | 55.2424
PAUL SWEET 2105 | 083252105 | CENTRAL COAST | CENTRAL COAST | 9.836 | 1033592.6667 | 46.3946 | 61.57% | 0.5614% | 33.7% | 17.58% | 10 | 0 | 13 | 31.27% | 25.61% | 6.803% | 53 | 68 | 0 | 0 | 41 | 4 | 10 | 6 | 6 | 147 | 46.9787 | 16 | 8 | 0 | 49 | 0 | 0 | 13 | 1 | 0.74116 | 1.5428 | 6.1566 | 7.0398 | High | Low | High | Mid | 380 | 518 | 9.4984
CORONA 1103 | 043491103 | NORTHERN | SONOMA | 1.2055 | 996177.6667 | 40.2778 | 6.019% | 0% | 76.96% | 23.04% | 0 | 0 | 0 | 76.96% | 23.04% | 0% | 1 | 5 | 0 | 0 | 10 | 2 | 0 | 0 | 0 | 18 | 34.5 | 0 | 2 | 0 | 6 | 0 | 0 | 0 | 0 | 0.1333 | 13.3391 | 3.9397 | 7.0052 | Low | High | Medium | Mid | 381 | 252 | 52.5523
ATASCADERO 1101 | 182541101 | CENTRAL COAST | LOS PADRES | 48.5498 | 1006188.3333 | 41.4182 | 24.47% | 0% | 78.63% | 16.95% | 10 | 5 | 40 | 78.81% | 19.87% | 8.61% | 90 | 59 | 0 | 393 | 391 | 110 | 10 | 9 | 13 | 1173 | 52.4545 | 280 | 145 | 15 | 577 | 0 | 0 | 40 | 0 | 0.36204 | 3.9898 | 4.7787 | 6.9028 | Medium | Medium | Medium | Mid | 382 | 424 | 19.0664
LOS COCHES 1101 | 182151101 | CENTRAL COAST | CENTRAL COAST | 2.6219 | 393335.3333 | 39.8649 | 6.6% | 0% | 100% | 0% | 0 | 0 | 0 | 12.86% | 87.14% | 5.405% | 1 | 14 | 0 | 0 | 12 | 3 | 0 | 0 | 0 | 37 | 10.8 | 4 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0.15319 | 29.4995 | 1.5275 | 6.9025 | Low | High | Low | Mid | 383 | 288 | 45.0597
SAN RAMON 2102 | 014232102 | CENTRAL COAST | MISSION | 1.7607 | 1716244.3333 | 52.1053 | 451.9% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 10.53% | 17 | 10 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25132 | 4.0028 | 6.8359 | 6.8768 | Low | Medium | High | Mid | 384 | 373 | 27.3627
TASSAJARA 2106 | 014662106 | BAY AREA | DIABLO | 0.35035 | 830488.3333 | 43.75 | 3.084% | 0% | 11.98% | 88.02% | 0 | 0 | 1 | 11.98% | 88.02% | 0% | 2 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 38.6667 | 2 | 1 | 0 | 3 | 0 | 0 | 1 | 0 | 0.14591 | 6.1501 | 7.5502 | 6.7755 | Low | Medium | High | Mid | 385 | 283 | 46.4347
SAN LUIS OBISPO 1108 | 182631108 | CENTRAL COAST | LOS PADRES | 2.4048 | 1467656 | 43.3696 | 112.3% | 0% | 23.43% | 14.17% | 0 | 0 | 2 | 23.43% | 14.17% | 0% | 3 | 2 | 0 | 3 | 10 | 1 | 0 | 1 | 1 | 47 | 28.8889 | 2 | 3 | 1 | 11 | 0 | 0 | 2 | 0 | 0.31519 | 3.9129 | 5.4833 | 6.7626 | Low | Medium | High | Mid | 386 | 402 | 21.4555
MORRO BAY 1101 | 183011101 | CENTRAL COAST | LOS PADRES | 7.6115 | 1054437 | 42.193 | 16.43% | 12.48% | 15.44% | 64.32% | 0 | 0 | 5 | 17.26% | 74.97% | 0% | 25 | 1 | 11 | 25 | 36 | 6 | 1 | 3 | 3 | 115 | 36.8462 | 6 | 6 | 0 | 27 | 0 | 0 | 5 | 0 | 0.41487 | 3.0723 | 5.2632 | 6.7086 | Medium | Medium | Medium | Mid | 387 | 450 | 16.1703
RACETRACK 1703 | 163761703 | CENTRAL VALLEY | YOSEMITE | 57.8457 | 1049270.3333 | 42.5404 | 112.5% | 6.292% | 65.59% | 17.44% | 8 | 0 | 126 | 50.66% | 39.55% | 5.133% | 291 | 706 | 1 | 0 | 434 | 169 | 10 | 25 | 46 | 1617 | 25.2642 | 201 | 181 | 30 | 645 | 0 | 0 | 126 | 0 | 0.41672 | 2.981 | 5.3557 | 6.653 | Medium | Medium | Medium | Mid | 388 | 452 | 15.9651
SHINGLE SPRINGS 2109 | 153652109 | NORTHERN | SIERRA | 214.6135 | 1317493.6667 | 43.0853 | 33.47% | 1.045% | 89.27% | 1.473% | 23 | 2 | 292 | 87.98% | 4.051% | 1.234% | 633 | 3363 | 51 | 0 | 597 | 353 | 22 | 31 | 54 | 5269 | 47.94 | 1002 | 638 | 70 | 2194 | 0 | 5 | 292 | 0 | 0.20119 | 7.6038 | 4.3282 | 6.6214 | Low | Medium | Medium | Mid | 389 | 339 | 32.911
SAN CARLOS 1103 | 024181103 | CENTRAL COAST | PENINSULA | 4.0359 | 1078094 | 43.125 | 24.85% | 0% | 31.87% | 31.47% | 1 | 1 | 11 | 28.23% | 38.59% | 13.82% | 35 | 46 | 0 | 0 | 76 | 18 | 0 | 1 | 4 | 152 | 14.2429 | 24 | 13 | 8 | 71 | 0 | 0 | 11 | 1 | 0.73959 | 1 | 8.9438 | 6.6147 | High | Low | High | Mid | 390 | 526 | 8.9438
JAMESON 1103 | 063801103 | NORTHERN | SACRAMENTO | 3.8489 | 503860 | 44.1489 | 8.384% | 0% | 91.62% | 8.383% | 0 | 0 | 0 | 91.62% | 8.383% | 2.083% | 5 | 37 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 48 | 26.2353 | 7 | 4 | 0 | 18 | 0 | 0 | 0 | 0 | 0.15795 | 9.962 | 4.1924 | 6.597 | Low | Medium | Medium | Mid | 391 | 298 | 41.7652
WALDO 0402 | 013350402 | BAY AREA | EAST BAY | 3.133 | 123975.6667 | 43.156 | 40.99% | 41.27% | 45.39% | 5.478% | 4 | 2 | 4 | 15.83% | 79.77% | 41.13% | 11 | 12 | 0 | 0 | 63 | 4 | 0 | 4 | 4 | 141 | 45.2857 | 8 | 26 | 5 | 43 | 0 | 0 | 4 | 1 | 0.71881 | 1 | 8.8774 | 6.3812 | High | Low | High | Mid | 392 | 530 | 8.8774
PACIFICA 1102 | 022811102 | CENTRAL COAST | PENINSULA | 6.4541 | 946069 | 43.4375 | 9.475% | 10.53% | 13.09% | 57.4% | 0 | 0 | 3 | 0% | 98.05% | 3.125% | 25 | 19 | 0 | 0 | 50 | 2 | 0 | 1 | 1 | 96 | 14.4211 | 6 | 4 | 5 | 22 | 1 | 0 | 3 | 0 | 0.48867 | 2.0338 | 6.3815 | 6.3422 | Medium | Low | High | Mid | 393 | 485 | 12.9785
SAN RAFAEL 1104 | 042011104 | BAY AREA | NORTH BAY | 12.8595 | 894448.6667 | 43.7289 | 9.62% | 1.035% | 17.71% | 75.04% | 13 | 2 | 31 | 13.96% | 80.31% | 4.762% | 88 | 121 | 4 | 1 | 164 | 109 | 0 | 9 | 17 | 462 | 35.7865 | 50 | 66 | 26 | 198 | 0 | 0 | 31 | 0 | 0.7301 | 1 | 8.682 | 6.3388 | High | Low | High | Mid | 394 | 535 | 8.682
PASO ROBLES 1104 | 182611104 | CENTRAL COAST | LOS PADRES | 42.6155 | 983878.3333 | 42.6529 | 71.31% | 13.13% | 75.36% | 3.966% | 0 | 0 | 42 | 81.22% | 11.95% | 3.22% | 72 | 13 | 1 | 92 | 191 | 95 | 0 | 5 | 10 | 559 | 41.4633 | 70 | 31 | 6 | 194 | 0 | 0 | 42 | 0 | 0.10492 | 16.4912 | 3.6294 | 6.2801 | Low | High | Low | Mid | 395 | 220 | 59.8537
CMC 1101 | 183111101 | CENTRAL COAST | LOS PADRES | 2.0609 | 0 | 44.7222 | 0% | 0% | 52.24% | 0% | 0 | 0 | 1 | 52.24% | 0% | 0% | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.36307 | 3.4262 | 5.0135 | 6.2367 | Medium | Medium | Medium | Mid | 396 | 441 | 17.1774
SAN RAFAEL 1101 | 042011101 | BAY AREA | NORTH BAY | 9.7957 | 1072501.6667 | 44.4457 | 8.888% | 2.542% | 18.89% | 70% | 7 | 0 | 20 | 18.46% | 72.98% | 10.16% | 120 | 99 | 6 | 1 | 142 | 137 | 12 | 8 | 11 | 443 | 30.6879 | 48 | 55 | 15 | 159 | 0 | 0 | 20 | 1 | 0.78794 | 1 | 7.8684 | 6.1998 | High | Low | High | Mid | 397 | 561 | 7.8684
WEIMAR 1101 | 152491101 | NORTHERN | SIERRA | 74.3116 | 525083.6667 | 42.7381 | 26.56% | 51.77% | 33.33% | 7.885% | 9 | 2 | 165 | 76.71% | 19.3% | 9.082% | 218 | 1115 | 16 | 1 | 329 | 188 | 9 | 26 | 37 | 1938 | 35.6812 | 389 | 212 | 19 | 878 | 0 | 2 | 165 | 0 | 0.19673 | 8.2398 | 3.8132 | 6.1813 | Low | Medium | Medium | Mid | 398 | 351 | 31.4198
OAK 0401 | 012600401 | BAY AREA | EAST BAY | 4.4257 | 107039 | 44.6053 | 45.28% | 6.689% | 37.47% | 25.47% | 0 | 0 | 5 | 1.207% | 89.88% | 47.37% | 12 | 31 | 0 | 2 | 25 | 3 | 2 | 6 | 13 | 152 | 55.7391 | 6 | 25 | 10 | 46 | 0 | 0 | 5 | 0 | 0.64455 | 1 | 9.5343 | 6.1453 | Medium | Low | High | Mid | 399 | 517 | 9.5343
HOLLISTER 2102 | 182492102 | CENTRAL COAST | CENTRAL COAST | 31.7344 | 522197.3333 | 50.8373 | 18.19% | 0.7013% | 42.11% | 6.044% | 0 | 0 | 11 | 42.46% | 57.54% | 10.95% | 115 | 107 | 8 | 4 | 36 | 20 | 0 | 4 | 4 | 210 | 16.5778 | 16 | 12 | 1 | 47 | 0 | 0 | 11 | 0 | 0.46472 | 10.11 | 1.3052 | 6.1323 | Medium | Medium | Low | Mid | 400 | 482 | 13.1959
BUELLTON 1102 | 183041102 | CENTRAL COAST | LOS PADRES | 16.9572 | 665292.3333 | 42.7893 | 47.68% | 3.595% | 53.83% | 12.51% | 0 | 0 | 33 | 57.71% | 13.56% | 1.471% | 33 | 33 | 1 | 120 | 98 | 33 | 0 | 8 | 9 | 340 | 25.0917 | 31 | 26 | 3 | 117 | 0 | 0 | 33 | 0 | 0.19293 | 10.1629 | 3.1254 | 6.1282 | Low | Medium | Low | Mid | 401 | 347 | 31.7635
OAKLAND X 1104 | 012541104 | BAY AREA | EAST BAY | 13.0513 | 312078.6667 | 45.438 | 49.79% | 4.765% | 61.12% | 19.37% | 12 | 4 | 43 | 35.41% | 57.39% | 20% | 127 | 120 | 0 | 1 | 316 | 13 | 52 | 19 | 31 | 550 | 19.375 | 24 | 66 | 34 | 157 | 0 | 0 | 43 | 0 | 0.64178 | 1.4326 | 6.6605 | 6.1236 | Medium | Low | High | Mid | 402 | 516 | 9.5416
VACAVILLE 1111 | 063601111 | NORTHERN | SACRAMENTO | 12.1732 | 730974 | 42.4232 | 68.03% | 10.69% | 44.05% | 28.98% | 1 | 0 | 13 | 44.9% | 38.83% | 4.437% | 49 | 139 | 6 | 0 | 65 | 14 | 0 | 5 | 8 | 293 | 30.0167 | 49 | 59 | 3 | 139 | 0 | 0 | 13 | 1 | 0.43303 | 3.2456 | 4.3457 | 6.1076 | Medium | Medium | Medium | Mid | 403 | 473 | 14.1045
ATASCADERO 1103 | 182541103 | CENTRAL COAST | LOS PADRES | 96.6947 | 871402 | 41.4933 | 70.47% | 3.698% | 79.43% | 12.11% | 2 | 3 | 89 | 73.22% | 24.88% | 6.851% | 176 | 76 | 1 | 272 | 663 | 179 | 6 | 20 | 31 | 1664 | 33.3787 | 245 | 128 | 4 | 602 | 0 | 0 | 88 | 0 | 0.11207 | 16.1071 | 3.3745 | 6.0916 | Low | High | Low | Mid | 404 | 241 | 54.3537
GREENBRAE 1102 | 043091102 | BAY AREA | NORTH BAY | 7.6047 | 1050311.6667 | 43.3746 | 18.35% | 0.2032% | 39.71% | 58.87% | 20 | 1 | 7 | 35.26% | 63.87% | 3.976% | 58 | 43 | 3 | 2 | 140 | 63 | 18 | 0 | 0 | 327 | 44.2289 | 26 | 30 | 14 | 85 | 0 | 0 | 7 | 1 | 0.79759 | 1 | 7.5934 | 6.0564 | High | Low | High | Mid | 405 | 568 | 7.5934
SPRUCE 0402 | 013340402 | BAY AREA | EAST BAY | 2.1044 | 0 | 43.9091 | 21.02% | 0% | 40.64% | 23.67% | 1 | 0 | 5 | 5.063% | 66.79% | 45.45% | 5 | 8 | 0 | 0 | 20 | 4 | 2 | 2 | 6 | 55 | 29.05 | 3 | 9 | 7 | 22 | 0 | 0 | 5 | 1 | 0.71004 | 1 | 8.4618 | 6.0082 | High | Low | High | Mid | 406 | 543 | 8.4618
LLAGAS 2101 | 083182101 | CENTRAL COAST | SAN JOSE | 23.8607 | 1657473.3333 | 42.5 | 7.639% | 1.247% | 96.57% | 2.004% | 0 | 0 | 23 | 95.36% | 4.461% | 6.984% | 44 | 131 | 0 | 14 | 97 | 14 | 0 | 4 | 4 | 315 | 24.1212 | 14 | 14 | 1 | 83 | 0 | 0 | 22 | 0 | 0.19551 | 9.3367 | 3.2614 | 5.9535 | Low | Medium | Low | Mid | 407 | 361 | 30.4511
HARTLEY 1102 | 043211102 | NORTHERN | HUMBOLDT | 5.905 | 539118.3333 | 45.7386 | 83.43% | 20.96% | 51.04% | 11.35% | 0 | 0 | 7 | 51.04% | 32.31% | 18.18% | 28 | 44 | 0 | 0 | 18 | 17 | 0 | 0 | 1 | 88 | 29.4054 | 11 | 12 | 0 | 38 | 0 | 0 | 7 | 0 | 0.46974 | 3.6499 | 3.4317 | 5.8836 | Medium | Medium | Low | Mid | 408 | 487 | 12.5252
SHINGLE SPRINGS 1103 | 153651103 | NORTHERN | SIERRA | 9.0287 | 773103 | 45.0222 | 26.7% | 0% | 80.57% | 0.4649% | 2 | 0 | 9 | 80.57% | 0.4649% | 0.8889% | 60 | 117 | 1 | 0 | 68 | 26 | 0 | 5 | 11 | 225 | 55.6071 | 32 | 63 | 6 | 112 | 0 | 0 | 9 | 0 | 0.21868 | 5.1181 | 5.2475 | 5.873 | Low | Medium | Medium | Mid | 409 | 379 | 26.8572
ZACA 1102 | 182681102 | CENTRAL COAST | LOS PADRES | 66.1296 | 626381.6667 | 42.3989 | 27.47% | 4.279% | 75.51% | 12.04% | 3 | 0 | 133 | 79.4% | 12.67% | 3.33% | 92 | 63 | 0 | 274 | 296 | 300 | 24 | 13 | 17 | 1141 | 28.724 | 82 | 82 | 3 | 357 | 0 | 0 | 131 | 0 | 0.15579 | 14.0871 | 2.6654 | 5.8494 | Low | High | Low | Mid | 410 | 316 | 37.5477
MORGAN HILL 2104 | 083242104 | CENTRAL COAST | SAN JOSE | 6.2528 | 979082.6667 | 43 | 23.93% | 1.22% | 98.69% | 0% | 2 | 0 | 11 | 100% | 0% | 5.333% | 17 | 32 | 0 | 0 | 28 | 4 | 0 | 6 | 7 | 75 | 36.2683 | 6 | 17 | 38 | 85 | 9 | 0 | 11 | 1 | 0.54864 | 2.6192 | 4.0646 | 5.8409 | Medium | Medium | Medium | Mid | 411 | 505 | 10.646
BELMONT 1103 | 024031103 | CENTRAL COAST | PENINSULA | 2.1749 | 1009738.6667 | 42.8873 | 3.119% | 0% | 46.55% | 53.45% | 1 | 0 | 12 | 46.55% | 53.45% | 7.042% | 17 | 48 | 0 | 0 | 78 | 8 | 0 | 5 | 6 | 142 | 11.0702 | 9 | 24 | 12 | 57 | 0 | 0 | 12 | 1 | 0.7262 | 1 | 7.9875 | 5.8005 | High | Low | High | Mid | 412 | 556 | 7.9875
SAN CARLOS 1104 | 024181104 | CENTRAL COAST | PENINSULA | 8.7241 | 1170594 | 43.2872 | 36.63% | 0.4447% | 39.83% | 28.96% | 6 | 0 | 24 | 37.62% | 41.59% | 11.08% | 45 | 83 | 0 | 2 | 230 | 26 | 0 | 4 | 12 | 397 | 29.3106 | 30 | 68 | 16 | 161 | 0 | 0 | 24 | 0 | 0.67498 | 1 | 8.55 | 5.7711 | High | Low | High | Mid | 413 | 540 | 8.55
VIEJO 2201 | 182852201 | CENTRAL COAST | CENTRAL COAST | 16.3884 | 946231 | 42.2955 | 14.97% | 2.949% | 36.71% | 23.86% | 23 | 5 | 55 | 17.52% | 59.59% | 15.56% | 60 | 143 | 0 | 9 | 246 | 32 | 37 | 17 | 28 | 540 | 36.5947 | 46 | 66 | 13 | 200 | 3 | 0 | 55 | 1 | 0.8768 | 1 | 6.5488 | 5.742 | High | Low | High | Mid | 414 | 613 | 6.5488
NORTH BRANCH 1101 | 163231101 | CENTRAL VALLEY | STOCKTON | 67.6297 | 539394.6667 | 43.3792 | 76.35% | 5.477% | 72.6% | 10.14% | 3 | 0 | 41 | 71% | 18.81% | 7.439% | 246 | 609 | 0 | 0 | 298 | 94 | 0 | 10 | 21 | 1277 | 27.9283 | 129 | 61 | 4 | 336 | 0 | 0 | 41 | 0 | 0.11885 | 8.9501 | 5.3505 | 5.6916 | Low | Medium | Medium | Mid | 415 | 275 | 47.8872
MORAGA 1104 | 013801104 | BAY AREA | DIABLO | 17.5873 | 532398.6667 | 44.5925 | 29.46% | 0% | 56.63% | 13.78% | 14 | 4 | 35 | 53.75% | 19.15% | 14.14% | 120 | 133 | 0 | 0 | 223 | 28 | 21 | 9 | 13 | 481 | 19.1368 | 42 | 104 | 33 | 219 | 0 | 0 | 35 | 1 | 0.71511 | 1.2163 | 6.4929 | 5.6473 | High | Low | High | Mid | 416 | 558 | 7.8972
CLARKSVILLE 2103 | 153612103 | NORTHERN | SIERRA | 34.4179 | 1667164.6667 | 43.3111 | 70.71% | 0.1511% | 99.61% | 0% | 2 | 0 | 15 | 99.74% | 0% | 0.8292% | 51 | 364 | 3 | 0 | 119 | 12 | 5 | 3 | 6 | 603 | 49.5714 | 78 | 82 | 9 | 210 | 0 | 0 | 15 | 0 | 0.16045 | 8.0221 | 4.3638 | 5.6169 | Low | Medium | Medium | Mid | 417 | 332 | 35.0065
DUNLAP 1102 | 254061102 | CENTRAL VALLEY | FRESNO | 55.7604 | 130517 | 40.8203 | 38.2% | 75.31% | 23.26% | 0% | 12 | 5 | 63 | 96.98% | 0% | 29.35% | 68 | 56 | 1 | 85 | 404 | 98 | 0 | 11 | 24 | 1097 | 11.9612 | 122 | 45 | 5 | 341 | 0 | 0 | 62 | 0 | 0.30752 | 8.8689 | 2.0526 | 5.5982 | Low | Medium | Low | Mid | 418 | 435 | 18.2043
SAN RAFAEL 1109 | 042011109 | BAY AREA | NORTH BAY | 11.6485 | 967675 | 43.8345 | 74.16% | 1.921% | 42.39% | 20.6% | 8 | 1 | 9 | 59.73% | 22.52% | 7.718% | 49 | 57 | 2 | 4 | 141 | 57 | 4 | 7 | 9 | 298 | 30.4255 | 26 | 24 | 15 | 95 | 0 | 1 | 9 | 1 | 0.6749 | 1 | 8.2237 | 5.5502 | High | Low | High | Mid | 419 | 550 | 8.2237
WISE 1102 | 152271102 | NORTHERN | SIERRA | 115.3011 | 586467.6667 | 42.7308 | 42.3% | 1.815% | 67.61% | 21.91% | 8 | 0 | 130 | 63.37% | 28% | 7.857% | 197 | 1584 | 10 | 0 | 316 | 146 | 58 | 19 | 39 | 2482 | 32.1484 | 452 | 309 | 10 | 1032 | 0 | 1 | 130 | 0 | 0.33606 | 3.9368 | 4.1412 | 5.4788 | Medium | Medium | Medium | Mid | 420 | 449 | 16.3028
RIDGE 0401 | 012840401 | BAY AREA | EAST BAY | 2.662 | 47847 | 44.2308 | 44.35% | 4.035% | 33.08% | 33.93% | 1 | 0 | 6 | 10.22% | 87.78% | 29.91% | 9 | 21 | 0 | 0 | 72 | 7 | 6 | 6 | 9 | 117 | 43.9 | 7 | 25 | 6 | 43 | 0 | 0 | 6 | 1 | 0.71977 | 1 | 7.5885 | 5.462 | High | Low | High | Mid | 421 | 569 | 7.5885
APPLE HILL 1103 | 153661103 | NORTHERN | SIERRA | 61.6574 | 603883 | 41.8106 | 19.54% | 49.2% | 27.98% | 7.434% | 10 | 2 | 109 | 75.99% | 13.71% | 2.511% | 146 | 783 | 12 | 0 | 356 | 196 | 6 | 8 | 14 | 1752 | 46.4663 | 296 | 169 | 23 | 675 | 0 | 0 | 109 | 0 | 0.14332 | 10.7653 | 3.4967 | 5.3949 | Low | Medium | Low | Mid | 422 | 315 | 37.6429
MARTELL 1102 | 163011102 | CENTRAL VALLEY | STOCKTON | 9.84 | 363802.3333 | 43.0645 | 67.6% | 0% | 60.56% | 7.422% | 3 | 0 | 8 | 53.89% | 34.16% | 1.29% | 21 | 73 | 0 | 0 | 45 | 21 | 0 | 4 | 7 | 155 | 29 | 16 | 5 | 3 | 41 | 0 | 0 | 8 | 0 | 0.37154 | 2.6842 | 5.3749 | 5.3603 | Medium | Medium | Medium | Mid | 423 | 469 | 14.4271
VIEJO 2202 | 182852202 | CENTRAL COAST | CENTRAL COAST | 14.9046 | 1361490 | 42.5173 | 30.45% | 2.66% | 35.44% | 27.21% | 20 | 5 | 47 | 9.565% | 64.62% | 10.2% | 74 | 91 | 0 | 10 | 244 | 15 | 8 | 20 | 36 | 549 | 40.142 | 55 | 54 | 11 | 174 | 0 | 0 | 47 | 1 | 0.85804 | 1 | 6.2054 | 5.3245 | High | Low | High | Mid | 424 | 625 | 6.2054
SONOMA 1102 | 042721102 | NORTHERN | SONOMA | 6.154 | 984388.6667 | 44.031 | 43.3% | 0% | 80.66% | 19.34% | 3 | 1 | 6 | 80.66% | 19.34% | 6.977% | 28 | 49 | 0 | 1 | 43 | 18 | 0 | 2 | 2 | 129 | 42.2778 | 13 | 22 | 2 | 54 | 0 | 0 | 6 | 1 | 0.37399 | 2.4554 | 5.6694 | 5.2062 | Medium | Medium | High | Mid | 425 | 475 | 13.9205
LOS GATOS 1108 | 082021108 | CENTRAL COAST | DE ANZA | 4.3173 | 505778.6667 | 44.1867 | 16.21% | 3.661% | 40.4% | 44.3% | 7 | 0 | 17 | 37.17% | 62.08% | 5.422% | 43 | 69 | 0 | 7 | 66 | 8 | 0 | 7 | 10 | 166 | 1.1447 | 15 | 23 | 15 | 78 | 0 | 0 | 17 | 1 | 0.77051 | 1 | 6.6966 | 5.1598 | High | Low | High | Mid | 426 | 604 | 6.6966
POSO MOUNTAIN 2101 | 253642101 | CENTRAL VALLEY | KERN | 50.7844 | 413243 | 42.8582 | 78.01% | 40.17% | 40.79% | 8.342% | 30 | 0 | 16 | 57.21% | 32.19% | 11.77% | 86 | 29 | 0 | 98 | 158 | 77 | 0 | 8 | 21 | 705 | 6.6789 | 35 | 10 | 3 | 117 | 0 | 1 | 15 | 0 | 0.46369 | 7.8088 | 1.4221 | 5.149 | Medium | Medium | Low | Mid | 427 | 502 | 11.1046
PAUL SWEET 2102 | 083252102 | CENTRAL COAST | CENTRAL COAST | 5.5176 | 1317659.6667 | 45.1149 | 107.4% | 0.05154% | 26.6% | 40.14% | 9 | 2 | 13 | 25.82% | 42.53% | 4.598% | 17 | 29 | 0 | 3 | 36 | 5 | 5 | 5 | 10 | 87 | 63 | 5 | 3 | 0 | 31 | 0 | 0 | 13 | 1 | 0.76947 | 1 | 6.6814 | 5.1412 | High | Low | High | Mid | 428 | 606 | 6.6814
VALLEY VIEW 1103 | 014341103 | BAY AREA | EAST BAY | 0.6427 | 857099 | 46.3636 | 0% | 86.99% | 0% | 4.309% | 0 | 0 | 0 | 0% | 91.3% | 0% | 4 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 11 | 0 | 1 | 3 | 0 | 4 | 0 | 0 | 0 | 0 | 0.18394 | 3.6934 | 7.5586 | 5.135 | Low | Medium | High | Mid | 429 | 371 | 27.917
MORGAN HILL 2110 | 083242110 | CENTRAL COAST | SAN JOSE | 2.1851 | 1472058.6667 | 44.7 | 7.402% | 0% | 79.23% | 15.35% | 0 | 0 | 7 | 56.73% | 37.85% | 12% | 20 | 34 | 0 | 0 | 8 | 2 | 0 | 2 | 2 | 50 | 11.2857 | 6 | 10 | 2 | 23 | 0 | 0 | 7 | 1 | 0.5356 | 2.3084 | 4.1363 | 5.114 | Medium | Low | Medium | Mid | 430 | 515 | 9.548
POTTER VALLEY P H 1104 | 042281104 | NORTHERN | HUMBOLDT | 7.7001 | 0 | 42.5714 | 22.89% | 0% | 51.2% | 47.83% | 0 | 0 | 3 | 51.2% | 47.83% | 9.434% | 16 | 47 | 0 | 1 | 24 | 11 | 0 | 4 | 7 | 106 | 27.0256 | 17 | 1 | 3 | 40 | 0 | 0 | 3 | 0 | 0.5682 | 5.2347 | 1.6975 | 5.049 | Medium | Medium | Low | Mid | 431 | 529 | 8.8859
SARATOGA 1103 | 083371103 | CENTRAL COAST | DE ANZA | 4.5983 | 534592 | 42.6816 | 20.02% | 8.864% | 37.78% | 34.42% | 5 | 1 | 19 | 46.64% | 34.42% | 10.61% | 27 | 30 | 0 | 0 | 120 | 10 | 0 | 5 | 9 | 179 | 8.0513 | 16 | 31 | 12 | 78 | 0 | 0 | 19 | 1 | 0.796 | 1 | 6.3393 | 5.0461 | High | Low | High | Mid | 432 | 619 | 6.3393
NAPA 1112 | 042021112 | BAY AREA | NORTH BAY | 19.8336 | 624532.6667 | 42.9805 | 14.88% | 0% | 75% | 8.553% | 3 | 1 | 13 | 72.43% | 27.57% | 16.61% | 44 | 120 | 0 | 0 | 49 | 58 | 0 | 3 | 4 | 307 | 31.4458 | 19 | 21 | 2 | 89 | 0 | 0 | 13 | 0 | 0.318 | 3.4143 | 4.6347 | 5.0322 | Low | Medium | Medium | Mid | 433 | 454 | 15.8244
OAKLAND K 1103 | 012101103 | BAY AREA | EAST BAY | 6.1448 | 472078.6667 | 45.4792 | 27.36% | 5.229% | 42.94% | 15.12% | 10 | 2 | 23 | 29.51% | 44.46% | 25% | 57 | 57 | 1 | 3 | 97 | 24 | 15 | 8 | 19 | 240 | 30.7857 | 19 | 34 | 8 | 72 | 0 | 0 | 22 | 0 | 0.76445 | 1 | 6.5519 | 5.0086 | High | Low | High | Mid | 434 | 612 | 6.5519
SARATOGA 1104 | 083371104 | CENTRAL COAST | DE ANZA | 1.8773 | 667755 | 41.3265 | 5.481% | 0% | 51.56% | 10.6% | 5 | 0 | 14 | 51.56% | 10.6% | 12.12% | 18 | 12 | 0 | 0 | 68 | 9 | 0 | 5 | 7 | 99 | 1.451 | 11 | 20 | 5 | 52 | 0 | 0 | 14 | 1 | 0.66903 | 1 | 7.4301 | 4.9709 | High | Low | High | Mid | 435 | 574 | 7.4301
ROSSMOOR 1106 | 014161106 | BAY AREA | DIABLO | 4.9819 | 896923 | 44.3871 | 65.85% | 0% | 48.66% | 32.51% | 3 | 0 | 8 | 38.49% | 42.67% | 11.54% | 31 | 45 | 0 | 0 | 65 | 3 | 0 | 1 | 3 | 156 | 21.7564 | 16 | 37 | 10 | 79 | 0 | 0 | 8 | 1 | 0.72089 | 1 | 6.7743 | 4.8836 | High | Low | High | Mid | 436 | 598 | 6.7743
FLORENCE 0401 | 012690401 | BAY AREA | EAST BAY | 1.7951 | 74733 | 44.0323 | 0% | 0% | 13.98% | 22.65% | 5 | 0 | 3 | 2.192% | 89.6% | 37.5% | 5 | 3 | 0 | 0 | 14 | 1 | 10 | 0 | 3 | 32 | 44.8 | 6 | 4 | 0 | 10 | 0 | 0 | 3 | 1 | 0.72014 | 1 | 6.7634 | 4.8706 | High | Low | High | Mid | 437 | 600 | 6.7634
RALSTON 1102 | 024141102 | CENTRAL COAST | PENINSULA | 3.4743 | 495767.6667 | 44.4444 | 15.12% | 0% | 50.03% | 1.248% | 2 | 0 | 11 | 50.03% | 1.248% | 4.444% | 4 | 5 | 0 | 0 | 81 | 2 | 0 | 6 | 8 | 90 | 28.4423 | 2 | 10 | 33 | 52 | 1 | 0 | 11 | 1 | 0.63487 | 1 | 7.6717 | 4.8705 | Medium | Low | High | Mid | 438 | 564 | 7.6717
OROVILLE 1104 | 102521104 | NORTHERN | NORTH VALLEY | 0.28474 | 627607.3333 | 0 | 4.031% | 0% | 65.82% | 34.18% | 0 | 0 | 0 | 65.82% | 34.18% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.17896 | 4.4448 | 6.1103 | 4.8605 | Low | Medium | High | Mid | 439 | 374 | 27.1591
PARADISE 1103 | 102831103 | NORTHERN | NORTH VALLEY | 41.5864 | 1124803.6667 | 43.0094 | 10.11% | 2.857% | 56.83% | 26.25% | 25 | 6 | 65 | 61.46% | 28.58% | 6.832% | 206 | 569 | 65 | 1 | 406 | 109 | 41 | 23 | 35 | 1493 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 65 | 1 | 0.74929 | 1.0005 | 6.4304 | 4.8204 | High | Low | High | Mid | 440 | 617 | 6.4334
PEABODY 2108 | 063642108 | NORTHERN | SACRAMENTO | 0.94269 | 1304830.6667 | 41.4286 | 296.8% | 0% | 50.32% | 1.388% | 0 | 0 | 0 | 50.32% | 1.388% | 0% | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 56.6667 | 1 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.21045 | 5.4692 | 4.1289 | 4.7523 | Low | Medium | Medium | Mid | 441 | 394 | 22.5819
PUTAH CREEK 1102 | 063681102 | NORTHERN | SACRAMENTO | 28.6295 | 404010 | 43.8606 | 44.46% | 0% | 90.58% | 9.42% | 0 | 0 | 16 | 90.58% | 9.42% | 4.307% | 99 | 294 | 8 | 0 | 82 | 19 | 0 | 3 | 6 | 534 | 22.3988 | 66 | 38 | 4 | 182 | 0 | 1 | 16 | 0 | 0.089636 | 19.4519 | 2.7226 | 4.7471 | Low | High | Low | Mid | 442 | 250 | 52.9594
DUNLAP 1103 | 254061103 | CENTRAL VALLEY | FRESNO | 70.8013 | 317583.3333 | 41.437 | 95.18% | 51.79% | 42.82% | 0.09684% | 19 | 2 | 59 | 94.48% | 0.7698% | 23.66% | 80 | 70 | 0 | 45 | 502 | 136 | 3 | 22 | 36 | 1196 | 12.7956 | 156 | 76 | 7 | 421 | 0 | 0 | 59 | 0 | 0.29453 | 6.9649 | 2.2879 | 4.6932 | Low | Medium | Low | Mid | 443 | 453 | 15.9347
WILLITS 1102 | 042661102 | NORTHERN | HUMBOLDT | 6.3612 | 451490 | 43.1897 | 26.26% | 3.841% | 23.89% | 49.54% | 0 | 0 | 11 | 23.89% | 56.8% | 9.195% | 28 | 60 | 0 | 1 | 65 | 7 | 0 | 3 | 5 | 174 | 28.8636 | 15 | 20 | 10 | 66 | 0 | 0 | 11 | 0 | 0.60528 | 2.4994 | 3.0894 | 4.6739 | Medium | Medium | Low | Mid | 444 | 563 | 7.7218
LOS OSITOS 2102 | 182082102 | CENTRAL COAST | CENTRAL COAST | 2.7527 | 758740.6667 | 39.7959 | 2.354% | 0% | 71.89% | 19.77% | 0 | 0 | 0 | 71.89% | 19.77% | 10.2% | 0 | 34 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 49 | 1.7778 | 3 | 2 | 0 | 11 | 0 | 0 | 0 | 0 | 0.14359 | 12.2495 | 2.6437 | 4.6502 | Low | Medium | Low | Mid | 445 | 343 | 32.3842
LLAGAS 2104 | 083182104 | CENTRAL COAST | SAN JOSE | 2.9141 | 524502.3333 | 37.2222 | 0% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 0% | 0 | 5 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 27 | 1.4444 | 2 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 0.14492 | 9.7685 | 3.2688 | 4.6274 | Low | Medium | Low | Mid | 446 | 346 | 31.9315
WHEATLAND 1105 | 152811105 | NORTHERN | SIERRA | 11.3149 | 387985.6667 | 45.3867 | 35.01% | 0% | 100% | 0% | 0 | 0 | 2 | 100% | 0% | 4.972% | 46 | 95 | 2 | 0 | 15 | 14 | 0 | 2 | 2 | 181 | 33.1633 | 31 | 6 | 0 | 53 | 0 | 0 | 2 | 0 | 0.18863 | 9.212 | 2.6356 | 4.5799 | Low | Medium | Low | Mid | 447 | 387 | 24.2792
SONOMA 1103 | 042721103 | NORTHERN | SONOMA | 14.1173 | 720886.6667 | 44.0377 | 30.67% | 0% | 95.21% | 4.746% | 1 | 3 | 9 | 90.87% | 9.088% | 5.021% | 47 | 166 | 0 | 0 | 29 | 10 | 1 | 5 | 5 | 239 | 47.1702 | 32 | 22 | 3 | 97 | 0 | 0 | 8 | 0 | 0.22636 | 3.9482 | 5.1063 | 4.5635 | Low | Medium | Medium | Mid | 448 | 414 | 20.1607
CAROLANDS 0404 | 024060404 | CENTRAL COAST | PENINSULA | 4.1147 | 322109 | 44.3949 | 46.95% | 3.653% | 18.37% | 52.56% | 7 | 0 | 24 | 16.49% | 83.51% | 19.75% | 21 | 39 | 0 | 0 | 93 | 20 | 6 | 0 | 3 | 157 | 43.913 | 13 | 36 | 8 | 71 | 0 | 0 | 24 | 1 | 0.79292 | 1 | 5.7269 | 4.541 | High | Low | High | Mid | 449 | 655 | 5.7269
VIEJO 2204 | 182852204 | CENTRAL COAST | CENTRAL COAST | 4.1676 | 1493490.3333 | 42.637 | 35.66% | 11.26% | 51.09% | 16.76% | 4 | 0 | 10 | 18.87% | 58.93% | 10.27% | 14 | 43 | 0 | 0 | 35 | 9 | 0 | 2 | 4 | 146 | 41.2093 | 13 | 19 | 0 | 44 | 2 | 0 | 10 | 1 | 0.76053 | 1 | 5.9272 | 4.5078 | High | Low | High | Mid | 450 | 637 | 5.9272
HARTLEY 1101 | 043211101 | NORTHERN | HUMBOLDT | 31.2788 | 1012195.3333 | 44.292 | 49.86% | 2.894% | 62.58% | 18.56% | 3 | 0 | 38 | 66.25% | 19.74% | 8.496% | 153 | 263 | 0 | 2 | 161 | 60 | 8 | 4 | 14 | 565 | 31.0041 | 114 | 47 | 4 | 244 | 0 | 0 | 38 | 0 | 0.29774 | 4.231 | 3.5693 | 4.4964 | Low | Medium | Low | Mid | 451 | 461 | 15.1018
TAR FLAT 0401 | 163240401 | CENTRAL VALLEY | YOSEMITE | 3.63 | 84058.6667 | 43.2394 | 0% | 0% | 25.68% | 42.5% | 4 | 0 | 4 | 6.884% | 93.12% | 14.79% | 33 | 41 | 0 | 0 | 51 | 17 | 0 | 0 | 1 | 142 | 29.4308 | 13 | 26 | 11 | 70 | 0 | 0 | 4 | 1 | 0.79867 | 1 | 5.6149 | 4.4845 | High | Low | High | Mid | 452 | 661 | 5.6149
LOS GATOS 1102 | 082021102 | CENTRAL COAST | DE ANZA | 1.2351 | 613031.3333 | 42.3276 | 8.803% | 0% | 53.25% | 36.39% | 2 | 0 | 4 | 53.25% | 46.75% | 18.97% | 3 | 20 | 0 | 2 | 23 | 8 | 0 | 2 | 2 | 58 | 0 | 7 | 7 | 7 | 22 | 0 | 0 | 4 | 1 | 0.63391 | 1 | 7.0409 | 4.4633 | Medium | Low | High | Mid | 453 | 584 | 7.0409
OAKLAND J 1102 | 012091102 | BAY AREA | EAST BAY | 6.3189 | 965953.6667 | 45.3663 | 11.05% | 2.379% | 37.3% | 29.17% | 5 | 1 | 22 | 16.33% | 55.88% | 17.88% | 66 | 47 | 1 | 0 | 190 | 5 | 0 | 9 | 15 | 274 | 20.1216 | 17 | 29 | 12 | 78 | 0 | 0 | 22 | 0 | 0.7059 | 1 | 6.3192 | 4.4607 | High | Low | High | Mid | 454 | 623 | 6.3192
LOS GATOS 1101 | 082021101 | CENTRAL COAST | DE ANZA | 10.2975 | 1000993 | 42.8101 | 22.58% | 2.826% | 54.09% | 41.84% | 13 | 0 | 46 | 54.67% | 44.09% | 4.545% | 80 | 146 | 0 | 0 | 197 | 11 | 0 | 18 | 23 | 396 | 6.3576 | 40 | 67 | 31 | 171 | 0 | 0 | 46 | 1 | 0.72044 | 1 | 6.1605 | 4.4382 | High | Low | High | Mid | 455 | 627 | 6.1605
SARATOGA 1106 | 083371106 | CENTRAL COAST | DE ANZA | 13.828 | 910023.6667 | 44.5 | 22.41% | 7.284% | 44.05% | 36.05% | 8 | 0 | 47 | 38.59% | 57.45% | 11.41% | 126 | 142 | 0 | 5 | 232 | 41 | 20 | 14 | 23 | 491 | 2.0973 | 57 | 82 | 31 | 237 | 0 | 0 | 47 | 0 | 0.62822 | 1 | 7.0258 | 4.4137 | Medium | Low | High | Mid | 456 | 585 | 7.0258
CORRAL 1101 | 162991101 | CENTRAL VALLEY | STOCKTON | 122.4932 | 1121144 | 42.3663 | 74.89% | 0.1268% | 82.86% | 8.016% | 3 | 2 | 135 | 82.83% | 8.175% | 11.06% | 287 | 1036 | 10 | 0 | 585 | 129 | 11 | 9 | 22 | 2433 | 9.0406 | 414 | 269 | 23 | 974 | 0 | 0 | 135 | 0 | 0.089599 | 9.7556 | 5.0466 | 4.4112 | Low | Medium | Medium | Mid | 457 | 271 | 49.2325
CLARKSVILLE 2104 | 153612104 | NORTHERN | SIERRA | 68.1625 | 1494335.3333 | 44.0434 | 54.18% | 0.3882% | 90.3% | 0% | 3 | 4 | 74 | 90.79% | 0% | 0.7107% | 248 | 843 | 29 | 0 | 134 | 90 | 0 | 13 | 25 | 1407 | 48.5196 | 223 | 237 | 19 | 557 | 0 | 0 | 74 | 0 | 0.052517 | 15.9304 | 5.2704 | 4.4093 | Low | High | Medium | Mid | 458 | 159 | 83.9591
BERKELEY F 1105 | 012061105 | BAY AREA | EAST BAY | 1.9192 | 695082.3333 | 46.131 | 4.802% | 0% | 60.21% | 19.91% | 2 | 0 | 9 | 29.09% | 70.02% | 35.71% | 20 | 25 | 0 | 0 | 32 | 3 | 7 | 8 | 11 | 84 | 25.6364 | 6 | 9 | 2 | 23 | 0 | 0 | 9 | 0 | 0.58515 | 1 | 7.5238 | 4.4025 | Medium | Low | High | Mid | 459 | 570 | 7.5238
BERESFORD 0403 | 024040403 | CENTRAL COAST | PENINSULA | 4.6093 | 327613.3333 | 42.0574 | 43.53% | 0% | 29.31% | 48.72% | 5 | 0 | 24 | 16.62% | 83.15% | 17.22% | 14 | 54 | 0 | 0 | 100 | 21 | 7 | 1 | 6 | 209 | 47.2625 | 13 | 44 | 8 | 80 | 1 | 0 | 24 | 1 | 0.80333 | 1 | 5.3755 | 4.3183 | High | Low | Medium | Mid | 460 | 675 | 5.3755
VALLEY VIEW 1105 | 014341105 | BAY AREA | EAST BAY | 5.9477 | 821930 | 43.2258 | 0% | 0% | 55.14% | 25.83% | 5 | 0 | 7 | 39.76% | 41.21% | 15.48% | 12 | 23 | 0 | 1 | 87 | 2 | 0 | 1 | 1 | 155 | 16.8333 | 17 | 18 | 1 | 49 | 0 | 0 | 7 | 0 | 0.62058 | 1 | 6.9552 | 4.3163 | Medium | Low | High | Mid | 461 | 589 | 6.9552
LAS AROMAS 0401 | 013600401 | BAY AREA | DIABLO | 5.9862 | 115734 | 44.5026 | 0% | 0.1907% | 68.28% | 16.32% | 8 | 2 | 14 | 1.339% | 87.73% | 31.09% | 41 | 59 | 0 | 6 | 68 | 9 | 8 | 2 | 6 | 193 | 44.6915 | 12 | 54 | 15 | 94 | 0 | 0 | 14 | 0 | 0.65372 | 1 | 6.5306 | 4.2692 | Medium | Low | High | Mid | 462 | 615 | 6.5306
WALDO 0401 | 013350401 | BAY AREA | EAST BAY | 1.7206 | 147915.3333 | 43.012 | 40.55% | 26.03% | 12.34% | 39.32% | 0 | 0 | 1 | 12.34% | 77.91% | 26.51% | 3 | 13 | 0 | 0 | 56 | 2 | 4 | 0 | 2 | 83 | 46.5455 | 5 | 11 | 7 | 24 | 0 | 0 | 1 | 0 | 0.50388 | 1 | 8.4574 | 4.2615 | Medium | Low | High | Mid | 463 | 544 | 8.4574
VIEJO 2203 | 182852203 | CENTRAL COAST | CENTRAL COAST | 3.9689 | 655455 | 47.4405 | 29.55% | 20.94% | 33.14% | 15.69% | 11 | 0 | 10 | 19.76% | 54.06% | 4.762% | 29 | 35 | 0 | 0 | 23 | 4 | 0 | 2 | 2 | 84 | 31.0909 | 7 | 4 | 1 | 23 | 0 | 0 | 9 | 1 | 0.72996 | 1 | 5.8229 | 4.2505 | High | Low | High | Mid | 464 | 646 | 5.8229
POTTER VALLEY P H 1105 | 042281105 | NORTHERN | HUMBOLDT | 49.5502 | 211374 | 42.6262 | 33.12% | 10.21% | 72.73% | 10.72% | 2 | 1 | 28 | 80.59% | 13.06% | 5.156% | 101 | 325 | 2 | 24 | 231 | 67 | 0 | 10 | 15 | 834 | 37.7011 | 87 | 30 | 8 | 273 | 0 | 1 | 28 | 0 | 0.10901 | 24.9211 | 1.5637 | 4.2481 | Low | High | Low | Mid | 465 | 309 | 38.9688
SAN RAFAEL 1106 | 042011106 | BAY AREA | NORTH BAY | 3.8001 | 931321 | 42.9082 | 24.99% | 11.6% | 22.06% | 23.41% | 5 | 0 | 3 | 22.06% | 35.01% | 1.02% | 12 | 25 | 0 | 0 | 47 | 12 | 0 | 2 | 3 | 98 | 36.125 | 14 | 7 | 3 | 48 | 0 | 0 | 3 | 0 | 0.52609 | 1 | 8.0737 | 4.2475 | Medium | Low | High | Mid | 466 | 553 | 8.0737
PALO SECO 0401 | 013180401 | BAY AREA | EAST BAY | 4.7078 | 111604.3333 | 45.0439 | 0% | 13.34% | 29.12% | 13.74% | 0 | 0 | 12 | 0% | 81.88% | 55.26% | 21 | 7 | 0 | 0 | 52 | 12 | 4 | 0 | 7 | 114 | 55.5227 | 9 | 24 | 7 | 46 | 0 | 0 | 12 | 1 | 0.62874 | 1 | 6.7383 | 4.2367 | Medium | Low | High | Mid | 467 | 601 | 6.7383
DOBBINS 1101 | 153741101 | NORTHERN | SIERRA | 80.9568 | 273408.3333 | 41.9471 | 29.91% | 12.82% | 76.24% | 2.657% | 7 | 0 | 82 | 93.55% | 2.657% | 6.025% | 170 | 1122 | 58 | 0 | 211 | 148 | 10 | 13 | 25 | 1892 | 39.7418 | 277 | 73 | 9 | 638 | 0 | 6 | 82 | 0 | 0.072378 | 14.2415 | 4.1027 | 4.229 | Low | High | Medium | Mid | 468 | 226 | 58.4285
RIDGE 0402 | 012840402 | BAY AREA | EAST BAY | 1.857 | 62430.6667 | 43.3951 | 69.08% | 0% | 44.06% | 36.54% | 0 | 0 | 2 | 30.41% | 69.44% | 23.46% | 7 | 21 | 0 | 0 | 33 | 1 | 2 | 3 | 5 | 81 | 44.4167 | 4 | 9 | 5 | 24 | 0 | 0 | 2 | 0 | 0.56589 | 1 | 7.47 | 4.2271 | Medium | Low | High | Mid | 469 | 572 | 7.47
SAN MIGUEL 1104 | 182661104 | CENTRAL COAST | LOS PADRES | 26.5441 | 1053624 | 41.345 | 83.2% | 0.2016% | 98.92% | 0.3796% | 0 | 1 | 12 | 99.4% | 0.5812% | 1.754% | 15 | 76 | 0 | 67 | 100 | 34 | 0 | 8 | 11 | 342 | 46.8646 | 41 | 19 | 2 | 100 | 0 | 1 | 11 | 0 | 0.19154 | 7.5083 | 2.911 | 4.1865 | Low | Medium | Low | Mid | 470 | 399 | 21.857
SO. CAL. EDISON #3 1101 | 258861101 | CENTRAL VALLEY | FRESNO | 6.4255 | 1140.3333 | 42.5 | 0% | 0% | 15.88% | 0% | 0 | 0 | 4 | 15.88% | 84.12% | 10% | 0 | 0 | 0 | 0 | 11 | 4 | 0 | 0 | 0 | 20 | 15.0769 | 10 | 3 | 0 | 17 | 0 | 0 | 4 | 0 | 0.37251 | 4.6056 | 2.4212 | 4.1539 | Medium | Medium | Low | Mid | 471 | 500 | 11.151
KONOCTI 1108 | 043311108 | NORTHERN | HUMBOLDT | 23.2432 | 650308.6667 | 45.7309 | 56.47% | 0% | 77.17% | 0.5813% | 4 | 1 | 15 | 77.17% | 0.5813% | 14.62% | 243 | 320 | 0 | 2 | 115 | 86 | 6 | 4 | 11 | 602 | 48.3822 | 107 | 96 | 34 | 261 | 0 | 0 | 15 | 0 | 0.23488 | 2.8782 | 6.0774 | 4.1084 | Low | Medium | High | Mid | 472 | 440 | 17.4919
INDIAN FLAT 1104 | 252691104 | CENTRAL VALLEY | YOSEMITE | 16.7358 | 311983 | 42.409 | 0% | 58.08% | 14.74% | 2.828% | 2 | 0 | 21 | 76.62% | 11.94% | 11.51% | 37 | 11 | 5 | 0 | 183 | 53 | 9 | 8 | 15 | 365 | 69.881 | 29 | 16 | 4 | 98 | 0 | 0 | 21 | 0 | 0.38718 | 3.3705 | 3.132 | 4.0872 | Medium | Medium | Low | Mid | 473 | 507 | 10.5564
DEL MONTE 2103 | 182222103 | CENTRAL COAST | CENTRAL COAST | 13.5735 | 1826126 | 43.6569 | 10.44% | 0.9828% | 60.53% | 9.887% | 13 | 3 | 47 | 19.33% | 53.28% | 10.76% | 95 | 132 | 0 | 9 | 120 | 31 | 5 | 12 | 18 | 446 | 33.367 | 43 | 34 | 2 | 121 | 0 | 0 | 47 | 1 | 0.73565 | 1 | 5.4971 | 4.044 | High | Low | High | Mid | 474 | 667 | 5.4971
OAKLAND K 1101 | 012101101 | BAY AREA | EAST BAY | 2.9361 | 516942 | 45.087 | 22.59% | 12.38% | 15.6% | 21.08% | 3 | 0 | 10 | 13.33% | 55.83% | 51.3% | 49 | 12 | 0 | 0 | 81 | 7 | 8 | 10 | 17 | 115 | 17.4643 | 6 | 10 | 8 | 30 | 0 | 0 | 10 | 0 | 0.65841 | 1 | 6.1353 | 4.0395 | Medium | Low | High | Mid | 475 | 630 | 6.1353
OAKHURST 1101 | 254421101 | CENTRAL VALLEY | YOSEMITE | 92.9272 | 802392 | 39.9706 | 63.81% | 51.99% | 38.39% | 3.996% | 2 | 1 | 71 | 86.64% | 7.922% | 24.32% | 57 | 394 | 1 | 2 | 873 | 142 | 0 | 24 | 32 | 2052 | 27.984 | 300 | 172 | 16 | 820 | 0 | 1 | 71 | 0 | 0.092651 | 11.2547 | 3.8539 | 4.0187 | Low | Medium | Medium | Mid | 476 | 291 | 43.3744
EL CERRITO G 1112 | 012501112 | BAY AREA | EAST BAY | 5.0582 | 676843.6667 | 43.3333 | 9.659% | 0% | 64% | 27.08% | 2 | 0 | 2 | 24.47% | 68.63% | 30.68% | 4 | 14 | 0 | 1 | 59 | 1 | 0 | 1 | 1 | 88 | 6.3448 | 7 | 12 | 0 | 29 | 0 | 0 | 2 | 0 | 0.46574 | 1 | 8.5484 | 3.9813 | Medium | Low | High | Mid | 477 | 541 | 8.5484
OAKHURST 1102 | 254421102 | CENTRAL VALLEY | YOSEMITE | 11.4965 | 459199.6667 | 40.0723 | 39.62% | 48.97% | 42.86% | 0% | 1 | 0 | 25 | 94.71% | 0.9497% | 23.71% | 18 | 59 | 0 | 0 | 168 | 27 | 0 | 6 | 11 | 350 | 38.9931 | 51 | 50 | 5 | 152 | 0 | 0 | 25 | 0 | 0.25737 | 3.9396 | 3.8815 | 3.9356 | Low | Medium | Medium | Mid | 478 | 459 | 15.2916
SAN MIGUEL 1105 | 182661105 | CENTRAL COAST | LOS PADRES | 1.3942 | 377495 | 43.6111 | 17.58% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 5.556% | 1 | 13 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 18 | 62.8571 | 5 | 1 | 0 | 7 | 0 | 0 | 1 | 0 | 0.22921 | 5.3197 | 3.2213 | 3.9278 | Low | Medium | Low | Mid | 479 | 442 | 17.1363
PLACERVILLE 1110 | 153081110 | NORTHERN | SIERRA | 34.3842 | 527171.3333 | 42.7593 | 19.84% | 23.11% | 46.88% | 17.8% | 6 | 0 | 77 | 54.68% | 33.1% | 0.201% | 153 | 498 | 15 | 0 | 190 | 41 | 0 | 10 | 29 | 995 | 48.9063 | 166 | 116 | 20 | 404 | 0 | 2 | 77 | 0 | 0.28065 | 3.5354 | 3.9518 | 3.9211 | Low | Medium | Medium | Mid | 480 | 474 | 13.9714
CLAY 1103 | 163341103 | CENTRAL VALLEY | STOCKTON | 56.3815 | 626730 | 44.3689 | 132.9% | 4.832% | 80.45% | 0.3339% | 2 | 3 | 25 | 73.75% | 13.44% | 7.906% | 199 | 436 | 0 | 0 | 264 | 92 | 0 | 8 | 23 | 936 | 32.4372 | 69 | 37 | 3 | 193 | 0 | 1 | 25 | 0 | 0.145 | 5.6318 | 4.7711 | 3.8961 | Low | Medium | Medium | Mid | 481 | 378 | 26.8697
MARIPOSA 2101 | 254452101 | CENTRAL VALLEY | YOSEMITE | 261.3822 | 909338.6667 | 40.3495 | 0% | 86.47% | 8.223% | 0.9472% | 8 | 3 | 223 | 84.61% | 12.03% | 23.6% | 172 | 1687 | 14 | 1 | 1903 | 292 | 5 | 33 | 54 | 5687 | 38.1209 | 914 | 417 | 33 | 2249 | 0 | 4 | 215 | 0 | 0.13837 | 9.8502 | 2.8455 | 3.8783 | Low | Medium | Low | Mid | 482 | 370 | 28.029
CURTIS 1705 | 163351705 | CENTRAL VALLEY | YOSEMITE | 84.8308 | 1039972 | 42.2644 | 0% | 22.69% | 56.89% | 4.67% | 6 | 1 | 144 | 78.75% | 14.77% | 3.447% | 333 | 1290 | 3 | 0 | 509 | 164 | 1 | 21 | 38 | 2321 | 22.3541 | 465 | 262 | 30 | 1105 | 0 | 0 | 142 | 0 | 0.12924 | 4.6492 | 6.3526 | 3.8172 | Low | Medium | High | Mid | 483 | 364 | 29.5347
BRYANT 0402 | 013090402 | BAY AREA | DIABLO | 1.5416 | 135820.3333 | 44.8026 | 0% | 38.71% | 10.43% | 50.86% | 2 | 0 | 2 | 3.005% | 96.99% | 23.68% | 31 | 17 | 0 | 0 | 29 | 1 | 0 | 0 | 0 | 76 | 42.2727 | 7 | 19 | 4 | 33 | 0 | 0 | 2 | 0 | 0.56816 | 1 | 6.7117 | 3.8133 | Medium | Low | High | Mid | 484 | 603 | 6.7117
PEORIA 1701 | 163781701 | CENTRAL VALLEY | YOSEMITE | 80.9793 | 522460 | 43.7626 | 0% | 41.46% | 28.14% | 2.464% | 6 | 3 | 94 | 70.58% | 3.53% | 4.754% | 408 | 811 | 3 | 0 | 296 | 287 | 10 | 9 | 35 | 1704 | 28.1064 | 256 | 177 | 21 | 684 | 0 | 0 | 93 | 0 | 0.18788 | 4.3409 | 4.6157 | 3.7645 | Low | Medium | Medium | Mid | 485 | 416 | 20.0363
IONE 1101 | 163881101 | CENTRAL VALLEY | STOCKTON | 16.9978 | 1124748.3333 | 42.5714 | 71.69% | 0% | 94.02% | 0% | 0 | 0 | 7 | 87.97% | 6.052% | 4.082% | 21 | 100 | 0 | 0 | 65 | 44 | 0 | 1 | 3 | 245 | 36.0345 | 26 | 12 | 2 | 61 | 0 | 0 | 7 | 0 | 0.17819 | 4.7899 | 4.4058 | 3.7604 | Low | Medium | Medium | Mid | 486 | 404 | 21.1036
OAKLAND J 1105 | 012091105 | BAY AREA | EAST BAY | 4.233 | 793234 | 44.6842 | 11.74% | 0% | 44.34% | 17.04% | 1 | 2 | 2 | 6.234% | 55.15% | 21.05% | 17 | 10 | 0 | 0 | 59 | 7 | 0 | 3 | 4 | 95 | 27.4615 | 6 | 12 | 7 | 27 | 0 | 0 | 2 | 0 | 0.61111 | 1 | 6.1504 | 3.7586 | Medium | Low | High | Mid | 487 | 628 | 6.1504
WISE 1101 | 152271101 | NORTHERN | SIERRA | 9.297 | 455854.6667 | 41.6791 | 51.02% | 0.3197% | 43.48% | 23.38% | 1 | 0 | 11 | 43.8% | 23.38% | 7.353% | 14 | 76 | 0 | 0 | 25 | 5 | 0 | 3 | 8 | 136 | 28.6667 | 22 | 12 | 1 | 55 | 0 | 0 | 11 | 0 | 0.50555 | 1.5447 | 4.7524 | 3.7113 | Medium | Low | Medium | Mid | 488 | 576 | 7.3411
WYANDOTTE 1105 | 102911105 | NORTHERN | NORTH VALLEY | 21.9604 | 306464.3333 | 41.028 | 95.88% | 0.04982% | 14.35% | 22.69% | 1 | 2 | 5 | 14.65% | 72.03% | 7.009% | 10 | 85 | 6 | 0 | 42 | 12 | 0 | 1 | 1 | 214 | 47.7627 | 30 | 8 | 0 | 64 | 0 | 1 | 5 | 1 | 0.59769 | 1.054 | 5.8853 | 3.7074 | Medium | Low | High | Mid | 489 | 626 | 6.2028
PAUL SWEET 2109 | 083252109 | CENTRAL COAST | CENTRAL COAST | 4.8379 | 921379.3333 | 44.5181 | 6.578% | 0.1206% | 62.21% | 29.35% | 0 | 1 | 8 | 63.94% | 30.95% | 9.639% | 12 | 40 | 0 | 1 | 27 | 8 | 0 | 2 | 2 | 83 | 39.5957 | 16 | 10 | 3 | 47 | 1 | 0 | 8 | 1 | 0.55732 | 1 | 6.6296 | 3.6948 | Medium | Low | High | Mid | 490 | 609 | 6.6296
SNEATH LANE 1101 | 022721101 | CENTRAL COAST | PENINSULA | 3.4169 | 423290.3333 | 42.5287 | 25.96% | 6.254% | 33.09% | 28.1% | 3 | 1 | 3 | 37.01% | 45.54% | 0% | 6 | 6 | 0 | 0 | 78 | 1 | 0 | 1 | 5 | 87 | 22.4286 | 9 | 13 | 4 | 29 | 0 | 0 | 3 | 1 | 0.65732 | 1 | 5.5993 | 3.6805 | Medium | Low | High | Mid | 491 | 663 | 5.5993
PEORIA 1704 | 163781704 | CENTRAL VALLEY | YOSEMITE | 69.8555 | 1152041.6667 | 42.2251 | 0% | 1.12% | 67.14% | 0.2721% | 2 | 1 | 42 | 66.78% | 16.39% | 5.376% | 215 | 651 | 0 | 0 | 269 | 197 | 0 | 14 | 36 | 1358 | 44.3532 | 198 | 105 | 11 | 425 | 0 | 0 | 41 | 0 | 0.15653 | 5.0902 | 4.6091 | 3.6724 | Low | Medium | Medium | Mid | 492 | 390 | 23.4613
SARATOGA 1105 | 083371105 | CENTRAL COAST | DE ANZA | 9.944 | 515332 | 44.3932 | 22.52% | 0.1397% | 67.73% | 19.61% | 1 | 0 | 36 | 68.56% | 19.61% | 10.68% | 52 | 50 | 0 | 1 | 101 | 12 | 0 | 10 | 16 | 206 | 4.8586 | 28 | 23 | 13 | 103 | 0 | 0 | 35 | 1 | 0.61503 | 1 | 5.9343 | 3.6498 | Medium | Low | High | Mid | 493 | 636 | 5.9343
SOBRANTE 1101 | 014671101 | BAY AREA | DIABLO | 16.0465 | 881948 | 45.22 | 69.58% | 1.748% | 33.94% | 22.64% | 7 | 0 | 34 | 24.53% | 33.92% | 34.66% | 179 | 102 | 0 | 0 | 235 | 16 | 0 | 6 | 21 | 502 | 27.0992 | 80 | 107 | 25 | 261 | 0 | 0 | 34 | 0 | 0.50746 | 1.13 | 6.3636 | 3.6492 | Medium | Low | High | Mid | 494 | 578 | 7.1911
SHINGLE SPRINGS 1104 | 153651104 | NORTHERN | SIERRA | 44.414 | 484282.3333 | 43.6518 | 33.15% | 1.429% | 96.25% | 0% | 2 | 2 | 36 | 98.43% | 0% | 1.228% | 116 | 539 | 17 | 0 | 183 | 41 | 4 | 6 | 8 | 1059 | 46.4609 | 160 | 204 | 21 | 456 | 0 | 0 | 36 | 0 | 0.069469 | 11.3519 | 4.6197 | 3.6432 | Low | Medium | Medium | Mid | 495 | 253 | 52.443
AUBERRY 1101 | 254151101 | CENTRAL VALLEY | FRESNO | 243.6273 | 954361.6667 | 40.614 | 47% | 27.66% | 65.22% | 2.352% | 27 | 2 | 260 | 92.44% | 2.791% | 25.83% | 179 | 468 | 3 | 533 | 1555 | 514 | 3 | 43 | 76 | 4583 | 14.7982 | 938 | 344 | 27 | 2021 | 0 | 6 | 260 | 0 | 0.21545 | 7.1086 | 2.3763 | 3.6394 | Low | Medium | Low | Mid | 496 | 444 | 16.8922
SONOMA 1106 | 042721106 | NORTHERN | SONOMA | 1.2651 | 969903.6667 | 42.8125 | 19.52% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 0% | 1 | 0 | 0 | 0 | 8 | 5 | 0 | 0 | 0 | 16 | 22.4 | 2 | 1 | 0 | 5 | 0 | 0 | 1 | 0 | 0.20325 | 3.2426 | 5.5195 | 3.6377 | Low | Medium | High | Mid | 497 | 437 | 17.8977
SAN RAFAEL 1105 | 042011105 | BAY AREA | NORTH BAY | 5.2298 | 1166879 | 43.9333 | 3.422% | 0% | 61.54% | 24.22% | 2 | 0 | 10 | 61.49% | 24.28% | 5.333% | 10 | 21 | 0 | 1 | 36 | 6 | 0 | 2 | 3 | 75 | 22.1 | 6 | 10 | 3 | 30 | 0 | 0 | 10 | 0 | 0.47677 | 1 | 7.6239 | 3.6348 | Medium | Low | High | Mid | 498 | 567 | 7.6239
VINEYARD 2107 | 014502107 | CENTRAL COAST | MISSION | 1.9947 | 1499744.3333 | 43.0233 | 12.4% | 0% | 50.79% | 49.21% | 0 | 1 | 10 | 50.79% | 49.21% | 13.95% | 5 | 36 | 0 | 1 | 26 | 3 | 0 | 3 | 4 | 86 | 20.973 | 14 | 20 | 0 | 40 | 0 | 0 | 10 | 1 | 0.69409 | 1 | 5.2344 | 3.6331 | High | Low | Medium | Mid | 499 | 685 | 5.2344
WHITMORE 1101 | 103601101 | NORTHERN | NORTH VALLEY | 92.5696 | 144177 | 40.5451 | 32.28% | 71.28% | 21.05% | 1.318% | 6 | 0 | 84 | 83.16% | 10.49% | 8.126% | 178 | 999 | 54 | 0 | 485 | 144 | 0 | 13 | 26 | 2006 | 37.5782 | 191 | 65 | 5 | 451 | 0 | 2 | 83 | 0 | 0.064368 | 25.3433 | 2.1627 | 3.528 | Low | High | Low | Mid | 500 | 240 | 54.8096
OAKLAND X 1105 | 012541105 | BAY AREA | EAST BAY | 4.3515 | 707029.6667 | 44.5041 | 18.3% | 0% | 68.95% | 30.73% | 1 | 1 | 2 | 20.97% | 79.03% | 36.59% | 26 | 17 | 0 | 2 | 77 | 17 | 16 | 1 | 1 | 123 | 15.6053 | 5 | 18 | 6 | 38 | 0 | 0 | 2 | 0 | 0.53834 | 1 | 6.5414 | 3.5215 | Medium | Low | High | Mid | 501 | 614 | 6.5414
SARATOGA 1115 | 083371115 | CENTRAL COAST | DE ANZA | 2.7261 | 861060.6667 | 43.0137 | 15.13% | 0% | 38.53% | 57.64% | 2 | 0 | 10 | 38.53% | 61.47% | 13.7% | 15 | 21 | 1 | 0 | 37 | 5 | 0 | 1 | 1 | 73 | 1.8684 | 9 | 8 | 2 | 38 | 0 | 0 | 9 | 0 | 0.60994 | 1 | 5.7678 | 3.518 | Medium | Low | High | Mid | 502 | 650 | 5.7678
SOLEDAD 2102 | 182052102 | CENTRAL COAST | CENTRAL COAST | 31.2821 | 1529844.6667 | 39.7018 | 81.38% | 0% | 83.82% | 14.88% | 3 | 1 | 7 | 83.17% | 15.53% | 6.818% | 9 | 56 | 0 | 2 | 60 | 15 | 0 | 4 | 5 | 220 | 27.9425 | 19 | 7 | 1 | 97 | 0 | 0 | 7 | 0 | 0.2142 | 18.3454 | 0.8933 | 3.5103 | Low | High | Low | Mid | 503 | 447 | 16.3879
EL CERRITO G 1110 | 012501110 | BAY AREA | EAST BAY | 2.1358 | 453257.6667 | 47.3438 | 70.74% | 0.1331% | 23.71% | 1.212% | 2 | 1 | 2 | 9.408% | 41.43% | 46.88% | 14 | 6 | 0 | 1 | 13 | 0 | 2 | 1 | 2 | 32 | 11 | 0 | 1 | 0 | 3 | 0 | 0 | 2 | 0 | 0.4024 | 1 | 8.6693 | 3.4885 | Medium | Low | High | Mid | 504 | 536 | 8.6693
HOLLYWOOD 0401 | 013170401 | BAY AREA | EAST BAY | 3.0693 | 172815 | 47.0073 | 0% | 5.048% | 50.61% | 12.22% | 0 | 0 | 8 | 0% | 100% | 62.77% | 57 | 17 | 0 | 0 | 63 | 2 | 6 | 3 | 7 | 137 | 42.7857 | 4 | 15 | 10 | 42 | 0 | 0 | 8 | 0 | 0.51878 | 1 | 6.6406 | 3.445 | Medium | Low | High | Mid | 505 | 608 | 6.6406
PIT NO 5 1101 | 101321101 | NORTHERN | NORTH VALLEY | 23.7942 | 22337.3333 | 43.757 | 97.46% | 51.05% | 3.644% | 0% | 4 | 1 | 18 | 82.26% | 13.75% | 12.38% | 138 | 153 | 4 | 1 | 200 | 74 | 4 | 13 | 26 | 541 | 25.9595 | 24 | 12 | 2 | 86 | 0 | 3 | 18 | 0 | 0.41374 | 10.1216 | 0.82163 | 3.4407 | Medium | Medium | Low | Mid | 506 | 546 | 8.3162
MORRO BAY 1102 | 183011102 | CENTRAL COAST | LOS PADRES | 22.9719 | 1059852 | 40.6152 | 47.97% | 1.978% | 7.314% | 71.06% | 2 | 0 | 42 | 9.464% | 79.15% | 7.58% | 30 | 25 | 0 | 36 | 189 | 27 | 8 | 8 | 10 | 343 | 24.2749 | 67 | 24 | 19 | 178 | 0 | 0 | 42 | 0 | 0.48819 | 1.0414 | 6.7615 | 3.4375 | Medium | Low | High | Mid | 507 | 583 | 7.0412
BAY MEADOWS 2102 | 024012102 | CENTRAL COAST | PENINSULA | 4.3938 | 1456927.6667 | 45.2119 | 33.71% | 0% | 37.33% | 2.397% | 7 | 0 | 9 | 27.78% | 13.79% | 11.86% | 24 | 29 | 1 | 1 | 67 | 11 | 0 | 3 | 8 | 118 | 28.5435 | 17 | 10 | 6 | 49 | 1 | 0 | 9 | 1 | 0.63615 | 1 | 5.3811 | 3.4232 | Medium | Low | High | Mid | 508 | 674 | 5.3811
UKIAH 1115 | 042771115 | NORTHERN | HUMBOLDT | 18.3 | 313014.3333 | 44.1337 | 0% | 3.584% | 71.18% | 13.35% | 2 | 0 | 18 | 74.77% | 17.33% | 5.185% | 96 | 150 | 0 | 1 | 124 | 65 | 0 | 10 | 11 | 405 | 37.3867 | 57 | 65 | 5 | 184 | 0 | 0 | 18 | 0 | 0.27079 | 4.5889 | 2.7266 | 3.3882 | Low | Medium | Low | Mid | 509 | 488 | 12.5122
OILFIELDS 1103 | 182391103 | CENTRAL COAST | CENTRAL COAST | 117.8387 | 676842 | 41.8217 | 59.82% | 7.064% | 80.84% | 0.0615% | 2 | 0 | 99 | 90.89% | 0.3467% | 8.601% | 74 | 195 | 1 | 319 | 370 | 80 | 0 | 24 | 37 | 1151 | 33.2937 | 112 | 68 | 8 | 446 | 0 | 0 | 99 | 0 | 0.078838 | 11.8293 | 3.6117 | 3.3683 | Low | Medium | Low | Mid | 510 | 296 | 42.7243
FULTON 1104 | 042561104 | NORTHERN | SONOMA | 0.58254 | 862530 | 48.3333 | 5.146% | 0% | 77.78% | 22.22% | 0 | 0 | 1 | 77.78% | 22.22% | 16.67% | 5 | 3 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 6 | 41.6 | 3 | 1 | 0 | 5 | 0 | 0 | 1 | 1 | 0.36699 | 2.2972 | 3.9527 | 3.3323 | Medium | Low | Medium | Mid | 511 | 523 | 9.0801
TIDEWATER 2106 | 014652106 | BAY AREA | DIABLO | 9.2683 | 1632499.3333 | 44.5088 | 0% | 0% | 11.65% | 21.24% | 1 | 0 | 4 | 14.27% | 21.24% | 39.47% | 15 | 25 | 0 | 0 | 25 | 10 | 0 | 0 | 0 | 114 | 46.9231 | 5 | 7 | 5 | 30 | 0 | 0 | 4 | 0 | 0.5414 | 1.1373 | 5.3892 | 3.3182 | Medium | Low | High | Mid | 512 | 631 | 6.129
TEMPLETON 2111 | 183052111 | CENTRAL COAST | LOS PADRES | 46.5161 | 707863.3333 | 43.1801 | 13.41% | 0.03222% | 76.19% | 14.78% | 10 | 1 | 87 | 76.19% | 19.38% | 7.533% | 134 | 67 | 2 | 202 | 359 | 201 | 0 | 14 | 19 | 1062 | 52.0586 | 242 | 184 | 19 | 547 | 0 | 1 | 87 | 0 | 0.29919 | 2.8834 | 3.7852 | 3.2654 | Low | Medium | Medium | Mid | 513 | 504 | 10.9143
FAIRVIEW 2207 | 013432207 | BAY AREA | DIABLO | 19.4269 | 1298953.3333 | 45.1845 | 0% | 5.883% | 33.15% | 20.54% | 2 | 3 | 24 | 18.87% | 51.21% | 13.57% | 110 | 168 | 0 | 1 | 148 | 8 | 22 | 12 | 35 | 516 | 29.1304 | 31 | 47 | 16 | 127 | 0 | 1 | 24 | 0 | 0.56089 | 1 | 5.8156 | 3.2619 | Medium | Low | High | Mid | 514 | 648 | 5.8156
ARLINGTON 0401 | 013700401 | BAY AREA | EAST BAY | 0.87294 | 79259.3333 | 45.2174 | 14.3% | 0% | 10.82% | 10.92% | 0 | 0 | 1 | 0% | 100% | 65.22% | 1 | 1 | 0 | 0 | 18 | 1 | 8 | 0 | 1 | 23 | 35.1818 | 2 | 4 | 2 | 11 | 0 | 0 | 1 | 0 | 0.41135 | 1 | 7.8902 | 3.2456 | Medium | Low | High | Mid | 515 | 560 | 7.8902
HICKS 1116 | 083431116 | CENTRAL COAST | SAN JOSE | 11.3852 | 890645.3333 | 43.0429 | 1.727% | 1.957% | 55.88% | 39.91% | 5 | 0 | 50 | 57.84% | 39.91% | 10.13% | 79 | 100 | 0 | 1 | 184 | 20 | 0 | 6 | 11 | 375 | 3.5269 | 49 | 80 | 15 | 190 | 0 | 0 | 50 | 0 | 0.54573 | 1 | 5.923 | 3.2323 | Medium | Low | High | Mid | 516 | 638 | 5.923
SAN LEANDRO U 1109 | 013111109 | CENTRAL COAST | MISSION | 13.1527 | 1027629.6667 | 44.4837 | 20.73% | 2.227% | 41.32% | 36.26% | 6 | 2 | 28 | 37.43% | 43.23% | 18.93% | 57 | 68 | 0 | 2 | 287 | 12 | 3 | 17 | 21 | 523 | 22.1133 | 37 | 68 | 21 | 156 | 0 | 0 | 28 | 0 | 0.73818 | 1 | 4.3591 | 3.2178 | High | Low | Medium | Mid | 517 | 725 | 4.3591
TAR FLAT 0402 | 163240402 | CENTRAL VALLEY | YOSEMITE | 5.7251 | 92911.3333 | 42.6374 | 0% | 0% | 24.67% | 60.03% | 0 | 0 | 4 | 24.18% | 71.75% | 5.464% | 26 | 85 | 0 | 0 | 53 | 22 | 0 | 0 | 0 | 183 | 37.6418 | 16 | 30 | 8 | 73 | 0 | 0 | 4 | 0 | 0.51697 | 1.162 | 5.2879 | 3.1764 | Medium | Low | Medium | Mid | 518 | 629 | 6.1443
SNEATH LANE 1106 | 022721106 | CENTRAL COAST | PENINSULA | 2.2996 | 639751.6667 | 42.5 | 30.17% | 0% | 43.71% | 15.94% | 6 | 0 | 6 | 43.71% | 19.05% | 8% | 4 | 10 | 0 | 0 | 34 | 0 | 0 | 3 | 8 | 50 | 38.2 | 2 | 5 | 3 | 18 | 0 | 0 | 6 | 1 | 0.58134 | 1 | 5.4125 | 3.1465 | Medium | Low | High | Mid | 519 | 672 | 5.4125
OLETA 1101 | 163541101 | CENTRAL VALLEY | STOCKTON | 91.7582 | 636401.6667 | 43.7272 | 66.43% | 3.039% | 81.21% | 9.707% | 4 | 2 | 49 | 79.19% | 15.36% | 3.26% | 294 | 946 | 0 | 0 | 430 | 145 | 0 | 7 | 23 | 1810 | 37.0636 | 252 | 118 | 10 | 522 | 0 | 6 | 48 | 0 | 0.061666 | 9.7544 | 5.1735 | 3.1119 | Low | Medium | Medium | Mid | 520 | 266 | 50.4642
SAN LEANDRO U 1114 | 013111114 | CENTRAL COAST | MISSION | 15.182 | 1226301 | 43.9513 | 28.75% | 0.1848% | 49.53% | 42.91% | 4 | 1 | 30 | 37.32% | 55.94% | 17.69% | 41 | 73 | 1 | 3 | 204 | 9 | 0 | 4 | 6 | 390 | 22.0924 | 26 | 56 | 14 | 125 | 0 | 0 | 30 | 0 | 0.6688 | 1 | 4.5847 | 3.0663 | High | Low | Medium | Mid | 521 | 714 | 4.5847
MC KEE 1107 | 083531107 | CENTRAL COAST | SAN JOSE | 2.8856 | 977403 | 43.5849 | 9.903% | 0% | 82.84% | 11.1% | 1 | 0 | 6 | 82.84% | 14.34% | 9.434% | 8 | 22 | 0 | 0 | 17 | 3 | 0 | 0 | 1 | 53 | 0 | 6 | 6 | 0 | 24 | 0 | 0 | 6 | 0 | 0.20895 | 4.9293 | 2.9617 | 3.0505 | Low | Medium | Low | Mid | 522 | 467 | 14.5991
COTTONWOOD 1103 | 102931103 | NORTHERN | NORTH VALLEY | 129.5388 | 1086587.3333 | 42.5679 | 51.9% | 49.26% | 45.06% | 4.398% | 5 | 0 | 88 | 94.32% | 4.398% | 9.656% | 293 | 1624 | 109 | 0 | 547 | 468 | 0 | 21 | 30 | 3252 | 52.9558 | 472 | 306 | 36 | 1127 | 0 | 5 | 88 | 0 | 0.082078 | 10.5165 | 3.5227 | 3.0407 | Low | Medium | Low | Mid | 523 | 319 | 37.0465
LAS PULGAS 0401 | 024120401 | CENTRAL COAST | PENINSULA | 0.12527 | 193094.3333 | 43.3333 | 39.18% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 6.667% | 1 | 2 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 15 | 87.7143 | 0 | 4 | 1 | 7 | 0 | 0 | 0 | 1 | 0.33866 | 1 | 8.9603 | 3.0345 | Medium | Low | High | Mid | 524 | 525 | 8.9603
FAIRMOUNT 0401 | 012650401 | BAY AREA | EAST BAY | 1.5131 | 126678 | 44.8611 | 31.51% | 0% | 89.61% | 3.405% | 2 | 0 | 3 | 0% | 100% | 51.39% | 2 | 7 | 0 | 0 | 7 | 1 | 0 | 1 | 2 | 72 | 37.9 | 2 | 11 | 4 | 21 | 0 | 0 | 3 | 0 | 0.34629 | 1 | 8.7552 | 3.0318 | Medium | Low | High | Mid | 525 | 533 | 8.7552
HORSESHOE 1101 | 152571101 | NORTHERN | SIERRA | 7.1108 | 675190 | 44.3243 | 32.3% | 0% | 61.55% | 2.707% | 0 | 0 | 11 | 61.55% | 2.707% | 2.703% | 13 | 79 | 0 | 0 | 8 | 3 | 0 | 2 | 8 | 111 | 44.2979 | 20 | 19 | 2 | 48 | 0 | 0 | 11 | 1 | 0.48077 | 1 | 6.2542 | 3.0068 | Medium | Low | High | Mid | 526 | 624 | 6.2542
MONTEREY 0402 | 182090402 | CENTRAL COAST | CENTRAL COAST | 0.9685 | 192008.6667 | 43.6842 | 38.49% | 29.84% | 0% | 41.97% | 0 | 0 | 1 | 0% | 75.46% | 42.11% | 0 | 4 | 0 | 0 | 17 | 1 | 0 | 0 | 0 | 38 | 69.5 | 2 | 4 | 1 | 10 | 0 | 0 | 1 | 1 | 0.50618 | 1 | 5.8785 | 2.9756 | Medium | Low | High | Mid | 527 | 642 | 5.8785
SAN JOAQUIN #3 1103 | 252531103 | CENTRAL VALLEY | YOSEMITE | 54.5173 | 0 | 40.4287 | 67.87% | 75.5% | 18.68% | 0.2307% | 3 | 4 | 33 | 85.23% | 9.182% | 23.94% | 37 | 214 | 0 | 1 | 491 | 56 | 14 | 5 | 8 | 1207 | 22.7551 | 195 | 69 | 12 | 526 | 0 | 0 | 32 | 0 | 0.26462 | 4.374 | 2.5612 | 2.9644 | Low | Medium | Low | Mid | 528 | 499 | 11.2024
CLAY 1101 | 163341101 | CENTRAL VALLEY | STOCKTON | 27.9248 | 622525 | 43.6759 | 32.66% | 0.6155% | 97.09% | 2.108% | 3 | 0 | 16 | 94.58% | 5.239% | 7.011% | 95 | 282 | 1 | 0 | 100 | 62 | 0 | 1 | 6 | 542 | 31.2308 | 71 | 41 | 1 | 162 | 0 | 1 | 16 | 0 | 0.13945 | 4.2814 | 4.9572 | 2.9597 | Low | Medium | Medium | Mid | 529 | 403 | 21.2237
CALAVERAS CEMENT 1101 | 162211101 | CENTRAL VALLEY | STOCKTON | 192.3056 | 882692.6667 | 43.0491 | 42.52% | 48.89% | 42.65% | 1.271% | 10 | 1 | 229 | 86.35% | 7.593% | 6.122% | 504 | 1805 | 8 | 0 | 1129 | 294 | 0 | 32 | 66 | 3822 | 26.369 | 644 | 228 | 15 | 1430 | 0 | 8 | 227 | 0 | 0.12984 | 5.1692 | 4.3663 | 2.9306 | Low | Medium | Medium | Mid | 530 | 395 | 22.5704
TYLER 1105 | 103571105 | NORTHERN | NORTH VALLEY | 62.3352 | 607112 | 41.0656 | 34.33% | 0.1812% | 99.82% | 0% | 3 | 0 | 26 | 100% | 0% | 6.205% | 53 | 627 | 28 | 2 | 222 | 94 | 0 | 7 | 8 | 1241 | 43.4947 | 118 | 44 | 3 | 295 | 0 | 0 | 26 | 0 | 0.096827 | 14.6898 | 2.0602 | 2.9304 | Low | High | Low | Mid | 531 | 362 | 30.2643
PENRYN 1105 | 152561105 | NORTHERN | SIERRA | 43.6524 | 716362.3333 | 42.7881 | 33.94% | 1.216% | 59.25% | 20.65% | 7 | 0 | 74 | 57.51% | 24.36% | 9.292% | 86 | 501 | 2 | 1 | 109 | 67 | 0 | 5 | 11 | 861 | 30.2798 | 165 | 112 | 9 | 375 | 0 | 0 | 74 | 0 | 0.34134 | 2.0241 | 4.2125 | 2.9105 | Medium | Low | Medium | Mid | 532 | 542 | 8.5266
AUBURN 1102 | 152161102 | NORTHERN | SIERRA | 2.613 | 435039 | 42.4 | 11.25% | 0% | 47.57% | 52.43% | 0 | 0 | 6 | 22.24% | 77.76% | 6.349% | 26 | 82 | 0 | 0 | 24 | 10 | 4 | 0 | 0 | 126 | 36.9818 | 25 | 10 | 8 | 55 | 0 | 0 | 6 | 0 | 0.57566 | 1 | 5.0497 | 2.9069 | Medium | Low | Medium | Mid | 533 | 699 | 5.0497
PEORIA 1705 | 163781705 | CENTRAL VALLEY | YOSEMITE | 61.6661 | 839391 | 43.4978 | 0% | 0.3851% | 69.22% | 7.749% | 2 | 1 | 58 | 68.93% | 10.16% | 3.057% | 243 | 767 | 1 | 0 | 254 | 114 | 4 | 10 | 24 | 1374 | 25.0452 | 203 | 90 | 10 | 516 | 0 | 0 | 58 | 0 | 0.12715 | 4.6382 | 4.8512 | 2.861 | Low | Medium | Medium | Mid | 534 | 397 | 22.5006
MC KEE 1108 | 083531108 | CENTRAL COAST | SAN JOSE | 1.0836 | 1053694.6667 | 44.6154 | 3.935% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 3 | 8 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 13 | 12.5 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0.23714 | 3.7762 | 3.1908 | 2.8573 | Low | Medium | Low | Mid | 535 | 491 | 12.0489
DIVIDE 1103 | 182571103 | CENTRAL COAST | LOS PADRES | 2.3909 | 265550 | 42.1918 | 11.28% | 0% | 30.11% | 67.53% | 1 | 0 | 3 | 30.11% | 66.02% | 0% | 16 | 4 | 0 | 5 | 53 | 7 | 0 | 0 | 0 | 78 | 25.2778 | 6 | 3 | 0 | 19 | 0 | 0 | 3 | 1 | 0.55177 | 1 | 5.17 | 2.8526 | Medium | Low | Medium | Mid | 536 | 693 | 5.17
FRANKLIN 1104 | 013921104 | BAY AREA | EAST BAY | 7.4881 | 983534.6667 | 48.2593 | 0% | 33.02% | 23.93% | 13.79% | 0 | 0 | 9 | 23.93% | 58.85% | 17.99% | 81 | 36 | 0 | 9 | 30 | 5 | 0 | 2 | 6 | 139 | 16.2917 | 10 | 6 | 1 | 29 | 0 | 0 | 9 | 0 | 0.47096 | 1 | 6.0394 | 2.8443 | Medium | Low | High | Mid | 537 | 634 | 6.0394
VACAVILLE 1109 | 063601109 | NORTHERN | SACRAMENTO | 0.50066 | 930867.3333 | 46.1111 | 51.41% | 0% | 12.32% | 87.68% | 0 | 0 | 0 | 12.32% | 87.68% | 10% | 5 | 0 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 10 | 37.3333 | 1 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0.15986 | 4.149 | 4.2802 | 2.8388 | Low | Medium | Medium | Mid | 538 | 439 | 17.7584
CEDAR CREEK 1101 | 103321101 | NORTHERN | NORTH VALLEY | 110.9 | 178675 | 41.2931 | 29.15% | 83.75% | 15.51% | 0% | 9 | 0 | 76 | 99.07% | 0.9185% | 15.51% | 78 | 1036 | 205 | 1 | 384 | 354 | 3 | 13 | 23 | 2527 | 36.609 | 236 | 81 | 5 | 596 | 0 | 2 | 76 | 0 | 0.17084 | 10.4136 | 1.5854 | 2.8205 | Low | Medium | Low | Mid | 539 | 446 | 16.5097
CHESTER 1102 | 103181102 | NORTHERN | NORTH VALLEY | 2.5304 | 123687.6667 | 43.4375 | 63.74% | 98.2% | 0% | 1.801% | 5 | 0 | 6 | 98.2% | 1.801% | 17.65% | 5 | 1 | 2 | 0 | 15 | 6 | 0 | 2 | 3 | 68 | 30.1111 | 3 | 3 | 3 | 10 | 0 | 0 | 6 | 1 | 0.63055 | 1 | 4.408 | 2.7794 | Medium | Low | Medium | Mid | 540 | 722 | 4.408
FROGTOWN 1702 | 163451702 | CENTRAL VALLEY | STOCKTON | 241.6432 | 1521660.3333 | 42.5691 | 36.1% | 2.94% | 84.05% | 3.711% | 7 | 1 | 127 | 77.02% | 15.61% | 4.634% | 533 | 2297 | 3 | 0 | 982 | 258 | 0 | 22 | 44 | 4618 | 28.5008 | 568 | 205 | 5 | 1292 | 0 | 1 | 127 | 0 | 0.08854 | 6.9375 | 4.5015 | 2.765 | Low | Medium | Medium | Mid | 541 | 355 | 31.2292
RINCON 1104 | 043321104 | NORTHERN | SONOMA | 2.7394 | 1072176.6667 | 42.5 | 124.6% | 0% | 21.97% | 15.06% | 2 | 1 | 8 | 21.97% | 15.06% | 20.31% | 11 | 24 | 0 | 0 | 26 | 8 | 0 | 4 | 6 | 64 | 38.6774 | 7 | 11 | 6 | 31 | 0 | 0 | 8 | 1 | 0.65299 | 1 | 4.2342 | 2.7649 | Medium | Low | Medium | Bottom | 542 | 732 | 4.2342
AUBURN 1101 | 152161101 | NORTHERN | SIERRA | 3.3599 | 215030.6667 | 44.5122 | 22.65% | 35.45% | 30.38% | 32.38% | 0 | 0 | 5 | 24.3% | 75.7% | 4.839% | 33 | 73 | 0 | 0 | 26 | 2 | 0 | 0 | 0 | 124 | 27.6111 | 22 | 16 | 8 | 56 | 0 | 0 | 5 | 0 | 0.52955 | 1 | 5.2096 | 2.7587 | Medium | Low | Medium | Bottom | 543 | 689 | 5.2096
WYANDOTTE 1102 | 102911102 | NORTHERN | NORTH VALLEY | 5.4206 | 1395187 | 43.9773 | 194% | 1.413% | 56.1% | 42.49% | 1 | 0 | 1 | 57.51% | 42.49% | 13.64% | 16 | 28 | 0 | 0 | 18 | 7 | 0 | 1 | 1 | 88 | 36.1875 | 6 | 4 | 1 | 19 | 0 | 0 | 1 | 0 | 0.46516 | 1 | 5.8389 | 2.716 | Medium | Low | High | Bottom | 544 | 645 | 5.8389
OAKLAND X 1101 | 012541101 | BAY AREA | EAST BAY | 0.53647 | 356371.6667 | 46.3462 | 2.387% | 0% | 23.35% | 23.76% | 0 | 0 | 0 | 23.35% | 67.92% | 19.23% | 11 | 2 | 0 | 1 | 14 | 3 | 0 | 2 | 4 | 26 | 26.875 | 2 | 4 | 1 | 8 | 0 | 0 | 0 | 0 | 0.39383 | 1 | 6.8698 | 2.7056 | Medium | Low | High | Bottom | 545 | 591 | 6.8698
BALCH NO 1 1101 | 252501101 | CENTRAL VALLEY | FRESNO | 14.6983 | 2345.3333 | 47.069 | 38.08% | 78.09% | 10.35% | 3.548% | 0 | 0 | 5 | 79.6% | 20.4% | 5.83% | 135 | 8 | 0 | 2 | 144 | 12 | 0 | 3 | 6 | 223 | 7.4444 | 5 | 1 | 2 | 21 | 0 | 0 | 5 | 0 | 0.31373 | 5.294 | 1.6177 | 2.6869 | Low | Medium | Low | Bottom | 546 | 539 | 8.5641
HOPLAND 1101 | 042251101 | NORTHERN | HUMBOLDT | 91.6366 | 662550 | 44.0373 | 35.32% | 10.05% | 75.48% | 12.02% | 2 | 0 | 44 | 80.88% | 16.66% | 13.03% | 257 | 408 | 1 | 4 | 291 | 150 | 0 | 5 | 7 | 1305 | 42.4963 | 142 | 55 | 15 | 433 | 0 | 0 | 44 | 0 | 0.08993 | 13.7277 | 2.1763 | 2.6867 | Low | High | Low | Bottom | 547 | 363 | 29.8751
MARTELL 1103 | 163011103 | CENTRAL VALLEY | STOCKTON | 20.9115 | 861488.3333 | 45.9909 | 28.77% | 4.141% | 64.78% | 4.509% | 0 | 0 | 17 | 79.74% | 8.434% | 4.989% | 104 | 172 | 1 | 0 | 124 | 76 | 0 | 4 | 5 | 441 | 35.2474 | 52 | 20 | 1 | 105 | 0 | 0 | 17 | 0 | 0.14531 | 3.6373 | 5.0111 | 2.6486 | Low | Medium | Medium | Bottom | 548 | 434 | 18.2269
COARSEGOLD 2104 | 254432104 | CENTRAL VALLEY | YOSEMITE | 249.6433 | 1435361.3333 | 40.5176 | 78.07% | 8.356% | 78.34% | 4.366% | 6 | 0 | 156 | 87.23% | 7.592% | 30.19% | 204 | 744 | 0 | 1 | 2019 | 429 | 11 | 25 | 39 | 4995 | 28.9785 | 762 | 876 | 95 | 2380 | 0 | 0 | 155 | 0 | 0.14241 | 4.7699 | 3.8787 | 2.6346 | Low | Medium | Medium | Bottom | 549 | 431 | 18.5007
LUCERNE 1103 | 043351103 | NORTHERN | HUMBOLDT | 33.4045 | 868095 | 44.6968 | 52.31% | 2.663% | 59.12% | 13.46% | 7 | 5 | 17 | 70.8% | 15.45% | 6.564% | 216 | 385 | 0 | 14 | 185 | 103 | 8 | 7 | 13 | 777 | 33.2283 | 133 | 72 | 18 | 317 | 0 | 0 | 17 | 0 | 0.28111 | 1.9423 | 4.8221 | 2.6329 | Low | Low | Medium | Bottom | 550 | 521 | 9.3662
PUTAH CREEK 1105 | 063681105 | NORTHERN | SACRAMENTO | 1.9567 | 900677 | 42.6562 | 13.07% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 3.03% | 9 | 23 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 33 | 69.8 | 1 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0.20027 | 42.6644 | 0.30666 | 2.6203 | Low | High | Low | Bottom | 551 | 484 | 13.0834
SNEATH LANE 1107 | 022721107 | CENTRAL COAST | PENINSULA | 3.0548 | 542027.6667 | 43.125 | 16.98% | 0% | 47.72% | 3.012% | 3 | 0 | 3 | 47.72% | 25.42% | 7.317% | 8 | 3 | 0 | 0 | 33 | 4 | 0 | 3 | 6 | 41 | 0 | 0 | 4 | 2 | 7 | 0 | 0 | 3 | 0 | 0.49868 | 1 | 5.241 | 2.6136 | Medium | Low | Medium | Bottom | 552 | 684 | 5.241
SANTA ROSA A 1107 | 042151107 | NORTHERN | SONOMA | 3.0424 | 623638.3333 | 45.6061 | 14.02% | 0% | 70.89% | 15.09% | 1 | 2 | 10 | 70.89% | 15.09% | 6.061% | 30 | 27 | 0 | 2 | 53 | 9 | 0 | 5 | 5 | 99 | 50.3784 | 6 | 13 | 5 | 37 | 0 | 0 | 10 | 1 | 0.57087 | 1 | 4.5577 | 2.6019 | Medium | Low | Medium | Bottom | 553 | 715 | 4.5577
DESCHUTES 1104 | 103351104 | NORTHERN | NORTH VALLEY | 84.9328 | 1165655 | 42.729 | 16.73% | 67.16% | 28.77% | 0% | 9 | 0 | 72 | 95.93% | 0% | 5.745% | 202 | 1450 | 45 | 1 | 180 | 201 | 0 | 6 | 12 | 2141 | 42.7229 | 367 | 252 | 14 | 810 | 0 | 1 | 72 | 0 | 0.12323 | 4.8181 | 4.3552 | 2.5858 | Low | Medium | Medium | Bottom | 554 | 405 | 20.9837
JARVIS 1108 | 013501108 | CENTRAL COAST | MISSION | 2.883 | 835206 | 41.2963 | 15.24% | 0.1315% | 50.79% | 48.89% | 0 | 0 | 6 | 34.3% | 65.38% | 7.407% | 2 | 5 | 0 | 0 | 18 | 0 | 0 | 1 | 1 | 27 | 14.1667 | 0 | 4 | 2 | 8 | 0 | 0 | 6 | 0 | 0.38853 | 1 | 6.6173 | 2.571 | Medium | Low | High | Bottom | 555 | 610 | 6.6173
CLARKSVILLE 2105 | 153612105 | NORTHERN | SIERRA | 11.2819 | 1512786 | 46.0406 | 96.87% | 0.3472% | 67.33% | 0.4438% | 0 | 0 | 8 | 67.68% | 0.4438% | 0.5% | 50 | 127 | 0 | 0 | 4 | 12 | 0 | 3 | 8 | 200 | 57.2407 | 22 | 20 | 5 | 54 | 0 | 0 | 8 | 0 | 0.25384 | 1.8669 | 5.3527 | 2.5366 | Low | Low | Medium | Bottom | 556 | 512 | 9.9932
CASTRO VALLEY 1104 | 014091104 | CENTRAL COAST | MISSION | 4.1983 | 925694.6667 | 43.25 | 16.78% | 0% | 46.38% | 24.52% | 0 | 0 | 5 | 8.709% | 63.59% | 6.931% | 6 | 20 | 0 | 0 | 61 | 2 | 0 | 1 | 3 | 101 | 9.6667 | 5 | 15 | 4 | 31 | 0 | 0 | 5 | 0 | 0.4875 | 1 | 5.1934 | 2.5318 | Medium | Low | Medium | Bottom | 557 | 692 | 5.1934
JARVIS 1110 | 013501110 | CENTRAL COAST | MISSION | 0.83431 | 874083.6667 | 0 | 3.699% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13589 | 2.5792 | 7.1237 | 2.4967 | Low | Medium | High | Bottom | 558 | 432 | 18.3733
KESWICK 1101 | 103451101 | NORTHERN | NORTH VALLEY | 52.2738 | 367563.6667 | 41.7379 | 46.35% | 52.86% | 31.75% | 1.08% | 4 | 1 | 55 | 82.79% | 13.43% | 8.664% | 177 | 666 | 75 | 0 | 249 | 131 | 0 | 18 | 36 | 1385 | 39.9348 | 136 | 92 | 10 | 367 | 0 | 2 | 54 | 0 | 0.076647 | 6.1074 | 5.2822 | 2.4727 | Low | Medium | Medium | Bottom | 559 | 344 | 32.2605
DIAMOND SPRINGS 1104 | 152261104 | NORTHERN | SIERRA | 15.1099 | 379179.6667 | 42.0509 | 34.6% | 39.88% | 33.95% | 17.87% | 4 | 0 | 24 | 63.86% | 27.84% | 0.2681% | 31 | 232 | 2 | 0 | 57 | 25 | 0 | 0 | 0 | 373 | 40.9058 | 65 | 43 | 2 | 141 | 0 | 0 | 24 | 0 | 0.33256 | 1.604 | 4.635 | 2.4724 | Medium | Low | Medium | Bottom | 560 | 573 | 7.4345
ANDERSON 1101 | 103261101 | NORTHERN | NORTH VALLEY | 10.7872 | 729481.3333 | 43.7986 | 50.24% | 33.96% | 39.57% | 0.4306% | 0 | 0 | 16 | 76.02% | 17.28% | 2.817% | 76 | 127 | 5 | 0 | 78 | 24 | 0 | 5 | 7 | 284 | 41.7361 | 19 | 16 | 4 | 77 | 0 | 0 | 16 | 0 | 0.24362 | 2.5234 | 4.0188 | 2.4705 | Low | Medium | Medium | Bottom | 561 | 511 | 10.141
OCEANO 1105 | 182601105 | CENTRAL COAST | LOS PADRES | 4.2689 | 1490372.6667 | 40.9722 | 23.17% | 4.358% | 11.27% | 54.32% | 0 | 0 | 2 | 1.35% | 68.6% | 19.44% | 3 | 2 | 0 | 3 | 20 | 6 | 0 | 4 | 5 | 36 | 17.4 | 3 | 2 | 3 | 11 | 0 | 0 | 2 | 0 | 0.46324 | 1 | 5.285 | 2.4483 | Medium | Low | Medium | Bottom | 562 | 679 | 5.285
OCEANO 1102 | 182601102 | CENTRAL COAST | LOS PADRES | 38.3364 | 0 | 42.0799 | 32.16% | 3.398% | 47.22% | 25.9% | 5 | 4 | 84 | 46.52% | 30.1% | 4.941% | 93 | 60 | 0 | 156 | 272 | 104 | 0 | 17 | 25 | 850 | 30.953 | 105 | 53 | 12 | 334 | 0 | 0 | 84 | 0 | 0.45559 | 1.1592 | 4.629 | 2.4447 | Medium | Low | Medium | Bottom | 563 | 677 | 5.3661
RALSTON 1101 | 024141101 | CENTRAL COAST | PENINSULA | 9.8432 | 1073316 | 44.1255 | 43.03% | 0% | 58.71% | 8.348% | 2 | 0 | 19 | 50.06% | 17.08% | 4.943% | 23 | 25 | 0 | 0 | 220 | 7 | 0 | 7 | 15 | 263 | 18.449 | 14 | 43 | 19 | 102 | 0 | 0 | 18 | 0 | 0.4125 | 1 | 5.8789 | 2.425 | Medium | Low | High | Bottom | 564 | 641 | 5.8789
PACIFICA 1101 | 022811101 | CENTRAL COAST | PENINSULA | 3.269 | 247844 | 42.5 | 32.81% | 0% | 49.98% | 0.5257% | 0 | 0 | 1 | 45.54% | 5.147% | 0% | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 4 | 52.4211 | 4 | 10 | 3 | 19 | 0 | 0 | 1 | 0 | 0.34121 | 1.1629 | 6.0989 | 2.42 | Medium | Low | High | Bottom | 565 | 582 | 7.0923
BURNEY 1101 | 103311101 | NORTHERN | NORTH VALLEY | 52.0491 | 536787 | 42.1151 | 32.24% | 82.94% | 2.126% | 0.1522% | 6 | 0 | 66 | 73.8% | 11.42% | 17.76% | 143 | 556 | 6 | 0 | 305 | 140 | 0 | 22 | 42 | 1470 | 26.4424 | 119 | 94 | 13 | 384 | 0 | 4 | 66 | 0 | 0.19288 | 4.8346 | 2.5914 | 2.4166 | Low | Medium | Low | Bottom | 566 | 486 | 12.5285
CALPELLA 1101 | 043411101 | NORTHERN | HUMBOLDT | 75.2133 | 522431.6667 | 44.3029 | 62.5% | 17.24% | 64.05% | 5.835% | 5 | 4 | 59 | 85.31% | 6.852% | 7.756% | 310 | 466 | 0 | 3 | 307 | 149 | 0 | 10 | 16 | 1212 | 42.6318 | 187 | 82 | 11 | 459 | 0 | 0 | 59 | 0 | 0.11846 | 8.5089 | 2.3965 | 2.4155 | Low | Medium | Low | Bottom | 567 | 410 | 20.3913
DIAMOND SPRINGS 1105 | 152261105 | NORTHERN | SIERRA | 128.5585 | 751877.6667 | 42.8131 | 36.02% | 7.677% | 75.25% | 4.002% | 11 | 3 | 137 | 81.54% | 5.39% | 2.246% | 384 | 1714 | 55 | 0 | 378 | 184 | 1 | 15 | 25 | 2939 | 42.0833 | 562 | 322 | 27 | 1100 | 0 | 3 | 137 | 0 | 0.089201 | 6.585 | 4.0987 | 2.4075 | Low | Medium | Medium | Bottom | 568 | 376 | 26.9898
LAKEWOOD 1102 | 013531102 | BAY AREA | DIABLO | 0.5008 | 379090.6667 | 38.3333 | 6.308% | 0% | 17.16% | 1.022% | 0 | 0 | 0 | 17.16% | 1.022% | 0% | 1 | 2 | 0 | 0 | 3 | 0 | 0 | 1 | 1 | 6 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0.40858 | 1 | 5.8765 | 2.401 | Medium | Low | High | Bottom | 569 | 643 | 5.8765
DEL MONTE 1101 | 182221101 | CENTRAL COAST | CENTRAL COAST | 0.22068 | 517133.6667 | 58.8462 | 97.1% | 0% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 13 | 25 | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.30013 | 1 | 7.9973 | 2.4002 | Low | Low | High | Bottom | 570 | 555 | 7.9973
DIAMOND SPRINGS 1107 | 152261107 | NORTHERN | SIERRA | 54.1952 | 1206886.3333 | 43.6342 | 17.79% | 13.78% | 72.19% | 2.187% | 3 | 0 | 81 | 85.78% | 2.386% | 0.3187% | 185 | 765 | 40 | 0 | 121 | 82 | 5 | 7 | 9 | 1255 | 46.2512 | 246 | 268 | 15 | 605 | 0 | 2 | 81 | 0 | 0.050584 | 11.5356 | 4.1074 | 2.3967 | Low | Medium | Medium | Bottom | 571 | 278 | 47.3811
ANDERSON 1103 | 103261103 | NORTHERN | NORTH VALLEY | 8.2733 | 374128.6667 | 42.6316 | 29.15% | 32.81% | 53.1% | 0% | 0 | 0 | 4 | 85.91% | 0% | 8.571% | 34 | 96 | 6 | 0 | 56 | 18 | 0 | 2 | 2 | 210 | 43.92 | 38 | 18 | 1 | 77 | 0 | 0 | 4 | 0 | 0.2342 | 2.6804 | 3.8114 | 2.3926 | Low | Medium | Medium | Bottom | 572 | 510 | 10.216
PIT NO 3 2101 | 103732101 | NORTHERN | NORTH VALLEY | 47.9266 | 228818 | 40.3882 | 81.88% | 48.93% | 15.56% | 0.328% | 2 | 1 | 18 | 63.08% | 27.99% | 28.61% | 49 | 420 | 6 | 0 | 206 | 61 | 5 | 17 | 36 | 1185 | 23.4096 | 26 | 18 | 2 | 95 | 0 | 2 | 18 | 0 | 0.27482 | 9.5194 | 0.91411 | 2.3914 | Low | Medium | Low | Bottom | 573 | 534 | 8.7018
PLACER 1102 | 152461102 | NORTHERN | SIERRA | 2.1407 | 8964.6667 | 44.9 | 150.8% | 0% | 15.97% | 28.73% | 0 | 0 | 7 | 18.98% | 28.73% | 0% | 18 | 30 | 0 | 0 | 13 | 3 | 0 | 1 | 2 | 50 | 33.15 | 8 | 5 | 0 | 20 | 0 | 0 | 7 | 0 | 0.45496 | 1 | 5.2537 | 2.3902 | Medium | Low | Medium | Bottom | 574 | 682 | 5.2537
WOODSIDE 1102 | 024251102 | CENTRAL COAST | PENINSULA | 0.12901 | 537438 | 40 | 0.2934% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 1 | 1 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 8 | 19.6667 | 0 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 0.27865 | 1 | 8.576 | 2.3897 | Low | Low | High | Bottom | 575 | 538 | 8.576
GIRVAN 1101 | 103401101 | NORTHERN | NORTH VALLEY | 107.3683 | 551410 | 41.9268 | 66.67% | 38.45% | 50.68% | 0.1729% | 2 | 0 | 88 | 92.96% | 0.3634% | 9.752% | 251 | 1261 | 70 | 3 | 450 | 209 | 17 | 19 | 30 | 2461 | 47.2913 | 314 | 242 | 19 | 761 | 0 | 4 | 88 | 0 | 0.065167 | 9.7381 | 3.7654 | 2.3895 | Low | Medium | Medium | Bottom | 576 | 322 | 36.6676
MARIPOSA 2102 | 254452102 | CENTRAL VALLEY | YOSEMITE | 248.8941 | 1035525 | 40.3388 | 57.51% | 50.91% | 44.57% | 0.08718% | 9 | 0 | 173 | 93.58% | 2.121% | 24.56% | 125 | 1484 | 0 | 4 | 1647 | 269 | 9 | 19 | 31 | 4739 | 43.5371 | 767 | 331 | 30 | 1884 | 0 | 2 | 171 | 0 | 0.1473 | 5.7432 | 2.8035 | 2.3716 | Low | Medium | Low | Bottom | 577 | 451 | 16.1011
SUMMIT 1102 | 152591102 | NORTHERN | SIERRA | 5.1556 | 79007.6667 | 44.9682 | 7.908% | 35.59% | 12.9% | 0% | 1 | 0 | 17 | 50.08% | 12.9% | 48.78% | 40 | 42 | 2 | 0 | 14 | 11 | 0 | 8 | 14 | 164 | 18.2 | 9 | 8 | 5 | 50 | 0 | 0 | 17 | 1 | 0.67488 | 1 | 3.4497 | 2.3281 | High | Low | Low | Bottom | 578 | 751 | 3.4497
OAKLAND J 1106 | 012091106 | BAY AREA | EAST BAY | 2.1598 | 785426.6667 | 44.6939 | 12.6% | 0% | 84.43% | 0% | 1 | 0 | 4 | 42.42% | 48.74% | 30.61% | 18 | 15 | 0 | 0 | 67 | 5 | 0 | 2 | 5 | 98 | 31.7273 | 5 | 9 | 3 | 24 | 0 | 0 | 4 | 0 | 0.40115 | 1 | 5.7729 | 2.3158 | Medium | Low | High | Bottom | 579 | 649 | 5.7729
ALTO 1123 | 042031123 | BAY AREA | NORTH BAY | 2.6839 | 971672 | 44 | 94.03% | 0% | 2.992% | 46.14% | 0 | 0 | 1 | 2.992% | 46.14% | 15% | 3 | 3 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 20 | 56 | 1 | 1 | 2 | 4 | 0 | 0 | 1 | 0 | 0.33055 | 1 | 6.9911 | 2.3109 | Medium | Low | High | Bottom | 580 | 586 | 6.9911
CORNING 1101 | 103331101 | NORTHERN | NORTH VALLEY | 51.4057 | 1242662 | 40.5836 | 65.5% | 83.56% | 2.678% | 0% | 1 | 2 | 36 | 94.64% | 0% | 4.807% | 42 | 760 | 57 | 0 | 81 | 72 | 18 | 11 | 14 | 1269 | 52.7519 | 233 | 88 | 8 | 543 | 0 | 1 | 36 | 0 | 0.118 | 4.8595 | 4.0295 | 2.3106 | Low | Medium | Medium | Bottom | 581 | 420 | 19.5816
HALSEY 1101 | 152241101 | NORTHERN | SIERRA | 72.9255 | 833727 | 42.2922 | 33.29% | 20.02% | 53.78% | 13.84% | 11 | 1 | 137 | 71.04% | 16.6% | 5.404% | 221 | 1275 | 6 | 1 | 391 | 134 | 7 | 20 | 37 | 2091 | 34.1417 | 377 | 315 | 42 | 908 | 0 | 1 | 137 | 1 | 0.4571 | 1.1192 | 4.492 | 2.298 | Medium | Low | Medium | Bottom | 582 | 700 | 5.0274
CORRAL 1103 | 162991103 | CENTRAL VALLEY | STOCKTON | 25.6729 | 706934 | 42.1524 | 46.13% | 0.08536% | 87.47% | 0% | 5 | 0 | 8 | 87.55% | 0% | 9.715% | 96 | 357 | 0 | 0 | 128 | 45 | 0 | 1 | 3 | 597 | 47.5245 | 156 | 93 | 2 | 288 | 0 | 0 | 8 | 0 | 0.1131 | 3.2436 | 6.2602 | 2.2966 | Low | Medium | High | Bottom | 583 | 412 | 20.3056
PINE GROVE 1101 | 163751101 | CENTRAL VALLEY | STOCKTON | 73.0596 | 1107892.3333 | 41.9271 | 39.09% | 18.75% | 70.66% | 0.8748% | 5 | 4 | 115 | 82.66% | 7.703% | 4.255% | 195 | 996 | 0 | 0 | 410 | 152 | 6 | 11 | 24 | 1833 | 38.345 | 352 | 201 | 11 | 785 | 0 | 1 | 114 | 0 | 0.071362 | 6.2186 | 5.0282 | 2.2314 | Low | Medium | Medium | Bottom | 584 | 354 | 31.2684
ROSSMOOR 1102 | 014161102 | BAY AREA | DIABLO | 0.23759 | 508088.6667 | 55 | 490.6% | 0% | 0% | 0% | 0 | 0 | 1 | 0% | 0% | 16.67% | 6 | 5 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.31985 | 1 | 6.8316 | 2.1851 | Low | Low | High | Bottom | 585 | 594 | 6.8316
PACIFICA 1104 | 022811104 | CENTRAL COAST | PENINSULA | 0.58219 | 361086.3333 | 46.4706 | 2.809% | 14.66% | 0% | 75.59% | 0 | 0 | 4 | 0% | 90.25% | 11.76% | 6 | 3 | 0 | 0 | 12 | 1 | 0 | 1 | 1 | 17 | 4.5 | 1 | 2 | 0 | 6 | 0 | 0 | 4 | 0 | 0.30434 | 1.1676 | 6.1375 | 2.1809 | Low | Low | High | Bottom | 586 | 579 | 7.1662
PLACER 1101 | 152461101 | NORTHERN | SIERRA | 0.97559 | 370014.6667 | 42.3333 | 14.04% | 0% | 2.378% | 12.82% | 0 | 0 | 2 | 3.106% | 66.22% | 6.667% | 6 | 14 | 0 | 0 | 15 | 1 | 0 | 1 | 2 | 30 | 32.25 | 5 | 1 | 0 | 9 | 0 | 0 | 2 | 0 | 0.40024 | 1 | 5.4221 | 2.1702 | Medium | Low | High | Bottom | 587 | 669 | 5.4221
BERKELEY F 0402 | 012060402 | BAY AREA | EAST BAY | 0.58346 | 175201 | 43.3333 | 30.72% | 0% | 85.64% | 13.87% | 5 | 0 | 1 | 34.97% | 64.79% | 16.67% | 1 | 1 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 6 | 42.25 | 0 | 0 | 1 | 4 | 0 | 0 | 1 | 0 | 0.29506 | 1 | 7.3537 | 2.1697 | Low | Low | High | Bottom | 588 | 575 | 7.3537
SAN RAMON 2117 | 014232117 | CENTRAL COAST | MISSION | 0.67335 | 1594385.6667 | 55 | 450.4% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 100% | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31589 | 1 | 6.8118 | 2.1518 | Low | Low | High | Bottom | 589 | 595 | 6.8118
GOLDTREE 1107 | 182581107 | CENTRAL COAST | LOS PADRES | 1.1277 | 95289 | 43.3333 | 58.4% | 0% | 5.234% | 7.596% | 0 | 0 | 0 | 5.234% | 7.596% | 0% | 5 | 0 | 0 | 6 | 5 | 1 | 0 | 0 | 2 | 16 | 34.25 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0.26296 | 1.5852 | 5.1526 | 2.1478 | Low | Low | Medium | Bottom | 590 | 552 | 8.168
ELK CREEK 1101 | 102781101 | NORTHERN | NORTH VALLEY | 97.876 | 245296.6667 | 39.9527 | 127.2% | 13.18% | 86.8% | 0% | 2 | 0 | 36 | 99.97% | 0% | 7.708% | 28 | 792 | 4 | 0 | 246 | 95 | 0 | 14 | 21 | 1479 | 40.4424 | 87 | 36 | 5 | 233 | 0 | 3 | 36 | 0 | 0.10469 | 25.9335 | 0.78561 | 2.1329 | Low | High | Low | Bottom | 591 | 411 | 20.3736
GRASS VALLEY 1102 | 152031102 | NORTHERN | SIERRA | 0.032103 | 368676.6667 | 38 | 5.665% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 60% | 1 | 0 | 0 | 0 | 3 | 1 | 0 | 1 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.44211 | 1 | 4.7939 | 2.1194 | Medium | Low | Medium | Bottom | 592 | 709 | 4.7939
SUMMIT 1101 | 152591101 | NORTHERN | SIERRA | 8.961 | 191693.3333 | 44.9231 | 9.625% | 37.13% | 22.51% | 0% | 1 | 0 | 24 | 37.55% | 22.3% | 43.73% | 55 | 69 | 0 | 1 | 33 | 19 | 6 | 15 | 26 | 263 | 29.8889 | 31 | 12 | 5 | 71 | 0 | 1 | 24 | 1 | 0.64235 | 1 | 3.2921 | 2.1147 | Medium | Low | Low | Bottom | 593 | 753 | 3.2921
PLACERVILLE 1111 | 153081111 | NORTHERN | SIERRA | 14.075 | 967719 | 41.9258 | 32.86% | 24.43% | 35.77% | 20.67% | 4 | 1 | 28 | 60.2% | 20.84% | 1.047% | 74 | 245 | 3 | 0 | 166 | 31 | 5 | 8 | 12 | 573 | 44.498 | 102 | 76 | 20 | 255 | 0 | 0 | 28 | 1 | 0.46103 | 1 | 4.5462 | 2.096 | Medium | Low | Medium | Bottom | 594 | 716 | 4.5462
DEL MONTE 2102 | 182222102 | CENTRAL COAST | CENTRAL COAST | 0.13454 | 1559551.3333 | 50 | 14.28% | 0% | 0% | 0% | 0 | 0 | 1 | 0% | 0% | 0% | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.27121 | 1 | 7.6365 | 2.0711 | Low | Low | High | Bottom | 595 | 566 | 7.6365
NORTH TOWER 2101 | 042042101 | BAY AREA | NORTH BAY | 1.3548 | 0 | 47 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0.4196% | 0% | 3 | 3 | 0 | 0 | 1 | 0 | 0 | 3 | 6 | 5 | 0 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 0.38534 | 1 | 5.3717 | 2.0699 | Medium | Low | Medium | Bottom | 596 | 676 | 5.3717
RIO DEL MAR 0402 | 083260402 | CENTRAL COAST | CENTRAL COAST | 2.2696 | 70566 | 44.4444 | 36.28% | 0% | 12.34% | 59.43% | 1 | 0 | 0 | 12.34% | 83.34% | 7.937% | 15 | 17 | 0 | 1 | 23 | 6 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34848 | 1 | 5.8894 | 2.0523 | Medium | Low | High | Bottom | 597 | 640 | 5.8894
DEL MAR 2109 | 152582109 | NORTHERN | SIERRA | 2.624 | 1116486 | 46.5385 | 117.4% | 0.5586% | 32.91% | 8.774% | 0 | 0 | 2 | 33.47% | 8.774% | 15.38% | 10 | 7 | 0 | 0 | 2 | 3 | 0 | 2 | 7 | 26 | 44 | 7 | 3 | 0 | 11 | 0 | 0 | 2 | 0 | 0.35594 | 1.3653 | 4.2223 | 2.0519 | Medium | Low | Medium | Bottom | 598 | 651 | 5.7648
IGNACIO 1103 | 042481103 | BAY AREA | NORTH BAY | 0.10132 | 793294.3333 | 47.1429 | 27.36% | 0% | 0% | 100% | 0 | 0 | 2 | 0% | 100% | 21.43% | 5 | 3 | 0 | 0 | 3 | 7 | 0 | 0 | 1 | 14 | 31.1429 | 2 | 2 | 1 | 7 | 0 | 0 | 2 | 1 | 0.29363 | 1 | 6.9815 | 2.05 | Low | Low | High | Bottom | 599 | 587 | 6.9815
ELECTRA 1101 | 162161101 | CENTRAL VALLEY | STOCKTON | 83.4541 | 732194.6667 | 42.3763 | 57.61% | 18.69% | 62.3% | 5.245% | 4 | 4 | 67 | 75.96% | 16.77% | 4.972% | 287 | 1122 | 1 | 0 | 569 | 155 | 7 | 15 | 40 | 2112 | 34.6052 | 346 | 188 | 13 | 750 | 0 | 1 | 67 | 0 | 0.099441 | 4.1963 | 4.9111 | 2.0493 | Low | Medium | Medium | Bottom | 600 | 408 | 20.6084
KERCKHOFF 1101 | 252561101 | CENTRAL VALLEY | YOSEMITE | 34.5924 | 62243 | 40.0179 | 33.34% | 4.787% | 62.85% | 7.22% | 1 | 1 | 27 | 58.51% | 16.85% | 24.91% | 30 | 41 | 0 | 24 | 284 | 29 | 0 | 6 | 16 | 570 | 16.9306 | 55 | 29 | 3 | 165 | 0 | 0 | 27 | 0 | 0.29197 | 2.3844 | 2.9222 | 2.0344 | Low | Low | Low | Bottom | 601 | 588 | 6.9676
HIGHLANDS 1101 | 043361101 | NORTHERN | HUMBOLDT | 0.026418 | 0 | 40 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36313 | 1 | 5.5033 | 1.9984 | Medium | Low | High | Bottom | 602 | 666 | 5.5033
CAMPHORA 1101 | 182071101 | CENTRAL COAST | CENTRAL COAST | 2.177 | 949679.6667 | 39.0909 | 9.398% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 4.545% | 0 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 22 | 0 | 1 | 1 | 0 | 4 | 0 | 0 | 1 | 0 | 0.10721 | 15.7705 | 1.1803 | 1.9957 | Low | High | Low | Bottom | 603 | 429 | 18.6144
SNEATH LANE 1102 | 022721102 | CENTRAL COAST | PENINSULA | 0.46314 | 607738.6667 | 42.4242 | 53.37% | 0% | 16.94% | 13.26% | 2 | 0 | 1 | 16.94% | 58.58% | 12.12% | 7 | 5 | 0 | 0 | 22 | 2 | 0 | 0 | 3 | 33 | 0.25 | 3 | 2 | 0 | 8 | 0 | 0 | 1 | 0 | 0.38201 | 1 | 5.2218 | 1.9948 | Medium | Low | Medium | Bottom | 604 | 686 | 5.2218
EL CERRITO G 1113 | 012501113 | BAY AREA | EAST BAY | 0.24171 | 889579.6667 | 42.5 | 7.767% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6 | 24 | 1 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0.23041 | 1 | 8.6451 | 1.9919 | Low | Low | High | Bottom | 605 | 537 | 8.6451
SAN RAMON 2119 | 014232119 | CENTRAL COAST | MISSION | 0.72877 | 1190973.3333 | 0 | 366.8% | 0% | 0% | 0% | 0 | 0 | 1 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 20 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.28888 | 1 | 6.8115 | 1.9677 | Low | Low | High | Bottom | 606 | 596 | 6.8115
COTTONWOOD 1101 | 102931101 | NORTHERN | NORTH VALLEY | 71.9061 | 576424 | 42.1748 | 0% | 56.03% | 37.89% | 0.2479% | 4 | 0 | 35 | 96.19% | 0.2479% | 5.753% | 89 | 836 | 77 | 0 | 262 | 167 | 0 | 8 | 17 | 1634 | 45.5487 | 178 | 94 | 8 | 435 | 0 | 4 | 35 | 0 | 0.062505 | 11.3331 | 2.7676 | 1.9605 | Low | Medium | Low | Bottom | 607 | 353 | 31.366
TASSAJARA 2103 | 014662103 | BAY AREA | DIABLO | 1.9027 | 1249838.6667 | 41.7647 | 38.85% | 0% | 16.52% | 63.81% | 0 | 0 | 2 | 16.52% | 63.81% | 0% | 0 | 1 | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 17 | 42.8571 | 0 | 3 | 2 | 8 | 0 | 0 | 1 | 0 | 0.27399 | 1 | 7.1533 | 1.9599 | Low | Low | High | Bottom | 608 | 580 | 7.1533
COARSEGOLD 2103 | 254432103 | CENTRAL VALLEY | YOSEMITE | 94.1821 | 1349627.3333 | 40.6886 | 85.78% | 0.6152% | 82.94% | 0.4203% | 4 | 0 | 59 | 85.6% | 0.4203% | 29.52% | 130 | 305 | 1 | 0 | 677 | 228 | 0 | 14 | 23 | 1992 | 34.5554 | 293 | 421 | 41 | 1031 | 0 | 0 | 59 | 0 | 0.13752 | 3.7859 | 3.7343 | 1.9442 | Low | Medium | Low | Bottom | 609 | 472 | 14.1375
BEAR VALLEY 2101 | 252192101 | CENTRAL VALLEY | YOSEMITE | 109.9397 | 330590 | 40.2159 | 0% | 22.27% | 68.68% | 0.7968% | 2 | 0 | 67 | 80.27% | 13.19% | 20.67% | 42 | 279 | 2 | 0 | 598 | 182 | 0 | 15 | 25 | 1630 | 30.9944 | 226 | 87 | 9 | 567 | 0 | 1 | 66 | 0 | 0.11438 | 6.4533 | 2.6256 | 1.938 | Low | Medium | Low | Bottom | 610 | 443 | 16.9437
WISHON 1101 | 251511101 | CENTRAL VALLEY | YOSEMITE | 7.7822 | 4220 | 42.7477 | 0% | 27.36% | 72.21% | 0.4235% | 0 | 0 | 2 | 78.45% | 21.55% | 12.7% | 24 | 8 | 0 | 1 | 40 | 3 | 0 | 0 | 4 | 126 | 14.7692 | 6 | 5 | 1 | 19 | 0 | 0 | 2 | 0 | 0.30598 | 2.4093 | 2.6231 | 1.9338 | Low | Medium | Low | Bottom | 611 | 622 | 6.3199
FLINT 1102 | 152531102 | NORTHERN | SIERRA | 0.092844 | 193432.6667 | 46.6667 | 21.4% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36537 | 1 | 5.272 | 1.9262 | Medium | Low | Medium | Bottom | 612 | 680 | 5.272
TEMPLETON 2108 | 183052108 | CENTRAL COAST | LOS PADRES | 3.1369 | 953723.3333 | 40.9694 | 26.48% | 0% | 51.92% | 32.41% | 2 | 0 | 19 | 51.92% | 32.41% | 10.71% | 20 | 9 | 0 | 41 | 78 | 20 | 0 | 1 | 5 | 196 | 57.2439 | 31 | 30 | 3 | 83 | 0 | 0 | 19 | 0 | 0.43947 | 1 | 4.3687 | 1.9199 | Medium | Low | Medium | Bottom | 613 | 724 | 4.3687
CLEAR LAKE 1102 | 042141102 | NORTHERN | HUMBOLDT | 4.9879 | 888198.3333 | 47.0139 | 12.15% | 0% | 54.06% | 4.215% | 0 | 0 | 4 | 54.06% | 4.215% | 12.5% | 37 | 38 | 0 | 1 | 18 | 9 | 0 | 0 | 1 | 72 | 29.75 | 18 | 11 | 1 | 38 | 0 | 0 | 4 | 0 | 0.44438 | 1 | 4.3199 | 1.9197 | Medium | Low | Medium | Bottom | 614 | 728 | 4.3199
SISQUOC 1102 | 182811102 | CENTRAL COAST | LOS PADRES | 52.3119 | 1118488.3333 | 42.2034 | 91.72% | 0% | 51.74% | 13.78% | 0 | 2 | 22 | 51% | 32.39% | 2.316% | 39 | 17 | 0 | 82 | 137 | 77 | 0 | 2 | 2 | 475 | 18.4194 | 25 | 4 | 2 | 95 | 0 | 0 | 22 | 0 | 0.24085 | 13.2082 | 0.60004 | 1.9089 | Low | High | Low | Bottom | 615 | 557 | 7.9255
SHEPHERD 2111 | 252062111 | CENTRAL VALLEY | FRESNO | 20.5291 | 0 | 43.4091 | 33.12% | 0% | 100% | 0% | 0 | 0 | 10 | 100% | 0% | 36.77% | 54 | 13 | 0 | 18 | 162 | 36 | 0 | 4 | 6 | 310 | 46.6993 | 76 | 57 | 1 | 173 | 0 | 0 | 10 | 0 | 0.21054 | 7.2895 | 1.2264 | 1.8822 | Low | Medium | Low | Bottom | 616 | 527 | 8.9398
CLARKSVILLE 2109 | 153612109 | NORTHERN | SIERRA | 5.6918 | 1630300.3333 | 48.0851 | 110.3% | 0% | 67.47% | 0% | 0 | 0 | 13 | 67.47% | 0% | 1.064% | 39 | 42 | 0 | 0 | 19 | 7 | 0 | 2 | 4 | 94 | 28.3514 | 12 | 18 | 2 | 37 | 0 | 0 | 13 | 1 | 0.3464 | 1 | 5.4176 | 1.8767 | Medium | Low | High | Bottom | 617 | 670 | 5.4176
LAKEWOOD 2224 | 013532224 | BAY AREA | DIABLO | 1.1155 | 828489.6667 | 44.6 | 15.02% | 0% | 86.93% | 13.07% | 1 | 0 | 1 | 28.76% | 71.24% | 8% | 8 | 8 | 0 | 0 | 11 | 1 | 0 | 0 | 0 | 25 | 53.3636 | 3 | 7 | 0 | 11 | 0 | 0 | 1 | 0 | 0.27727 | 1 | 6.7667 | 1.8762 | Low | Low | High | Bottom | 618 | 599 | 6.7667
GRASS VALLEY 1103 | 152031103 | NORTHERN | SIERRA | 86.458 | 534422 | 42.7367 | 43.7% | 41.13% | 51.11% | 1.285% | 9 | 2 | 125 | 90.34% | 3.412% | 12.68% | 112 | 1291 | 3 | 0 | 272 | 207 | 3 | 20 | 34 | 2035 | 38.7995 | 405 | 175 | 16 | 830 | 0 | 2 | 125 | 0 | 0.1218 | 3.2523 | 4.7244 | 1.8714 | Low | Medium | Medium | Bottom | 619 | 458 | 15.3651
CMC 1102 | 183111102 | CENTRAL COAST | LOS PADRES | 0.46264 | 0 | 0 | 0% | 0% | 0% | 6.672% | 0 | 0 | 0 | 0% | 6.672% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36318 | 1 | 5.1474 | 1.8694 | Medium | Low | Medium | Bottom | 620 | 695 | 5.1474
NARROWS 2104 | 153132104 | NORTHERN | SIERRA | 0.002841 | 0 | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.38633 | 1 | 4.8141 | 1.8598 | Medium | Low | Medium | Bottom | 621 | 708 | 4.8141
HALSEY 1102 | 152241102 | NORTHERN | SIERRA | 58.9603 | 966228.3333 | 42.6053 | 32.47% | 32.96% | 36.23% | 21.19% | 12 | 3 | 73 | 64.36% | 27.04% | 8.07% | 186 | 983 | 5 | 0 | 242 | 92 | 0 | 12 | 25 | 1549 | 35.5795 | 276 | 177 | 10 | 637 | 0 | 0 | 70 | 0 | 0.41881 | 1.0367 | 4.1798 | 1.8148 | Medium | Low | Medium | Bottom | 622 | 727 | 4.3333
WOODWARD 2108 | 255292108 | CENTRAL VALLEY | FRESNO | 32.5265 | 1243541.3333 | 41.8898 | 15.92% | 0.1617% | 83.65% | 0.009516% | 1 | 1 | 19 | 93.94% | 1.985% | 26.6% | 25 | 54 | 0 | 12 | 228 | 44 | 0 | 5 | 7 | 470 | 30.9934 | 55 | 53 | 6 | 171 | 0 | 0 | 19 | 0 | 0.20324 | 4.6388 | 1.9232 | 1.8131 | Low | Medium | Low | Bottom | 623 | 528 | 8.9211
KIRKER 2104 | 014452104 | BAY AREA | DIABLO | 5.6758 | 1460458 | 45.3472 | 150% | 24.28% | 41.33% | 12.22% | 0 | 0 | 5 | 41.33% | 36.49% | 33.33% | 14 | 19 | 0 | 0 | 11 | 7 | 0 | 2 | 5 | 72 | 19.6 | 2 | 2 | 1 | 8 | 0 | 0 | 5 | 0 | 0.35726 | 1 | 5.0593 | 1.8075 | Medium | Low | Medium | Bottom | 624 | 698 | 5.0593
COTATI 1104 | 042271104 | NORTHERN | SONOMA | 8.881 | 508263 | 43.7449 | 25.11% | 2.544% | 37.12% | 46.68% | 1 | 0 | 26 | 37.12% | 49.23% | 1.639% | 54 | 110 | 0 | 3 | 88 | 18 | 2 | 0 | 5 | 244 | 32.835 | 37 | 16 | 2 | 105 | 0 | 0 | 26 | 0 | 0.44174 | 1.0792 | 3.7782 | 1.8011 | Medium | Low | Medium | Bottom | 625 | 734 | 4.0773
TRIDAM POWERHOUSE 2101 | 168152101 | CENTRAL VALLEY | YOSEMITE | 0.050313 | 0 | 45 | 0% | 100% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.50016 | 1 | 3.5959 | 1.7985 | Medium | Low | Low | Bottom | 626 | 749 | 3.5959
FORT ORD 2107 | 182402107 | CENTRAL COAST | CENTRAL COAST | 4.2048 | 0 | 44.4175 | 29.09% | 18.37% | 1.01% | 9.598% | 0 | 0 | 11 | 1.01% | 88.05% | 2.913% | 3 | 12 | 0 | 1 | 71 | 6 | 0 | 3 | 4 | 103 | 9.7143 | 2 | 1 | 1 | 8 | 1 | 0 | 11 | 0 | 0.39817 | 1 | 4.4491 | 1.7715 | Medium | Low | Medium | Bottom | 627 | 720 | 4.4491
WYANDOTTE 1110 | 102911110 | NORTHERN | NORTH VALLEY | 15.7768 | 980007.6667 | 42.2344 | 73.74% | 0.1738% | 61.82% | 17.2% | 2 | 0 | 13 | 62% | 17.2% | 3.125% | 24 | 189 | 1 | 0 | 43 | 39 | 0 | 1 | 3 | 320 | 52.8548 | 59 | 30 | 3 | 133 | 0 | 2 | 13 | 0 | 0.2573 | 1 | 6.8825 | 1.7709 | Low | Low | High | Bottom | 628 | 590 | 6.8825
CLAYTON 2211 | 012022211 | BAY AREA | DIABLO | 0.14792 | 1278512.6667 | 45 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.31499 | 1 | 5.5818 | 1.7582 | Low | Low | High | Bottom | 629 | 664 | 5.5818
SAN RAMON 2101 | 014232101 | CENTRAL COAST | MISSION | 0.78266 | 1284209.3333 | 56 | 353.9% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 13.33% | 14 | 3 | 0 | 0 | 1 | 2 | 0 | 0 | 1 | 15 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.25765 | 1 | 6.8071 | 1.7539 | Low | Low | High | Bottom | 630 | 597 | 6.8071
LAS GALLINAS A 1104 | 042991104 | BAY AREA | NORTH BAY | 1.251 | 1034461.3333 | 46 | 6.426% | 0% | 29.11% | 67.07% | 0 | 0 | 1 | 29.11% | 67.07% | 10% | 2 | 1 | 0 | 0 | 7 | 1 | 0 | 0 | 0 | 10 | 45.6667 | 1 | 1 | 1 | 3 | 0 | 0 | 1 | 0 | 0.22128 | 1 | 7.8951 | 1.747 | Low | Low | High | Bottom | 631 | 559 | 7.8951
COVELO 1101 | 043061101 | NORTHERN | HUMBOLDT | 18.5991 | 367965 | 41.3529 | 4.242% | 62.02% | 34.97% | 0% | 1 | 0 | 7 | 100% | 0% | 7.059% | 11 | 68 | 0 | 1 | 32 | 19 | 0 | 1 | 2 | 170 | 28.7045 | 15 | 7 | 0 | 49 | 0 | 0 | 7 | 0 | 0.30522 | 9.0051 | 0.63351 | 1.7412 | Low | Medium | Low | Bottom | 632 | 656 | 5.7048
EL CERRITO G 1108 | 012501108 | BAY AREA | EAST BAY | 0.774 | 593206 | 0 | 2.573% | 0% | 43.34% | 44.78% | 0 | 1 | 0 | 0% | 98.55% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1974 | 1 | 8.776 | 1.7324 | Low | Low | High | Bottom | 633 | 532 | 8.776
OCEANO 1106 | 182601106 | CENTRAL COAST | LOS PADRES | 2.3362 | 1355756.3333 | 46.3265 | 113.1% | 0% | 11.98% | 23.42% | 0 | 0 | 2 | 11.98% | 23.42% | 6.122% | 13 | 0 | 0 | 10 | 8 | 11 | 0 | 2 | 3 | 49 | 25.5714 | 8 | 2 | 1 | 15 | 0 | 0 | 2 | 0 | 0.33198 | 1 | 5.1395 | 1.7062 | Medium | Low | Medium | Bottom | 634 | 696 | 5.1395
MONROE 2107 | 043302107 | NORTHERN | SONOMA | 0.75479 | 2185651 | 45 | 2.435% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 61.54% | 0 | 2 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 13 | 60.6667 | 1 | 1 | 0 | 6 | 0 | 0 | 1 | 1 | 0.39704 | 1 | 4.2684 | 1.6947 | Medium | Low | Medium | Bottom | 635 | 730 | 4.2684
HORSESHOE 1104 | 152571104 | NORTHERN | SIERRA | 1.2893 | 585906.6667 | 44.8571 | 33.6% | 0% | 91.7% | 0% | 0 | 0 | 5 | 91.7% | 0% | 0% | 3 | 29 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 35 | 41.963 | 7 | 17 | 2 | 29 | 0 | 0 | 5 | 0 | 0.264 | 1 | 6.3837 | 1.6853 | Low | Low | High | Bottom | 636 | 618 | 6.3837
EDENVALE 2107 | 082952107 | CENTRAL COAST | SAN JOSE | 4.8106 | 2048224.3333 | 42.8571 | 18.79% | 0% | 54.93% | 0% | 0 | 0 | 0 | 54.93% | 0% | 14.29% | 8 | 5 | 0 | 3 | 16 | 0 | 0 | 2 | 3 | 28 | 0 | 1 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.2962 | 1.8399 | 3.081 | 1.6792 | Low | Low | Low | Bottom | 637 | 659 | 5.6689
SAN ARDO 1101 | 182191101 | CENTRAL COAST | CENTRAL COAST | 2.7868 | 271781.3333 | 39.359 | 8.763% | 0% | 88.24% | 11.76% | 0 | 0 | 0 | 88.24% | 11.76% | 17.5% | 1 | 9 | 0 | 0 | 12 | 1 | 0 | 0 | 0 | 40 | 19.1538 | 7 | 1 | 0 | 13 | 0 | 0 | 0 | 0 | 0.11775 | 7.1101 | 1.9981 | 1.6728 | Low | Medium | Low | Bottom | 638 | 471 | 14.2067
HIGHLANDS 1104 | 043361104 | NORTHERN | HUMBOLDT | 12.02 | 1046439 | 45.9626 | 24.73% | 0% | 75.88% | 1.167% | 0 | 1 | 28 | 75.88% | 1.167% | 7.467% | 128 | 189 | 0 | 2 | 118 | 39 | 15 | 5 | 9 | 375 | 51.0793 | 53 | 71 | 20 | 170 | 0 | 0 | 28 | 1 | 0.29309 | 1 | 5.6794 | 1.6645 | Low | Low | High | Bottom | 639 | 658 | 5.6794
WOOD 0401 | 013380401 | BAY AREA | EAST BAY | 0.4661 | 127718.3333 | 45 | 0% | 0% | 99.35% | 0% | 1 | 0 | 0 | 46.88% | 52.82% | 42.86% | 2 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 7 | 70 | 0 | 3 | 0 | 3 | 0 | 0 | 0 | 0 | 0.2397 | 1 | 6.8397 | 1.6395 | Low | Low | High | Bottom | 640 | 593 | 6.8397
JESSUP 1103 | 103441103 | NORTHERN | NORTH VALLEY | 4.4405 | 665870.6667 | 42.4419 | 0% | 48.78% | 44.06% | 0.7795% | 1 | 0 | 9 | 97.48% | 2.521% | 13.18% | 20 | 65 | 6 | 0 | 23 | 17 | 0 | 2 | 2 | 129 | 40.0182 | 26 | 17 | 1 | 56 | 0 | 0 | 9 | 0 | 0.33083 | 1.2953 | 3.8162 | 1.6353 | Medium | Low | Medium | Bottom | 641 | 702 | 4.9431
CALPELLA 1102 | 043411102 | NORTHERN | HUMBOLDT | 8.9876 | 855830 | 43.4234 | 13.53% | 0% | 71% | 20.72% | 0 | 0 | 4 | 71% | 20.72% | 14.41% | 13 | 57 | 0 | 4 | 14 | 27 | 0 | 1 | 2 | 111 | 56.9783 | 11 | 8 | 3 | 50 | 0 | 0 | 4 | 0 | 0.41149 | 1.5474 | 2.5544 | 1.6265 | Medium | Low | Low | Bottom | 642 | 742 | 3.9527
PLACERVILLE 1109 | 153081109 | NORTHERN | SIERRA | 0.020146 | 0 | 50 | 1.037% | 42.3% | 0% | 0% | 0 | 0 | 1 | 0% | 42.3% | 0% | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.39891 | 1 | 4.0646 | 1.6214 | Medium | Low | Medium | Bottom | 643 | 736 | 4.0646
LAKEWOOD 2109 | 013532109 | BAY AREA | DIABLO | 0.27299 | 1133254.6667 | 40.4167 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 8.333% | 0 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 12 | 57.8571 | 3 | 1 | 1 | 7 | 0 | 0 | 0 | 0 | 0.21104 | 1 | 7.6658 | 1.6177 | Low | Low | High | Bottom | 644 | 565 | 7.6658
TULE POWER HOUSE 1101 | 258591101 | CENTRAL VALLEY | FRESNO | 4.0927 | 0 | 38.9041 | 0% | 81.39% | 18.61% | 0% | 0 | 0 | 1 | 3.215% | 96.78% | 55.26% | 4 | 0 | 0 | 5 | 48 | 5 | 0 | 0 | 1 | 76 | 1 | 2 | 1 | 0 | 6 | 0 | 0 | 1 | 0 | 0.30988 | 2.0821 | 2.5025 | 1.6146 | Low | Low | Low | Bottom | 645 | 688 | 5.2104
CLARKSVILLE 2110 | 153612110 | NORTHERN | SIERRA | 0.17765 | 1795877.6667 | 0 | 658.2% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29789 | 1 | 5.3871 | 1.6048 | Low | Low | High | Bottom | 646 | 673 | 5.3871
ECHO SUMMIT 1101 | 158031101 |  |  | 7.2766 | 57440 | 42.0245 | 77.68% | 99.88% | 0% | 0% | 9 | 0 | 12 | 99.88% | 0% | 1.198% | 26 | 14 | 0 | 0 | 18 | 9 | 4 | 7 | 17 | 167 | 35.7674 | 23 | 10 | 0 | 43 | 0 | 0 | 12 | 1 | 0.6628 | 1 | 2.3846 | 1.5805 | High | Low | Low | Bottom | 647 | 767 | 2.3846
LAS GALLINAS A 1106 | 042991106 | BAY AREA | NORTH BAY | 6.4929 | 743147.3333 | 44.3443 | 29.21% | 0.2812% | 77.31% | 4.193% | 0 | 0 | 4 | 77.31% | 8.339% | 3.226% | 13 | 9 | 0 | 0 | 43 | 6 | 0 | 0 | 0 | 62 | 15.8235 | 3 | 3 | 4 | 17 | 0 | 0 | 4 | 0 | 0.20631 | 1 | 7.5211 | 1.5517 | Low | Low | High | Bottom | 648 | 571 | 7.5211
CLARKSVILLE 2106 | 153612106 | NORTHERN | SIERRA | 0.99996 | 1619131.3333 | 48.3333 | 197.4% | 0% | 0% | 0% | 0 | 0 | 1 | 0% | 0% | 0% | 1 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0.2699 | 1 | 5.6989 | 1.5381 | Low | Low | High | Bottom | 649 | 657 | 5.6989
PENRYN 1107 | 152561107 | NORTHERN | SIERRA | 43.5049 | 1131270 | 42.5192 | 47.95% | 1.169% | 68.49% | 12.43% | 2 | 0 | 101 | 65.57% | 16.68% | 7.843% | 83 | 611 | 2 | 0 | 143 | 54 | 5 | 17 | 22 | 918 | 28.8128 | 147 | 152 | 11 | 402 | 0 | 0 | 101 | 0 | 0.15717 | 1.8038 | 5.3775 | 1.5245 | Low | Low | High | Bottom | 650 | 513 | 9.6998
EL CERRITO G 1111 | 012501111 | BAY AREA | EAST BAY | 0.97377 | 404613.3333 | 43.3333 | 1.769% | 0% | 15.73% | 83.98% | 0 | 0 | 1 | 6.068% | 93.64% | 0% | 2 | 4 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 15 | 44.5 | 0 | 2 | 0 | 4 | 0 | 0 | 1 | 0 | 0.16872 | 1 | 8.9706 | 1.5136 | Low | Low | High | Bottom | 651 | 524 | 8.9706
PACIFIC GROVE 0422 | 182440422 | CENTRAL COAST | CENTRAL COAST | 0.65447 | 111011.6667 | 48.9286 | 104.5% | 0% | 0% | 0% | 0 | 0 | 1 | 0% | 100% | 0% | 13 | 11 | 0 | 0 | 1 | 2 | 2 | 2 | 3 | 14 | 5.3333 | 0 | 2 | 0 | 3 | 0 | 0 | 1 | 0 | 0.2389 | 1 | 6.3303 | 1.5123 | Low | Low | High | Bottom | 652 | 620 | 6.3303
CLAY 1102 | 163341102 | CENTRAL VALLEY | STOCKTON | 1.2491 | 70737.6667 | 48.125 | 345.3% | 0% | 0% | 0% | 1 | 0 | 0 | 0% | 0% | 6.25% | 7 | 5 | 0 | 0 | 5 | 0 | 0 | 0 | 2 | 16 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.30842 | 1 | 4.8947 | 1.5096 | Low | Low | Medium | Bottom | 653 | 704 | 4.8947
FRANKLIN 1101 | 013921101 | BAY AREA | EAST BAY | 1.5676 | 1072709.6667 | 50.1923 | 0% | 0% | 6.206% | 20.54% | 0 | 0 | 1 | 0% | 36.62% | 7.692% | 7 | 5 | 0 | 0 | 8 | 8 | 0 | 0 | 3 | 26 | 15.4 | 1 | 3 | 0 | 5 | 0 | 0 | 1 | 0 | 0.26112 | 1 | 5.7623 | 1.5047 | Low | Low | High | Bottom | 654 | 652 | 5.7623
SAN LUIS OBISPO 1102 | 182631102 | CENTRAL COAST | LOS PADRES | 0.68163 | 1030598 | 38.6667 | 11.17% | 0% | 99.44% | 0% | 0 | 0 | 2 | 99.03% | 0.4172% | 0% | 0 | 3 | 0 | 0 | 11 | 0 | 0 | 2 | 2 | 15 | 16.2 | 2 | 0 | 0 | 5 | 0 | 0 | 2 | 0 | 0.20447 | 1 | 7.3203 | 1.4968 | Low | Low | High | Bottom | 655 | 577 | 7.3203
HIGGINS 1108 | 152691108 | NORTHERN | SIERRA | 0.020411 | 0 | 0 | 0% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.38633 | 1 | 3.8713 | 1.4956 | Medium | Low | Medium | Bottom | 656 | 744 | 3.8713
HOLLISTER 2102 | 182492102 | CENTRAL COAST | CENTRAL COAST | 31.7344 | 522197.3333 | 38.3333 | 25.09% | 15.35% | 77.48% | 1.755% | 0 | 0 | 4 | 92.84% | 1.755% | 2.778% | 2 | 13 | 0 | 0 | 51 | 1 | 0 | 0 | 0 | 72 | 1.6667 | 2 | 3 | 1 | 10 | 0 | 0 | 4 | 0 | 0.11331 | 10.11 | 1.3052 | 1.4952 | Low | Medium | Low | Bottom | 657 | 482 | 13.1959
ALHAMBRA 1102 | 014101102 | BAY AREA | DIABLO | 0.37374 | 999803 | 44.1667 | 0.05608% | 31.31% | 27.66% | 31.86% | 0 | 0 | 2 | 31.31% | 59.51% | 50% | 2 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 12 | 20.6 | 0 | 3 | 1 | 5 | 0 | 0 | 2 | 1 | 0.29792 | 1 | 5.0186 | 1.4952 | Low | Low | Medium | Bottom | 658 | 701 | 5.0186
RIO DEL MAR 0401 | 083260401 | CENTRAL COAST | CENTRAL COAST | 1.8233 | 68016.3333 | 53.75 | 36.6% | 0% | 18.3% | 26.83% | 0 | 0 | 0 | 18.3% | 28.42% | 25% | 2 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25383 | 1 | 5.8637 | 1.4884 | Low | Low | High | Bottom | 659 | 644 | 5.8637
BUTTE 1105 | 103081105 | NORTHERN | NORTH VALLEY | 2.5574 | 849032.6667 | 43.2143 | 15.51% | 1.765% | 65.2% | 0% | 0 | 0 | 26 | 66.97% | 0% | 2.381% | 8 | 16 | 0 | 0 | 8 | 1 | 0 | 11 | 15 | 42 | 38.7328 | 116 | 83 | 5 | 273 | 0 | 0 | 26 | 0 | 0.28197 | 1 | 5.2496 | 1.4802 | Low | Low | Medium | Bottom | 660 | 683 | 5.2496
CHESTER 1101 | 103181101 | NORTHERN | NORTH VALLEY | 2.9117 | 277170.3333 | 41.6162 | 6.963% | 86.02% | 9.547% | 3.579% | 0 | 0 | 4 | 95.56% | 3.579% | 15.84% | 3 | 7 | 5 | 0 | 33 | 16 | 0 | 0 | 0 | 101 | 54.0345 | 11 | 13 | 3 | 29 | 0 | 0 | 4 | 0 | 0.33112 | 1 | 4.4592 | 1.4765 | Medium | Low | Medium | Bottom | 661 | 719 | 4.4592
LOYOLA 1102 | 082161102 | CENTRAL COAST | DE ANZA | 0.10967 | 1120181.3333 | 42.5 | 0.365% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.26157 | 1 | 5.6407 | 1.4755 | Low | Low | High | Bottom | 662 | 660 | 5.6407
CARMEL 0402 | 182040402 | CENTRAL COAST | CENTRAL COAST | 0.32816 | 137085.6667 | 43.6364 | 1.047% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 80.99% | 18.18% | 0 | 3 | 0 | 0 | 6 | 0 | 0 | 1 | 1 | 11 | 4.3333 | 2 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.25216 | 1 | 5.8204 | 1.4677 | Low | Low | High | Bottom | 663 | 647 | 5.8204
SAN JOAQUIN #3 1102 | 252531102 | CENTRAL VALLEY | YOSEMITE | 11.5194 | 0 | 41.5593 | 25.3% | 37.17% | 21.4% | 0% | 0 | 0 | 5 | 68.21% | 30.26% | 18.18% | 46 | 29 | 0 | 0 | 155 | 8 | 0 | 2 | 4 | 297 | 27.3223 | 28 | 33 | 8 | 127 | 0 | 0 | 5 | 0 | 0.4064 | 1.2475 | 2.8926 | 1.4666 | Medium | Low | Low | Bottom | 664 | 748 | 3.6086
REEDLEY 1104 | 252341104 | CENTRAL VALLEY | FRESNO | 2.6606 | 1032168.6667 | 38.913 | 12.44% | 8.961% | 65.68% | 25.36% | 0 | 0 | 1 | 74.64% | 25.36% | 4.348% | 0 | 20 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 1 | 0 | 4 | 0 | 0 | 1 | 0 | 0.12433 | 4.6705 | 2.501 | 1.4523 | Low | Medium | Low | Bottom | 665 | 496 | 11.6811
HIGGINS 1109 | 152691109 | NORTHERN | SIERRA | 140.9716 | 609072.3333 | 43.312 | 37.7% | 4.367% | 88.44% | 1.787% | 5 | 0 | 164 | 92.68% | 1.939% | 15.2% | 162 | 1680 | 11 | 0 | 219 | 382 | 10 | 17 | 27 | 2894 | 37.946 | 519 | 279 | 22 | 1112 | 0 | 4 | 164 | 0 | 0.071544 | 5.1067 | 3.9221 | 1.433 | Low | Medium | Medium | Bottom | 666 | 417 | 20.0289
CAMBRIA 1101 | 182771101 | CENTRAL COAST | LOS PADRES | 27.8539 | 191645.6667 | 39.814 | 163% | 0% | 66.28% | 19.72% | 1 | 0 | 16 | 1.731% | 84.26% | 1.163% | 14 | 39 | 1 | 16 | 228 | 89 | 0 | 9 | 11 | 430 | 27.8571 | 9 | 10 | 5 | 44 | 0 | 0 | 16 | 0 | 0.30267 | 1.4617 | 3.2384 | 1.4327 | Low | Low | Low | Bottom | 667 | 710 | 4.7336
NARROWS 2105 | 153132105 | NORTHERN | SIERRA | 179.3789 | 1278710 | 42.6748 | 33% | 1.996% | 83.86% | 2.835% | 7 | 6 | 207 | 85.79% | 2.997% | 13.3% | 337 | 2666 | 22 | 0 | 303 | 459 | 20 | 24 | 43 | 4227 | 50.4105 | 855 | 356 | 18 | 1719 | 0 | 5 | 207 | 0 | 0.1137 | 2.325 | 5.3456 | 1.4131 | Low | Low | Medium | Bottom | 668 | 489 | 12.4285
NARROWS 2101 | 153132101 | NORTHERN | SIERRA | 61.1189 | 168654 | 45.2804 | 72.81% | 0.5616% | 92.09% | 3.646% | 3 | 1 | 49 | 83.47% | 12.83% | 7.893% | 247 | 431 | 45 | 0 | 158 | 189 | 0 | 11 | 24 | 1267 | 41.9685 | 222 | 73 | 7 | 401 | 0 | 4 | 49 | 0 | 0.075116 | 4.1813 | 4.4896 | 1.4101 | Low | Medium | Medium | Bottom | 669 | 428 | 18.7726
COARSEGOLD 2102 | 254432102 | CENTRAL VALLEY | YOSEMITE | 69.5656 | 333162 | 41.1098 | 105% | 50.59% | 24.23% | 0.6864% | 2 | 0 | 72 | 81.55% | 17.93% | 26.38% | 129 | 250 | 0 | 1 | 713 | 131 | 0 | 23 | 41 | 1664 | 30.7496 | 254 | 171 | 15 | 664 | 0 | 0 | 71 | 0 | 0.15087 | 2.686 | 3.4666 | 1.4048 | Low | Medium | Low | Bottom | 670 | 522 | 9.3112
BOSTON 0401 | 013320401 | BAY AREA | EAST BAY | 0.68358 | 0 | 45 | 63.38% | 0% | 19.82% | 0% | 0 | 0 | 0 | 0% | 100% | 88.89% | 1 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 9 | 25 | 0 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 0.21197 | 1 | 6.6079 | 1.4007 | Low | Low | High | Bottom | 671 | 611 | 6.6079
MIRA VISTA 0403 | 012330403 | BAY AREA | EAST BAY | 0.1074 | 159961.3333 | 0 | 19.33% | 0% | 100% | 0% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.16858 | 1 | 8.3009 | 1.3994 | Low | Low | High | Bottom | 672 | 547 | 8.3009
SYCAMORE CREEK 1109 | 102971109 | NORTHERN | NORTH VALLEY | 0.79158 | 908767 | 45 | 1.821% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.26871 | 1 | 5.1691 | 1.389 | Low | Low | Medium | Bottom | 673 | 694 | 5.1691
MORGAN HILL 2109 | 083242109 | CENTRAL COAST | SAN JOSE | 2.6411 | 1764272 | 43.2609 | 6.413% | 39.24% | 60.41% | 0% | 1 | 0 | 3 | 99.65% | 0% | 4.348% | 13 | 21 | 0 | 1 | 19 | 1 | 0 | 0 | 1 | 46 | 15.8571 | 8 | 17 | 8 | 42 | 0 | 0 | 3 | 0 | 0.33392 | 1 | 4.0649 | 1.3574 | Medium | Low | Medium | Bottom | 674 | 735 | 4.0649
ROSSMOOR 1104 | 014161104 | BAY AREA | DIABLO | 0.29689 | 875410 | 42.7778 | 3.845% | 0% | 100% | 0% | 0 | 0 | 1 | 16.15% | 83.85% | 55.56% | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 9 | 5.5 | 3 | 2 | 0 | 6 | 0 | 0 | 1 | 0 | 0.21373 | 1 | 6.3299 | 1.3529 | Low | Low | High | Bottom | 675 | 621 | 6.3299
PLACER 1104 | 152461104 | NORTHERN | SIERRA | 1.6895 | 1114406.3333 | 42.5 | 29.92% | 2.335% | 25.27% | 24.57% | 0 | 0 | 2 | 25.35% | 26.82% | 0% | 3 | 12 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 16 | 29.2 | 1 | 2 | 0 | 6 | 0 | 0 | 2 | 0 | 0.2546 | 1 | 5.2079 | 1.3259 | Low | Low | Medium | Bottom | 676 | 690 | 5.2079
FORT ORD 2106 | 182402106 | CENTRAL COAST | CENTRAL COAST | 2.0208 | 481847.3333 | 45.25 | 110.4% | 0% | 0% | 0% | 0 | 0 | 0 | 0% | 64.18% | 0% | 1 | 0 | 0 | 0 | 39 | 1 | 0 | 5 | 9 | 40 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.29315 | 1 | 4.487 | 1.3154 | Low | Low | Medium | Bottom | 677 | 718 | 4.487
MERCED FALLS 1102 | 252811102 | CENTRAL VALLEY | YOSEMITE | 121.7278 | 1387449.6667 | 43.8872 | 0% | 1.165% | 74.99% | 0% | 2 | 0 | 103 | 88.44% | 0.08232% | 39.16% | 339 | 369 | 3 | 6 | 1235 | 219 | 0 | 11 | 26 | 2689 | 28.1762 | 492 | 290 | 17 | 1062 | 0 | 2 | 103 | 0 | 0.10838 | 3.5035 | 3.4266 | 1.3011 | Low | Medium | Low | Bottom | 678 | 494 | 12.0052
BELL 1109 | 152701109 | NORTHERN | SIERRA | 13.5619 | 554865.3333 | 42.1143 | 18.6% | 0% | 65.29% | 17.96% | 1 | 0 | 22 | 51.05% | 32.2% | 5.698% | 41 | 211 | 2 | 0 | 50 | 22 | 0 | 4 | 5 | 351 | 35.5733 | 68 | 39 | 6 | 152 | 0 | 0 | 22 | 0 | 0.29387 | 1 | 4.4251 | 1.3004 | Low | Low | Medium | Bottom | 679 | 721 | 4.4251
REEDLEY 1112 | 252341112 | CENTRAL VALLEY | FRESNO | 1.4284 | 1165789 | 44.0909 | 20.53% | 0% | 99.8% | 0.1962% | 0 | 0 | 1 | 99.8% | 0.1962% | 18.18% | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 11 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0.24502 | 2.0451 | 2.5413 | 1.2734 | Low | Low | Low | Bottom | 680 | 691 | 5.1972
ESTUDILLO 0401 | 013480401 | CENTRAL COAST | MISSION | 0.86867 | 127000 | 39.5652 | 9.741% | 0% | 70.62% | 23.67% | 1 | 0 | 3 | 21.47% | 72.82% | 13.04% | 1 | 4 | 0 | 0 | 10 | 1 | 0 | 0 | 0 | 23 | 14.5 | 2 | 7 | 1 | 10 | 0 | 0 | 3 | 0 | 0.28808 | 1 | 4.3503 | 1.2532 | Low | Low | Medium | Bottom | 681 | 726 | 4.3503
PRUNEDALE 1110 | 182961110 | CENTRAL COAST | CENTRAL COAST | 0.11844 | 1394297.3333 | 41.6667 | 0.2327% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 1 | 0.29459 | 1 | 4.2019 | 1.2378 | Low | Low | Medium | Bottom | 682 | 733 | 4.2019
SAN MIGUEL 1106 | 182661106 | CENTRAL COAST | LOS PADRES | 39.7691 | 362299 | 41.392 | 58.88% | 3.399% | 94.25% | 0.3695% | 0 | 0 | 10 | 96.61% | 3.388% | 5.666% | 42 | 9 | 0 | 48 | 178 | 40 | 0 | 0 | 0 | 353 | 24.5357 | 40 | 12 | 1 | 95 | 0 | 0 | 10 | 0 | 0.083464 | 5.814 | 2.5469 | 1.2359 | Low | Medium | Low | Bottom | 683 | 465 | 14.8075
SWIFT 2107 | 083392107 | CENTRAL COAST | SAN JOSE | 3.1689 | 1385965 | 43 | 8.6% | 0% | 50.39% | 49.61% | 1 | 0 | 3 | 50.39% | 49.61% | 7.5% | 0 | 7 | 1 | 1 | 13 | 2 | 0 | 1 | 1 | 40 | 33.1765 | 4 | 5 | 1 | 17 | 0 | 0 | 3 | 1 | 0.50063 | 1 | 2.4641 | 1.2336 | Medium | Low | Low | Bottom | 684 | 766 | 2.4641
WILLOW PASS 2107 | 013912107 | BAY AREA | DIABLO | 0.64814 | 1229122.3333 | 50 | 20.04% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 20% | 10 | 0 | 0 | 0 | 8 | 2 | 0 | 0 | 0 | 10 | 2.6667 | 3 | 0 | 0 | 3 | 0 | 0 | 1 | 0 | 0.25197 | 1 | 4.8811 | 1.2299 | Low | Low | Medium | Bottom | 685 | 705 | 4.8811
BURNEY 1102 | 103311102 | NORTHERN | NORTH VALLEY | 0.75732 | 217117 | 43.1667 | 27.27% | 95.7% | 4.303% | 0% | 0 | 0 | 3 | 65.2% | 34.8% | 6.667% | 8 | 16 | 0 | 0 | 9 | 2 | 0 | 5 | 8 | 30 | 48.4444 | 0 | 3 | 1 | 9 | 0 | 0 | 3 | 0 | 0.39507 | 1 | 3.0566 | 1.2076 | Medium | Low | Low | Bottom | 686 | 757 | 3.0566
BANGOR 1101 | 103191101 | NORTHERN | NORTH VALLEY | 198.8492 | 791087 | 42.4606 | 48.55% | 0.5655% | 84.37% | 6.825% | 16 | 17 | 173 | 83.4% | 8.32% | 4.776% | 421 | 2528 | 124 | 0 | 321 | 309 | 7 | 35 | 57 | 4439 | 41.3142 | 717 | 219 | 6 | 1540 | 0 | 8 | 172 | 0 | 0.1452 | 1.5986 | 5.1617 | 1.1981 | Low | Low | Medium | Bottom | 687 | 549 | 8.2517
MC KEE 1103 | 083531103 | CENTRAL COAST | SAN JOSE | 3.2596 | 768497.3333 | 44.5652 | 24.26% | 0% | 23.43% | 63.61% | 0 | 0 | 2 | 13.27% | 73.77% | 17.39% | 6 | 13 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 23 | 13.6667 | 0 | 1 | 0 | 6 | 0 | 0 | 2 | 0 | 0.2612 | 1.3747 | 3.3365 | 1.1981 | Low | Low | Low | Bottom | 688 | 713 | 4.5867
HIGGINS 1107 | 152691107 | NORTHERN | SIERRA | 17.5954 | 691949.3333 | 43.0574 | 37.22% | 0.02922% | 94.44% | 0% | 3 | 0 | 17 | 94.47% | 0% | 5.96% | 25 | 384 | 1 | 0 | 15 | 18 | 10 | 7 | 12 | 453 | 46.5368 | 92 | 59 | 6 | 192 | 0 | 0 | 17 | 0 | 0.21897 | 1.3406 | 4.0406 | 1.1861 | Low | Low | Medium | Bottom | 689 | 671 | 5.4168
COTTONWOOD 1102 | 102931102 | NORTHERN | NORTH VALLEY | 62.6112 | 771151.6667 | 41.6414 | 0% | 42.26% | 50.57% | 0.4287% | 2 | 0 | 57 | 92.83% | 0.4287% | 8.442% | 114 | 733 | 45 | 0 | 293 | 134 | 27 | 5 | 12 | 1386 | 49.295 | 206 | 118 | 2 | 455 | 0 | 1 | 57 | 0 | 0.08656 | 4.0518 | 3.3252 | 1.1662 | Low | Medium | Low | Bottom | 690 | 479 | 13.473
GIRVAN 1102 | 103401102 | NORTHERN | NORTH VALLEY | 46.0035 | 665380.3333 | 43.1333 | 37.64% | 36.8% | 43.85% | 0% | 4 | 1 | 62 | 93.18% | 1.609% | 10.01% | 199 | 698 | 20 | 1 | 176 | 143 | 0 | 14 | 33 | 1289 | 42.3467 | 186 | 137 | 5 | 465 | 0 | 2 | 62 | 0 | 0.065579 | 3.8498 | 4.6134 | 1.1647 | Low | Medium | Medium | Bottom | 691 | 438 | 17.7608
BROWNS VALLEY 1101 | 152921101 | NORTHERN | SIERRA | 41.7706 | 201976 | 42.608 | 31.69% | 0% | 89.81% | 7.84% | 4 | 0 | 37 | 82.72% | 17.28% | 4.742% | 84 | 489 | 27 | 0 | 107 | 59 | 0 | 10 | 19 | 949 | 40.0779 | 150 | 69 | 1 | 334 | 0 | 3 | 37 | 0 | 0.083871 | 3.0913 | 4.4402 | 1.1512 | Low | Medium | Medium | Bottom | 692 | 476 | 13.726
BELL 1108 | 152701108 | NORTHERN | SIERRA | 68.8953 | 1348734 | 43.0846 | 32.43% | 2.226% | 73.48% | 8.798% | 6 | 0 | 76 | 77.62% | 9.142% | 5.112% | 224 | 1117 | 6 | 0 | 123 | 83 | 25 | 16 | 24 | 1565 | 36.5314 | 292 | 257 | 39 | 715 | 0 | 3 | 75 | 0 | 0.11856 | 2.3851 | 4.0188 | 1.1365 | Low | Low | Medium | Bottom | 693 | 514 | 9.5852
SMARTVILLE 1101 | 153791101 | NORTHERN | SIERRA | 15.8868 | 96105 | 43.9017 | 44.78% | 0.3694% | 81.7% | 10.89% | 0 | 0 | 17 | 82.07% | 10.89% | 2.586% | 50 | 90 | 43 | 0 | 55 | 13 | 0 | 4 | 6 | 348 | 35.8868 | 50 | 28 | 2 | 115 | 0 | 1 | 17 | 0 | 0.16709 | 1.4125 | 4.7638 | 1.1243 | Low | Low | Medium | Bottom | 694 | 602 | 6.7286
WILLOW PASS 2108 | 013912108 | BAY AREA | DIABLO | 0.19204 | 1123036.3333 | 45 | 18.01% | 0% | 75.41% | 24.59% | 0 | 0 | 1 | 75.41% | 24.59% | 0% | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 87 | 0 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 0.23051 | 1 | 4.8379 | 1.1152 | Low | Low | Medium | Bottom | 695 | 707 | 4.8379
ANTLER 1101 | 103271101 | NORTHERN | NORTH VALLEY | 61.4203 | 341088.3333 | 41.8627 | 43.84% | 84.36% | 4.793% | 1.216% | 12 | 2 | 46 | 90.43% | 1.339% | 7.462% | 180 | 737 | 45 | 0 | 408 | 178 | 0 | 27 | 36 | 1635 | 43.2549 | 199 | 125 | 18 | 476 | 0 | 4 | 45 | 0 | 0.12287 | 2.813 | 3.1543 | 1.0903 | Low | Medium | Low | Bottom | 696 | 531 | 8.873
WILLOW PASS 1101 | 013911101 | BAY AREA | DIABLO | 0.8295 | 370736.6667 | 47 | 63.82% | 10.52% | 62.15% | 0% | 0 | 0 | 2 | 72.66% | 0% | 40% | 9 | 6 | 0 | 0 | 1 | 3 | 0 | 0 | 1 | 15 | 0.66667 | 1 | 1 | 0 | 4 | 0 | 0 | 2 | 0 | 0.27234 | 1 | 3.9927 | 1.0874 | Low | Low | Medium | Bottom | 697 | 739 | 3.9927
LAKEWOOD 2110 | 013532110 | BAY AREA | DIABLO | 0.50309 | 1187370 | 0 | 9.113% | 0% | 73.94% | 10.16% | 0 | 0 | 0 | 31.68% | 52.42% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15113 | 1 | 7.1259 | 1.0769 | Low | Low | High | Bottom | 698 | 581 | 7.1259
DOLAN ROAD 1101 | 182381101 | CENTRAL COAST | CENTRAL COAST | 6.1776 | 415279.6667 | 39.9324 | 9.734% | 0% | 69.26% | 21.58% | 0 | 0 | 2 | 73.63% | 21.58% | 14.86% | 1 | 30 | 0 | 0 | 34 | 2 | 0 | 0 | 1 | 74 | 19.7179 | 12 | 5 | 0 | 40 | 0 | 0 | 2 | 0 | 0.22086 | 1 | 4.8606 | 1.0735 | Low | Low | Medium | Bottom | 699 | 706 | 4.8606
CLARK ROAD 1102 | 103091102 | NORTHERN | NORTH VALLEY | 126.4512 | 506713.6667 | 42.3085 | 57.53% | 1.404% | 83.59% | 7.319% | 3 | 1 | 107 | 80.81% | 13.46% | 6.255% | 237 | 1205 | 59 | 0 | 355 | 171 | 4 | 28 | 42 | 2510 | 42.8078 | 336 | 133 | 7 | 730 | 0 | 13 | 104 | 0 | 0.047318 | 4.2677 | 5.2944 | 1.0692 | Low | Medium | Medium | Bottom | 700 | 393 | 22.5952
JESSUP 1102 | 103441102 | NORTHERN | NORTH VALLEY | 55.2091 | 877468 | 40.9455 | 0% | 67.4% | 22.82% | 0.03146% | 3 | 3 | 65 | 90.16% | 0.08954% | 6.697% | 54 | 1031 | 45 | 0 | 125 | 91 | 2 | 7 | 12 | 1523 | 42.5389 | 281 | 108 | 3 | 578 | 0 | 6 | 65 | 0 | 0.056661 | 5.3608 | 3.5021 | 1.0638 | Low | Medium | Low | Bottom | 701 | 427 | 18.7745
SEACLIFF 0402 | 083500402 | CENTRAL COAST | CENTRAL COAST | 1.0712 | 24358 | 40 | 86.6% | 0% | 21.9% | 76.41% | 1 | 0 | 0 | 21.9% | 76.41% | 0% | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.17641 | 1 | 5.9918 | 1.057 | Low | Low | High | Bottom | 702 | 635 | 5.9918
LINCOLN 1101 | 153701101 | NORTHERN | SIERRA | 15.4033 | 1254118 | 42.8797 | 17.41% | 0.2279% | 69.74% | 15.81% | 3 | 0 | 24 | 69.66% | 16.12% | 8.857% | 47 | 232 | 1 | 0 | 26 | 15 | 0 | 3 | 5 | 350 | 31.0065 | 72 | 43 | 3 | 158 | 0 | 0 | 24 | 0 | 0.2797 | 1 | 3.7779 | 1.0567 | Low | Low | Medium | Bottom | 703 | 746 | 3.7779
POSO MOUNTAIN 2103 | 253642103 | CENTRAL VALLEY | KERN | 19.5559 | 2531102 | 41.4823 | 634.8% | 53.78% | 6.828% | 4.128% | 0 | 0 | 4 | 59.97% | 4.774% | 13.72% | 7 | 7 | 0 | 39 | 17 | 19 | 0 | 1 | 5 | 226 | 9.2308 | 5 | 1 | 0 | 26 | 0 | 0 | 4 | 0 | 0.30673 | 11.9418 | 0.2873 | 1.0524 | Low | Medium | Low | Bottom | 704 | 752 | 3.4309
CORRAL 1102 | 162991102 | CENTRAL VALLEY | STOCKTON | 51.2858 | 770762.3333 | 43.7391 | 73.37% | 0.5883% | 75.4% | 11.43% | 1 | 0 | 44 | 75.99% | 11.43% | 10.18% | 304 | 620 | 6 | 0 | 249 | 103 | 0 | 3 | 11 | 1267 | 32.2722 | 252 | 174 | 9 | 533 | 0 | 0 | 44 | 0 | 0.050231 | 3.8123 | 5.4683 | 1.0472 | Low | Medium | High | Bottom | 705 | 407 | 20.8467
PANORAMA 1101 | 103461101 | NORTHERN | NORTH VALLEY | 12.3478 | 578348.6667 | 46.6862 | 34.74% | 89.3% | 5.86% | 0% | 0 | 0 | 16 | 95.16% | 0% | 6.776% | 192 | 291 | 4 | 1 | 16 | 76 | 0 | 0 | 2 | 428 | 60.6062 | 127 | 128 | 25 | 302 | 0 | 1 | 16 | 0 | 0.19097 | 1 | 5.4631 | 1.0433 | Low | Low | High | Bottom | 706 | 668 | 5.4631
ALTO 1121 | 042031121 | BAY AREA | NORTH BAY | 0.066131 | 581015 | 0 | 1.842% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15069 | 1 | 6.8577 | 1.0334 | Low | Low | High | Bottom | 707 | 592 | 6.8577
COAST RD 0401 | 088820401 | CENTRAL COAST | CENTRAL COAST | 2.6666 | 0 | 40 | 36.1% | 36.1% | 0% | 16.75% | 0 | 0 | 1 | 0% | 100% | 0% | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 3 | 0 | 0 | 1 | 0 | 0.17721 | 1 | 5.7489 | 1.0187 | Low | Low | High | Bottom | 708 | 654 | 5.7489
WYANDOTTE 1109 | 102911109 | NORTHERN | NORTH VALLEY | 56.7801 | 1419512 | 42.1136 | 31.89% | 0.2035% | 79.09% | 14.66% | 2 | 0 | 42 | 74% | 19.88% | 3.313% | 133 | 704 | 28 | 0 | 163 | 24 | 0 | 7 | 11 | 1298 | 41.1795 | 231 | 83 | 2 | 498 | 0 | 0 | 42 | 0 | 0.085646 | 2.0554 | 5.745 | 1.0114 | Low | Low | High | Bottom | 709 | 495 | 11.8085
FROGTOWN 1701 | 163451701 | CENTRAL VALLEY | STOCKTON | 70.7853 | 668544.6667 | 43.2019 | 45.77% | 44.34% | 42.74% | 1.166% | 4 | 1 | 86 | 81.99% | 6.255% | 7.251% | 302 | 744 | 0 | 0 | 482 | 100 | 0 | 10 | 26 | 1710 | 24.0812 | 237 | 136 | 17 | 570 | 0 | 1 | 86 | 0 | 0.066096 | 2.7561 | 5.5434 | 1.0098 | Low | Medium | High | Bottom | 710 | 460 | 15.2784
MONTEREY 0401 | 182090401 | CENTRAL COAST | CENTRAL COAST | 0.30119 | 192386.6667 | 42.7273 | 79.84% | 0% | 69.45% | 19.02% | 0 | 0 | 0 | 0% | 88.47% | 18.18% | 0 | 2 | 0 | 0 | 5 | 0 | 0 | 0 | 1 | 11 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.16998 | 1 | 5.9171 | 1.0058 | Low | Low | High | Bottom | 711 | 639 | 5.9171
RED BLUFF 1104 | 103541104 | NORTHERN | NORTH VALLEY | 71.2322 | 647331.3333 | 41.8722 | 81.92% | 12.93% | 72.82% | 6.502% | 2 | 4 | 34 | 89.91% | 6.617% | 6.063% | 115 | 516 | 48 | 0 | 265 | 136 | 0 | 12 | 19 | 1336 | 44.7473 | 168 | 110 | 10 | 386 | 0 | 4 | 34 | 0 | 0.041784 | 7.4316 | 3.1769 | 0.98649 | Low | Medium | Low | Bottom | 712 | 389 | 23.6094
PENRYN 1106 | 152561106 | NORTHERN | SIERRA | 1.0234 | 977537 | 39.0909 | 1.374% | 0% | 37.58% | 62.42% | 0 | 0 | 0 | 37.58% | 62.42% | 18.18% | 1 | 12 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 22 | 17.75 | 1 | 1 | 1 | 4 | 0 | 0 | 0 | 0 | 0.18875 | 1 | 5.2111 | 0.98359 | Low | Low | Medium | Bottom | 713 | 687 | 5.2111
WEIMAR 1102 | 152491102 | NORTHERN | SIERRA | 23.0263 | 158885.3333 | 41.8349 | 22.14% | 53.36% | 15.48% | 14.14% | 1 | 5 | 41 | 73.63% | 14.14% | 6.56% | 44 | 402 | 3 | 0 | 79 | 45 | 6 | 6 | 12 | 625 | 36.6398 | 154 | 111 | 5 | 350 | 0 | 0 | 40 | 0 | 0.24313 | 1.0248 | 3.9433 | 0.98249 | Low | Low | Medium | Bottom | 714 | 738 | 4.041
SHINGLE SPRINGS 2110 | 153652110 | NORTHERN | SIERRA | 63.9953 | 1226260.6667 | 42.4151 | 45.26% | 0.2067% | 83.25% | 5.136% | 7 | 0 | 83 | 83.46% | 5.097% | 2.134% | 173 | 1013 | 12 | 0 | 308 | 69 | 13 | 15 | 27 | 1593 | 42.395 | 338 | 181 | 15 | 644 | 0 | 6 | 83 | 0 | 0.050897 | 4.0293 | 4.7906 | 0.98245 | Low | Medium | Medium | Bottom | 715 | 422 | 19.3026
BANCROFT 0402 | 013030402 | BAY AREA | EAST BAY | 1.1676 | 137398.3333 | 43.3333 | 0% | 0% | 66.62% | 25.97% | 0 | 0 | 0 | 1.548% | 91.05% | 50% | 1 | 2 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 12 | 44.6 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 0 | 0.23001 | 1 | 4.2377 | 0.97474 | Low | Low | Medium | Bottom | 716 | 731 | 4.2377
SAN LEANDRO U 1107 | 013111107 | CENTRAL COAST | MISSION | 0.097818 | 1147965 | 0 | 1.3% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20554 | 1 | 4.68 | 0.96191 | Low | Low | Medium | Bottom | 717 | 711 | 4.68
SCE VEGAS 1701 | 188881701 | CENTRAL COAST | LOS PADRES | 0.17032 | 0 | 0 | 0% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.23885 | 1 | 3.9643 | 0.94686 | Low | Low | Medium | Bottom | 718 | 740 | 3.9643
DIAMOND SPRINGS 1103 | 152261103 | NORTHERN | SIERRA | 35.304 | 845974.3333 | 42.1526 | 20.18% | 37.61% | 37.93% | 10.24% | 4 | 6 | 53 | 75.54% | 11.02% | 1.149% | 110 | 513 | 9 | 0 | 236 | 47 | 0 | 4 | 12 | 957 | 43.9837 | 200 | 146 | 9 | 433 | 0 | 0 | 53 | 0 | 0.11388 | 1.9067 | 4.2233 | 0.91703 | Low | Low | Medium | Bottom | 719 | 554 | 8.0525
CLAYTON 2217 | 012022217 | BAY AREA | DIABLO | 0.67567 | 1167387 | 0 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14964 | 1 | 6.1247 | 0.9165 | Low | Low | High | Bottom | 720 | 632 | 6.1247
OREGON TRAIL 1103 | 103521103 | NORTHERN | NORTH VALLEY | 118.6709 | 743676.6667 | 42.5605 | 47.64% | 60.02% | 31.71% | 0.2304% | 2 | 0 | 117 | 95.36% | 0.3707% | 8.405% | 379 | 1728 | 86 | 3 | 437 | 244 | 3 | 22 | 38 | 3141 | 44.1023 | 472 | 252 | 12 | 1023 | 0 | 8 | 117 | 0 | 0.062522 | 3.3776 | 4.3191 | 0.91208 | Low | Medium | Medium | Bottom | 721 | 468 | 14.5882
NEWBURG 1132 | 192151132 | NORTHERN | HUMBOLDT | 2.5461 | 888833.3333 | 40.119 | 3.343% | 0% | 16% | 83.22% | 0 | 0 | 1 | 16% | 83.22% | 42.86% | 2 | 5 | 0 | 0 | 30 | 2 | 4 | 0 | 0 | 42 | 40.9333 | 2 | 1 | 0 | 16 | 0 | 0 | 1 | 0 | 0.31788 | 1 | 2.8437 | 0.90395 | Low | Low | Low | Bottom | 722 | 760 | 2.8437
VASONA 1102 | 083771102 | CENTRAL COAST | DE ANZA | 0.075415 | 960837.3333 | 38 | 2.142% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 5 | 0 | 2 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.10648 | 1 | 8.4479 | 0.8995 | Low | Low | High | Bottom | 723 | 545 | 8.4479
OAKLAND J 1116 | 012091116 | BAY AREA | EAST BAY | 0.10355 | 1036186 | 40.7143 | 7.798% | 0% | 100% | 0% | 0 | 0 | 0 | 0% | 100% | 42.86% | 0 | 1 | 0 | 0 | 4 | 2 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13957 | 1 | 6.4353 | 0.89816 | Low | Low | High | Bottom | 724 | 616 | 6.4353
MESA 1103 | 182821103 | CENTRAL COAST | LOS PADRES | 12.4594 | 1425053 | 44.5775 | 7.311% | 0% | 72.42% | 11.33% | 2 | 0 | 21 | 72.42% | 11.33% | 9.722% | 56 | 8 | 0 | 44 | 66 | 50 | 0 | 1 | 2 | 216 | 27.7941 | 37 | 9 | 1 | 105 | 0 | 0 | 20 | 0 | 0.19267 | 1.1375 | 4.0787 | 0.89387 | Low | Low | Medium | Bottom | 725 | 712 | 4.6394
SO. CAL. EDISON #2 1101 | 258851101 | CENTRAL VALLEY | YOSEMITE | 1.1766 | 1647 | 44.375 | 0% | 64.34% | 35.66% | 0% | 0 | 0 | 0 | 100% | 0% | 27.27% | 4 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.36946 | 1 | 2.3755 | 0.87763 | Medium | Low | Low | Bottom | 726 | 768 | 2.3755
OAKLAND J 1118 | 012091118 | BAY AREA | EAST BAY | 0.75276 | 549257.6667 | 44.6667 | 21.9% | 0% | 92.61% | 7.387% | 0 | 0 | 0 | 17.8% | 82.2% | 0% | 0 | 1 | 0 | 0 | 11 | 1 | 0 | 0 | 0 | 15 | 15 | 0 | 3 | 2 | 5 | 0 | 0 | 0 | 0 | 0.17051 | 1 | 5.115 | 0.87215 | Low | Low | Medium | Bottom | 727 | 697 | 5.115
SANTA ROSA A 1110 | 042151110 | NORTHERN | SONOMA | 0.037484 | 897090.6667 | 0 | 1.125% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19275 | 1 | 4.513 | 0.8699 | Low | Low | Medium | Bottom | 728 | 717 | 4.513
LONE TREE 2105 | 013232105 | BAY AREA | DIABLO | 10.6094 | 907615.3333 | 46.4773 | 17.08% | 0% | 96.44% | 3.562% | 0 | 0 | 9 | 95.57% | 4.426% | 14.77% | 34 | 94 | 0 | 0 | 12 | 6 | 0 | 0 | 0 | 176 | 35.5946 | 11 | 18 | 1 | 42 | 0 | 0 | 9 | 0 | 0.21788 | 1 | 3.9619 | 0.86319 | Low | Low | Medium | Bottom | 729 | 741 | 3.9619
STELLING 1109 | 083481109 | CENTRAL COAST | DE ANZA | 0.65955 | 933086 | 45.5769 | 16.19% | 0% | 83.51% | 4.856% | 0 | 0 | 2 | 83.51% | 16.49% | 3.846% | 6 | 11 | 0 | 0 | 8 | 3 | 0 | 0 | 0 | 26 | 0 | 6 | 3 | 0 | 12 | 0 | 0 | 2 | 0 | 0.15296 | 1 | 5.6048 | 0.85733 | Low | Low | High | Bottom | 730 | 662 | 5.6048
BELLEVUE 1102 | 043181102 | NORTHERN | SONOMA | 0.26889 | 926382.3333 | 55 | 0.1733% | 0% | 2.546% | 0% | 0 | 0 | 0 | 0% | 2.546% | 0% | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 70 | 0 | 1 | 1 | 2 | 0 | 0 | 0 | 0 | 0.27028 | 1 | 3.1712 | 0.8571 | Low | Low | Low | Bottom | 731 | 756 | 3.1712
SAND CREEK 1103 | 254601103 | CENTRAL VALLEY | FRESNO | 149.7701 | 442223.3333 | 42.4289 | 59.2% | 16.96% | 68.29% | 0.003395% | 7 | 6 | 102 | 95.28% | 0.003395% | 29.38% | 279 | 462 | 0 | 262 | 1101 | 213 | 0 | 9 | 23 | 2999 | 16.3756 | 520 | 171 | 6 | 1198 | 0 | 0 | 102 | 0 | 0.10796 | 2.3955 | 3.2681 | 0.8452 | Low | Medium | Low | Bottom | 732 | 562 | 7.8287
DEL MAR 1103 | 152581103 | NORTHERN | SIERRA | 0.034858 | 435349.3333 | 0 | 0.3486% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15089 | 1 | 5.5468 | 0.83698 | Low | Low | High | Bottom | 733 | 665 | 5.5468
DIAMOND SPRINGS 1106 | 152261106 | NORTHERN | SIERRA | 111.1641 | 910047.3333 | 42.3542 | 21.14% | 50.87% | 39.12% | 2.759% | 6 | 6 | 145 | 90.16% | 2.867% | 1.338% | 225 | 1554 | 44 | 0 | 468 | 170 | 6 | 13 | 21 | 2840 | 40.1305 | 599 | 221 | 12 | 1114 | 0 | 3 | 145 | 0 | 0.087538 | 2.5895 | 3.6341 | 0.82376 | Low | Medium | Low | Bottom | 734 | 520 | 9.4103
AUBERRY 1102 | 254151102 | CENTRAL VALLEY | FRESNO | 127.9128 | 604229.6667 | 41.5586 | 28.6% | 6.247% | 83.97% | 0.2351% | 0 | 5 | 129 | 89.34% | 1.146% | 30.21% | 106 | 167 | 0 | 253 | 780 | 244 | 0 | 15 | 29 | 2208 | 17.2949 | 512 | 211 | 22 | 1137 | 0 | 0 | 129 | 0 | 0.098189 | 3.2245 | 2.5632 | 0.81154 | Low | Medium | Low | Bottom | 735 | 548 | 8.265
CARMEL 0405 | 182040405 | CENTRAL COAST | CENTRAL COAST | 0.54211 | 183473.6667 | 0 | 14.22% | 0% | 82.89% | 17.11% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14108 | 1 | 5.7517 | 0.81142 | Low | Low | High | Bottom | 736 | 653 | 5.7517
RISING RIVER 1101 | 103551101 | NORTHERN | NORTH VALLEY | 49.9892 | 170107.3333 | 40.6554 | 93.85% | 84.68% | 0.9855% | 0.04943% | 10 | 2 | 39 | 83.99% | 1.994% | 25.66% | 45 | 423 | 2 | 0 | 388 | 80 | 18 | 8 | 17 | 1091 | 28.8968 | 113 | 63 | 4 | 320 | 0 | 3 | 39 | 0 | 0.31716 | 1.5403 | 1.6242 | 0.79347 | Low | Low | Low | Bottom | 737 | 765 | 2.5018
RED BLUFF 1101 | 103541101 | NORTHERN | NORTH VALLEY | 48.8637 | 558800.6667 | 40.8648 | 19.94% | 7.923% | 92.07% | 0% | 3 | 0 | 25 | 99.99% | 0% | 10.26% | 22 | 669 | 40 | 0 | 148 | 126 | 0 | 3 | 3 | 1140 | 50.2513 | 216 | 64 | 6 | 387 | 0 | 2 | 25 | 0 | 0.067369 | 4.7159 | 2.4645 | 0.783 | Low | Medium | Low | Bottom | 738 | 497 | 11.6225
TIVY VALLEY 1107 | 252941107 | CENTRAL VALLEY | FRESNO | 122.1496 | 758900.6667 | 41.6268 | 53.64% | 15.55% | 80.65% | 0.7768% | 9 | 3 | 84 | 95.12% | 3.052% | 28.24% | 106 | 204 | 0 | 190 | 680 | 182 | 0 | 12 | 26 | 2015 | 18.0469 | 337 | 162 | 16 | 823 | 0 | 1 | 82 | 0 | 0.1277 | 2.3799 | 2.5509 | 0.77522 | Low | Low | Low | Bottom | 739 | 633 | 6.0709
OLETA 1102 | 163541102 | CENTRAL VALLEY | STOCKTON | 65.7192 | 435994 | 43.7225 | 32.18% | 2.003% | 83.86% | 9.889% | 2 | 0 | 45 | 83.64% | 12.11% | 3.201% | 224 | 697 | 4 | 1 | 223 | 95 | 0 | 5 | 9 | 1281 | 34.8693 | 145 | 64 | 9 | 350 | 0 | 0 | 43 | 0 | 0.040535 | 3.9755 | 4.7775 | 0.76989 | Low | Medium | Medium | Bottom | 740 | 425 | 18.993
GREENBRAE 1104 | 043091104 | BAY AREA | NORTH BAY | 0.37143 | 843442.6667 | 44.5455 | 40.95% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 10 | 1 | 0 | 0 | 0 | 11 | 10.3333 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0.11506 | 1 | 6.6496 | 0.76508 | Low | Low | High | Bottom | 741 | 607 | 6.6496
WYANDOTTE 1107 | 102911107 | NORTHERN | NORTH VALLEY | 106.7969 | 810745 | 41.8392 | 36.08% | 1.122% | 84.3% | 8.984% | 8 | 3 | 72 | 83.97% | 10.45% | 4.967% | 191 | 1673 | 36 | 2 | 203 | 123 | 2 | 9 | 17 | 2577 | 40.75 | 437 | 146 | 5 | 952 | 0 | 2 | 72 | 0 | 0.041139 | 2.9393 | 6.2964 | 0.76135 | Low | Medium | High | Bottom | 742 | 430 | 18.5071
SAN JOAQUIN #2 1103 | 252521103 | CENTRAL VALLEY | YOSEMITE | 82.7368 | 0 | 40.7023 | 70.75% | 24.8% | 64.51% | 0.9869% | 4 | 1 | 63 | 95.56% | 3.878% | 24.95% | 55 | 282 | 0 | 3 | 535 | 189 | 0 | 11 | 19 | 1551 | 24.2935 | 267 | 99 | 18 | 659 | 0 | 2 | 62 | 0 | 0.19463 | 1.3732 | 2.847 | 0.7609 | Low | Low | Low | Bottom | 743 | 743 | 3.9094
EAST MARYSVILLE 1108 | 152331108 | NORTHERN | SIERRA | 0.72214 | 645128.6667 | 49.4737 | 235.6% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 0% | 6 | 3 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 19 | 58 | 1 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0.22041 | 1 | 3.2275 | 0.71136 | Low | Low | Low | Bottom | 744 | 754 | 3.2275
SERRAMONTE 1104 | 022861104 | CENTRAL COAST | PENINSULA | 0.061541 | 836402 | 0 | 12.92% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1413 | 1 | 4.9418 | 0.69828 | Low | Low | Medium | Bottom | 745 | 703 | 4.9418
PEABODY 2106 | 063642106 | NORTHERN | SACRAMENTO | 1.0067 | 1339227.6667 | 44.375 | 294.9% | 0% | 71.61% | 0% | 0 | 0 | 1 | 71.61% | 0% | 12.5% | 0 | 9 | 0 | 0 | 4 | 2 | 0 | 0 | 0 | 16 | 13 | 0 | 0 | 1 | 4 | 0 | 0 | 1 | 0 | 0.17102 | 1 | 4.056 | 0.69365 | Low | Low | Medium | Bottom | 746 | 737 | 4.056
LLAGAS 2105 | 083182105 | CENTRAL COAST | SAN JOSE | 1.0027 | 1887415.3333 | 39.1667 | 44.62% | 0% | 28.55% | 71.45% | 0 | 0 | 0 | 28.55% | 71.45% | 25% | 2 | 6 | 0 | 0 | 4 | 0 | 0 | 1 | 1 | 12 | 2.3333 | 1 | 1 | 0 | 3 | 0 | 0 | 0 | 0 | 0.17908 | 1 | 3.8581 | 0.69092 | Low | Low | Medium | Bottom | 747 | 745 | 3.8581
DESCHUTES 1101 | 103351101 | NORTHERN | NORTH VALLEY | 114.8711 | 486589.3333 | 41.1437 | 66.27% | 61.81% | 33.84% | 1.545% | 6 | 1 | 79 | 95.65% | 1.545% | 9.249% | 183 | 1490 | 93 | 1 | 308 | 255 | 0 | 11 | 23 | 2584 | 47.1203 | 288 | 163 | 14 | 677 | 0 | 12 | 79 | 0 | 0.044915 | 4.2763 | 3.5025 | 0.67273 | Low | Medium | Low | Bottom | 748 | 462 | 14.9779
ATASCADERO 1102 | 182541102 | CENTRAL COAST | LOS PADRES | 0.06615 | 401190.6667 | 40.5405 | 2.402% | 0% | 100% | 0% | 0 | 0 | 1 | 100% | 0% | 13.51% | 5 | 1 | 0 | 1 | 29 | 1 | 0 | 0 | 0 | 37 | 50.625 | 7 | 5 | 0 | 16 | 0 | 0 | 1 | 0 | 0.18797 | 1 | 3.5119 | 0.66013 | Low | Low | Low | Bottom | 749 | 750 | 3.5119
JESSUP 1101 | 103441101 | NORTHERN | NORTH VALLEY | 66.1287 | 798939 | 41.3006 | 0% | 57.53% | 38.98% | 0% | 5 | 0 | 58 | 96.41% | 0.4507% | 7.582% | 163 | 1135 | 44 | 0 | 201 | 135 | 0 | 12 | 23 | 1807 | 39.5921 | 288 | 144 | 12 | 687 | 0 | 7 | 58 | 0 | 0.042059 | 4.3919 | 3.5388 | 0.65369 | Low | Medium | Low | Bottom | 750 | 457 | 15.5421
HIGGINS 1103 | 152691103 | NORTHERN | SIERRA | 75.7487 | 680134.6667 | 42.9244 | 42.22% | 6.927% | 75.99% | 0.3822% | 6 | 4 | 107 | 83.25% | 0.3822% | 11.41% | 176 | 1365 | 6 | 0 | 249 | 131 | 0 | 6 | 26 | 2007 | 41.9881 | 432 | 162 | 15 | 859 | 0 | 4 | 106 | 0 | 0.056665 | 2.4937 | 4.465 | 0.63094 | Low | Medium | Medium | Bottom | 751 | 501 | 11.1346
OREGON TRAIL 1104 | 103521104 | NORTHERN | NORTH VALLEY | 46.6336 | 454202.6667 | 42.6543 | 48.06% | 45.35% | 41.08% | 0.05981% | 0 | 0 | 64 | 86.28% | 0.2109% | 7.73% | 129 | 714 | 12 | 0 | 194 | 96 | 0 | 5 | 9 | 1216 | 42.5193 | 178 | 122 | 9 | 458 | 0 | 2 | 64 | 0 | 0.032789 | 4.4935 | 4.2518 | 0.62645 | Low | Medium | Medium | Bottom | 752 | 423 | 19.1052
OREGON TRAIL 1102 | 103521102 | NORTHERN | NORTH VALLEY | 46.8334 | 435781.3333 | 43.1527 | 54.14% | 40.11% | 44.99% | 0% | 2 | 0 | 32 | 85.51% | 0.0627% | 6.973% | 175 | 688 | 25 | 0 | 200 | 94 | 2 | 12 | 29 | 1176 | 43.0439 | 169 | 99 | 6 | 402 | 0 | 5 | 32 | 0 | 0.046428 | 2.7529 | 4.8585 | 0.62096 | Low | Medium | Medium | Bottom | 753 | 481 | 13.3748
PLACERVILLE 1112 | 153081112 | NORTHERN | SIERRA | 27.7419 | 782510.3333 | 42.0833 | 27.34% | 53.09% | 21.45% | 9.376% | 5 | 0 | 49 | 73.74% | 10.17% | 1.063% | 108 | 405 | 23 | 0 | 257 | 50 | 2 | 4 | 10 | 941 | 51.9846 | 163 | 130 | 29 | 395 | 0 | 0 | 49 | 0 | 0.14218 | 1 | 4.2874 | 0.60958 | Low | Low | Medium | Bottom | 754 | 729 | 4.2874
STILLWATER 1101 | 103561101 | NORTHERN | NORTH VALLEY | 36.1073 | 327931.3333 | 42.6121 | 40.19% | 54.86% | 25% | 2.059% | 3 | 0 | 46 | 87.51% | 2.675% | 10.53% | 149 | 577 | 31 | 0 | 154 | 107 | 0 | 6 | 14 | 1073 | 34.6416 | 131 | 82 | 7 | 365 | 0 | 2 | 46 | 0 | 0.073854 | 1.8134 | 4.5151 | 0.60469 | Low | Low | Medium | Bottom | 755 | 551 | 8.1877
SWIFT 2102 | 083392102 | CENTRAL COAST | SAN JOSE | 0.43953 | 1152399 | 44.5 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0.24835 | 1 | 2.373 | 0.58934 | Low | Low | Low | Bottom | 756 | 769 | 2.373
WESTLEY 1103 | 162671103 | CENTRAL VALLEY | YOSEMITE | 0.92376 | 1373691.3333 | 0 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.20126 | 1 | 2.9097 | 0.5856 | Low | Low | Low | Bottom | 757 | 759 | 2.9097
SWIFT 2109 | 083392109 | CENTRAL COAST | SAN JOSE | 0.49434 | 1180547 | 43.3333 | 4.779% | 0% | 54.76% | 45.24% | 0 | 0 | 1 | 54.15% | 45.85% | 33.33% | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 27.5 | 2 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 0.22298 | 1 | 2.6247 | 0.58525 | Low | Low | Low | Bottom | 758 | 761 | 2.6247
NARROWS 2102 | 153132102 | NORTHERN | SIERRA | 96.3992 | 1160087.6667 | 42.8608 | 41.46% | 4.305% | 80.42% | 2.279% | 3 | 0 | 154 | 84.91% | 2.279% | 9.627% | 117 | 1399 | 5 | 0 | 136 | 217 | 0 | 8 | 27 | 2171 | 52.4735 | 369 | 185 | 8 | 819 | 0 | 1 | 154 | 0 | 0.043566 | 2.6317 | 5.0863 | 0.58317 | Low | Medium | Medium | Bottom | 759 | 480 | 13.3857
FORT BRAGG A 1103 | 042761103 | NORTHERN | HUMBOLDT | 0.50874 | 386751 | 40 | 2.71% | 0% | 0% | 100% | 1 | 0 | 0 | 0% | 100% | 0% | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 3 | 49 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0.15568 | 1 | 3.7413 | 0.58244 | Low | Low | Low | Bottom | 760 | 747 | 3.7413
SAN BERNARD 1101 | 253191101 | CENTRAL VALLEY | KERN | 1.7421 | 784387.3333 | 42.1429 | 70.29% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 42.86% | 2 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 14 | 6 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0.22097 | 1 | 2.5803 | 0.57017 | Low | Low | Low | Bottom | 761 | 764 | 2.5803
TEJON 1103 | 252931103 | CENTRAL VALLEY | KERN | 3.2497 | 897475.6667 | 40.8824 | 4.224% | 0% | 100% | 0% | 0 | 0 | 1 | 88.41% | 11.59% | 52.94% | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 17 | 1.2 | 1 | 0 | 0 | 6 | 0 | 0 | 1 | 0 | 0.18525 | 1 | 2.954 | 0.54721 | Low | Low | Low | Bottom | 762 | 758 | 2.954
STILLWATER 1102 | 103561102 | NORTHERN | NORTH VALLEY | 78.3748 | 518238.3333 | 42.6453 | 42.29% | 77.66% | 16.93% | 0% | 8 | 5 | 63 | 94.68% | 0% | 11.96% | 241 | 1330 | 52 | 2 | 272 | 284 | 0 | 18 | 25 | 2299 | 46.4434 | 381 | 218 | 12 | 843 | 0 | 7 | 63 | 0 | 0.079759 | 1.606 | 4.1614 | 0.53305 | Low | Low | Medium | Bottom | 763 | 605 | 6.6833
BRENTWOOD 2105 | 014592105 | BAY AREA | DIABLO | 10.7235 | 1598214.6667 | 48.0282 | 23.28% | 0% | 79.56% | 0.7279% | 3 | 0 | 18 | 79.56% | 0.7279% | 14.08% | 56 | 36 | 1 | 0 | 17 | 19 | 0 | 3 | 6 | 142 | 33.3421 | 12 | 7 | 1 | 50 | 0 | 0 | 18 | 0 | 0.28358 | 1 | 1.8205 | 0.51626 | Low | Low | Low | Bottom | 764 | 771 | 1.8205
MC ARTHUR 1102 | 103491102 | NORTHERN | NORTH VALLEY | 2.2681 | 280004 | 42.2973 | 16.68% | 100% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 37.84% | 0 | 6 | 0 | 0 | 15 | 4 | 0 | 0 | 0 | 37 | 28.8333 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0.39471 | 3.3784 | 0.37689 | 0.50258 | Medium | Medium | Low | Bottom | 765 | 776 | 1.2733
HIGGINS 1104 | 152691104 | NORTHERN | SIERRA | 71.3117 | 882750.6667 | 43.8098 | 60.2% | 44.82% | 29.59% | 0% | 8 | 0 | 107 | 79.96% | 0% | 13.54% | 308 | 1332 | 13 | 1 | 60 | 229 | 0 | 19 | 34 | 1890 | 49.9248 | 434 | 324 | 31 | 902 | 0 | 2 | 100 | 0 | 0.088904 | 1.0484 | 5.0837 | 0.47386 | Low | Low | Medium | Bottom | 766 | 678 | 5.33
HIGGINS 1110 | 152691110 | NORTHERN | SIERRA | 51.6137 | 531035.6667 | 43.0525 | 38.98% | 2.132% | 82.19% | 0% | 6 | 1 | 79 | 87.32% | 0% | 11.38% | 102 | 808 | 9 | 3 | 41 | 127 | 5 | 13 | 19 | 1186 | 39.8986 | 219 | 103 | 6 | 444 | 0 | 5 | 79 | 0 | 0.098957 | 1.0828 | 4.0439 | 0.43328 | Low | Low | Medium | Bottom | 767 | 723 | 4.3785
PIT NO 7 1101 | 103501101 | NORTHERN | NORTH VALLEY | 2.7098 | 24 | 37.2881 | 46.77% | 100% | 0% | 0% | 0 | 0 | 1 | 100% | 0% | 1.695% | 0 | 31 | 3 | 0 | 15 | 0 | 0 | 0 | 0 | 59 | 75 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0.35697 | 1 | 1.1934 | 0.42598 | Medium | Low | Low | Bottom | 768 | 777 | 1.1934
PIT NO 1 1101 | 103721101 | NORTHERN | NORTH VALLEY | 27.8419 | 391147 | 41.2516 | 91.04% | 80.42% | 7.618% | 0.6016% | 0 | 0 | 31 | 79.09% | 20.74% | 17.39% | 33 | 408 | 1 | 39 | 134 | 70 | 0 | 7 | 13 | 782 | 29.2965 | 77 | 45 | 4 | 212 | 0 | 2 | 30 | 0 | 0.20078 | 1.1824 | 1.7429 | 0.41377 | Low | Low | Low | Bottom | 769 | 770 | 2.0608
RAWSON 1103 | 103531103 | NORTHERN | NORTH VALLEY | 5.0552 | 1257835.6667 | 40.1695 | 10.33% | 0% | 90.01% | 9.99% | 0 | 0 | 2 | 90.01% | 9.99% | 1.695% | 3 | 18 | 2 | 0 | 23 | 2 | 0 | 1 | 1 | 59 | 19 | 0 | 1 | 0 | 2 | 0 | 0 | 2 | 0 | 0.14966 | 6.7789 | 0.38645 | 0.39207 | Low | Medium | Low | Bottom | 770 | 763 | 2.6197
MILPITAS 1105 | 082831105 | CENTRAL COAST | SAN JOSE | 0.10454 | 946778.6667 | 45 | 1.045% | 0% | 0% | 100% | 0 | 0 | 0 | 0% | 100% | 0% | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0.11479 | 1 | 3.2168 | 0.36927 | Low | Low | Low | Bottom | 771 | 755 | 3.2168
RED BLUFF 1105 | 103541105 | NORTHERN | NORTH VALLEY | 16.0727 | 975762 | 42.9052 | 46.95% | 0.2553% | 83.45% | 0.8702% | 0 | 0 | 14 | 83.71% | 0.8702% | 6.728% | 22 | 117 | 16 | 0 | 88 | 26 | 0 | 1 | 2 | 327 | 50.9636 | 61 | 77 | 9 | 168 | 0 | 1 | 14 | 0 | 0.12081 | 1.085 | 2.4168 | 0.31682 | Low | Low | Low | Bottom | 772 | 762 | 2.6224
SPAULDING 1101 | 152251101 | NORTHERN | SIERRA | 20.6639 | 74813.3333 | 41.5306 | 37.59% | 78.87% | 19.25% | 1.193% | 1 | 0 | 33 | 71.79% | 28.19% | 17.71% | 94 | 121 | 1 | 0 | 147 | 46 | 0 | 5 | 15 | 463 | 30.2105 | 30 | 13 | 0 | 85 | 0 | 0 | 33 | 0 | 0.33581 | 14.0857 | 0.065741 | 0.31097 | Medium | High | Low | Bottom | 773 | 778 | 0.926
SOLEDAD 1114 | 182051114 | CENTRAL COAST | CENTRAL COAST | 1.7938 | 597876.6667 | 39.4118 | 6.374% | 0% | 18.9% | 74.54% | 0 | 0 | 0 | 18.9% | 74.54% | 17.65% | 0 | 4 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 17 | 17.25 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0.15817 | 1 | 1.7451 | 0.27603 | Low | Low | Low | Bottom | 774 | 773 | 1.7451
RED BLUFF 1103 | 103541103 | NORTHERN | NORTH VALLEY | 15.9772 | 989293.3333 | 41.8375 | 31.22% | 0% | 100% | 0% | 1 | 0 | 14 | 100% | 0% | 7.463% | 21 | 220 | 38 | 2 | 76 | 12 | 0 | 3 | 6 | 402 | 47.6957 | 74 | 25 | 0 | 141 | 0 | 2 | 14 | 0 | 0.16041 | 2.6012 | 0.61946 | 0.25847 | Low | Medium | Low | Bottom | 775 | 775 | 1.6113
COPPERMINE 1104 | 252411104 | CENTRAL VALLEY | FRESNO | 9.886 | 1003301.3333 | 41.5625 | 17.21% | 9.552% | 90.37% | 0% | 0 | 0 | 4 | 97.34% | 2.581% | 14.84% | 6 | 18 | 0 | 8 | 48 | 5 | 0 | 0 | 0 | 128 | 9.8889 | 22 | 10 | 0 | 48 | 0 | 0 | 4 | 0 | 0.14052 | 1.5859 | 1.1235 | 0.25038 | Low | Low | Low | Bottom | 776 | 772 | 1.7818
SOLEDAD 2101 | 182052101 | CENTRAL COAST | CENTRAL COAST | 7.4381 | 1365073.3333 | 39.569 | 32.52% | 0% | 83.79% | 16.21% | 0 | 0 | 1 | 83.79% | 16.21% | 5.085% | 3 | 24 | 0 | 1 | 20 | 6 | 0 | 0 | 0 | 59 | 33.3333 | 3 | 1 | 1 | 12 | 0 | 0 | 1 | 0 | 0.1398 | 3.375 | 0.50049 | 0.23613 | Low | Medium | Low | Bottom | 777 | 774 | 1.6891
MARTELL 1101 | 163011101 | CENTRAL VALLEY | STOCKTON | 74.5727 | 692481.6667 | 42.5623 | 56.3% | 16.45% | 73.74% | 2.423% | 4 | 0 | 79 | 91.43% | 2.88% | 4.213% | 176 | 820 | 0 | 0 | 334 | 222 | 0 | 15 | 27 | 1614 | 36.5019 | 283 | 119 | 4 | 547 | 0 | 1 | 79 | 0 | 0.044052 | 1.0495 | 5.0105 | 0.23166 | Low | Low | Medium | Bottom | 778 | 681 | 5.2587
OROSI 1102 | 252841102 | CENTRAL VALLEY | FRESNO | 1.0335 | 201733.6667 | 40 | 2.259% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 5 | 1 | 0 | 0 | 0 | 8 | 7 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.17536 | 1 | 0.7238 | 0.12693 | Low | Low | Low | Bottom | 779 | 779 | 0.7238
EEL RIVER 1103 | 192381103 | NORTHERN | HUMBOLDT | 3.2275 | 0 | 39.717 | 3.864% | 0% | 5.057% | 94.94% | 0 | 0 | 1 | 0% | 100% | 15.09% | 0 | 1 | 0 | 0 | 42 | 2 | 0 | 0 | 0 | 53 | 10.3846 | 3 | 1 | 1 | 14 | 0 | 0 | 1 | 0 | 0.28292 | 1 | 0.37138 | 0.10507 | Low | Low | Low | Bottom | 780 | 780 | 0.37138
MC ARTHUR 1101 | 103491101 | NORTHERN | NORTH VALLEY | 76.2929 | 713606.6667 | 41.1192 | 53.09% | 80.41% | 18.32% | 1.11% | 4 | 0 | 38 | 80.84% | 19% | 18.85% | 86 | 642 | 11 | 1 | 363 | 134 | 11 | 7 | 17 | 1379 | 30.9336 | 108 | 47 | 5 | 305 | 0 | 2 | 38 | 0 | 0.21959 | 11.1195 | 0.012434 | 0.030362 | Low | Medium | Low | Bottom | 781 | 781 | 0.13826
ANTELOPE 1101 | 252021101 | CENTRAL VALLEY | KERN | 1.4593 | 220377.6667 | 45.2941 | 32.34% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 31.6667 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.21502 | 1 | 0 | 0 | Low | Low | Low | Bottom | 782 | 782 | 0
ARBUCKLE 1104 | 062081104 | NORTHERN | SACRAMENTO | 2.7857 | 1582717.6667 | 42.9167 | 25.06% | 0% | 53.89% | 0% | 0 | 0 | 0 | 53.89% | 0% | 30.56% | 0 | 24 | 0 | 0 | 1 | 11 | 0 | 0 | 0 | 36 | 36.4286 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0.26855 | 35.4977 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
BOGARD 1101 | 103301101 | NORTHERN | NORTH VALLEY | 0.51623 | 4451.6667 | 44.0909 | 1.719% | 100% | 0% | 0% | 1 | 0 | 2 | 100% | 0% | 18.18% | 5 | 0 | 0 | 0 | 4 | 1 | 0 | 0 | 0 | 11 | 44.5 | 1 | 0 | 2 | 4 | 0 | 0 | 2 | 1 | 0.54342 | 1 | 0 | 0 | Medium | Low | Low | Bottom | 782 | 782 | 0
CAL WATER 1102 | 255451102 | CENTRAL VALLEY | KERN | 4.089 | 1154810.3333 | 38.5 | 258.7% | 2.159% | 97.84% | 0% | 0 | 0 | 1 | 100% | 0% | 4.545% | 5 | 1 | 0 | 0 | 31 | 3 | 0 | 0 | 0 | 44 | 20.2 | 0 | 0 | 1 | 6 | 0 | 0 | 1 | 0 | 0.143 | 21.9936 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
CHOLAME 2102 | 182562102 | CENTRAL COAST | LOS PADRES | 61.1274 | 747236.6667 | 43.55 | 43.58% | 0% | 99.9% | 0% | 0 | 0 | 15 | 99.99% | 0% | 4.558% | 143 | 4 | 1 | 25 | 275 | 133 | 0 | 3 | 3 | 702 | 32.6042 | 57 | 15 | 4 | 155 | 0 | 0 | 15 | 0 | 0.136 | 12.0996 | 0 | 0 | Low | Medium | Low | Bottom | 782 | 782 | 0
CORTINA 1101 | 063121101 | NORTHERN | SACRAMENTO | 1.8918 | 629529.6667 | 39.6667 | 33.7% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 9.625 | 2 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0.11269 | 57.3601 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
CUYAMA 1103 | 253141103 | CENTRAL VALLEY | KERN | 3.0287 | 510804.3333 | 36.9048 | 151.4% | 100% | 0% | 0% | 0 | 0 | 0 | 100% | 0% | 2.381% | 0 | 0 | 0 | 0 | 29 | 1 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.28678 | 19.2951 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
GONZALES 1101 | 182131101 | CENTRAL COAST | CENTRAL COAST | 4.0882 | 645442.6667 | 39.3636 | 5.493% | 0% | 100% | 0% | 1 | 0 | 3 | 100% | 0% | 9.091% | 0 | 16 | 0 | 3 | 29 | 3 | 0 | 2 | 3 | 55 | 6.3333 | 8 | 1 | 0 | 16 | 0 | 0 | 3 | 0 | 0.16692 | 23.766 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
GONZALES 1104 | 182131104 | CENTRAL COAST | CENTRAL COAST | 1.2503 | 882987 | 33.5 | 12.61% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 8 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 10 | 11.8 | 1 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0.13772 | 33.2799 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
HOLLISTER 2105 | 182492105 | CENTRAL COAST | CENTRAL COAST | 65.1927 | 929904.3333 | 39.1655 | 39.8% | 0% | 93.72% | 6.248% | 1 | 1 | 28 | 72.38% | 27.58% | 14.62% | 15 | 170 | 0 | 6 | 378 | 37 | 0 | 3 | 6 | 732 | 13.0778 | 68 | 18 | 4 | 181 | 0 | 0 | 28 | 0 | 0.11723 | 30.1446 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
HOLLISTER 2106 | 182492106 | CENTRAL COAST | CENTRAL COAST | 7.5432 | 1499231.3333 | 38.8372 | 10.94% | 13.15% | 47.54% | 39.32% | 1 | 0 | 6 | 60.68% | 39.32% | 6.154% | 4 | 69 | 0 | 1 | 48 | 1 | 0 | 2 | 2 | 130 | 7.875 | 1 | 6 | 0 | 25 | 0 | 0 | 6 | 0 | 0.38778 | 22.2831 | 0 | 0 | Medium | High | Low | Bottom | 782 | 782 | 0
KERN OIL 1106 | 252721106 | CENTRAL VALLEY | KERN | 1.699 | 2034157.3333 | 44.375 | 64.02% | 71.87% | 14.58% | 0% | 0 | 0 | 0 | 33.5% | 54.13% | 12.5% | 4 | 0 | 1 | 1 | 6 | 2 | 0 | 1 | 2 | 16 | 8.25 | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 0 | 0.22347 | 1 | 0 | 0 | Low | Low | Low | Bottom | 782 | 782 | 0
LAMONT 1102 | 253911102 | CENTRAL VALLEY | KERN | 2.6581 | 1861598.6667 | 30 | 268.1% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 0.18236 | 15.9013 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
LOGAN CREEK 2102 | 103142102 | NORTHERN | NORTH VALLEY | 3.7103 | 5213559.3333 | 39.7321 | 18.3% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 5.357% | 0 | 47 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 56 | 38.5 | 1 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 0.14988 | 43.0895 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
LOS MOLINOS 1101 | 103481101 | NORTHERN | NORTH VALLEY | 0.48216 | 389350.6667 | 40.8333 | 2.935% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 2 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 6 | 46.6667 | 1 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0.20779 | 6.0236 | 0 | 0 | Low | Medium | Low | Bottom | 782 | 782 | 0
MADISON 1105 | 063171105 | NORTHERN | SACRAMENTO | 0.39195 | 665239 | 41.6667 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 11.11% | 3 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 9 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 0 | 0 | 0.19729 | 1 | 0 | 0 | Low | Low | Low | Bottom | 782 | 782 | 0
MADISON 2101 | 063172101 | NORTHERN | SACRAMENTO | 11.0838 | 2158591 | 39.7436 | 43.35% | 0% | 92.2% | 0% | 0 | 0 | 0 | 98.13% | 1.654% | 0% | 4 | 31 | 4 | 0 | 24 | 1 | 0 | 1 | 1 | 78 | 34.7391 | 4 | 3 | 1 | 25 | 0 | 0 | 0 | 0 | 0.18239 | 33.1406 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
MAXWELL 1105 | 062881105 | NORTHERN | SACRAMENTO | 5.6752 | 0 | 39.3333 | 163.5% | 0% | 100% | 0% | 0 | 0 | 3 | 100% | 0% | 1.667% | 3 | 33 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 60 | 33.2 | 1 | 1 | 1 | 6 | 0 | 0 | 3 | 0 | 0.2019 | 20.9871 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
PANOCHE 1103 | 253671103 | CENTRAL VALLEY | YOSEMITE | 45.8174 | 375649.3333 | 39.2123 | 0% | 5.007% | 94.85% | 0% | 0 | 0 | 13 | 99.86% | 0% | 9.06% | 10 | 99 | 0 | 7 | 419 | 29 | 0 | 4 | 5 | 585 | 12.4105 | 30 | 8 | 0 | 100 | 0 | 0 | 13 | 0 | 0.1229 | 18.0183 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
POSO MOUNTAIN 2104 | 253642104 | CENTRAL VALLEY | KERN | 10.6702 | 636738.6667 | 45.6306 | 256.2% | 36.67% | 12.88% | 4.505% | 0 | 0 | 6 | 7.714% | 46.34% | 9.91% | 42 | 0 | 0 | 22 | 6 | 2 | 0 | 3 | 8 | 111 | 15.2727 | 0 | 0 | 0 | 12 | 0 | 1 | 6 | 0 | 0.27482 | 1 | 0 | 0 | Low | Low | Low | Bottom | 782 | 782 | 0
SISQUOC 1103 | 182811103 | CENTRAL COAST | LOS PADRES | 31.0209 | 410840.6667 | 41.4564 | 66.35% | 7.979% | 81.09% | 10.21% | 0 | 2 | 14 | 75.22% | 24.06% | 9.153% | 41 | 29 | 0 | 78 | 143 | 50 | 0 | 2 | 3 | 437 | 25.2137 | 40 | 8 | 1 | 138 | 0 | 0 | 14 | 0 | 0.1372 | 18.4213 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0
SPENCE 1122 | 182201122 | CENTRAL COAST | CENTRAL COAST | 10.095 | 1053579.3333 | 38.2432 | 12.27% | 0% | 70.1% | 29.9% | 0 | 0 | 8 | 40.54% | 59.46% | 9.189% | 2 | 101 | 1 | 5 | 36 | 9 | 0 | 3 | 3 | 185 | 14.8378 | 25 | 5 | 0 | 77 | 0 | 0 | 8 | 0 | 0.34488 | 17.4168 | 0 | 0 | Medium | High | Low | Bottom | 782 | 782 | 0
SPENCE 1123 | 182201123 | CENTRAL COAST | CENTRAL COAST | 3.6031 | 662970.6667 | 40.5128 | 8.968% | 0% | 72.53% | 27.47% | 0 | 0 | 3 | 72.53% | 27.47% | 17.95% | 2 | 1 | 0 | 0 | 35 | 3 | 0 | 0 | 0 | 39 | 11.7778 | 2 | 1 | 0 | 9 | 0 | 0 | 3 | 0 | 0.22621 | 8.3263 | 0 | 0 | Low | Medium | Low | Bottom | 782 | 782 | 0
STONE CORRAL 1108 | 252921108 | CENTRAL VALLEY | FRESNO | 3.1209 | 556516.3333 | 40.3125 | 12.95% | 0% | 72.81% | 27.19% | 0 | 0 | 1 | 15.34% | 84.66% | 41.18% | 4 | 0 | 0 | 0 | 17 | 7 | 0 | 0 | 1 | 51 | 0 | 0 | 2 | 0 | 7 | 0 | 0 | 1 | 0 | 0.25854 | 1 | 0 | 0 | Low | Low | Low | Bottom | 782 | 782 | 0
STONE CORRAL 1110 | 252921110 | CENTRAL VALLEY | FRESNO | 3.0023 | 354094.6667 | 38.8462 | 3.702% | 0% | 82.82% | 17.18% | 0 | 0 | 1 | 53.37% | 46.63% | 33.33% | 3 | 0 | 0 | 10 | 7 | 1 | 0 | 0 | 0 | 42 | 8.5556 | 3 | 0 | 0 | 10 | 0 | 0 | 1 | 0 | 0.19694 | 3.3888 | 0 | 0 | Low | Medium | Low | Bottom | 782 | 782 | 0
TRES PINOS 1111 | 183221111 | CENTRAL COAST | CENTRAL COAST | 0.10269 | 110901.6667 | 35 | 0% | 0% | 100% | 0% | 0 | 0 | 0 | 100% | 0% | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0.21599 | 19.9979 | 0 | 0 | Low | High | Low | Bottom | 782 | 782 | 0

## Tx - Inspection
Tx Prioritization Output - Inspections
Circuit Information |  |  |  | Independent Variables | [7 empty] | Dependent Variable | Risk Scoring |  |  |  |  | Risk Tiers
Feeder Name | Circuit ID | District | Number of structures | # of Bird Notifications | # of Structure Crack Notifications | % of Horizontal frames along line | % of Tri-arm frames along line | % of Wishbone frames along line | Miles of Conductor Size - 4/0 | % Conductor Type - Copper | % of structures steel | Above average outage indicator | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Consolidated Risk Score | Likelihood of failure | Likelihood of spread and consequence | Egress Score | Rank Cons Risk | Rank P*C | P*C
DRUM-GRASS VALLEY-WEIMAR - 60 kV | ETL.6760 | SIERRA | 722 | 5 | 0 | 2.014% | 80.43% | 0% | 0 | 76.79% | 6.043% | 1 | 0.99999 | 61.4248 | 1.6093 | 98.852 | High | High | Medium | 1 | 1 | 61.4243
DONNELLS-CURTIS - 115 kV | ETL.1400 | YOSEMITE | 261 | 0 | 0 | 0.3831% | 0% | 0% | 0 | 0% | 28.35% | 1 | 0.83858 | 43.9281 | 2.5696 | 94.658 | High | High | High | 2 | 4 | 36.8371
COLGATE-CHALLENGE - 60 kV | ETL.6480 | SIERRA | 231 | 0 | 0 | 1.299% | 86.15% | 0% | 0 | 39.37% | 3.896% | 1 | 0.88412 | 53.9348 | 1.6444 | 78.4139 | High | High | Medium | 3 | 2 | 47.685
SNEATH LANE-HALF MOON BAY - 60 kV | ETL.7212 | PENINSULA | 145 | 0 | 0 | 8.271% | 11.28% | 20.3% | 0 | 0% | 27.07% | 1 | 0.49769 | 56.971 | 2.7544 | 78.0978 | High | High | High | 4 | 10 | 28.3536
FULTON-CALISTOGA - 60 kV | ETL.6880 | SONOMA | 411 | 0 | 0 | 1.496% | 29.93% | 0% | 0 | 32.66% | 35.91% | 1 | 0.99284 | 34.4741 | 2.1816 | 74.6698 | High | High | High | 5 | 5 | 34.2273
IGNACIO-BOLINAS #2 - 60 kV | ETL.7180 | NORTH BAY | 304 | 0 | 0 | 12.76% | 49.31% | 0% | 0 | 2.157% | 15.17% | 1 | 0.91039 | 30.0537 | 2.6424 | 72.2984 | High | High | High | 6 | 12 | 27.3605
COLGATE-ALLEGHANY - 60 kV | ETL.6470 | SIERRA | 673 | 0 | 0 | 2.526% | 91.53% | 0% | 0 | 8.346e-05% | 2.377% | 1 | 0.9999 | 42.804 | 1.4581 | 62.404 | High | High | Low | 7 | 3 | 42.7996
TIGER CREEK-VALLEY SPRINGS - 230 kV | ETL.5790 | STOCKTON | 129 | 0 | 0 | 0% | 1.55% | 0% | 0 | 0% | 100% | 1 | 0.61815 | 40.1602 | 2.4336 | 60.4132 | High | High | High | 8 | 17 | 24.825
IGNACIO-BOLINAS #1 - 60 kV | ETL.7140 | NORTH BAY | 192 | 0 | 0 | 3.684% | 23.16% | 0% | 0 | 0% | 3.158% | 0 | 0.58811 | 30.7705 | 3.2833 | 59.4163 | High | High | High | 9 | 37 | 18.0964
DRUM-HIGGINS - 115 kV | ETL.4393 | SIERRA | 271 | 0 | 0 | 0.3717% | 0.3717% | 0% | 17.15 | 0.08243% | 85.5% | 1 | 0.92443 | 34.4371 | 1.8446 | 58.7222 | High | High | Medium | 10 | 8 | 31.8348
MIDDLE FORK-GOLD HILL - 230 kV | ETL.5140 | SIERRA | 309 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 32.68% | 1 | 0.89699 | 33.5605 | 1.8785 | 56.5498 | High | High | Medium | 11 | 9 | 30.1034
VALLEY SPRINGS #2 - 60 kV | ETL.9460 | STOCKTON | 177 | 0 | 0 | 3.55% | 82.84% | 0% | 1.96 | 96.38% | 2.367% | 1 | 0.87735 | 27.3903 | 2.3528 | 56.5388 | High | High | High | 12 | 19 | 24.0309
CARIBOU-PLUMAS JCT - 60 kV | ETL.6290 | NORTH VALLEY | 316 | 0 | 0 | 0% | 76.71% | 0% | 0 | 9.544% | 10.96% | 1 | 0.91037 | 37.4705 | 1.6483 | 56.2262 | High | High | Medium | 13 | 6 | 34.1121
DRUM-RIO OSO #1 - 115 kV | ETL.1420 | SIERRA | 253 | 0 | 0 | 0% | 15.92% | 0% | 39248.74 | 62.17% | 100% | 1 | 0.92417 | 34.6401 | 1.6999 | 54.4181 | High | High | Medium | 14 | 7 | 32.0133
BURNS-LONE STAR #2 - 60 kV | ETL.6240 | CENTRAL COAST | 120 | 0 | 0 | 0% | 71.67% | 0% | 5.88 | 100% | 3.333% | 1 | 0.6844 | 27.3586 | 2.8962 | 54.2296 | High | High | High | 15 | 36 | 18.7243
MONTA VISTA-BURNS-60 kV | ETL.7590 | CENTRAL COAST | 192 | 0 | 0 | 0% | 37.37% | 0.5263% | 2.86 | 15.95% | 3.158% | 1 | 0.74624 | 26.9169 | 2.5939 | 52.1025 | High | High | High | 16 | 29 | 20.0865
MORAGA-OAKLAND #3 - 115 kV | ETL.2740 | EAST BAY | 32 | 0 | 0 | 3.125% | 0% | 0% | 4.69 | 92.14% | 96.88% | 0 | 0.45876 | 38.9244 | 2.8994 | 51.775 | High | High | High | 17 | 39 | 17.857
LOWER LAKE-HOMESTAKE - 115 kV | ETL.1481 | NORTH BAY | 286 | 0 | 0 | 1.099% | 77.66% | 0% | 0 | 0% | 0.7326% | 1 | 0.89488 | 26.1579 | 2.0768 | 48.6142 | High | High | Medium | 18 | 22 | 23.4083
FULTON-PUEBLO - 115 kV | ETL.1600 | SONOMA | 236 | 0 | 0 | 0% | 7.547% | 0% | 0 | 52.55% | 90.09% | 1 | 0.92191 | 25.8687 | 1.9488 | 46.4771 | High | High | Medium | 19 | 21 | 23.8486
KESWICK-CASCADE - 60 kV | ETL.7260 | NORTH VALLEY | 173 | 0 | 0 | 7.784% | 72.46% | 0% | 0 | 95.04% | 2.395% | 1 | 0.83687 | 25.1187 | 2.1885 | 46.0052 | High | High | High | 20 | 26 | 21.0211
OLEUM-G #1 - 115 kV | ETL.3150 | EAST BAY | 70 | 0 | 0 | 0% | 1.562% | 0% | 0 | 97.34% | 100% | 0 | 0.69963 | 19.9899 | 3.1716 | 44.3565 | High | High | High | 21 | 54 | 13.9855
EL DORADO-MISSOURI FLAT #1 - 115 kV | ETL.1530 | SIERRA | 123 | 0 | 0 | 0% | 14.78% | 0% | 8.7 | 52.37% | 80% | 1 | 0.58562 | 44.9626 | 1.6434 | 43.272 | High | High | Medium | 22 | 13 | 26.3311
WEIMAR #1 - 60 kV | ETL.7560 | SIERRA | 208 | 0 | 0 | 0% | 60.1% | 0% | 0 | 3.154% | 9.615% | 1 | 0.67014 | 35.5947 | 1.7849 | 42.5755 | High | High | Medium | 23 | 20 | 23.8534
SOBRANTE-GRIZZLY-CLAREMONT #1 - 115 kV | ETL.3740 | EAST BAY | 72 | 0 | 0 | 0% | 0% | 0% | 2.47 | 45.95% | 94.03% | 1 | 0.28433 | 50.2279 | 2.9401 | 41.9877 | Medium | High | High | 24 | 53 | 14.2811
SOBRANTE-R #1 - 115 kV | ETL.3770 | DIABLO | 39 | 0 | 0 | 0% | 0% | 0% | 4.99 | 90.89% | 100% | 0 | 0.3256 | 34.917 | 3.4918 | 39.6988 | Medium | High | High | 25 | 77 | 11.3691
CASCADE-BENTON-DESCHUTES - 60 kV | ETL.6310 | NORTH VALLEY | 216 | 0 | 0 | 3.646% | 80.73% | 0% | 0 | 27.28% | 3.646% | 1 | 0.73686 | 26.702 | 1.9397 | 38.1647 | High | High | Medium | 26 | 32 | 19.6756
WOODLEAF-PALERMO - 115 kV | ETL.4220 | NORTH VALLEY | 216 | 0 | 0 | 6.863% | 10.78% | 20.59% | 0 | 0% | 23.53% | 1 | 0.7943 | 19.3341 | 2.4478 | 37.5916 | High | High | High | 27 | 47 | 15.3571
CARIBOU #2 - 60 kV | ETL.6280 | NORTH VALLEY | 979 | 0 | 0 | 0% | 77.27% | 0% | 0 | 46.53% | 6.025% | 1 | 1 | 26.0762 | 1.4257 | 37.1764 | High | High | Low | 28 | 15 | 26.0762
LAURELES-OTTER - 60 kV | ETL.7380 | CENTRAL COAST | 186 | 0 | 0 | 0.5495% | 43.41% | 3.297% | 0 | 0% | 1.648% | 1 | 0.68883 | 29.7893 | 1.8027 | 36.9913 | High | High | Medium | 29 | 27 | 20.5197
DESABLA-CENTERVILLE-60 kV | ETL.6720 | NORTH VALLEY | 118 | 0 | 0 | 2.586% | 33.62% | 0% | 0 | 0% | 7.759% | 1 | 0.32671 | 40.6722 | 2.7737 | 36.8568 | Medium | High | High | 30 | 58 | 13.2881
GOLD HILL #1 - 60 kV | ETL.6950 | STOCKTON | 309 | 0 | 0 | 3.448% | 73.56% | 0% | 0 | 0% | 21.46% | 1 | 0.87734 | 19.7877 | 2.101 | 36.4738 | High | High | Medium | 31 | 41 | 17.3605
CORTINA-MENDOCINO #1 - 115 kV | ETL.1330 | HUMBOLDT | 279 | 1 | 0 | 0% | 0% | 0% | 0 | 0% | 99.62% | 1 | 0.93671 | 21.4265 | 1.7981 | 36.0883 | High | High | Medium | 32 | 30 | 20.0705
VACA-SUISUN - 115 kV | ETL.4070 | SACRAMENTO | 60 | 0 | 0 | 0% | 0% | 0% | 0 | 80.46% | 100% | 0 | 0.34087 | 59.1312 | 1.7846 | 35.9715 | Medium | High | Medium | 33 | 28 | 20.1561
EAGLE ROCK-REDBUD - 115 kV | ETL.1480 | HUMBOLDT | 210 | 0 | 0 | 0.4785% | 53.11% | 0% | 0 | 0% | 38.76% | 1 | 0.74696 | 19.8086 | 2.3308 | 34.487 | High | High | High | 34 | 50 | 14.7963
MORRO BAY-MESA - 230 kV | ETL.5290 | LOS PADRES | 142 | 2 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.59752 | 25.4896 | 2.2562 | 34.3625 | High | High | High | 35 | 48 | 15.2305
SOBRANTE-GRIZZLY-CLAREMONT #2 - 115 kV | ETL.3750 | EAST BAY | 51 | 0 | 0 | 0% | 0% | 0% | 2.92 | 52.61% | 93.48% | 0 | 0.23186 | 51.1677 | 2.8735 | 34.091 | Medium | High | High | 36 | 73 | 11.864
WEST POINT-VALLEY SPRINGS - 60 kV | ETL.8350 | STOCKTON | 243 | 0 | 0 | 2.49% | 61.41% | 0% | 9.84 | 2.865% | 4.149% | 1 | 0.80835 | 18.1513 | 2.3207 | 34.0502 | High | Medium | High | 37 | 51 | 14.6726
MORAGA-CLAREMONT #1 - 115 kV | ETL.2700 | EAST BAY | 28 | 0 | 0 | 0% | 0% | 0% | 0.5 | 54.61% | 78.57% | 0 | 0.16808 | 71.155 | 2.8221 | 33.7502 | Medium | High | High | 38 | 71 | 11.9594
KESWICK-TRINITY - 60 kV | ETL.7270 | NORTH VALLEY | 559 | 0 | 0 | 0.1842% | 45.49% | 0% | 0 | 0.3941% | 29.1% | 1 | 0.99907 | 19.4324 | 1.7309 | 33.6046 | High | High | Medium | 39 | 33 | 19.4143
CARIBOU-WESTWOOD - 60 kV | ETL.6300 | NORTH VALLEY | 471 | 0 | 0 | 0% | 63.12% | 0% | 0 | 0% | 0.2169% | 1 | 0.99339 | 17.0098 | 1.9829 | 33.505 | High | Medium | Medium | 40 | 44 | 16.8973
BRIDGEVILLE-COTTONWOOD - 115 kV | ETL.1110 | NORTH VALLEY | 615 | 0 | 0 | 0% | 0.1664% | 0% | 0 | 0% | 47.75% | 1 | 0.99967 | 26.1443 | 1.2791 | 33.4312 | High | High | Low | 41 | 14 | 26.1358
MORAGA-LAKEWOOD - 115 kV | ETL.3741 | DIABLO | 38 | 0 | 0 | 0% | 0% | 0% | 7.01 | 89.99% | 100% | 0 | 0.29211 | 38.833 | 2.9063 | 32.9682 | Medium | High | High | 42 | 78 | 11.3436
MORAGA-OAKLAND #1 - 115 kV | ETL.2720 | EAST BAY | 34 | 0 | 0 | 0% | 0% | 0% | 5.08 | 100% | 100% | 0 | 0.34143 | 33.1672 | 2.9027 | 32.8706 | Medium | High | High | 43 | 79 | 11.3242
TIGER CREEK-ELECTRA - 230 kV | ETL.5780 | STOCKTON | 108 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.29608 | 42.8453 | 2.4711 | 31.3479 | Medium | High | High | 44 | 63 | 12.6858
MORAGA-CLAREMONT #2 - 115 kV | ETL.2710 | DIABLO | 5 | 0 | 0 | 0% | 0% | 0% | 0 | 58.46% | 80% | 0 | 0.12578 | 85.4511 | 2.8877 | 31.0378 | Medium | High | High | 45 | 85 | 10.7483
VACA-VACAVILLE-JAMESON-NORTH TOWER - 115 kV | ETL.4100 | SACRAMENTO | 64 | 0 | 1 | 0% | 0% | 0% | 20.42 | 65.56% | 100% | 1 | 0.29048 | 59.1312 | 1.784 | 30.6436 | Medium | High | Medium | 46 | 42 | 17.1765
KONOCTI-MIDDLETOWN-60 kV | ETL.6380 | HUMBOLDT | 200 | 0 | 0 | 2.809% | 44.38% | 0% | 0 | 0% | 29.78% | 1 | 0.59745 | 22.9913 | 2.1952 | 30.1533 | High | High | High | 47 | 55 | 13.7361
ELK-GUALALA - 60 kV | ETL.8410 | HUMBOLDT | 281 | 0 | 0 | 2.632% | 1.128% | 50.38% | 0 | 0.2315% | 8.271% | 1 | 0.9027 | 24.7621 | 1.3336 | 29.8106 | High | High | Low | 48 | 23 | 22.3527
EAGLE ROCK-CORTINA - 115 kV | ETL.1470 | HUMBOLDT | 139 | 0 | 0 | 1.439% | 82.73% | 0% | 0 | 0% | 7.914% | 1 | 0.49119 | 25.2351 | 2.3948 | 29.6841 | High | High | High | 49 | 67 | 12.3951
OAKHURST TAP - 115 kV | ETL.1252 | YOSEMITE | 229 | 0 | 0 | 26.67% | 0.8889% | 0% | 0 | 0% | 98.67% | 0 | 0.86013 | 20.9951 | 1.6281 | 29.4008 | High | High | Medium | 50 | 38 | 18.0585
SALINAS-LAURELES - 60 kV | ETL.7930 | CENTRAL COAST | 352 | 1 | 0 | 4.334% | 71.83% | 0.3096% | 12.03 | 48.34% | 3.715% | 1 | 0.99115 | 15.7708 | 1.8636 | 29.1309 | High | Medium | Medium | 51 | 46 | 15.6312
FORT ROSS-GUALALA-60 kV | ETL.6980 | SONOMA | 347 | 0 | 0 | 8.116% | 27.83% | 0.5797% | 0 | 0.1345% | 9.275% | 1 | 0.97451 | 20.2736 | 1.4732 | 29.105 | High | High | Low | 52 | 31 | 19.7568
TRINITY-COTTONWOOD - 115 kV | ETL.4040 | NORTH VALLEY | 358 | 0 | 0 | 0.2849% | 0% | 0% | 0 | 0% | 34.47% | 1 | 0.96283 | 17.7613 | 1.6847 | 28.8109 | High | Medium | Medium | 53 | 43 | 17.101
MONTE RIO-FORT ROSS-60 kV | ETL.6979 | SONOMA | 107 | 0 | 0 | 5.941% | 17.82% | 0.9901% | 0 | 0% | 16.83% | 0 | 0.36878 | 36.6287 | 2.0774 | 28.0616 | Medium | High | Medium | 54 | 56 | 13.5078
MORAGA-OAKLAND #4 - 115 kV | ETL.2750 | DIABLO | 1 | 0 | 0 | 0% | 0% | 0% | 4.69 | 91.96% | 0% | 0 | 0.11062 | 85.4511 | 2.8615 | 27.0487 | Low | High | High | 55 | 90 | 9.4527
CASCADE-COTTONWOOD-115 kV | ETL.1240 | NORTH VALLEY | 125 | 0 | 0 | 0% | 0% | 0% | 0 | 73.26% | 39.82% | 1 | 0.47998 | 29.817 | 1.8377 | 26.2996 | High | High | Medium | 56 | 52 | 14.3115
JOLON TAP - 60 kV | ETL.7321 | CENTRAL COAST | 239 | 0 | 0 | 2.532% | 74.68% | 0% | 0 | 0% | 0.4219% | 0 | 0.83995 | 21.1123 | 1.474 | 26.1385 | High | High | Low | 57 | 40 | 17.7332
CABRILLO-SANTA YNEZ SW STA - 115 kV | ETL.1200 | LOS PADRES | 121 | 0 | 0 | 6.034% | 47.41% | 0% | 0 | 0% | 99.14% | 1 | 0.55894 | 21.2809 | 2.1513 | 25.5891 | High | High | High | 58 | 72 | 11.8948
HUMBOLDT-TRINITY - 115 kV | ETL.1820 |  | 459 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 11.73% | 1 | 0.99018 | 15.2143 | 1.6866 | 25.4077 | High | Medium | Medium | 59 | 49 | 15.0649
DIABLO-MIDWAY #3 - 500 kV | ETL.5980 | LOS PADRES | 205 | 21 | 10 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.82048 | 13.5839 | 2.1095 | 23.5106 | High | Medium | Medium | 60 | 80 | 11.1453
PHILO JCT-ELK - 60 kV | ETL.7780 | HUMBOLDT | 372 | 0 | 0 | 0% | 49.12% | 0% | 0 | 0% | 2.924% | 1 | 0.95021 | 20.1257 | 1.2279 | 23.4827 | High | High | Low | 61 | 34 | 19.1237
DRUM-RIO OSO #2 - 115 kV | ETL.1430 | SIERRA | 124 | 0 | 0 | 0% | 0% | 0% | 39248.74 | 66.44% | 99.19% | 1 | 0.41869 | 51.148 | 1.0915 | 23.3745 | High | High | Low | 62 | 24 | 21.4153
GREEN VALLEY-LLAGAS - 115 kV | ETL.1720 | SAN JOSE | 100 | 0 | 0 | 1.087% | 3.261% | 0% | 13.88 | 56.08% | 43.48% | 0 | 0.52714 | 23.9919 | 1.8163 | 22.9715 | High | High | Medium | 63 | 64 | 12.6471
TRINITY-MAPLE CREEK - 60 kV | ETL.8170 |  | 690 | 0 | 0 | 0% | 44.13% | 0% | 0 | 0% | 8.798% | 1 | 0.99988 | 19.0199 | 1.2009 | 22.8391 | High | High | Low | 64 | 35 | 19.0177
DIABLO-MIDWAY #2 - 500 kV | ETL.5970 | LOS PADRES | 199 | 8 | 8 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.80133 | 13.303 | 2.1027 | 22.4149 | High | Medium | Medium | 65 | 86 | 10.6601
CARIBOU-PALERMO - 115 kV | ETL.3190 | NORTH VALLEY | 416 | 0 | 0 | 0.2421% | 0% | 0% | 13.17 | 0.008246% | 99.52% | 1 | 0.99301 | 11.062 | 2.0087 | 22.0649 | High | Medium | Medium | 66 | 82 | 10.9848
MONTE RIO-FULTON-60 kV | ETL.7630 | SONOMA | 67 | 0 | 0 | 0% | 31.15% | 0% | 0 | 0.5814% | 21.31% | 1 | 0.14207 | 61.445 | 2.4798 | 21.6477 | Medium | High | High | 67 | 97 | 8.7296
COLGATE-GRASS VALLEY - 60 kV | ETL.6490 | SIERRA | 318 | 0 | 0 | 1.045% | 82.23% | 0% | 0 | 100% | 4.53% | 1 | 0.97627 | 11.036 | 1.9598 | 21.1148 | High | Medium | Medium | 68 | 84 | 10.7741
ATASCADERO-CAYUCOS-70 kV | ETL.8480 | LOS PADRES | 78 | 0 | 0 | 0% | 26.32% | 30.26% | 11.77 | 0% | 9.211% | 1 | 0.39088 | 31.2999 | 1.7198 | 21.041 | Medium | High | Medium | 69 | 69 | 12.2345
MONTA VISTA-COYOTE SW STA - 230 kV | ETL.5090 | SAN JOSE | 118 | 1 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.47387 | 19.2506 | 2.3056 | 21.0321 | High | High | High | 70 | 95 | 9.1222
WATSONVILLE-SALINAS - 60 kV | ETL.8310 | CENTRAL COAST | 114 | 0 | 0 | 6.542% | 39.25% | 0% | 13.89 | 98.95% | 0% | 1 | 0.62734 | 20.2425 | 1.6512 | 20.9684 | High | High | Medium | 71 | 62 | 12.6989
DIVIDE-CABRILLO #2 - 115 kV | ETL.1370 | LOS PADRES | 88 | 10 | 0 | 2.817% | 5.634% | 0% | 0 | 0% | 7.042% | 1 | 0.36218 | 20.0715 | 2.8774 | 20.9167 | Medium | High | High | 72 | 111 | 7.2694
LAKEVILLE #2 - 60 kV | ETL.7340 | NORTH BAY | 135 | 0 | 0 | 2.542% | 80.51% | 0% | 0 | 55.51% | 0.8475% | 1 | 0.60017 | 20.6905 | 1.6469 | 20.4512 | High | High | Medium | 73 | 66 | 12.4178
BRIDGEVILLE-GARBERVILLE - 60 kV | ETL.6220 | HUMBOLDT | 385 | 0 | 0 | 0% | 64.84% | 0% | 0 | 0% | 5.859% | 1 | 0.826 | 29.4235 | 0.82836 | 20.1322 | High | High | Low | 74 | 18 | 24.3038
VOLTA-DESCHUTES - 60 kV | ETL.8290 | NORTH VALLEY | 452 | 0 | 0 | 0.2257% | 93.91% | 0% | 0 | 98.66% | 6.095% | 1 | 0.99859 | 12.2897 | 1.6223 | 19.9096 | High | Medium | Medium | 75 | 68 | 12.2723
EAGLE ROCK-FULTON-SILVERADO - 115 kV | ETL.4392 | SONOMA | 132 | 0 | 0 | 0% | 0% | 0% | 0 | 18.43% | 100% | 1 | 0.46278 | 27.2597 | 1.4902 | 18.7994 | High | High | Medium | 76 | 65 | 12.6153
DEER CREEK-DRUM - 60 kV | ETL.6690 | SIERRA | 149 | 0 | 0 | 0.6711% | 77.18% | 0% | 0 | 100% | 12.75% | 1 | 0.8129 | 34.8559 | 0.65761 | 18.6327 | High | High | Low | 77 | 11 | 28.3342
KONOCTI-EAGLE ROCK - 60 kV | ETL.6861 | SONOMA | 122 | 0 | 0 | 1.786% | 21.43% | 0% | 0 | 0% | 8.929% | 0 | 0.33835 | 27.224 | 2.0219 | 18.624 | Medium | High | Medium | 78 | 93 | 9.2112
CORDELIA #1 TAP - 60 kV | ETL.8182 | SACRAMENTO | 70 | 0 | 0 | 4.478% | 62.69% | 0% | 0 | 92.89% | 2.985% | 0 | 0.58387 | 15.7603 | 2.0137 | 18.5298 | High | Medium | Medium | 79 | 94 | 9.202
CLAY-MARTEL - 60 kV | ETL.8250 | STOCKTON | 339 | 0 | 0 | 2.857% | 74.6% | 0% | 0 | 21.08% | 5.397% | 1 | 0.96289 | 8.2748 | 2.3219 | 18.5006 | High | Medium | High | 80 | 102 | 7.9678
MAPLE CREEK-HOOPA - 60 kV | ETL.7490 | HUMBOLDT | 302 | 0 | 0 | 0% | 86.69% | 0% | 0 | 0% | 12.23% | 1 | 0.89043 | 23.6929 | 0.86821 | 18.3166 | High | High | Low | 81 | 25 | 21.0969
MORRO BAY-SOLAR SW STA #1 - 230 kV | ETL.5300 | LOS PADRES | 162 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.4843 | 22.7322 | 1.6471 | 18.1336 | High | High | Medium | 82 | 81 | 11.0091
ORO FINO TAP - 60 kV | ETL.6721 | NORTH VALLEY | 21 | 0 | 0 | 0% | 57.14% | 0% | 0 | 0% | 0% | 0 | 0.070214 | 98.1657 | 2.6165 | 18.0342 | Low | High | High | 83 | 116 | 6.8926
GREEN VALLEY-PAUL SWEET - 115 kV | ETL.1730 | CENTRAL COAST | 89 | 0 | 0 | 3.529% | 1.176% | 1.176% | 0 | 0% | 34.12% | 0 | 0.36819 | 18.5437 | 2.583 | 17.6358 | Medium | High | High | 84 | 118 | 6.8276
PARKWAY-MORAGA - 230 kV | ETL.5930 | DIABLO | 93 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.23696 | 26.2836 | 2.8197 | 17.5612 | Medium | High | High | 85 | 131 | 6.228
PITTSBURG-SAN MATEO - 230 kV | ETL.5463 | MISSION | 75 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.17334 | 36.8125 | 2.7367 | 17.4633 | Medium | High | High | 86 | 126 | 6.3812
FULTON-IGNACIO #1 - 230 kV | ETL.4680 | SONOMA | 103 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.25011 | 38.2444 | 1.778 | 17.0066 | Medium | High | Medium | 87 | 89 | 9.5651
CHRISTIE-SOBRANTE - 115 kV | ETL.1260 | DIABLO | 48 | 1 | 0 | 0% | 0% | 0% | 0 | 60.31% | 100% | 0 | 0.46455 | 13.2892 | 2.7172 | 16.7744 | High | Medium | High | 88 | 132 | 6.1734
CONTRA COSTA-MORAGA #1 - 230 kV | ETL.5452 | DIABLO | 84 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.18381 | 31.9897 | 2.8304 | 16.6433 | Medium | High | High | 89 | 139 | 5.8802
VALLEY SPRINGS #1 - 60 kV | ETL.8210 | STOCKTON | 258 | 0 | 0 | 1.456% | 87.86% | 0% | 10 | 63.45% | 3.865% | 1 | 0.8768 | 7.5551 | 2.4628 | 16.3145 | High | Medium | High | 90 | 121 | 6.6243
ATASCADERO-SAN LUIS OBISPO - 70 kV | ETL.8490 | LOS PADRES | 135 | 0 | 0 | 0.9174% | 55.05% | 0% | 0 | 0% | 100% | 0 | 0.52956 | 18.5 | 1.644 | 16.1058 | High | High | Medium | 91 | 88 | 9.7969
SAN LUIS OBISPO-CAYUCOS - 70 kV | ETL.9090 | LOS PADRES | 114 | 5 | 0 | 0% | 6.604% | 15.09% | 0 | 0% | 0.9434% | 0 | 0.54085 | 13.1078 | 2.2712 | 16.101 | High | Medium | High | 92 | 114 | 7.0894
MORAGA-SAN LEANDRO #1 - 115 kV | ETL.2770 | MISSION | 65 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.16093 | 37.37 | 2.6685 | 16.0479 | Medium | High | High | 93 | 135 | 6.0138
SAN RAMON-MORAGA - 230 kV | ETL.5660 | MISSION | 24 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.084467 | 65.076 | 2.8801 | 15.8316 | Low | High | High | 94 | 144 | 5.4968
MORAGA-SAN LEANDRO #3 - 115 kV | ETL.2790 | MISSION | 67 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15853 | 37.1227 | 2.6749 | 15.7419 | Medium | High | High | 95 | 138 | 5.8851
GREEN VALLEY-CAMP EVERS - 115 kV | ETL.1710 | CENTRAL COAST | 110 | 0 | 0 | 0% | 1.961% | 0% | 0 | 0% | 22.55% | 0 | 0.30512 | 19.6234 | 2.5987 | 15.5596 | Medium | High | High | 96 | 136 | 5.9876
COTTONWOOD-RED BLUFF-60 kV | ETL.6660 | NORTH VALLEY | 231 | 0 | 0 | 2.752% | 89.91% | 0% | 0 | 32.99% | 11.01% | 0 | 0.87152 | 11.547 | 1.5085 | 15.1802 | High | Medium | Medium | 97 | 87 | 10.0634
METCALF-GREEN VALLEY - 115 kV | ETL.2540 | SAN JOSE | 93 | 0 | 0 | 2.439% | 7.317% | 0% | 14.85 | 59% | 35.37% | 0 | 0.51905 | 15.9312 | 1.7851 | 14.7613 | High | Medium | Medium | 98 | 99 | 8.2691
MISSOURI FLAT-GOLD HILL #1 - 115 kV | ETL.2660 | SIERRA | 74 | 0 | 0 | 1.493% | 0% | 0% | 0 | 0% | 100% | 1 | 0.24614 | 27.0187 | 2.2195 | 14.7608 | Medium | High | High | 99 | 120 | 6.6505
ROSSMOOR #2 TAP - 230 kV | ETL.5461 | DIABLO | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 85.4511 | 2.9397 | 14.732 | Low | High | High | 100 | 153 | 5.0113
DIABLO-GATES #1 - 500 kV | ETL.5960 | LOS PADRES | 149 | 23 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.54511 | 12.0892 | 2.2246 | 14.6603 | High | Medium | High | 101 | 123 | 6.59
STANISLAUS-MANTECA #2 - 115 kV | ETL.3820 | STOCKTON | 163 | 1 | 0 | 0% | 0% | 0% | 0 | 66.59% | 100% | 1 | 0.83915 | 8.1034 | 2.1426 | 14.5694 | High | Medium | High | 102 | 119 | 6.8
GEYSERS #3-CLOVERDALE - 115 kV | ETL.1650 | SONOMA | 137 | 1 | 0 | 2.273% | 12.88% | 27.27% | 0 | 0% | 25.76% | 1 | 0.71774 | 18.344 | 1.0961 | 14.4312 | High | Medium | Low | 103 | 59 | 13.1662
DEL MONTE-FORT ORD #1 - 60 kV | ETL.8400 | CENTRAL COAST | 4 | 4 | 0 | 0% | 0% | 0% | 0 | 67.27% | 100% | 1 | 0.29486 | 14.9507 | 3.2599 | 14.3705 | Medium | Medium | High | 104 | 166 | 4.4083
SOBRANTE-MORAGA - 115 kV | ETL.3742 | DIABLO | 27 | 0 | 0 | 11.54% | 0% | 0% | 0 | 53.12% | 76.92% | 0 | 0.23288 | 20.9352 | 2.9376 | 14.322 | Medium | High | High | 105 | 155 | 4.8755
FULTON-HOPLAND - 60 kV | ETL.6890 | SONOMA | 423 | 0 | 0 | 5.729% | 71.88% | 0% | 0 | 0.1792% | 5.729% | 1 | 0.98005 | 11.7783 | 1.2205 | 14.0891 | High | Medium | Low | 106 | 75 | 11.5434
ROSSMOOR #1 TAP - 230 kV | ETL.5451 | DIABLO | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 78.7645 | 2.9473 | 14.0787 | Low | High | High | 107 | 159 | 4.7769
MENDOCINO-HARTLEY - 60 kV | ETL.7510 | HUMBOLDT | 203 | 1 | 0 | 0.5128% | 43.59% | 0% | 0 | 0% | 16.41% | 1 | 0.81995 | 14.4552 | 1.1845 | 14.0398 | High | Medium | Low | 108 | 74 | 11.8525
SALT SPRINGS-TIGER CREEK - 115 kV | ETL.3500 | STOCKTON | 129 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 100% | 1 | 0.74544 | 10.8896 | 1.727 | 14.0189 | High | Medium | Medium | 109 | 100 | 8.1176
SAN LUIS OBISPO-SANTA MARIA *-70 kV | ETL.9100 | LOS PADRES | 159 | 0 | 0 | 6.299% | 74.8% | 9.449% | 0 | 0% | 0% | 0 | 0.53973 | 13.5383 | 1.9157 | 13.998 | High | Medium | Medium | 110 | 110 | 7.307
STANISLAUS-MELONES SW STA-MANTECA #1 - 115 kV | ETL.3830 | STOCKTON | 214 | 2 | 0 | 0% | 0% | 0% | 0 | 63.66% | 100% | 1 | 0.92889 | 7.1298 | 2.0949 | 13.8739 | High | Medium | Medium | 111 | 122 | 6.6228
MELONES-RACETRACK - 115 kV | ETL.2400 | YOSEMITE | 164 | 0 | 0 | 1.829% | 52.44% | 0% | 0 | 0% | 16.46% | 0 | 0.54953 | 13.1733 | 1.914 | 13.8556 | High | Medium | Medium | 112 | 112 | 7.2391
MADISON-VACA - 115 kV | ETL.2170 | SACRAMENTO | 28 | 0 | 0 | 0% | 0% | 0% | 15.73 | 68.19% | 90% | 0 | 0.1909 | 47.2462 | 1.5325 | 13.8215 | Medium | High | Medium | 113 | 96 | 9.0192
VALLEY SPRINGS-MARTELL #1 - 60 kV | ETL.8240 | STOCKTON | 147 | 0 | 0 | 2.381% | 79.37% | 0% | 0 | 81.13% | 22.22% | 1 | 0.75213 | 8.6642 | 2.12 | 13.8154 | High | Medium | Medium | 114 | 125 | 6.5166
COTTONWOOD-BENTON #1 - 60 kV | ETL.6640 | NORTH VALLEY | 153 | 0 | 0 | 1.653% | 87.6% | 0% | 0 | 44.61% | 10.74% | 0 | 0.55031 | 14.1226 | 1.7764 | 13.8063 | High | Medium | Medium | 115 | 105 | 7.7719
CASTRO VALLEY-NEWARK - 230 kV | ETL.4450 | MISSION | 58 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.13826 | 38.3261 | 2.5251 | 13.3801 | Medium | High | High | 116 | 149 | 5.2989
LAYTONVILLE-WILLITS - 60 kV | ETL.8360 | HUMBOLDT | 168 | 0 | 0 | 0% | 29.33% | 0% | 0 | 0% | 30.67% | 1 | 0.46288 | 26.4063 | 1.0804 | 13.2053 | High | High | Low | 117 | 70 | 12.2229
ROUND MTN-TABLE MTN #2 - 500 kV | ETL.6070 | NORTH VALLEY | 336 | 0 | 3 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.94958 | 8.7331 | 1.5887 | 13.1748 | High | Medium | Medium | 118 | 98 | 8.2928
FULTON-LAKEVILLE - 230 kV | ETL.4950 | SONOMA | 65 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15383 | 48.1674 | 1.7767 | 13.1643 | Medium | High | Medium | 119 | 107 | 7.4094
COLGATE-PALERMO - 60 kV | ETL.6500 | SIERRA | 450 | 0 | 0 | 2.294% | 75.69% | 0% | 0 | 91.72% | 12.39% | 1 | 0.99844 | 5.7267 | 2.2868 | 13.075 | High | Medium | High | 120 | 141 | 5.7177
SNEATH LANE-PACIFICA - 60 kV | ETL.7575 | PENINSULA | 26 | 0 | 0 | 26.09% | 30.43% | 0% | 0 | 0% | 8.696% | 1 | 0.13491 | 37.4097 | 2.5649 | 12.9451 | Medium | High | High | 121 | 152 | 5.0471
SLY CREEK TAP-115 kV | ETL.4221 | NORTH VALLEY | 67 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 40.3% | 0 | 0.1146 | 81.3433 | 1.3796 | 12.8608 | Low | High | Low | 122 | 92 | 9.3222
MORRO BAY-TEMPLETON - 230 kV | ETL.5933 | LOS PADRES | 41 | 1 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.2171 | 33.8305 | 1.7446 | 12.8136 | Medium | High | Medium | 123 | 109 | 7.3447
SOBRANTE-G #1 - 115 kV | ETL.3720 | DIABLO | 39 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.10933 | 32.8223 | 3.5139 | 12.6099 | Low | High | High | 124 | 189 | 3.5886
LAKEVILLE #1 - 60 kV | ETL.7360 | SONOMA | 92 | 0 | 0 | 1.205% | 55.42% | 0% | 0 | 0% | 6.024% | 0 | 0.20998 | 29.3876 | 2.0086 | 12.3942 | Medium | High | Medium | 125 | 133 | 6.1707
TULE-SPRINGVILLE - 70 kV | ETL.9040 | FRESNO | 250 | 0 | 0 | 6.8% | 83.6% | 0% | 0 | 97.54% | 11.6% | 0 | 0.96576 | 6.5337 | 1.9522 | 12.3185 | High | Medium | Medium | 126 | 129 | 6.3101
COTTONWOOD-BENTON #2-60 kV | ETL.6650 | NORTH VALLEY | 119 | 0 | 0 | 0% | 0% | 0% | 0 | 33.59% | 20.91% | 0 | 0.28981 | 23.7227 | 1.753 | 12.0518 | Medium | High | Medium | 127 | 117 | 6.8751
LAYTONVILLE-COVELO-60 kV | ETL.7390 | HUMBOLDT | 156 | 0 | 0 | 0% | 39.56% | 0% | 0 | 0% | 17.58% | 1 | 0.23104 | 56.1906 | 0.92584 | 12.0195 | Medium | High | Low | 128 | 60 | 12.9823
BRUNSWICK #1 TAP - 115 kV | ETL.1422 | SIERRA | 49 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.12211 | 50.5163 | 1.9411 | 11.9732 | Medium | High | Medium | 129 | 134 | 6.1684
ROUND MTN-TABLE MTN #1 - 500 kV | ETL.6060 | NORTH VALLEY | 317 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.94229 | 8.2624 | 1.5197 | 11.8321 | High | Medium | Medium | 130 | 104 | 7.7856
MONTA VISTA-JEFFERSON #1 - 230 kV | ETL.5220 | DE ANZA | 78 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.18651 | 21.606 | 2.8977 | 11.6767 | Medium | High | High | 131 | 180 | 4.0297
SMARTVILLE-CAMP FAR WEST (12KV)-60 kV | ETL.7970 | SIERRA | 202 | 0 | 0 | 0.5882% | 90.59% | 0% | 12.92 | 72.87% | 1.176% | 0 | 0.80957 | 8.8778 | 1.6099 | 11.5703 | High | Medium | Medium | 132 | 113 | 7.1871
CARIBOU-TABLE MTN - 230 kV | ETL.4440 | NORTH VALLEY | 364 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 99.73% | 1 | 0.9759 | 5.8371 | 2.028 | 11.5526 | High | Medium | Medium | 133 | 143 | 5.6964
MENDOCINO-WILLITS-60 kV | ETL.7540 | HUMBOLDT | 137 | 0 | 0 | 0% | 68.25% | 0% | 0 | 100% | 15.08% | 0 | 0.70514 | 15.3023 | 1.0505 | 11.3354 | High | Medium | Low | 134 | 83 | 10.7903
TIDEWATER-SOBRANTE - 230 kV | ETL.5770 | DIABLO | 29 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.09163 | 44.2993 | 2.7623 | 11.2123 | Low | High | High | 135 | 179 | 4.0591
VACA-PARKWAY - 230 kV | ETL.5850 | SACRAMENTO | 78 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.1708 | 33.4455 | 1.9396 | 11.0802 | Medium | High | Medium | 136 | 142 | 5.7125
POTTER VALLEY-WILLITS - 60 kV | ETL.7820 | HUMBOLDT | 128 | 0 | 0 | 0% | 61.11% | 0% | 0 | 0% | 7.937% | 1 | 0.32143 | 35.8966 | 0.92196 | 10.6377 | Medium | High | Low | 137 | 76 | 11.5382
PINE GROVE TAP - 60 kV | ETL.8351 | STOCKTON | 61 | 0 | 0 | 1.639% | 36.07% | 0% | 0 | 0% | 0% | 0 | 0.14644 | 28.6948 | 2.4978 | 10.4957 | Medium | High | High | 138 | 176 | 4.202
SONOMA-PUEBLO-115 kV | ETL.3810 | SONOMA | 59 | 0 | 0 | 7.692% | 71.79% | 0% | 0 | 0% | 12.82% | 0 | 0.17628 | 42.8745 | 1.3815 | 10.4412 | Medium | High | Low | 139 | 106 | 7.558
BURNS-LONE STAR #1 - 60 kV | ETL.6230 | CENTRAL COAST | 76 | 0 | 0 | 0% | 64.47% | 0% | 5.3 | 94.31% | 10.53% | 1 | 0.44686 | 8.2597 | 2.8196 | 10.4072 | High | Medium | High | 140 | 186 | 3.691
KILARC-DESCHUTES - 60 kV | ETL.7300 | NORTH VALLEY | 511 | 0 | 0 | 1.042% | 90.83% | 0% | 0 | 0% | 3.125% | 1 | 0.99679 | 6.265 | 1.6316 | 10.1894 | High | Medium | Medium | 141 | 130 | 6.2449
MTN GATE JCT-CASCADE - 60 kV | ETL.7640 | NORTH VALLEY | 79 | 0 | 0 | 0% | 49.37% | 0% | 0 | 56.22% | 2.532% | 0 | 0.32162 | 15.7763 | 1.9995 | 10.1454 | Medium | Medium | Medium | 142 | 151 | 5.074
ROCK CREEK-POE - 230 kV | ETL.5630 | NORTH VALLEY | 210 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 97.14% | 1 | 0.71771 | 7.6521 | 1.8212 | 10.0023 | High | Medium | Medium | 143 | 145 | 5.492
CORDELIA #2 TAP - 60 kV | ETL.8184 | SACRAMENTO | 68 | 0 | 0 | 5.769% | 76.92% | 0% | 0 | 94.91% | 9.615% | 0 | 0.47767 | 9.2746 | 2.2539 | 9.9853 | High | Medium | High | 144 | 165 | 4.4302
MENDOCINO-WILLITS-FORT BRAGG - 60 kV | ETL.7550 | HUMBOLDT | 464 | 0 | 0 | 0.2242% | 49.1% | 0% | 0 | 0.2473% | 8.744% | 1 | 0.99389 | 8.0077 | 1.2514 | 9.9595 | High | Medium | Low | 145 | 103 | 7.9588
STANISLAUS-NEWARK #2 (12KV)-115 kV | ETL.3860 | MISSION | 10 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 100% | 0 | 0.23929 | 24.3184 | 1.6895 | 9.8315 | Medium | High | Medium | 146 | 140 | 5.819
LOS ESTEROS-METCALF - 230 kV | ETL.5353 | SAN JOSE | 105 | 1 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.48277 | 14.6793 | 1.3743 | 9.7392 | High | Medium | Low | 147 | 115 | 7.0868
HAMILTON BRANCH-CHESTER-60 kV | ETL.7000 | NORTH VALLEY | 211 | 0 | 0 | 3.846% | 75% | 0% | 0 | 18.59% | 3.365% | 1 | 0.78454 | 5.7331 | 2.1502 | 9.6713 | High | Medium | High | 148 | 164 | 4.4978
MOSS LANDING-METCALF - 500 kV | ETL.6050 | CENTRAL COAST | 95 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.22429 | 24.359 | 1.7645 | 9.6403 | Medium | High | Medium | 149 | 146 | 5.4635
DRUM-SUMMIT #2 - 115 kV | ETL.1450 | SIERRA | 369 | 0 | 0 | 0.2786% | 0% | 0% | 0 | 0% | 10.03% | 1 | 0.96007 | 14.0077 | 0.70775 | 9.5181 | High | Medium | Low | 150 | 57 | 13.4484
PALERMO-OROVILLE #1 - 60 kV | ETL.7730 | NORTH VALLEY | 34 | 0 | 0 | 0% | 91.67% | 0% | 0 | 71.28% | 0% | 0 | 0.36861 | 10.3019 | 2.4926 | 9.4654 | Medium | Medium | High | 151 | 184 | 3.7974
CENTERVILLE-TABLE MTN-OROVILLE - 60 kV | ETL.6330 | NORTH VALLEY | 250 | 0 | 0 | 1.471% | 76.47% | 0% | 0 | 5.701% | 20.1% | 1 | 0.71968 | 5.0692 | 2.57 | 9.3759 | High | Medium | High | 152 | 188 | 3.6482
POTTER VALLEY-MENDOCINO - 60 kV | ETL.7810 | HUMBOLDT | 70 | 0 | 0 | 4.918% | 14.75% | 0% | 8.83 | 80.27% | 67.21% | 1 | 0.56781 | 16.4832 | 0.985 | 9.219 | High | Medium | Low | 153 | 91 | 9.3593
LAKEWOOD-MEADOW LANE-CLAYTON - 115 kV | ETL.2080 | DIABLO | 11 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.064845 | 51.7285 | 2.7428 | 9.2003 | Low | High | High | 154 | 194 | 3.3543
DRUM-SPAULDING-60 kV | ETL.6770 | SIERRA | 240 | 0 | 0 | 1.25% | 80.42% | 0% | 0 | 0.1479% | 6.667% | 1 | 0.81522 | 31.1007 | 0.35929 | 9.1093 | High | High | Low | 155 | 16 | 25.3538
PLACER-GOLD HILL #1 - 115 kV | ETL.3340 | SIERRA | 73 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.16093 | 24.9379 | 2.2668 | 9.0971 | Medium | High | High | 156 | 181 | 4.0132
CLEAR LAKE-HOPLAND - 60 kV | ETL.6390 | HUMBOLDT | 99 | 0 | 0 | 0% | 37.5% | 0% | 0 | 0% | 19.32% | 0 | 0.22391 | 28.1878 | 1.4179 | 8.9494 | Medium | High | Low | 157 | 128 | 6.3116
MELONES-CURTIS - 115 kV | ETL.2390 | YOSEMITE | 135 | 0 | 0 | 0% | 2.256% | 0% | 0 | 0% | 6.767% | 0 | 0.36964 | 11.599 | 2.0786 | 8.912 | Medium | Medium | Medium | 158 | 172 | 4.2875
GARBERVILLE-LAYTONVILLE - 60 kV | ETL.8365 | HUMBOLDT | 209 | 0 | 0 | 0% | 32.29% | 0% | 0 | 0% | 23.96% | 1 | 0.25626 | 31.1751 | 1.099 | 8.7796 | Medium | High | Low | 159 | 101 | 7.989
SAN LUIS OBISPO-OCEANO - 115 kV | ETL.3530 | LOS PADRES | 108 | 0 | 0 | 3.659% | 4.878% | 0% | 0 | 0% | 52.44% | 0 | 0.26981 | 16.2584 | 1.9633 | 8.6122 | Medium | Medium | Medium | 160 | 169 | 4.3867
MORRO BAY-SAN LUIS OBISPO #1 - 115 kV | ETL.2810 | LOS PADRES | 75 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15853 | 22.3563 | 2.424 | 8.5911 | Medium | High | High | 161 | 191 | 3.5442
PLACER-DEL MAR - 60 kV | ETL.7800 | SIERRA | 113 | 0 | 0 | 0% | 86.96% | 0% | 0 | 0% | 13.04% | 0 | 0.2549 | 15.3025 | 2.1065 | 8.2166 | Medium | Medium | Medium | 162 | 182 | 3.9007
APPLE HILL #2 TAP - 115 kV | ETL.1541 | SIERRA | 36 | 0 | 0 | 0% | 69.44% | 0% | 0 | 0% | 11.11% | 0 | 0.11041 | 41.1042 | 1.8034 | 8.1842 | Low | High | Medium | 163 | 163 | 4.5381
METCALF-MOSS LANDING #1 - 230 kV | ETL.5100 | CENTRAL COAST | 71 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.1708 | 25.5515 | 1.8421 | 8.0395 | Medium | High | Medium | 164 | 170 | 4.3642
CRAG VIEW-CASCADE - 115 kV | ETL.1350 | NORTH VALLEY | 189 | 2 | 0 | 0.5348% | 0% | 0% | 0 | 100% | 20.86% | 1 | 0.93996 | 5.1187 | 1.6538 | 7.9571 | High | Medium | Medium | 165 | 158 | 4.8114
DIVIDE-CABRILLO #1 - 115 kV | ETL.1380 | LOS PADRES | 94 | 2 | 0 | 0% | 0% | 0% | 0 | 0% | 7.692% | 1 | 0.22416 | 12.3046 | 2.8685 | 7.9118 | Medium | Medium | High | 166 | 209 | 2.7582
DRUM-SUMMIT #1 - 115 kV | ETL.1440 | SIERRA | 342 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 24.62% | 1 | 0.92005 | 13.9593 | 0.6087 | 7.8177 | High | Medium | Low | 167 | 61 | 12.8433
ELECTRA-BELLOTA - 230 kV | ETL.4670 | STOCKTON | 103 | 0 | 0 | 0% | 0% | 0% | 0 | 54.25% | 100% | 0 | 0.425 | 7.8762 | 2.2355 | 7.4831 | High | Medium | High | 168 | 195 | 3.3474
PITTSBURG-SAN RAMON - 230 kV | ETL.5490 | MISSION | 58 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.14257 | 19.8618 | 2.5983 | 7.3574 | Medium | High | High | 169 | 207 | 2.8316
MORAGA-CASTRO VALLEY - 230 kV | ETL.5250 | MISSION | 58 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.12403 | 20.8469 | 2.837 | 7.3356 | Medium | High | High | 170 | 214 | 2.5857
AUBERRY TAP - 70 kV | ETL.9331 | FRESNO | 38 | 0 | 0 | 0% | 78.95% | 0% | 0 | 0% | 76.32% | 0 | 0.15331 | 22.9945 | 2.0626 | 7.2709 | Medium | High | Medium | 171 | 192 | 3.5252
CRESTA-RIO OSO-230 kV | ETL.4590 | NORTH VALLEY | 150 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.47094 | 6.7598 | 2.2643 | 7.2084 | High | Medium | High | 172 | 197 | 3.1834
WASHOE TAP - 60 kV | ETL.6911 | SONOMA | 20 | 0 | 0 | 0% | 85% | 0% | 0 | 0% | 5% | 0 | 0.10205 | 48.0744 | 1.4685 | 7.2044 | Low | High | Low | 173 | 154 | 4.9058
WINDSOR-FITCH MOUNTAIN-60 kV | ETL.6900 | SONOMA | 23 | 0 | 0 | 21.43% | 64.29% | 0% | 0 | 87.17% | 7.143% | 0 | 0.33946 | 19.2589 | 1.1 | 7.1911 | Medium | High | Low | 174 | 124 | 6.5375
COLEMAN-RED BLUFF - 60 kV | ETL.6440 | NORTH VALLEY | 322 | 0 | 0 | 0.9615% | 83.33% | 0% | 0 | 77.46% | 6.731% | 1 | 0.97754 | 4.9413 | 1.4686 | 7.0936 | High | Medium | Low | 175 | 157 | 4.8303
PIT #1-COTTONWOOD - 230 kV | ETL.5390 | NORTH VALLEY | 481 | 12 | 1 | 0% | 0% | 0% | 0 | 53.22% | 99.77% | 1 | 0.9989 | 5.4111 | 1.2916 | 6.9812 | High | Medium | Low | 176 | 148 | 5.4051
APPLE HILL #1 TAP - 115 kV | ETL.1531 | SIERRA | 33 | 0 | 0 | 3.03% | 72.73% | 0% | 0 | 0% | 18.18% | 0 | 0.11801 | 32.5892 | 1.7777 | 6.8366 | Medium | High | Medium | 177 | 183 | 3.8457
VOLTA-SOUTH - 60 kV | ETL.8300 | NORTH VALLEY | 106 | 0 | 0 | 0% | 93.4% | 0% | 0 | 100% | 2.83% | 0 | 0.66072 | 8.1846 | 1.2482 | 6.7501 | High | Medium | Low | 178 | 147 | 5.4077
GEYSERS #12-FULTON - 230 kV | ETL.4750 | SONOMA | 104 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.26028 | 16.9231 | 1.5237 | 6.7114 | Medium | Medium | Medium | 179 | 167 | 4.4048
SOBRANTE-G #2 | ETL.3730 | DIABLO | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.061672 | 35.3263 | 2.9751 | 6.4816 | Low | High | High | 180 | 225 | 2.1787
COTTONWOOD-DELEVAN #2 - 230 kV | ETL.4580 | NORTH VALLEY | 115 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.16093 | 26.2598 | 1.5215 | 6.4296 | Medium | High | Medium | 181 | 174 | 4.2259
COTTONWOOD-DELEVAN #1 - 230 kV | ETL.4550 | NORTH VALLEY | 115 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15853 | 26.6607 | 1.5208 | 6.4276 | Medium | High | Medium | 182 | 173 | 4.2265
HUMBOLDT BAY-HUMBOLDT #1 - 115 kV | ETL.1800 | HUMBOLDT | 15 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.071649 | 27.4389 | 3.2495 | 6.3884 | Low | High | High | 183 | 236 | 1.966
POE-RIO OSO - 230 kV | ETL.5540 | NORTH VALLEY | 136 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.35066 | 7.7264 | 2.3308 | 6.3149 | Medium | Medium | High | 184 | 211 | 2.7093
VALLEY SPRINGS-CLAY - 60 kV | ETL.8264 | STOCKTON | 181 | 0 | 0 | 3.974% | 51.66% | 0% | 0 | 0% | 27.81% | 1 | 0.51292 | 5.7271 | 2.1466 | 6.3057 | High | Medium | High | 185 | 200 | 2.9376
NORTH DUBLIN-CAYETANO - 230 kV | ETL.4500 | MISSION | 13 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.071649 | 34.2648 | 2.5406 | 6.2373 | Low | High | High | 186 | 220 | 2.455
ROUND MTN-COTTONWOOD #3 - 230 kV | ETL.5650 | NORTH VALLEY | 262 | 0 | 0 | 0% | 0% | 0% | 0 | 94.71% | 100% | 1 | 0.95896 | 4.4821 | 1.4455 | 6.2128 | High | Medium | Low | 187 | 171 | 4.2982
TEMPLETON-ATASCADERO - 70 kV | ETL.9410 | LOS PADRES | 92 | 0 | 0 | 0% | 82.76% | 0% | 0 | 0% | 0% | 0 | 0.22106 | 13.2748 | 2.0918 | 6.1384 | Medium | Medium | Medium | 188 | 201 | 2.9346
SANTA ROSA-CORONA - 115 kV | ETL.4309 | SONOMA | 31 | 0 | 17 | 0% | 86.96% | 0% | 0 | 0% | 0% | 0 | 0.10353 | 33.253 | 1.7528 | 6.0348 | Low | High | Medium | 189 | 193 | 3.4428
FRUITLAND TAP - 60 kV | ETL.6221 | HUMBOLDT | 55 | 1 | 0 | 0% | 36.73% | 0% | 0 | 0% | 8.163% | 0 | 0.23651 | 31.1256 | 0.80932 | 5.9577 | Medium | High | Low | 190 | 108 | 7.3614
IGNACIO-SOBRANTE - 230 kV | ETL.4920 | DIABLO | 73 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15853 | 13.3276 | 2.7472 | 5.8044 | Medium | Medium | High | 191 | 228 | 2.1128
UKIAH-HOPLAND-CLOVERDALE - 115 kV | ETL.4050 | SONOMA | 221 | 0 | 0 | 62.98% | 8.654% | 0% | 0 | 0% | 20.67% | 1 | 0.73412 | 8.1275 | 0.95966 | 5.7258 | High | Medium | Low | 192 | 137 | 5.9665
KERCKHOFF-CLOVIS-SANGER #1 - 115 kV | ETL.1890 | FRESNO | 74 | 3 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.24564 | 19.8199 | 1.1657 | 5.6753 | Medium | High | Low | 193 | 156 | 4.8686
NEWARK-LIVERMORE - 60 kV | ETL.7660 | MISSION | 60 | 0 | 0 | 0% | 23.53% | 0% | 15.04 | 92.93% | 61.76% | 0 | 0.42836 | 6.6688 | 1.9573 | 5.5914 | High | Medium | Medium | 194 | 206 | 2.8567
FULTON-MOLINO-COTATI-60 kV | ETL.6910 | SONOMA | 37 | 0 | 0 | 2.941% | 85.29% | 0% | 0 | 0% | 2.941% | 1 | 0.15382 | 24.5452 | 1.4744 | 5.5669 | Medium | High | Medium | 195 | 185 | 3.7756
BAHIA-MORAGA - 230 kV | ETL.4340 | EAST BAY | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 33.1956 | 2.7655 | 5.475 | Low | High | High | 196 | 235 | 1.9797
NEWARK-JARVIS #1 - 115 kV | ETL.3020 | MISSION | 15 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.062713 | 39.6873 | 2.1568 | 5.368 | Low | High | High | 197 | 219 | 2.4889
HIGGINS-BELL - 115 kV | ETL.1412 | SIERRA | 60 | 0 | 0 | 0% | 0% | 0% | 8.3 | 79.27% | 100% | 0 | 0.3569 | 8.0509 | 1.86 | 5.3444 | Medium | Medium | Medium | 198 | 205 | 2.8734
BRICEBURG JCT-MARIPOSA TAP-70 kV | ETL.8651 | YOSEMITE | 159 | 0 | 0 | 0% | 76.1% | 0% | 0 | 0% | 3.145% | 0 | 0.51228 | 7.9535 | 1.3046 | 5.3157 | High | Medium | Low | 199 | 178 | 4.0745
VIEJO-MONTEREY - 60 kV | ETL.8270 | CENTRAL COAST | 18 | 0 | 0 | 14.29% | 64.29% | 0% | 0 | 0% | 0% | 1 | 0.15694 | 13.2834 | 2.5329 | 5.2804 | Medium | Medium | High | 200 | 230 | 2.0847
VALLEY SPRINGS-CALAVERAS CEMENT - 60 kV | ETL.8220 | STOCKTON | 97 | 0 | 0 | 0% | 67.02% | 0% | 0 | 0% | 0% | 0 | 0.21747 | 11.5528 | 2.0852 | 5.2388 | Medium | Medium | Medium | 201 | 217 | 2.5124
MENDOCINO-PHILO JCT-HOPLAND - 60 kV | ETL.7520 | HUMBOLDT | 207 | 0 | 0 | 2.618% | 71.73% | 0% | 21.34 | 90.54% | 12.57% | 1 | 0.8716 | 5.9217 | 1.0001 | 5.1617 | High | Medium | Low | 202 | 150 | 5.1614
HALSEY-PLACER - 60 kV | ETL.6990 | SIERRA | 50 | 1 | 0 | 0% | 76.47% | 0% | 0 | 0% | 2.941% | 0 | 0.2087 | 11.571 | 2.0612 | 4.9774 | Medium | Medium | Medium | 203 | 221 | 2.4148
CAMP EVERS-PAUL SWEET-115 kV | ETL.1220 | CENTRAL COAST | 2 | 0 | 0 | 50% | 0% | 0% | 0 | 0% | 50% | 0 | 0.10201 | 18.1631 | 2.6683 | 4.9439 | Low | Medium | High | 204 | 240 | 1.8528
PIT #1-HAT CREEK #2-BURNEY - 60 kV | ETL.7040 | NORTH VALLEY | 156 | 0 | 0 | 4.605% | 70.39% | 0% | 3.44 | 25.75% | 1.974% | 1 | 0.59732 | 7.8133 | 1.0522 | 4.9108 | High | Medium | Low | 205 | 162 | 4.667
MORRO BAY-SAN LUIS OBISPO #2 - 115 kV | ETL.2820 | LOS PADRES | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 35.3263 | 2.3373 | 4.8423 | Low | High | High | 206 | 231 | 2.0717
SOBRANTE-STANDARD OIL SW STA #1 - 115 kV | ETL.3800 | DIABLO | 53 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 98% | 0 | 0.12829 | 12.9722 | 2.8218 | 4.6959 | Medium | Medium | High | 207 | 248 | 1.6642
CALLENDER SW STA-MESA-115 kV | ETL.1210 | LOS PADRES | 66 | 1 | 0 | 30.23% | 0% | 0% | 0 | 0% | 55.81% | 1 | 0.26354 | 11.4832 | 1.5456 | 4.6773 | Medium | Medium | Medium | 208 | 199 | 3.0263
LAKEVILLE-SONOMA #1 - 115 kV | ETL.2063 | SONOMA | 32 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.085858 | 33.9799 | 1.5569 | 4.5422 | Low | High | Medium | 209 | 202 | 2.9174
CLEAR LAKE-KONOCTI-60 kV | ETL.6852 | HUMBOLDT | 52 | 0 | 0 | 0% | 50% | 0% | 0 | 0% | 16.67% | 1 | 0.11164 | 18.0084 | 2.2425 | 4.5085 | Low | Medium | High | 210 | 234 | 2.0105
WISHON-SAN JOAQUIN #3 - 70 kV | ETL.9340 | YOSEMITE | 116 | 0 | 0 | 0% | 83.62% | 0% | 0 | 100% | 43.1% | 1 | 0.71159 | 5.043 | 1.2458 | 4.4705 | High | Medium | Low | 211 | 190 | 3.5886
PEORIA TAP - 115 kV | ETL.2391 | YOSEMITE | 11 | 0 | 0 | 0% | 72.73% | 0% | 0 | 0% | 0% | 0 | 0.085275 | 30.24 | 1.6368 | 4.2207 | Low | High | Medium | 212 | 215 | 2.5787
COTTONWOOD-LOGAN CREEK - 230 kV | ETL.4570 | NORTH VALLEY | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 47.6367 | 1.4961 | 4.1797 | Low | High | Medium | 213 | 208 | 2.7937
SALINAS-FORT ORD #2 - 60 kV | ETL.8423 | CENTRAL COAST | 46 | 6 | 0 | 0% | 0% | 0% | 0 | 99.4% | 100% | 1 | 0.55922 | 3.8242 | 1.9307 | 4.1289 | High | Medium | Medium | 214 | 226 | 2.1386
MENDOCINO-UKIAH - 115 kV | ETL.2420 | HUMBOLDT | 66 | 0 | 0 | 31.03% | 12.07% | 0% | 0 | 0% | 55.17% | 0 | 0.21612 | 15.4176 | 1.2364 | 4.1197 | Medium | Medium | Low | 215 | 196 | 3.332
LAKEVILLE-IGNACIO #2 - 230 kV | ETL.3745 | NORTH BAY | 19 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 23.8842 | 2.8386 | 4.1118 | Low | High | High | 216 | 265 | 1.4485
PARADISE-BUTTE - 115 kV | ETL.4396 | NORTH VALLEY | 98 | 0 | 0 | 2.247% | 11.24% | 0% | 0 | 0% | 100% | 0 | 0.44063 | 3.5439 | 2.6142 | 4.0823 | High | Medium | High | 217 | 257 | 1.5616
DUNLAP TAP - 70 kV | ETL.9061 | FRESNO | 131 | 1 | 0 | 0.7812% | 61.72% | 0% | 0 | 0% | 39.06% | 0 | 0.62003 | 4.9797 | 1.2753 | 3.9376 | High | Medium | Low | 218 | 198 | 3.0876
DEL MONTE-VIEJO - 60 kV | ETL.6710 | CENTRAL COAST | 130 | 0 | 0 | 11.76% | 68.07% | 0% | 0 | 0% | 3.361% | 1 | 0.45397 | 3.5892 | 2.4052 | 3.919 | High | Medium | High | 219 | 250 | 1.6294
RINCON #1 TAP - 115 kV | ETL.1601 | SONOMA | 5 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.062713 | 36.5812 | 1.7059 | 3.9136 | Low | High | Medium | 220 | 223 | 2.2941
SANTA YNEZ TAP - 115 kV | ETL.3701 | LOS PADRES | 130 | 0 | 0 | 2.941% | 38.24% | 0% | 0 | 0% | 14.71% | 0 | 0.11716 | 24.6206 | 1.3466 | 3.8842 | Medium | High | Low | 221 | 204 | 2.8845
GRANITE ROCK TAP - 60 kV | ETL.8311 | CENTRAL COAST | 27 | 0 | 0 | 0% | 70.37% | 0% | 0 | 0% | 0% | 0 | 0.11035 | 24.2838 | 1.4298 | 3.8316 | Low | High | Low | 222 | 213 | 2.6797
GOLDTREE TAP-115 kV | ETL.2821 | LOS PADRES | 36 | 0 | 0 | 10% | 0% | 0% | 0 | 0% | 0% | 0 | 0.053861 | 30.3689 | 2.2874 | 3.7415 | Low | High | High | 223 | 249 | 1.6357
RIO DELL JCT-BRIDGEVILLE - 60 kV | ETL.7850 | HUMBOLDT | 199 | 0 | 0 | 1.163% | 58.14% | 0% | 0 | 0.1406% | 2.326% | 1 | 0.55921 | 8.5185 | 0.78075 | 3.7192 | High | Medium | Low | 224 | 160 | 4.7637
DRUM PH #2 TAP - 115 kV | ETL.6375 | SIERRA | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 50% | 0 | 0.18316 | 34.713 | 0.58054 | 3.6911 | Medium | High | Low | 225 | 127 | 6.3582
HILLSDALE JCT-HALF MOON BAY - 60 kV | ETL.7060 | PENINSULA | 68 | 0 | 0 | 6.897% | 13.79% | 0% | 0 | 0% | 12.07% | 1 | 0.15109 | 9.6421 | 2.4536 | 3.5745 | Medium | Medium | High | 226 | 263 | 1.4569
SPAULDING-SUMMIT - 60 kV | ETL.8060 | SIERRA | 482 | 0 | 0 | 2.179% | 69.72% | 0% | 0 | 2.811% | 6.754% | 1 | 0.99566 | 4.7316 | 0.75111 | 3.5385 | High | Medium | Low | 227 | 161 | 4.711
PARADISE-TABLE MTN - 115 kV | ETL.4316 | NORTH VALLEY | 168 | 0 | 0 | 0% | 9.036% | 0% | 0 | 0% | 73.49% | 1 | 0.61237 | 2.3622 | 2.3592 | 3.4127 | High | Low | High | 228 | 266 | 1.4466
PARDEE #1 TAP-60 kV | ETL.8231 | STOCKTON | 3 | 0 | 0 | 33.33% | 0% | 0% | 0 | 100% | 0% | 0 | 0.21675 | 7.8122 | 1.9731 | 3.341 | Medium | Medium | Medium | 229 | 247 | 1.6933
VINEYARD-NEWARK - 230 kV | ETL.4536 | MISSION | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 26.5534 | 2.1284 | 3.3145 | Low | High | Medium | 230 | 258 | 1.5572
RIO DELL TAP - 60 kV | ETL.7851 | HUMBOLDT | 9 | 0 | 0 | 0% | 0% | 0% | 0 | 92.88% | 20% | 0 | 0.13601 | 18.8205 | 1.2939 | 3.3121 | Medium | High | Low | 231 | 216 | 2.5597
COTTONWOOD-PANORAMA - 115 kV | ETL.1340 | NORTH VALLEY | 35 | 0 | 0 | 6.667% | 0% | 76.67% | 0 | 0% | 10% | 0 | 0.18099 | 10.2504 | 1.7753 | 3.2935 | Medium | Medium | Medium | 232 | 239 | 1.8552
PIT #3-PIT #1 - 230 kV | ETL.5400 | NORTH VALLEY | 174 | 16 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.7099 | 4.1096 | 1.1257 | 3.2841 | High | Medium | Low | 233 | 203 | 2.9174
TULUCAY-NAPA #1 - 60 kV | ETL.8180 | NORTH BAY | 75 | 0 | 1 | 16.18% | 8.824% | 41.18% | 0 | 0% | 7.353% | 1 | 0.23194 | 7.0004 | 2.0049 | 3.2552 | Medium | Medium | Medium | 234 | 251 | 1.6237
HUMBOLDT-MAPLE CREEK - 60 kV | ETL.7130 | HUMBOLDT | 103 | 1 | 0 | 2.151% | 21.51% | 0% | 0 | 0.3595% | 6.452% | 1 | 0.42871 | 3.1488 | 2.3953 | 3.2334 | High | Medium | High | 235 | 270 | 1.3499
LAS POSITAS-NEWARK - 230 kV | ETL.4980 | MISSION | 50 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.09163 | 17.1079 | 1.9982 | 3.1324 | Low | Medium | Medium | 236 | 256 | 1.5676
HARTLEY-CLEARLAKE - 60 kV | ETL.7515 | HUMBOLDT | 55 | 0 | 0 | 2.5% | 67.5% | 0% | 0 | 0% | 5% | 0 | 0.13895 | 13.1263 | 1.704 | 3.1078 | Medium | Medium | Medium | 237 | 242 | 1.8239
COLGATE PH-COLGATE SW STA - 60 kV | ETL.6460 | SIERRA | 3 | 0 | 0 | 0% | 33.33% | 0% | 0 | 0% | 100% | 0 | 0.21742 | 7.3326 | 1.8937 | 3.0191 | Medium | Medium | Medium | 238 | 252 | 1.5943
CAPE HORN TAP - 60 kV | ETL.6761 | SIERRA | 6 | 0 | 0 | 0% | 33.33% | 0% | 0 | 0% | 0% | 0 | 0.078567 | 23.8842 | 1.6088 | 3.019 | Low | High | Medium | 239 | 237 | 1.8765
IBM HARRY RD #1 TAP - 115 kV | ETL.2501 | SAN JOSE | 7 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.064845 | 34.073 | 1.361 | 3.0072 | Low | High | Low | 240 | 224 | 2.2095
COLGATE-SMARTVILLE #2 - 60 kV | ETL.6520 | SIERRA | 155 | 0 | 0 | 0% | 60% | 0% | 0 | 97.48% | 5.806% | 1 | 0.78257 | 1.961 | 1.9468 | 2.9877 | High | Low | Medium | 241 | 259 | 1.5347
RACETRACK TAP - 115 kV | ETL.2393 | YOSEMITE | 52 | 0 | 0 | 5.769% | 53.85% | 0% | 0 | 0% | 1.923% | 0 | 0.11969 | 10.4549 | 2.3414 | 2.9299 | Medium | Medium | High | 242 | 275 | 1.2514
TESLA-NEWARK #2 - 230 kV | ETL.5354 | MISSION | 58 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.096185 | 15.1725 | 2.0026 | 2.9225 | Low | Medium | Medium | 243 | 262 | 1.4594
ROUND MTN-COTTONWOOD #2 - 230 kV | ETL.5640 | NORTH VALLEY | 193 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.60326 | 3.5005 | 1.3808 | 2.9158 | High | Medium | Low | 244 | 229 | 2.1117
DUTCH FLAT #2 TAP - 115 kV | ETL.1421 | SIERRA | 9 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 11.11% | 0 | 0.035633 | 77.203 | 1.0341 | 2.8449 | Low | High | Low | 245 | 210 | 2.751
WEIMAR-HALSEY-60 kV | ETL.8340 | SIERRA | 139 | 0 | 0 | 0% | 73.38% | 0% | 0 | 0% | 0.7194% | 0 | 0.47932 | 3.3 | 1.7926 | 2.8355 | High | Medium | Medium | 246 | 255 | 1.5818
IBM HARRY RD #2 TAP - 115 kV | ETL.2481 | SAN JOSE | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 35.3263 | 1.3659 | 2.8297 | Low | High | Low | 247 | 231 | 2.0717
CENTERVILLE-TABLE MTN - 60 kV | ETL.6320 | NORTH VALLEY | 128 | 0 | 0 | 3.361% | 82.35% | 0% | 0 | 0% | 24.37% | 1 | 0.39408 | 2.7385 | 2.6091 | 2.8157 | High | Low | High | 248 | 283 | 1.0792
MTN QUARRIES TAP - 60 kV | ETL.6991 | SIERRA | 29 | 0 | 0 | 4% | 20% | 0% | 0 | 0% | 84% | 0 | 0.18233 | 7.493 | 2.0513 | 2.8025 | Medium | Medium | Medium | 249 | 268 | 1.3662
FORT BRAGG-ELK - 60 kV | ETL.2060 | HUMBOLDT | 293 | 0 | 0 | 0.3745% | 1.498% | 0% | 0 | 0% | 4.12% | 1 | 0.86512 | 1.5755 | 2.0302 | 2.7673 | High | Low | Medium | 250 | 269 | 1.363
METCALF-EDENVALE #1 - 115 kV | ETL.2480 | SAN JOSE | 13 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.065935 | 30.9398 | 1.3535 | 2.7613 | Low | High | Low | 251 | 233 | 2.04
MANVILLE TAP - 115 kV | ETL.1372 | LOS PADRES | 29 | 0 | 0 | 5.263% | 5.263% | 0% | 0 | 0% | 47.37% | 0 | 0.11477 | 9.147 | 2.6302 | 2.7612 | Low | Medium | High | 252 | 286 | 1.0498
PARDEE #2 TAP - 60 kV | ETL.8251 | STOCKTON | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 0% | 0 | 0.12363 | 11.2183 | 1.9729 | 2.7363 | Medium | Medium | Medium | 253 | 267 | 1.387
PALERMO-WYANDOTTE - 115 kV | ETL.4315 | NORTH VALLEY | 13 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.065935 | 16.344 | 2.5311 | 2.7277 | Low | Medium | High | 254 | 284 | 1.0777
EXCHEQUER-YOSEMITE - 70 kV | ETL.8650 | YOSEMITE | 241 | 3 | 0 | 0% | 0% | 0% | 60380.9 | 0.0006683% | 99.58% | 1 | 0.74668 | 2.4937 | 1.4623 | 2.7229 | High | Low | Low | 255 | 238 | 1.862
IGNACIO-ALTO-SAUSALITO #2 - 60 kV | ETL.7170 | NORTH BAY | 7 | 0 | 0 | 0% | 0% | 0% | 0 | 10.49% | 16.67% | 0 | 0.041249 | 24.3184 | 2.6882 | 2.6965 | Low | High | High | 256 | 296 | 1.0031
CAYUCOS-CAMBRIA-70 kV | ETL.8560 | LOS PADRES | 80 | 0 | 0 | 5.797% | 21.74% | 0% | 0 | 0% | 47.83% | 1 | 0.22061 | 5.4658 | 2.2009 | 2.6538 | Medium | Medium | High | 257 | 277 | 1.2058
METCALF-EL PATIO #1 - 115 kV | ETL.2500 | SAN JOSE | 15 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.07406 | 24.6539 | 1.4188 | 2.5905 | Low | High | Low | 258 | 241 | 1.8259
EXCHEQUER-MARIPOSA - 70 kV | ETL.8640 | YOSEMITE | 157 | 0 | 0 | 9.032% | 72.26% | 0% | 0 | 0% | 82.58% | 1 | 0.69191 | 3.6004 | 1.0232 | 2.5489 | High | Medium | Low | 259 | 218 | 2.4911
LAKEVILLE-IGNACIO #1 - 230 kV | ETL.4940 | NORTH BAY | 21 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.061672 | 13.9866 | 2.952 | 2.5463 | Low | Medium | High | 260 | 306 | 0.86259
TESLA-NEWARK #1 - 230 kV | ETL.5720 | MISSION | 44 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.087269 | 14.3508 | 1.9802 | 2.48 | Low | Medium | Medium | 261 | 274 | 1.2524
HUMBOLDT BAY-RIO DELL JCT - 60 kV | ETL.7100 | HUMBOLDT | 28 | 0 | 0 | 6.667% | 13.33% | 0% | 0 | 0% | 0% | 1 | 0.11244 | 15.2359 | 1.4347 | 2.4578 | Low | Medium | Low | 262 | 246 | 1.7131
VASONA-METCALF - 230 kV | ETL.5932 | SAN JOSE | 15 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.07406 | 23.2955 | 1.4185 | 2.4473 | Low | High | Low | 263 | 245 | 1.7253
BELLOTA-RIVERBANK-MELONES SW STA-115 kV | ETL.1070 | STOCKTON | 146 | 0 | 0 | 7.965% | 36.28% | 11.5% | 0 | 0% | 7.08% | 1 | 0.40221 | 3.3186 | 1.8272 | 2.4389 | High | Medium | Medium | 264 | 271 | 1.3348
HUMBOLDT-BRIDGEVILLE - 115 kV | ETL.1810 | HUMBOLDT | 161 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 90.91% | 0 | 0.15661 | 6.333 | 2.4403 | 2.4203 | Medium | Medium | High | 265 | 297 | 0.99179
VACA-BAHIA - 230 kV | ETL.5810 | SACRAMENTO | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 24.3184 | 1.6227 | 2.3534 | Low | High | Medium | 266 | 264 | 1.4503
PALERMO-NICOLAUS - 115 kV | ETL.3210 | NORTH VALLEY | 9 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.067043 | 13.679 | 2.5088 | 2.3008 | Low | Medium | High | 267 | 302 | 0.91709
TESLA-METCALF - 500 kV | ETL.6110 | SAN JOSE | 121 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.33857 | 6.2884 | 1.079 | 2.2973 | Medium | Medium | Low | 268 | 227 | 2.1291
OLEUM-MARTINEZ - 115 kV | ETL.3170 | DIABLO | 31 | 5 | 0 | 0% | 0% | 0% | 0 | 72.9% | 100% | 0 | 0.4164 | 2.4614 | 2.2389 | 2.2946 | High | Low | High | 269 | 291 | 1.0249
NEWARK-VALLECITOS - 60 kV | ETL.7670 | MISSION | 19 | 0 | 0 | 0% | 0% | 0% | 0 | 56.75% | 100% | 0 | 0.1604 | 6.8018 | 2.0915 | 2.2819 | Medium | Medium | Medium | 270 | 282 | 1.091
MOSS LANDING-COBURN - 230 kV | ETL.5330 | CENTRAL COAST | 154 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 98.57% | 0 | 0.4242 | 9.7186 | 0.52954 | 2.1831 | High | Medium | Low | 271 | 177 | 4.1226
FITCH MTN #1 TAP - 60 kV | ETL.6891 | SONOMA | 8 | 0 | 0 | 0% | 66.67% | 0% | 0 | 0% | 0% | 0 | 0.11618 | 14.9507 | 1.2404 | 2.1545 | Low | Medium | Low | 272 | 244 | 1.737
METCALF-EDENVALE #2 - 115 kV | ETL.2490 | SAN JOSE | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 26.5534 | 1.3418 | 2.1249 | Low | High | Low | 273 | 254 | 1.5836
KILARC-CEDAR CREEK - 60 kV | ETL.7290 | NORTH VALLEY | 285 | 0 | 0 | 2.456% | 82.81% | 0% | 0 | 98.94% | 8.07% | 1 | 0.97905 | 16.473 | 0.13083 | 2.11 | High | Medium | Low | 274 | 45 | 16.1279
BUENA VISTA BIOMASS POWER TAP - 60 kV | ETL.8252 | STOCKTON | 8 | 0 | 0 | 0% | 16.67% | 0% | 0 | 0% | 66.67% | 0 | 0.12313 | 7.9754 | 2.1044 | 2.0666 | Medium | Medium | Medium | 275 | 298 | 0.98201
NARROWS #1 TAP - 60 kV | ETL.6511 | SIERRA | 35 | 0 | 0 | 2.857% | 45.71% | 0% | 0 | 98.91% | 2.857% | 0 | 0.36774 | 2.7386 | 2.0499 | 2.0644 | Medium | Low | Medium | 276 | 294 | 1.0071
CARBERRY SW STA-ROUND MTN - 230 kV | ETL.5410 | NORTH VALLEY | 107 | 0 | 0 | 0% | 0% | 0% | 0 | 1.577% | 100% | 0 | 0.29751 | 9.0701 | 0.76387 | 2.0613 | Medium | Medium | Low | 277 | 212 | 2.6985
PLACER-GOLD HILL #2 - 115 kV | ETL.4290 | SIERRA | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.058646 | 14.9507 | 2.3223 | 2.0362 | Low | Medium | High | 278 | 303 | 0.87679
RINCON #2 TAP - 115 kV | ETL.1611 | SONOMA | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 19.9979 | 1.7143 | 2.0105 | Low | High | Medium | 279 | 279 | 1.1728
SISQUOC-SANTA YNEZ SW STA - 115 kV | ETL.3700 | LOS PADRES | 209 | 0 | 0 | 2.01% | 45.73% | 0% | 0 | 0% | 10.55% | 0 | 0.68552 | 3.4359 | 0.84239 | 1.9841 | High | Medium | Low | 280 | 222 | 2.3554
ROLLINS TAP - 60 kV | ETL.6762 | SIERRA | 14 | 0 | 0 | 0% | 28.57% | 0% | 0 | 0% | 7.143% | 0 | 0.065688 | 18.6162 | 1.6163 | 1.9765 | Low | High | Medium | 281 | 276 | 1.2228
STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA - 115 kV | ETL.3840 | STOCKTON | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 94.33% | 100% | 1 | 0.22977 | 4.4061 | 1.9495 | 1.9737 | Medium | Medium | Medium | 282 | 292 | 1.0124
COLGATE-SMARTVILLE #1 - 60 kV | ETL.6510 | SIERRA | 147 | 0 | 0 | 1.361% | 57.14% | 0% | 0 | 0% | 29.93% | 0 | 0.49903 | 2.0231 | 1.9467 | 1.9654 | High | Low | Medium | 283 | 293 | 1.0096
COLEMAN-SOUTH - 60 kV | ETL.6450 | NORTH VALLEY | 285 | 0 | 0 | 1.053% | 89.47% | 0% | 0 | 0% | 3.509% | 0 | 0.91502 | 1.675 | 1.2793 | 1.9608 | High | Low | Low | 284 | 260 | 1.5327
METCALF-HICKS 1 & 2-115 kV | ETL.4317 | SAN JOSE | 15 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.071649 | 18.4058 | 1.443 | 1.903 | Low | High | Low | 285 | 272 | 1.3188
LIMESTONE TAP - 60 kV | ETL.6951 | SIERRA | 15 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.035232 | 24.4349 | 2.1549 | 1.8552 | Low | High | High | 286 | 307 | 0.86089
PALERMO-COLGATE - 230 kV | ETL.5360 | SIERRA | 83 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.19477 | 4.3458 | 2.1658 | 1.8332 | Medium | Medium | High | 287 | 308 | 0.84642
FLINT TAP - 115 kV | ETL.3341 | SIERRA | 29 | 0 | 0 | 9.524% | 47.62% | 0% | 0 | 0% | 23.81% | 0 | 0.11687 | 6.9205 | 2.2484 | 1.8185 | Medium | Medium | High | 288 | 312 | 0.80878
FORBESTOWN TAP - 115 kV | ETL.4222 | NORTH VALLEY | 10 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 60% | 0 | 0.051442 | 21.4427 | 1.632 | 1.8002 | Low | High | Medium | 289 | 281 | 1.103
CHINESE CAMP (ULTRA POWER) TAP - 115 kV | ETL.2392 | YOSEMITE | 28 | 0 | 0 | 0% | 73.68% | 0% | 0 | 0% | 0% | 0 | 0.097093 | 11.3729 | 1.6132 | 1.7813 | Low | Medium | Medium | 290 | 280 | 1.1042
GARCIA TAP - 60 kV | ETL.8411 | HUMBOLDT | 34 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 8.824% | 0 | 0.053703 | 29.5269 | 1.1095 | 1.7594 | Low | High | Low | 291 | 253 | 1.5857
MIDDLE FORK #1-60 kV | ETL.8405 | SIERRA | 140 | 0 | 0 | 0% | 56.43% | 0% | 0 | 0% | 4.286% | 1 | 0.34383 | 3.1094 | 1.6015 | 1.7121 | Medium | Medium | Medium | 292 | 285 | 1.0691
MORRO BAY-SOLAR SW STA #2 - 230 kV | ETL.5310 | LOS PADRES | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.063771 | 12.4421 | 2.146 | 1.7027 | Low | Medium | High | 293 | 313 | 0.79344
CRAZY HORSE CANYON-SALINAS-SOLEDAD #1-115 kV | ETL.2900 | CENTRAL COAST | 90 | 1 | 0 | 0% | 0% | 0% | 4.71 | 20.51% | 100% | 1 | 0.45606 | 8.0653 | 0.44956 | 1.6536 | High | Medium | Low | 294 | 187 | 3.6783
PALERMO-OROVILLE #2 - 60 kV | ETL.7740 | NORTH VALLEY | 26 | 0 | 0 | 0% | 71.43% | 0% | 2.19 | 21.64% | 0% | 0 | 0.13523 | 4.2065 | 2.8893 | 1.6436 | Medium | Medium | High | 295 | 327 | 0.56884
DIVIDE-VANDENBERG #1 - 70 kV | ETL.8620 | LOS PADRES | 66 | 2 | 0 | 6.25% | 7.812% | 0% | 0 | 0% | 0% | 0 | 0.2799 | 2.2323 | 2.4872 | 1.5541 | Medium | Low | High | 296 | 323 | 0.62484
SMARTVILLE-NICOLAUS #1 - 60 kV | ETL.7990 | SIERRA | 99 | 0 | 0 | 3.191% | 81.91% | 0% | 0 | 39.61% | 10.53% | 1 | 0.45049 | 1.8155 | 1.8264 | 1.4938 | High | Low | Medium | 297 | 311 | 0.81788
STANISLAUS-NEWARK #1 (12KV)-115 kV | ETL.3850 | MISSION | 43 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.076546 | 9.1224 | 2.0433 | 1.4268 | Low | Medium | Medium | 298 | 317 | 0.69828
MALIN-ROUND MTN #2 - 500 kV | ETL.6020 | NORTH VALLEY | 302 | 0 | 1 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.93064 | 4.7226 | 0.32103 | 1.4109 | High | Medium | Low | 299 | 168 | 4.395
SMARTVILLE-NICOLAUS #2 - 60 kV | ETL.8000 | SIERRA | 95 | 0 | 0 | 2.105% | 83.16% | 0% | 0 | 89.13% | 91.58% | 1 | 0.76869 | 1 | 1.8274 | 1.4047 | High | Low | Medium | 300 | 316 | 0.76869
NORTH TOWER-MARTINEZ JCT #1 (21KV)-115 kV | ETL.3130 | EAST BAY | 12 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.070471 | 7.8135 | 2.522 | 1.3887 | Low | Medium | High | 301 | 330 | 0.55063
OCEANO-CALLENDER SW STA-115 kV | ETL.2394 | LOS PADRES | 50 | 0 | 0 | 9.302% | 32.56% | 0% | 0 | 0% | 0% | 0 | 0.12249 | 5.3295 | 2.0624 | 1.3464 | Medium | Medium | Medium | 302 | 319 | 0.65283
GEYSERS #11-EAGLE ROCK - 115 kV | ETL.4391 | SONOMA | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.061672 | 12.6592 | 1.719 | 1.342 | Low | Medium | Medium | 303 | 315 | 0.78072
JEFFERSON-LAS PULGAS - 60 kV | ETL.7200 | PENINSULA | 6 | 0 | 0 | 0% | 100% | 0% | 0 | 0% | 0% | 0 | 0.35719 | 1 | 3.6666 | 1.3097 | Medium | Low | High | 304 | 348 | 0.35719
SPI (BURNEY) TAP - 230 kV | ETL.5392 | NORTH VALLEY | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 14.9507 | 1.4639 | 1.2835 | Low | Medium | Low | 305 | 303 | 0.87679
BELL-PLACER - 115 kV | ETL.4395 | SIERRA | 21 | 0 | 0 | 0% | 0% | 0% | 2.89 | 57.57% | 100% | 0 | 0.15037 | 3.6855 | 2.2704 | 1.2582 | Medium | Medium | High | 306 | 329 | 0.55417
GEYSERS #13 TAP - 230 kV | ETL.4781 | HUMBOLDT | 11 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.069311 | 11.8328 | 1.4729 | 1.208 | Low | Medium | Low | 307 | 310 | 0.82014
DELTA-MTN GATE JCT - 60 kV | ETL.6750 | NORTH VALLEY | 191 | 0 | 0 | 3.158% | 34.74% | 0% | 0 | 99.21% | 9.474% | 1 | 0.91983 | 1 | 1.2525 | 1.1521 | High | Low | Low | 308 | 301 | 0.91983
EL DORADO-MISSOURI FLAT #2-115 kV | ETL.1540 | SIERRA | 21 | 0 | 0 | 4.762% | 33.33% | 0% | 8.7 | 53.84% | 52.38% | 1 | 0.24471 | 2.6346 | 1.7022 | 1.0974 | Medium | Low | Medium | 309 | 322 | 0.64472
MENDOCINO #1 - 60 kV | ETL.7530 | HUMBOLDT | 53 | 0 | 0 | 3.774% | 62.26% | 0% | 3.15 | 71.56% | 5.66% | 0 | 0.348 | 2.9465 | 1.062 | 1.0889 | Medium | Low | Low | 310 | 290 | 1.0254
IGNACIO-ALTO-SAUSALITO #1 - 60 kV | ETL.7160 | NORTH BAY | 41 | 0 | 0 | 0% | 0% | 0% | 0 | 9.188% | 81.25% | 0 | 0.098061 | 3.9148 | 2.6865 | 1.0313 | Low | Medium | High | 311 | 346 | 0.38389
DIABLO-MESA - 230 kV | ETL.4620 | LOS PADRES | 46 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.11833 | 3.4238 | 2.507 | 1.0157 | Medium | Medium | High | 312 | 344 | 0.40514
PORT COSTA BRICK TAP - 60 kV | ETL.6371 | DIABLO | 31 | 0 | 0 | 0% | 9.677% | 3.226% | 1.49 | 100% | 3.226% | 0 | 0.42961 | 1 | 2.3115 | 0.99303 | High | Low | High | 313 | 339 | 0.42961
MOSS LANDING-LOS BANOS - 500 kV | ETL.6040 | CENTRAL COAST | 94 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.132 | 9.0027 | 0.8104 | 0.96305 | Medium | Medium | Low | 314 | 278 | 1.1884
SMARTVILLE-MARYSVILLE - 60 kV | ETL.7980 | SIERRA | 109 | 0 | 0 | 1.031% | 83.51% | 0% | 0 | 65.15% | 10.31% | 1 | 0.52297 | 1 | 1.7718 | 0.9266 | High | Low | Medium | 315 | 331 | 0.52297
FORKS OF THE BUTTE TAP - 60 kV | ETL.6722 | NORTH VALLEY | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.030161 | 11.463 | 2.6042 | 0.90038 | Low | Medium | High | 316 | 350 | 0.34574
WISHON-COPPERMINE - 70 kV | ETL.9330 | FRESNO | 108 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.28505 | 1.9756 | 1.5652 | 0.8814 | Medium | Low | Medium | 317 | 328 | 0.56314
FRENCH MEADOWS-MIDDLE FORK - 60 kV | ETL.6870 | SIERRA | 240 | 0 | 0 | 0% | 87.5% | 0% | 0 | 0% | 14.58% | 1 | 0.80761 | 1.5569 | 0.67927 | 0.85409 | High | Low | Low | 318 | 273 | 1.2574
TEJON-LEBEC - 70 kV | ETL.9250 | KERN | 97 | 1 | 0 | 11.49% | 58.62% | 0% | 0 | 0% | 18.39% | 0 | 0.40208 | 1 | 2.056 | 0.82666 | High | Low | Medium | 319 | 345 | 0.40208
SALMON CREEK TAP - 60 kV | ETL.6981 | SONOMA | 80 | 0 | 0 | 43.06% | 0% | 0% | 0 | 0% | 6.944% | 0 | 0.13171 | 3.1309 | 1.9979 | 0.82389 | Medium | Medium | Medium | 320 | 343 | 0.41237
GEYSERS #16 TAP - 230 kV | ETL.4760 | HUMBOLDT | 7 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.064845 | 7.6624 | 1.6396 | 0.81465 | Low | Medium | Medium | 321 | 334 | 0.49687
BOTTLE ROCK TAP D.W.R. - 230 kV | ETL.4771 | HUMBOLDT | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.063771 | 6.721 | 1.8892 | 0.80973 | Low | Medium | Medium | 322 | 340 | 0.42861
MIDWAY-WHIRLWIND - 500 kV | ETL.6030 | KERN | 38 | 2 | 7 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.2111 | 2.2333 | 1.6917 | 0.79756 | Medium | Low | Medium | 323 | 337 | 0.47145
MISSION POWER TAP-115 kV | ETL.1651 | SONOMA | 22 | 1 | 0 | 13.64% | 0% | 0% | 0 | 0% | 54.55% | 0 | 0.22227 | 2.9024 | 1.1636 | 0.75064 | Medium | Low | Low | 324 | 321 | 0.64512
IGNACIO-STAFFORD-60 kV | ETL.1042 | NORTH BAY | 20 | 0 | 0 | 30.77% | 46.15% | 0% | 0 | 0% | 0% | 0 | 0.087593 | 3.3581 | 2.5477 | 0.74938 | Low | Medium | High | 325 | 356 | 0.29414
BELDEN TAP - 230 kV | ETL.4441 | NORTH VALLEY | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 16.5456 | 0.73184 | 0.73437 | Low | Medium | Low | 326 | 295 | 1.0034
HAT CREEK #1-WESTWOOD - 60 kV | ETL.7030 | NORTH VALLEY | 1023 | 0 | 0 | 0.7752% | 89.04% | 0% | 0 | 100% | 2.993% | 1 | 1 | 1.0339 | 0.70458 | 0.7285 | High | Low | Low | 327 | 288 | 1.0339
LONE STAR TAP - 60 kV | ETL.6231 | CENTRAL COAST | 16 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.032884 | 8.2286 | 2.6652 | 0.72118 | Low | Medium | High | 328 | 364 | 0.27059
CHRISTIE-WILLOW PASS - 60 kV | ETL.6370 | DIABLO | 47 | 0 | 0 | 6.977% | 41.86% | 0% | 12.86 | 81.55% | 6.977% | 1 | 0.31965 | 1 | 2.1817 | 0.69739 | Medium | Low | High | 329 | 353 | 0.31965
DIVIDE-VANDENBERG #2 - 70 kV | ETL.8630 | LOS PADRES | 52 | 0 | 0 | 37.25% | 1.961% | 0% | 0 | 0% | 0% | 0 | 0.13869 | 1.9478 | 2.4969 | 0.67451 | Medium | Low | High | 330 | 365 | 0.27014
MOSS LANDING-DEL MONTE #1 - 115 kV | ETL.2830 | CENTRAL COAST | 53 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.11466 | 2.6032 | 2.2536 | 0.67267 | Low | Low | High | 331 | 355 | 0.29848
HELMS-GREGG #1 - 230 kV | ETL.4870 | FRESNO | 182 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.55546 | 1.2035 | 0.99638 | 0.66606 | High | Low | Low | 332 | 318 | 0.66848
PLUMAS-SIERRA TAP - 60 kV | ETL.6291 | NORTH VALLEY | 8 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.029134 | 11.2183 | 1.9892 | 0.65014 | Low | Medium | Medium | 333 | 352 | 0.32684
IONE TAP - 60 kV | ETL.8253 | STOCKTON | 53 | 0 | 0 | 0% | 56.82% | 0% | 0 | 0% | 4.545% | 0 | 0.10537 | 2.7598 | 2.2241 | 0.6468 | Low | Low | High | 334 | 357 | 0.29081
JEFFERSON-STANFORD - 60 kV | ETL.7220 | PENINSULA | 67 | 0 | 0 | 20.97% | 1.613% | 0% | 0 | 0% | 3.226% | 0 | 0.15176 | 1 | 4.0198 | 0.61007 | Medium | Low | High | 335 | 393 | 0.15176
ELK CREEK TAP - 60 kV | ETL.6921 | NORTH VALLEY | 61 | 0 | 0 | 0% | 53.33% | 0% | 0 | 0.835% | 3.333% | 1 | 0.077126 | 6.6027 | 1.157 | 0.58918 | Low | Medium | Low | 336 | 332 | 0.50924
EVERGREEN-ALMADEN - 60 kV | ETL.6830 | SAN JOSE | 8 | 0 | 0 | 0% | 100% | 0% | 0 | 0% | 0% | 0 | 0.3531 | 1 | 1.629 | 0.57521 | Medium | Low | Medium | 337 | 349 | 0.3531
BRIGHTON-CLAYTON #1-115 kV | ETL.1120 | DIABLO | 13 | 0 | 0 | 0% | 0% | 0% | 6.64 | 100% | 100% | 0 | 0.25929 | 1 | 2.2084 | 0.57261 | Medium | Low | High | 338 | 366 | 0.25929
OLEUM-NORTH TOWER-CHRISTIE - 115 kV | ETL.3180 | DIABLO | 30 | 0 | 0 | 0% | 0% | 0% | 1.48 | 67.31% | 93.33% | 1 | 0.22195 | 1 | 2.482 | 0.55087 | Medium | Low | High | 339 | 376 | 0.22195
CHRISTIE-FRANKLIN #2 - 60 kV | ETL.6360 | EAST BAY | 22 | 0 | 0 | 4.545% | 13.64% | 50% | 0 | 0% | 4.545% | 0 | 0.19878 | 1 | 2.541 | 0.5051 | Medium | Low | High | 340 | 379 | 0.19878
MONTICELLO PH TAP - 115 kV | ETL.1602 | SACRAMENTO | 16 | 0 | 0 | 0% | 18.75% | 0% | 0 | 0% | 26.32% | 0 | 0.088685 | 8.9217 | 0.63341 | 0.50117 | Low | Medium | Low | 341 | 314 | 0.79122
TABLE MTN-PALERMO - 230 kV | ETL.5690 | NORTH VALLEY | 43 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 97.37% | 0 | 0.10573 | 1.6725 | 2.7651 | 0.48895 | Low | Low | High | 342 | 382 | 0.17683
HAT CREEK #1-PIT #1 - 60 kV | ETL.7020 | NORTH VALLEY | 89 | 0 | 0 | 0% | 49.44% | 0% | 5.86 | 96.95% | 34.83% | 1 | 0.57724 | 1 | 0.80722 | 0.46596 | High | Low | Low | 343 | 325 | 0.57724
FROGTOWN #1 TAP - 115 kV | ETL.3831 | STOCKTON | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 100% | 0 | 0.22968 | 1 | 2.0276 | 0.46569 | Medium | Low | Medium | 344 | 371 | 0.22968
NARROWS #2 TAP-60 kV | ETL.6521 | SIERRA | 48 | 0 | 0 | 0% | 39.58% | 0% | 0 | 0% | 6.25% | 0 | 0.11357 | 1.9771 | 2.059 | 0.46233 | Low | Low | Medium | 345 | 375 | 0.22455
MERCED FALLS-EXCHEQUER - 70 kV | ETL.8990 | YOSEMITE | 30 | 0 | 0 | 0% | 0% | 0% | 0 | 93.98% | 100% | 1 | 0.29771 | 1.393 | 1.0875 | 0.45101 | Medium | Low | Low | 346 | 342 | 0.41472
PIT #5-ROUND MTN #2 - 230 kV | ETL.5430 | NORTH VALLEY | 134 | 0 | 0 | 1.493% | 1.493% | 0% | 0 | 0% | 41.04% | 0 | 0.44052 | 1.9709 | 0.51681 | 0.44871 | High | Low | Low | 347 | 305 | 0.86823
SURF TAP - 115 kV | ETL.1381 | LOS PADRES | 35 | 1 | 0 | 0% | 68.75% | 0% | 0 | 0% | 6.25% | 0 | 0.16981 | 1 | 2.4883 | 0.42254 | Medium | Low | High | 348 | 384 | 0.16981
PITTSBURG-TESLA #1 - 230 kV | ETL.5510 | DIABLO | 77 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.18651 | 1 | 2.2232 | 0.41465 | Medium | Low | High | 349 | 380 | 0.18651
IGNACIO-ALTO - 60 kV | ETL.7150 | NORTH BAY | 38 | 0 | 0 | 4.545% | 50% | 0% | 0 | 1.34% | 4.545% | 0 | 0.13169 | 1 | 3.0733 | 0.40472 | Medium | Low | High | 350 | 399 | 0.13169
KANAKA TAP-115 kV | ETL.4223 | NORTH VALLEY | 33 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 36.36% | 0 | 0.064113 | 4.252 | 1.4609 | 0.39826 | Low | Medium | Low | 351 | 363 | 0.27261
CHRISTIE-FRANKLIN #1 - 60 kV | ETL.6350 | EAST BAY | 25 | 0 | 0 | 8.696% | 17.39% | 39.13% | 0 | 0% | 0% | 0 | 0.15486 | 1 | 2.5427 | 0.39376 | Medium | Low | High | 352 | 392 | 0.15486
MONTA VISTA-LOS GATOS - 60 kV | ETL.7610 | DE ANZA | 39 | 0 | 0 | 2.857% | 77.14% | 0% | 0 | 0% | 0% | 1 | 0.12447 | 1 | 3.0933 | 0.38504 | Medium | Low | High | 353 | 404 | 0.12447
GEYSERS #18 TAP - 230 kV | ETL.4784 | SONOMA | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.061672 | 4.4877 | 1.363 | 0.37723 | Low | Medium | Low | 354 | 361 | 0.27677
CHOWCHILLA-KERCKHOFF - 115 kV | ETL.1250 | YOSEMITE | 120 | 0 | 0 | 3.093% | 54.64% | 0% | 0 | 0% | 36.08% | 1 | 0.2816 | 1 | 1.2617 | 0.35529 | Medium | Low | Low | 355 | 359 | 0.2816
IGNACIO-SAN RAFAEL #3 - 115 kV | ETL.1860 | NORTH BAY | 10 | 0 | 0 | 0% | 50% | 0% | 0 | 0% | 0% | 0 | 0.11436 | 1 | 3.038 | 0.34744 | Low | Low | High | 356 | 407 | 0.11436
CASTAIC TAP - 70 kV | ETL.9253 | KERN | 1 | 0 | 0 | 100% | 0% | 0% | 0 | 0% | 0% | 0 | 0.16658 | 1 | 2.0854 | 0.34739 | Medium | Low | Medium | 357 | 385 | 0.16658
BUCKS CREEK-ROCK CREEK-CRESTA - 230 kV | ETL.4430 | NORTH VALLEY | 85 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.21814 | 1.2843 | 1.2165 | 0.34081 | Medium | Low | Low | 358 | 360 | 0.28017
BEALE AFB (WAPA) #1 TAP - 60 kV | ETL.8001 | SIERRA | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 100% | 0 | 0.22968 | 1 | 1.4333 | 0.3292 | Medium | Low | Low | 359 | 371 | 0.22968
DINOSAUR POINT TAP-70 kV | ETL.8961 | CENTRAL COAST | 13 | 0 | 0 | 18.18% | 27.27% | 0% | 0 | 65.69% | 0% | 0 | 0.24807 | 1 | 1.2955 | 0.32137 | Medium | Low | Low | 360 | 369 | 0.24807
WINTU TAP-60 kV | ETL.6311 | NORTH VALLEY | 13 | 0 | 0 | 27.27% | 45.45% | 0% | 0 | 0% | 0% | 0 | 0.14999 | 1 | 2.0875 | 0.31309 | Medium | Low | Medium | 361 | 394 | 0.14999
PITTSBURG-COLUMBIA STEEL - 115 kV | ETL.3300 | DIABLO | 9 | 1 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.13966 | 1 | 2.1957 | 0.30666 | Medium | Low | High | 362 | 398 | 0.13966
CRUSHER TAP - 60 kV | ETL.6241 | CENTRAL COAST | 25 | 0 | 0 | 8% | 8% | 0% | 0 | 0% | 4% | 0 | 0.10917 | 1 | 2.7507 | 0.30028 | Low | Low | High | 363 | 408 | 0.10917
CONTRA COSTA-LAS POSITAS - 230 kV | ETL.4510 | MISSION | 66 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.14924 | 1 | 1.9509 | 0.29114 | Medium | Low | Medium | 364 | 395 | 0.14924
PITTSBURG-MARTINEZ #1 - 115 kV | ETL.3320 | DIABLO | 7 | 1 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.1313 | 1 | 2.2121 | 0.29045 | Medium | Low | High | 365 | 401 | 0.1313
BRIONES TAP - 60 kV | ETL.7055 | DIABLO | 91 | 0 | 0 | 0% | 80.56% | 0% | 0 | 0% | 0% | 0 | 0.14549 | 1 | 1.9905 | 0.2896 | Medium | Low | Medium | 366 | 396 | 0.14549
TESLA-SALADO-MANTECA - 115 kV | ETL.4000 | YOSEMITE | 44 | 0 | 0 | 0% | 21.05% | 10.53% | 0 | 18.28% | 0% | 0 | 0.22462 | 1 | 1.2632 | 0.28375 | Medium | Low | Low | 367 | 374 | 0.22462
COLEMAN-COTTONWOOD - 60 kV | ETL.6430 | NORTH VALLEY | 37 | 0 | 0 | 0% | 74.07% | 0% | 0 | 0% | 3.704% | 0 | 0.07954 | 2.0334 | 1.6429 | 0.26572 | Low | Low | Medium | 368 | 386 | 0.16174
ARCO-POLONIO PASS PP - 70 kV | ETL.8450 | KERN | 129 | 2 | 0 | 1.653% | 84.3% | 0% | 0 | 0% | 2.479% | 0 | 0.57257 | 1 | 0.45771 | 0.26207 | High | Low | Low | 369 | 326 | 0.57257
IGNACIO-SAN RAFAEL #1 - 115 kV | ETL.1850 | NORTH BAY | 23 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.075294 | 1 | 3.3963 | 0.25572 | Low | Low | High | 370 | 420 | 0.075294
BEALE AFB (WAPA) #2 TAP - 60 kV | ETL.7971 | SIERRA | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 100% | 50% | 0 | 0.17272 | 1 | 1.4324 | 0.2474 | Medium | Low | Low | 371 | 383 | 0.17272
PIT #5-ROUND MTN #1 - 230 kV | ETL.5420 | NORTH VALLEY | 131 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 41.22% | 0 | 0.29001 | 1.603 | 0.52519 | 0.24415 | Medium | Low | Low | 372 | 338 | 0.46488
PIT #3-CARBERRY SW STA - 230 kV | ETL.5450 | NORTH VALLEY | 82 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.18381 | 1.14 | 1.1176 | 0.23419 | Medium | Low | Low | 373 | 377 | 0.20954
FORT SEWARD TAP - 60 kV | ETL.6222 | HUMBOLDT | 58 | 0 | 0 | 0% | 12.5% | 0% | 0 | 0% | 12.5% | 0 | 0.078687 | 3.4952 | 0.84794 | 0.23321 | Low | Medium | Low | 374 | 362 | 0.27503
TULLOCH TAP - 115 kV | ETL.1071 | STOCKTON | 5 | 0 | 0 | 0% | 66.67% | 0% | 0 | 0% | 0% | 0 | 0.11618 | 1 | 1.8639 | 0.21656 | Low | Low | Medium | 375 | 405 | 0.11618
JEFFERSON-HILLSDALE JCT - 60 kV | ETL.7190 | PENINSULA | 28 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 77.78% | 0 | 0.06669 | 1 | 3.1931 | 0.21295 | Low | Low | High | 376 | 434 | 0.06669
UNION CHEMICAL TAP - 60 kV | ETL.6351 | EAST BAY | 11 | 0 | 0 | 0% | 75% | 0% | 0 | 0% | 0% | 0 | 0.08119 | 1 | 2.573 | 0.2089 | Low | Low | High | 377 | 415 | 0.08119
TESLA-LOS BANOS #1 - 500 kV | ETL.6100 | YOSEMITE | 18 | 5 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.16011 | 1 | 1.2754 | 0.20419 | Medium | Low | Low | 378 | 388 | 0.16011
TRACY-LOS BANOS - 500 kV | ETL.6130 | YOSEMITE | 16 | 10 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15772 | 1 | 1.2703 | 0.20034 | Medium | Low | Low | 379 | 390 | 0.15772
OXBOW TAP - 60 kV | ETL.7561 | SIERRA | 3 | 0 | 0 | 0% | 33.33% | 0% | 0 | 0% | 0% | 0 | 0.11618 | 1 | 1.7161 | 0.19938 | Low | Low | Medium | 380 | 405 | 0.11618
FIBREBOARD STANDARD TAP - 115 kV | ETL.1404 | YOSEMITE | 3 | 0 | 0 | 66.67% | 0% | 0% | 0 | 0% | 0% | 0 | 0.073687 | 1 | 2.6129 | 0.19254 | Low | Low | High | 381 | 423 | 0.073687
BUTTE VALLEY-CARIBOU-115 kV | ETL.1180 | NORTH VALLEY | 65 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 93.75% | 1 | 0.15471 | 1.1597 | 1.0396 | 0.18651 | Medium | Low | Low | 382 | 381 | 0.17941
PITTSBURG-CLAYTON #1 - 115 kV | ETL.3280 | DIABLO | 20 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.079108 | 1 | 2.3268 | 0.18406 | Low | Low | High | 383 | 416 | 0.079108
BEARDSLEY TAP - 115 kV | ETL.1401 | YOSEMITE | 38 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 16.67% | 0 | 0.058707 | 2.4196 | 1.2908 | 0.18336 | Low | Low | Low | 384 | 397 | 0.14205
PITTSBURG-CLAYTON #3 - 115 kV | ETL.3290 | DIABLO | 16 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.075294 | 1 | 2.3404 | 0.17622 | Low | Low | High | 385 | 420 | 0.075294
SAN MATEO-HILLSDALE JCT - 60 kV | ETL.7950 | PENINSULA | 18 | 0 | 0 | 35.71% | 0% | 0% | 0 | 0% | 7.143% | 0 | 0.069099 | 1 | 2.4707 | 0.17073 | Low | Low | High | 386 | 430 | 0.069099
TOCALOMA TAP - 60 kV | ETL.7721 | NORTH BAY | 10 | 0 | 0 | 0% | 30% | 0% | 0 | 0% | 0% | 0 | 0.066994 | 1 | 2.5224 | 0.16899 | Low | Low | High | 387 | 433 | 0.066994
HELMS-GREGG #2 - 230 kV | ETL.4880 | FRESNO | 104 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.25347 | 1 | 0.64108 | 0.16249 | Medium | Low | Low | 388 | 367 | 0.25347
NEWARK-LAWRENCE LAB - 115 kV | ETL.3060 | MISSION | 1 | 0 | 0 | 0% | 0% | 0% | 64486.08 | 100% | 100% | 0 | 0.07622 | 1 | 2.1299 | 0.16234 | Low | Low | Medium | 389 | 419 | 0.07622
GRIZZLY TAP - 115 kV | ETL.2395 | NORTH VALLEY | 28 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.077912 | 23.3943 | 0.088896 | 0.16203 | Low | High | Low | 390 | 243 | 1.8227
ARCO-CHOLAME - 70 kV | ETL.8440 | KERN | 82 | 12 | 0 | 4.255% | 63.83% | 0% | 23.2 | 0% | 8.511% | 1 | 0.35869 | 1 | 0.45011 | 0.16145 | Medium | Low | Low | 391 | 347 | 0.35869
PITTSBURG-EASTSHORE - 230 kV | ETL.5462 | DIABLO | 13 | 0 | 1 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.071649 | 1 | 2.249 | 0.16114 | Low | Low | High | 392 | 425 | 0.071649
MUSTANG TAP - 70 kV | ETL.9091 | LOS PADRES | 9 | 0 | 0 | 66.67% | 0% | 0% | 0 | 0% | 0% | 0 | 0.081339 | 1 | 1.9588 | 0.15932 | Low | Low | Medium | 393 | 414 | 0.081339
MTN GATE TAP - 60 kV | ETL.7641 | NORTH VALLEY | 11 | 0 | 0 | 0% | 72.73% | 0% | 0 | 0% | 0% | 0 | 0.085275 | 1 | 1.8682 | 0.15931 | Low | Low | Medium | 394 | 411 | 0.085275
DIABLO UNIT #2 - 500 kV | ETL.5950 | LOS PADRES | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.063771 | 1 | 2.4808 | 0.1582 | Low | Low | High | 395 | 439 | 0.063771
DIABLO UNIT #1 - 500 kV | ETL.5940 | LOS PADRES | 5 | 0 | 1 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.062713 | 1 | 2.4859 | 0.1559 | Low | Low | High | 396 | 442 | 0.062713
MILLBRAE-SNEATH LANE - 60 kV | ETL.7570 | PENINSULA | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 4.846% | 100% | 0 | 0.067324 | 1 | 2.3087 | 0.15543 | Low | Low | High | 397 | 431 | 0.067324
PIT #6 JCT-ROUND MTN - 230 kV | ETL.5440 | NORTH VALLEY | 80 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 38.75% | 0 | 0.13894 | 1.6386 | 0.67814 | 0.1544 | Medium | Low | Low | 398 | 373 | 0.22767
GEYSERS #5-GEYSERS #3 - 115 kV | ETL.1670 | SONOMA | 9 | 0 | 0 | 22.22% | 22.22% | 0% | 0 | 0% | 0% | 0 | 0.10219 | 1 | 1.4634 | 0.14954 | Low | Low | Low | 399 | 409 | 0.10219
BUELLTON TAP - 115 kV | ETL.1201 | LOS PADRES | 28 | 0 | 0 | 4% | 56% | 0% | 0 | 0% | 0% | 0 | 0.13152 | 1 | 1.13 | 0.14862 | Medium | Low | Low | 400 | 400 | 0.13152
DIABLO PP STANDBY SUPPLY - 230 kV | ETL.4610 | LOS PADRES | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 1 | 2.484 | 0.14814 | Low | Low | High | 401 | 449 | 0.059639
MONTA VISTA-SARATOGA - 230 kV | ETL.5240 | DE ANZA | 5 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 1 | 2.4828 | 0.14807 | Low | Low | High | 402 | 449 | 0.059639
JEFFERSON-MARTIN - 230 kV | ETL.5710 | PENINSULA | 13 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.065935 | 1 | 2.2286 | 0.14694 | Low | Low | High | 403 | 435 | 0.065935
GRAPEVINE TAP - 70 kV | ETL.9252 | KERN | 3 | 0 | 0 | 33.33% | 0% | 0% | 0 | 0% | 0% | 0 | 0.073687 | 1 | 1.9596 | 0.1444 | Low | Low | Medium | 404 | 423 | 0.073687
SILVERADO-FULTON JCT - 115 kV | ETL.1610 | NORTH BAY | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 99.73% | 0% | 1 | 0.12512 | 1 | 1.1339 | 0.14188 | Medium | Low | Low | 405 | 403 | 0.12512
MARTIN-SNEATH LANE - 60 kV | ETL.7210 | PENINSULA | 8 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 1 | 2.322 | 0.14082 | Low | Low | High | 406 | 443 | 0.060648
MELONES-WILSON - 230 kV | ETL.5080 | YOSEMITE | 28 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.084467 | 1 | 1.6558 | 0.13986 | Low | Low | Medium | 407 | 412 | 0.084467
JEFFERSON #1 - 60 kV | ETL.6831 | PENINSULA | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 33.33% | 0 | 0.037725 | 1 | 3.6885 | 0.13915 | Low | Low | High | 408 | 466 | 0.037725
PITTSBURG-TASSAJARA - 230 kV | ETL.5470 | DIABLO | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 1 | 2.2494 | 0.13642 | Low | Low | High | 409 | 443 | 0.060648
CONTRA COSTA-MORAGA #2 - 230 kV | ETL.5453 | DIABLO | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 1 | 2.2504 | 0.13421 | Low | Low | High | 410 | 449 | 0.059639
US WINDPOWER #3 TAP - 230 kV | ETL.4521 | MISSION | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 1 | 2.2728 | 0.13329 | Low | Low | High | 411 | 455 | 0.058646
PITTSBURG-CLAYTON #4 - 115 kV | ETL.3291 | DIABLO | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 1 | 2.2207 | 0.13023 | Low | Low | High | 412 | 455 | 0.058646
CRYSTAL SPRINGS TAP-60 kV | ETL.7211 | PENINSULA | 5 | 0 | 0 | 20% | 0% | 0% | 0 | 0% | 20% | 0 | 0.056012 | 1 | 2.2732 | 0.12733 | Low | Low | High | 413 | 461 | 0.056012
LONE TREE-CAYETANO - 230 kV | ETL.6160 | MISSION | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 1 | 2.0663 | 0.12532 | Low | Low | Medium | 414 | 443 | 0.060648
MCSWAIN TAP - 70 kV | ETL.8991 | YOSEMITE | 13 | 0 | 0 | 0% | 62.5% | 0% | 0 | 0% | 0% | 0 | 0.12567 | 1 | 0.94815 | 0.11915 | Medium | Low | Low | 415 | 402 | 0.12567
MONTA VISTA-PERMANENTE - 60 kV | ETL.7620 | DE ANZA | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 1 | 2.0112 | 0.11795 | Low | Low | Medium | 416 | 455 | 0.058646
KERCKHOFF #1-KERCKHOFF #2 - 115 kV | ETL.1880 | FRESNO | 13 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.071649 | 1 | 1.6245 | 0.1164 | Low | Low | Medium | 417 | 425 | 0.071649
JESSUP TAP - 115 kV | ETL.4041 | NORTH VALLEY | 9 | 0 | 0 | 0% | 22.22% | 0% | 0 | 0% | 22.22% | 0 | 0.067151 | 1 | 1.7222 | 0.11564 | Low | Low | Medium | 418 | 432 | 0.067151
PIT #1-MCARTHUR | ETL.7790 | NORTH VALLEY | 44 | 0 | 0 | 6.977% | 62.79% | 0% | 0 | 0% | 41.86% | 1 | 0.16033 | 1 | 0.70971 | 0.11379 | Medium | Low | Low | 419 | 387 | 0.16033
GEYSERS #17-FULTON - 230 kV | ETL.4770 | SONOMA | 8 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.065935 | 1 | 1.7045 | 0.11239 | Low | Low | Medium | 420 | 435 | 0.065935
BRUNSWICK #2 TAP - 115 kV | ETL.1431 | SIERRA | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 1 | 1.8401 | 0.10791 | Low | Low | Medium | 421 | 455 | 0.058646
COTTLE-MELONES - 230 kV | ETL.4530 | STOCKTON | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 1 | 1.6592 | 0.097305 | Low | Low | Medium | 422 | 455 | 0.058646
SANTA FE GEOTHERMAL TAP - 230 kV | ETL.4782 | SONOMA | 8 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.065935 | 1 | 1.4721 | 0.097064 | Low | Low | Low | 423 | 435 | 0.065935
MESA-SISQUOC - 115 kV | ETL.2460 | LOS PADRES | 21 | 0 | 0 | 0% | 44.44% | 0% | 0 | 0% | 11.11% | 0 | 0.082574 | 1 | 1.1534 | 0.095243 | Low | Low | Low | 424 | 413 | 0.082574
GEYSERS #3-EAGLE ROCK - 115 kV | ETL.1660 | SONOMA | 20 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 65% | 0 | 0.063056 | 1 | 1.4649 | 0.092369 | Low | Low | Low | 425 | 441 | 0.063056
TESLA-SALADO #1 - 115 kV | ETL.3990 | YOSEMITE | 12 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.070471 | 1 | 1.2655 | 0.089179 | Low | Low | Low | 426 | 427 | 0.070471
QUINTO SW STA-WESTLEY - 230 kV | ETL.5070 | YOSEMITE | 12 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.070471 | 1 | 1.2646 | 0.089119 | Low | Low | Low | 427 | 427 | 0.070471
GEYSERS #7-EAGLE ROCK - 115 kV | ETL.1680 | SONOMA | 16 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 56.25% | 0 | 0.055437 | 1 | 1.5297 | 0.084803 | Low | Low | Medium | 428 | 462 | 0.055437
YANKE (NORTH FORK) TAP-70 kV | ETL.9341 | YOSEMITE | 8 | 0 | 0 | 0% | 12.5% | 0% | 0 | 0% | 0% | 0 | 0.064797 | 1 | 1.1743 | 0.07609 | Low | Low | Low | 429 | 438 | 0.064797
SAN BRUNO TAP - 60 kV | ETL.7572 | PENINSULA | 13 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.031223 | 1 | 2.335 | 0.072905 | Low | Low | High | 430 | 468 | 0.031223
SPRING GAP TAP - 115 kV | ETL.1402 | YOSEMITE | 21 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 14.29% | 0 | 0.044777 | 1 | 1.5822 | 0.070848 | Low | Low | Medium | 431 | 464 | 0.044777
MESA-SANTA MARIA - 115 kV | ETL.2450 | LOS PADRES | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 1 | 1.1658 | 0.06953 | Low | Low | Low | 432 | 449 | 0.059639
LUCERNE #2 TAP - 115 kV | ETL.2411 | HUMBOLDT | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 50% | 0 | 0.041802 | 1 | 1.6445 | 0.068743 | Low | Low | Medium | 433 | 465 | 0.041802
PERMANENTE #2 TAP - 60 kV | ETL.7622 | DE ANZA | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.030161 | 1 | 2.007 | 0.060533 | Low | Low | Medium | 434 | 469 | 0.030161
SMARTVILLE TAP - 60 kV | ETL.6522 | SIERRA | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.028634 | 1 | 2.0448 | 0.05855 | Low | Low | Medium | 435 | 473 | 0.028634
PERMANENTE #1 TAP - 60 kV | ETL.7621 | DE ANZA | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.028634 | 1 | 2.0089 | 0.057521 | Low | Low | Medium | 436 | 473 | 0.028634
COLLINS PINE TAP | ETL.7001 | NORTH VALLEY | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.029134 | 1 | 1.9662 | 0.057285 | Low | Low | Medium | 437 | 471 | 0.029134
MORRO BAY-GATES #2 - 230 kV | ETL.5280 | LOS PADRES | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.058646 | 1 | 0.87602 | 0.051375 | Low | Low | Low | 438 | 455 | 0.058646
LUCERNE #1 TAP - 115 kV | ETL.1331 | HUMBOLDT | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.029643 | 1 | 1.6452 | 0.04877 | Low | Low | Medium | 439 | 470 | 0.029643
PIT #7 TAP - 230 kV | ETL.5442 | NORTH VALLEY | 34 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 55.88% | 0 | 0.074679 | 1 | 0.63028 | 0.047068 | Low | Low | Low | 440 | 422 | 0.074679
SANDBAR TAP - 115 kV | ETL.1403 | YOSEMITE | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.029134 | 1 | 1.5673 | 0.045661 | Low | Low | Medium | 441 | 471 | 0.029134
COBURN-OIL FIELDS #1 - 60 kV | ETL.6410 | CENTRAL COAST | 11 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.028634 | 1 | 1.3363 | 0.038263 | Low | Low | Low | 442 | 473 | 0.028634
MALACHA TAP - 230 kV | ETL.5910 | NORTH VALLEY | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 1 | 0.54048 | 0.032234 | Low | Low | Low | 443 | 449 | 0.059639
HUMBOLDT #1 - 60 kV | ETL.7113 | HUMBOLDT | 9 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.028634 | 1 | 0.83674 | 0.023959 | Low | Low | Low | 444 | 473 | 0.028634
JANES CREEK TAP - 60 kV | ETL.6805 | HUMBOLDT | 5 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.028634 | 1 | 0.83596 | 0.023937 | Low | Low | Low | 445 | 473 | 0.028634
PIT #4 TAP - 230 kV | ETL.5432 | NORTH VALLEY | 62 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.15616 | 1 | 0.083247 | 0.013 | Medium | Low | Low | 446 | 391 | 0.15616
PIT #6 TAP - 230 kV | ETL.5441 | NORTH VALLEY | 41 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 29.27% | 0 | 0.069709 | 4.0454 | 0.031412 | 0.0088581 | Low | Medium | Low | 447 | 358 | 0.282
BRENTWOOD-KELSO - 230 kV | ETL.4410 | DIABLO | 22 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.079108 | 1 | 0.077202 | 0.0061072 | Low | Low | Low | 448 | 416 | 0.079108
BLACK TAP - 230 kV | ETL.5431 | NORTH VALLEY | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 1 | 0.086236 | 0.00523 | Low | Low | Low | 449 | 443 | 0.060648
CLOVER CREEK TAP - 60 kV | ETL.7291 | NORTH VALLEY | 1 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 0% | 0 | 0.028634 | 1 | 0.018613 | 0.00053297 | Low | Low | Low | 450 | 473 | 0.028634
KINGS RIVER-SANGER-REEDLEY - 115 kV | ETL.2030 | FRESNO | 26 | 0 | 0 | 5% | 10% | 25% | 0 | 0% | 55% | 1 | 0.20768 | 7.2289 | 0 | 0 | Medium | Medium | Low | 451 | 261 | 1.5013
MIDWAY-SANTA MARIA-115 kV | ETL.9240 | LOS PADRES | 170 | 0 | 0 | 0% | 0% | 1.98% | 0 | 0% | 88.12% | 0 | 0.46596 | 9.0233 | 0 | 0 | High | Medium | Low | 451 | 175 | 4.2045
COBURN-PANOCHE - 230 kV | ETL.4460 | CENTRAL COAST | 81 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.17852 | 5.178 | 0 | 0 | Medium | Medium | Low | 451 | 299 | 0.92438
DELEVAN-VACA #2 - 230 kV | ETL.4231 | SACRAMENTO | 51 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.065935 | 14.0021 | 0 | 0 | Low | Medium | Low | 451 | 300 | 0.92324
COALINGA #1-SAN MIGUEL - 70 kV | ETL.8580 | LOS PADRES | 114 | 0 | 0 | 0% | 5.208% | 0% | 18.15 | 48.09% | 95.83% | 1 | 0.64888 | 1 | 0 | 0 | High | Low | Low | 451 | 320 | 0.64888
HAAS-MCCALL - 230 kV | ETL.4850 | FRESNO | 136 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.37542 | 1.3485 | 0 | 0 | Medium | Low | Low | 451 | 333 | 0.50624
BALCH-SANGER - 115 kV | ETL.1050 | FRESNO | 113 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 1 | 0.29608 | 1.1292 | 0 | 0 | Medium | Low | Low | 451 | 351 | 0.33433
TEMPLETON-GATES - 230 kV | ETL.5934 | LOS PADRES | 57 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.097748 | 1 | 0 | 0 | Low | Low | Low | 451 | 410 | 0.097748
TEMBLOR-SAN LUIS OBISPO - 115 kV | ETL.3960 | LOS PADRES | 185 | 0 | 0 | 0% | 0% | 0% | 0 | 99.7% | 100% | 1 | 0.83275 | 1 | 0 | 0 | High | Low | Low | 451 | 309 | 0.83275
CRAZY HORSE CANYON-SAN BENITO-115 kV | ETL.2152 | CENTRAL COAST | 21 | 2 | 0 | 0% | 0% | 0% | 0 | 86.25% | 100% | 0 | 0.4282 | 1 | 0 | 0 | High | Low | Low | 451 | 341 | 0.4282
COTTONWOOD #1 - 60 kV | ETL.6620 | NORTH VALLEY | 66 | 0 | 0 | 0% | 0% | 0% | 0 | 2.224% | 100% | 1 | 0.15841 | 1 | 0 | 0 | Medium | Low | Low | 451 | 389 | 0.15841
COPPERMINE-TIVY VALLEY - 70 kV | ETL.8590 | FRESNO | 116 | 0 | 0 | 15.38% | 30.77% | 0% | 0 | 0% | 23.08% | 1 | 0.12685 | 8.1495 | 0 | 0 | Medium | Medium | Low | 451 | 289 | 1.0338
SISQUOC-GAREY - 115 kV | ETL.3690 | LOS PADRES | 11 | 0 | 0 | 0% | 12.5% | 0% | 0 | 0% | 0% | 0 | 0.064797 | 7.3865 | 0 | 0 | Low | Medium | Low | 451 | 336 | 0.47862
VEDDER TAP - 115 kV | ETL.2141 | KERN | 54 | 0 | 0 | 11.32% | 62.26% | 0% | 44754.84 | 99.64% | 15.09% | 0 | 0.29985 | 1 | 0 | 0 | Medium | Low | Low | 451 | 354 | 0.29985
CORTINA #4 - 60 kV | ETL.6610 | SACRAMENTO | 16 | 0 | 0 | 0% | 75% | 0% | 0 | 45.48% | 25% | 1 | 0.24748 | 1 | 0 | 0 | Medium | Low | Low | 451 | 370 | 0.24748
HAAS-WOODCHUCK - 70 kV | ETL.8730 | FRESNO | 109 | 0 | 0 | 2.174% | 63.04% | 0% | 0 | 0% | 1.087% | 1 | 0.25231 | 1 | 0 | 0 | Medium | Low | Low | 451 | 368 | 0.25231
VACA-LAKEVILLE #1 - 230 kV | ETL.5840 | NORTH BAY | 97 | 0 | 1 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.20915 | 1 | 0 | 0 | Medium | Low | Low | 451 | 378 | 0.20915
GLENN #2-60 kV | ETL.6930 | NORTH VALLEY | 5 | 1 | 0 | 0% | 100% | 0% | 0 | 0% | 0% | 1 | 0.57849 | 1 | 0 | 0 | High | Low | Low | 451 | 324 | 0.57849
TULUCAY-VACA - 230 kV | ETL.5800 | SACRAMENTO | 2 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.059639 | 1 | 0 | 0 | Low | Low | Low | 451 | 449 | 0.059639
COVE ROAD TAP-230 kV | ETL.5421 | NORTH VALLEY | 6 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.063771 | 1 | 0 | 0 | Low | Low | Low | 451 | 439 | 0.063771
KM GREEN TAP-115 kV | ETL.3505 | STOCKTON | 3 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 1 | 0 | 0 | Low | Low | Low | 451 | 443 | 0.060648
GRIZZLY TAP (SVP) - 115 kV | ETL.1231 | NORTH VALLEY | 4 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 25% | 0 | 0.036142 | 1 | 0 | 0 | Low | Low | Low | 451 | 467 | 0.036142
OROVILLE-THERMALITO-TABLE MTN #1 (CDWR) - 230 kV | ETL.6621 | NORTH VALLEY | 33 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.079108 | 1 | 0 | 0 | Low | Low | Low | 451 | 416 | 0.079108
OROVILLE-THERMALITO-TABLE MTN #3 (CDWR) - 230 kV | ETL.6622 | NORTH VALLEY | 23 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.070471 | 1 | 0 | 0 | Low | Low | Low | 451 | 427 | 0.070471
PINE FLAT PH TAP (CDWR) - 230 kV | ETL.4821 | FRESNO | 5 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.060648 | 1 | 0 | 0 | Low | Low | Low | 451 | 443 | 0.060648
PITTSBURG-TESLA #2 - 230 kV | ETL.5520 | DIABLO | 11 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 45.45% | 0 | 0.047178 | 1 | -0.087351 | -0.0041211 | Low | Low | Low | 476 | 463 | 0.047178
SPAULDING #3-SPAULDING #1 - 60 kV | ETL.8050 | SIERRA | 27 | 0 | 0 | 0% | 59.26% | 0% | 0 | 100% | 0% | 1 | 0.49124 | 1 | -0.028496 | -0.013998 | High | Low | Low | 477 | 335 | 0.49124
CORTINA-VACA - 230 kV | ETL.4540 | SACRAMENTO | 56 | 0 | 0 | 0% | 0% | 0% | 0 | 0% | 100% | 0 | 0.070471 | 14.8543 | -2.0491 | -2.145 | Low | Medium | Low | 478 | 287 | 1.0468

## Notes
Notes
(1) Number of miles and number of circuits vary between EVM and SH / Inspection since circuits without trees tagged to them were considered out of scope for the prioritization
(2) Number of miles and number of circuits vary between Dx-SH and Dx-Inspection due to the methodologies used to arrive at the estimated miles. Whereas System Hardening was based upon protection zones with at least some area touching HFTD, Distribution Prioritization miles were based on the true miles within HFTD, potentially not including the entire circuit. This was done intentionally due to the operational nature of the work since it is difficult to complete system hardening intermittently on a line; whereas, it is less difficult to complete Distribution Prioritization intermittently
(3) Prioritization may vary during the implementation of the programs due to operational considerations (e.g. land and environment, safety, planned projects, geographic access, weather, government relations, production-related, and customer communications).
(4) Total miles for across protection zones in Dx-SH and Dx-Inspection is greater than the established 25,200 circuit miles in the HFTD. In the STAR dataset, which is the source of the conductor information, some segments are identified as either idle and proposed segments. These segments were included for analysis to allow futher analysis to be conducted for operational planning. Additionally, the STAR conductor dataset identified if a segment was located in Tier 2 or Tier 3. The analysis relied on this identification.
(5) Dx - EVM planned implementation: Not all portions of circuits highlighted for implementation in 2019 will be worked during 2019. Operational considerations limited work to certain portions of these selected circuits.