## Area 6 DD
Detailed Daily Drilldown |  | 2021-07-14
Auburn
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
6 | Auburn | CHAPMAN, KEVIN | Completed | 1 | OIS DSP | 2021-07-14 13:07 |  | 2021-07-14 13:07 | 44391.5501 | 44391.5672 | 44391.6042 | 77.97 | 24.67 | 12 | 12.67 | 53.3 | 30 | 23.3 | 16.6 | 36.7 | T005341752 | 1 | AD | 15300 MCELROY RD, MEADOW VISTA | 9030 | 9320 |  |  |  | AXS-AXS OK XSTR-MEADOW VISTA RD PWR-Y COMPLETE OUT - REPLACE BUSS AT TRANSFORMER , CONNECTORS AT SERVICE POLE ON 7/9/21 ANDNOW OUT OF POWER AGAIN SINCE 7/13 AFTERNOON. CUSTOMER REQ CALL IN ADVANCE |  | T1tkrc3. Power test ok with mega-beast. 118.6, 118.5 and 238.2 at meter socket. Found tripped/open breaker to trailer on customer side. Nobody present at time of tests. Breaker left in open position. SRF left at front door. PGE ok.
|  |  | Completed | 1 | OIS DSP | 2021-07-14 15:37 |  | 2021-07-14 15:37 | 44391.6937 | 44391.7228 | 44391.7472 | 77.14 | 41.87 | 12 | 29.87 | 35.27 | 44 | -8.73 | 16.6 | 18.67 | T005341926 | 1 | AD | 9492 TREELAKE RD, GRANITE BAY | 9130 | 9320 |  |  |  | AXS-DOG : GOLDEN RETRIEVER XSTR-SWAN LAKE PWR-Y ELECTRICIAN ADVISED TO CALLPGE FOR FLICKERING LIGHTS/ ROOMS : MASTER BED, AND KI TCHEN MOSTLY. |  | T1tkrc3. Power test ok with mega beast. Main breaker failed when opened to remove meter. Breaker would not reset. Breaker might be cause of customers flickering. Power ok. PGE ok.
|  |  | Completed | 2 | 4APKERA | 2021-07-14 20:31 |  | 2021-07-14 20:28 | 44391.8614 | 44391.8755 | 44391.8981 | 52.89 | 20.27 | 12 | 8.27 | 32.62 | 32 | 0.62 | 21.9 | 10.72 | 1130178131 | 0 | AD | 5630 SAUNDERS AVE, LOOMIS | 1120 | 1320 |  |  |  | FD ONS REQ ELECTRIC RESPOND, NO WIRE DOWN REQ ETA 530-886-5375 | ETA 2100 CHAPMAN | T1tkrc3. Responded to small fire at customers shed. Non PGE related. Checked power ok with mega beast and confirmed good voltage. Replaced preform tie to service. PGE ok.
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 13:11 |  | 2021-07-14 13:10 |  |  | 44391.5564 | [9 empty] | T005341759 | 0 | AD | UNKNOWN BETWEEN 1392-1398 ATHE, LINCOLN | 9250 |  |  |  |  | AXS-AXS OK WIRE DOWN, FIRE DEPT ON THE SCENE. POLE NEEDS TO BE INSPECTED
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 14:40 |  | 2021-07-14 14:40 |  |  | 44391.7883 | [9 empty] | T005341854 | 2 | AD | STRLIGHT 12160 MONT VISTA DR, AUBURN | 9500 |  |  |  |  | MONT VISTA CIRCLE & SIERRA VISTA CT
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 14:41 |  | 2021-07-14 14:40 |  |  | 44391.7884 | [9 empty] | T005341856 | 2 | AD | STRLIGHT PALOMINO CT & SOUTHRID, AUBURN | 9500 |  |  |  |  | SAP EQUIP ID #43968778; SWC PALOMINO CT & SOUTHRIDGE DR
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 14:41 |  | 2021-07-14 14:41 |  |  | 44391.7884 | [9 empty] | T005341857 | 2 | AD | STRLIGHT 5401 ALLEN DR, ROCKLIN | 9500
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Auburn | HART, EMMETT | Completed | 1 | OIS DSP | 2021-07-14 10:13 |  | 2021-07-14 10:12 | 44391.4333 | 44391.4878 | 44391.5814 | 213.28 | 78.43 | 12 | 66.43 | 134.85 | 52 | 82.85 | 0 | 134.85 | T005341545 | 1 | AD | 5101 SUNSET BLVD W #A, ROSEVILLE | 9150 | 9002 |  |  |  | AXS-ACCESS OK XSTR-FIDDYMENT PWR-Y COW PASTURE, PLEASE OPEN/CLOSE SAME GATE |  | refused ok, checked pwr ok.
|  |  | Completed | 1 | OIS DSP | 2021-07-14 11:34 |  | 2021-07-14 11:33 | 44391.5817 | 44391.6134 | 44391.6669 | 122.63 | 45.6 | 12 | 33.6 | 77.03 | 30 | 47.03 | 0 | 77.03 | T005341663 | 1 | AD | 180 OLD AIRPORT RD, AUBURN | 9030 | 9002 |  |  |  | A:LOCKED GATE / NO DOGS;X:BOWMAN RD;R:COMPLETE OUTAGE / LOCKED GATE PGE LOCK |  | This was Tx. level outage. refused Tx. ok, checked pwr ok. outage tx. cgc# 222698646572 has mtr#1009642947 , #1005408359 & unmtr. street light. Cgc#222694446535 is showing mtr#1005408359 incorrectly
|  |  | Completed | 2 | 4APKERA | 2021-07-14 16:33 |  | 2021-07-14 16:28 | 44391.7103 | 44391.7625 | 44391.83 | 172.41 | 75.13 | 12 | 63.13 | 97.28 | 31 | 66.28 | 33.3 | 63.98 | 1502228247 | 1 | AD | 4483 PACIFIC ST, ROCKLIN | 1240 | 1163 |  |  |  | Access/Safety: Locked Gate or Cabinet; LOW WIRE FROM POLE TO BUILDING UNSURE IF POWER LINE PLEASE CALL ELMO SIMPSON 916-768-6836 |  | Removed branchs from service line causeing strain, resagged service.
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 06:30 |  | 2021-07-14 06:30 |  |  | 44391.4264 | [9 empty] | T005341192 | 2 | AD | STRLIGHT 12160 MONT VISTA DR, AUBURN | 9500 |  |  |  |  | MONT VISTA CIRCLE & SIERRA VISTA CT
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 06:31 |  | 2021-07-14 06:30 |  |  | 44391.4266 | [9 empty] | T005341194 | 2 | AD | STRLIGHT PALOMINO CT & SOUTHRID, AUBURN | 9500 |  |  |  |  | SAP EQUIP ID #43968778; SWC PALOMINO CT & SOUTHRIDGE DR
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Auburn | ORCUTT, JEFF | Completed | 4 | 4APKERA | 2021-07-14 16:19 |  | 2021-06-28 14:51 | 44391.6985 | 44391.6986 | 44391.7005 | 2.88 | 0.05 | 12 | -11.95 | 2.83 | 25 | -22.17 | 20 | -17.17 | 6919565738 | 2 | AD | 2282 RANCH VIEW DR, ROCKLIN | 2094 | 2094 |  |  |  | CON/SET; INSP OK; LOT 27; SITE CNTC SCOTT BAKER 916-257-4216; SUBDV PROMINENCE; TRAVEL NORTH ON HWY. 65 EXIT WHITNEY RANCH PARKWAY LEFT RANCH VIEW DRIVE. |  | connect at splice box and set meter
|  |  | Completed | 4 | 4APKERA | 2021-07-14 16:19 |  | 2021-06-28 14:53 | 44391.7014 | 44391.7015 | 44391.7028 | 1.95 | 0.02 | 12 | -11.98 | 1.93 | 25 | -23.07 | 20 | -18.07 | 9676964564 | 2 | AD | 2280 RANCH VIEW DR, ROCKLIN | 2094 | 2094 |  |  |  | CON/SET; INSP OK; LOT 28; SITE CNTC SCOTT BAKER 916-257-4216; SUBDV PROMINENCE; TRAVEL NORTH ON HWY. 65 EXIT WHITNEY RANCH PARKWAY LEFT RANCH VIEW DRIVE. |  | connect at splice box and set meter
|  |  | Completed | 4 | 4APKERA | 2021-07-14 16:19 |  | 2021-06-28 14:55 | 44391.703 | 44391.703 | 44391.704 | 1.37 | 0.02 | 12 | -11.98 | 1.35 | 25 | -23.65 | 20 | -18.65 | 5504215116 | 2 | AD | 2278 RANCH VIEW DR, ROCKLIN | 2094 | 2094 |  |  |  | CON/SET; INSP OK; LOT 29; SITE CNTC SCOTT BAKER 916-257-4216; SUBDV PROMINENCE; TRAVEL NORTH ON HWY. 65 EXIT WHITNEY RANCH PARKWAY LEFT RANCH VIEW DRIVE. |  | connect at splice box and set meter
|  |  | Completed | 4 | 4APKERA | 2021-07-14 16:19 |  | 2021-06-28 14:57 | 44391.7042 | 44391.7042 | 44391.705 | 1.22 | 0.02 | 12 | -11.98 | 1.2 | 25 | -23.8 | 20 | -18.8 | 4788534874 | 2 | AD | 2276 RANCH VIEW DR, ROCKLIN | 2094 | 2094 |  |  |  | CON/SET; INSP OK; LOT 30; SITE CNTC SCOTT BAKER 916-257-4216; SUBDV PROMINENCE; TRAVEL NORTH ON HWY. 65 EXIT WHITNEY RANCH PARKWAY LEFT RANCH VIEW DRIVE. |  | connect at splice box and set meter
|  |  | Completed | 4 | 4APKERA | 2021-07-14 16:19 |  | 2021-06-28 14:59 | 44391.7053 | 44391.7053 | 44391.7067 | 2.1 | 0.02 | 12 | -11.98 | 2.08 | 25 | -22.92 | 20 | -17.92 | 3474879927 | 2 | AD | 2274 RANCH VIEW DR, ROCKLIN | 2094 | 2094 |  |  |  | CON/SET; INSP OK; LOT 31; SITE CNTC SCOTT BAKER 916-257-4216; SUBDV PROMINENCE; TRAVEL NORTH ON HWY. 65 EXIT WHITNEY RANCH PARKWAY LEFT RANCH VIEW DRIVE. |  | connect at splice box and set meter
|  |  | Completed | 4 | 4APKERA | 2021-07-14 16:19 |  | 2021-06-28 15:01 | 44391.7072 | 44391.7072 | 44391.7079 | 1 | 0.02 | 12 | -11.98 | 0.98 | 25 | -24.02 | 20 | -19.02 | 9552373218 | 2 | AD | 2272 RANCH VIEW DR, ROCKLIN | 2094 | 2094 |  |  |  | CON/SET; INSP OK; LOT 32; SITE CNTC SCOTT BAKER 916-257-4216; SUBDV PROMINENCE; TRAVEL NORTH ON HWY. 65 EXIT WHITNEY RANCH PARKWAY LEFT RANCH VIEW DRIVE. |  | connect at splice box and set meter
|  |  | Completed | 4 | 4APKERA | 2021-07-14 16:19 |  | 2021-06-28 15:03 | 44391.7081 | 44391.7081 | 44391.7089 | 1.12 | 0.02 | 12 | -11.98 | 1.1 | 25 | -23.9 | 20 | -18.9 | 6786458621 | 2 | AD | 2270 RANCH VIEW DR, ROCKLIN | 2094 | 2094 |  |  |  | CON/SET; INSP OK; LOT 33; SITE CNTC SCOTT BAKER 916-257-4216; SUBDV PROMINENCE; TRAVEL NORTH ON HWY. 65 EXIT WHITNEY RANCH PARKWAY LEFT RANCH VIEW DRIVE. |  | connect at splice box and set meter
|  |  | Completed | 4 | 4APKERA | 2021-07-14 16:19 |  | 2021-06-28 15:06 | 44391.7098 | 44391.7098 | 44391.7105 | 1.03 | 0 | 12 | -12 | 1.03 | 25 | -23.97 | 20 | -18.97 | 8990679698 | 2 | AD | 2268 RANCH VIEW DR, ROCKLIN | 2094 | 2094 |  |  |  | CON/SET; INSP OK; LOT 34; SITE CNTC SCOTT BAKER 916-257-4216; SUBDV PROMINENCE; TRAVEL NORTH ON HWY. 65 EXIT WHITNEY RANCH PARKWAY LEFT RANCH VIEW DRIVE. |  | connect at splice box and set meter
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Auburn | PASQUA, MARK | Completed | 1 | OIS DSP | 2021-07-14 08:08 |  | 2021-07-14 08:08 | 44391.3399 | 44391.3614 | 44391.4174 | 111.62 | 31 | 12 | 19 | 80.62 | 61 | 19.62 | 0 | 80.62 | T005341314 | 0 | AD | 5881 CHURCH ST, FORESTHILL | 9080 | 9002 |  |  |  | AXS-AXS K; XSTR- PWR-I PER ANN |  | t1tmjpg 1/3blwn@5911 squirrel contact@SSD6277 refuse4test,test good
|  |  | Completed | 1 | OIS DSP | 2021-07-14 10:02 |  | 2021-07-14 10:02 | 44391.4184 | 44391.447 | 44391.5575 | 200.3 | 41.15 | 12 | 29.15 | 159.15 | 61 | 98.15 | 0 | 159.15 | T005341529 | 0 | AD | 6725 CASA VISTA DR, LOOMIS | 9080 | 9002 |  |  |  | SMART MTR AUTO-GENERATED TAGCST STATES POSSIBLE TRANSFORMER BLOWN. |  | t1tmjpg,2/3blwn@5097 assist tag for tman mike refuse4test,test good
|  |  | Completed | 1 | OIS DSP | 2021-07-14 13:21 |  | 2021-07-14 13:21 | 44391.558 | 44391.5798 | 44391.6332 | 108.35 | 31.43 | 12 | 19.43 | 76.92 | 30 | 46.92 | 0 | 76.92 | T005341777 | 0 | AD | UNKNOWN BETWEEN 1392-1398 ATHE, LINCOLN | 9250 | 9002 |  |  |  | AXS-AXS OK WIRE DOWN, FIRE DEPT ON THE SCENE. POLE NEEDS TO BE INSPECTED |  | t1tmjpg,need to bolt on Xarms to temp repair cracked pole&ajust bird guard@second location e.c. tag made called for crew to make repairs
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 14:25 |  | 2021-07-14 14:16 | 44391.6496 | 44391.6496 | 44391.6654 | 22.75 | 0.02 | 12 | -11.98 | 22.73 | 26 | -3.27 | 22.6 | 0.13 | 6147577639 | 1 | AD | 2601 DYCE LN, LINCOLN | 1230 | 1056 |  |  |  | AXS OK; XST LAKESIDE; NEWLY BUILT HOME; CUSTOMER BELIEVES GROUNDING ISSUE; WHEN CHANGED A CLOCK ON OVEN IT WILL JUMP DIFFERENT TIME; MICROWAVE RUNS FASTER APPLIANCE SHUT OFF |  | t1tmjpg,good volts with beast 117/121 also checked conn.@s/b good
|  |  | Completed | 1 | OIS DSP | 2021-07-14 15:50 |  | 2021-07-14 15:49 | 44391.6656 | 44391.6722 | 44391.6793 | 19.72 | 9.6 | 12 | -2.4 | 10.12 | 30 | -19.88 | 16.6 | -6.48 | T005341934 | 0 | AD | 144 5TH ST, LINCOLN | 9250 | 9320 |  |  |  | AXS-AXS OK XSTR- PWR-Y WIRE DOWN UNSURE HOW WIRE WAS CONNECTED |  | t1tmjpg, line down is cable line
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:05 |  | 2021-06-22 13:54 | 44391.6795 | 44391.693 | 44391.8061 | 182.32 | 19.5 | 12 | 7.5 | 162.82 | 25 | 137.82 | 20 | 142.82 | 5088938261 | 2 | AD | 3104 LE BOURGET LN, LINCOLN | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 17; CONTACT: SCOTT HODGES 916-357-4079, SUBDIVISION: LAKESIDE #6 |  | t1tmjpg,conn.svc.&set mtr good volts@mtr jaw main is off
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:05 |  | 2021-06-22 13:52 | 44391.8066 | 44391.8067 | 44391.8086 | 2.85 | 0.08 | 12 | -11.92 | 2.77 | 25 | -22.23 | 20 | -17.23 | 1207939702 | 2 | AD | 3080 LE BOURGET LN, LINCOLN | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 15; CONTACT: SCOTT HODGES 916-357-4079, SUBDIVISION: LAKESIDE #6 |  | t1tmjpg,conn.svc.&set mtr good volts@mtr jaw main is off
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:05 |  | 2021-06-22 13:53 | 44391.809 | 44391.809 | 44391.8107 | 2.56 | 0.03 | 12 | -11.97 | 2.53 | 25 | -22.47 | 20 | -17.47 | 0143365737 | 2 | AD | 3092 LE BOURGET LN, LINCOLN | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 16; CONTACT: SCOTT HODGES 916-357-4079, SUBDIVISION: LAKESIDE #6 |  | t1tmjpg,conn.svc.&set mtr good volts@mtr jaw main is off
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:05 |  | 2021-06-22 14:20 | 44391.8109 | 44391.811 | 44391.8139 | 4.25 | 0.02 | 12 | -11.98 | 4.23 | 25 | -20.77 | 20 | -15.77 | 6484365083 | 2 | AD | 3116 LE BOURGET LN, LINCOLN | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 18; CONTACT: SCOTT HODGES 916-357-4079, SUBDIVISION: LAKESIDE #6 |  | t1tmjpg,conn.svc.&set mtr good volts@mtr jaw main is off
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:05 |  | 2021-06-22 14:17 | 44391.8141 | 44391.8141 | 44391.8155 | 2.07 | 0.02 | 12 | -11.98 | 2.05 | 25 | -22.95 | 20 | -17.95 | 3099907058 | 2 | AD | 3128 LE BOURGET LN, LINCOLN | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 19; CONTACT: SCOTT HODGES 916-357-4079, SUBDIVISION: LAKESIDE #6 |  | t1tmjpg,conn.svc.&set mtr good volts@mtr jaw main is off
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:05 |  | 2021-06-22 14:16 | 44391.8157 | 44391.8157 | 44391.8175 | 2.56 | 0.03 | 12 | -11.97 | 2.53 | 25 | -22.47 | 20 | -17.47 | 1459785169 | 2 | AD | 3140 LE BOURGET LN, LINCOLN | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 20; CONTACT: SCOTT HODGES 916-357-4079, SUBDIVISION: LAKESIDE #6 |  | t1tmjpg,conn.svc.&set mtr good volts@mtr jaw main is off
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:05 |  | 2021-06-22 14:26 | 44391.8177 | 44391.8177 | 44391.8194 | 2.38 | 0.03 | 12 | -11.97 | 2.35 | 25 | -22.65 | 20 | -17.65 | 8746330662 | 2 | AD | 3152 LE BOURGET LN, LINCOLN | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 21; CONTACT: SCOTT HODGES 916-357-4079, SUBDIVISION: LAKESIDE #6 |  | t1tmjpg,conn.svc.&set mtr good volts@mtr jaw main is off
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:05 |  | 2021-06-22 14:30 | 44391.8201 | 44391.8201 | 44391.8215 | 2.1 | 0.02 | 12 | -11.98 | 2.08 | 25 | -22.92 | 20 | -17.92 | 3641186793 | 2 | AD | 3164 LE BOURGET LN, LINCOLN | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 22; CONTACT: SCOTT HODGES 916-357-4079, SUBDIVISION: LAKESIDE #6 |  | t1tmjpg,conn.svc.&set mtr good volts@mtr jaw main is off
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:05 |  | 2021-06-22 14:32 | 44391.8217 | 44391.8217 | 44391.823 | 1.9 | 0.02 | 12 | -11.98 | 1.88 | 25 | -23.12 | 20 | -18.12 | 4036565618 | 2 | AD | 3176 LE BOURGET LN, LINCOLN | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 23; CONTACT: SCOTT HODGES 916-357-4079, SUBDIVISION: LAKESIDE #6 |  | t1tmjpg,conn.svc.&set mtr good volts@mtr jaw main is off
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:05 |  | 2021-06-22 14:34 | 44391.8232 | 44391.8232 | 44391.825 | 2.68 | 0.03 | 12 | -11.97 | 2.65 | 25 | -22.35 | 20 | -17.35 | 0574230958 | 2 | AD | 3188 LE BOURGET LN, LINCOLN | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 24; CONTACT: SCOTT HODGES 916-357-4079, SUBDIVISION: LAKESIDE #6 |  | t1tmjpg,conn.svc.&set mtr good volts@mtr jaw main is off
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 08:08 |  | 2021-07-14 08:07 |  |  | 44391.349 | [9 empty] | T005341310 | 0 | AD | 5881 CHURCH ST, FORESTHILL | 9080 |  |  |  |  | AXS-AXS K; XSTR- PWR-I PER ANN
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 08:23 |  | 2021-07-14 08:23 |  |  | 44391.3833 | [9 empty] | T005341338 | 1 | AD | 5101 SUNSET BLVD W #A, ROSEVILLE | 9150 |  |  |  |  | AXS-ACCESS OK XSTR-FIDDYMENT PWR-Y COW PASTURE, PLEASE OPEN/CLOSE SAME GATE
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Auburn | TOMASI, MICHAEL | Completed | 5 | 4APGBF4 | 2021-07-14 09:08 |  | 2021-07-13 07:27 | 44391.383 | 44391.3968 | 44391.4108 | 39.98 | 19.88 | 12 | 7.88 | 20.1 | 30 | -9.9 | 5.6 | 14.5 | 4205884060 | 2 | AM | 6281 BROOKSHIRE DR, ROCKLIN | 2640 | 0980 |  |  |  | EXC - AXS OK; CTC MIKE: 916-597-4057, DISC ONLY 200A - UG PNL; REP: MIBF 916-204-2243; NOTIF #: 121689700 - OK TO SERVE | put on Tomasi per Hattrup | 6821 BROOKSHIRE DR SVC DISCONNECTED IT TX UPON ARRIVAL.
|  |  | Completed | 1 | OIS DSP | 2021-07-14 09:55 |  | 2021-07-14 09:54 | 44391.4156 | 44391.4239 | 44391.5569 | 203.52 | 11.92 | 12 | -0.08 | 191.6 | 61 | 130.6 | 0 | 191.6 | T005341516 | 0 | AD | 6725 CASA VISTA DR, LOOMIS | 9080 | 9002 |  |  |  | SMART MTR AUTO-GENERATED TAGCST STATES POSSIBLE TRANSFORMER BLOWN. |  | 2 OF 3 BLOWN AT SSD 5097, #1, #2. PATROLLED AND NO CAUSE FOUND. REFUSED AND CLOSED 5097, TEST OK. LOAD 12, 5, 14
|  |  | Completed | 4 | 4APKERA | 2021-07-14 17:57 |  | 2021-07-14 16:25 | 44391.7532 | 44391.7744 | 44391.7861 | 47.26 | 30.48 | 12 | 18.48 | 16.78 | 31 | -14.22 | 33.1 | -16.32 | 0899259747 | 1 | AD | 2350 BALD HILL RD, AUBURN | 1240 | 1058 |  |  |  | No Access or Safety Issues; PER LAN ID - J03V, CAR HIT POLE, POLE IS ATTACHED BUT SPLINTERED, SAP EQUIP ID 100039932, 2 SPANS TO SOUTHEAST OF CAPACITOR, OPERATING NUMBER OF FUSE # 9431, CONTACT # 619-987-7324 |  | pole previously identified. notif-120507309. pm-35269898.
|  |  | Completed | 1 | OIS DSP | 2021-07-14 21:27 |  | 2021-07-14 21:27 | 44391.8974 | 44391.9206 | 44391.9937 | 138.65 | 33.37 | 12 | 21.37 | 105.28 | 30 | 75.28 | 0 | 105.28 | T005342106 | 1 | AD | 2273 DELMAR AVE, PENRYN | 9030 | 9002 |  |  |  | , PWR-I |  | found 2 of 3 blown at ssd 8585, #1, #2. patrolled and found no cause. refused 8585, test ok. load 8, 8, 4
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 08:49 |  | 2021-07-14 08:49 |  |  | 44391.368 | [9 empty] | T005341394 | 2 | AD | STRLIGHT 21660 SWEET EARTH RD, COLFAX | 9500 |  |  |  |  | LIGHTBULB BURNED OUT ONCE IN A WHILE IT WILL COME ON FOR A MOMENT BEFORE GOING BACK OFF; LIGHT WAS ALSO SUPPOSED TO BE REPLACED LED AND NEVER WAS
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 08:54 |  | 2021-07-14 08:54 |  |  | 44391.3997 | [9 empty] | T005341403 | 2 | AD | STRLIGHT 21660 SWEET EARTH RD, COLFAX | 9500 |  |  |  |  | LIGHTBULB BURNED OUT ONCE IN A WHILE IT WILL COME ON FOR A MOMENT BEFORE GOING BACK OFF; LIGHT WAS ALSO SUPPOSED TO BE REPLACED LED AND NEVER WAS
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 09:12 |  | 2021-07-14 09:11 |  |  | 44391.4254 | [9 empty] | T005341445 | 1 | AD | 5101 SUNSET BLVD W #A, ROSEVILLE | 9150 |  |  |  |  | AXS-ACCESS OK XSTR-FIDDYMENT PWR-Y COW PASTURE, PLEASE OPEN/CLOSE SAME GATE
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 10:14 |  | 2021-07-14 10:14 |  |  | 44391.6113 | [9 empty] | T005341546 | 2 | AD | STRLIGHT 12160 MONT VISTA DR, AUBURN | 9500 |  |  |  |  | MONT VISTA CIRCLE & SIERRA VISTA CT
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 10:14 |  | 2021-07-14 10:14 |  |  | 44391.6116 | [9 empty] | T005341549 | 2 | AD | STRLIGHT PALOMINO CT & SOUTHRID, AUBURN | 9500 |  |  |  |  | SAP EQUIP ID #43968778; SWC PALOMINO CT & SOUTHRIDGE DR
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 10:37 |  | 2021-07-14 10:36 |  |  | 44391.6118 | [9 empty] | T005341584 | 2 | AD | STRLIGHT 5401 ALLEN DR, ROCKLIN | 9500
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 15:31 |  | 2021-07-14 15:30 |  |  | 44391.6507 | [9 empty] | T005341919 | 1 | AD | 9492 TREELAKE RD, GRANITE BAY | 9130 |  |  |  |  | AXS-DOG : GOLDEN RETRIEVER XSTR-SWAN LAKE PWR-Y ELECTRICIAN ADVISED TO CALLPGE FOR FLICKERING LIGHTS/ ROOMS : MASTER BED, AND KI TCHEN MOSTLY.
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 21:28 |  | 2021-07-14 21:27 |  |  | 44391.8979 | [9 empty] | T005342107 | 1 | AD | 1575 ENGLISH COLONY WAY, PENRYN | 9030 |  |  |  |  | , PWR-I
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Auburn | TURNEY, RJ | Reassigned | 1 | OIS DSP | 2021-07-14 07:20 |  | 2021-07-14 07:19 | 44391.3077 | 44391.3314 | 44391.3621 | 34.2 | 34.2 |  | 34.2 | [5 empty] | T005341237 | 0 | AD | 1660 MEADOW VISTA RD, MEADOW VISTA | 9080 |  |  |  |  | A:DOG;;X:;R:PER JAMES, PWR-I
|  |  | Completed | 1 | OIS DSP | 2021-07-14 08:25 |  | 2021-07-14 08:25 | 44391.3621 | 44391.3762 | 44391.4078 | 65.9 | 20.28 | 12 | 8.28 | 45.62 | 39 | 6.62 | 0 | 45.62 | T005341341 | 0 | AD | 1420 SAGE RD, COLFAX | 9000 | 9002 |  |  |  | AXS-UNKNOWN XSTR-UNKOWN PWR-I CALLER ADVISED FIRE ON TRANSFORMER ADVISED TO CALL 911, WAS NOT ABLE TO GO OVER SAFETY |  | Tx at front of driveway, svc's burnt open at secondary buss. Need to lower tx and install new c/o arm and new c/o's. Replace secondary buss, run new svc wire to both meters, make up new connestions at tx.
|  |  | Completed | 10 | 4APGBF4 | 2021-07-14 09:04 |  | 2021-07-12 16:20 | 44391.4333 | 44391.4778 | 44391.4993 | 95 | 64.12 | 12 | 52.12 | 30.88 | 31 | -0.12 | 22.6 | 8.28 | 1035623577 | 1 | AD | 7237 PALISADE RD, SODA SPRINGS | 1240 | 1056 |  |  |  | GIVE TO RJ. SPOKE TO CUSTOMER, NEED TO MAKE SURE PANEL IS SAFE |  | Placed panel cover back on panel and re-sealed
|  |  | Completed | 1 | OIS DSP | 2021-07-14 11:49 |  | 2021-07-14 11:48 | 44391.4994 | 44391.5462 | 44391.5553 | 80.5 | 67.43 | 12 | 55.43 | 13.07 | 32 | -18.93 | 16.6 | -3.53 | T005341685 | 0 | AD | 20292 HUMMINGBIRD HILL RD, COLFAX | 9190 | 9320 |  |  |  | A:LCK GATE/DOG;X:;R:DEAD PINETREES REACIG HIGH VOLTAGE. CUSTMER HEARDTREE SNAP FRM WINDS, PWR-Y |  | Notified ACRT about dead pine trees that need to be assessed
|  |  | Completed | 1 | OIS DSP | 2021-07-14 09:36 |  | 2021-07-14 09:35 | 44391.5566 | 44391.5655 | 44391.5775 | 30.15 | 12.8 | 12 | 0.8 | 17.35 | 60 | -42.65 | 54 | -36.65 | T005341490 | 2 | AD | STRLIGHT 21660 SWEET EARTH RD, COLFAX | 9500 | 9500 |  |  |  | LIGHTBULB BURNED OUT ONCE IN A WHILE IT WILL COME ON FOR A MOMENT BEFORE GOING BACK OFF; LIGHT WAS ALSO SUPPOSED TO BE REPLACED LED AND NEVER WAS |  | Replaced broken photocell, and checked light working
|  |  | Completed | 18 | SAP DSP | 2021-07-14 09:13 |  | 2021-06-30 11:45 | 44391.5877 | 44391.6269 | 44391.6448 | 82.21 | 56.43 | 12 | 44.43 | 25.78 | 60 | -34.22 | 60 | -34.22 | S000761576 | 3 | AD | 1250 MAT TELL DR, Alta | S436 | S400 |  |  |  | Need KVA and serial # of TX on pole SAPID: 100009741 |  | The tx requested for info is a Pennsylvania, serial#20934-41 and is a 5 kva
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 07:25 |  | 2021-07-14 07:24 |  |  | 44391.3129 | [9 empty] | T005341243 | 0 | AD | UNKNOWN MEADOW LN, MEADOW VISTA | 9080 |  |  |  |  | AXS-OK
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 08:01 |  | 2021-07-14 08:00 |  |  | 44391.3676 | [9 empty] | T005341286 | 2 | AD | STRLIGHT 21660 SWEET EARTH RD, COLFAX | 9500 |  |  |  |  | LIGHTBULB BURNED OUT ONCE IN A WHILE IT WILL COME ON FOR A MOMENT BEFORE GOING BACK OFF; LIGHT WAS ALSO SUPPOSED TO BE REPLACED LED AND NEVER WAS
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 08:01 |  | 2021-07-14 08:01 |  |  | 44391.3388 | [9 empty] | T005341287 | 0 | AD | 5881 CHURCH ST, FORESTHILL | 9080 |  |  |  |  | AXS-AXS K; XSTR- PWR-I PER ANN
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 08:31 |  | 2021-07-14 08:30 |  |  | 44391.363 | [9 empty] | T005341355 | 0 | AD | UNKNOWN 1420 SAGE RD, COLFAX | 9000 |  |  |  |  | AXS-OK .OIS 1404064. TRANSFORMER ON FIRE AND VEG FIRE. FD ETA 530-477-5761
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 08:42 |  | 2021-07-14 08:41 |  |  | 44391.377 | [9 empty] | T005341380 | 0 | AD | 1660 MEADOW VISTA RD, MEADOW VISTA | 9080 |  |  |  |  | A:DOG;;X:;R:PER JAMES, PWR-I
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 08:50 |  | 2021-07-14 08:50 |  |  | 44391.3709 | [9 empty] | T005341395 | 2 | AD | STRLIGHT 21660 SWEET EARTH RD, COLFAX | 9500 |  |  |  |  | LIGHTBULB BURNED OUT ONCE IN A WHILE IT WILL COME ON FOR A MOMENT BEFORE GOING BACK OFF; LIGHT WAS ALSO SUPPOSED TO BE REPLACED LED AND NEVER WAS
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 12:50 |  | 2021-07-14 12:49 |  |  | 44391.5466 | [9 empty] | T005341742 | 1 | AD | 15300 MCELROY RD, MEADOW VISTA | 9030 |  |  |  |  | AXS-AXS OK XSTR-MEADOW VISTA RD PWR-Y COMPLETE OUT - REPLACE BUSS AT TRANSFORMER , CONNECTORS AT SERVICE POLE ON 7/9/21 ANDNOW OUT OF POWER AGAIN SINCE 7/13 AFTERNOON. CUSTOMER REQ CALL IN ADVANCE
Burney
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
6 | Burney | KNAUP, GEORGE | Completed | 1 | OIS DSP | 2021-07-14 15:05 |  | 2021-07-14 15:04 | 44391.6477 | 44391.6538 | 44391.7385 | 130.78 | 8.9 | 19 | -10.1 | 121.88 | 43 | 78.88 | 0 | 121.88 | T005341887 | 1 | AD | 28345 SPRING CREEK RD, FALL RIVER M | 9040 | 9221 |  |  |  | AXS-LOCKD GT XSTR- PWR-Y AG/CIA ;SMTR MTR STATUS: POWER ON; NO CURRNT HAZRD; REPORTS OF ARCING LINES EARLIER TODAY; NO NO POWER TO PUMP |  | customer service panel burnt up
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Burney | LOMMEN, ANTHONY | Completed | 8 | 4APBXET | 2021-07-14 08:12 |  | 2021-07-12 14:26 | 44391.3686 | 44391.3687 | 44391.3697 | 1.55 | 0.08 | 19 | -18.92 | 1.47 | 35 | -33.53 | 5.6 | -4.13 | 1003688616 | 2 | AM | 10177 TILTON MINE RD, REDDING | 2220 | 0980 |  |  |  | No Access or Safety Issues;Reconnect,Reason for disconnect due to - DE-RATE OF MAIN BREAKER, KELLY 530-342-7304 NORTHSTATE SOLAR |  | Solar company having issue sourcing the correct breaker for main
|  |  | Completed | 8 | 4APBXET | 2021-07-14 08:12 |  | 2021-07-12 14:23 | 44391.3699 | 44391.3699 | 44391.3709 | 1.5 | 0.05 | 19 | -18.95 | 1.45 | 30 | -28.55 | 5.6 | -4.15 | 1005875738 | 2 | AM | 10177 TILTON MINE RD, REDDING | 2640 | 0980 |  |  |  | No Access or Safety Issues; Temp Disconnect, Reason for request - DE-RATE THE MAIN BREAKER ONLY, KELLY 530-342-7304 NORTHSTATE SOLAR |  | Solar company having issues sourcing correct main breaker
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 09:00 |  | 2021-07-14 08:54 | 44391.3956 | 44391.4014 | 44391.4023 | 9.58 | 8.35 | 19 | -10.65 | 1.23 | 30 | -28.77 | 5.6 | -4.37 | 1009194096 | 1 | AD | 10177 TILTON MINE RD, REDDING | 2640 | 0980 |  |  |  | Temp Disconnect, Reason for request - DE-RATE THE MAIN BREAKER ONLY, KELLY 530-342-7304 NORTHSTATE SOLAR |  | solar company having issues sourcing correct main breaker replacement
|  |  | Completed | 1 | OIS DSP | 2021-07-14 09:28 |  | 2021-07-14 09:27 | 44391.4066 | 44391.4094 | 44391.429 | 32.22 | 3.97 | 19 | -15.03 | 28.25 | 32 | -3.75 | 16.6 | 11.65 | T005341479 | 0 | AD | 11730 BRINDA LN, REDDING | 9190 | 9320 |  |  |  | AXS-AXS OK XSTR-LEWIS LN PWR-I MYLAR BALLOON INT HE TOP PRIMARY WIRES, NO ARCING/ POWER IS OK. CUST SAYS THE BALLOON IS MORE ON LEWIS LN (THE SREET APPROACHING CUST ADDRESS) BEEN THERE SINCE SUNDAY |  | removed mylar balloon from phone level
|  |  | Completed | 4 | 4APNWA1 | 2021-07-14 10:03 |  | 2021-07-12 16:58 | 44391.4581 | 44391.4848 | 44391.5786 | 173.42 | 38.37 | 19 | 19.37 | 135.05 | 35 | 100.05 | 20 | 115.05 | 1013407091 | 2 | AM | 29584 HWY 44, SHINGLETOWN | 2220 | 2220 |  |  |  | Access/Safety: Locked Gate or Cabinet;BRSC RECONNECT;PANEL MAINTENANCE;AXS LOCKED GATE-WILL NLOCK FOR APT;ALT PH 279-222-7281 |  | Ran new 1/0 service and made up both sides of connection, closed fuses checked power okay
|  |  | Completed | 5 | 4APNWA1 | 2021-07-14 10:03 |  | 2021-07-13 17:12 | 44391.5843 | 44391.5904 | 44391.6172 | 47.36 | 8.78 | 19 | -10.22 | 38.58 | 31 | 7.58 | 20 | 18.58 | 0002515275 | 1 | AD | UNKNOWN PREMISES DO NOT CHANGE, SHINGLETOWN | 1240 | 2220 |  |  |  | WB HWY 44 AT MT LASSEN, MT LASSEN WOODS, RECONNECT STREET LIGHT, CONTACT BOBBY AT 530-945-4949, OPEN AT BYPASS PLUGS ON BOTH PEDASTAL |  | closed test lugs at panel checked volts good
|  |  | Completed | 1 | OIS DSP | 2021-07-14 15:10 |  | 2021-07-14 15:09 | 44391.6321 | 44391.6895 | 44391.7206 | 127.46 | 82.68 | 19 | 63.68 | 44.78 | 43 | 1.78 | 5.6 | 39.18 | T005341893 | 1 | AD | 28345 SPRING CREEK RD, FALL RIVER M | 9040 | 0980 |  |  |  | AXS-LOCKD GT XSTR- PWR-Y AG/CIA ;SMTR MTR STATUS: POWER ON; NO CURRNT HAZRD; REPORTS OF ARCING LINES EARLIER TODAY; NO NO POWER TO PUMP |  | GXKI primary on tag. Cust panel issue
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 18:52 |  | 2021-07-14 18:51 |  |  | 44391.7916 | [9 empty] | T005342040 | 1 | AD | COLLEGE ST & HWY 299 N, BIEBER | 9030 |  |  |  |  | AXS-AXS OK XSTR- PWR-Y COMPLETE OUT;CONTACTDAVID 239-896-5680
|  |  | Unworked | 15 | SAP DSP | 2021-09-21 08:01 |  | 2021-09-10 13:46 | [12 empty] | S000771749 | 3 | AD | End of F risby Rd, Oak Run | S438 |  |  |  |  | COL Field Verification, Closest SSD 451856 , Meter ID 256870250,Please fill out TEAMS form. See communication for link¿ COL PH# (530)337-6581
|  |  | Unworked | 15 | SAP DSP | 2021-09-21 08:01 |  | 2021-09-10 14:14 | [12 empty] | S000771766 | 3 | AD | SILVER S PRINGS HYDRO S/O PI, Montgomery C | S438 |  |  |  |  | COL Field Verification, Closest SSD 8243 , Meter ID 255384382, Pleasefill out TEAMS form. See communication for link¿ COL PH# (530) 337-6332
|  |  | Unworked | 15 | SAP DSP | 2021-09-21 08:01 |  | 2021-09-10 15:02 | [12 empty] | S000771768 | 3 | AD | Nelson C reek Rd, Montgomery C | S438 |  |  |  |  | COL Field Verification, Closest SSD 8607 , Meter ID 255482879, Pleasefill out TEAMS form. See communication for link¿ COL PH# (530) 378-8000
|  |  | Unworked | 15 | SAP DSP | 2021-09-21 08:01 |  | 2021-09-10 15:05 | [12 empty] | S000771769 | 3 | AD | 100 BIG BEND RD 4S/O 10SE/O 3E, Montgomery C | S438 |  |  |  |  | COL Field Verification, Closest SSD 90846 , Meter ID 256870249,Please fill out TEAMS form. See communication for link¿ COL PH# (530)337-6158
Chico
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
6 | Chico | BISCHEL, JASON | Completed | 1 | OIS DSP | 2021-07-14 07:14 |  | 2021-07-14 07:13 | 44391.3028 | 44391.3148 | 44391.3687 | 94.82 | 17.3 | 10 | 7.3 | 77.52 | 32 | 45.52 | 31.1 | 46.42 | T005341234 | 0 | AD | UNKNOWN E 6TH ST, CHICO | 9190 | 9190 |  |  |  | AXS-OK |  | tree crew from PGE to cut limb down,city tree crew to clean up limb
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:44 |  | 2021-07-13 13:03 | 44391.3688 | 44391.3688 | 44391.3969 | 40.51 | 0.03 | 10 | -9.97 | 40.48 | 30 | 10.48 | 15 | 25.48 | 0663516822 | 2 | AM | 464 E 20TH ST, CHICO | 2640 | 2640 |  |  |  | Disconnect electric service POC DANIEL TURRI 530-570-7988 |  | customer to install new panel and gutter can.Will re-energize original panel only
|  |  | Completed | 1 | OIS DSP | 2021-07-14 09:35 |  | 2021-07-14 09:33 | 44391.3999 | 44391.4099 | 44391.4356 | 51.42 | 14.37 | 10 | 4.37 | 37.05 | 30 | 7.05 | 0 | 37.05 | T005341485 | 0 | AD | 901 ESPLANADE, CHICO | 9060 | 9221 |  |  |  | A:OK;X:W SACRAMENTO AV;R:CIA/DRILL RIG HIT ELCTRIC LINE/CHICO HIGH SCHOOL/BRANNAN/HANKINS/ |  | Santos contracting crew struct 3rd party solar line.PGE good.PGE does have facilites in area.Contractor was informed from PGE dig in investigator to stop and have PGE power lines remarked before proceeding
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:44 |  | 2021-07-13 13:05 | 44391.5389 | 44391.5539 | 44391.603 | 92.43 | 21.7 | 10 | 11.7 | 70.73 | 35 | 35.73 | 20 | 50.73 | 0668269948 | 2 | PM | 464 E 20TH ST, CHICO | 2220 | 2220 |  |  |  | Reconnect electric service POC DANIEL TURRI 530-570-7988 |  | service is energized to existing panel,customer will need inspection before PGE will connect new panel fed off same gutter can
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Chico | BRANCH, SCOTT | Completed | 2 | 4APNWA1 | 2021-07-14 06:45 |  | 2021-07-12 14:56 | 44391.2972 | 44391.3476 | 44391.3615 | 92.58 | 72.48 | 10 | 62.48 | 20.1 | 30 | -9.9 | 15 | 5.1 | 0696831357 | 2 | AM | 715 DEAD END CT, CHICO | 2640 | 2640 |  |  |  | AXS OK; CTC Denise Funsten: 530-345-6980, DIS/REC 200A TO 200A - UG PNL CHG, L4L; Cust to ensure clear/level workspace; REP: CYCC 530-228-6873; TMAN TO VERIFY INSP/ NOTIF #:120951585: - OK TO SERVE / CONTACT KIETH DAY OF APPT 530.961.3500 |  | live front trans , no disconect point. taped at panel
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:45 |  | 2021-07-13 12:35 | 44391.362 | 44391.375 | 44391.3948 | 47.13 | 18.7 | 10 | 8.7 | 28.43 | 25 | 3.43 | 30 | -1.57 | 4558470315 | 2 | AD | 739 REECE LN, CHICO | 2094 | 2052 | 2090 |  |  | CON/SET; INSP OK; LOT 5; SITE CNTC PAUL MELLO 530-680-4520; SUBDV: MORSEMAN |  | connect and set. 123/124/245v
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:45 |  | 2021-07-13 12:32 | 44391.3948 | 44391.3949 | 44391.4085 | 19.71 | 0.03 | 10 | -9.97 | 19.68 | 25 | -5.32 | 30 | -10.32 | 5426750607 | 2 | AD | 755 REECE LN, CHICO | 2094 | 2052 | 2090 |  |  | CON/SET; INSP OK; LOT 1; SITE CNTC PAUL MELLO 530-680-4520; SUBDV: MORSEMAN |  | 123/124/246v. main off
|  |  | Completed | 1 | AFW DSP | 2021-07-12 14:15 |  | 2021-07-12 14:15 | 44391.4112 | 44391.4571 | 44391.4884 | 111.17 | 66.07 | 10 | 56.07 | 45.1 | 90 | -44.9 | 0 | 45.1 | W106971803 | 2 | UD | , | W114 | W114
|  |  | Completed | 5 | 4APBXET | 2021-07-13 07:16 |  | 2021-07-02 12:17 | 44391.4885 | 44391.5053 | 44391.5413 | 76.14 | 24.17 | 10 | 14.17 | 51.97 | 16 | 35.97 | 30 | 21.97 | 0298553476 | 2 | AD | 818 CHESTNUT ST UNIT 2, CHICO | 2124 | 2052 | 2090 |  |  | TMAN TO DISC/RECO, SET 2ND MTR ON NEW DUAL MTR PANEL. CAN USE BUCKET TRUCK TO AXS W/HEAD CUST STATES CLEAR PATH FROM ROAD TO W/HEAD. TMAN TO VERIFY INSP - FLD CNT ROBERT EVANS 530-966-0120 REP NICHOLAS DE LA FUENTE 916-296-8189, ORD34460998 N#121584287 | WONT BE READY FOR INSPECTION TIL 07/14 PER BRANCH | install meter for unit 2 , land old meter for unit 1.reconnect. all hot
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:45 |  | 2021-07-12 14:59 | 44391.5414 | 44391.6249 | 44391.6379 | 138.9 | 120.2 | 10 | 110.2 | 18.7 | 35 | -16.3 | 20 | -1.3 | 0698851874 | 2 | AD | 715 DEAD END CT, CHICO | 2220 | 2220 |  |  |  | AXS OK; CTC Denise Funsten: 530-345-6980, DIS/REC 200A TO 200A - UG PNL CHG, L4L; Cust to ensure clear/level workspace; REP: CYCC 530-228-6873; TMAN TO VERIFY INSP/ NOTIF #:120951585: - OK TO SERVE / CONTACT KIETH DAY OF APPT 530.961.3500 |  | 124/124/246v
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 13:49 |  | 2021-07-14 13:49 |  |  | 44391.6168 | [9 empty] | T005341803 | 1 | AD | 13872 HIGHWAY 99 N, CHICO | 9140 |  |  |  |  | AXS-OK XSTR-WILSON LANDING RD PWR-Y ELECTRICIAN ADVISED TOO MUCH POWER COMING INTO PANEL. 150 ON EACH SIDE
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Chico | CAMPBELL, SCOTT | Completed | 2 | 4APNWA1 | 2021-07-14 06:42 |  | 2021-07-10 10:56 | 44391.3111 | 44391.3726 | 44391.4466 | 195 | 88.43 | 10 | 78.43 | 106.57 | 30 | 76.57 | 15 | 91.57 | 0702031105 | 2 | AD | CSUC INSTRU MEDIA CNTR FLEA, OROVILLE | 2640 | 2640 |  |  |  | TMAN TO DISCONNECT EXISTING OVERHEAD SERVICE TO DIGITAL PATH SHELTER, SHORTEN SERVICE WIRE, REMOVE # 1010502365 FROM OLD SHELTER, CTC: KEVIN ANDERSON (530) 826-6582, REP: RYAN FLORES (530) 339-0342, NOT # 120921380 |  | Disc and transfer serv and mtr to new panel
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:42 |  | 2021-07-10 11:01 | 44391.4466 | 44391.4466 | 44391.4695 | 32.87 | 0.02 | 10 | -9.98 | 32.85 | 35 | -2.15 | 20 | 12.85 | 0702474246 | 2 | AD | CSUC INSTRU MEDIA CNTR FLEA, OROVILLE | 2220 | 2220 |  |  |  | RE-CONNECT TO NEW WEATHER HEAD ON SHELTER,RE-INSTALL IN NEW PANEL ON NEW SHELTER, CTC: KEVIN ANDERSON (530) 826-6582, REP: RYAN FLORES (530) 339-0342, NOT# 120921380 |  | Insp panel ok, swing serv and reconn. Chk volt ok and transfer mtr
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Chico | SHERROD, LARRY | Completed | 1 | OIS DSP | 2021-07-14 09:51 |  | 2021-07-14 09:51 | 44391.4108 | 44391.4159 | 44391.4331 | 32.02 | 7.35 | 10 | -2.65 | 24.67 | 30 | -5.33 | 5.6 | 19.07 | T005341512 | 0 | AD | 901 ESPLANADE, CHICO | 9060 | 0980 |  |  |  | A:OK;X:W SACRAMENTO AV;R:CIA/DRILL RIG HIT ELCTRIC LINE/CHICO HIGH SCHOOL/BRANNAN/HANKINS/ |  | BISCHELL HAS PRIMARY TAG
|  |  | Completed | 1 | AFW DSP | 2021-07-06 19:05 |  | 2021-07-06 19:04 | 44391.4331 | 44391.4352 | 44391.4645 | 45.23 | 2.93 | 10 | -7.07 | 42.3 | 120 | -77.7 | 0 | 42.3 | W106700004 | 2 | UD | , | W112 | W112
|  |  | Completed | 1 | OIS DSP | 2021-07-14 12:17 |  | 2021-07-14 12:16 | 44391.5384 | 44391.5459 | 44391.558 | 28.27 | 10.77 | 10 | 0.77 | 17.5 | 30 | -12.5 | 16.6 | 0.9 | T005341712 | 1 | AD | 46 EMIGRANT WAY APT B, CHICO | 9030 | 9320 |  |  |  | AXS-AXS OK XSTR-12TH AND IVY PWR-I CIA/ COMPLETE OUT/ CAR RAN INTO BUILDING ON 06-26-2021 POWER SHOWS ON CALLER SAY NO POWER AND CHECKED BREAKERS. |  | MTR WAS BOOTED FOR DISCONNECT. CALLED IN FOR RECONNECT TAG
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 13:21 |  | 2021-07-14 13:16 | 44391.5581 | 44391.5581 | 44391.5834 | 36.41 | 0.03 | 10 | -9.97 | 36.38 | 35 | 1.38 | 20 | 16.38 | 0693845043 | 1 | AD | 46 EMIGRANT WAY APT B, CHICO | 2220 | 2220 |  |  |  | give to Sherrod |  | REMOVED BOOTS OF LOAD SIDE OF MTR. RECONNECT AT MTR. PANEL. PWR OK
|  |  | Completed | 1 | OIS DSP | 2021-07-14 14:12 |  | 2021-07-14 14:12 | 44391.5948 | 44391.6188 | 44391.6315 | 52.75 | 34.47 | 10 | 24.47 | 18.28 | 51 | -32.72 | 16.6 | 1.68 | T005341831 | 1 | AD | 844 CARRGROVE CT, CHICO | 9140 | 9320 |  |  |  | A:UNK;X:UNK;R:PER EIM CASE 2145586 SOME OF MY LIGHTS DIM WHEN THE REFRIGERATOR IN THE GARAGE KICKS ON. CAN SOMEONE COME OUT AND CHECK WHY IT`S HAPPENING? THANKS., PWR-Y |  | CUST. SAYS LIGHTS DIMMING. RAN A BEAST OF BURDEN TEST WITH GOOD RESULTS. GOOD PWR TO MTR. ALL CONNECTIONS IN PANEL ARE GOOD AND TIGHT. CUST. PANEL IS NEW. ADVISED TO GET A ELECTRICIAN. PGE PWR OK WHEN LEFT
|  |  | Completed | 1 | OIS DSP | 2021-07-14 14:48 |  | 2021-07-14 14:48 | 44391.6318 | 44391.6447 | 44391.6624 | 44.12 | 18.6 | 10 | 8.6 | 25.52 | 51 | -25.48 | 16.6 | 8.92 | T005341861 | 1 | AD | 13872 HIGHWAY 99 N, CHICO | 9140 | 9320 |  |  |  | AXS-OK XSTR-WILSON LANDING RD PWR-Y ELECTRICIAN ADVISED TOO MUCH POWER COMING INTO PANEL. 150 ON EACH SIDE |  | TESTED PWR OK AT TWO SEPRATES MTR LOCATIONS AT 2 SEPRATE TRANS LOCATIONS WITH GOOD POWER. RAN A BEAST OF BURDEN TEST WITH GOOD RESULTS. PGE PWR OK
|  |  | Completed | 1 | OIS DSP | 2021-07-14 16:57 |  | 2021-07-14 16:57 | 44391.7108 | 44391.7305 | 44391.7837 | 104.97 | 28.35 | 10 | 18.35 | 76.62 | 52 | 24.62 | 0 | 76.62 | T005341968 | 1 | AD | CANA HWY SS 4 SPANS, CHICO | 9150 | 9002 |  |  |  | AXS-OK XSTR-CANA RD PWR-I *CIA* LEG OUT P/ELECTRICIAN* CONTACT STEVE * |  | NG THREE PHASE TRANS IN ORCHARD
|  |  | Completed | 1 | OIS DSP | 2021-07-14 20:57 |  | 2021-07-14 20:57 | 44391.8745 | 44391.8941 | 44391.943 | 98.5 | 28.12 | 10 | 18.12 | 70.38 | 36 | 34.38 | 16.6 | 53.78 | T005342091 | 0 | AD | 2595 HIGHWAY 32, CHICO | 9010 | 9320 |  |  |  | AXS-DOGS XSTR-KENNEY / HWY 32 PWR-Y WOODEN POLE HAS FRACTURES CUSTOMER CONCERN POLE IS LEANING CAR HIT THE POLE LAST NIGHT |  | POLE WAS HIT ON THE NIGHT OF 7-13-21. CHP ON SCENE NIGHT OF, NO CALL TO PGE. DUG AROUND POLE 2' DOWN NO SIGN OF BREAKAGE. OLDER PLE. WITH CRACKS. PGE PWR OK
|  |  | Reassigned | 1 | AFW DSP | 2021-07-06 19:05 |  | 2021-07-06 19:04 |  |  | 44391.2509 | [9 empty] | W106700009 | 2 | UD | , | W114
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Chico | THORNE III, ALLAN | Completed | 2 | 4APNWA1 | 2021-07-14 06:43 |  | 2021-06-17 11:26 | 44391.2949 | 44391.3123 | 44391.328 | 47.67 | 25.02 | 10 | 15.02 | 22.65 | 30 | -7.35 | 15 | 7.65 | 0705593384 | 2 | AM | 4841 ROUND VALLEY RANCH RD, PARADISE | 2640 | 2640 |  |  |  | EXC - AXS OK; CTC Erick Mendez: 916-820-9318, DIS/REC 200A TO 200A - OH PNL CHG, L4L; REP: JNK3 916-599-2202; TMAN TO VERIFY INSP/ NOTIF #: 000121390766 - OK TO SERVE |  | DISCONN, CUST ONSITE, VERIFIED W CONTACT, ELECTR COMING TODAY
|  |  | Completed | 4 | 4APNWA1 | 2021-07-14 09:52 |  | 2021-07-14 07:47 | 44391.4493 | 44391.4795 | 44391.5037 | 78.29 | 43.42 | 10 | 33.42 | 34.87 | 31 | 3.87 | 33.3 | 1.57 | 1988911740 | 1 | AD | 8369 HUGH BARBER LN 1.68 MI, CHICO | 1240 | 1163 |  |  |  | AXS OK, Jasmin Ramirez 530-342-0839, WIRE PGE REPLACED IS TOO LOW TO HOUSES, NO SIDE, BRANCH FELL ON WIRE 7-12-21 & PGE WAS OUT, THERE IS ALSO WOOD POLE LEANING, X-ST ORD FERRY RD |  | FND LOW AWAC, SAP 100439452, NOTIFIED D SPOON, NEED POLE INSTALLED, SENT A TAG ON INSPECT
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 12:03 |  | 2021-07-14 11:55 | 44391.5038 | 44391.5286 | 44391.5401 | 52.28 | 35.75 | 10 | 25.75 | 16.53 | 31 | -14.47 | 21.9 | -5.37 | 0629325607 | 0 | AD | 4571 SUNSET OAKS DR, PARADISE | 1240 | 1320 |  |  |  | Access/Safety: Dog(s);TRANSFORMER LEAK FROM 2 WEEKS AGO AND A LARGE AMOUNT OF THE FLUIDHAS SPILLED ONTO THE CONCRETE UNDER THE TRANSFORMER AND THE FLUID HAS SOAKED THE SOIL AND TOWARD THE PROPERTY LINE. MCOR WOULD LIKE THE WHOLE AREA TO BE DE-CONTAMINATE |  | T 1994 WAS RECENTLY REPLACED PER CUST, OLD TX LEAKY, CUST WANTS OIL CLEANED UP AROUND NEW TX, NOTIFIED DAVID SPOON AT MC CHICO WE NEED ENVIRO CLEAN UP
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:43 |  | 2021-06-17 11:27 | 44391.5402 | 44391.5496 | 44391.5625 | 32.22 | 13.6 | 10 | 3.6 | 18.62 | 35 | -16.38 | 20 | -1.38 | 0705241293 | 2 | AD | 4841 ROUND VALLEY RANCH RD, PARADISE | 2220 | 2220 |  |  |  | EXC - AXS OK; CTC Erick Mendez: 916-820-9318, DIS/REC 200A TO 200A - OH PNL CHG, L4L; REP: JNK3 916-599-2202; TMAN TO VERIFY INSP/ NOTIF #: 000121390766 - OK TO SERVE |  | RECONN SVC, NO PNL CHANGE PER SUNRUN ELECTR, SAYS NEEDS 400A PNL AT LATER DATE, 248V AT SOCKET, BRKRS LEFT OFF
|  |  | Completed | 1 | OIS DSP | 2021-07-14 14:51 |  | 2021-07-14 14:51 | 44391.6204 | 44391.6408 | 44391.7158 | 137.35 | 29.28 | 10 | 19.28 | 108.07 | 59 | 49.07 | 0 | 108.07 | T005341867 | 0 | AD | 13525 BADER MINE RD, PARADISE | 9260 | 9002 |  |  |  | SMART MTR AUTO-GENERATED TAG |  | WIRE DOWN, OAK TREE, CREW TO RPR WIRE DOWN
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:43 |  | 2021-06-29 09:01 | 44391.7166 | 44391.7323 | 44391.7548 | 55.12 | 22.7 | 10 | 12.7 | 32.42 | 30 | 2.42 | 15 | 17.42 | 0701915575 | 2 | PM | 6047 PARTRIDGE WAY, MAGALIA | 2640 | 2640 |  |  |  | Access/Safety: Dog(s); WIRE GO THROUGH TREES; LOCATED ON EASEMENT IN BACK OF PROPERTY; TEMP DISCONNECT; TREE TRIMMING |  | DISCONN SVC FROM OAK TREE, CUST REQ FOR TREE REMOVALS
|  |  | Completed | 1 | OIS DSP | 2021-07-14 18:13 |  | 2021-07-14 18:12 | 44391.7593 | 44391.7838 | 44391.8052 | 66 | 35.3 | 10 | 25.3 | 30.7 | 30 | 0.7 | 0 | 30.7 | T005342011 | 1 | AD | 280 SCHLAF DR, OROVILLE | 9030 | 9002 |  |  |  | SMART MTR AUTO-GENERATED TAG |  | ILB
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 15:18 |  | 2021-07-14 15:17 |  |  | 44391.6376 | [9 empty] | T005341905 | 0 | AD | UNKNOWN 13699 BADER MINE RD, PARADISE | 9260 |  |  |  |  | AXS-OK FD ONSITE WIRES DOWN-OUTAGE ETA REQ WHEN AVLB
Grass Valley
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
6 | Grass Valley | CROOKS, MICHAEL | Completed | 4 | 4APNWA1 | 2021-07-14 06:34 |  | 2021-07-13 08:28 | 44391.3006 | 44391.312 | 44391.3454 | 64.52 | 16.52 | 16.3 | 0.22 | 48 | 30 | 18 | 15 | 33 | 1209643181 | 1 | AD | 15311 GARDEN BAR RD, GRASS VALLEY | 2640 | 2640 |  |  |  | GIVE TO SHADEGBF4:OTHER;GBF4:OTHER; |  | CUT FROM POLE
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:14 |  | 2021-07-07 09:35 | 44391.3456 | 44391.3767 | 44391.3892 | 62.68 | 44.73 | 16.3 | 28.43 | 17.95 | 30 | -12.05 | 15 | 2.95 | 1076094896 | 2 | AM | 11585 TAMMY WAY, GRASS VALLEY | 2640 | 2640 |  |  |  | EXC AXS OK; CUST CHRIS 916-778-7064; DIS/REC L4L 200 PNL CHG, INSP REQ; REP SRRQ 2092728553; NOTIF 121669612 |  | CUT AND TIED IN TREE
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:14 |  | 2021-07-06 14:04 | 44391.3899 | 44391.3988 | 44391.407 | 24.72 | 12.92 | 16.3 | -3.38 | 11.8 | 30 | -18.2 | 15 | -3.2 | 1108396691 | 2 | AM | 20328 CASA LOMA DR, GRASS VALLEY | 2640 | 2640 |  |  |  | EXC - AXS OK; CTC Kevin Bryan, 530-575-1834, DIS/REC 200A TO 200A - OH PNL CHNG/ L4L; REP: A3JK 916-926-7486; TMAN TO VERIFY INSP / NOTIF #: 121542617 - OK TO SERVE |  | KJHERGQJK;FWERBJKWFBJSDFBKLDSFBJK
|  |  | Completed | 1 | OIS DSP | 2021-07-14 09:43 |  | 2021-07-14 09:43 | 44391.4102 | 44391.4141 | 44391.452 | 60.18 | 5.58 | 16.3 | -10.72 | 54.6 | 36 | 18.6 | 0 | 54.6 | T005341502 | 0 | AD | 11803 RAINBOW RD, GRASS VALLEY | 9010 | 9002 |  |  |  | AXS-AXS OK XSTR-PAMILA PWR-Y NEW LEANING POLE WOOD POLE WHICH IS CAUSING A STRAIN ON THE SERVICE WIREPLS CALL WHEN IN ROUTE |  | POLE LEANING AT ROAD, PRIMARY TOO TIGHT TO PULL GUYS. NEIGHBORS SERVICE WOULD BE TOO TIGHT IF POLE STRAIGHTENED. ADDED WIRE TO CUST DROP. IF CLAIM IS MADE FOR DAMAGE TO ROOF OR WEATHERHEAD- PGE IS RESPONSIBLE
|  |  | Completed | 1 | AFW DSP | 2021-07-13 15:40 |  | 2021-07-13 15:39 | 44391.4532 | 44391.4532 | 44391.4547 | 2.23 | 0.03 | 16.3 | -16.27 | 2.2 | 120 | -117.8 | 5.6 | -3.4 | W107518804 | 2 | UD | , | W112 | 0980 | [5 empty] | CONTRACT CREW SWITCHED
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 09:10 |  | 2021-07-14 09:04 | 44391.4559 | 44391.4932 | 44391.5141 | 83.82 | 53.8 | 16.3 | 37.5 | 30.02 | 27 | 3.02 | 5.6 | 24.42 | 3485052423 | 1 | AD | 17498 WOLF MOUNTAIN RD # B, GRASS VALLEY | 1050 | 0980 |  |  |  | SAP ID 100103358; CONTRACTOR ANDY REPORTING MIDDLE INSULATOR COMPROMISED AND SHIFTED OFF POLE; PLEASE SAFETY CHECK; CALL ANDY WITH ANY QUESTIONS 213-200-1370 |  | NO HAZARD
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:14 |  | 2021-07-07 09:36 | 44391.5686 | 44391.5848 | 44391.6227 | 77.89 | 23.42 | 16.3 | 7.12 | 54.47 | 35 | 19.47 | 20 | 34.47 | 1070550432 | 2 | AD | 11585 TAMMY WAY, GRASS VALLEY | 2220 | 2220 |  |  |  | EXC AXS OK; CUST CHRIS 916-778-7064; DIS/REC L4L 200 PNL CHG, INSP REQ; REP SRRQ 2092728553; NOTIF 121669612 |  | RECONNECTED
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:14 |  | 2021-07-06 14:05 | 44391.6228 | 44391.6295 | 44391.6493 | 38.1 | 9.65 | 16.3 | -6.65 | 28.45 | 35 | -6.55 | 20 | 8.45 | 1101228413 | 2 | AD | 20328 CASA LOMA DR, GRASS VALLEY | 2220 | 2220 |  |  |  | EXC - AXS OK; CTC Kevin Bryan, 530-575-1834, DIS/REC 200A TO 200A - OH PNL CHNG/ L4L; REP: A3JK 916-926-7486; TMAN TO VERIFY INSP / NOTIF #: 121542617 - OK TO SERVE |  | RECONNECTED
|  |  | Completed | 6 | 4APNWA1 | 2021-07-14 14:50 |  | 2021-07-13 08:29 | 44391.6499 | 44391.6739 | 44391.7006 | 73.04 | 34.67 | 16.3 | 18.37 | 38.37 | 35 | 3.37 | 20 | 18.37 | 1200962960 | 2 | AD | 15311 GARDEN BAR RD, GRASS VALLEY | 2220 | 2220 |  |  |  | GIVE TO SHADEGBF4:OTHER; |  | RECONNECTED
|  |  | Completed | 1 | OIS DSP | 2021-07-14 14:58 |  | 2021-07-14 14:57 | 44391.7092 | 44391.7626 | 44391.7955 | 124.27 | 76.87 | 16.3 | 60.57 | 47.4 | 32 | 15.4 | 31.1 | 16.3 | T005341875 | 0 | AD | 12546 GAYLE LN, NEVADA CITY | 9190 | 9190 |  |  |  | AXS-DOG XSTR-GAYLE PWR-Y TREEIN THE WIRES, GOOD CONDITION OF TREE, AXS OK ; BRANCH ON THE TOP AND SECONDARY POWER LINE, BRACH ST ILL ATTACHED TO POWER LINES |  | TREE ONNTREE
|  |  | Completed | 1 | AFW DSP | 2021-07-13 15:24 |  | 2021-07-13 15:24 | 44391.7957 | 44391.7957 | 44391.7962 | 0.82 | 0.02 | 16.3 | -16.28 | 0.8 | 120 | -119.2 | 5.6 | -4.8 | W105305602 | 2 | UD | , | W112 | 0980 | [5 empty] | CREW PUSHING OPUT TO 2100 AND WILL SWITCH THEMSELVES
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 07:41 |  | 2021-07-14 07:40 |  |  | 44391.3649 | [9 empty] | T005341265 | 1 | AD | 19831 NOATAK CANYON WAY, GRASS VALLEY | 9030 |  |  |  |  | AXS-OK XSTR-CASA LOMA PWR-I CUSTOMER WITHOUT POWER, METER STATUS SHOWS INDETERMINATE. PREVIOUS NOTES STATE PANEL WAS DAMAGED DUE TO CAR POLE ACCIDENT. CUSTOMER STATES PANEL IS FINE. PLS INVESTIGATE AND ADV CUSTOMER.
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Grass Valley | RYAN, RUSSELL | Completed | 2 | 4APNWA1 | 2021-07-14 13:03 |  | 2021-07-14 13:00 | 44391.5589 | 44391.5804 | 44391.5859 | 38.82 | 30.95 | 16.3 | 14.65 | 7.87 | 31 | -23.13 | 21.9 | -14.03 | 0996521882 | 1 | AD | 10231 GOLD DR, GRASS VALLEY | 1240 | 1320 |  |  |  | AXS-AXS OK XStr-SQUIRREL CREEK Pwr-Y BRANCH IS RESTING ON TOP LINE/POLE TO POLE/IN FRONT YARD CLOSE TO STREET |  | PINE BRANCH GROWN OVER SERVICES AND AWAC, NO HAZARDS
|  |  | Completed | 1 | AFW DSP | 2021-07-13 15:40 |  | 2021-07-13 15:39 |  |  | 44391.0257 | 127.23 | 76.58 | 16.3 | 60.28 | 50.65 | 120 | -69.35 | 0 | 50.65 | W107518801 | 2 | UD | , | W110 | W110
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 12:45 |  | 2021-07-14 12:44 |  |  | 44391.5415 | [9 empty] | T005341740 | 0 | AD | 10231 GOLD DR, GRASS VALLEY | 9190 |  |  |  |  | AXS-AXS OK XSTR-SQUIRREL CREEK PWR-Y BRANCH IS RESTING ON TOP LINE/POLE TO POLE/IN FRONT YARD CLOSE TO STREET
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Grass Valley | SHADE, BRIAN | Completed | 1 | AFW DSP | 2021-07-13 15:24 |  | 2021-07-13 15:24 | 44391.2128 | 44391.3523 | 44391.416 | 292.59 | 200.92 | 16.3 | 184.62 | 91.67 | 120 | -28.33 | 0 | 91.67 | W105305601 | 2 | UD | , | W110 | W110
|  |  | Completed |  | SAP DSP | 2021-07-13 22:56 |  | 2021-07-13 | 44391.4161 | 44391.4161 | 44391.4171 | 1.45 | 0.03 | 16.3 | -16.27 | 1.42 | 0 | 1.42 | 0 | 1.42 | S000765445 | 2 | UD | WOLF RD. 1 MO. NW/O HWY 49, Grass Valley | S108
|  |  | Completed | 1 | AFW DSP | 2021-07-13 15:40 |  | 2021-07-13 15:39 |  |  | 44391.0178 | 116.75 | 39.02 | 16.3 | 22.72 | 77.73 | 120 | -42.27 | 0 | 77.73 | W107518803 | 2 | UD | , | W110 | W110
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Grass Valley | TURNES, JOSEPH | Completed | 2 | 4APGBF4 | 2021-07-14 06:17 |  | 2021-07-06 10:05 | 44391.3329 | 44391.3431 | 44391.3623 | 42.22 | 14.67 | 16.3 | -1.63 | 27.55 | 30 | -2.45 | 15 | 12.55 | 0998200436 | 2 | AM | 13935 GLENN PINES RD, GRASS VALLEY | 2640 | 2640 |  |  |  | EXC - AXS OK; CTC Eric: 530-788-2871, DIS/REC 200A TO 200A - OH PNL CHG, L4L; REP: S0KA 530-401-4431; TMAN TO VERIFY INSP/ NOTIF #: 121638910 - OK TO SERVE |  | DISC FROM WEATHERHEAD AS WELL
|  |  | Completed | 6 | 4APGBF4 | 2021-07-14 07:49 |  | 2021-07-07 07:47 | 44391.3631 | 44391.3829 | 44391.4011 | 54.72 | 28.45 | 16.3 | 12.15 | 26.27 | 30 | -3.73 | 15 | 11.27 | 1324959768 | 2 | AM | 18050 FOXTAIL DR, PENN VALLEY | 2640 | 2640 |  |  |  | EXC - AXS OK; CTC, Jeff; 530-559-9173; DIS/REC 200A TO 200A - UG PNL CHG, L4L; REP: ALFI 916 618-3201; TMAN TO VERIFY INSP/ NOTIF # 121470816: - OK TO SERVE |  | D
|  |  | Completed | 4 | 4APGBF4 | 2021-07-14 07:49 |  | 2021-07-01 15:47 | 44391.4013 | 44391.4145 | 44391.4321 | 44.35 | 18.98 | 16.3 | 2.68 | 25.37 | 30 | -4.63 | 15 | 10.37 | 1304762859 | 2 | AM | 16106 HILLAIRE RD, ROUGH AND RE | 2640 | 2640 |  |  |  | EXC - AXS OK; CTC Melanie Duggan, 530-274-3671, DISC/REC 150A TO 200A - OH PNL CHNG/ UPG - TRANSFER METER; REP: A3JK 916-926-7486; TMAN TO VERIFY INSP / NOTIF #:121190261 - OK TO SERVE |  | D
|  |  | Completed | 4 | 4APGBF4 | 2021-07-14 10:48 |  | 2021-07-12 10:12 | 44391.4535 | 44391.4699 | 44391.4852 | 45.63 | 23.6 | 16.3 | 7.3 | 22.03 | 31 | -8.97 | 21.9 | 0.13 | 1126475184 | 2 | AM | 16189 INDIAN SPRINGS RANCH R, GRASS VALLEY | 1240 | 1320 |  |  |  | No Access or Safety Issues; REQUESTING TREE TRIMMING/SERVICE DROP/INSPECTION REQUESTED/LEW TURNER |  | WHY WAS THIS TAG EVEN CREATED? CUST WANTED TO SCHEDULE A SERVICE DROP FOR THE 26TH. WHY WASTE A T-MANS TIME ON THE 14TH TO, I DONT KNOW, CONFIRM IT CAN BE DONE?
|  |  | Completed | 1 | AFW DSP | 2021-07-13 15:40 |  | 2021-07-13 15:39 | 44391.5004 | 44391.5135 | 44391.5139 | 19.55 | 18.95 | 16.3 | 2.65 | 0.6 | 120 | -119.4 | 5.6 | -5 | W107518802 | 2 | UD | , | W112 | 0980
|  |  | Completed | 1 | OIS DSP | 2021-07-14 12:44 |  | 2021-07-14 12:43 | 44391.5317 | 44391.5437 | 44391.5698 | 54.79 | 17.32 | 16.3 | 1.02 | 37.47 | 32 | 5.47 | 16.6 | 20.87 | T005341739 | 0 | AD | 11317 E BENNETT RD, GRASS VALLEY | 9190 | 9320 |  |  |  | AXS-GATE XSTR-BRUNSWICK HWY PWR-Y CIA;P/JOE NEWLY INSTALLED POWER POLE SETTLED CAUSING LOOSE GUY WIRE, TRUCK JUST CLIPPED PH LIN E NOW POLE LEANING, AND GUY WIRE LOOSE/DAMAGED?;AXS GATE AFTER 10 PM |  | RECENTLY SET POLE HAS SLACKED DG s IN 2 DIRECTIONS CUST STATES POLE SETTLED AFTER PHONE COMPANY PULLED THE BUTT AND TRANSFERED THEIR WIRE. CUST ALSO CONTACTED ATT ABOUT THE HEIGHT OF THEIR WIRE ACROSS HIS COMERCIAL PROPERTY CONTACTED CONS
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:17 |  | 2021-07-06 10:06 | 44391.6151 | 44391.628 | 44391.6655 | 72.58 | 18.63 | 16.3 | 2.33 | 53.95 | 35 | 18.95 | 20 | 33.95 | 0995509643 | 2 | AD | 13935 GLENN PINES RD, GRASS VALLEY | 2220 | 2220 |  |  |  | EXC - AXS OK; CTC Eric: 530-788-2871, DIS/REC 200A TO 200A - OH PNL CHG, L4L; REP: S0KA 530-401-4431; TMAN TO VERIFY INSP/ NOTIF #: 121638910 - OK TO SERVE |  | REC
|  |  | Completed | 4 | 4APKERA | 2021-07-14 16:01 |  | 2021-07-01 15:50 | 44391.6702 | 44391.6821 | 44391.6987 | 41 | 17.18 | 16.3 | 0.88 | 23.82 | 35 | -11.18 | 20 | 3.82 | 1303582666 | 2 | AD | 16106 HILLAIRE RD, ROUGH AND RE | 2220 | 2220 |  |  |  | EXC - AXS OK; CTC Melanie Duggan, 530-274-3671, DISC/REC 150A TO 200A - OH PNL CHNG/ UPG - TRANSFER METER; REP: A3JK 916-926-7486; TMAN TO VERIFY INSP / NOTIF #:121190261 - OK TO SERVE |  | REC
|  |  | Completed | 6 | 4APGBF4 | 2021-07-14 10:45 |  | 2021-07-07 07:47 | 44391.6989 | 44391.7104 | 44391.7571 | 83.93 | 16.65 | 16.3 | 0.35 | 67.28 | 35 | 32.28 | 20 | 47.28 | 1326975321 | 2 | AD | 18050 FOXTAIL DR, PENN VALLEY | 2220 | 2220 |  |  |  | EXC - AXS OK; CTC, Jeff; 530-559-9173; DIS/REC 200A TO 200A - UG PNL CHG, L4L; REP: ALFI 916 618-3201; TMAN TO VERIFY INSP/ NOTIF # 121470816: - OK TO SERVE | Turnes worked am since Ryan was on a half day rest | REC
Marysville
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
6 | Marysville | BARRIE, JESSE | Completed | 2 | 4APGBF4 | 2021-07-14 06:21 |  | 2021-07-08 12:20 | 44391.3153 | 44391.3386 | 44391.3797 | 92.68 | 33.58 | 11.9 | 21.68 | 59.1 | 30 | 29.1 | 15 | 44.1 | 1356118907 | 2 | AM | 1124 MURPHY RD, OLIVEHURST | 2640 | 2640 |  |  |  | EXC - AXS OK; CTC: Valerie: 916-314-7253: DIS/REC 125A TO 200A - OH PNL UPG; REP: ALFI 916 618-3201; TMAN TO VERIFY INSP / NOTIF #: 121574526: - OK TO SERVE |  | DISCONN
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:22 |  | 2021-07-07 09:41 | 44391.3798 | 44391.3892 | 44391.4097 | 42.98 | 13.55 | 11.9 | 1.65 | 29.43 | 25 | 4.43 | 20 | 9.43 | 1233817760 | 2 | AD | 4781 WESTERN AVE, OLIVEHURST | 2094 | 2094 |  |  |  | 2-TMAN NEEDED, XRING RD, 85' 1/O TPX , NEED PART 4 FOR COP ATTACHMENT. 1P 200A 120/240V E1, CTC JOGINDER DULAI 530-300-4550 NOT 120814016 PM 35250097 | original to Barrie, dup to Brown | INSTALLED SERVICE AND SET METER
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 09:25 |  | 2021-07-14 09:21 | 44391.4113 | 44391.4198 | 44391.4389 | 39.71 | 12.28 | 11.9 | 0.38 | 27.43 | 31 | -3.57 | 37.4 | -9.97 | 0002908384 | 0 | AD | UNKNOWN PREMISES DO NOT CHANGE, MARYSVILLE | 1240 | 1057 |  |  |  | AX UNK,CALLER MIKE REPORTING CRACKED LID ON PGE FIBERGLASS BOX LOCATED AT 3RD ST AND D ST IN FRONT OF THE LIBRARY IN CITY OF MARYSVILLE |  | replaced secondary lid
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:21 |  | 2021-07-08 12:22 | 44391.6683 | 44391.6805 | 44391.7311 | 90.45 | 17.6 | 11.9 | 5.7 | 72.85 | 35 | 37.85 | 20 | 52.85 | 1355630755 | 2 | AD | 1124 MURPHY RD, OLIVEHURST | 2220 | 2220 |  |  |  | EXC - AXS OK; CTC: Valerie: 916-314-7253: DIS/REC 125A TO 200A - OH PNL UPG; REP: ALFI 916 618-3201; TMAN TO VERIFY INSP / NOTIF #: 121574526: - OK TO SERVE |  | reconnect
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 10:10 |  | 2021-07-14 10:10 |  |  | 44391.4252 | [9 empty] | T005341540 | 2 | AD | STRLIGHT 1155 JONES BAR TRAIL, OLIVEHURST | 9500
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Marysville | BROWN, TYLER | Completed | 2 | 4APGBF4 | 2021-07-14 06:22 |  | 2021-07-07 09:41 | 44391.3352 | 44391.3751 | 44391.4105 | 108.36 | 57.43 | 11.9 | 45.53 | 50.93 | 25 | 25.93 | 5.6 | 45.33 | X316147926 | 2 | AD | 4781 WESTERN AVE, OLIVEHURST | 2094 | 0980 |  |  |  | 2-TMAN NEEDED, XRING RD, 85' 1/O TPX , NEED PART 4 FOR COP ATTACHMENT. 1P 200A 120/240V E1, CTC JOGINDER DULAI 530-300-4550 NOT 120814016 PM 35250097 | original to Barrie, dup to Brown & dup to McBride | ASSISTED JESSE BARRIE
|  |  | Completed | 1 | OIS DSP | 2021-07-14 11:15 |  | 2021-07-14 11:15 | 44391.4748 | 44391.5049 | 44391.5374 | 90.15 | 43.23 | 11.9 | 31.33 | 46.92 | 52 | -5.08 | 0 | 46.92 | T005341641 | 1 | AD | GARDEN HWY ES .70MI, NICOLAUS | 9150 | 9221 |  |  |  | AXS-OK XSTR-GRDE HWY PWR-Y CIA; 480 VOLT PUMP STATION, ONE LEG DEAD PER DAVID WILLIAMS, 530-632-9342; CALL AND CAN MEET OUT THER E |  | PWR GOOD TO METER AND CT'S. NO POWER FROM CUSTOMER SWITCH TO CUST OWNED TX. OPENED FUSES WILL CALL BACK FOR RECCONECT.
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 12:56 |  | 2021-07-14 12:53 | 44391.5391 | 44391.5391 | 44391.5406 | 2.2 | 0.03 | 11.9 | -11.87 | 2.17 | 30 | -27.83 | 20 | -17.83 | 1113737576 | 1 | AD | GARDEN HWY ES .70MI N/SANKEY, NICOLAUS | 2640 | 2641 |  |  |  | give to Brown |  | OPENED FUSES SO CUSTOMER COULD REPAIR MAIN BREAKER
|  |  | Completed | 1 | OIS DSP | 2021-07-14 11:18 |  | 2021-07-14 11:17 | 44391.5406 | 44391.5576 | 44391.6556 | 165.6 | 24.4 | 11.9 | 12.5 | 141.2 | 60 | 81.2 | 54 | 87.2 | T005341643 | 2 | AD | STRLIGHT 1155 JONES BAR TRAIL, OLIVEHURST | 9500 | 9500 | [5 empty] | REPLACED ST LIGHT WITH 43W LED. ONLY OPTION IN YARD
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Marysville | HOWARD, JIMMY | Completed | 2 | 4APGBF4 | 2021-07-14 06:20 |  | 2021-07-01 14:41 | 44391.3165 | 44391.3541 | 44391.3601 | 62.8 | 54.13 | 11.9 | 42.23 | 8.67 | 30 | -21.33 | 15 | -6.33 | 1142572028 | 2 | AM | 150 WILSON AVE, YUBA CITY | 2640 | 2640 |  |  |  | EXC - AXS OK; CTC Robert Witzel: 530-513-1619, DIS/REC 100A TO 200A - OH PNL UPG; RELOCATING PNL TO EXTERIOR, WEATHER MUST STAY IN SAME POSITION; REP: CYCC 530-228-6873; TMAN TO VERIFY INSP/ NOTIF #:121625918 - OK TO SERVE |  | disconnected service
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 08:37 |  | 2021-07-14 08:33 | 44391.3603 | 44391.3676 | 44391.4075 | 68.05 | 10.58 | 11.9 | -1.32 | 57.47 | 29 | 28.47 | 5.6 | 51.87 | 1069699645 | 0 | AD | 1988 TAYLOR ST, YUBA CITY | 1160 | 0980 |  |  |  | No Access or Safety Issues; BACK HOE HIT PGE WIRE TAKING OUT POWER. WIRE ACCROSS THE STREET PROBABLY POLE TO POLE. OUTAGE TICKET. . XST : WALTON. |  | Created outage tag
|  |  | Completed | 1 | OIS DSP | 2021-07-14 09:46 |  | 2021-07-14 09:45 | 44391.4076 | 44391.4077 | 44391.4143 | 9.7 | 0.15 | 11.9 | -11.75 | 9.55 | 45 | -35.45 | 0 | 9.55 | T005341507 | 0 | AD | 1988 TAYLOR ST, YUBA CITY | 9062 | 9002 |  |  |  | A:UNK;X:UNK;R:GIVE TO HOWARD;NO ACCESS OR SAFETY ISSUES; BACK HOE HIT PGE WIRE TAKING OUT POWER. WIRE ACCROSS THE STREET PROBA BLY POLE TO POLE. OUTAGE TICKET. . XST : WALT, PWR-I |  | Need crew to make repairs to secondary dig in. Crew can replace sweethearts in splice box and get one customer hot while repairs are made to service. Need gas crew
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 11:57 |  | 2021-07-14 11:56 | 44391.4979 | 44391.5009 | 44391.5354 | 53.98 | 4.3 | 11.9 | -7.6 | 49.68 | 31 | 18.68 | 21.9 | 27.78 | 1273367336 | 1 | AD | 655 W ONSTOTT RD, YUBA CITY | 1240 | 1320 |  |  |  | give to Howard |  | Checked voltage OK at panel
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:20 |  | 2021-07-01 14:41 | 44391.5767 | 44391.5842 | 44391.6185 | 60.2 | 10.8 | 11.9 | -1.1 | 49.4 | 35 | 14.4 | 20 | 29.4 | 1147173342 | 2 | AD | 150 WILSON AVE, YUBA CITY | 2220 | 2220 |  |  |  | EXC - AXS OK; CTC Robert Witzel: 530-513-1619, DIS/REC 100A TO 200A - OH PNL UPG; RELOCATING PNL TO EXTERIOR, WEATHER MUST STAY IN SAME POSITION; REP: CYCC 530-228-6873; TMAN TO VERIFY INSP/ NOTIF #:121625918 - OK TO SERVE |  | reconnected service
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 08:28 |  | 2021-07-14 08:27 |  |  | 44391.3604 | [9 empty] | T005341344 | 1 | AD | 1988 TAYLOR ST, YUBA CITY | 9030 |  |  |  |  | SMART MTR AUTO-GENERATED TAGAXS O K NO DGS
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Marysville | JOHNSON, RYAN | Completed | 1 | OIS DSP | 2021-07-14 15:06 |  | 2021-07-14 15:05 | 44391.6301 | 44391.6514 | 44391.7172 | 125.33 | 30.58 | 11.9 | 18.68 | 94.75 | 43 | 51.75 | 0 | 94.75 | T005341889 | 0 | AD | RD ZZ ES, BUTTE CITY | 9040 | 9002 |  |  |  | SMART MTR AUTO-GENERATED TAG |  | car pole accident c-6592 and pole on the ground, no wire down
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Marysville | LAFFOND, DAN | Completed | 1 | OIS DSP | 2021-07-14 11:27 |  | 2021-07-14 11:27 | 44391.478 | 44391.5777 | 44391.611 | 191.54 | 143.62 | 11.9 | 131.72 | 47.92 | 30 | 17.92 | 5.6 | 42.32 | T005341656 | 0 | AD | UNKNOWN LAT;39.208901 LON;-121, COLUSA | 9250 | 0930 |  |  |  | AXS-OK POLE TO POLE SERVICE LINE ON GROUND; SEEMS TO BE DISCONNCTED/NOT LIVE; CHARDED BRANCHES AROUND; |  | idle line. no hazard.
|  |  | Completed | 1 | OIS DSP | 2021-07-14 15:02 |  | 2021-07-14 15:02 | 44391.642 | 44391.679 | 44391.7489 | 153.97 | 53.25 | 11.9 | 41.35 | 100.72 | 43 | 57.72 | 0 | 100.72 | T005341882 | 0 | AD | RD ZZ ES, BUTTE CITY | 9040 | 9002 |  |  |  | SMART MTR AUTO-GENERATED TAG |  | crew to replace 50/2 pole on co. rd. z in butte city
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Marysville | LOMELI, JAMES | Completed | 2 | 4APGBF4 | 2021-07-14 11:27 |  | 2021-07-14 11:24 | 44391.4995 | 44391.6535 | 44391.6553 | 224.33 | 221.78 | 11.9 | 209.88 | 2.55 | 15 | -12.45 | 10 | -7.45 | 0998881635 | 1 | AD | 26120 COUNTY RD 6, DUNNIGAN | 2412 | 2412 |  |  |  | give to Lomeli & dup to Johnson;INSTALLED RVM. VLTS AT TIME 495-493-493. WILL FOLLOW UP WITH REMOVAL |  | PULLED DATA ON RVM AND SENT TO ENGINEERING.
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Marysville | MARINO, TONY | Completed | 4 | 4APGBF4 | 2021-07-14 06:20 |  | 2021-07-02 15:36 | 44391.486 | 44391.5297 | 44391.5849 | 142.42 | 62.82 | 11.9 | 50.92 | 79.6 | 35 | 44.6 | 20 | 59.6 | 3446540924 | 2 | AD | 12607 RICES CROSSING RD, OREGON HOUSE | 2220 | 2220 |  |  |  | EXC AXS OK; CUST JAMES 415- 425-1032; DIS/REC -CUSTOMER REQ WORK AT METER 1010237111, NO INSP REQUIRED; REP SRRQ 2092728553/; NOTIF 121630207 |  | made reconnect chk pwr ok
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 14:14 |  | 2021-07-14 13:58 | 44391.6558 | 44391.6559 | 44391.6748 | 27.37 | 0.1 | 11.9 | -11.8 | 27.27 | 31 | -3.73 | 22.6 | 4.67 | 0001026031 | 1 | AD | UNKNOWN PREMISES DO NOT CHANGE, LOMA RICA | 1240 | 1056 |  |  |  | BROKEN POLE-NON HAZARDOUS LIVE STOCK AROUND,CAN FALL INTO ST ON FRUITLAND AXS K;Addr=ACROSS FROM PUBLIC WORKS FRUITLAND/VIRGINIA;Contact Name=MELISSA GALEA;Contact Phone=(530) 300-1404; WOOD POLE (OLDER) POSS. HIT BY A CAR |  | phone pole was hit NOT pge chk safe at this time
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Marysville | MCBRIDE, MIKE | Completed | 2 | 4APGBF4 | 2021-07-14 08:27 |  | 2021-07-07 09:41 | 44391.3558 | 44391.3836 | 44391.4122 | 81.28 | 40.03 | 11.9 | 28.13 | 41.25 | 25 | 16.25 | 55 | -13.75 | X316148180 | 2 | AD | 4781 WESTERN AVE, OLIVEHURST | 2094 | 2120 |  |  |  | 2-TMAN NEEDED, XRING RD, 85' 1/O TPX , NEED PART 4 FOR COP ATTACHMENT. 1P 200A 120/240V E1, CTC JOGINDER DULAI 530-300-4550 NOT 120814016 PM 35250097 | original to Barrie, dup to Brown | ok
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:07 |  | 2021-07-08 10:14 | 44391.4123 | 44391.4378 | 44391.4696 | 82.43 | 36.65 | 11.9 | 24.75 | 45.78 | 25 | 20.78 | 20 | 25.78 | 1948008508 | 2 | AD | 1790 STINSON WY, PLUMAS LAKE | 2094 | 2094 |  |  |  | CON/SET; INSP OK--LOT 40 ; CONTACT: Jeff Minasian 916-542-3780, SUBDIVISION: Woodside Village 2 AKA Cresleigh Homes Meadows |  | ok
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:07 |  | 2021-07-08 10:18 | 44391.4697 | 44391.4697 | 44391.4806 | 15.64 | 0.02 | 11.9 | -11.88 | 15.62 | 25 | -9.38 | 20 | -4.38 | 2300628411 | 2 | AD | 1786 STINSON WY, PLUMAS LAKE | 2094 | 2094 |  |  |  | CON/SET; INSP OK--LOT 41 ; CONTACT: Jeff Minasian 916-542-3780, SUBDIVISION: Woodside Village 2 AKA Cresleigh Homes Meadows |  | ok
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:07 |  | 2021-07-08 10:09 | 44391.4806 | 44391.4879 | 44391.4888 | 11.75 | 10.47 | 11.9 | -1.43 | 1.28 | 25 | -23.72 | 20 | -18.72 | 6408817205 | 2 | AD | 1796 STINSON WY, PLUMAS LAKE | 2094 | 2094 |  |  |  | CON/SET; INSP OK--LOT 39 ; CONTACT: Jeff Minasian 916-542-3780, SUBDIVISION: Woodside Village 2 AKA Cresleigh Homes Meadows |  | ok
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:07 |  | 2021-07-08 10:02 | 44391.4889 | 44391.4889 | 44391.5069 | 26.04 | 0.02 | 11.9 | -11.88 | 26.02 | 25 | 1.02 | 20 | 6.02 | 8189256304 | 2 | AD | 1800 STINSON WY, PLUMAS LAKE | 2094 | 2094 |  |  |  | CON/SET; INSP OK--LOT 38; CONTACT: Jeff Minasian 916-542-3780, SUBDIVISION: Woodside Village 2 AKA Cresleigh Homes Meadows |  | ok
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:07 |  | 2021-07-08 09:53 | 44391.5071 | 44391.5081 | 44391.511 | 5.65 | 1.4 | 11.9 | -10.5 | 4.25 | 25 | -20.75 | 20 | -15.75 | 9183882533 | 2 | AD | 1806 STINSON WY, PLUMAS LAKE | 2094 | 2094 |  |  |  | CON/SET; INSP OK--LOT 37; CONTACT: Jeff Minasian 916-542-3780, SUBDIVISION: Woodside Village 2 AKA Cresleigh Homes Meadows |  | gk,j
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 12:44 |  | 2021-07-14 12:42 | 44391.5345 | 44391.5489 | 44391.5693 | 50.16 | 20.78 | 11.9 | 8.88 | 29.38 | 35 | -5.62 | 20 | 9.38 | 1230700422 | 1 | AD | BEAR RIVER DR S/S 1SPN W/BR, WHEATLAND | 2220 | 2220 |  |  |  | give to McBride |  | ok
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 06:53 |  | 2021-07-14 06:52 |  |  | 44391.4165 | [9 empty] | T005341209 | 2 | AD | STRLIGHT 1155 JONES BAR TRAIL, MARYSVILLE | 9500 | [5 empty] | Pleasant Grove
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 10:12 |  | 2021-07-14 10:12 |  |  | 44391.4704 | [9 empty] | T005341544 | 2 | AD | STRLIGHT 1155 JONES BAR TRAIL, OLIVEHURST | 9500
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 11:14 |  | 2021-07-14 11:13 |  |  | 44391.4691 | [9 empty] | T005341639 | 1 | AD | GARDEN HWY ES .70MI, NICOLAUS | 9150 |  |  |  |  | AXS-OK XSTR-GRDE HWY PWR-Y CIA; 480 VOLT PUMP STATION, ONE LEG DEAD PER DAVID WILLIAMS, 530-632-9342; CALL AND CAN MEET OUT THER E
Orland
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
6 | Orland | AGEE, BOBBY | Completed | 2 | 4APNWA1 | 2021-07-14 06:56 |  | 2021-06-30 14:51 | 44391.3225 | 44391.3627 | 44391.3854 | 90.67 | 57.92 | 17.2 | 40.72 | 32.75 | 30 | 2.75 | 15 | 17.75 | 0704590311 | 2 | AM | 280 N CULVER ST, WILLOWS | 2640 | 2640 |  |  |  | EXC- AXS OK; CTC: MICHEAL MARTINDALE @ 530-519-4498 OH DISC/RECO 100A - 200A OH PNL UPG, NO ADDED LOAD; REP: SBJ5 916-214-7283; TMAN TO VERIFY INSP-CUST TO REMV DOWNSPOUT AND SPIGOT- NOTIF#: 121626082- OK TO SERVE |  | N
|  |  | Completed | 1 | OIS DSP | 2021-07-14 08:09 |  | 2021-07-14 08:09 | 44391.3868 | 44391.4347 | 44391.4826 | 137.98 | 68.98 | 17.2 | 51.78 | 69 | 36 | 33 | 31.1 | 37.9 | T005341319 | 0 | AD | 3915 LAGODA LEESVILLE RD, STONYFORD | 9010 | 9190 |  |  |  | AXS-OK XSTR-COOK SPRINGS RD PWR-Y LEANING POLE LARGE OAK TREE BRANCH FELL INTO GUIDE WIRE AND IS HANGING ON POLE LEANING BADLY N O SPARKS NO INJURY VISUAL ACROSS ST FROMBIG WINDMILL |  | N
|  |  | Completed | 1 | OIS DSP | 2021-07-14 11:30 |  | 2021-07-14 11:29 | 44391.4935 | 44391.5135 | 44391.5408 | 68.12 | 28.87 | 17.2 | 11.67 | 39.25 | 43 | -3.75 | 16.6 | 22.65 | T005341659 | 1 | AD | RD 62 SS/ W/RD D, WILLOWS | 9040 | 9320 |  |  |  | AXS-DOG XSTR-62 PWR-Y CIA//AG PUMP - COMPLETE OUTAGE; CONTACT: RUTHANNE SOETH. BORDER COLLIE |  | Brkr
|  |  | Completed | 1 | OIS DSP | 2021-07-14 11:24 |  | 2021-07-14 11:23 | 44391.5409 | 44391.5409 | 44391.5415 | 0.9 | 0.05 | 17.2 | -17.15 | 0.85 | 30 | -29.15 | 16.6 | -15.75 | T005341653 | 1 | AD | 975 ROAD-D, WILLOWS | 9030 | 9320 |  |  |  | AXS-DOG XSTR-62 PWR-Y COMPLTE OUTAGE; CONTACT: RUTHANNE SOETH. BORDER COLLIE |  | Brkr
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 07:30 |  | 2021-07-14 07:25 | 44391.5991 | 44391.5992 | 44391.6054 | 8.98 | 0.03 | 17.2 | -17.17 | 8.95 | 31 | -22.05 | 21.9 | -12.95 | 0657343589 | 1 | AD | 7837 ROAD 41, GLENN | 1240 | 1320 |  |  |  | Other Access/LOW WIRE ; SE CORNER OF COUNTY RD W AND COUNTY RD 41 GLENN 95943 ENTR ON 41..... SGLE TRAVEL TRILER 42 FT / NOT OVER ST OR THRU TREES / OFF INSULATOR / 530) 519-5153 FRANK |  | K
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:56 |  | 2021-06-30 14:52 | 44391.6216 | 44391.6217 | 44391.652 | 43.68 | 0.03 | 17.2 | -17.17 | 43.65 | 35 | 8.65 | 20 | 23.65 | 0702599716 | 2 | AD | 280 N CULVER ST, WILLOWS | 2220 | 2220 |  |  |  | EXC- AXS OK; CTC: MICHEAL MARTINDALE @ 530-519-4498 OH DISC/RECO 100A - 200A OH PNL UPG, NO ADDED LOAD; REP: SBJ5 916-214-7283; TMAN TO VERIFY INSP-CUST TO REMV DOWNSPOUT AND SPIGOT- NOTIF#: 121626082- OK TO SERVE |  | K
|  |  | Completed | 1 | OIS DSP | 2021-07-14 17:35 |  | 2021-07-14 17:34 | 44391.7581 | 44391.8147 | 44391.8228 | 93.18 | 81.5 | 17.2 | 64.3 | 11.68 | 52 | -40.32 | 54.9 | -43.22 | T005341993 | 1 | AD | HWY 32 NS OPP SAC AVE, HAMILTON CIT | 9150 | 9140 |  |  |  | AXS-NONE XSTR- PWR-Y CALLER ADV HAVING HI/LOW VOLTAGE |  | Traffic
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 15:00 |  | 2021-07-14 14:59 |  |  | 44391.6263 | [9 empty] | T005341877 | 0 | AD | UNKNOWN CO RD Z S OF STE RTE 1, WILLOWS | 9250 |  |  |  |  | AXS-OK CHP , FD ENROUTE HAY TRACTOR PULLED LINES DOWN GRASS FIRE ONSITE ETA REQ WHEN AVLBP#120254958
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Orland | GARRETSON, GREG | Completed | 2 | 4APNWA1 | 2021-07-14 10:31 |  | 2021-07-14 10:21 | 44391.4452 | 44391.4527 | 44391.4809 | 51.43 | 10.78 | 17.2 | -6.42 | 40.65 | 31 | 9.65 | 27.8 | 12.85 | 0000802107 | 1 | AD | UNKNOWN PREMISES DO NOT CHANGE, ORLAND | 1240 | 1000 |  |  |  | No Access or Safety Issues;Addr=15 MILL ST, ORLAND, CA, 95963;Xstr1=MILL ST;Xstr2=EAST ST;Landmark=UNK;Contact Name=BEN ALCANTRA;Contact Phone=(530) 517-2595;WIRES GROWING THROUGH TREE BRANCH, SECONDARY WIRE. |  | broken neutral from tree branch - repaired/pwr ok
Oroville
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
6 | Oroville | MAYS, SEAN | Completed | 1 | OIS DSP | 2021-07-14 08:51 |  | 2021-07-14 08:50 | 44391.3753 | 44391.4158 | 44391.4454 | 100.95 | 58.25 | 11.4 | 46.85 | 42.7 | 51 | -8.3 | 16.6 | 26.1 | T005341398 | 1 | AD | 6355 LINCOLN BLVD SPC 3, OROVILLE | 9140 | 9320 |  |  |  | AXS-2 DOGS-TERRIER/SNAUSER NO LK G XSTR-UNK PWR-Y ENTIRE HSE-THEY FLICKER ALL THE TIME-LOW AND HIGH VOLTAGE-FLUCTUATING |  | everything is ok
|  |  | Completed | 1 | OIS DSP | 2021-07-14 14:11 |  | 2021-07-14 14:10 | 44391.6238 | 44391.6238 | 44391.6357 | 17.23 | 0.03 | 11.4 | -11.37 | 17.2 | 30 | -12.8 | 16.6 | 0.6 | T005341827 | 0 | AD | 5036 LARKIN RD, OROVILLE | 9250 | 9320 |  |  |  | AXS-OK XSTR- PWR-I CAVIN KRATER WHO LIVES @ 5038 LARKIN RD CALLD TO REPORT DOWN WIRE IN FRONT OF 5036 LARKIN RD; POLE TO HOUSE |  | fille out tag on inspect app
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Oroville | MENZEL, KILE | Completed | 1 | AFW DSP | 2021-07-12 13:36 |  | 2021-07-12 13:36 | 44391.2834 | 44391.3251 | 44391.372 | 127.57 | 59.95 | 11.4 | 48.55 | 67.62 | 120 | -52.38 | 0 | 67.62 | W107699905 | 2 | UD | , | W110 | W110
|  |  | Completed | 1 | OIS DSP | 2021-07-14 10:57 |  | 2021-07-14 10:56 | 44391.4577 | 44391.4629 | 44391.4841 | 38.02 | 7.45 | 11.4 | -3.95 | 30.57 | 30 | 0.57 | 16.6 | 13.97 | T005341611 | 0 | AD | 474 JUSTESON AVE, GRIDLEY | 9250 | 9320 |  |  |  | AXS-AXS OK XSTR-W BRIGSLEY RD PWR-I POLE TO POLE; |  | secondary span guy down, unknown how, repaired
|  |  | Completed | 1 | AFW DSP | 2021-07-12 13:36 |  | 2021-07-12 13:36 | 44391.4842 | 44391.493 | 44391.5287 | 64.15 | 12.6 | 11.4 | 1.2 | 51.55 | 120 | -68.45 | 0 | 51.55 | W107699906 | 2 | UD | , | W112 | W112
|  |  | Cancelled |  | WO DSP |  |  | 2021-07-14 09:18 |  |  | 44391.5594 | [9 empty] | 1545112377 | 2 | AM | 21 LONGMAN LN, OROVILLE | 2640 |  |  |  |  | EXC - AXS OK; CTC Jennifer: 847-693-4427, DIS/REC 200A TO 200A - OH PNL CHG, L4L; REP: S0KA 530-401-4431; TMAN TO VERIFY INSP/ NOTIF #: 121598774 - OK TO SERVE
|  |  | Cancelled |  | WO DSP |  |  | 2021-07-14 09:20 |  |  | 44391.5596 | [9 empty] | 1548005106 | 2 | AD | 21 LONGMAN LN, OROVILLE | 2220 |  |  |  |  | EXC - AXS OK; CTC Jennifer: 847-693-4427, DIS/REC 200A TO 200A - OH PNL CHG, L4L; REP: S0KA 530-401-4431; TMAN TO VERIFY INSP/ NOTIF #: 121598774 - OK TO SERVE
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Oroville | SPARKS, MARTY | Completed | 1 | AFW DSP | 2021-07-12 13:36 |  | 2021-07-12 13:36 | 44391.2949 | 44391.3326 | 44391.3737 | 113.39 | 54.32 | 11.4 | 42.92 | 59.07 | 120 | -60.93 | 0 | 59.07 | W107699903 | 2 | UD | , | W110 | W110
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:53 |  | 2021-07-13 11:07 | 44391.374 | 44391.3741 | 44391.3767 | 3.85 | 0.07 | 11.4 | -11.33 | 3.78 | 30 | -26.22 | 20 | -16.22 | 6384448742 | 2 | AM | CLARDY RD SS, GRIDLEY | 2640 | 2641 |  |  |  | CIA AXS OK, BRSC, TEMP DISC/RECONN. FOR PANEL WORK ONLY. CONTACT JASBIR 530+570+8769 |  | completed
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:53 |  | 2021-07-13 11:10 | 44391.4568 | 44391.4603 | 44391.4716 | 21.29 | 5.12 | 11.4 | -6.28 | 16.17 | 35 | -18.83 | 20 | -3.83 | 6381382250 | 2 | PM | CLARDY RD SS, GRIDLEY | 2220 | 2220 |  |  |  | CIA/ AXS OK, BRSC, RECONNECT, PANEL WORK. CONTACT JASPBIR 530-570-8769 |  | Complete
|  |  | Completed | 1 | AFW DSP | 2021-07-12 13:36 |  | 2021-07-12 13:36 | 44391.4717 | 44391.4932 | 44391.5299 | 83.85 | 31 | 11.4 | 19.6 | 52.85 | 120 | -67.15 | 0 | 52.85 | W107699904 | 2 | UD | , | W112 | W112
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 10:46 |  | 2021-07-14 10:45 |  |  | 44391.4559 | [9 empty] | T005341592 | 0 | AD | 474 JUSTESON AVE, GRIDLEY | 9250 |  |  |  |  | AXS-AXS OK XSTR-W BRIGSLEY RD PWR-I POLE TO POLE;
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Oroville | WOODMANSEE, MATTHEW | Completed | 1 | OIS DSP | 2021-07-14 19:41 |  | 2021-07-14 19:41 | 44391.8451 | 44391.8611 | 44391.8731 | 40.36 | 23.03 | 11.4 | 11.63 | 17.33 | 30 | -12.67 | 5.6 | 11.73 | T005342056 | 1 | AD | 85 TUSCAN VILLA DR APT 75, OROVILLE | 9030 | 0980 |  |  |  | , PWR-Y |  | checked pwr ok
Placerville
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
6 | Placerville | CURTIS, MARK | Completed | 1 | AFW DSP | 2021-07-13 14:18 |  | 2021-07-13 14:17 | 44391.2145 | 44391.2593 | 44391.3542 | 201.2 | 64.53 | 11 | 53.53 | 136.67 | 120 | 16.67 | 0 | 136.67 | W107756703 | 2 | UD | , | W110 | W110
|  |  | Completed | 1 | OIS DSP | 2021-07-14 11:33 |  | 2021-07-14 11:32 | 44391.4842 | 44391.5229 | 44391.5624 | 112.6 | 55.62 | 11 | 44.62 | 56.98 | 51 | 5.98 | 16.6 | 40.38 | T005341662 | 1 | AD | 4300 YEW WOODS WAY, CAMINO | 9140 | 9320 |  |  |  | AXS-AX-OK XSTR- PWR-Y AT,T TECH WILSON,DAVE 916-761-3624; HAS STATED LIGHTING ARESTOR OR CRACKED INSULATOR IS CAUSING INTERNET O UTAGES IN THE AREA; |  | CONTACTED COMM TECH TO HELP LOCATE RTVI ISSUE IN AREA.
|  |  | Completed | 1 | OIS DSP | 2021-07-14 15:46 |  | 2021-07-14 15:45 | 44391.6621 | 44391.684 | 44391.6996 | 53.98 | 31.53 | 11 | 20.53 | 22.45 | 32 | -9.55 | 16.6 | 5.85 | T005341931 | 0 | AD | 1950 SUNDOWN TRL, PLACERVILLE | 9190 | 9320 |  |  |  | AXS-AXS OK XSTR-HWY 49 ,TEAL PONDCT PWR-Y TREE IN THE WIRES/HEALTHYTREE FROM POLE TO POLE. CONTINIUAL CONTACT. |  | SENT EMAIL TO VEG MGMT TO FOLLOW UP WITH CUSTOMER ON TREE CONCERN
|  |  | Completed | 1 | OIS DSP | 2021-07-14 16:51 |  | 2021-07-14 16:50 | 44391.7021 | 44391.7163 | 44391.7443 | 60.85 | 20.47 | 11 | 9.47 | 40.38 | 30 | 10.38 | 31.1 | 9.28 | T005341964 | 0 | AD | 4601 DOE ST, SHINGLE SPRI | 9250 | 9190 |  |  |  | A:DOG;X:;R:1 DOG SHIH TZU; DOWN POWER LINE CAUSED BY HUGE TREE BANCH ON PROPERTY; POLE TO HOUSE;, PWR-YPOWER POLE LEANING AS WEL L |  | CUT TREE OFF PARALLEL SERVICE DROPS
|  |  | Completed | 1 | OIS DSP | 2021-07-14 18:40 |  | 2021-07-14 18:39 | 44391.778 | 44391.778 | 44391.7805 | 3.54 | 0.02 | 11 | -10.98 | 3.52 | 30 | -26.48 | 31.1 | -27.58 | T005342029 | 0 | AD | 4601 DOE ST, SHINGLE SPRI | 9250 | 9190 |  |  |  | A:DOG;X:;R:1 DOG SHIH TZU; DOWN POWER LINE CAUSED BY HUGE TREE BANCH ON PROPERTY; POLE TO HOUSE;, PWR-YPOWER POLE LEANING AS WEL L |  | CUT TREE OFF SERVICE DROP
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 12:25 |  | 2021-07-14 12:24 |  |  | 44391.546 | [9 empty] | T005341724 | 0 | AD | 6480 TEAL LN, POLLOCK PINE | 9190 |  |  |  |  | AXS-AXS OK XSTR- PWR-Y DEAD TREE LEANING TOWARDS HIGH VOLTAGE LINES. WEVE PREVIOUSLY PERFORMED TREE TRIMMNG AT THIS PROPERY
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Placerville | DEQUNIE, WES | Completed | 2 | 4APGBF4 | 2021-07-14 06:26 |  | 2021-06-23 08:38 | 44391.289 | 44391.3431 | 44391.357 | 97.9 | 78 | 11 | 67 | 19.9 | 30 | -10.1 | 15 | 4.9 | 8242710386 | 2 | AM | 9084 ORCHID SHADE DR, EL DORADO HI | 2640 | 2640 |  |  |  | EXC - AXS OK; CTC: SHEWETHA PRASAD: 916-589-6585, DIS/REC 200A TO 200A - UG PNL CHG, L4L; REP: ALSE 916-767-2513; TMAN TO VERIFY INSP/ NOTIF #: 120860433 - OK TO SERVE |  | DISCO
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:28 |  | 2021-07-06 12:36 | 44391.3571 | 44391.3676 | 44391.3763 | 27.75 | 15.13 | 11 | 4.13 | 12.62 | 30 | -17.38 | 15 | -2.38 | 1552466238 | 2 | AM | 4153 BRISBANE CIR, EL DORADO HI | 2640 | 2640 |  |  |  | EXC - AXS OK; CTC Shewetha Prasad: 916-589-6585, DIS/REC 125A TO 125A - UG PNL CHG, L4L; Cust to ensure clear/level workspace; REP: CYCC 530- 228-6873; TMAN TO VERIFY INSP/ NOTIF #:121580451: - OK TO SERVE |  | DISCO
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:28 |  | 2021-07-12 16:45 | 44391.3764 | 44391.4049 | 44391.4123 | 51.69 | 40.97 | 11 | 29.97 | 10.72 | 27 | -16.28 | 37.4 | -26.68 | 1373808214 | 2 | AD | 6320 SCHENCK RANCH RD, SHINGLE SPRI | 1050 | 1057 |  |  |  | AXS-UNK, report of woodpecker damaged pole. 2nd pole S/O Bugtown Mine Rd. SAP # 101383010. GPS 38.59346307 -120.9304096439 - CAP# 121659548 - Per legal, Cust attorney put us on notice that this is a hazard. Pls issue EC tag. Thx... |  | WROTE EC TAG FOR POLE REPLACEMENT
|  |  | Completed | 3 | SAP DSP | 2021-07-13 13:55 |  | 2021-07-13 13:50 | 44391.4125 | 44391.4755 | 44391.4994 | 125.15 | 90.72 | 11 | 79.72 | 34.43 | 60 | -25.57 | 60 | -25.57 | S000765435 | 3 | AD | 6862 MOU NT AUKUM ROAD, SOMERSET | S438 | S400 |  |  |  | VOLTAGE COMPLAINT/6862 MOUNT AUKUM RD., SOMERSET/PIONEER UNION SCHOOLDISTRICT/MTR: 1009510318/T9919/SSD: 20813. CUSTOMER IS COMPLAINING OFVOLTAGE IMBALANCE NOT ALLOWING WATER PUMPS TO RUN. VERIFY PG&EEQUIPMENT AND CABLES ARE FUNCTIONING NORMALLY. IF NOTHING ABNORMAL ISFOUND IN THE FIELD, SET RVM FOR 7 DAYS TO FURTHER TROUBLESHOOTCUSTOMER ISSUE. CONTACT DANNY PERNES (D1PT) 559-720-3480 FOR QUESTIONSON THIS COMPLAINT. |  | SET RVM ON T9919
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:28 |  | 2021-07-06 12:38 | 44391.4995 | 44391.5593 | 44391.5882 | 127.61 | 86.08 | 11 | 75.08 | 41.53 | 35 | 6.53 | 20 | 21.53 | 1557690635 | 2 | AD | 4153 BRISBANE CIR, EL DORADO HI | 2220 | 2220 |  |  |  | EXC - AXS OK; CTC Shewetha Prasad: 916-589-6585, DIS/REC 125A TO 125A - UG PNL CHG, L4L; Cust to ensure clear/level workspace; REP: CYCC 530- 228-6873; TMAN TO VERIFY INSP/ NOTIF #:121580451: - OK TO SERVE |  | RECON
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:26 |  | 2021-06-23 08:38 | 44391.5882 | 44391.6306 | 44391.6327 | 64.05 | 60.98 | 11 | 49.98 | 3.07 | 35 | -31.93 | 20 | -16.93 | 8242398793 | 2 | AD | 9084 ORCHID SHADE DR, EL DORADO HI | 2220 | 2220 |  |  |  | EXC - AXS OK; CTC: SHEWETHA PRASAD: 916-589-6585, DIS/REC 200A TO 200A - UG PNL CHG, L4L; REP: ALSE 916-767-2513; TMAN TO VERIFY INSP/ NOTIF #: 120860433 - OK TO SERVE |  | RECON
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 16:07 |  | 2021-07-14 16:06 | 44391.6725 |  | 44391.6785 | [9 empty] | T005341944 | 0 | AD | 4601 DOE ST, SHINGLE SPRI | 9250 |  |  |  |  | A:DOG;X:;R:1 DOG SHIH TZU; DOWN POWER LINE CAUSED BY HUGE TREE BANCH ON PROPERTY; POLE TO HOUSE;, PWR-Y
|  |  | Completed | 1 | OIS DSP | 2021-07-14 16:10 |  | 2021-07-14 16:10 | 44391.6784 | 44391.6874 | 44391.751 | 104.53 | 13.05 | 11 | 2.05 | 91.48 | 63 | 28.48 | 0 | 91.48 | T005341947 | 0 | AD | 2826 KNOLLWOOD DR, CAMERON PARK | 9090 | 9002 |  |  |  | SMART MTR AUTO-GENERATED TAGWIRE NOT ACROSS ST. NO BRANCHES. POWER OUT. SERVICE DROP NOT LOW. NOT IN TREES BUT IN CUST BACKYARD. HEARD EXPLOSION AS WELL. UNSURE IF POLE TO POLE. NO INJURIES. NO EMERGENCY PEOPLE.KIMBERLY RD XST |  | ATT CREW GOT WIRE TOGETHER BACKYARD EASMENT. CREW WAS CLIMBING BACKYARD POLES. REFUSED 30E. POWER OK.
|  |  | Completed | 1 | OIS DSP | 2021-07-14 16:17 |  | 2021-07-14 16:16 | 44391.751 | 44391.7511 | 44391.7514 | 0.55 | 0.02 | 11 | -10.98 | 0.53 | 30 | -29.47 | 5.6 | -5.07 | T005341949 | 0 | AD | 4601 DOE ST, SHINGLE SPRI | 9250 | 0980 |  |  |  | A:DOG;X:;R:1 DOG SHIH TZU; DOWN POWER LINE CAUSED BY HUGE TREE BANCH ON PROPERTY; POLE TO HOUSE;, PWR-YPOWER POLE LEANING AS WEL L |  | RESOLVED BY TMAN CURTIS
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Placerville | DEVLIN, MICHAEL | Completed | 1 | AFW DSP | 2021-07-13 14:18 |  | 2021-07-13 14:17 | 44391.2123 | 44391.2552 | 44391.378 | 238.63 | 61.7 | 11 | 50.7 | 176.93 | 120 | 56.93 | 0 | 176.93 | W107756701 | 2 | UD | , | W110 | W110
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:29 |  | 2021-07-12 13:56 | 44391.4338 | 44391.4875 | 44391.5493 | 166.34 | 77.22 | 11 | 66.22 | 89.12 | 35 | 54.12 | 35 | 54.12 | 1439644241 | 2 | AD | 4020 STOPE DR, PLACERVILLE | 2220 | 2220 | 2002 |  |  | INSP OK. T-MAN TO RECONNECT 72' SVC COILED TO TREE & SET120/208V,1PH,200A ELE MTR. SITE CTC TODD 916-897-1686, REP S9BF 916-634-5159, PM 44610995/ 121320781. |  | power on
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 06:26 |  | 2021-07-14 00:25 | 44391.5494 | 44391.5908 | 44391.6229 | 105.85 | 59.63 | 11 | 48.63 | 46.22 | 31 | 15.22 | 21.9 | 24.32 | 1428505136 | 1 | AD | 2020 OAK KNOLL CT, PLACERVILLE | 1240 | 1320 |  |  |  | AXS-AXS UNKNOWN XStr-UNKNOWN Pwr-Y EIM2141436 7/13/2021@1243PM CUST REPORTS TREES TOUCHIN TOP WIRES IN FRONT YARD ON PROPERTY LINE/MED OAK TREES/ TREES LEANING ALSO |  | trimmed service drop
|  |  | Completed | 2 | 4APGBF4 | 2021-07-14 13:52 |  | 2021-07-14 13:49 | 44391.6231 | 44391.6442 | 44391.6653 | 60.8 | 30.42 | 11 | 19.42 | 30.38 | 31 | -0.62 | 21.9 | 8.48 | 1464849827 | 1 | AD | 8992 QUIET CANYON RD, PLACERVILLE | 1240 | 1320 |  |  |  | No Access or Safety Issues; WIRE HANGING LOW; CROSSES DRIVEWAY;NO BRANCHES;NO HI/LOW VOLTAGE;CONNECTED TO INSULATOR;SVC DROP UNDERGROUND |  | phone
|  |  | Completed | 1 | OIS DSP | 2021-07-14 15:46 |  | 2021-07-14 15:46 | 44391.6654 | 44391.7431 | 44391.7661 | 145.04 | 111.92 | 11 | 100.92 | 33.12 | 59 | -25.88 | 0 | 33.12 | T005341932 | 0 | AD | 2535 PAWPRINT PATH, PLACERVILLE | 9260 | 9002 |  |  |  | AXS-DOG LOCKED UP XSTR- PWR-Y DRIVEWAY, POLE TO HOUSE, HANGING LOW ENOUGH THAT SOMEONE CAN TOUCH IT, NO BLDG AND NO TREES |  | oak branch fell on service made repaires power ok
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 15:28 |  | 2021-07-14 15:28 |  |  | 44391.6569 | [9 empty] | T005341915 | 0 | AD | 1950 SUNDOWN TRL, PLACERVILLE | 9190 |  |  |  |  | AXS-AXS OK XSTR-HWY 49 ,TEAL PONDCT PWR-Y TREE IN THE WIRES/HEALTHYTREE FROM POLE TO POLE. CONTINIUAL CONTACT.
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Placerville | MYERS, STEVEN | Completed | 1 | OIS DSP | 2021-07-14 13:06 |  | 2021-07-14 13:06 | 44391.5464 | 44391.5776 | 44391.5976 | 73.75 | 44.9 | 11 | 33.9 | 28.85 | 32 | -3.15 | 16.6 | 12.25 | T005341751 | 0 | AD | 6480 TEAL LN, POLLOCK PINE | 9190 | 9320 |  |  |  | AXS-AXS OK XSTR- PWR-Y DEAD TREE LEANING TOWARDS HIGH VOLTAGE LINES. WEVE PREVIOUSLY PERFORMED TREE TRIMMNG AT THIS PROPERY |  | cust observed dead tree near power lines. pics and info forwarded to veg mgmt
|  |  | Completed | 1 | OIS DSP | 2021-07-14 14:06 |  | 2021-07-14 14:06 | 44391.5977 | 44391.6378 | 44391.6501 | 75.53 | 57.8 | 11 | 46.8 | 17.73 | 30 | -12.27 | 16.6 | 1.13 | T005341820 | 1 | AD | 7031 MORNING CANYON RD, SOMERSET | 9030 | 9320 |  |  |  | A:LOCKED GATE, NO DOGS;X:SAND RIDGE;R:METER BUTTON GRAYED OUT, SM OPT OUT |  | good power at meter. pwr ok
|  |  | Completed | 1 | OIS DSP | 2021-07-14 15:45 |  | 2021-07-14 15:44 | 44391.6562 | 44391.6806 | 44391.698 | 60.22 | 35.15 | 11 | 24.15 | 25.07 | 32 | -6.93 | 16.6 | 8.47 | T005341929 | 0 | AD | 10076 GRIZZLY FLAT RD, GRIZZLY FLAT | 9190 | 9320 |  |  |  | AXS-AXS OKAY XSTR-MOUNT PLEASANT PWR-Y TREES IN WIRES,POLE TO POLE, WIRE RESTING ON BRANCH GREEN PINE TREE, VACANT HOME NEIGHBOR IS CALLING CONCERNED ABOUT FIRES. CONTACT PAUL |  | only found branches touching service line. no threat to hight voltage. pwr ok
|  |  | Completed | 1 | OIS DSP | 2021-07-14 19:24 |  | 2021-07-14 19:24 | 44391.8193 | 44391.8345 | 44391.8534 | 49.2 | 21.93 | 11 | 10.93 | 27.27 | 51 | -23.73 | 16.6 | 10.67 | T005342050 | 1 | AD | 2860 BIRCH CT, CAMINO | 9140 | 9320 |  |  |  | AXS-AXS-OKAY XSTR-CEDAR PWR-Y CUST EXPERIENCING LOW VOLTAGE, CUST SPOKE TO DISTRIBUTION READ IS 113.5 AND 227 ACROSSCAPACITOR BANK 2065 OFFLINE |  | cust not home. replaced suspect connectors at tx pole. pwr ok
Quincy
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
6 | Quincy | BRUNELLE, MICHAEL | Completed | 1 | OIS DSP | 2021-07-14 11:13 |  | 2021-07-14 11:13 | 44391.473 | 44391.473 | 44391.5686 | 137.8 | 0.03 | 12 | -11.97 | 137.77 | 43 | 94.77 | 5.6 | 132.17 | T005341637 | 1 | AD | 207 MAIN ST, GREENVILLE | 9040 | 0980 |  |  |  | , PWR-I |  | transmission outage
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Quincy | GWALTNEY, CODY | Completed | 1 | OIS DSP | 2021-07-14 11:12 |  | 2021-07-14 11:12 | 44391.4736 | 44391.4736 | 44391.5893 | 166.64 | 0.02 | 12 | -11.98 | 166.62 | 43 | 123.62 | 5.6 | 161.02 | T005341634 | 1 | AD | 268 MAIN ST, CHESTER | 9040 | 0930 |  |  |  | SMART MTR AUTO-GENERATED TAG |  | otage restored by control center
|  |  | Completed | 1 | OIS DSP | 2021-07-14 14:54 |  | 2021-07-14 14:53 | 44391.6275 | 44391.6335 | 44391.6564 | 41.55 | 8.62 | 12 | -3.38 | 32.93 | 51 | -18.07 | 5.6 | 27.33 | T005341872 | 1 | AD | 666-975 SPRING CREEK DR, WESTWOOD | 9140 | 0930 |  |  |  | AXS-AXS OK XSTR-RAINBOW DR PWR-Y DIRTY PWR NOT RUNNING FULL 3PHASE HAD TO TURN ON GENRATOR CAN HEAR MOTOR RUNNIN |  | address was for 666-975 highway 147 customer figured out issue with pwr on customer side
|  |  | Completed | 1 | OIS DSP | 2021-07-14 15:38 |  | 2021-07-14 15:38 | 44391.6566 | 44391.6617 | 44391.6814 | 35.78 | 7.4 | 12 | -4.6 | 28.38 | 30 | -1.62 | 5.6 | 22.78 | T005341927 | 1 | AD | 168 PENINSULA DR, LAKE ALMANOR | 9030 | 0930 |  |  |  | AXS-AXS OK XSTR-COUNTY RD PWR-I AXS OK;COMPLTE OUT; CUSTOMER STATES ITS BEEN FEW HOURS; |  | contacted customer and havnt heard back pwr is good at this address
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Quincy | MCMILLAN, CALEB | Completed | 1 | OIS DSP | 2021-07-14 11:13 |  | 2021-07-14 11:12 | 44391.5267 | 44391.6929 | 44391.6933 | 239.86 | 239.33 | 12 | 227.33 | 0.53 | 43 | -42.47 | 5.6 | -5.07 | T005341635 | 1 | AD | 1953 E MAIN ST # 1, QUINCY | 9040 | 0980 |  |  |  | SMART MTR AUTO-GENERATED TAG, PWR-N |  | transmission
|  |  | Completed | 1 | OIS DSP | 2021-07-14 16:18 |  | 2021-07-14 16:17 | 44391.6933 | 44391.6984 | 44391.8841 | 274.7 | 7.25 | 12 | -4.75 | 267.45 | 30 | 237.45 | 0 | 267.45 | T005341951 | 1 | AD | 39280 HIGHWAY 70, QUINCY | 9030 | 9221 |  |  |  | AXS-GATE; DOGS XSTR-CHANDLER PWR-Y COMP OUT |  | transfer swith malfuncution
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 15:33 |  | 2021-07-14 15:33 |  |  | 44391.6514 | [9 empty] | T005341924 | 1 | AD | 168 PENINSULA DR, LAKE ALMANOR | 9030 |  |  |  |  | AXS-AXS OK XSTR-COUNTY RD PWR-I AXS OK;COMPLTE OUT; CUSTOMER STATES ITS BEEN FEW HOURS;
Red Bluff
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
6 | Red Bluff | CERRO, RICHARD | Completed | 2 | 4APNWA1 | 2021-07-14 06:58 |  | 2021-06-16 14:14 | 44391.2926 | 44391.326 | 44391.3731 | 115.93 | 48.08 | 17.6 | 30.48 | 67.85 | 30 | 37.85 | 15 | 52.85 | X316147979 | 2 | AM | 3298 MARGUERITE AVE, CORNING | 2640 | 2640 |  |  |  | EXC ~ 2TMEN; ACS OK; CTC: ROBIN @559-335-4589; DIS/REC 200A TO 200A - OH PNL UPG; DIS/RMVE EXISTING SVC IN AM/INSTALL 60' 1/0 TPX IN PM; REP: ALSE 916-767-2513;TMAN TO VERIFY INSP/NOTIF: 1207185901 - OK TO SERVE | TAGS GIVEN TO MASON AND CERRO | DISCONNECT SERVICE
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:58 |  | 2021-06-16 14:17 | 44391.3732 | 44391.3732 | 44391.3751 | 2.71 | 0.03 | 17.6 | -17.57 | 2.68 | 35 | -32.32 | 75 | -72.32 | X316147978 | 2 | AD | 3298 MARGUERITE AVE, CORNING | 2220 | 2120 | 2220 |  |  | EXC ~ 2TMEN; ACS OK; CTC: ROBIN @559-335-4589; DIS/REC 200A TO 200A - OH PNL UPG; DIS/RMVE EXISTING SVC IN AM/INSTALL 60' 1/0 TPX IN PM; REP: ALSE 916-767-2513;TMAN TO VERIFY INSP/NOTIF: 1207185901 - OK TO SERVE | TAGS GIVEN TO MASON AND CERRO | INSTALLED SERVICE AND TRANSFERRED METER
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 09:29 |  | 2021-07-14 09:25 | 44391.4145 | 44391.4341 | 44391.4481 | 48.37 | 28.15 | 17.6 | 10.55 | 20.22 | 27 | -6.78 | 33.3 | -13.08 | 0978842507 | 1 | AD | 18625 HOOKER CREEK RD, COTTONWOOD | 1050 | 1163 |  |  |  | CLAIRE COLEMAN 530-524-2359 REPORTING ROTTEN SERVICE; PLEASE MAKE SAFE |  | MADE SAFE
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 11:32 |  | 2021-07-14 11:26 | 44391.5012 | 44391.5059 | 44391.5069 | 8.18 | 6.73 | 17.6 | -10.87 | 1.45 | 29 | -27.55 | 21.9 | -20.45 | 3337498157 | 0 | AD | 13833 BAKER RD, RED BLUFF | 1160 | 1320 |  |  |  | DOGS IN BACK. LOW WIRES IN DRIVEWAY. POLE TO POLE. POWER OK. CUST STATES STEEL CABLE. ALMOST HIT BY VEHICLE. CUST CONCERNED ABOUT DELIVERY TRUCKS. XSTS: PLYMIRE RD. CONTACT: CAROLYN 530-200-6839 LIVES AT 13831 BAKER RD (SHARES DRIVEWAY). |  | CABLE TV CONTRACTORS STRINGING NEW CONDUCTOR NO HAZARD
|  |  | Completed | 4 | 4APNWA1 | 2021-07-14 14:36 |  | 2021-07-12 08:30 | 44391.6122 | 44391.6525 | 44391.6853 | 105.27 | 58.07 | 17.6 | 40.47 | 47.2 | 25 | 22.2 | 20 | 27.2 | 0768751348 | 2 | AD | PAYNES CRK SPORTSMAN @ CLUB-C, PAYNES CREEK | 2094 | 2094 |  |  |  | TMAN TO INSTALL 60'OF 1/0 TPX ASN SET 100AMP METER, CONTACT MARY DECKER 707-592-9112,REP AMADO PEREZ 530-410-2193, PM#44626901, NOTIF#121601569 |  | INSTALLED SERVICE SET METER
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Red Bluff | LAUGHLIN, RON | Completed | 1 | AFW DSP | 2021-07-09 08:46 |  | 2021-07-09 08:46 | 44391.284 | 44391.3558 | 44391.4089 | 179.83 | 103.4 | 17.6 | 85.8 | 76.43 | 120 | -43.57 | 0 | 76.43 | W107613703 | 2 | UD | , | W110 | W110
|  |  | Completed | 1 | AFW DSP | 2021-07-09 08:46 |  | 2021-07-09 08:46 | 44391.409 | 44391.409 | 44391.4433 | 49.45 | 0.02 | 17.6 | -17.58 | 49.43 | 120 | -70.57 | 0 | 49.43 | W107613704 | 2 | UD | , | W112 | W112
|  |  | Completed | 1 | OIS DSP | 2021-07-14 08:29 |  | 2021-07-14 08:29 | 44391.4434 | 44391.4564 | 44391.4712 | 39.94 | 18.62 | 17.6 | 1.02 | 21.32 | 43 | -21.68 | 16.6 | 4.72 | T005341348 | 1 | AD | 37735 HWY 36 E, MINERAL | 9040 | 9320 |  |  |  | SMART MTR AUTO-GENERATED TAG |  | PWR OK, CUST. FUSE
|  |  | Completed | 1 | OIS DSP | 2021-07-14 09:00 |  | 2021-07-14 09:00 | 44391.4778 | 44391.4778 | 44391.4903 | 18.09 | 0.02 | 17.6 | -17.58 | 18.07 | 60 | -41.93 | 54 | -35.93 | T005341410 | 2 | AD | STRLIGHT 41543 HWY 36 E, MILL CREEK | 9500 | 9500 |  |  |  | THE VILLAGE AT CHILDS MEADDOW, RV PARK, 35W LED |  | HAS PWR, TURNED ON AND OFF SEVERAL TIMES, LEFT ON APROX 10MIN
|  |  | Completed | 1 | OIS DSP | 2021-07-14 12:29 |  | 2021-07-14 12:29 | 44391.5214 | 44391.5216 | 44391.599 | 111.79 | 0.22 | 17.6 | -17.38 | 111.57 | 51 | 60.57 | 16.6 | 94.97 | T005341728 | 1 | AD | E/MINERAL LODGE, MINERAL | 9140 | 9320 |  |  |  | A:UNK;X:UNK;R:GIVE TO LAUGHLIN, PWR-Y |  | CHKD PWR OK, REPLACED GREY SERV. INSTALLED 40' 1/0TPX
|  |  | Completed | 1 | OIS DSP | 2021-07-13 21:44 |  | 2021-07-13 21:44 |  |  | 44391.0192 | 153.49 | 51.02 | 17.6 | 33.42 | 102.47 | 30 | 72.47 | 0 | 102.47 | T005341104 | 1 | AD | 31481 BRIAR RD, WHITMORE | 9030 | 9002 |  |  |  | IVR,MTR UNK ON,NO DOG,LOCKED GATE |  | OVERLOADED TX - GROW, CREW TO MAKE REPAIRS
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Red Bluff | MASON, LAINE | Completed | 2 | 4APNWA1 | 2021-07-14 06:59 |  | 2021-06-16 14:14 | 44391.3931 | 44391.3994 | 44391.4009 | 11.2 | 9.05 | 17.6 | -8.55 | 2.15 | 30 | -27.85 | 5.6 | -3.45 | 0722975804 | 2 | AM | 3298 MARGUERITE AVE, CORNING | 2640 | 0980 |  |  |  | EXC ~ 2TMEN; ACS OK; CTC: ROBIN @559-335-4589; DIS/REC 200A TO 200A - OH PNL UPG; DIS/RMVE EXISTING SVC IN AM/INSTALL 60' 1/0 TPX IN PM; REP: ALSE 916-767-2513;TMAN TO VERIFY INSP/NOTIF: 1207185901 - OK TO SERVE | TAGS GIVEN TO MASON AND CERRO | 1
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:59 |  | 2021-06-16 14:17 | 44391.4011 | 44391.4011 | 44391.4015 | 0.59 | 0.02 | 17.6 | -17.58 | 0.57 | 35 | -34.43 | 5.6 | -5.03 | 0724950570 | 2 | AD | 3298 MARGUERITE AVE, CORNING | 2220 | 0980 |  |  |  | EXC ~ 2TMEN; ACS OK; CTC: ROBIN @559-335-4589; DIS/REC 200A TO 200A - OH PNL UPG; DIS/RMVE EXISTING SVC IN AM/INSTALL 60' 1/0 TPX IN PM; REP: ALSE 916-767-2513;TMAN TO VERIFY INSP/NOTIF: 1207185901 - OK TO SERVE | TAGS GIVEN TO MASON AND CERRO | 1
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:59 |  | 2021-07-13 14:32 | 44391.4018 | 44391.4284 | 44391.4409 | 56.35 | 38.35 | 17.6 | 20.75 | 18 | 35 | -17 | 20 | -2 | 7902049851 | 2 | AD | 16835 ELDER CREEK CIR, CORNING | 2220 | 2220 |  |  |  | TMAN___RECONN SVC - MTR UIS SET_SVC RUN__ OK APPF CNCT JIMMY 916-871-4276 XST IN RANCHO TEHAMA RESRV XST PAST AIRPORT ON RANCHO R ON RED OK RD TO ELDER CREEK, |  | 1
|  |  | Completed |  | AFW DSP | 2021-09-21 06:31 |  | 2021-09-21 06:27 | 44460.3797 | 44460.4187 | 44460.4189 | 56.51 | 56.23 | 17.6 | 38.63 | 0.28 | 90 | 0.28 | 0 | 0.28 | W111617908 | 2 | UD | , | W114 | W114
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Red Bluff | PARKS, JAMES | Completed |  | AFW DSP | 2021-09-21 06:27 |  | 2021-09-21 06:27 | 44460.3101 | 44460.3102 | 44460.4198 | 157.92 | 0.05 | 17.6 | -17.55 | 157.87 | 90 | 157.87 | 0 | 157.87 | W111617909 | 2 | UD | , | W114 | W114
Redding
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
6 | Redding | ANDRADE, SHAWN | Completed | 1 | OIS DSP | 2021-07-14 11:50 |  | 2021-07-14 11:49 | 44391.4969 | 44391.5139 | 44391.5192 | 32.12 | 24.45 | 16.5 | 7.95 | 7.67 | 32 | -24.33 | 5.6 | 2.07 | T005341687 | 0 | AD | UNKNOWN PLACER RD , REDDING | 9190 | 0980 |  |  |  | AXS-OK BLACK BOX HANGING FROM WIRES ON POLE ABOUT 10 F FROM GROUND ACROSS FROM SCHRADER PLANETIEM |  | communication line cust is calling on, advised cust. not pge area, redding electric utility area also
|  |  | Completed | 4 | SAP DSP | 2021-07-14 11:52 |  | 2021-07-13 17:14 | 44391.5192 | 44391.5457 | 44391.546 | 38.52 | 38.07 | 16.5 | 21.57 | 0.45 | 60 | -59.55 | 60 | -59.55 | S000765441 | 3 | AD | 7021 Eas tside Road, Anderson | S438 | S400 |  |  |  | (GAS JOB C-1612)TMan to disconnect AC Service at top of pole to rectifier both hot andneutral. |  | completed
|  |  | Completed | 4 | 4APNWA1 | 2021-07-14 14:44 |  | 2021-07-07 10:25 | 44391.6142 | 44391.6215 | 44391.6333 | 27.55 | 10.55 | 16.5 | -5.95 | 17 | 35 | -18 | 20 | -3 | 0840627761 | 2 | AD | 2945 SILO CT, ANDERSON | 2220 | 2220 |  |  |  | EXC AXS OK; CUST TRINI 909-277-8078; DIS/REC L4L 100 PNL CHG, INSP REQ; REP MQ1W 209-272-8699/209-292-1010; NOTIF 120251529 |  | reconnect chk power ok
|  |  | Completed | 3 | AFW DSP | 2021-07-14 15:43 |  | 2021-07-09 08:49 | 44391.6557 | 44391.677 | 44391.7493 | 134.79 | 30.62 | 16.5 | 14.12 | 104.17 | 120 | -15.83 | 0 | 104.17 | W106147004 | 2 | UD | , | W112 | W112 | [5 empty] | cmplt
|  |  | Cancelled |  | WO DSP |  |  | 2021-06-25 16:19 |  |  | 44391.4486 | [9 empty] | 0822610753 | 2 | AM | 4261 STORY LN, ANDERSON | 2640 |  |  |  |  | EXC - AXS OK PER restoration super Scott STG3 Okay with 1 T Men, service pole crosses side street; CTC: Amber: 916-206-4137, DIS/REC -200A TO 200A - OH PNL CHG, L4L; REP: ALFI 916 618-3201; TMAN TO VERIFY INSP/ NOTIF #: 120678980 - OK TO SERVE
|  |  | Cancelled |  | WO DSP |  |  | 2021-06-25 16:19 |  |  | 44391.4488 | [9 empty] | 0827779262 | 2 | AD | 4261 STORY LN, ANDERSON | 2220 |  |  |  |  | EXC - AXS OK PER restoration super Scott STG3 Okay with 1 T Men, service pole crosses side street; CTC: Amber: 916-206-4137, DIS/REC -200A TO 200A - OH PNL CHG, L4L; REP: ALFI 916 618-3201; TMAN TO VERIFY INSP/ NOTIF #: 120678980 - OK TO SERVE
|  |  | Cancelled |  | WO DSP |  |  | 2021-07-07 08:58 |  |  | 44391.4329 | [9 empty] | 0841673792 | 2 | AM | 19870 LITTLE ACRES LN, REDDING | 2640 |  |  |  |  | Access/Safety: Dog(s);BRSC DISCONNECT;REPAIRING BUS BAR;PER BRETT BARNES
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Redding | COLGATE, CALEM | Completed | 2 | 4APNWA1 | 2021-07-14 07:04 |  | 2021-07-12 11:57 | 44391.3071 | 44391.3133 | 44391.333 | 37.36 | 9.03 | 16.5 | -7.47 | 28.33 | 30 | -1.67 | 15 | 13.33 | 1057574198 | 2 | AM | 3453 HICKORY ST, COTTONWOOD | 2640 | 2640 |  |  |  | TMNA___ DISC E# 1006192281 OH FOR L4L PANEL CHG__OK ED NORMAND CNCT JASON FOLMER 530-921-5625 XST I-5 E ON 4TH THEN 2ND R PAST NEW COTONWOOD FIRE STA TO HICKORY ST |  | n/a
|  |  | Completed | 6 | 4APNWA1 | 2021-07-14 07:23 |  | 2021-07-06 12:12 | 44391.343 | 44391.3545 | 44391.3549 | 17.08 | 16.48 | 16.5 | -0.02 | 0.6 | 30 | -29.4 | 15 | -14.4 | 0922511695 | 2 | AM | 19853 LOOP ST, ANDERSON | 2640 | 2640 |  |  |  | TMAN___EXC - AXS OK; CTC: MIKE FREUDE: 530-209-9053, DIS/REC 100A TO 200A - OH PNL UPG; CUST TO ENSURE GREENBOOK STANDARDS ARE MET.REP: ALSE 916-767- 2513; TMAN TO VERIFY INSP/ NOTIF #: 121416590 - OK TO SERVE xst I-5 SB W ON RIVERSIDE L 2ND S__PGE CNCL |  | N/A
|  |  | Completed | 6 | 4APNWA1 | 2021-07-14 07:23 |  | 2021-07-08 09:24 | 44391.3552 | 44391.3575 | 44391.3612 | 8.65 | 3.28 | 16.5 | -13.22 | 5.37 | 30 | -24.63 | 5.6 | -0.23 | 0910036756 | 2 | AM | 2431 ALEXANDER AVE, ANDERSON | 2640 | 0980 |  |  |  | EXC - AXS OK; CTC KENDALL: 530-949-0359, DIS/REC 100A TO 100A - OH PNL CHG, L4L; REP A7HG 916-216-0708; TMAN TO VERIFY INSP/ NOTIF #: 121547327- OK TO SERVE |  | NEW PANEL ALREADY
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 07:04 |  | 2021-07-07 10:22 | 44391.3615 | 44391.3716 | 44391.3797 | 26.1 | 14.43 | 16.5 | -2.07 | 11.67 | 30 | -18.33 | 15 | -3.33 | 0840221654 | 2 | AM | 2945 SILO CT, ANDERSON | 2640 | 2640 |  |  |  | EXC AXS OK; CUST TRINI 909-277-8078; DIS/REC L4L 100 PNL CHG, INSP REQ; REP MQ1W 209-272-8699/209-292-1010; NOTIF 120251529 |  | N/A
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 07:04 |  | 2021-07-08 08:13 | 44391.3798 | 44391.3863 | 44391.4283 | 69.93 | 9.4 | 16.5 | -7.1 | 60.53 | 30 | 30.53 | 15 | 45.53 | 1037323979 | 2 | AM | 5711 GREEN ACRES DR, ANDERSON | 2640 | 2640 |  |  |  | EXC- AXS OK; CTC: ANDY DICKSON @ 530-410-4245 OH DISC/RECO 100A - 200A UG PNL UPG, NO ADDED LOAD; REP: SBJ5 916-214-7283; TMAN TO VERIFY INSP- NOTIF#: 121369724- OK TO SERVE |  | N/A
|  |  | Completed | 6 | 4APNWA1 | 2021-07-14 07:23 |  | 2021-07-08 09:26 | 44391.4285 | 44391.4285 | 44391.4288 | 0.45 | 0.02 | 16.5 | -16.48 | 0.43 | 35 | -34.57 | 5.6 | -5.17 | 0918290596 | 2 | AD | 2431 ALEXANDER AVE, ANDERSON | 2220 | 0980 |  |  |  | EXC - AXS OK; CTC KENDALL: 530-949-0359, DIS/REC 100A TO 100A - OH PNL CHG, L4L; REP A7HG 916-216-0708; TMAN TO VERIFY INSP/ NOTIF #: 121547327- OK TO SERVE |  | N/A
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 07:04 |  | 2021-07-08 08:13 | 44391.4289 | 44391.4289 | 44391.4292 | 0.51 | 0.03 | 16.5 | -16.47 | 0.48 | 35 | -34.52 | 20 | -19.52 | 1036243796 | 2 | AD | 5711 GREEN ACRES DR, ANDERSON | 2220 | 2220 |  |  |  | EXC- AXS OK; CTC: ANDY DICKSON @ 530-410-4245 OH DISC/RECO 100A - 200A UG PNL UPG, NO ADDED LOAD; REP: SBJ5 916-214-7283; TMAN TO VERIFY INSP- NOTIF#: 121369724- OK TO SERVE |  | N/A
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 07:04 |  | 2021-07-13 18:33 | 44391.4297 | 44391.4487 | 44391.4918 | 89.5 | 27.4 | 16.5 | 10.9 | 62.1 | 35 | 27.1 | 20 | 42.1 | 0567182613 | 2 | AD | 5680 BALLS FERRY RD, ANDERSON | 2220 | 2220 |  |  |  | PER WALLER NEEDS RECONNECT 7/14 |  | N/A
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 11:11 |  | 2021-07-14 11:09 | 44391.492 | 44391.492 | 44391.4935 | 2.18 | 0.03 | 16.5 | -16.47 | 2.15 | 19 | -16.85 | 15 | -12.85 | 0563147986 | 1 | AD | 5680 BALLS FERRY RD, ANDERSON | 2002 | 2002 |  |  |  | GIVE TO TMAN COLGATE - CUSTOMER REQUESTED ANALOG METER; SMART METER OPT OUT |  | OPT OUT ANALOG METER
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 07:04 |  | 2021-07-13 06:19 | 44391.494 | 44391.5339 | 44391.5357 | 60.05 | 57.55 | 16.5 | 41.05 | 2.5 | 25 | -22.5 | 35 | -32.5 | 3125285460 | 2 | AD | 2550 W HILLSIDE DR, ANDERSON | 2094 | 2220 | 2052 |  |  | HEAT & SET CNC: ROB STRIEFF 530/277-4708 & REP: EIN1 530/691-9037 121592462 |  | USED THE METER THAT WAS ALREADY THERE
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 07:04 |  | 2021-07-12 12:01 | 44391.5859 | 44391.5978 | 44391.6364 | 72.6 | 17.05 | 16.5 | 0.55 | 55.55 | 35 | 20.55 | 20 | 35.55 | 1053017523 | 2 | PM | 3453 HICKORY ST, COTTONWOOD | 2220 | 2220 |  |  |  | TMAN__RECONN E# 1006192281 AFTER L4L PNL CHG W STICKER_ OK ED NORMAND CALL JASON FOLMER 530-921-5625 XSY I-5 E ON 4TH, LOOK R AFTER NEW COTTONWOOD FIRE STATION |  | N/A
|  |  | Completed | 6 | 4APNWA1 | 2021-07-14 07:23 |  | 2021-07-06 12:14 | 44391.6364 | 44391.6418 | 44391.6879 | 74.08 | 7.7 | 16.5 | -8.8 | 66.38 | 35 | 31.38 | 20 | 46.38 | 0926680713 | 2 | PM | 19853 LOOP ST, ANDERSON | 2220 | 2220 |  |  |  | TMAN__EXC - AXS OK; CTC: MIKE FREUDE: 530-209-9053, DIS/REC 100A TO 200A - OH PNL UPG; CUST TO ENSURE GREENBOOK STANDARDS ARE MET.REP: ALSE 916-767- 2513; TMAN TO VERIFY INSP/ NOTIF #: 121416590 - OK TO SERVE PGE CNCL |  | N/A
|  |  | Cancelled |  | WO DSP |  |  | 2021-07-07 09:01 |  |  | 44391.4331 | [9 empty] | 0847938211 | 2 | AD | 19870 LITTLE ACRES LN, REDDING | 2220 |  |  |  |  | No Access or Safety Issues;BRSC RECONNECT;REPAIRING BUS BAR;PER BRETT BARNES
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Redding | WALLER, KENNETH | Completed | 9 | 4APNWA1 | 2021-07-14 07:02 |  | 2021-07-13 14:57 | 44391.3318 | 44391.3318 | 44391.3465 | 21.17 | 0.02 | 16.5 | -16.48 | 21.15 | 31 | -9.85 | 21.9 | -0.75 | 0995697859 | 1 | AD | 20525 DURYEE LN, REDDING | 1240 | 1320 |  |  |  | Access/Safety: Dog(s); WIRE IS POLE TO HOUSE AND SAGGING LOW. HE IS NOT ABLE TO PARK HIS TRAILER IN THE BACKYARD WITHOUT THE WIRE TOUCHING. | CUSTOMER NEEDS TO MOVE CARS. ROLL TILL 7/14 PER TMAN | RAISED CUSTOMER SERVICE AS HIGH AS POSSIBLE SHOULD CLEAR, JUST OVER 12' AT HOUSE
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 07:00 |  | 2021-07-13 07:08 | 44391.3472 | 44391.3564 | 44391.4016 | 78.26 | 13.28 | 16.5 | -3.22 | 64.98 | 30 | 34.98 | 45 | 19.98 | 0977254989 | 2 | AM | 21913 BELMONT DR, PALO CEDRO | 2640 | 2092 |  |  |  | TMAN___DISC & SWING TO NEW PANEL__ INSP OK 200A CALL BRUCE 530-605-9386 XST DESCHUTES,,NO BUCKET ACCESS CALL AHD, OK R3PC. POSSS NEEDS NEW MTR..resked from 7/12 |  | SWUNG SERVICE FROM OLD PANEL TO NEW PANEL
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 07:00 |  | 2021-07-13 07:09 | 44391.4017 | 44391.4018 | 44391.4059 | 6.01 | 0.03 | 16.5 | -16.47 | 5.98 | 35 | -29.02 | 35 | -29.02 | 0975685585 | 2 | AD | 21913 BELMONT DR, PALO CEDRO | 2220 | 2002 | 2220 |  |  | TMAN___RECON AFTER SWING TO NEW PANEL__ INSP OK 200A CALL BRUCE 530-605-9386 XST DESCHUTES,,NO BUCKET ACCESS CALL AHD, OK R3PC. POSSS NEEDS NEW MTRTJV2:OTHER; |  | HOUSE FIRE RESTORATION NO METER IN PANEL, INSTALLED NEW CONNECTED SERVICE AT CLEARANCE POLE
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 07:01 |  | 2021-07-06 13:06 | 44391.4115 | 44391.4115 | 44391.4126 | 1.5 | 0.02 | 16.5 | -16.48 | 1.48 | 30 | -28.52 | 5.6 | -4.12 | 1003692318 | 2 | AM | 30877 TINKERBELL LN, SHINGLETOWN | 2640 | 0980 |  |  |  | TMAN__ CO CODE HAZ TAG_ DISC E# 5000082218 CALL AHD MARC 530-806-5181 XST HWY 44E L ON SHASTA FOREST DR R ON TINKERBELL. MEET MARC ONS. |  | CONTACTED COEDE INFORCEMENT OFFICER AND HE SAID TO CANCEL THE ORDER AS THE CUSTOMER WAS COMPLYING WITH HIS REQUESTS
|  |  | Completed | 1 | OIS DSP | 2021-07-14 10:04 |  | 2021-07-14 10:03 | 44391.4194 | 44391.4567 | 44391.6493 | 331.09 | 53.67 | 16.5 | 37.17 | 277.42 | 30 | 247.42 | 0 | 277.42 | T005341532 | 1 | AD | 20809 GILMAN RD, LAKEHEAD | 9030 | 9002 |  |  |  | SMART MTR AUTO-GENERATED TAG |  | MULTIPLE OUTAGES, UNABLE TO FIND CAUSE INSTALLED FI'S AND TESTED UG CABLE SEPARATE FROM REST OF LINE WITH NO EOBLEMS FUSES HOLDING AT THIS TIMNE
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 10:50 |  | 2021-07-14 10:43 | 44391.6495 | 44391.6755 | 44391.6909 | 59.61 | 37.48 | 16.5 | 20.98 | 22.13 | 31 | -8.87 | 25 | -2.87 | 3420950803 | 1 | AD | GREGORY CREEK, LAKEHEAD | 1240 | 2640 | 2402 |  |  | CLAIRE COLEMAN 530-524-2359 REQUESTING SAFETY CHECK OF POSSIBLE ENERGIZED SERIVCE CONNECTED TO BURNT POLE AFTER SALT CREEK FIRE; PLEASE DISCONNECT IF STILL ENERGIZED |  | CUSTOMER SERVICE POLE BURNT UP IN SALT FIRE METER IS MELTED AND TRANSFORMER FUSES BLOWN REMOVED HIGH SIDE TX LEADS AND CUT DOWN SERVICE
|  |  | Completed | 2 | 4APKERA | 2021-07-14 16:30 |  | 2021-07-14 16:28 | 44391.691 | 44391.691 | 44391.6929 | 2.7 | 0.02 | 16.5 | -16.48 | 2.68 | 30 | -27.32 | 5.6 | -2.92 | 3429089132 | 1 | AD | GREGORY CREEK, LAKEHEAD | 2640 | 0980 |  |  |  | for tman waller |  | I WAS ABLE TO COMPLETE DISCONNECT ON 1240 TAG THAT I WAS ALREADY ON
|  |  | Completed | 2 | AFW DSP | 2021-07-12 12:32 |  | 2021-07-09 08:49 | 44391.6931 | 44391.6931 | 44391.694 | 1.3 | 0.02 | 16.5 | -16.48 | 1.28 | 120 | -118.72 | 5.6 | -4.32 | W106147003 | 2 | UD | , | W110 | 0980 | [5 empty] | UNABLE TO COMOLETE TAG GAVE TO #1 TMAN
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 11:22 |  | 2021-07-14 11:22 |  |  | 44391.4926 | [9 empty] | T005341650 | 0 | AD | UNKNOWN PLACER RD , REDDING | 9190 |  |  |  |  | AXS-OK BLACK BOX HANGING FROM WIRES ON POLE ABOUT 10 F FROM GROUND ACROSS FROM SCHRADER PLANETIEM
Vacaville
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
6 | Vacaville | BOHN, JOSEPH | Completed | 2 | 4APNWA1 | 2021-07-14 06:29 |  | 2021-05-06 10:57 | 44391.3098 | 44391.3401 | 44391.3498 | 57.62 | 43.65 | 13.4 | 30.25 | 13.97 | 30 | -16.03 | 15 | -1.03 | 4517570294 | 2 | AM | 522 ARROYO GRANDE LN, SUISUN CITY | 2640 | 2640 |  |  |  | EXC - AXS OK; CTC Aiko Saito: 707-376-9023, DIS/REC 100A TO 100A - UG PNL CHG, L4L; REP: CYCC 530-228-6873; TMAN TO VERIFY INSP/ NOTIF #:120846713: - OK TO SERVE |  | insulate and isolate taped per electrician ok
|  |  | Completed | 4 | SAP DSP | 2021-07-14 06:29 |  | 2021-07-13 09:49 | 44391.3506 | 44391.3688 | 44391.4448 | 135.55 | 26.22 | 13.4 | 12.82 | 109.33 | 60 | 49.33 | 60 | 49.33 | S000765424 | 3 | AD | Flannery rd, Fairfield | S438 | S400 |  |  |  | Patrol Peabody-2107 between pole SAP 103956874 & 101582029. Pleasetake 3 or more photos from various angles during the patrol (more isbetter), even if you don¿t find obvious problems.Please upload pictures, your description of any findings, and repairtags into FAS,& Email to Steve Alexander at smas@pge.com.
|  |  | Completed | 1 | OIS DSP | 2021-07-14 10:27 |  | 2021-07-14 10:26 | 44391.4449 | 44391.4649 | 44391.5752 | 187.59 | 28.82 | 13.4 | 15.42 | 158.77 | 43 | 115.77 | 0 | 158.77 | T005341574 | 1 | AD | 5269 CLAYTON RD (FARM), FAIRFIELD | 9040 | 9002 |  |  |  | SMART MTR AUTO-GENERATED TAG |  | found no cause so i walked line a few times just to be sure and then refused and it held chk pwr ok
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:29 |  | 2021-05-06 10:59 | 44391.5753 | 44391.6013 | 44391.6317 | 81.27 | 37.42 | 13.4 | 24.02 | 43.85 | 35 | 8.85 | 20 | 23.85 | 4517480534 | 2 | AD | 522 ARROYO GRANDE LN, SUISUN CITY | 2220 | 2220 |  |  |  | EXC - AXS OK; CTC Aiko Saito: 707-376-9023, DIS/REC 100A TO 100A - UG PNL CHG, L4L; REP: CYCC 530-228-6873; TMAN TO VERIFY INSP/ NOTIF #:120846713: - OK TO SERVE |  | had to extend service panel to high spliced 1o/t ug service
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 11:21 |  | 2021-07-14 11:21 |  |  | 44391.5155 | [9 empty] | T005341647 | 1 | AD | 600 KENTUCKY ST, FAIRFIELD | 9150 |  |  |  |  | AXS-UNKNOWN CKD GATE/NO DOGS XSTR-UNION PWR-I CIA .. VOLTAGE ISSUES INSIDE POST OFFICE .. RESET BREAKER .. METER STATUS: INDETER MINATE .. DAMAGE TO POLE ON UNION AND LOUISIANA .. CONTACT CHRIS HERNANDON @ (707) 639-0798
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Vacaville | DECKER, VALERIE | Completed | 2 | 4APNWA1 | 2021-07-14 06:29 |  | 2021-07-01 13:53 | 44391.2999 | 44391.331 | 44391.3732 | 105.47 | 44.8 | 13.4 | 31.4 | 60.67 | 25 | 35.67 | 20 | 40.67 | 1768694572 | 2 | AD | 1376 Renewal Lane, FAIRFIELD | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 44; CONTACT: BEN SHARIF 925-787-1938, SUBDIVISION: MARIGOLD |  | CONNECT SET METER
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:29 |  | 2021-07-01 13:32 | 44391.3733 | 44391.3733 | 44391.3741 | 1.25 | 0.02 | 13.4 | -13.38 | 1.23 | 25 | -23.77 | 20 | -18.77 | 7000825496 | 2 | AD | 1365 RENEWAL LANE, FAIRFIELD | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 80; CONTACT: BEN SHARIF 925-787-1938, SUBDIVISION: MARIGOLD |  | CONNECT SET METER
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:29 |  | 2021-07-01 13:31 | 44391.3742 | 44391.3742 | 44391.3864 | 17.52 | 0.02 | 13.4 | -13.38 | 17.5 | 25 | -7.5 | 20 | -2.5 | 2027746477 | 2 | AD | 1361 Renewal Lane, FAIRFIELD | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 79; CONTACT: BEN SHARIF 925-787-1938, SUBDIVISION: MARIGOLD |  | CONNECT SET MTR
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:29 |  | 2021-07-01 13:31 | 44391.3865 | 44391.3865 | 44391.4036 | 24.67 | 0.02 | 13.4 | -13.38 | 24.65 | 25 | -0.35 | 20 | 4.65 | 1106954565 | 2 | AD | 1357 Renewal Lane, FAIRFIELD | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 78; CONTACT: BEN SHARIF 925-787-1938, SUBDIVISION: MARIGOLD |  | CONNECT SET MTR
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:29 |  | 2021-07-01 13:29 | 44391.4037 | 44391.4037 | 44391.407 | 4.73 | 0.03 | 13.4 | -13.37 | 4.7 | 25 | -20.3 | 20 | -15.3 | 5418696742 | 2 | AD | 1353 Renewal Lane, FAIRFIELD | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 77; CONTACT: BEN SHARIF 925-787-1938, SUBDIVISION: MARIGOLD |  | CONNECT SET MTR
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:29 |  | 2021-07-01 13:54 | 44391.4335 | 44391.4548 | 44391.4923 | 84.59 | 30.62 | 13.4 | 17.22 | 53.97 | 25 | 28.97 | 20 | 33.97 | 5154496573 | 2 | AD | 1349 Renewal Lane, FAIRFIELD | 2094 | 2094 |  |  |  | CON/SET; INSP OK-LOT 76; CONTACT: BEN SHARIF 925-787-1938, SUBDIVISION: MARIGOLD |  | CONNECT SET MTR
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:31 |  | 2021-06-23 13:52 | 44391.4925 | 44391.5309 | 44391.5631 | 101.67 | 55.3 | 13.4 | 41.9 | 46.37 | 25 | 21.37 | 20 | 26.37 | 9964719978 | 2 | AD | 618 BARNSTABLE DR, VACAVILLE | 2094 | 2094 |  |  |  | CON/SET; INSP OK--LOT 31; CONTACT: ,Adrea Vladyka 530-218-5040 SUBDIVISION: Cerrito at Vanden Estates. Use Waze directions |  | CONNECT SET MTR
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Vacaville | GUMATAOTAO, FRANK | Completed | 2 | 4APNWA1 | 2021-07-14 06:30 |  | 2021-06-09 14:19 | 44391.3031 | 44391.3129 | 44391.3635 | 87.01 | 14.13 | 13.4 | 0.73 | 72.88 | 30 | 42.88 | 5.6 | 67.28 | 4345417416 | 2 | AM | 7515 PADDON RD, VACAVILLE | 2640 | 0980 |  |  |  | EXC - AXS OK; CTC Aiko: 707-376-9023, DIS/REC 200A TO 200A - OH PNL CHG, L4L; REP: S0KA 530-401-4431; TMAN TO VERIFY INSP/ NOTIF #: 121424370 - OK TO SERVE |  | electricians to reschedule
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:30 |  | 2021-06-09 14:20 | 44391.4295 | 44391.4295 | 44391.4301 | 0.83 | 0.03 | 13.4 | -13.37 | 0.8 | 35 | -34.2 | 5.6 | -4.8 | 4349338625 | 2 | AD | 7515 PADDON RD, VACAVILLE | 2220 | 0980 |  |  |  | EXC - AXS OK; CTC Aiko: 707-376-9023, DIS/REC 200A TO 200A - OH PNL CHG, L4L; REP: S0KA 530-401-4431; TMAN TO VERIFY INSP/ NOTIF #: 121424370 - OK TO SERVE |  | cancel per electrician
|  |  | Completed | 1 | OIS DSP | 2021-07-14 12:22 |  | 2021-07-14 12:22 | 44391.5197 | 44391.533 | 44391.5581 | 55.3 | 19.17 | 13.4 | 5.77 | 36.13 | 52 | -15.87 | 0 | 36.13 | T005341720 | 1 | AD | 600 KENTUCKY ST, FAIRFIELD | 9150 | 9002 |  |  |  | AXS-UNKNOWN CKD GATE/NO DOGS XSTR-UNION PWR-I CIA .. VOLTAGE ISSUES INSIDE POST OFFICE .. RESET BREAKER .. METER STATUS: INDETER MINATE .. DAMAGE TO POLE ON UNION AND LOUISIANA .. CONTACT CHRIS HERNANDON @ (707) 639-0798 |  | dead squirel on arm/ blown fuse/ refu w/ 10E / check 3 phase power back on
|  |  | Completed | 1 | OIS DSP | 2021-07-14 13:19 |  | 2021-07-14 13:18 | 44391.5592 | 44391.5663 | 44391.6011 | 60.37 | 10.2 | 13.4 | -3.2 | 50.17 | 59 | -8.83 | 61.4 | -11.23 | T005341772 | 0 | AD | 4391 OLIVE AVE, FAIRFIELD | 9260 | 9260 |  |  |  | AXS-AXS UNSURE XSTR-OLIVE/TABER PWR-I SERVICE WIRE CAUGHT FIRE AND IS DOWN. CUSTOMER PUT OUT FIRE. |  | made EC tag for crew to replace oh svc x-ing street
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Vacaville | KLEIN, JACOB | Completed | 1 | AFW DSP | 2021-07-13 14:09 |  | 2021-07-13 14:09 | 44391.1915 | 44391.2389 | 44391.2777 | 124.1 | 68.25 | 13.4 | 54.85 | 55.85 | 120 | -64.15 | 0 | 55.85 | W107780001 | 2 | UD | , | W110 | W110 | [5 empty] | switching log 21-77800
|  |  | Completed | 1 | OIS DSP | 2021-07-14 08:47 |  | 2021-07-14 08:47 | 44391.3676 | 44391.4331 | 44391.4951 | 183.6 | 94.32 | 13.4 | 80.92 | 89.28 | 52 | 37.28 | 0 | 89.28 | T005341389 | 1 | AD | 17645 HWY 160, RIO VISTA | 9150 | 9002 |  |  |  | AXS-OK XSTR-TWITCHEL PWR-Y POSSIBLE LEG OUT - CHRIS LOGAN - MOBILE HOME PARK |  | 2 of 3 blwn #2 & #3 @12587. patrole found no cause. refused for test pwr OK
|  |  | Completed | 1 | AFW DSP | 2021-07-13 14:09 |  | 2021-07-13 14:09 | 44391.6085 | 44391.6085 | 44391.6093 | 1.13 | 0.03 | 13.4 | -13.37 | 1.1 | 120 | -118.9 | 5.6 | -4.5 | W107780002 | 2 | UD | , | W112 | 0930 | [5 empty] | DO said crew was going to do the goback
|  |  | Cancelled | 2 | 4APNWA1 | 2021-07-14 10:07 |  | 2021-07-14 09:59 |  |  | 44391.4286 | [9 empty] | 4206589709 | 1 | AD | 17645 HWY 160, RIO VISTA | 1210 |  |  |  |  | AXS OK;BIG PARK;CALL TO BE LED TO PUMP; HALF OF THE PARK IS OUT OF POWER; NORTH HALF OF THE STATE PARK;NO GFI SWITCH/CHECKED BRKRS FUSES;TALK TO I.J. DICKSON;PH: 9512556896 | PART OF OIS 1404101
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 10:12 |  | 2021-07-14 10:11 |  |  | 44391.4472 | [9 empty] | T005341541 | 1 | AD | 2420 W BRANNAN ISLAND RD, ISLETON | 9030 |  |  |  |  | AXS-OK XSTR-160 / TWICHELL PWR-I *PER ANDY GIANNINI SUPER FUSES OUT AT POLE E/O W BRANNAN ISLAND RD , 160* LEFT ON BRANNAN; STA TES IS FLOOR EMERGENCY AS THIS CIRCUIT FEEDS PUMP*SENSITIVE CUSTOMER *;7000 ACRES;PUMP OFF
|  |  | Reassigned | 1 | OIS DSP | 2021-07-14 10:12 |  | 2021-07-14 10:11 |  |  | 44391.4472 | [9 empty] | T005341542 | 1 | AD | 17645 HWY 160, RIO VISTA | 9150 |  |  |  |  | AXS-OK XSTR-TWITCHEL PWR-Y POSSIBLE LEG OUT - CHRIS LOGAN - MOBILE HOME PARK
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Vacaville | VIALE, JASON | Completed | 2 | 4APNWA1 | 2021-07-14 06:32 |  | 2021-06-23 11:43 | 44391.3066 | 44391.3248 | 44391.3533 | 67.25 | 26.28 | 13.4 | 12.88 | 40.97 | 30 | 10.97 | 15 | 25.97 | 4403773728 | 2 | AM | 140 E DEODARA ST, VACAVILLE | 2640 | 2640 |  |  |  | EXC - AXS OK, CTC MIRIAM (415) 637-7774. DIS/REC 100A TO 200A OH PNL UPG. REP: S9BF 916-634-5159; INSPECTION REQ NOTIF #: 121548249 |  | SERVICE DISCONNECTED, METER REMOVED
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:32 |  | 2021-06-17 08:13 | 44391.3642 | 44391.3682 | 44391.383 | 27.18 | 5.8 | 13.4 | -7.6 | 21.38 | 30 | -8.62 | 15 | 6.38 | 4341390615 | 2 | AM | 631 CORTE CASTRO, VACAVILLE | 2640 | 2640 |  |  |  | EXC - AXS OK; CTC: TRINI RAMIREZ: 909-277-8078, DIS/REC 125A TO 125A - UG PNL CHG, L4L; CUST TO ENSURE CLEAR/LEVEL WORKSPACE.REP: ALSE 916-767- 2513; TMAN TO VERIFY INSP/ NOTIF #: 121375174 |  | DISCONNECTED SERVICE, REMOVED METER
|  |  | Completed | 2 | SAP DSP | 2021-07-14 07:06 |  | 2021-07-13 21:21 | 44391.3911 | 44391.4071 | 44391.4446 | 77.1 | 23.07 | 13.4 | 9.67 | 54.03 | 60 | -5.97 | 60 | -5.97 | S000765443 | 3 | AD | VacaDixo n 1105, Vacaville | S438 | S400 |  |  |  | Inspect the equipment from pole w/ SAP #: 101599003 To pole w/ SAP#:101600438. Patrol map attached. ¿ Check for tree and bush clearance,indications of bird activity, sagging spans, insulator and crossarmdamage, etc.¿ Create tags for problem locations that are suspected to be thecause of the outages.¿ If no root cause is found then please identify potentialproblems along these sections. |  | SAGS ARE GOOD, NO DAMAGE TO ANYTHING, NO EVIDENCE OF BIRD ACTIVITY AND NO TREES IN THE PRIMARY.
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:32 |  | 2021-06-23 13:36 | 44391.4448 | 44391.4448 | 44391.4466 | 2.62 | 0.02 | 13.4 | -13.38 | 2.6 | 30 | -27.4 | 5.6 | -3 | 4464696936 | 2 | AM | 212 FERN WAY, VACAVILLE | 2640 | 0910 |  |  |  | EXC - AXS OK; CTC Ashley Donald: 707-595-8641, DIS/REC 200A TO 200A - UG PNL CHG, L4L; REP: CYCC 530-228-6873; TMAN TO VERIFY INSP/ NOTIF #:120921126: - OK TO SERVE |  | ELECTRICIAN STATES CANNOT DE ENERGIZE DUE TO NO ONE EIGHTEEN OR OLDER AT RESIDENCE.
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:32 |  | 2021-06-23 11:43 | 44391.6144 | 44391.6178 | 44391.6463 | 45.98 | 4.98 | 13.4 | -8.42 | 41 | 35 | 6 | 20 | 21 | 4404651832 | 2 | AD | 140 E DEODARA ST, VACAVILLE | 2220 | 2220 |  |  |  | EXC - AXS OK, CTC MIRIAM (415) 637-7774. DIS/REC 100A TO 200A OH PNL UPG. REP: S9BF 916-634-5159; INSPECTION REQ NOTIF #: 121548249 |  | RECONNECTED SERVICE AND SET METER
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 11:29 |  | 2021-07-14 11:27 | 44391.6464 | 44391.6496 | 44391.6539 | 10.73 | 4.58 | 13.4 | -8.82 | 6.15 | 31 | -24.85 | 21.9 | -15.75 | 4329844455 | 1 | AD | 372 KIRBYSON CT, VACAVILLE | 1240 | 1320 |  |  |  | INSPECTOR COURTNEY LUNA 510-301-6894; NEEDS GENERATOR DISCONNECTED THAT FEEDS #3 BOX IN FRONT OF THIS ADDRESS; CREW ON SITE REPLACING TRANSFORMER; OMC SUPERVISOR TOD DILLON REQUESTING; CALL COURTNEY WITH ANY QUESTIONS |  | ASSISTED CREW WITH BOX INSTALLATION. HERNANDEZ IS WATCHING THEM NOW.
|  |  | Completed | 1 | OIS DSP | 2021-07-14 13:50 |  | 2021-07-14 13:49 | 44391.6545 | 44391.6739 | 44391.683 | 41.03 | 28.03 | 13.4 | 14.63 | 13 | 30 | -17 | 16.6 | -3.6 | T005341805 | 1 | AD | 538 COOT LN, SUISUN CITY | 9030 | 9320 |  |  |  | AXS-AXS OKAY XSTR-HWY 12/ SNOW DR PWR-Y METER STATUS POWER ON , CUSTOMER TRIED BREAKERS AND FUSES, PWR STILL NOT ON, VACANT HOUS E LOCK BOX# 6727 |  | NO ANSWER AT DOOR OR PHONE. RE SET MAIN BREAKER. DID NOT CLOSE. LEFT TROUBLE REPORT INSTRUCTING CUSTOMER TO CLOSE THE BREAKER.
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:32 |  | 2021-06-17 08:14 | 44391.6836 | 44391.7071 | 44391.7141 | 43.98 | 33.95 | 13.4 | 20.55 | 10.03 | 35 | -24.97 | 20 | -9.97 | 4342902671 | 2 | AD | 631 CORTE CASTRO, VACAVILLE | 2220 | 2220 |  |  |  | EXC - AXS OK; CTC: TRINI RAMIREZ: 909-277-8078, DIS/REC 125A TO 125A - UG PNL CHG, L4L; CUST TO ENSURE CLEAR/LEVEL WORKSPACE.REP: ALSE 916-767- 2513; TMAN TO VERIFY INSP/ NOTIF #: 121375174 |  | SERVICE RECONNECTED, METER SET
|  |  | Completed | 1 | OIS DSP | 2021-07-14 17:52 |  | 2021-07-14 17:51 | 44391.7466 | 44391.7583 | 44391.782 | 51.08 | 16.95 | 13.4 | 3.55 | 34.13 | 44 | -9.87 | 16.6 | 17.53 | T005342000 | 1 | AD | 481 WILLAMETTE DR, VACAVILLE | 9130 | 9320 |  |  |  | AXS-AXS OK XSTR-ALAMO/SANDSTONE PWR-I FLICKERING LIGHTS; LIVING ROOM,GARAGE, LAUNDRY ROOM, DINING ROOM; METER STATUS INDETERMINA TE; NO CAUSE FOR FLICKERING |  | GOOD VOLTAGE, PASSED LOAD TEST. CUSTOMER STATES FLICKER IS OCCAIONALLY HAPPENING. CHANGED METER. OLD BADGE# 1010692660 NEW BADGE# 1011035409
|  |  | Completed | 2 | 4APKERA | 2021-07-14 18:45 |  | 2021-07-14 18:43 | 44391.7821 | 44391.7821 | 44391.7834 | 1.87 | 0.02 | 13.4 | -13.38 | 1.85 | 19 | -17.15 | 22.3 | -20.45 | 4374628977 | 1 | AD | 481 WILLAMETTE DR, VACAVILLE | 2002 | 1050 |  |  |  | FOR TMAN VIALE |  | OLD BADGE# 1010692660 NEW BADGE#1011035409
|  |  | Completed | 2 | 4APKERA | 2021-07-14 18:20 |  | 2021-07-14 18:10 | 44391.7838 | 44391.7984 | 44391.864 | 115.4 | 20.98 | 13.4 | 7.58 | 94.42 | 31 | 63.42 | 47.1 | 47.32 | 4617978825 | 1 | AD | 355 HOLLY CT, DIXON | 1240 | 1140 |  |  |  | No Access or Safety Issues; CSTMR STATES MELTING WIRES, CAME OUT AND MADE TEMP FIX, THEN FOREMAN CAME BACK OUT & SAID HAZZARD. NOTES DO NOT SHOW THIS..HIGH ANXIETY CSTMR. REQUESTING WE GO OUT ASAP TO MAKE SAFE OR SHUT MAIN OFF. |  | CREW TO LOCATE AND REPAIR 1/0 NEUTRAL
|  |  | Completed | 1 | OIS DSP | 2021-07-14 21:17 |  | 2021-07-14 21:13 | 44391.8881 | 44391.8991 | 44391.9687 | 116.05 | 15.77 | 13.4 | 2.37 | 100.28 | 30 | 70.28 | 0 | 100.28 | T005342099 | 1 | AD | 7340 STOCKING LN, VACAVILLE | 9030 | 9002 |  |  |  | , PWR-I |  | PATROLLED AND FOUND NOTHING. GOOD TEST
|  |  | Cancelled | 2 | 4APNWA1 | 2021-07-14 06:32 |  | 2021-06-23 13:38 |  |  | 44391.5652 | [9 empty] | 4461204321 | 2 | AD | 212 FERN WAY, VACAVILLE | 2220 |  |  |  |  | EXC - AXS OK; CTC Ashley Donald: 707-595-8641, DIS/REC 200A TO 200A - UG PNL CHG, L4L; REP: CYCC 530-228-6873; TMAN TO VERIFY INSP/ NOTIF #:120921126: - OK TO SERVE
Woodland
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
6 | Woodland | GUTIERREZ, MIGUEL | Completed | 1 | AFW DSP | 2021-07-13 13:45 |  | 2021-07-13 13:44 | 44391.2126 | 44391.3044 | 44391.3423 | 186.78 | 132.13 | 14.5 | 117.63 | 54.65 | 120 | -65.35 | 0 | 54.65 | W106766303 | 2 | UD | , | W110 | W110
|  |  | Completed | 4 | 4APNWA1 | 2021-07-14 06:41 |  | 2021-06-18 12:16 | 44391.3425 | 44391.3566 | 44391.3875 | 64.83 | 20.43 | 14.5 | 5.93 | 44.4 | 30 | 14.4 | 15 | 29.4 | 5226975710 | 2 | AM | 4061 VISTA WAY, DAVIS | 2640 | 2640 |  |  |  | EXC - AXS OK; CTC ROBIN @559-335-4589; DIS/REC 125A TO 125A - UG PNL CHG, L4L; REP: JNK3 916-599-2202; TMAN TO VERIFY INSP/ NOTIF #: 000120771878 - OK TO SERVE |  | power off
|  |  | Completed | 1 | OIS DSP | 2021-07-14 08:36 |  | 2021-07-14 08:36 | 44391.3876 | 44391.3939 | 44391.3957 | 11.65 | 9.07 | 14.5 | -5.43 | 2.58 | 30 | -27.42 | 16.6 | -14.02 | T005341368 | 1 | AD | 24146 COUNTY ROAD 95, DAVIS | 9030 | 9320 |  |  |  | SMART MTR AUTO-GENERATED TAG |  | no pge issue
|  |  | Completed | 1 | AFW DSP | 2021-07-13 13:45 |  | 2021-07-13 13:44 | 44391.5077 | 44391.5102 | 44391.5111 | 4.85 | 3.62 | 14.5 | -10.88 | 1.23 | 120 | -118.77 | 5.6 | -4.37 | W106766304 | 2 | UD | , | W112 | 0980
|  |  | Completed | 4 | 4APNWA1 | 2021-07-14 06:41 |  | 2021-06-18 12:17 | 44391.5894 | 44391.6189 | 44391.6525 | 90.85 | 42.57 | 14.5 | 28.07 | 48.28 | 35 | 13.28 | 20 | 28.28 | 5226628789 | 2 | AD | 4061 VISTA WAY, DAVIS | 2220 | 2220 |  |  |  | EXC - AXS OK; CTC ROBIN @559-335-4589; DIS/REC 125A TO 125A - UG PNL CHG, L4L; REP: JNK3 916-599-2202; TMAN TO VERIFY INSP/ NOTIF #: 000120771878 - OK TO SERVE |  | power on
|  |  | Completed | 2 | 4APKERA | 2021-07-14 16:11 |  | 2021-07-14 16:02 | 44391.6991 | 44391.7106 | 44391.7286 | 42.42 | 16.5 | 14.5 | 2 | 25.92 | 27 | -1.08 | 37.4 | -11.48 | 0245229881 | 0 | AD | 5316 FOX RIDGE CT, FAIRFIELD | 1050 | 1057 |  |  |  | Access/Safety: Dog(s);POSSIBLE ARCING AT METER/ELECTRICIAN ON SITE/ BLACKENED METER/ X STREETS: BRITTLE RIDGE AND BAY RIDGE. CUST NAME: HARGURJIT CONTACT NUMBER 7074004359 |  | NG meter
|  |  | Completed | 2 | 4APKERA | 2021-07-14 17:24 |  | 2021-07-14 17:22 | 44391.7292 | 44391.7293 | 44391.7315 | 3.3 | 0.07 | 14.5 | -14.43 | 3.23 | 28 | -24.77 | 25 | -21.77 | 0244122039 | 1 | AD | 5316 FOX RIDGE CT, FAIRFIELD | 2000 | 2000 |  |  |  | for tman gutierrez |  | back of meter damaged. Screen blank. Power ok after changing meter
|  |  | Completed | 2 | 4APKERA | 2021-07-14 17:06 |  | 2021-07-14 17:01 | 44391.7468 | 44391.7468 | 44391.7626 | 22.82 | 0.05 | 14.5 | -14.45 | 22.77 | 31 | -8.23 | 32.2 | -9.43 | 4506279357 | 1 | AD | 1643 SAN BRUNO ST, FAIRFIELD | 1240 | 1010 |  |  |  | Access/Safety: Dog(s);WOODEN POLE LEANING FROM NEIGHBORS HOUSE, LEANING BECOMING GREATER NOW ON TO FENCE AREA.BETWEEN THIS ADDRESS AND NEXT DOOR |  | Tag created for crew to replace backyard pole
|  |  | Completed | 1 | OIS DSP | 2021-07-14 17:43 |  | 2021-07-14 17:43 | 44391.7628 | 44391.7749 | 44391.7756 | 18.48 | 17.4 | 14.5 | 2.9 | 1.08 | 30 | -28.92 | 16.6 | -15.52 | T005341998 | 0 | AD | 1600 KIDDER AVE, FAIRFIELD | 9250 | 9320 |  |  |  | AXS-AXS OK XSTR-SAN MARCOS ST PWR-Y AXS OK, DOWNED POWER LINE ON THE CORNER OF SAN MARCOS ST , KIDDER AVE, POLE TO POLE NOT IN A NY BRANCHES/TREES AND NOT OVER A BUILDING, CUSTOMER WAS DRIVING BY AND CALLED IT IN, TANIA 707-249-2880 |  | power ok. cable tx line. Not PGE issue
|  |  | Completed | 1 | OIS DSP | 2021-07-14 21:24 |  | 2021-07-14 21:23 | 44391.8939 | 44391.9369 | 44391.939 | 65.01 | 61.93 | 14.5 | 47.43 | 3.08 | 30 | -26.92 | 5.6 | -2.52 | T005342105 | 1 | AD | RICH ISLAND, SUISUN CITY | 9030 | 0980 |  |  |  | AXS-UNKNOWN XSTR-UNKNOWN PWR-I CIA NO POWER- CALL DROPPED COUND NOT SUPPLY SAFETY INFO - MR WATERS CALLED FROM NUMBER BELOW- POS S ISODUCK CLUB-- NO OTHER INFO FOUND |  | grizzley island. customer will need to call in during the day
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Woodland | HESTEAD, NICK | Completed | 2 | 4APNWA1 | 2021-07-14 06:26 |  | 2021-07-08 11:16 | 44391.3373 | 44391.3442 | 44391.3527 | 22.17 | 9.9 | 14.5 | -4.6 | 12.27 | 30 | -17.73 | 15 | -2.73 | 5416332703 | 2 | AM | 22 MARYLAND AVE, WOODLAND | 2640 | 2640 |  |  |  | EXC - AXS OK; CTC SUSAN GONZALEZ: 530-304-4078, DIS/REC 100A TO 100A - UG PNL CHG, L4L; REP: NRA6 916-406-4053; TMAN TO VERIFY INSP/ NOTIF #: 121675733 - OK TO SERVE |  | DISCO SRV AT SPLICER FOR PAN UP
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Woodland | RAPADAS, ANTHONY | Completed | 4 | 4APKERA | 2021-07-14 15:24 |  | 2021-07-08 11:17 | 44391.6497 | 44391.6522 | 44391.6666 | 24.31 | 3.63 | 14.5 | -10.87 | 20.68 | 35 | -14.32 | 35 | -14.32 | 5419474956 | 2 | AD | 22 MARYLAND AVE, WOODLAND | 2220 | 2220 | 2002 |  |  | EXC - AXS OK; CTC SUSAN GONZALEZ: 530-304-4078, DIS/REC 100A TO 100A - UG PNL CHG, L4L; REP: NRA6 916-406-4053; TMAN TO VERIFY INSP/ NOTIF #: 121675733 - OK TO SERVE | NO INSPECTIONS AS OF 1522. ALSO NEEDS NEW METER | 2220
|  |  | Completed | 1 | OIS DSP | 2021-07-14 18:45 |  | 2021-07-14 18:45 | 44391.8704 | 44391.8833 | 44391.8934 | 33.15 | 18.55 | 14.5 | 4.05 | 14.6 | 32 | -17.4 | 5.6 | 9 | T005342036 | 0 | AD | 508 F ST, DAVIS | 9190 | 0980 |  |  |  | A:OK;X:5TH AND F ST;R:DAVIS CITY TREE - TREE TYPE DUTCH ELM TREE 150 YEARS OLD; CALLED CITY IN THE MORNIN BUT REFUSE TO RESPOND - TREE ALIVE AND LYING ON THE WIREIF IMMEDIATE THREAT PLZ ADVISE RESIDENTS, LANDLORD CALLED IN. |  | CITY OF DAVIS TREE HAS A CRACKED BRANCH... NOT TOUCHING ANY POWER LINES... CALLED CITY OF DAVIS URBAN FORESTRY DIVISION FOR CUST AND LEFT MESSAGE WITH ALL NECESSARY INFORMATION
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Woodland | SHIELDS, SPENCER | Completed | 2 | 4APKERA | 2021-07-14 16:27 |  | 2021-07-14 16:24 | 44391.689 | 44391.689 | 44391.6895 | 0.75 | 0.03 | 14.5 | -14.47 | 0.72 | 37 | -36.28 | 5.6 | -4.88 | 5063401258 | 1 | AD | 1228 SACRAMENTO AVE, WEST SACRAME | 1040 | 0980 |  |  |  | AXS OK P/ANNA LARA UNIT # 35; COMPLETE OUTAGE. SENT SIGNAL TO METER; METER ON. # 916-513-9651 |  | trailer park cust breaker issue
Tech Info |  |  | Dispatch Info |  |  |  |  | FO Timestamp Info |  |  |  | Elapsed Times | [8 empty] | Order Info
Area | HQ | Tech | Order State | Order Dispatch Count | Dispatch User ID | Last Dispatch Timestamp | Returned to Pending | Date Taken Timestamp | Enroute Time | Onsite Time | Completed Time | Total Time Billed To Order | En Route Minutes | Expected HQ Drive Time | Variance | On Site Minutes | Expected Job Time Issued | Variance | Total Expected CC Time | Variance | Order Number | Priority | Appointment Window | Address | Job Code 1 | CC1 | CC2 | CC3 | CC4 | Office Remarks | Dispatcher Remarks | Tech Remarks
| Woodland | WILLIAMS, MICAH | Completed | 1 | AFW DSP | 2021-07-13 13:45 |  | 2021-07-13 13:44 | 44391.2159 | 44391.2553 | 44391.3466 | 188.24 | 56.67 | 14.5 | 42.17 | 131.57 | 120 | 11.57 | 0 | 131.57 | W106766301 | 2 | UD | , | W110 | W110
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 07:33 |  | 2021-07-14 07:27 | 44391.3467 | 44391.3618 | 44391.3656 | 27.22 | 21.77 | 14.5 | 7.27 | 5.45 | 29 | -23.55 | 15.9 | -10.45 | 0791579678 | 0 | AD | 1570 S RIVER RD, WEST SACRAME | 1160 | 1161 |  |  |  | No Access or Safety Issues; POLE TO POLE; PUBLIC SAFETY; LOW WIRE (POLE #341349) 8FT ONTO THE LANE; PER CALLER VEHICLE WRECKED INTO FENCE THIS MORNING AT RAMOS OIL COMPANY; JEROMY SHEPLER (DRIVING BY & ALSO A CITY EMPLOYEE) |  | att pole =non pge
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 06:28 |  | 2021-07-12 09:37 | 44391.3658 | 44391.3728 | 44391.397 | 44.9 | 10.12 | 14.5 | -4.38 | 34.78 | 30 | 4.78 | 15 | 19.78 | 5189455660 | 2 | AM | 833 WATER ST, WEST SACRAME | 2640 | 2640 |  |  |  | EXC AXS OK; CUST ROSE 530-417-7482; DIS SVC FROM W/H FOR MTR 1003845990, NO PNL CHANGE, NO INSP REQ; REP MQ1W 209-272-8699; NOTIF 121640380 |  | removed seervice which was disconnected perviously duuue to structure fire
|  |  | Completed | 1 | AFW DSP | 2021-07-13 13:45 |  | 2021-07-13 13:44 | 44391.3971 | 44391.3971 | 44391.3978 | 0.98 | 0 | 14.5 | -14.5 | 0.98 | 120 | -119.02 | 5.6 | -4.62 | W106766302 | 2 | UD | , | W112 | 0980 | [5 empty] | cancel per woodland construction no parts
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 11:54 |  | 2021-07-14 11:50 | 44391.4997 | 44391.5268 | 44391.5598 | 86.45 | 39 | 14.5 | 24.5 | 47.45 | 27 | 20.45 | 22.3 | 25.15 | 5408987041 | 0 | AD | 2647 BRANNAN WAY, WEST SACRAME | 1050 | 1050 |  |  |  | Access/Safety: Dog(s); POSSIBLE ARCING METER, CONTRACTOR ON SITE STATES PANEL IS ARCING AS HE WAS TURNING ON THE PANEL , XST: CONSTITUTION, |  | part of the customer meter socket is damaged need to fix and then reconnected
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 13:26 |  | 2021-07-14 13:24 | 44391.5604 | 44391.5604 | 44391.5632 | 3.94 | 0.02 | 14.5 | -14.48 | 3.92 | 30 | -26.08 | 15 | -11.08 | 5404768729 | 1 | AD | 2647 BRANNAN WAY, WEST SACRAME | 2640 | 2640 |  |  |  | GIVE TO WILLIAMS |  | customer need to repair service
|  |  | Completed | 1 | OIS DSP | 2021-07-14 12:00 |  | 2021-07-14 11:59 | 44391.5632 | 44391.5686 | 44391.6127 | 71.28 | 7.78 | 14.5 | -6.72 | 63.5 | 32 | 31.5 | 31.1 | 32.4 | T005341697 | 0 | AD | 2328 DIABLO ST, WEST SACRAME | 9190 | 9190 |  |  |  | AXS-DOG XSTR- PWR-Y P/PROP MANAGEMENT (KAITLYN) -LARGE MULBERRY TREE BRNCHES COMING INTO CONTACT W/ SERVCE DROP; CAUSING FLICKER ING LIGHTS |  | repared service
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 14:23 |  | 2021-07-14 14:19 | 44391.613 | 44391.6928 | 44391.7011 | 126.92 | 114.97 | 14.5 | 100.47 | 11.95 | 28 | -16.05 | 15 | -3.05 | 8248518185 | 2 | AD | .5 MI E/BUCKEYE RD S/S RD, WINTERS | 2090 | 2090 |  |  |  | GIVE TO TMAN WILLIAMS - RECONNECT AT TX |  | connected service
|  |  | Completed | 2 | 4APNWA1 | 2021-07-14 14:23 |  | 2021-07-14 14:22 | 44391.7012 | 44391.7013 | 44391.7022 | 1.35 | 0.02 | 14.5 | -14.48 | 1.33 | 25 | -23.67 | 25 | -23.67 | 8247758205 | 1 | AD | .5 MI E/BUCKEYE RD S/S RD, WINTERS | 2056 | 2056 |  |  |  | GIVE TO TMAN WILLIAMS - FOLLOW UP TO FO ID 8248518185 |  | set new meter
|  |  | Completed |  | 4APNWA1 | 2021-09-21 11:28 |  | 2021-09-02 14:56 | 44460.4828 | 44460.4828 | 44460.4836 | 1.04 | 0.02 | 14.5 | -14.48 | 1.02 | 35 | 1.02 | 20 | 1.02 | 4258002431 | 2 | AD | 1001 OPAL DR, VACAVILLE | 2220 | 2220 |  |  |  | DISC/RECO - UG -L4L - OK TO SERVE EXC - AXS OK ; CTC; Tamree: 707-305-4817;DIS/REC 200A TO 200A-UG PNL CHG, L4L; REP: ALFI 916 618-3201; TMAN TO VERIFY INSP/ NOTIF# 121960028: | T-MAN GUMATAOTAO COMPLETED THIS JOB ON 09/20/21-HE IS HAVING FAS ISSUES | resonnect completed by Frank
|  |  | Completed |  | 4APNWA1 | 2021-09-21 11:28 |  | 2021-08-31 16:27 | 44460.4838 | 44460.4838 | 44460.4845 | 1.02 | 0.02 | 14.5 | -14.48 | 1 | 35 | 1 | 20 | 1 | 4039856129 | 2 | AD | 2425 MANKAS BLVD, FAIRFIELD | 2220 | 2220 |  |  |  | No Access or Safety Issues; EXC AXS OK; CUST CHRISTOPHER 707-474-4800; DIS/REC L4L 100 PNL CHG, INSP REQ; REP SRRQ 2092728553; NOTIF 121974419 | T-MAN GUMATAOTAO COMPLETED THIS JOB ON 09/20/21-HE IS HAVING FAS ISSUES | T-MAN GUMATAOTAO COMPLETED THIS JOB ON 09/20/21-HE IS HAVING FAS ISSUES